	[image: image8.jpg]logics




In Vitro Report

Title:  ENVIRONMENTAL MONITORING REPORT – Q3  2008
	Doc: 
Rev: A

Page 2 of 12



1.0 PURPOSE
The purpose of this procedure is to evaluate conformance to 67-0297 CER Environmental Monitoring, and to archive the applicable reports of analysis and Medlogics Device Corporation’s (MDC) CER Differential Pressure logs.  

2.0 REFERENCES

67-0297

CER Environmental Monitoring

EMS Report L1204
Report of Analysis 7/21/2008
EMS Report L1214
Report of Analysis 9/04/2008

EMS Report L1216
Report of Analysis 9/22/2008


3.0 DISCUSSION

The data in this report contains 7/2/08 through 9/30/08.  Airstrip count, contact plate count, and particle counts are reported from Environmental Monitoring Services with different analysis dates.    
3.1 CER Airstrip Count

Figure 1 shows the average monthly airstrip counts for combined bacterial and fungal counts for the three CERs.  As can be seen from the plots, total counts range from approximately 2 to 12 counts of the combined bacterial and fungal analysis.  The range above is in compliance with the specification limits for alert and action limits established by 67-0297 CER Environmental Monitoring. 
3.2 CER Contact Plate Count

Figure 2 shows the average monthly contact plate counts for combined bacterial and fungal counts for the three CERs.  As can be seen from the plots, total counts range from below 1 to approximately 4, in compliance with specification limits for alert action limits established by 67-0297 CER Environmental Monitoring.
3.3 CER Particulate Counts

Figure 3 and 4 shows the average monthly 0.5μm/ft3 and 5.0μm/ft3 particulate counts for the three CERs, respectively.  As can be seen from Figures 3 and 4, the monthly average counts are in compliance with the specification limits for alert and action limits established by 67-0297 CER Environmental Monitoring for CERs1 and 3, which are different from CER2 requirements.
3.4 CER Differential Pressure

Figures 5 and 6 show the daily and average monthly (respectively) differential pressure values for the three CERs and for the CER changing room.  As can be seen from the plots, all pressure differential values are in compliance with the specifications of 67-0297 CER Environmental Monitoring except CER1.  In late July, CER 1 differential pressure fell below the alert level.  The values remained above the action level. CER 1 was investigated. No other action was taken.  
3.5 CER2 Biosafety Cabinet Differential Pressure

Figures 7 and 8 show the daily and average monthly (respectively) differential pressure values (and downflow and exhaust values, as applicable) for the four biosafety cabinets in CER2.  As can be seen from the plots, R&D Bio-Safety Cabinet North reached Alert level in figure 7. All other pressure differential values are in compliance with the specifications of 67-0297 CER Environmental Monitoring.  
 An investigation revealed that the Mfg. bio-safety cabinet South is malfunctioning, and is currently out of service while undergoing repairs.   
[image: image1.emf]0

1

2

3

4

5

6

7

1/3/08 2/3/08 3/5/08 4/5/08 5/6/08 6/6/08 7/7/08 8/7/08 9/7/08

Contact Plate Count

Date

Figure 2. Average Contact Plate Count

CER 1

CER 2

CER 3

Alert Level

Action Level






 EMBED Excel.Sheet.8  
[image: image10.png]Figure 1. Average Airstrip Count

45
40
35
30
" —+—CER1
c CER2
325 CER3
g ~ Alert Level
—Action Level
i
520
o
o
S15
]
I
10 +—
5
0 T T T T T
1/3/08 2/22/08 4/12/08 6/1/08 7/21/08 9/9/08

Date




[image: image4.emf]0

0.02

0.04

0.06

0.08

0.1

0.12

Diff. Pressure (Water Column In.)

Date

Figure 5.  CER Differential Pressure Daily Run Chart

CER1

CER Change Room

CER2

CER3

CER Alert Level

CER Action Level



[image: image5.emf]0.000

0.010

0.020

0.030

0.040

0.050

0.060

0.070

0.080

0.090

0.100

Diff. Pressure (Water Column In.)

Date

Figure 6.  CER Differential Pressure -Monthly Average

CER1

CER Change Room

CER 2

CER 3

CER Alert Level

CER Action Level



[image: image6.emf]0

100

200

300

400

500

600

700

800

900

1000

1100

1200

1300

0

0.1

0.2

0.3

0.4

0.5

0.6

0.7

Jan-08 Feb-08 Mar-08 Apr-08 May-08 Jun-08 Jul-08 Aug-08 Sep-08

Mfg Bio

-

Safety Cabinet South CFM

Diff. Pressure (Water Column In.)

Date

Figure 7.  CER2 Bio-Safety Cabinet Differential Pressure Daily Run Chart

Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet North (left axis)

R&D Bio-Safety Cabinet South (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)



[image: image7.emf]-100

100

300

500

700

900

1100

1300

0

0.1

0.2

0.3

0.4

0.5

0.6

0.7

Mfg Bio

-

Safety Cabinet (cfm)

Diff. Pressure (Water Column In.)

Date

Figure 8.  Bio-Safety Cabinet Differential Pressure -Monthly Average

Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

R&D Bio-Safety Cabinet South (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)








[image: image8.jpg][image: image9.jpg]logics



_1294660023.xls
Airstrip Count

		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148

		39206		39206		39206		39148		39148

		39230		39230		39230		39167		39167

		39267		39267		39267		39206		39206

		39297		39297		39297		39230		39230

		39349		39349		39349		39267		39267

		39392		39392		39392		39297		39297

		39427		39427		39427		39349		39349

		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713



CER 1

CER 2

CER3

Alert Level

Action Level

Date

Average CER Count

Figure 1.  Average Airstrip Count

3.625

6

29

10

15

5.375

7.5

28

10

15

13.125

13.25

28.75

10

15

13.25

11

27.75

10

15

4.25

5.25

24.5

10

15

4

1.75

11.75

10

15

4.25

9.25

10

15

19.5

5.5

22.5

10

15

5.75

4.25

13

10

15

3.25

1

4.75

10

15

11.625

8

18.25

10

15

3.875

1.75

10.5

10

15

4.125

2

10

35

45

1.125

0.5

3.5

35

45

3

1.25

6.5

35

45

3.25

0.75

5.25

35

45

2

0.75

2.75

35

45

6.375

1.75

8.25

35

45

13.5

1.25

10.25

35

45

2.6666666667

2.6666666667

11.25

35

45

6.2

4

3.75

35

45

6.2666666667

2

3.75

35

45

7.6666666667

3

7.5

35

45

9.4

2.8888888889

9

35

45

8.4

3.4444444444

6.5

35

45

6.5333333333

2.3333333333

8.5

35

45



Contact Plate Count

		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148

		39206		39206		39206		39148		39148

		39230		39230		39230		39167		39167

		39267		39267		39267		39206		39206

		39297		39297		39297		39230		39230

		39349		39349		39349		39267		39267

		39392		39392		39392		39297		39297

		39427		39427		39427		39392		39392

		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

Alert Level

Action Level

Date

Contact Plate Count

Figure 2. Average Contact Plate Count

1.4285714286

0.25

2.5

10

15

3.7142857143

2.75

4

10

15

1.1428571429

1.75

0.8333333333

10

15

2.4285714286

3

2.5

10

15

2.4285714286

0.75

3.1666666667

10

15

5.5714285714

3.25

5

10

15

5.2857142857

5.2

10

15

2.7142857143

1.5

2

10

15

1.1428571429

0

2

10

15

3.1428571429

1

3.25

10

15

3.4285714286

3.25

2.25

10

15

1.5714285714

0.75

1.5

10

15

1.7142857143

1

2.25

6

7

0.5714285714

0.5

2.25

6

7

1.5714285714

0.5

3

6

7

2

0.75

2.5

6

7

0.7142857143

0.25

1.75

6

7

3.4285714286

1.25

3.25

6

7

4

1

3.75

6

7

1.5333333333

1

3

6

7

2

1

2.25

6

7

1.7333333333

0.6666666667

1.5

6

7

0.9333333333

0.4444444444

1.5

6

7

0.9333333333

0.7777777778

2.5

6

7

1.1333333333

0.6666666667

1.75

6

7

0.9333333333

0.6666666667

1.5

6

7



0.5micron Count

		38776		38776		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126		39126		39126

		39148		39167		39167		39148		39148		39148		39148

		39148		39206		39206		39148		39148		39148		39148

		39167		39230		39230		39167		39167		39167		39167

		39206		39267		39267		39206		39206		39206		39206

		39230		39297		39297		39230		39230		39297		39297

		39267		39349		39349		39267		39267		39349		39349

		39297		39392		39392		39297		39297		39392		39392

		39392		39427		39427		39392		39392		39427		39427

		39545		39545		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

CER 1,3 Alert Level

CER 1,3 Action Level

CER 2 Alert Level

CER 2 Action Level

Date

0.5um/cu ft Count

Figure 3.  Average 0.5mm/cu ft Count

194

383

3263.8

5000

10000

5000

10000

339.5

338.3333333333

1210.4

5000

10000

5000

10000

362.75

719.3333333333

2800.4

5000

10000

5000

10000

688.125

416.3333333333

1999.6

5000

10000

5000

10000

618.75

336.6666666667

2033

5000

10000

5000

10000

692.625

1000

1857.4

5000

10000

5000

10000

401.375

1423.2

5000

10000

5000

10000

523.125

842

2313.2

5000

10000

5000

10000

273

292.3333333333

624.4

5000

10000

5000

10000

588.875

620

1580.4

5000

10000

5000

10000

714

474.6666666667

1255.6

5000

10000

5000

10000

755.625

587.3333333333

1139.8

5000

10000

5000

10000

772.875

643

1484

3800

4500

1250

1500

244

896.6666666667

1571.2

3800

4500

1250

1500

551.75

704.3333333333

2714

3800

4500

1250

1500

678.625

553

1781.8

3800

4500

1250

1500

369.625

300

731.6

3800

4500

1250

1500

664

478

1178.6

3800

4500

1250

1500

835.625

525

1260.6

3800

4500

1250

1500

699

83.7777777778

1354.8

3800

4500

1250

1500

635

204.4444444444

620.8

3800

4500

1250

1500

606

181.3333333333

750.8

3800

4500

1250

1500

606

109.5555555556

474.6

3800

4500

1250

1500

612.0666666667

156.7777777778

659.8

3800

4500

1250

1500

285.1333333333

190.5555555556

945.2

3800

4500

1250

1500

474

216.3333333333

768.6

3800

4500

1250

1500



5.0micron Count

		38776		38776		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148		39148		39148

		39206		39206		39206		39148		39148		39148		39148

		39230		39230		39230		39167		39167		39167		39167

		39267		39267		39267		39206		39206		39267		39267

		39297		39297		39297		39230		39230		39297		39297

		39349		39349		39349		39267		39267		39349		39349

		39392		39392		39392		39297		39297		39392		39392

		39427		39427		39427		39392		39392		39427		39427

		39545		39545		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

CER 1,3 Alert Level

CER 1,3 Action Level

CER 2 Alert Level

CER 2 Action Level

Date

5.0um/cu ft Count

Figure 4.  Average 5.0mm/cu ft Count

14.125

48.6666666667

226.8

30

50

30

50

33.625

49.3333333333

104.4

30

50

30

50

36.25

49

211.4

30

50

30

50

126.75

76.6666666667

305.2

30

50

30

50

67.875

37.3333333333

344.6

30

50

30

50

71.75

72.3333333333

166.4

30

50

30

50

43.5

235

30

50

30

50

65.125

37.3333333333

219.4

30

50

30

50

33.125

31.3333333333

50.6

30

50

30

50

47.75

50.6666666667

99.4

30

50

30

50

43.875

32.3333333333

79.2

30

50

30

50

47.125

44.3333333333

92.8

30

50

30

50

49

43.3333333333

92.2

410

500

90

105

30.75

75.6666666667

129.2

410

500

90

105

78.875

89

258.4

410

500

90

105

60

44

147

410

500

90

105

28.375

22.6666666667

53

410

500

90

105

26.125

20.3333333333

58

410

500

90

105

45.125

24.3333333333

80.8

410

500

90

105

37.3333333333

10

69.2

410

500

90

105

34.6

12.5555555556

33.2

410

500

90

105

29

9.3333333333

34

410

500

90

105

29

7.1111111111

33

410

500

90

105

30.0666666667

8.8888888889

27.6

410

500

78

83

18.7333333333

11.5555555556

43.4

410

500

78

83

24.3333333333

9.8888888889

37.6

410

500

78

83



CER 1

				AIRSTRIPS:																																																																																																		CONTACT PLATES:																																																																																																		PARTICLE COUNTS

				A						B						C						D						E						F						G						H						I						J						K						L						M						N						O						Average								A						B						C						D						E						F						G						H						I						J						K						L						M						N						O						Average								A				B				C				D				E				F				G				H				I				J				K				L				M				N				O				Average

		Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 1		Date		Alert Level		Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 1		Date		Alert Level		Action Level		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		CER 1 0.5um/ cu ft		Date		CER 1,3 Alert Level		CER 1,3 Action Level		CER 1 5.0um/cu ft		Date		CER 1,3 Alert Level		CER 1,3 Action Level

		2/28/06		2		0		2		4		0		4		5		0		5		4		0		4		8		0		8		0		0		0		3		0		3		3		0		3																																												4		2/28/06		10		15		0		0		0		0		0		0		1		0		1		0		0		0		2		0		2		0		0		0		3		0		3		4		0		4						0						0						0						0						0						0						0		1		2/28/06		10		15		207		8		291		16		133		12		278		21		134		13		25		5		262		22		222		16																														194		02/28/06		5000		10000		14		2/28/06		30		50

		3/30/06		4		0		4		4		0		4		7		0		7		6		0		6		10		0		10		2		0		2		6		0		6		4		0		4																																												5		3/30/06		10		15		1		0		1		3		0		3		6		0		6		3		0		3		2		0		2		5		0		5		3		0		3		3		0		3						0						0						0						0						0						0						0		4		3/30/06		10		15		310		48		483		69		134		18		263		24		444		31		679		40		199		8		204		31																														340		03/30/06		5000		10000		34		3/30/06		30		50

		4/28/06		4		0		4		12		0		12		12		0		12		15		0		15		17		0		17		6		4		10		12		0		12		23		0		23																																												13		4/28/06		10		15		0		0		0		2		0		2		2		0		2		0		0		0		0		0		0		0		0		0		4		0		4		0		0		0						0						0						0						0						0						0						0		1		4/28/06		10		15		487		81		221		21		261		19		390		32		480		60		287		23		321		19		455		35																														363		04/28/06		5000		10000		36		4/28/06		30		50

		5/30/06		6		0		6		10		0		10		12		0		12		17		0		17		19		0		19		9		0		9		12		0		12		21		0		21																																												13		5/30/06		10		15		1		0		1		4		0		4		3		0		3		0		0		0		1		0		1		0		0		0		7		0		7		1		0		1						0						0						0						0						0						0						0		2		5/30/06		10		15		678		124		1084		137		214		36		113		21		1478		449		220		32		1009		120		709		95																														688		05/30/06		5000		10000		127		5/30/06		30		50

		7/7/06		4		0		4		2		0		2		6		0		6		4		0		4		8		0		8		1		0		1		4		0		4		5		0		5																																												4		7/7/06		10		15		1		0		1		2		0		2		1		0		1		2		0		2		2		0		2		1		0		1		4		0		4		4		0		4						0						0						0						0						0						0						0		2		7/7/06		10		15		631		86		779		72		1234		81		282		38		464		75		694		93		564		65		302		33																														619		07/07/06		5000		10000		68		7/7/06		30		50

		9/5/06		4		0		4		4		0		4		6		0		6		5		0		5		2		0		2		2		0		2		4		0		4		5		0		5																																												4		9/5/06		10		15		4		0		4		6		0		6		4		0		4		3		0		3		6		0		6		5		0		5		5		0		5		6		0		6						0						0						0						0						0						0						0		6		9/5/06		10		15		1056		113		622		73		227		35		828		84		603		57		875		95		545		56		785		61																														693		09/05/06		5000		10000		72		9/5/06		30		50

		10/5/06		5		0		5		4		0		4		4		0		4		5		0		5		6		0		6		4		0		4		3		0		3		3		0		3																																												4		10/5/06		10		15		5		0		5		6		0		6		4		0		4		4		0		4		5		0		5		3		0		3		6		0		6		4		0		4						0						0						0						0						0						0						0		5		10/5/06		10		15		122		14		263		18		352		48		540		69		361		38		421		63		389		41		763		57																														401		10/05/06		5000		10000		44		10/5/06		30		50

		11/14/06		11		0		11		27		0		27		10		0		10		24		0		24		26		0		26		32		0		32		12		0		12		14		0		14																																												20		11/14/06		10		15		1		0		1		1		0		1		0		0		0		0		0		0		5		0		5		1		0		1		2		0		2		9		0		9						0						0						0						0						0						0						0		3		11/14/06		10		15		596		71		455		67		641		77		585		62		991		81		357		52		62		60		498		51																														523		11/14/06		5000		10000		65		11/14/06		30		50

		12/20/06		2		0		2		1		0		1		5		0		5		1		0		1		13		0		13		7		0		7		13		0		13		4		0		4																																												6		12/20/06		10		15		1		0		1		2		0		2		0		0		0		1		0		1		3		0		3		1		0		1		0		0		0		0		0		0						0						0						0						0						0						0						0		1		12/20/06		10		15		367		35		390		46		168		18		321		30		343		32		191		14		90		25		314		65																														273		12/20/06		5000		10000		33		12/20/06		30		50

		1/16/07		3		0		3		2		0		2		4		0		4		6		0		6		2		0		2		2		0		2		3		0		3		4		0		4																																												3		1/16/07		10		15		2		0		2		2		0		2		1		0		1		3		0		3		4		0		4		2		0		2		4		0		4		4		0		4						0						0						0						0						0						0						0		3		1/16/07		10		15		361		21		449		56		304		35		265		31		761		42		804		62		901		64		866		71																														589		01/16/07		5000		10000		48		1/16/07		30		50

		2/13/07		11		0		11		5		0		5		10		0		10		6		0		6		24		0		24		6		0		6		10		0		10		21		0		21																																												12		2/13/07		10		15		1		0		1		8		0		8		3		0		3		2		0		2		0		0		0		4		0		4		2		0		2		4		0		4						0						0						0						0						0						0						0		3		2/13/07		10		15		611		41		862		50		841		42		942		61		744		40		622		33		402		24		688		60																														714		02/13/07		5000		10000		44		2/13/07		30		50

		3/26/07		3		0		3		4		0		4		4		0		4		6		0		6		2		0		2		4		0		4		6		0		6		2		0		2																																												4		3/7/07		10		15		1		0		1		1		0		1		2		0		2		0		0		0		1		0		1		2		0		2		2		0		2		2		0		2						0						0						0						0						0						0						0		2		3/7/07		10		15		721		51		640		42		871		48		901		52		844		48		408		36		799		49		861		51																														756		03/07/07		5000		10000		47		3/7/07		30		50

		5/4/07		4		0		4		4		0		4		3		0		3		4		0		4		6		0		6		2		0		2		6		0		6		4		0		4																																												4		3/7/07		35		45		2		0		2		1		0		1		2		0		2		1		0		1		0		0		0		1		0		1		2		0		2		3		0		3						0						0						0						0						0						0						0		2		3/7/07		6		7		641		41		722		52		699		47		944		61		872		45		698		41		662		37		945		68																														773		03/07/07		3800		4500		49		3/7/07		410		500

		5/28/07		1		0		1		1		0		1		2		0		2		0		0		0		2		0		2		1		0		1		1		0		1		1		0		1																																												1		3/26/07		35		45		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1						0						0						0						0						0						0						0		1		3/26/07		6		7		161		17		200		21		251		36		275		28		320		53		101		15		460		55		184		21																														244		03/26/07		3800		4500		31		3/26/07		410		500

		7/4/07		2		0		2		3		0		3		3		0		3		3		0		3		2		0		2		4		0		4		4		0		4		3		0		3																																												3		5/4/07		35		45		2		0		2		2		0		2		1		0		1		0		0		0		1		0		1		1		0		1		2		0		2		2		0		2						0						0						0						0						0						0						0		2		5/4/07		6		7		346		64		339		37		537		77		301		55		492		86		292		31		896		120		1211		161																														552		05/04/07		3800		4500		79		5/4/07		410		500

		8/3/07		4		0		4		2		0		2		3		0		3		2		0		2		2		0		2		4		0		4		4		0		4		5		0		5																																												3		5/28/07		35		45		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		3		0		3		3		0		3		2		0		2						0						0						0						0						0						0						0		2		5/28/07		6		7		221		20		107		19		647		49		587		37		744		87		907		78		1241		101		975		89																														679		05/28/07		3800		4500		60		5/28/07		410		500

		9/24/07		2		0		2		1		0		1		1		0		1		2		0		2		3		0		3		3		0		3		2		0		2		2		0		2																																												2		7/4/07		35		45		0		0		0		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		2		0		2		2		0		2						0						0						0						0						0						0						0		1		7/4/07		6		7		310		27		488		31		210		20		401		29		121		18		404		31		601		41		422		30																														370		07/04/07		3800		4500		28		7/4/07		410		500

		11/6/07		6		0		6		4		0		4		4		0		4		4		0		4		8		0		8		7		0		7		8		0		8		10		0		10																																												6		8/3/07		35		45		2		0		2		2		0		2		3		0		3		1		0		1		3		0		3		5		0		5		4		0		4		4		0		4						0						0						0						0						0						0						0		3		8/3/07		6		7		523		33		678		25		498		14		671		22		687		23		721		33		856		34		678		25																														664		08/03/07		3800		4500		26		8/3/07		410		500

		12/11/07		10		0		10		9		0		9		11		0		11		12		0		12		12		0		12		15		0		15		21		0		21		18		0		18																																												14		9/24/07		35		45		2		0		2		1		0		1		3		0		3		4		0		4		4		0		4		4		0		4		3		0		3		7		0		7						0						0						0						0						0						0						0		4		11/6/07		6		7		678		36		761		31		734		34		891		44		851		33		781		33		1011		81		978		69																														836		11/06/07		3800		4500		45		11/6/07		410		500

		4/7/08		6		0		6		5		0		5		7		0		7		6		0		6		0		0		0		0		0		0		2		0		2		4		0		4		4		0		4		3		0		3		2		0		2		0		0		0		0		0		0		0		0		0		1		0		1		3		4/7/08		35		45		2		0		2		1		0		1		3		0		3		3		0		3		2		0		2		1		0		1		1		0		1		0		0		0		2		0		2		0		0		0		2		0		2		1		0		1		1		0		1		2		0		2		2		0		2		2		4/7/08		6		7		989		45		1045		58		1349		61		1305		60		689		46		430		30		1027		60		899		42		621		24		318		19		501		24		313		33		295		13		303		21		401		24		699		04/07/08		3800		4500		37		4/7/08		410		500

		5/7/08		9		0		9		8		0		8		7		0		7		8		0		8		3		0		3		3		0		3		3		0		3		7		0		7		7		0		7		4		0		4		8		0		8		4		0		4		8		0		8		9		0		9		5		0		5		6		5/7/08		35		45		3		0		3		2		0		2		2		0		2		2		0		2		3		0		3		3		0		3		2		0		2		1		0		1		1		0		1		1		0		1		2		0		2		2		0		2		2		0		2		2		0		2		2		0		2		2		5/7/08		6		7		782		44		671		39		724		41		454		22		576		33		430		30		671		32		572		28		781		37		671		32		677		33		476		41		672		31		781		43		587		33		635		05/07/08		3800		4500		35		5/7/08		410		500

		6/3/08		8		0		8		8		0		8		4		0		4		5		0		5		6		0		6		6		0		6		5		0		5		5		0		5		5		0		5		4		0		4		7		0		7		8		0		8		8		0		8		9		0		9		6		0		6		6		6/3/08		35		45		3		0		3		1		0		1		1		0		1		2		0		2		1		0		1		3		0		3		1		0		1		2		0		2		2		0		2		0		0		0		2		0		2		1		0		1		2		0		2		2		0		2		3		0		3		2		6/3/08		6		7		621		33		393		22		891		31		671		25		1192		44		671		19		781		22		245		19		1325		44		601		41		418		31		351		29		301		21		290		23		339		31		606		06/03/08		3800		4500		29		6/3/08		410		500

		7/1/08		9		0		9		9		0		9		7		0		7		9		0		9		8		0		8		5		0		5		8		0		8		8		0		8		8		0		8		6		0		6		11		0		11		6		0		6		9		0		9		9		0		9		3		0		3		8		7/1/08		35		45		1		0		1		2		0		2		0		0		0		1		0		1		1		0		1		1		0		1		0		0		0		0		0		0		2		0		2		1		0		1		1		0		1		2		0		2		0		0		0		1		0		1		1		0		1		1		7/1/08		6		7		621		33		393		22		891		31		671		25		1192		44		671		19		781		22		245		19		1325		44		601		41		418		31		351		29		301		21		290		23		339		31		606		07/01/08		3800		4500		29		7/1/08		410		500

		7/21/08		11		0		11		11		0		11		5		0		5		5		0		5		12		0		12		11		0		11		12		0		12		6		0		6		6		0		6		9		0		9		14		0		14		15		0		15		11		0		11		6		0		6		7		0		7		9		7/21/08		35		45		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		7/21/08		6		7		232		23		452		26		337		27		671		33		476		27		501		28		488		28		782		37		561		27		442		28		891		38		590		29		876		31		991		42		891		27		612		07/21/08		3800		4500		30		7/21/08		410		500

		9/4/08		10		0		10		9		0		9		6		0		6		7		0		7		7		0		7		9		0		9		6		0		6		9		0		9		11		0		11		12		0		12		10		0		10		9		0		9		6		0		6		6		0		6		9		0		9		8		9/4/08		35		45		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		9/4/08		6		7		219		19		140		14		275		16		101		9		244		16		301		21		189		19		181		17		176		17		215		21		414		24		409		21		357		21		454		19		602		27		285		09/04/08		3800		4500		19		9/4/08		410		500

		9/22/08		5		0		5		5		0		5		9		0		9		5		0		5		5		0		5		9		0		9		11		0		11		4		0		4		11		0		11		5		0		5		5		0		5		6		0		6		6		0		6		8		0		8		4		0		4		7		9/22/08		35		45		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		0		0		0		2		0		2		1		0		1		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		9/22/08		6		7		332		21		254		19		354		21		548		31		369		22		584		26		651		22		448		26		296		19		489		29		336		21		754		32		565		26		665		29		465		21		474		09/22/08		3800		4500		24		9/22/08		410		500

		11/6/08		3		0		3		3		0		3		5		0		5		4		0		4		4		0		4		3		0		3		4		0		4		4		0		4		4		0		4		5		0		5		5		0		5		3		0		3		3		0		3		3		0		3		4		0		4		4		11/6/08		35		45		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		1		0		1		0		11/6/08		6		7		721		31		867		39		253		12		458		22		357		20		445		28		432		22		685		31		591		28		241		9		219		8		473		19		501		21		765		33		801		36		521		11/06/08		3800		4500		24		11/6/08		410		500

		12/1/08		2		0		2		0		0		0		0		0		0		2		0		2		2		0		2		3		0		3		0		0		0		1		0		1		4		0		4		3		0		3		2		0		2		1		0		1		0		0		0		2		0		2		3		0		3		2		12/1/08		35		45		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		1		12/1/08		6		7		110		9		89		9		122		13		25		6		59		8		131		18		40		7		274		19		157		12		88		6		150		9		114		8		517		32		180		15		234		21		153		12/01/08		3800		4500		13		12/1/08		410		500

		12/16/08		3		0		3		2		0		2		3		0		3		2		0		2		2		0		2		3		0		3		4		0		4		3		0		3		5		0		5		4		0		4		4		0		4		3		0		3		3		0		3		3		0		3		3		0		3		3		12/16/08		35		45		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		1		0		1		1		12/16/08		6		7		291		18		178		11		271		19		189		14		177		14		276		18		198		11		187		14		278		17		91		7		87		6		287		16		376		21		301		17		227		19		228		12/16/08		3800		4500		15		12/16/08		410		500



&L&"Arial Narrow,Bold"&14CER 1&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER 2

										AIRSTRIPS:																																																												CONTACT PLATES:																																																						PARTICLE COUNTS

				A						B						C						D						E						F						G						H						I						Average						A						B						C						D						E						F						G						H						I						Average						A				B				C				D				E				F				G				H				I				Average

		Sample Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 2		Alert Level		Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 2		Total Alert Level		Total Action Level		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		CER 2 0.5um/cu ft		Date		CER 2 Alert Level		CER 2 Action Level		CER 2 5.0um/cu ft		Date		CER 2 Alert Level		CER 2 Action Level

		2/28/06								6		0		6		0		0		0		9		0		9		9		0		9																										6		10		15								0		0		0		0		0		0		1		0		1		0		0		0																										0		10		15		297		39		288		43		0		0		564		64																						383		2/28/06		5000		10000		49		02/28/06		30		50

		3/30/06								9		0		9		1		0		1		8		0		8		12		0		12																										8		10		15								2		0		2		0		0		0		6		0		6		3		0		3																										3		10		15		460		68		264		39		0		0		291		41																						338		3/30/06		5000		10000		49		03/30/06		30		50

		4/28/06								29		0		29		0		0		0		22		0		22		2		0		2																										13		10		15								2		0		2		2		0		2		0		0		0		3		0		3																										2		10		15		1084		67		543		41		0		0		531		39																						719		4/28/06		5000		10000		49		04/28/06		30		50

		5/30/06								21		0		21		0		0		0		19		0		19		4		0		4																										11		10		15								4		0		4		2		0		2		1		0		1		5		0		5																										3		10		15		435		87		354		66		0		0		460		77																						416		5/30/06		5000		10000		77		05/30/06		30		50

		7/7/06								5		0		5		0		0		0		8		0		8		8		0		8																										5		10		15								0		0		0		0		0		0		2		0		2		1		0		1																										1		10		15		232		33		299		39		0		0		479		40																						337		7/7/06		5000		10000		37		07/07/06		30		50

		9/5/06								3		0		3		0		0		0		2		0		2		2		0		2																										2		10		15								4		0		4		0		0		0		4		0		4		5		0		5																										3		10		15		1289		79		289		30		0		0		1422		108																						1000		9/5/06		5000		10000		72		09/05/06		30		50

		10/5/06																																																																																																																																																																10/5/06		5000		10000				10/05/06		30		50

		11/14/06								16		0		16		0		0		0		4		0		4		2		0		2																										6		10		15								1		0		1		0		0		0		4		0		4		1		0		1																										2		10		15		961		41		877		40		0		0		688		31																						842		11/14/06		5000		10000		37		11/14/06		30		50

		12/20/06								5		0		5		4		0		4		6		0		6		2		0		2																										4		10		15								0		0		0		0		0		0		0		0		0		0		0		0																										0		10		15		463		36		141		17		0		0		273		41																						292		12/20/06		5000		10000		31		12/20/06		30		50

		1/16/07								2		0		2		0		0		0		1		0		1		1		0		1																										1		10		15								1		0		1		0		0		0		1		0		1		2		0		2																										1		10		15		781		62		451		32		0		0		628		58																						620		1/16/07		5000		10000		51		01/16/07		30		50

		2/13/07								12		0		12		0		0		0		10		0		10		10		0		10																										8		10		15								4		0		4		0		0		0		4		0		4		4		1		5																										3		10		15		640		31		285		44		0		0		499		22																						475		2/13/07		5000		10000		32		02/13/07		30		50

		3/26/07								2		0		2		0		0		0		2		0		2		3		0		3																										2		35		45								1		0		1		0		0		0		1		0		1		1		0		1																										1		6		7		490		40		684		51		0		0		588		42																						587		3/7/07		5000		10000		44		03/07/07		30		50

		5/4/07								2		0		2		0		0		0		3		0		3		3		0		3																										2		35		45								1		0		1		0		0		0		1		0		1		2		0		2																										1		6		7		640		41		585		37		0		0		704		52																						643		3/7/07		1250		1500		43		03/07/07		90		105

		5/28/07								0		0		0		0		0		0		1		0		1		1		0		1																										1		35		45								1		0		1		0		0		0		0		0		0		1		0		1																										1		6		7		1104		101		944		81		0		0		642		45																						897		3/26/07		1250		1500		76		03/26/07		90		105

		7/4/07								1		0		1		0		0		0		2		0		2		2		0		2																										1		35		45								0		0		0		0		0		0		1		0		1		1		0		1																										1		6		7		10		0		962		123		0		0		1141		132																						704		5/4/07		1250		1500		89		07/04/07		90		105

		8/3/07								0		0		0		0		0		0		1		0		1		2		0		2																										1		35		45								1		0		1		0		0		0		1		0		1		1		0		1																										1		6		7		0		0		784		61		0		0		875		71																						553		8/3/07		1250		1500		44		08/03/07		90		105

		9/24/07								1		0		1		0		0		0		1		0		1		1		0		1																										1		35		45								0		0		0		0		0		0		0		0		0		1		0		1																										0		6		7		0		0		199		19		0		0		701		49																						300		9/24/07		1250		1500		23		09/24/07		90		105

		11/6/07								1		0		1		0		0		0		3		0		3		3		0		3																										2		35		45								1		0		1		0		0		0		2		0		2		2		0		2																										1		6		7		4		0		563		22		0		0		867		39																						478		11/6/07		1250		1500		20		11/06/07		90		105

		12/11/07								0		0		0		0		0		0		2		0		2		3		0		3																										1		35		45								0		0		0		0		0		0		3		0		3		1		0		1																										1		6		7		2		0		672		36		0		0		901		37																						525		12/11/07		1250		1500		24		12/11/07		90		105

		4/7/08		0		0		0		4		0		4		7		0		7		0		0		0		4		0		4		0		0		0		6		0		6		3		0		3		0		0		0		3		35		45		0		0		0		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		2		0		2		2		0		2		0		0		0		1		6		7		0		0		162		23		208		25		0		0		93		19		0		0		90		6		201		17		0		0		84		4/7/08		1250		1500		10		04/07/08		90		105

		5/7/08		0		0		0		3		0		3		9		0		9		0		0		0		8		0		8		0		0		0		8		0		8		8		0		8		0		0		0		4		35		45		0		0		0		2		0		2		3		0		3		0		0		0		2		0		2		0		0		0		1		0		1		1		0		1		0		0		0		1		6		7		0		0		401		24		489		25		0		0		281		22		0		0		187		18		482		24		0		0		204		5/7/08		1250		1500		13		05/07/08		90		105

		6/3/08		0		0		0		3		0		3		3		0		3		0		0		0		5		0		5		0		0		0		5		0		5		2		0		2		0		0		0		2		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		0		1		0		0		0		1		6		7		0		0		267		10		498		22		0		0		268		22		0		0		301		19		298		11		0		0		181		6/3/08		1250		1500		9		06/03/08		90		105

		7/1/08		0		0		0		8		0		8		0		0		0		8		0		8		6		0		6		0		0		0		3		0		3		2		0		2		0		0		0		3		35		45		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		0		6		7		0		0		403		22		0		0		153		11		287		19		1		0		21		1		121		11		0		0		110		7/1/08		1250		1500		7		07/01/08		90		105

		7/21/08		0		0		0		6		0		6		0		0		0		7		0		7		7		0		7		0		0		0		4		0		4		2		0		2		0		0		0		3		35		45		0		0		0		2		0		2		0		0		0		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		0		0		0		1		6		7		0		0		376		19		0		0		298		17		337		21		0		0		109		8		291		15		0		0		157		7/21/08		1250		1500		9		07/21/08		78		83

		9/4/08		0		0		0		7		0		7		9		0		9		0		0		0		4		0		4		0		0		0		4		0		4		4		0		4		3		0		3		3		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		6		7		0		0		210		19		175		11		0		0		361		18		0		0		101		7		162		9		706		40		191		9/4/08		1250		1500		12		09/04/08		78		83

		9/22/08		0		0		0		5		0		5		4		0		4		0		0		0		4		0		4		0		0		0		2		0		2		4		0		4		2		0		2		2		35		45		0		0		0		2		0		2		0		0		0		0		0		0		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		1		6		7		0		0		332		21		296		15		0		0		194		9		0		0		265		11		295		11		565		22		216		9/22/08		1250		1500		10		09/22/08		78		83

		11/6/08		0		0		0		2		0		2		3		0		3		0		0		0		2		0		2		0		0		0		3		0		3		3		0		3		2		0		2		2		35		45		0		0		0		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		6		7		0		0		776		22		409		19		0		0		292		8		0		0		301		16		228		11		220		9		247		11/6/08		1250		1500		9		11/06/08		78		83

		12/1/08		0		0		0		3		0		3		2		0		2		0		0		0		3		0		3		0		0		0		2		0		2		0		0		0		1		0		1		1		35		45		0		0		0		1		0		1		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		6		7		0		0		290		12		203		11		0		0		221		12		0		0		313		21		19		3		148		10		133		12/1/08		1250		1500		8		12/01/08		78		83

		12/16/08		0		0		0		4		0		4		3		0		3		0		0		0		3		0		3		0		0		0		3		0		3		0		0		0		1		0		1		2		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		6		7		0		0		199		9		289		16		0		0		167		7		0		0		267		17		89		6		177		11		132		12/16/08		1250		1500		7		12/16/08		78		83



&L&"Arial Narrow,Bold"&14CER 2&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER 3

				AIRSTRIPS:																														CONTACT PLATES:																																				PARTICLE COUNTS

				A						B						D						E						Average						A						B						C						D						E						Average						A				B				C				D				E				Average

		Sample Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER3		Total Alert Level		Total Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 3		Total Alert Level		Total Action Level		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		CER 3 0.5um/cu ft		0.5um/cu ft Alert Level		0.5um/cu ft Action Level		CER 3 5.0um/cu ft		5.0um/cu ft Alert Level		5.0um/cu ft Action Level

		2/28/06		29		1		30		21		0		21		28		0		28		37		0		37		29		10		15		3		0		3		3		0		3		3		0		3		2		0		2		4		0		4		3		10		15		4411		344		3943		271		3664		229		3068		212		1233		78		3264		5000		10000		227		30		50

		3/30/06		32		1		33		26		0		26		21		0		21		32		0		32		28		10		15		5		0		5		4		0		4		6		0		6		4		0		4		5		0		5		4		10		15		1261		119		979		81		1461		101		1721		120		630		101		1210		5000		10000		104		30		50

		4/28/06		29		2		31		32		0		32		23		0		23		29		0		29		29		10		15		2		0		2		3		0		3		0		0		0		0		0		0		0		0		0		1		10		15		4536		307		3293		245		2424		222		2637		211		1112		72		2800		5000		10000		211		30		50

		5/30/06		31		0		31		29		0		29		21		1		22		29		0		29		28		10		15		4		0		4		5		0		5		2		0		2		1		0		1		3		0		3		3		10		15		1914		327		2122		327		2561		413		1572		207		1829		252		2000		5000		10000		305		30		50

		7/7/06		26		0		26		19		0		19		22		0		22		31		0		31		25		10		15		4		0		4		5		0		5		3		0		3		2		0		2		5		0		5		3		10		15		2150		382		2668		423		2561		401		2022		399		764		118		2033		5000		10000		345		30		50

		9/5/06		10		0		10		12		0		12		11		0		11		14		0		14		12		10		15		6		0		6		4		0		4		4		0		4		6		0		6		5		0		5		5		10		15		2286		180		2142		171		1829		162		1749		171		1281		148		1857		5000		10000		166		30		50

		10/5/06		9		0		9		10		0		10		10		0		10		8		0		8		9		10		15		7		0		7		5		0		5		6		0		6		4		0		4		4		0		4		5		10		15		1679		346		793		137		1841		241		1429		248		1374		203		1423		5000		10000		235		30		50

		11/14/06		19		2		21		26		0		26		26		0		26		17		0		17		23		10		15		2		0		2		1		0		1		0		0		0		1		0		1		6		0		6		2		10		15		2241		243		2301		231		1974		198		2475		224		2575		201		2313		5000		10000		219		30		50

		12/20/06		10		0		10		13		0		13		13		0		13		16		0		16		13		10		15		5		0		5		1		0		1		0		0		0		3		0		3		1		0		1		2		10		15		406		33		727		46		923		94		604		41		462		39		624		5000		10000		51		30		50

		1/16/07		4		0		4		5		0		5		7		0		7		3		0		3		5		10		15		3		0		3		2		0		2		3		0		3		4		0		4		4		0		4		3		10		15		485		41		1785		101		1986		128		1785		109		1861		118		1580		5000		10000		99		30		50

		2/13/07		12		0		12		22		0		22		18		0		18		21		0		21		18		10		15		2		0		2		4		0		4		2		0		2		1		0		1		2		0		2		2		10		15		1261		87		1641		98		901		62		988		61		1487		88		1256		5000		10000		79		30		50

		3/26/07		11		0		11		12		0		12		10		0		10		9		0		9		11		35		45		2		0		2		1		0		1		2		0		2		1		0		1		2		0		2		2		6		7		1421		109		1221		101		866		71		949		82		1242		101		1140		3800		4500		93		410		500

		5/4/07		10		0		10		10		0		10		9		0		9		11		0		11		10		35		45		2		0		2		3		0		3		1		0		1		2		0		2		2		0		2		2		6		7		1741		110		1444		91		1235		81		1479		87		1521		92		1484		3800		4500		92		410		500

		5/28/07		6		0		6		4		0		4		2		0		2		2		0		2		4		35		45		4		0		4		2		0		2		1		0		1		1		0		1		2		0		2		2		6		7		1421		102		1387		100		1842		169		1785		154		1421		121		1571		3800		4500		129		410		500

		7/4/07		7		0		7		6		0		6		6		0		6		7		0		7		7		35		45		4		0		4		3		0		3		2		0		2		1		0		1		4		0		4		3		6		7		3950		375		2745		292		1658		177		2431		201		2786		247		2714		3800		4500		258		410		500

		8/3/07		6		0		6		6		0		6		4		0		4		5		0		5		5		35		45		3		0		3		3		0		3		2		0		2		2		0		2		2		0		2		3		6		7		1672		145		1897		152		1866		149		1987		151		1487		138		1782		3800		4500		147		410		500

		9/24/07		4		0		4		3		0		3		2		0		2		2		0		2		3		35		45		2		0		2		2		0		2		2		0		2		1		0		1		2		0		2		2		6		7		781		61		1011		72		689		49		768		52		409		31		732		3800		4500		53		410		500

		11/6/07		7		0		7		9		0		9		8		0		8		9		0		9		8		35		45		3		0		3		3		0		3		5		0		5		1		0		1		6		0		6		3		6		7		1276		78		1454		65		1109		55		987		45		1067		47		1179		3800		4500		58		410		500

		12/11/07		9		0		9		12		0		12		9		0		9		11		0		11		10		35		45		2		0		2		4		0		4		4		0		4		5		0		5		4		0		4		4		6		7		1853		101		1321		99		901		45		1241		87		987		72		1261		3800		4500		81		410		500

		4/7/08		8		0		8		15		0		15		12		0		12		10		0		10		11		35		45		2		0		2		3		0		3		2		0		2		3		0		3		4		0		4		3		6		7		1047		69		1642		79		1421		67		1677		71		987		60		1355		3800		4500		69		410		500

		5/7/08		3		0		3		4		0		4		4		0		4		4		0		4		4		35		45		4		0		4		3		0		3		4		0		4		1		0		1		1		0		1		2		6		7		561		31		761		44		660		39		451		21		671		31		621		3800		4500		33		410		500

		6/3/08		3		0		3		4		0		4		4		0		4		4		0		4		4		35		45		2		0		2		2		0		2		2		0		2		1		0		1		1		0		1		2		6		7		409		26		391		33		782		34		891		33		1281		44		751		3800		4500		34		410		500

		7/1/08		7		0		7		7		0		7		8		0		8		8		0		8		8		35		45		2		0		2		2		0		2		1		0		1		1		0		1		1		0		1		2		6		7		1121		81		677		42		339		22		125		11		111		9		475		3800		4500		33		410		500

		7/21/08		9		0		9		8		0		8		8		0		8		11		0		11		9		35		45		3		0		3		3		0		3		2		0		2		2		0		2		2		0		2		3		6		7		891		41		781		33		789		31		499		21		339		12		660		3800		4500		28		410		500

		9/4/08		6		0		6		9		0		9		4		0		4		7		0		7		7		35		45		2		0		2		2		0		2		1		0		1		2		0		2		1		0		1		2		6		7		793		37		1044		44		977		39		1011		57		901		40		945		3800		4500		43		410		500

		9/22/08		9		0		9		9		0		9		9		0		9		7		0		7		9		35		45		1		0		1		2		0		2		2		0		2		2		0		2		1		0		1		2		6		7		984		44		564		31		965		33		698		41		632		39		769		3800		4500		38		410		500

		11/6/08		6		0		6		6		0		6		4		0		4		3		0		3		5		35		45		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		1		6		7		1198		81		901		67		789		43		761		41		904		61		911		3800		4500		59		410		500

		12/1/08		7		0		7		7		0		7		6		0		6		7		0		7		7		35		45		2		0		2		1		0		1		2		0		2		1		0		1		1		0		1		1		6		7		1198		81		901		67		789		43		761		41		904		61		911		3800		4500		59		410		500

		12/16/08		8		0		8		8		0		8		6		0		6		9		0		9		8		35		45		1		0		1		2		0		2		1		0		1		1		0		1		1		0		1		1		6		7		892		41		1098		69		892		34		901		44		1167		72		990		3800		4500		52		410		500



&L&"Arial Narrow,Bold"&14CER 3&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER Pressure

		Daily				Monthly				Daily				Monthly				Daily																		Monthly																		Daily								Monthly								Specs

		Date		CER1		Month		CER1		Date		CER Change Room		Month		CER Change Room		Date		CER2		Temp (F)		Relative Humidity (%)		R&D Bio-Safety Cabinet North (left axis)		R&D Bio-Safety Cabinet South (left axis)		Mfg Bio-Safety Cabinet North (left axis)		Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)		Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)		Month		CER 2		Temp (F)		Relative Humidity (%)		R&D Bio-Safety Cabinet North (left axis)		R&D Bio-Safety Cabinet South (left axis)		Mfg Bio-Safety Cabinet North (left axis)		Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)		Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)		Date		CER3		Temp (ºF)		Humidity (%RH)		Month		CER 3		Temp (ºF)		Humidity (%RH)		Date		CER Alert Level		CER Action Level		Bio-Safety Cabinet Alert Level (left axis)		Bio-Safety Cabinet Action  Level (left axis)		Mfg Bio-Safety Cabinet South Alert Level (right axis)		Mfg Bio-Safety Cabinet South Alarm Level (right axis)

		4/24/06		0.05		April-06		0.045		3/31/06		0.05		March-06		0.055		3/31/06		0.09																March-06		0.090																6/19/06		0.05						June-06		0.051						4/30/06		0.05		0.03

		4/24/06		0.05		May-06		0.022		3/31/06		0.06		April-06		0.053		3/31/06		0.09																April-06		0.089																6/19/06		0.06						July-06		0.061						5/31/06		0.05		0.03

		4/25/06		0.05		June-06		0.013		4/4/06		0.05		May-06		0.050		4/4/06		0.09																July-06		0.076																6/28/06		0.03						August-06		0.055						6/30/06		0.05		0.03

		4/25/06		0.04		July-06		0.041		4/4/06		0.05		June-06		0.046		4/4/06		0.09																August-06		0.068																6/28/06		0.06						September-06		0.052						7/31/06		0.05		0.03

		4/26/06		0.06		August-06		0.033		4/5/06		0.05		July-06		0.048		4/5/06		0.09																September-06		0.062																6/29/06		0.03						October-06		0.051						8/31/06		0.05		0.03

		4/26/06		0.04		September-06		0.027		4/5/06		0.06		August-06		0.050		4/5/06		0.09																October-06		0.034																6/29/06		0.06						November-06		0.053						9/30/06		0.05		0.03

		4/27/06		0.04		October-06		0.033		4/6/06		0.05		September-06		0.048		4/6/06		0.09																November-06		0.020																6/30/06		0.06						December-06		0.051						10/31/06		0.05		0.03

		4/27/06		0.045		November-06		0.028		4/6/06		0.06		October-06		0.053		4/6/06		0.09																December-06		0.012																6/30/06		0.06						February-07		0.040						11/30/06		0.05		0.03

		4/28/06		0.05		December-06		0.030		4/7/06		0.055		November-06		0.035		4/7/06		0.09																January-07		0.011																7/5/06		0.03						March-07		0.037						12/31/06		0.05		0.03

		4/28/06		0.04		January-07		0.030		4/7/06		0.05		December-06		0.031		4/7/06		0.09																February-07		0.013																7/5/06		0.03						April-07		0.038						1/31/07		0.05		0.03

		4/29/06		0.035		February-07		0.038		4/10/06		0.055		January-07		0.031		4/10/06		0.095																March-07		0.031																7/6/06		0.06						May-07		0.038						1/28/07		0.05		0.03

		4/29/06		0.035		March-07		0.037		4/10/06		0.055		February-07		0.035		4/10/06		0.09																April-07		0.033																7/6/06		0.06						June-07		0.040						3/7/07		0.05		0.03

		5/1/06		0.025		April-07		0.031		4/11/06		0.055		March-07		0.036		4/11/06		0.095																May-07		0.044																7/7/06		0.06						July-07		0.057						3/7/07		0.03		0.005

		5/1/06		0.03		May-07		0.027		4/11/06		0.055		April-07		0.035		4/11/06		0.095																June-07		0.048																7/7/06		0.06						August-07		0.053						4/30/07		0.03		0.005

		5/2/06		0.025		June-07		0.027		4/12/06		0.055		May-07		0.032		4/12/06		0.09																July-07		0.050																7/10/06		0.06						September-07		0.050						5/16/07		0.03		0.005

		5/2/06		0.03		July-07		0.035		4/12/06		0.055		June-07		0.028		4/12/06		0.09																August-07		0.042																7/10/06		0.06						October-07		0.049						5/16/07		0.015		0.005

		5/3/06		0.015		August-07		0.032		4/13/06		0.055		July-07		0.030		4/13/06		0.09																September-07		0.046						0.610		0.408								7/11/06		0.06						November-07		0.047						5/31/07		0.015		0.005

		5/4/06		0.03		September-07		0.030		4/13/06		0.055		August-07		0.032		4/13/06		0.095																October-07		0.041						0.620		0.420								7/11/06		0.06						December-07		0.043						6/30/07		0.015		0.005

		5/5/06		0.03		October-07		0.030		4/17/06		0.06		September-07		0.029		4/17/06		0.095																November-07		0.035						0.632		0.424								7/12/06		0.06						January-08		0.040						7/31/07		0.015		0.005

		5/5/06		0.03		November-07		0.065		4/17/06		0.055		October-07		0.027		4/17/06		0.09																December-07		0.030						0.643		0.426								7/12/06		0.06						February-08		0.040						8/31/07		0.015		0.005

		5/6/06		0.03		December-07		0.077		4/18/06		0.055		November-07		0.044		4/18/06		0.095																January-08																		7/13/06		0.06						March-08		0.040						9/5/07		0.015		0.005		0.25		0.1

		5/6/06		0.025		January-08		0.088		4/18/06		0.06		December-07		0.043		4/18/06		0.09																February-08		0.049		69.778		46.100		0.281		0.309		0.428		62.091		1180.364		7/13/06		0.06						April-08		0.048		70.864		42.636		9/30/07		0.015		0.005		0.25		0.1

		5/7/06		0.03		February-08		0.035		4/19/06		0.045		January-08		0.032		4/19/06		0.085																March-08		0.063		70.000		39.750		0.272		0.318		0.441		63.000		1193.000		7/14/06		0.06						May-08		0.040		72.696		37.435		10/31/07		0.015		0.005		0.25		0.1

		5/8/06		0.03		March-08		0.041		4/19/06		0.05		February-08		0.035		4/19/06		0.09																April-08		0.053		71.045		41.000		0.276		0.320		0.454		62.333		1196.333		7/14/06		0.06						June-08		0.025		72.136		33.909		11/30/07		0.015		0.005		0.25		0.1

		5/8/06		0.03		April-08		0.043		4/20/06		0.055		March-08		0.039		4/20/06		0.079																May-08		0.043		72.304		35.913		0.282		0.320		0.449		60.652		1194.957		7/17/06		0.06						July-08		0.059		71.920		39.400		12/31/07		0.015		0.005		0.25		0.1

		5/9/06		0.025		May-08		0.041		4/20/06		0.05		April-08		0.040		4/20/06		0.08																June-08		0.043		71.826		33.522		0.288		0.318		0.447		57.913		790.783		7/17/06		0.06						August-08		0.057		71.600		40.040		1/31/08		0.015		0.005		0.25		0.1

		5/9/06		0.025		June-08		0.039		4/24/06		0.06		May-08		0.040		4/21/06		0.085																July-08		0.077		71.800		38.360		0.285		0.320		0.447		59.789		882.526		7/18/06		0.06						September-08		0.059		71.240		38.000		2/29/08		0.015		0.005		0.25		0.1

		5/10/06		0.025		July-08		0.027		4/24/06		0.06		June-08		0.037		4/21/06		0.085																August-08		0.061		71.440		38.480		0.272		0.318		0.448		0.000		0.000		7/18/06		0.06														3/31/08		0.015		0.005		0.25		0.1

		5/10/06		0.025		August-08		0.031		4/25/06		0.06		July-08		0.040		4/25/06		0.086																September-08		0.059		70.640		38.280		0.259		0.319		0.439		0.000		0.000		7/19/06		0.06														4/1/31		0.015		0.005		0.25		0.1

		5/11/06		0.015		September-08		0.030		4/25/06		0.06		August-08		0.041		4/25/06		0.085																																		7/19/06		0.06														5/31/08		0.015		0.005		0.25		0.1

		5/11/06		0.025						4/26/06		0.05		September-08		0.041		4/26/06		0.085																																		7/20/06		0.07														6/30/08		0.015		0.005		0.25		0.1

		5/12/06		0.025						4/26/06		0.02						4/26/06		0.087																																		7/20/06		0.07														7/31/08		0.015		0.005		0.25		0.1

		5/12/06		0.02						4/27/06		0.06						4/27/06		0.085																																		7/21/06		0.07														8/30/08		0.015		0.005		0.25		0.1

		5/15/06		0.02						4/27/06		0.055						4/27/06		0.085																																		7/21/06		0.07														9/30/08		0.015		0.005		0.25		0.1

		5/15/06		0.025						4/28/06		0.04						4/28/06		0.09																																		7/22/06		0.07

		5/16/06		0.01						4/28/06		0.055						4/28/06		0.08																																		7/22/06		0.07

		5/16/06		0.01						4/29/06		0.05						7/25/06		0.085																																		7/24/06		0.07

		5/17/06		0.01						4/29/06		0.05						7/25/06		0.085																																		7/24/06		0.07

		5/17/06		0.025						5/1/06		0.05						7/26/06		0.085																																		7/25/06		0.06

		5/18/06		0.02						5/1/06		0.055						7/26/06		0.075																																		7/25/06		0.06

		5/18/06		0.02						5/2/06		0.05						7/27/06		0.08																																		7/26/06		0.06

		5/19/06		0.03						5/2/06		0.055						7/27/06		0.08																																		7/26/06		0.06

		5/19/06		0.02						5/3/06		0.05						7/28/06		0.075																																		7/27/06		0.06

		5/20/06		0.01						5/4/06		0.045						7/28/06		0.079																																		7/27/06		0.06

		5/20/06		0.02						5/5/06		0.055						7/29/06		0.069																																		8/1/06		0.06

		5/22/06		0.015						5/5/06		0.05						7/29/06		0.07																																		8/1/06		0.06

		5/22/06		0.015						5/6/06		0.065						7/30/06		0.069																																		8/2/06		0.06

		5/23/06		0.015						5/6/06		0.055						7/30/06		0.069																																		8/2/06		0.06

		5/23/06		0.015						5/7/06		0.05						7/31/06		0.075																																		8/3/06		0.06

		5/24/06		0.015						5/8/06		0.05						7/31/06		0.073																																		8/3/06		0.06

		5/24/06		0.015						5/8/06		0.05						8/1/06		0.07																																		8/4/06		0.06

		5/25/06		0.015						5/9/06		0.05						8/1/06		0.075																																		8/4/06		0.06

		5/25/06		0.03						5/9/06		0.055						8/2/06		0.07																																		8/7/06		0.055

		5/30/06		0.015						5/10/06		0.045						8/2/06		0.07																																		8/7/06		0.06

		5/30/06		0.02						5/10/06		0.04						8/3/06		0.07																																		8/8/06		0.06

		6/1/06		0.01						5/11/06		0.045						8/3/06		0.074																																		8/8/06		0.06

		6/1/06		0.01						5/11/06		0.055						8/4/06		0.074																																		8/9/06		0.06

		6/2/06		0.015						5/12/06		0.05						8/4/06		0.074																																		8/9/06		0.06

		6/5/06		0.01						5/12/06		0.06						8/7/06		0.073																																		8/10/06		0.055

		6/5/06		0.013						5/15/06		0.045						8/7/06		0.073																																		8/10/06		0.055

		6/6/06		0.01						5/15/06		0.055						8/8/06		0.073																																		8/11/06		0.055

		6/6/06		0.01						5/16/06		0.05						8/8/06		0.073																																		8/11/06		0.055

		6/7/06		0.01						5/16/06		0.055						8/10/06		0.074																																		8/14/06		0.055

		6/7/06		0.01						5/17/06		0.04						8/10/06		0.071																																		8/14/06		0.055

		6/8/06		0.01						5/17/06		0.045						8/14/06		0.07																																		8/15/06		0.055

		6/8/06		0.01						5/18/06		0.05						8/15/06		0.069																																		8/15/06		0.055

		6/9/06		0.01						5/18/06		0.055						8/16/06		0.069																																		8/16/06		0.055

		6/9/06		0.01						5/19/06		0.04						8/16/06		0.07																																		8/16/06		0.055

		6/12/06		0.03						5/19/06		0.045						8/17/06		0.069																																		8/17/06		0.055

		6/12/06		0.01						5/20/06		0.04						8/17/06		0.069																																		8/17/06		0.06

		6/13/06		0.03						5/20/06		0.043						8/18/06		0.07																																		8/18/06		0.05

		6/13/06		0.01						5/22/06		0.05						8/18/06		0.068																																		8/18/06		0.065

		6/16/06		0.01						5/22/06		0.05						8/21/06		0.065																																		8/19/06		0.05

		6/16/06		0.01						5/23/06		0.05						8/22/06		0.06																																		8/19/06		0.055

		7/6/06		0.05						5/23/06		0.05						8/22/06		0.065																																		8/21/06		0.055

		7/6/06		0.04						5/24/06		0.045						8/23/06		0.065																																		8/21/06		0.05

		7/7/06		0.04						5/24/06		0.05						8/23/06		0.068																																		8/22/06		0.05

		7/8/06		0.04						5/25/06		0.05						8/24/06		0.065																																		8/22/06		0.056

		7/10/06		0.05						5/25/06		0.05						8/24/06		0.055																																		8/23/06		0.055

		7/11/06		0.04						5/30/06		0.045						8/25/06		0.065																																		8/23/06		0.055

		7/12/06		0.05						5/30/06		0.05						8/25/06		0.065																																		8/24/06		0.05

		7/13/06		0.05						6/1/06		0.045						8/28/06		0.065																																		8/24/06		0.05

		7/17/06		0.06						6/1/06		0.05						8/28/06		0.065																																		8/25/06		0.05

		7/18/06		0.04						6/2/06		0.04						8/30/06		0.065																																		8/25/06		0.055

		7/19/06		0.04						6/5/06		0.05						8/30/06		0.063																																		8/26/06		0.05

		7/20/06		0.04						6/5/06		0.055						8/31/06		0.065																																		8/26/06		0.05

		7/21/06		0.033						6/6/06		0.055						8/31/06		0.065																																		8/28/06		0.05

		7/22/06		0.04						6/6/06		0.05						9/1/06		0.06																																		8/28/06		0.05

		7/23/06		0.04						6/7/06		0.055						9/1/06		0.065																																		8/29/06		0.05

		7/24/06		0.04						6/7/06		0.05						9/5/06		0.065																																		8/29/06		0.05

		7/25/06		0.04						6/8/06		0.05						9/5/06		0.065																																		8/30/06		0.05

		7/26/06		0.035						6/8/06		0.05						9/6/06		0.055																																		8/30/06		0.05

		7/26/06		0.04						6/9/06		0.045						9/6/06		0.065																																		8/31/06		0.05

		7/27/06		0.03						6/9/06		0.05						9/7/06		0.055																																		8/31/06		0.05

		7/27/06		0.04						6/12/06		0.01						9/7/06		0.063																																		9/1/06		0.055

		7/28/06		0.04						6/12/06		0.05						9/8/06		0.06																																		9/6/06		0.05

		7/31/06		0.03						6/13/06		0.01						9/8/06		0.063																																		9/6/06		0.05

		8/1/06		0.035						6/13/06		0.05						9/11/06		0.06																																		9/7/06		0.05

		8/2/06		0.03						6/14/06		0.05						9/11/06		0.065																																		9/7/06		0.05

		8/3/06		0.03						6/14/06		0.055						9/12/06		0.06																																		9/8/06		0.05

		8/4/06		0.03						6/15/06		0.055						9/12/06		0.065																																		9/8/06		0.05

		8/7/06		0.03						6/15/06		0.06						9/13/06		0.06																																		9/11/06		0.05

		8/8/06		0.03						6/16/06		0.05						9/13/06		0.065																																		9/11/06		0.05

		8/10/06		0.03						6/16/06		0.04						9/14/06		0.06																																		9/12/06		0.05

		8/10/06		0.05						6/17/06		0.045						9/14/06		0.065																																		9/12/06		0.06

		8/11/06		0.03						6/17/06		0.05						9/15/06		0.06																																		9/13/06		0.05

		8/11/06		0.05						6/19/06		0.05						9/15/06		0.065																																		9/13/06		0.055

		8/14/06		0.03						6/19/06		0.05						9/18/06		0.06																																		9/14/06		0.05

		8/15/06		0.03						6/20/06		0.05						9/18/06		0.063																																		9/14/06		0.04

		8/16/06		0.05						6/20/06		0.05						9/19/06		0.065																																		9/15/06		0.05

		8/16/06		0.03						6/21/06		0.04						9/19/06		0.055																																		9/15/06		0.05

		8/17/06		0.035						6/21/06		0.05						9/20/06		0.065																																		9/18/06		0.055

		8/17/06		0.03						6/22/06		0.04						9/20/06		0.06																																		9/18/06		0.06

		8/18/06		0.03						6/22/06		0.045						9/21/06		0.065																																		9/19/06		0.05

		8/18/06		0.03						6/26/06		0.04						9/21/06		0.062																																		9/19/06		0.055

		8/19/06		0.035						6/27/06		0.04						9/23/06		0.065																																		9/20/06		0.05

		8/19/06		0.03						6/28/06		0.04						9/23/06		0.062																																		9/20/06		0.05

		8/20/06		0.035						6/29/06		0.04						9/25/06		0.059																																		9/21/06		0.055

		8/21/06		0.03						7/5/06		0.04						9/25/06		0.06																																		9/21/06		0.055

		8/21/06		0.03						7/6/06		0.04						10/2/06		0.06																																		9/22/06		0.05

		8/22/06		0.025						7/7/06		0.05						10/2/06		0.05																																		9/22/06		0.055

		8/22/06		0.035						7/8/06		0.05						10/3/06		0.048																																		9/23/06		0.06

		8/23/06		0.035						7/10/06		0.03						10/3/06		0.042																																		9/23/06		0.06

		8/23/06		0.035						7/11/06		0.05						10/4/06		0.048																																		9/25/06		0.05

		8/24/06		0.035						7/12/06		0.04						10/6/06		0.038																																		9/25/06		0.055

		8/24/06		0.035						7/13/06		0.0425						10/9/06		0.055																																		9/26/06		0.05

		8/25/06		0.035						7/17/06		0.04						10/9/06		0.036																																		9/26/06		0.05

		8/25/06		0.035						7/18/06		0.05						10/10/06		0.037																																		9/27/06		0.05

		8/26/06		0.03						7/19/06		0.05						10/10/06		0.032																																		9/27/06		0.05

		8/26/06		0.035						7/20/06		0.05						10/11/06		0.032																																		9/28/06		0.05

		8/28/06		0.03						7/21/06		0.055						10/11/06		0.032																																		9/28/06		0.05

		8/28/06		0.03						7/22/06		0.055						10/12/06		0.033																																		9/29/06		0.05

		8/29/06		0.03						7/23/06		0.055						10/12/06		0.03																																		9/29/06		0.05

		8/29/06		0.03						7/24/06		0.055						10/13/06		0.031																																		10/2/06		0.055

		8/30/06		0.03						7/25/06		0.05						10/13/06		0.03																																		10/2/06		0.06

		8/30/06		0.035						7/26/06		0.055						10/16/06		0.033																																		10/3/06		0.05

		8/31/06		0.03						7/26/06		0.05						10/16/06		0.032																																		10/3/06		0.05

		8/31/06		0.03						7/27/06		0.05						10/17/06		0.032																																		10/4/06		0.055

		9/1/06		0.03						7/27/06		0.05						10/17/06		0.03																																		10/4/06		0.05

		9/5/06		0.03						7/28/06		0.05						10/18/06		0.033																																		10/5/06		0.05

		9/5/06		0.03						7/31/06		0.05						10/18/06		0.03																																		10/5/06		0.05

		9/6/06		0.02						8/1/06		0.05						10/19/06		0.025																																		10/9/06		0.05

		9/7/06		0.02						8/2/06		0.05						10/19/06		0.03																																		10/9/06		0.05

		9/8/06		0.03						8/3/06		0.05						10/20/06		0.03																																		10/10/06		0.05

		9/11/06		0.03						8/4/06		0.05						10/20/06		0.035																																		10/10/06		0.05

		9/11/06		0.03						8/7/06		0.05						10/23/06		0.032																																		10/11/06		0.05

		9/12/06		0.03						8/8/06		0.05						10/23/06		0.026																																		10/11/06		0.05

		9/12/06		0.03						8/11/06		0.03						10/24/06		0.029																																		10/12/06		0.05

		9/13/06		0.025						8/11/06		0.05						10/24/06		0.029																																		10/12/06		0.05

		9/13/06		0.03						8/14/06		0.05						10/26/06		0.03																																		10/13/06		0.05

		9/14/06		0.03						8/15/06		0.035						10/26/06		0.03																																		10/13/06		0.05

		9/15/06		0.03						8/16/06		0.05						10/30/06		0.025																																		10/14/06		0.05

		9/18/06		0.03						8/17/06		0.05						10/30/06		0.023																																		10/14/06		0.05

		9/19/06		0.03						8/17/06		0.05						10/31/06		0.025																																		10/16/06		0.05

		9/19/06		0.03						8/18/06		0.05						10/31/06		0.015																																		10/16/06		0.05

		9/20/06		0.03						8/18/06		0.05						11/1/06		0.026																																		10/17/06		0.05

		9/20/06		0.03						8/19/06		0.05						11/1/06		0.022																																		10/17/06		0.05

		9/21/06		0.02						8/19/06		0.05						11/2/06		0.025																																		10/18/06		0.05

		9/21/06		0.02						8/20/06		0.05						11/2/06		0.015																																		10/18/06		0.05

		9/22/06		0.02						8/21/06		0.05						11/3/06		0.025																																		10/19/06		0.05

		9/22/06		0.02						8/21/06		0.05						11/3/06		0.015																																		10/19/06		0.05

		9/23/06		0.02						8/22/06		0.045						11/6/06		0.025																																		10/20/06		0.05

		9/23/06		0.03						8/22/06		0.05						11/6/06		0.023																																		10/20/06		0.05

		9/25/06		0.02						8/23/06		0.05						11/7/06		0.02																																		10/23/06		0.05

		9/25/06		0.02						8/23/06		0.055						11/7/06		0.018																																		10/23/06		0.055

		9/26/06		0.02						8/24/06		0.05						11/8/06		0.04																																		10/24/06		0.05

		9/26/06		0.02						8/24/06		0.055						11/8/06		0.018																																		10/24/06		0.05

		9/27/06		0.02						8/25/06		0.05						11/9/06		0.02																																		10/25/06		0.05

		9/27/06		0.05						8/25/06		0.055						11/9/06		0.019																																		10/25/06		0.05

		9/28/06		0.03						8/26/06		0.05						11/10/06		0.02																																		10/26/06		0.05

		9/28/06		0.03						8/26/06		0.05						11/10/06		0.015																																		10/26/06		0.05

		9/29/06		0.02						8/28/06		0.05						11/13/06		0.02																																		10/27/06		0.05

		9/29/06		0.03						8/28/06		0.055						11/13/06		0.02																																		10/27/06		0.05

		10/2/06		0.04						8/29/06		0.05						11/14/06		0.02																																		10/28/06		0.05

		10/3/06		0.03						8/29/06		0.05						11/14/06		0.02																																		10/28/06		0.05

		10/3/06		0.03						8/30/06		0.05						11/15/06		0.02																																		10/30/06		0.05

		10/4/06		0.03						8/30/06		0.05						11/15/06		0.02																																		10/30/06		0.05

		10/4/06		0.03						8/31/06		0.05						11/16/06		0.02																																		10/31/06		0.05

		10/5/06		0.04						8/31/06		0.055						11/17/06		0.02																																		10/31/06		0.05

		10/5/06		0.03						9/1/06		0.05						11/17/06		0.018																																		11/1/06		0.05

		10/6/06		0.02						9/5/06		0.045						11/20/06		0.02																																		11/1/06		0.05

		10/7/06		0.05						9/5/06		0.05						11/20/06		0.015																																		11/2/06		0.05

		10/7/06		0.05						9/6/06		0.045						11/21/06		0.02																																		11/2/06		0.055

		10/9/06		0.04						9/7/06		0.05						11/21/06		0.012																																		11/3/06		0.045

		10/9/06		0.04						9/8/06		0.05						11/22/06		0.02																																		11/3/06		0.05

		10/10/06		0.02						9/11/06		0.05						11/22/06		0.02																																		11/6/06		0.05

		10/10/06		0.02						9/11/06		0.05						11/27/06		0.02																																		11/6/06		0.05

		10/11/06		0.03						9/12/06		0.05						11/27/06		0.04																																		11/7/06		0.05

		10/11/06		0.04						9/12/06		0.05						11/28/06		0.02																																		11/7/06		0.055

		10/12/06		0.035						9/13/06		0.05						11/28/06		0.01																																		11/8/06		0.05

		10/12/06		0.035						9/13/06		0.05						11/29/06		0.02																																		11/8/06		0.06

		10/13/06		0.04						9/14/06		0.05						11/29/06		0.015																																		11/9/06		0.05

		10/13/06		0.04						9/15/06		0.05						11/30/06		0.02																																		11/9/06		0.05

		10/14/06		0.04						9/18/06		0.05						11/30/06		0.015																																		11/10/06		0.05

		10/14/06		0.035						9/19/06		0.05						12/1/06		0.01																																		11/10/06		0.05

		10/16/06		0.04						9/19/06		0.05						12/1/06		0.012																																		11/13/06		0.05

		10/16/06		0.035						9/20/06		0.05						12/4/06		0.01																																		11/13/06		0.06

		10/17/06		0.03						9/20/06		0.05						12/4/06		0.015																																		11/14/06		0.06

		10/17/06		0.04						9/21/06		0.05						12/5/06		0.01																																		11/14/06		0.05

		10/18/06		0.03						9/21/06		0.05						12/5/06		0.015																																		11/15/06		0.055

		10/18/06		0.03						9/22/06		0.05						12/6/06		0.01																																		11/15/06		0.05

		10/19/06		0.025						9/22/06		0.05						12/6/06		0.01																																		11/16/06		0.055

		10/19/06		0.02						9/23/06		0.05						12/7/06		0.02																																		11/16/06		0.055

		10/20/06		0.035						9/23/06		0.05						12/7/06		0.01																																		11/17/06		0.05

		10/20/06		0.05						9/25/06		0.05						12/8/06		0.01																																		11/17/06		0.055

		10/21/06		0.04						9/25/06		0.05						12/8/06		0.01																																		11/18/06		0.05

		10/21/06		0.03						9/26/06		0.05						12/11/06		0.01																																		11/18/06		0.065

		10/23/06		0.035						9/26/06		0.05						12/11/06		0.015																																		11/20/06		0.05

		10/23/06		0.04						9/27/06		0.05						12/12/06		0.01																																		11/20/06		0.06

		10/24/06		0.02						9/27/06		0.02						12/12/06		0.015																																		11/21/06		0.05

		10/24/06		0.02						9/28/06		0.03						12/13/06		0.01																																		11/21/06		0.06

		10/25/06		0.035						9/28/06		0.03						12/13/06		0.015																																		11/22/06		0.05

		10/25/06		0.035						9/29/06		0.05						12/14/06		0.02																																		11/22/06		0.05

		10/26/06		0.025						9/29/06		0.05						12/18/06		0.01																																		11/27/06		0.05

		10/26/06		0.045						10/2/06		0.04						12/18/06		0.01																																		11/27/06		0.05

		10/27/06		0.03						10/3/06		0.05						12/19/06		0.01																																		11/28/06		0.055

		10/27/06		0.03						10/3/06		0.05						12/19/06		0.009																																		11/28/06		0.06

		10/28/06		0.03						10/4/06		0.05						12/20/06		0.01																																		11/29/06		0.05

		10/28/06		0.025						10/4/06		0.05						12/20/06		0.01																																		11/29/06		0.055

		10/30/06		0.035						10/5/06		0.04						12/21/06		0.01																																		11/30/06		0.05

		10/30/06		0.035						10/5/06		0.04						12/21/06		0.008																																		11/30/06		0.05

		10/31/06		0.03						10/6/06		0.03						12/22/06		0.01																																		12/1/06		0.05

		11/1/06		0.025						10/7/06		0.03						12/27/06		0.03																																		12/1/06		0.065

		11/2/06		0.035						10/7/06		0.03						12/28/06		0.01																																		12/2/06		0.05

		11/2/06		0.03						10/9/06		0.03						12/28/06		0.01																																		12/2/06		0.065

		11/3/06		0.02						10/9/06		0.03						12/29/06		0.01																																		12/4/06		0.045

		11/6/06		0.015						10/10/06		0.05						12/29/06		0.01																																		12/4/06		0.05

		11/7/06		0.02						10/10/06		0.05						1/2/07		0.01																																		12/5/06		0.045

		11/8/06		0.025						10/11/06		0.03						1/2/07		0.01																																		12/5/06		0.05

		11/9/06		0.03						10/11/06		0.04						1/3/07		0.01																																		12/6/06		0.05

		11/10/06		0.025						10/12/06		0.035						1/3/07		0.01																																		12/6/06		0.05

		11/11/06		0.035						10/12/06		0.035						1/4/07		0.01																																		12/7/06		0.05

		11/13/06		0.035						10/13/06		0.03						1/4/07		0.01																																		12/7/06		0.05

		11/13/06		0.02						10/13/06		0.04						1/5/07		0.01																																		12/8/06		0.05

		11/14/06		0.02						10/14/06		0.03						1/5/07		0.01																																		12/8/06		0.05

		11/14/06		0.02						10/14/06		0.035						1/8/07		0.01																																		12/9/06		0.05

		11/15/06		0.03						10/16/06		0.04						1/8/07		0.01																																		12/9/06		0.05

		11/15/06		0.035						10/16/06		0.04						1/9/07		0.01																																		12/11/06		0.05

		11/16/06		0.035						10/17/06		0.04						1/9/07		0.01																																		12/11/06		0.05

		11/17/06		0.03						10/17/06		0.04						1/10/07		0.01																																		12/12/06		0.05

		11/17/06		0.035						10/18/06		0.04						1/10/07		0.01																																		12/12/06		0.05

		11/18/06		0.03						10/18/06		0.04						1/11/07		0.02																																		12/13/06		0.055

		11/18/06		0.03						10/19/06		0.04						1/11/07		0.01																																		12/13/06		0.055

		11/20/06		0.045						10/19/06		0.04						1/12/07		0.01																																		12/14/06		0.04

		11/21/06		0.035						10/20/06		0.04						1/12/07		0.01																																		12/14/06		0.05

		11/22/06		0.025						10/20/06		0.04						1/15/07		0.02																																		12/15/06		0.05

		11/22/06		0.035						10/21/06		0.03						1/15/07		0.01																																		12/15/06		0.05

		11/27/06		0.03						10/21/06		0.04						1/16/07		0.01																																		2/28/07		0.04

		11/27/06		0.035						10/23/06		0.035						1/16/07		0.015																																		2/28/07		0.04

		11/28/06		0.015						10/23/06		0.04						1/17/07		0.01																																		3/1/07		0.04

		11/29/06		0.015						10/24/06		0.035						1/17/07		0.01																																		3/2/07		0.04

		11/30/06		0.025						10/24/06		0.035						1/18/07		0.01																																		3/3/07		0.04

		12/1/06		0.025						10/25/06		0.03						1/18/07		0.01																																		3/5/07		0.04

		12/2/06		0.025						10/25/06		0.045						1/19/07		0.01																																		3/6/07		0.04

		12/4/06		0.025						10/26/06		0.045						1/19/07		0.01																																		3/7/07		0.04

		12/5/06		0.03						10/26/06		0.04						1/22/07		0.01																																		3/8/07		0.04

		12/6/06		0.03						10/27/06		0.035						1/22/07		0.02																																		3/9/07		0.04

		12/6/06		0.03						10/27/06		0.03						1/23/07		0.01																																		3/12/07		0.045

		12/7/06		0.03						10/28/06		0.03						1/23/07		0.01																																		3/13/07		0.04

		12/7/06		0.035						10/28/06		0.05						1/24/07		0.01																																		3/14/07		0.04

		12/8/06		0.03						10/30/06		0.035						1/24/07		0.005																																		3/15/07		0.03

		12/8/06		0.03						10/30/06		0.035						1/25/07		0.01																																		3/16/07		0.04

		12/9/06		0.03						10/31/06		0.035						1/25/07		0.01																																		3/17/07		0.04

		12/11/06		0.03						11/1/06		0.035						1/26/07		0.01																																		3/19/07		0.03

		12/11/06		0.03						11/2/06		0.035						1/26/07		0.01																																		3/20/07		0.04

		12/12/06		0.03						11/2/06		0.04						1/29/07		0.01																																		3/21/07		0.04

		12/12/06		0.035						11/3/06		0.035						1/29/07		0.01																																		3/22/07		0.03

		12/13/06		0.03						11/6/06		0.05						1/30/07		0.01																																		3/23/07		0.03

		12/13/06		0.03						11/7/06		0.035						1/30/07		0.01																																		3/26/07		0.04

		12/14/06		0.03						11/8/06		0.04						1/31/07		0.01																																		3/27/07		0.03

		12/14/06		0.03						11/9/06		0.035						1/31/07		0.01																																		3/28/07		0.04

		12/15/06		0.03						11/10/06		0.045						2/1/07		0.01																																		3/29/07		0.03

		12/15/06		0.03						11/11/06		0.04						2/1/07		0.005																																		3/30/07		0.04

		12/18/06		0.03						11/13/06		0.04						2/2/07		0.01																																		3/31/07		0.03

		12/18/06		0.03						11/13/06		0.05						2/2/07		0.005																																		4/2/07		0.03

		12/19/06		0.03						11/14/06		0.04						2/5/07		0.01																																		4/3/07		0.045

		12/19/06		0.03						11/14/06		0.04						2/5/07		0.005																																		4/4/07		0.04

		12/20/06		0.03						11/15/06		0.03						2/6/07		0.01																																		4/5/07		0.04

		12/21/06		0.03						11/15/06		0.03						2/6/07		0.005																																		4/6/07		0.04

		12/21/06		0.03						11/16/06		0.03						2/7/07		0.01																																		4/9/07		0.04

		12/22/06		0.02						11/17/06		0.03						2/7/07		0.005																																		4/10/07		0.03

		12/22/06		0.035						11/17/06		0.035						2/8/07		0.01																																		4/11/07		0.04

		12/27/06		0.03						11/18/06		0.03						2/8/07		0.015																																		4/12/07		0.04

		12/27/06		0.03						11/18/06		0.03						2/9/07		0.01																																		4/13/07		0.035

		12/28/06		0.03						11/20/06		0.015						2/9/07		0.018																																		4/16/07		0.035

		12/28/06		0.03						11/21/06		0.03						2/12/07		0.01																																		4/17/07		0.04

		12/29/06		0.03						11/22/06		0.035						2/12/07		0.012																																		4/18/07		0.035

		12/29/06		0.035						11/22/06		0.035						2/13/07		0.01																																		4/19/07		0.04

		1/2/07		0.03						11/27/06		0.035						2/13/07		0.02																																		4/20/07		0.04

		1/2/07		0.03						11/27/06		0.03						2/14/07		0.02																																		4/23/07		0.03

		1/3/07		0.03						11/28/06		0.035						2/14/07		0.015																																		4/24/07		0.04

		1/3/07		0.03						11/29/06		0.035						2/15/07		0.02																																		4/25/07		0.035

		1/4/07		0.03						11/30/06		0.035						2/16/07		0.01																																		4/26/07		0.035

		1/5/07		0.03						12/1/06		0.03						2/20/07		0.015																																		4/27/07		0.035

		1/5/07		0.03						12/2/06		0.03						2/20/07		0.015																																		4/28/07		0.045

		1/8/07		0.03						12/4/06		0.03						2/21/07		0.02																																		4/30/07		0.04

		1/8/07		0.03						12/5/06		0.03						2/21/07		0.015																																		5/1/07		0.04

		1/9/07		0.03						12/6/06		0.03						2/22/07		0.02																																		5/2/07		0.04

		1/9/07		0.03						12/6/06		0.035						2/22/07		0.018																																		5/3/07		0.04

		1/10/07		0.03						12/7/06		0.03						2/23/07		0.02																																		5/4/07		0.04

		1/10/07		0.03						12/7/06		0.03						2/23/07		0.016																																		5/5/07		0.04

		1/11/07		0.03						12/8/06		0.03						2/26/07		0.015																																		5/7/07		0.035

		1/11/07		0.03						12/8/06		0.035						2/26/07		0.014																																		5/8/07		0.04

		1/12/07		0.03						12/9/06		0.03						2/27/07		0.015																																		5/9/07		0.045

		1/13/07		0.03						12/11/06		0.03						2/27/07		0.014																																		5/10/07		0.04

		1/13/07		0.03						12/11/06		0.03						2/28/07		0.01																																		5/11/07		0.035

		1/15/07		0.03						12/12/06		0.03						3/1/07		0.015																																		5/14/07		0.03

		1/15/07		0.03						12/12/06		0.03						3/2/07		0.015																																		5/15/07		0.035

		1/16/07		0.03						12/13/06		0.03						3/5/07		0.01																																		5/16/07		0.045

		1/16/07		0.025						12/13/06		0.03						3/6/07		0.01																																		5/17/07		0.035

		1/17/07		0.02						12/14/06		0.03						3/7/07		0.04																																		5/18/07		0.04

		1/18/07		0.02						12/14/06		0.035						3/8/07		0.04																																		5/19/07		0.04

		1/19/07		0.03						12/15/06		0.03						3/9/07		0.04																																		5/21/07		0.04

		1/19/07		0.03						12/15/06		0.035						3/12/07		0.04																																		5/22/07		0.04

		1/20/07		0.03						12/18/06		0.03						3/13/07		0.04																																		5/23/07		0.045

		1/22/07		0.03						12/18/06		0.03						3/14/07		0.04																																		5/24/07		0.04

		1/23/07		0.03						12/19/06		0.03						3/15/07		0.035																																		5/29/07		0.03

		1/24/07		0.03						12/19/06		0.03						3/16/07		0.04																																		5/30/07		0.03

		1/24/07		0.03						12/20/06		0.03						3/19/07		0.035																																		5/31/07		0.035

		1/25/07		0.03						12/21/06		0.03						3/20/07		0.035																																		6/1/07		0.035

		1/25/07		0.03						12/21/06		0.035						3/21/07		0.035																																		6/2/07		0.05

		1/26/07		0.03						12/22/06		0.03						3/22/07		0.032																																		6/4/07		0.035

		1/26/07		0.035						12/22/06		0.03						3/23/07		0.03																																		6/5/07		0.04

		1/29/07		0.03						12/27/06		0.03						3/26/07		0.03																																		6/6/07		0.04

		1/29/07		0.035						12/27/06		0.03						3/27/07		0.03																																		6/7/07		0.04

		1/30/07		0.035						12/28/06		0.03						3/28/07		0.035																																		6/8/07		0.045

		1/30/07		0.035						12/28/06		0.035						3/29/07		0.035																																		6/9/07		0.04

		1/31/07		0.03						12/29/06		0.03						3/30/07		0.03																																		6/11/07		0.04

		1/31/07		0.035						12/29/06		0.035						4/2/07		0.03																																		6/12/07		0.04

		2/1/07		0.03						1/2/07		0.03						4/3/07		0.025																																		6/13/07		0.04

		2/1/07		0.03						1/2/07		0.03						4/4/07		0.03																																		6/14/07		0.035

		2/2/07		0.03						1/3/07		0.03						4/5/07		0.025																																		6/15/07		0.045

		2/2/07		0.03						1/3/07		0.03						4/6/07		0.03																																		6/16/07		0.05

		2/3/07		0.03						1/4/07		0.03						4/9/07		0.025																																		6/19/07		0.04

		2/3/07		0.035						1/5/07		0.03						4/10/07		0.03																																		6/20/07		0.04

		2/5/07		0.03						1/5/07		0.03						4/11/07		0.03																																		6/21/07		0.035

		2/5/07		0.03						1/8/07		0.03						4/12/07		0.03																																		6/22/07		0.04

		2/6/07		0.03						1/8/07		0.03						4/13/07		0.028																																		6/23/07		0.04

		2/6/07		0.03						1/9/07		0.03						4/16/07		0.032																																		6/25/07		0.04

		2/7/07		0.05						1/9/07		0.03						4/17/07		0.03																																		6/26/07		0.04

		2/7/07		0.04						1/10/07		0.03						4/18/07		0.025																																		6/27/07		0.04

		2/8/07		0.04						1/10/07		0.035						4/19/07		0.025																																		6/28/07		0.04

		2/8/07		0.03						1/11/07		0.03						4/23/07		0.04																																		6/29/07		0.04

		2/10/07		0.03						1/11/07		0.03						4/24/07		0.044																																		7/2/07		0.04

		2/10/07		0.05						1/12/07		0.03						4/25/07		0.049																																		7/3/07		0.045

		2/12/07		0.03						1/13/07		0.03						4/26/07		0.049																																		7/5/07		0.05

		2/13/07		0.035						1/13/07		0.03						4/27/07		0.045																																		7/6/07		0.05

		2/13/07		0.04						1/15/07		0.03						4/30/07		0.045																																		7/9/07		0.045

		2/14/07		0.04						1/15/07		0.03						5/1/07		0.042																																		7/10/07		0.07

		2/14/07		0.04						1/16/07		0.03						5/2/07		0.045																																		7/11/07		0.045

		2/15/07		0.05						1/16/07		0.03						5/3/07		0.042																																		7/12/07		0.055

		2/15/07		0.04						1/17/07		0.03						5/4/07		0.045																																		7/13/07		0.05

		2/16/07		0.04						1/18/07		0.03						5/7/07		0.045																																		7/14/07		0.05

		2/16/07		0.04						1/19/07		0.035						5/8/07		0.045																																		7/16/07		0.055

		2/20/07		0.05						1/19/07		0.03						5/9/07		0.045																																		7/17/07		0.05

		2/20/07		0.05						1/20/07		0.03						5/10/07		0.045																																		7/18/07		0.075

		2/21/07		0.04						1/22/07		0.03						5/11/07		0.045																																		7/19/07		0.07

		2/21/07		0.055						1/23/07		0.03						5/14/07		0.046																																		7/20/07		0.07

		2/22/07		0.04						1/24/07		0.03						5/15/07		0.05																																		7/23/07		0.07

		2/22/07		0.05						1/24/07		0.03						5/16/07		0.055																																		7/24/07		0.07

		2/23/07		0.03						1/25/07		0.03						5/17/07		0.045																																		7/25/07		0.065

		2/23/07		0.05						1/25/07		0.03						5/18/07		0.04																																		7/26/07		0.055

		2/26/07		0.05						1/26/07		0.03						5/21/07		0.044																																		7/27/07		0.06

		2/26/07		0.04						1/26/07		0.035						5/22/07		0.045																																		7/28/07		0.065

		2/27/07		0.03						1/29/07		0.035						5/23/07		0.045																																		7/30/07		0.05

		2/27/07		0.04						1/29/07		0.035						5/24/07		0.04																																		7/31/07		0.06

		2/28/07		0.03						1/30/07		0.03						5/24/07		0.04																																		8/1/07		0.06

		2/28/07		0.03						1/30/07		0.03						5/29/07		0.025																																		8/2/07		0.06

		3/1/07		0.04						1/31/07		0.03						5/30/07		0.045																																		8/3/07		0.06

		3/2/07		0.04						1/31/07		0.035						5/31/07		0.05																																		8/6/07		0.06

		3/5/07		0.04						2/1/07		0.035						6/1/07		0.051																																		8/7/07		0.06

		3/6/07		0.04						2/1/07		0.03						6/4/07		0.044																																		8/8/07		0.05

		3/7/07		0.04						2/2/07		0.03						6/5/07		0.047																																		8/9/07		0.05

		3/8/07		0.04						2/2/07		0.03						6/6/07		0.046																																		8/10/07		0.05

		3/9/07		0.04						2/3/07		0.03						6/7/07		0.05																																		8/11/07		0.05

		3/12/07		0.04						2/3/07		0.03						6/8/07		0.048																																		8/13/07		0.06

		3/13/07		0.03						2/5/07		0.03						6/9/07		0.049																																		8/14/07		0.05

		3/14/07		0.03						2/5/07		0.03						6/11/07		0.049																																		8/15/07		0.05

		3/15/07		0.04						2/6/07		0.03						6/12/07		0.05																																		8/16/07		0.055

		3/16/07		0.04						2/6/07		0.035						6/13/07		0.045																																		8/17/07		0.055

		3/19/07		0.03						2/7/07		0.03						6/14/07		0.048																																		8/20/07		0.05

		3/20/07		0.04						2/7/07		0.03						6/15/07		0.045																																		8/21/07		0.05

		3/21/07		0.035						2/8/07		0.03						6/18/07		0.045																																		8/22/07		0.05

		3/22/07		0.04						2/8/07		0.03						6/19/07		0.045																																		8/23/07		0.05

		3/23/07		0.04						2/10/07		0.03						6/20/07		0.045																																		8/24/07		0.05

		3/26/07		0.035						2/10/07		0.04						6/21/07		0.045																																		8/27/07		0.05

		3/27/07		0.04						2/12/07		0.03						6/25/07		0.042																																		8/28/07		0.05

		3/28/07		0.035						2/13/07		0.035						6/26/07		0.045																																		8/29/07		0.05

		3/29/07		0.035						2/13/07		0.05						6/27/07		0.04																																		8/30/07		0.05

		3/30/07		0.03						2/14/07		0.04						6/28/07		0.063																																		8/31/07		0.05

		3/31/07		0.035						2/14/07		0.04						6/29/07		0.061																																		9/4/07		0.05

		4/2/07		0.04						2/15/07		0.05						7/2/07		0.06																																		9/5/07		0.05

		4/3/07		0.035						2/15/07		0.04						7/3/07		0.062																																		9/6/07		0.05

		4/4/07		0.035						2/16/07		0.04						7/5/07		0.06																																		9/7/07		0.055

		4/5/07		0.035						2/16/07		0.04						7/6/07		0.058																																		9/10/07		0.045

		4/6/07		0.035						2/20/07		0.05						7/9/07		0.06																																		9/11/07		0.05

		4/9/07		0.035						2/20/07		0.05						7/10/07		0.06																																		9/12/07		0.05

		4/10/07		0.03						2/21/07		0.04						7/11/07		0.055																																		9/13/07		0.045

		4/11/07		0.03						2/21/07		0.035						7/12/07		0.056																																		9/14/07		0.05

		4/12/07		0.03						2/22/07		0.04						7/13/07		0.056																																		9/17/07		0.05

		4/13/07		0.03						2/22/07		0.04						7/16/07		0.055																																		9/18/07		0.045

		4/14/07		0.03						2/23/07		0.03						7/17/07		0.05																																		9/19/07		0.05

		4/16/07		0.03						2/23/07		0.04						7/18/07		0.045																																		9/20/07		0.05

		4/17/07		0.03						2/26/07		0.03						7/19/07		0.045																																		9/21/07		0.05

		4/18/07		0.025						2/26/07		0.035						7/20/07		0.04																																		9/22/07		0.05

		4/19/07		0.03						2/27/07		0.03						7/23/07		0.04																																		9/24/07		0.05

		4/20/07		0.035						2/27/07		0.03						7/24/07		0.04																																		9/25/07		0.05

		4/21/07		0.035						2/28/07		0.03						7/25/07		0.04																																		9/26/07		0.05

		4/23/07		0.025						3/1/07		0.03						7/26/07		0.04																																		9/27/07		0.05

		4/24/07		0.02						3/2/07		0.03						7/28/07		0.04																																		9/28/07		0.05

		4/25/07		0.03						3/5/07		0.03						7/30/07		0.044																																		10/1/07		0.05

		4/26/07		0.04						3/6/07		0.03						7/31/07		0.044																																		10/2/07		0.06

		4/27/07		0.025						3/7/07		0.04						8/1/07		0.04																																		10/3/07		0.05

		4/30/07		0.025						3/8/07		0.04						8/2/07		0.04																																		10/4/07		0.05

		5/1/07		0.03						3/9/07		0.04						8/3/07		0.04																																		10/5/07		0.045

		5/2/07		0.02						3/12/07		0.04						8/4/07		0.042																																		10/8/07		0.05

		5/3/07		0.02						3/13/07		0.04						8/6/07		0.04																																		10/9/07		0.05

		5/4/07		0.02						3/14/07		0.03						8/7/07		0.04																																		10/10/07		0.05

		5/5/07		0.02						3/15/07		0.035						8/8/07		0.034																																		10/11/07		0.05

		5/7/07		0.02						3/16/07		0.035						8/9/07		0.032																																		10/12/07		0.05

		5/8/07		0.025						3/19/07		0.035						8/10/07		0.043																																		10/15/07		0.05

		5/9/07		0.03						3/20/07		0.04						8/13/07		0.045																																		10/16/07		0.045

		5/10/07		0.025						3/21/07		0.04						8/14/07		0.045																																		10/17/07		0.05

		5/11/07		0.005						3/22/07		0.04						8/15/07		0.043																																		10/18/07		0.05

		5/14/07		0.035						3/23/07		0.035						8/16/07		0.04																																		10/19/07		0.045

		5/15/07		0.035						3/26/07		0.035						8/17/07		0.04																																		10/22/07		0.05

		5/16/07		0.03						3/27/07		0.04						8/20/07		0.04																																		10/23/07		0.05

		5/17/07		0.03						3/28/07		0.04						8/21/07		0.03																																		10/24/07		0.045

		5/18/07		0.03						3/29/07		0.035						8/22/07		0.04																																		10/25/07		0.045

		5/19/07		0.03						3/30/07		0.03						8/23/07		0.04																																		10/26/07		0.05

		5/21/07		0.025						3/31/07		0.035						8/24/07		0.04																																		10/29/07		0.05

		5/22/07		0.025						4/2/07		0.035						8/27/07		0.045																																		10/30/07		0.045

		5/23/07		0.025						4/3/07		0.035						8/28/07		0.04																																		10/31/07		0.05

		5/24/07		0.02						4/4/07		0.04						8/29/07		0.055																																		11/1/07		0.045

		5/25/07		0.025						4/5/07		0.04						8/30/07		0.055																																		11/2/07		0.05

		5/29/07		0.025						4/6/07		0.04						8/31/07		0.05																																		11/5/07		0.05

		5/30/07		0.048						4/9/07		0.035						9/4/07		0.05																																		11/6/07		0.045

		5/31/07		0.04						4/10/07		0.035						9/5/07		0.04						0.61		0.4																										11/7/07		0.05

		6/1/07		0.025						4/11/07		0.04						9/6/07		0.05						0.61		0.41																										11/8/07		0.05

		6/2/07		0.03						4/12/07		0.035						9/7/07		0.045						0.6		0.41																										11/9/07		0.05

		6/4/07		0.03						4/13/07		0.035						9/8/07		0.04						0.6		0.41																										11/12/07		0.045

		6/5/07		0.0175						4/14/07		0.03						9/10/07		0.055						0.61		0.41																										11/13/07		0.05

		6/6/07		0.03						4/16/07		0.035						9/11/07		0.05						0.61		0.41																										11/14/07		0.045

		6/7/07		0.04						4/17/07		0.035						9/12/07		0.05						0.61		0.41																										11/15/07		0.045

		6/8/07		0.025						4/18/07		0.04						9/13/07		0.05						0.61		0.41																										11/16/07		0.045

		6/9/07		0.02						4/19/07		0.035						9/14/07		0.05						0.6		0.42																										11/19/07		0.045

		6/11/07		0.04						4/20/07		0.04						9/15/07		0.05						0.6		0.4																										11/20/07		0.045

		6/12/07		0.02						4/21/07		0.035						9/17/07		0.054						0.6		0.41																										11/21/07		0.045

		6/13/07		0.03						4/23/07		0.035						9/18/07		0.054						0.61		0.41																										11/26/07		0.045

		6/14/07		0.025						4/24/07		0.02						9/19/07		0.045						0.65		0.4																										11/27/07		0.045

		6/15/07		0.02						4/25/07		0.04						9/20/07		0.045						0.61		0.41																										11/28/07		0.045

		6/18/07		0.025						4/26/07		0.035						9/21/07		0.04						0.6		0.4																										11/29/07		0.045

		6/19/07		0.02						4/27/07		0.04						9/24/07		0.035						0.6		0.4																										11/30/07		0.045

		6/20/07		0.03						4/30/07		0.025						9/25/07		0.04						0.62		0.4																										12/1/07		0.045

		6/21/07		0.016						5/1/07		0.03						9/26/07		0.04						0.62		0.42																										12/3/07		0.045

		6/22/07		0.025						5/2/07		0.03						9/27/07		0.04						0.62		0.42																										12/4/07		0.045

		6/25/07		0.02						5/3/07		0.03						9/28/07		0.05						0.6		0.4																										12/5/07		0.045

		6/26/07		0.025						5/4/07		0.035						10/1/07		0.04						0.62		0.42																										12/6/07		0.045

		6/27/07		0.03						5/5/07		0.035						10/2/07		0.045						0.62		0.42																										12/7/07		0.045

		6/28/07		0.045						5/7/07		0.04						10/3/07		0.045						0.62		0.42																										12/8/07		0.045

		6/29/07		0.025						5/8/07		0.045						10/4/07		0.05						0.61		0.42																										12/10/07		0.045

		7/2/07		0.04						5/9/07		0.03						10/5/07		0.05						0.62		0.42																										12/11/07		0.04

		7/3/07		0.04						5/10/07		0.04						10/8/07		0.05						0.62		0.42																										12/12/07		0.04

		7/5/07		0.04						5/11/07		0.03						10/9/07		0.04						0.62		0.42																										12/13/07		0.04

		7/6/07		0.04						5/14/07		0.03						10/10/07		0.04						0.62		0.42																										12/14/07		0.04

		7/9/07		0.04						5/15/07		0.03						10/11/07		0.05						0.62		0.42																										12/17/07		0.04

		7/10/07		0.03						5/16/07		0.03						10/12/07		0.045						0.62		0.42																										12/18/07		0.045

		7/11/07		0.035						5/17/07		0.03						10/13/07		0.04						0.62		0.42																										12/19/07		0.04

		7/12/07		0.035						5/18/07		0.03						10/15/07		0.04						0.61		0.41																										12/20/07		0.04

		7/13/07		0.03						5/19/07		0.03						10/16/07		0.04						0.62		0.42																										12/26/07		0.04

		7/16/07		0.03						5/21/07		0.03						10/17/07		0.04						0.61		0.41																										12/27/07		0.04

		7/17/07		0.035						5/22/07		0.03						10/18/07		0.04						0.62		0.42																										12/28/07		0.04

		7/18/07		0.03						5/23/07		0.03						10/19/07		0.04						0.62		0.42																										12/31/07		0.05

		7/19/07		0.03						5/24/07		0.03						10/22/07		0.045						0.62		0.42																										1/2/08		0.04

		7/20/07		0.03						5/25/07		0.03						10/23/07		0.05						0.64		0.44																										1/3/08		0.04

		7/23/07		0.04						5/29/07		0.035						10/24/07		0.045						0.62		0.42																										1/4/08		0.04

		7/24/07		0.035						5/30/07		0.02						10/25/07		0.03						0.62		0.42																										1/7/08		0.04

		7/25/07		0.035						5/31/07		0.03						10/26/07		0.035						0.62		0.42																										1/8/08		0.04

		7/26/07		0.04						6/1/07		0.03						10/29/07		0.03						0.62		0.42																										1/9/08		0.04

		7/27/07		0.04						6/2/07		0.03						10/30/07		0.025						0.62		0.42																										1/10/08		0.04

		7/30/07		0.035						6/4/07		0.03						10/31/07		0.03						0.62		0.42																										1/11/08		0.04

		7/31/07		0.035						6/5/07		0.04						11/1/07		0.035						0.62		0.42																										1/14/08		0.04

		8/1/07		0.03						6/6/07		0.025						11/2/07		0.035						0.62		0.42																										1/15/08		0.04

		8/2/07		0.035						6/7/07		0.03						11/5/07		0.025						0.62		0.4																										1/16/08		0.04

		8/3/07		0.04						6/8/07		0.03						11/6/07		0.04						0.62		0.41																										1/17/08		0.04

		8/4/07		0.03						6/9/07		0.025						11/7/07		0.02						0.62		0.42																										1/18/08		0.04

		8/6/07		0.03						6/11/07		0.03						11/8/07		0.03						0.62		0.42																										1/21/08		0.04

		8/7/07		0.035						6/12/07		0.02						11/9/07		0.02						0.62		0.42																										1/22/08		0.04

		8/8/07		0.03						6/13/07		0.03						11/12/07		0.035						0.62		0.42																										1/23/08		0.04

		8/9/07		0.03						6/14/07		0.025						11/13/07		0.04						0.62		0.4																										1/24/08		0.04

		8/10/07		0.04						6/15/07		0.025						11/14/07		0.04						0.62		0.42																										1/25/08		0.045

		8/13/07		0.03						6/18/07		0.03						11/15/07		0.04						0.62		0.42																										1/28/08		0.04

		8/14/07		0.03						6/19/07		0.025						11/16/07		0.035						0.62		0.42																										1/29/08		0.04

		8/15/07		0.03						6/20/07		0.03						11/19/07		0.045						0.66		0.44																										1/30/08		0.04

		8/17/07		0.03						6/21/07		0.03						11/20/07		0.04						0.64		0.42																										1/31/08		0.04

		8/20/07		0.03						6/22/07		0.02						11/21/07		0.04						0.64		0.42																										2/1/08		0.04

		8/21/07		0.03						6/25/07		0.02						11/26/07		0.04						0.66		0.44																										2/4/08		0.04

		8/22/07		0.03						6/26/07		0.02						11/27/07		0.042						0.66		0.44																										2/5/08		0.04

		8/23/07		0.03						6/27/07		0.03						11/28/07		0.04						0.66		0.44																										2/6/08		0.04

		8/24/07		0.03						6/28/07		0.03						11/29/07		0.03						0.64		0.44																										2/7/08		0.04

		8/25/07		0.02						6/29/07		0.04						11/30/07		0.03						0.64		0.44																										2/8/08		0.04

		8/27/07		0.04						7/2/07		0.03						12/3/07		0.04						0.64		0.44																										2/11/08		0.04

		8/28/07		0.035						7/3/07		0.025						12/4/07		0.03						0.64		0.42																										2/12/08		0.04

		8/29/07		0.04						7/5/07		0.03						12/5/07		0.03						0.64		0.44																										2/13/08		0.04

		8/30/07		0.03						7/6/07		0.025						12/6/07		0.03						0.64		0.42																										2/14/08		0.04

		8/31/07		0.03						7/9/07		0.025						12/7/07		0.03						0.64		0.44																										2/15/08		0.04

		9/4/07		0.03						7/10/07		0.03						12/10/07		0.03						0.64		0.44																										2/16/08		0.04

		9/5/07		0.03						7/11/07		0.035						12/11/07		0.03						0.66		0.42																										2/19/08		0.04

		9/6/07		0.035						7/12/07		0.035						12/12/07		0.03						0.6		0.42																										2/20/08		0.045

		9/7/07		0.02						7/13/07		0.03						12/13/07		0.045						0.66		0.42																										2/21/08		0.04

		9/8/07		0.04						7/16/07		0.03						12/14/07		0.03						0.66		0.42																										2/22/08		0.04

		9/10/07		0.025						7/17/07		0.03						12/17/07		0.03						0.64		0.42																										2/25/08		0.04

		9/11/07		0.035						7/18/07		0.025						12/18/07		0.03						0.66		0.4																										2/26/08		0.04

		9/12/07		0.035						7/19/07		0.025						12/19/07		0.02						0.66		0.42																										2/27/08		0.04

		9/13/07		0.03						7/20/07		0.035						12/20/07		0.03						0.64		0.42																										2/28/08		0.04

		9/14/07		0.03						7/23/07		0.03						12/21/07		0.04						0.66		0.42																										2/29/08		0.04

		9/17/07		0.03						7/24/07		0.025						12/26/07		0.03						0.64		0.42																										3/1/08		0.04

		9/18/07		0.025						7/25/07		0.035						12/27/07		0.025						0.62		0.44																										3/2/08		0.04

		9/19/07		0.04						7/26/07		0.03						12/28/07		0.025						0.64		0.44																										3/3/08		0.04

		9/20/07		0.04						7/27/07		0.03						12/31/07		0.02						0.64		0.44																										3/4/08		0.04

		9/21/07		0.03						7/30/07		0.035																																										3/5/08		0.04

		9/24/07		0.025						7/31/07		0.04						2/14/08		0.04						0.292		0.309		0.485		61		1180																				3/6/08		0.04

		9/25/07		0.035						8/1/07		0.03						2/15/08		0.037		69		50		0.28		0.31		0.414		61		1172																				3/7/08		0.04

		9/26/07		0.025						8/2/07		0.035						2/19/08		0.035		69		48		0.293		0.309		0.426		60		1184																				3/8/08		0.04

		9/27/07		0.02						8/3/07		0.03						2/20/08		0.03		70		46		0.26		0.309		0.41		63		1184																				3/10/08		0.04

		9/28/07		0.02						8/4/07		0.03						2/21/08		0.032		70		46		0.29		0.305		0.441		62		1164																				3/11/08		0.04

		9/29/07		0.02						8/6/07		0.03						2/22/08		0.031		70		45		0.281		0.307		0.419		62		1184																				3/12/08		0.04

		10/1/07		0.015						8/7/07		0.025						2/25/08		0.069		70		46		0.288		0.311		0.421		63		1184																				3/13/08		0.04

		10/2/07		0.035						8/8/07		0.03						2/26/08		0.068		70		44		0.281		0.312		0.413		64		1192																				3/14/08		0.04

		10/3/07		0.03						8/9/07		0.045						2/27/08		0.067		70		45		0.288		0.311		0.413		62		1184																				3/15/08		0.04

		10/4/07		0.04						8/10/07		0.04						2/28/08		0.063		70		46		0.283		0.31		0.457		62		1172																				3/17/08		0.04

		10/5/07		0.025						8/13/07		0.04						2/29/08		0.064		70		45		0.256		0.311		0.409		63		1184																				3/18/08		0.04

		10/8/07		0.03						8/14/07		0.04						3/3/08		0.07		70		33		0.285		0.311		0.435		63		1204																				3/19/08		0.04

		10/9/07		0.03						8/15/07		0.04						3/4/08		0.07		70		44		0.261		0.311		0.438		63		1184																				3/20/08		0.04

		10/10/07		0.03						8/17/07		0.04						3/5/08		0.069		70		44		0.291		0.311		0.445		63		1184																				3/21/08		0.04

		10/11/07		0.03						8/20/07		0.03						3/6/08		0.068		70		44		0.281		0.311		0.458		61		1184																				3/22/08		0.04

		10/12/07		0.02						8/21/07		0.03						3/7/08		0.067		70		44		0.282		0.322		0.455		63		1192																				3/24/08		0.04

		10/15/07		0.03						8/22/07		0.035						3/10/08		0.069		70		46		0.264		0.321		0.428		64		1184																				3/25/08		0.04

		10/16/07		0.02						8/23/07		0.03						3/11/08		0.071		70		43		0.285		0.322		0.438		63		1204																				3/26/08		0.045

		10/17/07		0.04						8/24/07		0.035						3/12/08		0.056		70		44		0.261		0.312		0.422		62		1188																				3/27/08		0.04		70		25

		10/18/07		0.04						8/25/07		0.02						3/14/08		0.067		70		43		0.261		0.321		0.451		63		1184																				3/28/08		0.04		70		41

		10/19/07		0.025						8/27/07		0.025						3/17/08		0.069		70		45		0.26		0.32		0.439		63		1196																				3/31/08		0.04		70		28

		10/22/07		0.03						8/28/07		0.025						3/18/08		0.062		70		47		0.279		0.32		0.422		63		1196																				4/1/08		0.04		70		29

		10/23/07		0.03						8/29/07		0.03						3/19/08		0.053		70		44		0.273		0.321		0.419		64		1192																				4/2/08		0.055		70		36

		10/24/07		0.04						8/30/07		0.03						3/20/08		0.064		70		33		0.262		0.321		0.431		64		1192																				4/3/08		0.04		69		40

		10/25/07		0.035						8/31/07		0.03						3/21/08		0.063		70		35		0.277		0.322		0.439		63		1196																				4/4/08		0.045		70		44

		10/26/07		0.045						9/4/07		0.03						3/24/08		0.052		70		42		0.238		0.321		0.418		63		1184																				4/5/08		0.04		70		41

		10/29/07		0.02						9/5/07		0.03						3/25/08		0.057		70		38		0.264		0.319		0.445		63		1192																				4/7/08		0.05		70		44

		10/30/07		0.02						9/6/07		0.03						3/26/08		0.056		70		35		0.276		0.321		0.447		63		1204																				4/8/08		0.05		70		44

		10/31/07		0.02						9/7/07		0.03						3/27/08		0.07		70		24		0.28		0.32		0.46		63		1204																				4/9/08		0.05		70		44

		11/1/07		0.03						9/8/07		0.03						3/28/08		0.05		70		40		0.26		0.32		0.44		63		1192																				4/10/08		0.05		70		44

		11/2/07		0.025						9/10/07		0.02						3/31/08		0.06		70		27		0.3		0.32		0.48		63		1204																				4/11/08		0.05		70		46

		11/5/07		0.03						9/11/07		0.02						4/1/08		0.06		70		28		0.28		0.32		0.46		61		1192																				4/14/08		0.05		72		41

		11/6/07		0.025						9/12/07		0.03						4/2/08		0.06		70		30		0.28		0.32		0.44		63		1204																				4/15/08		0.05		74		42

		11/7/07		0.025						9/13/07		0.02						4/3/08		0.06		70		38		0.28		0.32		0.44		64		1192																				4/16/08		0.05		70		45

		11/8/07		0.085						9/14/07		0.035						4/4/08		0.05		70		44		0.26		0.32		0.44		63		1196																				4/17/08		0.045		72		46

		11/9/07		0.08						9/17/07		0.03						4/5/08		0.05		70		40		0.26		0.32		0.44		63		1196																				4/18/08		0.04		70		48

		11/12/07		0.075						9/18/07		0.03						4/7/08		0.055		70		44		0.26		0.32		0.46		65		1204																				4/19/08		0.05		69		48

		11/13/07		0.08						9/19/07		0.04						4/8/08		0.055		70		44		0.28		0.32		0.44		61		1192																				4/21/08		0.05		73		47

		11/14/07		0.075						9/20/07		0.04						4/9/08		0.055		70		46		0.28		0.32		0.44		63		1196																				4/22/08		0.045		77		46

		11/15/07		0.075						9/21/07		0.03						4/10/08		0.05		70		45		0.28		0.32		0.44		61		1204																				4/23/08		0.05		71		45

		11/16/07		0.07						9/24/07		0.025						4/11/08		0.05		70		42		0.28		0.32		0.44		61		1192																				4/24/08		0.045		73		46

		11/19/07		0.075						9/25/07		0.025						4/14/08		0.05		70		43		0.28		0.32		0.46		61		1196																				4/25/08		0.04		70		46

		11/20/07		0.07						9/26/07		0.03						4/15/08		0.05		73		41		0.28		0.32		0.44		62		1196																				4/30/08		0.06		69		26

		11/21/07		0.075						9/27/07		0.03						4/16/08		0.05		72		43		0.28		0.32		0.48		62		1196																				5/1/08		0.04		75		42

		11/26/07		0.08						9/28/07		0.03						4/17/08		0.05		72		44		0.28		0.32		0.48		62		1196																				5/2/08		0.04		72		35

		11/27/07		0.08						9/29/07		0.025						4/18/08		0.05		72		45		0.28		0.32		0.48		62		1196																				5/3/08		0.04		78		34

		11/28/07		0.08						10/1/07		0.03						4/19/08		0.06		72		44		0.28		0.32		0.48		62		1196																				5/5/08		0.04		71		40

		11/29/07		0.075						10/2/07		0.025						4/21/08		0.055		71		45		0.28		0.32		0.46		64		1196																				5/6/08		0.045		75		40

		11/30/07		0.08						10/3/07		0.03						4/22/08		0.05		72		43		0.28		0.32		0.46		64		1196																				5/7/08		0.05		72		36

		12/3/07		0.07						10/4/07		0.03						4/23/08		0.05		73		42		0.28		0.32		0.48		63		1196																				5/8/08		0.045		72		38

		12/4/07		0.08						10/5/07		0.02						4/24/08		0.055		73		45		0.28		0.32		0.46		63		1196																				5/9/08		0.04		74		34

		12/5/07		0.07						10/8/07		0.03						4/25/08		0.05		73		41		0.26		0.32		0.44		63		1204																				5/10/08		0.045		72		34

		12/6/07		0.08						10/9/07		0.02						4/28/08								0.26		0.32		0.44		63		1204																				5/12/08		0.055		69		28

		12/7/07		0.075						10/10/07		0.025						4/29/08								0.28		0.32		0.44		60		1184																				5/13/08		0.04		75		31

		12/10/07		0.075						10/11/07		0.03						4/30/08		0.06		70		25		0.28		0.32		0.46		60		1192																				5/14/08		0.05		71		38

		12/11/07		0.075						10/12/07		0.02						5/1/08		0.055		73		39		0.28		0.32		0.46		60		1196																				5/15/08		0.04		72		42

		12/12/07		0.075						10/15/07		0.025						5/2/08		0.045		72		34		0.28		0.32		0.46		60		1210																				5/16/08		0.04		71		48

		12/13/07		0.075						10/16/07		0.025						5/3/08		0.05		73		38		0.28		0.32		0.46		60		1210																				5/19/08		0.04		75		42

		12/14/07		0.075						10/17/07		0.03						5/5/08		0.04		72		38		0.28		0.32		0.44		60		1192																				5/20/08		0.04		73		44

		12/17/07		0.08						10/18/07		0.025						5/6/08		0.04		73		42		0.28		0.32		0.44		60		1184																				5/21/08		0.04		71		36

		12/18/07		0.075						10/19/07		0.025						5/7/08		0.04		73		37		0.28		0.32		0.44		62		1196																				5/22/08		0.04		73		30

		12/19/07		0.08						10/22/07		0.025						5/8/08		0.04		73		35		0.28		0.32		0.44		60		1196																				5/23/08		0.04		71		36

		12/20/07		0.08						10/23/07		0.02						5/9/08		0.04		72		34		0.3		0.32		0.46		62		1204																				5/27/08		0.02		73		37

		12/21/07		0.08						10/24/07		0.035						5/10/08		0.04		72		32		0.3		0.32		0.46		62		1204																				5/28/08		0.03		71		39

		12/26/07		0.08						10/25/07		0.025						5/12/08		0.055		68		28		0.26		0.32		0.42		60		1196																				5/29/08		0.03		74		39

		12/27/07		0.08						10/26/07		0.035						5/13/08		0.04		73		31		0.26		0.32		0.46		61		1192																				5/30/08		0.04		72		38

		12/28/07		0.075						10/29/07		0.025						5/14/08		0.045		73		25		0.3		0.32		0.46		60		1184																				5/31/08		0.025		72		39

		12/31/07		0.08						10/30/07		0.03						5/15/08		0.035		73		39		0.3		0.32		0.46		60		1196																				6/2/08		0.025		74		27

		1/2/08		0.09						10/31/07		0.03						5/16/08		0.035		73		45		0.3		0.32		0.44		60		1184																				6/3/08		0.02		71		34

		1/3/08		0.075						11/1/07		0.04						5/19/08		0.045		72		41		0.28		0.32		0.44		60		1204																				6/4/08		0.025		69		33

		1/4/08		0.09						11/2/07		0.03						5/20/08		0.045		73		42		0.28		0.32		0.44		62		1196																				6/5/08		0.025		71		39

		1/7/08		0.125						11/5/07		0.025						5/21/08		0.045		70		35		0.28		0.32		0.46		60		1196																				6/6/08		0.025		71		32

		1/8/08		0.08						11/6/07		0.03						5/22/08		0.045		72		30		0.28		0.32		0.42		61		1176																				6/9/08		0.03		72		43

		1/9/08		0.08						11/7/07		0.035						5/23/08		0.045		73		34		0.28		0.32		0.46		61		1172																				6/10/08		0.03		73		33

		1/10/08		0.08						11/8/07		0.05						5/27/08		0.035		73		36		0.28		0.32		0.44		61		1196																				6/11/08		0.025		70		33

		1/11/08		0.08						11/9/07		0.05						5/28/08		0.04		72		37		0.28		0.32		0.44		61		1204																				6/12/08		0.025		71		35

		1/14/08		0.09						11/12/07		0.03						5/29/08		0.04		73		37		0.26		0.32		0.44		61		1200																				6/13/08		0.025		75		32

		1/15/08		0.085						11/13/07		0.05						5/30/08		0.04		72		37		0.28		0.32		0.48		61		1196																				6/16/08		0.025		72		37

		1/16/08		0.09						11/14/07		0.05						6/2/08		0.04		71		30		0.28		0.28		0.44		60		1200																				6/17/08		0.03		72		26

		1/17/08		0.08						11/15/07		0.05						6/3/08		0.035		72		35		0.28		0.32		0.42		61		1196																				6/18/08		0.025		73		33

		1/18/08		0.09						11/16/07		0.05						6/4/08		0.035		70		33		0.28		0.32		0.44		61		1188																				6/19/08		0.025		71		29

		1/21/08		0.04						11/19/07		0.05						6/5/08		0.035		71		37		0.3		0.32		0.44		61		1192																				6/20/08		0.02		73		33

		1/22/08		0.11						11/20/07		0.05						6/6/08		0.035		71		31		0.28		0.32		0.44		61		1188																				6/21/08		0.025		74		27

		1/23/08		0.09						11/21/07		0.05						6/9/08		0.04		72		40		0.32		0.32		0.48		61		1188																				6/23/08		0.02		72		37

		1/24/08		0.09						11/26/07		0.05						6/10/08		0.04		72		31		0.3		0.32		0.44		55		1172																				6/24/08		0.025		73		35

		1/25/08		0.095						11/27/07		0.05						6/11/08		0.04		70		34		0.3		0.32		0.48		55		1196																				6/25/08		0.03		72		36

		1/28/08		0.09						11/28/07		0.05						6/12/08		0.04		72		31		0.3		0.32		0.48		55		1196																				6/26/08		0.03		74		35

		1/29/08		0.09						11/29/07		0.045						6/13/08		0.05		71		36		0.26		0.32		0.44		55		1208																				6/27/08		0.02		71		39

		1/30/08		0.1						11/30/07		0.05						6/16/08		0.05		73		34		0.3		0.32		0.46		55		1204																				6/30/08		0.02		73		38

		1/31/08		0.105						12/3/07		0.05						6/17/08		0.05		73		24		0.28		0.32		0.44		55		1216																				7/1/08		0.055		73		39

		2/1/08		0.09						12/4/07		0.05						6/18/08		0.05		73		31		0.3		0.32		0.44		55		1196																				7/2/08		0.055		73		38

		2/4/08		0.03						12/5/07		0.045						6/19/08		0.05		71		30		0.28		0.32		0.46		55		1196																				7/3/08		0.065		71		39

		2/5/08		0.04						12/6/07		0.05						6/20/08		0.05		73		28		0.28		0.32		0.46		55		1196																				7/7/08		0.055		75		38

		2/6/08		0.025						12/7/07		0.045						6/21/08		0.045		72		30		0.26		0.32		0.46		55		32																				7/8/08		0.05		72		40

		2/7/08		0.02						12/10/07		0.05						6/23/08		0.05		73		39		0.28		0.32		0.44		57		32																				7/9/08		0.06		73		39

		2/8/08		0.04						12/11/07		0.045						6/24/08		0.05		72		34		0.28		0.32		0.42		60		32																				7/10/08		0.06		74		39

		2/9/08		0.05						12/12/07		0.045						6/25/08		0.04		73		36		0.28		0.32		0.44		60		32																				7/11/08		0.06		71		40

		2/11/08		0.02						12/13/07		0.045						6/26/08		0.04		72		34		0.28		0.32		0.44		60		32																				7/12/08		0.06		73		42

		2/12/08		0.035						12/14/07		0.045						6/27/08		0.04		71		38		0.32		0.32		0.44		60		32																				7/14/08		0.06		72		41

		2/13/08		0.025						12/17/07		0.045						6/30/08		0.04		73		37		0.3		0.32		0.44		60		32																				7/15/08		0.06		71		41

		2/14/08		0.025						12/18/07		0.04						7/1/08		0.035		71		38		0.28		0.32		0.44		60		32																				7/16/08		0.065		72		40

		2/15/08		0.03						12/19/07		0.04						7/2/08		0.07		72		38		0.3		0.32		0.46		60		32																				7/17/08		0.05		71		41

		2/19/08		0.03						12/20/07		0.03						7/3/08		0.08		72		38		0.32		0.32		0.48		57		32																				7/18/08		0.065		72		40

		2/20/08		0.05						12/21/07		0.04						7/7/08		0.06		73		40		0.28		0.32		0.44		57		32																				7/19/08		0.06		72		39

		2/21/08		0.03						12/26/07		0.04						7/8/08		0.06		72		38		0.28		0.32		0.42		60		32																				7/21/08		0.06		71		40

		2/22/08		0.03						12/27/07		0.04						7/9/08		0.06		73		39		0.28		0.32		0.42																								7/22/08		0.05		74		36

		2/23/08		0.035						12/28/07		0.04						7/10/08		0.07		72		40		0.32		0.32		0.48		55		1104																				7/23/08		0.07		72		39

		2/24/08		0.035						12/31/07		0.04						7/11/08		0.065		71		39		0.3		0.32		0.48		55		1104																				7/24/08		0.05		72		37

		2/25/08		0.03						1/2/08		0.04						7/12/08		0.08		73		40																														7/25/08		0.06		71		38

		2/26/08		0.035						1/3/08		0.04						7/14/08		0.08		72		40		0.3		0.32		0.48		61		1200																				7/26/08		0.07		71		38

		2/27/08		0.03						1/4/08		0.04						7/15/08		0.09		71		40		0.28		0.32		0.42		61		1200																				7/28/08		0.06		70		41

		2/28/08		0.03						1/7/08		0.025						7/16/08		0.09		72		39		0.28		0.32		0.42		61		1200																				7/29/08		0.06		70		41

		2/29/08		0.03						1/8/08		0.03						7/17/08		0.08		72		39		0.28		0.32		0.44		61		1200																				7/30/08		0.06		71		39

		3/1/08		0.035						1/9/08		0.03						7/18/08		0.09		72		38		0.3		0.32		0.48		61		1200																				7/31/08		0.065		71		40

		3/3/08		0.03						1/10/08		0.03						7/19/08		0.09		73		37																														8/1/08		0.06		73		36

		3/4/08		0.035						1/11/08		0.03						7/21/08		0.09		72		38		0.28		0.32		0.4		61		1200																				8/2/08		0.06		71		40

		3/5/08		0.043						1/14/08		0.025						7/22/08		0.08		73		37		0.24		0.32		0.42		61		1200																				8/4/08		0.06		72		40

		3/6/08		0.043						1/15/08		0.03						7/23/08		0.09		71		38		0.28		0.32		0.44		61		1200																				8/5/08		0.06		73		39

		3/7/08		0.043						1/16/08		0.03						7/24/08		0.09		72		36		0.26		0.32		0.46		61		1200																				8/6/08		0.06		71		41

		3/10/08		0.043						1/17/08		0.03						7/25/08		0.09		72		36		0.24		0.32		0.42		61		1200																				8/7/08		0.06		72		39

		3/11/08		0.042						1/18/08		0.025						7/26/08		0.09		71		37		0.28		0.32		0.46		61		1200																				8/8/08		0.05		72		40

		3/12/08		0.039						1/21/08		0.035						7/28/08		0.09		71		38		0.3		0.32		0.46		61		1200																				8/9/08		0.055		71		40

		3/13/08		0.03						1/22/08		0.03						7/29/08		0.06		70		40		0.3		0.32		0.44																								8/11/08		0.06		71		39

		3/14/08		0.041						1/23/08		0.035						7/30/08		0.07		71		38		0.3		0.32		0.48																								8/12/08		0.065		71		41

		3/17/08		0.047						1/24/08		0.03						7/31/08		0.075		71		38																														8/13/08		0.055		71		41

		3/18/08		0.048						1/25/08		0.035						8/1/08		0.07		72		37		0.3		0.32		0.48																								8/14/08		0.05		71		41

		3/19/08		0.047						1/28/08		0.035						8/2/08		0.07		72		38																														8/15/08		0.05		72		39

		3/20/08		0.042						1/29/08		0.035						8/4/08		0.07		73		37		0.28		0.32		0.44																								8/16/08		0.06		72		40

		3/21/08		0.043						1/30/08		0.025						8/5/08		0.06		73		37		0.28		0.34		0.48																								8/18/08		0.06		72		41

		3/22/08		0.045						1/31/08		0.03						8/6/08		0.07		71		38		0.28		0.32		0.48																								8/19/08		0.06		72		41

		3/24/08		0.043						2/1/08		0.03						8/7/08		0.06		71		38		0.32		0.32		0.48																								8/20/08		0.06		71		40

		3/25/08		0.045						2/4/08		0.035						8/8/08		0.06		72		38		0.26		0.32		0.44																								8/21/08		0.05		73		44

		3/26/08		0.043						2/5/08		0.025						8/9/08		0.06		71		40																														8/22/08		0.05		72		40

		3/27/08		0.04						2/6/08		0.035						8/11/08		0.07		71		38		0.28		0.32		0.44																								8/23/08		0.05		72		41

		3/28/08		0.04						2/7/08		0.025						8/12/08		0.07		71		40		0.28		0.32		0.44																								8/25/08		0.06		71		40

		3/31/08		0.045						2/8/08		0.02						8/13/08		0.065		71		40		0.28		0.3		0.46																								8/26/08		0.06		70		39

		4/1/08		0.045						2/9/08		0.02						8/14/08		0.05		71		39		0.26		0.32		0.42																								8/27/08		0.05		71		40

		4/2/08		0.045						2/14/08		0.035						8/15/08		0.06		71		38		0.26		0.32		0.42																								8/28/08		0.055		71		40

		4/3/08		0.04						2/15/08		0.033						8/16/08		0.06		71		40																														8/29/08		0.055		72		39

		4/4/08		0.045						2/19/08		0.036						8/18/08		0.065		71		41		0.26		0.32		0.42																								9/2/08		0.055		69		32

		4/5/08		0.045						2/20/08		0.037						8/19/08		0.06		72		40		0.28		0.32		0.44																								9/3/08		0.055		72		39

		4/7/08		0.045						2/21/08		0.037						8/20/08		0.06		71		31		0.26		0.32		0.42																								9/4/08		0.055		70		38

		4/8/08		0.04						2/22/08		0.034						8/21/08		0.05		73		42		0.28		0.32		0.48																								9/5/08		0.06		71		36

		4/9/08		0.04						2/25/08		0.044						8/22/08		0.06		71		38		0.24		0.32		0.44																								9/6/08		0.06		71		39

		4/10/08		0.04						2/26/08		0.043						8/23/08		0.06		72		40																														9/8/08		0.06		74		38

		4/11/08		0.045						2/27/08		0.043						8/25/08		0.06		71		40		0.26		0.32		0.46																								9/9/08		0.06		72		40

		4/14/08		0.045						2/28/08		0.044						8/26/08		0.06		70		38		0.26		0.32		0.44																								9/10/08		0.06		72		40

		4/15/08		0.04						2/29/08		0.046						8/27/08		0.05		71		38		0.26		0.32		0.44																								9/11/08		0.06		71		41

		4/16/08		0.04						3/3/08		0.045						8/28/08		0.05		71		38		0.26		0.3		0.44																								9/12/08		0.06		70		40

		4/17/08		0.04						3/4/08		0.044						8/29/08		0.065		72		38		0.28		0.3		0.44																								9/13/08		0.06		70		41

		4/18/08		0.04						3/5/08		0.039						9/2/08		0.06		69		31		0.24		0.32		0.42																								9/15/08		0.06		70		40

		4/19/08		0.05						3/6/08		0.039						9/3/08		0.06		72		40		0.28		0.32		0.44																								9/16/08		0.06		71		40

		4/21/08		0.05						3/7/08		0.038						9/4/08		0.06		70		37		0.26		0.32		0.44																								9/17/08		0.06		70		30

		4/22/08		0.045						3/10/08		0.037						9/5/08		0.06		70		36		0.26		0.32		0.44																								9/18/08		0.06		71		37

		4/23/08		0.04						3/11/08		0.04						9/6/08		0.06		70		38																														9/19/08		0.06		72		43

		4/24/08		0.04						3/12/08		0.036						9/8/08		0.06		72		41		0.24		0.32		0.42																								9/20/08		0.06		72		42

		4/25/08		0.04						3/14/08		0.039						9/9/08		0.06		71		40		0.24		0.32		0.44																								9/22/08		0.06		71		39

		4/30/08		0.04						3/17/08		0.038						9/10/08		0.06		70		41		0.28		0.32		0.46																								9/23/08		0.065		72		37

		5/1/08		0.04						3/18/08		0.038						9/11/08		0.06		70		41		0.26		0.32		0.42																								9/24/08		0.055		70		33

		5/2/08		0.04						3/19/08		0.037						9/12/08		0.06		70		40		0.28		0.32		0.48																								9/25/08		0.06		72		32

		5/3/08		0.045						3/20/08		0.039						9/13/08		0.06		70		40																														9/26/08		0.06		72		43

		5/5/08		0.04						3/21/08		0.038						9/15/08		0.06		69		41		0.3		0.32		0.44																								9/27/08		0.06		70		37

		5/6/08		0.04						3/24/08		0.038						9/16/08		0.06		69		41		0.24		0.3		0.42																								9/29/08		0.06		71		40

		5/7/08		0.045						3/25/08		0.038						9/17/08		0.07		69		38		0.26		0.32		0.46																								9/30/08		0.06		75		33

		5/8/08		0.04						3/26/08		0.039						9/18/08		0.06		70		38		0.26		0.32		0.42

		5/9/08		0.04						3/27/08		0.045						9/19/08		0.06		73		42		0.26		0.32		0.42

		5/10/08		0.04						3/28/08		0.04						9/20/08		0.05		73		41

		5/12/08		0.04						3/31/08		0.04						9/22/08		0.06		71		38		0.24		0.32		0.44

		5/13/08		0.04						4/1/08		0.04						9/23/08		0.065		71		37		0.26		0.32		0.44

		5/14/08		0.04						4/2/08		0.04						9/24/08		0.055		71		32		0.26		0.32		0.42

		5/15/08		0.04						4/3/08		0.035						9/25/08		0.06		71		32		0.28		0.32		0.48

		5/16/08		0.04						4/4/08		0.04						9/26/08		0.055		73		41		0.24		0.32		0.44

		5/19/08		0.04						4/5/08		0.035						9/27/08		0.06		71		35

		5/20/08		0.04						4/7/08		0.04						9/29/08		0.06		70		40		0.26		0.32		0.44

		5/21/08		0.04						4/8/08		0.04						9/30/08		0.05		71		36		0.24		0.32		0.44

		5/22/08		0.04						4/9/08		0.035						10/1/08								0.24		0.32		0.44

		5/23/08		0.04						4/10/08		0.04						10/2/08								0.24		0.32		0.44

		5/27/08		0.04						4/11/08		0.04

		5/28/08		0.04						4/14/08		0.04

		5/29/08		0.05						4/15/08		0.04

		5/30/08		0.04						4/16/08		0.04

		5/31/08		0.045						4/17/08		0.04

		6/2/08		0.04						4/18/08		0.035

		6/3/08		0.04						4/19/08		0.05

		6/4/08		0.04						4/21/08		0.05

		6/5/08		0.04						4/22/08		0.04

		6/6/08		0.04						4/23/08		0.04

		6/9/08		0.04						4/24/08		0.04

		6/10/08		0.04						4/25/08		0.04

		6/11/08		0.04						4/30/08		0.04

		6/12/08		0.04						5/1/08		0.04

		6/13/08		0.04						5/2/08		0.04

		6/16/08		0.04						5/3/08		0.04

		6/17/08		0.04						5/5/08		0.04

		6/18/08		0.04						5/6/08		0.04

		6/19/08		0.04						5/7/08		0.04

		6/20/08		0.04						5/8/08		0.04

		6/21/08		0.035						5/9/08		0.04

		6/23/08		0.035						5/10/08		0.04

		6/24/08		0.04						5/12/08		0.04

		6/25/08		0.035						5/13/08		0.04

		6/26/08		0.035						5/14/08		0.04

		6/27/08		0.035						5/15/08		0.04

		6/30/08		0.035						5/16/08		0.04

		7/1/08		0.03						5/19/08		0.04

		7/2/08		0.03						5/20/08		0.04

		7/3/08		0.035						5/21/08		0.04

		7/7/08		0.03						5/22/08		0.04

		7/8/08		0.03						5/23/08		0.04

		7/9/08		0.035						5/27/08		0.04

		7/10/08		0.035						5/28/08		0.04

		7/11/08		0.035						5/29/08		0.04

		7/12/08		0.03						5/30/08		0.04

		7/14/08		0.025						6/2/08		0.04

		7/15/08		0.03						6/3/08		0.035

		7/16/08		0.03						6/4/08		0.035

		7/17/08		0.03						6/5/08		0.035

		7/18/08		0.04						6/6/08		0.035

		7/19/08		0.03						6/9/08		0.035

		7/21/08		0.03						6/10/08		0.035

		7/22/08		0.03						6/11/08		0.035

		7/23/08		0.02						6/12/08		0.035

		7/24/08		0.025						6/13/08		0.04

		7/25/08		0.01						6/16/08		0.035

		7/26/08		0.01						6/17/08		0.045

		7/28/08		0.01						6/18/08		0.045

		7/29/08		0.03						6/19/08		0.045

		7/30/08		0.01						6/20/08		0.035

		7/31/08		0.015						6/21/08		0.035

		8/1/08		0.025						6/23/08		0.035

		8/2/08		0.03						6/24/08		0.045

		8/4/08		0.03						6/25/08		0.035

		8/5/08		0.03						6/26/08		0.035

		8/6/08		0.04						6/27/08		0.035

		8/7/08		0.035						6/30/08		0.035

		8/8/08		0.03						7/1/08		0.04

		8/9/08		0.03						7/2/08		0.04

		8/11/08		0.035						7/3/08		0.04

		8/12/08		0.035						7/7/08		0.04

		8/13/08		0.035						7/8/08		0.04

		8/14/08		0.03						7/9/08		0.04

		8/15/08		0.03						7/10/08		0.04

		8/16/08		0.03						7/11/08		0.04

		8/18/08		0.03						7/12/08		0.04

		8/19/08		0.04						7/14/08		0.04

		8/20/08		0.03						7/15/08		0.04

		8/21/08		0.03						7/16/08		0.04

		8/22/08		0.03						7/17/08		0.04

		8/23/08		0.03						7/18/08		0.04

		8/25/08		0.03						7/19/08		0.04

		8/26/08		0.03						7/21/08		0.04

		8/27/08		0.03						7/22/08		0.04

		8/28/08		0.03						7/23/08		0.04

		8/29/08		0.03						7/24/08		0.04

		9/2/08		0.03						7/25/08		0.04

		9/3/08		0.03						7/26/08		0.04

		9/4/08		0.03						7/28/08		0.04

		9/5/08		0.03						7/29/08		0.04

		9/6/08		0.03						7/30/08		0.04

		9/8/08		0.03						7/31/08		0.04

		9/9/08		0.03						8/1/08		0.045

		9/10/08		0.03						8/2/08		0.04

		9/11/08		0.03						8/4/08		0.04

		9/12/08		0.03						8/5/08		0.04

		9/13/08		0.03						8/6/08		0.05

		9/15/08		0.035						8/7/08		0.04

		9/16/08		0.03						8/8/08		0.04

		9/17/08		0.03						8/9/08		0.04

		9/18/08		0.03						8/11/08		0.04

		9/19/08		0.03						8/12/08		0.04

		9/20/08		0.03						8/13/08		0.04

		9/22/08		0.03						8/14/08		0.04

		9/23/08		0.03						8/15/08		0.04

		9/24/08		0.025						8/16/08		0.04

		9/25/08		0.03						8/18/08		0.04

		9/26/08		0.03						8/19/08		0.04

		9/27/08		0.03						8/20/08		0.04

		9/29/08		0.03						8/21/08		0.04

		9/30/08		0.03						8/22/08		0.04

		10/1/08		0.03						8/23/08		0.04

		10/2/08		0.03						8/25/08		0.04

		10/3/08		0.03						8/26/08		0.04

		10/4/08		0.03						8/27/08		0.04

		10/6/08		0.03						8/28/08		0.04

		10/7/08		0.04						8/29/08		0.04

		10/8/08		0.03						9/2/08		0.04

		10/9/08		0.03						9/3/08		0.04

		10/10/08		0.03						9/4/08		0.04

		10/11/08		0.03						9/5/08		0.04

		10/13/08		0.03						9/6/08		0.04

		10/14/08		0.03						9/8/08		0.04

		10/15/08		0.03						9/9/08		0.04

		10/16/08		0.04						9/10/08		0.04

		10/17/08		0.03						9/11/08		0.04

		10/18/08		0.03						9/12/08		0.04

		10/20/08		0.03						9/13/08		0.04

		10/21/08		0.03						9/15/08		0.04

		10/22/08		0.03						9/16/08		0.04

		10/23/08		0.03						9/17/08		0.04

		10/24/08		0.03						9/18/08		0.04

		10/25/08		0.03						9/19/08		0.04

		10/27/08		0.03						9/20/08		0.04

		10/28/08		0.03						9/22/08		0.04

		10/29/08		0.03						9/23/08		0.045

		10/30/08		0.03						9/24/08		0.045

		10/31/08		0.03						9/25/08		0.045

		11/3/08		0.03						9/26/08		0.04

		11/4/08		0.03						9/27/08		0.04

										9/29/08		0.04

										9/30/08		0.04

										10/1/08		0.04

										10/2/08		0.04

										10/3/08		0.04

										10/4/08		0.04

										10/6/08		0.04

										10/7/08		0.05

										10/8/08		0.045

										10/9/08		0.04

										10/10/08		0.04

										10/11/08		0.04

										10/13/08		0.045

										10/14/08		0.04

										10/15/08		0.045

										10/16/08		0.04

										10/17/08		0.04

										10/18/08		0.04

										10/20/08		0.04

										10/21/08		0.04

										10/22/08		0.04

										10/23/08		0.04

										10/24/08		0.04

										10/25/08		0.04

										10/27/08		0.04

										10/28/08		0.04

										10/29/08		0.04

										10/30/08		0.04

										10/31/08		0.04

										11/3/08		0.04

										11/4/08		0.04

										11/5/08		0.05

										11/6/08		0.04

										11/7/08		0.04

										11/8/08		0.045

										11/10/08		0.04

										11/11/08		0.04

										11/12/08		0.04

										11/13/08		0.04

										11/14/08		0.04

										11/15/08		0.04

										11/17/08		0.04

										11/18/08		0.04

										11/19/08		0.04

										11/20/08		0.045

										11/21/08		0.045

										11/22/08		0.04

										11/24/08		0.04

										11/25/08		0.04

										11/26/08		0.04

										12/1/08		0.04





CER Pressure

		



Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)

R&D Bio-Safety Cabinet South (left axis)

Date

Diff. Pressure (Water Column In.)

Mfg Bio-Safety Cabinet South CFM

Figure 7.  CER2 Bio-Safety Cabinet Differential Pressure Daily Run Chart



Conf-Rel

		



Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

R&D Bio-Safety Cabinet South (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)

Date

Diff. Pressure (Water Column In.)

Mfg Bio-Safety Cabinet (cfm)

Figure 8.  Bio-Safety Cabinet Differential Pressure - Monthly Average



Temp-Humid

		



CER1

CER Change Room

CER2

CER3

CER Alert Level

CER Action Level

Date

Diff. Pressure (Water Column In.)

Figure 5.  CER Differential Pressure Daily Run Chart



Sheet1

		



CER1

CER Change Room

CER 2

CER 3

CER Alert Level

CER Action Level

Date

Diff. Pressure (Water Column In.)

Figure 6.  CER Differential Pressure - Monthly Average



		TO:		DCN 0273 File

		FROM:		Andy Pearson

		DATE:		3/3/07

		RE:		Confidence and Reliability Levels for CER Monitoring

		The table below shows 95/95, and 95/99 confidence/reliability levels for  CER and Change Room

		monitoring carried out from Feb 06 to Feb 07.

		Recommended action and alert levels correspond to worst case 95/95 (alert) and 95/99 (action) values.

						95/95 Limit		Recommended Alert Level		95/99 Limit		95/99 Limit		Recommended Action Level

		Airstrips (utl)		CER1		17		35		21		21		45

				CER2		15				20		20

				CER3		34				43		43

		Contact Plates (utl)		CER1		5		6		6		6		7

				CER2		4				5		5

				CER3		6				7		7

		0.5um Particle Counts (utl)		CER1		1092		3800		1324		1324		4500

				CER3		3797				4549		4549

				CER2		1232		1250		1495		1495		1500

		5.0um Particle Counts (utl)		CER1		159		410		200		200		500

				CER3		410				497		497

				CER2		91		90		107		107		105

		Pressure Differential (ltl)		CER1		0.011		0.030		0.003		0.003		0.005

				CER1/2 Chg Rm		0.021				0.013		0.013

				CER2		-0.021				-0.045		-0.045

				CER3		0.040				0.035		0.035

		Andy Pearson

		Sr.Quality Engineer





		CER2								CER1								CER3								QA

		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 2 Temperature(°F)		CER 2 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 1 Temperature(°F)		CER 1 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 3 Temperature(°F)		CER 3 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		QA Temperature(°F)		QA Humidity(%)

		29-Aug-07		16:07:10		75.81		46.5		29-Aug-07		16:06:20		76.4		48		29-Aug-07		16:07:53		75.81		74		9-Oct-07		16:25:59		78.2		33

		29-Aug-07		18:07:10		74.01		40.5		29-Aug-07		18:06:20		70.41		41.5		29-Aug-07		18:07:53		74.6		41.5		9-Oct-07		18:25:59		75.81		35.5

		29-Aug-07		20:07:10		74.6		40.5		29-Aug-07		20:06:20		71.6		43.5		29-Aug-07		20:07:53		73.4		43		9-Oct-07		20:25:59		75.2		34.5

		29-Aug-07		22:07:10		75.81		40.5		29-Aug-07		22:06:20		71.6		46.5		29-Aug-07		22:07:53		74.6		42		9-Oct-07		22:25:59		74.6		35

		30-Aug-07		0:07:10		75.81		40.5		30-Aug-07		0:06:20		71.6		47.5		30-Aug-07		0:07:53		75.2		41.5		10-Oct-07		0:25:59		73.4		36

		30-Aug-07		2:07:10		75.81		41		30-Aug-07		2:06:20		71		49		30-Aug-07		2:07:53		75.81		41.5		10-Oct-07		2:25:59		72.8		37

		30-Aug-07		4:07:10		75.2		42.5		30-Aug-07		4:06:20		71		51		30-Aug-07		4:07:53		75.2		41.5		10-Oct-07		4:25:59		72.21		38

		30-Aug-07		6:07:10		75.81		41		30-Aug-07		6:06:20		71.6		46.5		30-Aug-07		6:07:53		75.2		42		10-Oct-07		6:25:59		72.21		39

		30-Aug-07		8:07:10		75.81		45.5		30-Aug-07		8:06:20		72.21		55.5		30-Aug-07		8:07:53		75.2		44		10-Oct-07		8:25:59		71.6		41.5

		30-Aug-07		10:07:10		74.6		43.5		30-Aug-07		10:06:20		72.21		41.5		30-Aug-07		10:07:53		74.6		45		10-Oct-07		10:25:59		72.8		42.5

		30-Aug-07		12:07:10		74.6		43.5		30-Aug-07		12:06:20		71.6		46		30-Aug-07		12:07:53		72.8		45.5		10-Oct-07		12:25:59		74.01		42.5

		30-Aug-07		14:07:10		74.6		43		30-Aug-07		14:06:20		72.21		43		30-Aug-07		14:07:53		72.21		44.5		10-Oct-07		14:25:59		75.2		43

		30-Aug-07		16:07:10		75.2		43.5		30-Aug-07		16:06:20		72.21		43.5		30-Aug-07		16:07:53		72.8		44.5		10-Oct-07		16:25:59		75.2		42

		30-Aug-07		18:07:10		75.2		45		30-Aug-07		18:06:20		70.41		49.5		30-Aug-07		18:07:53		71.6		46		10-Oct-07		18:25:59		75.2		41

		30-Aug-07		20:07:10		75.2		45.5		30-Aug-07		20:06:20		71.6		52		30-Aug-07		20:07:53		75.81		45		10-Oct-07		20:25:59		74.01		42.5

		30-Aug-07		22:07:10		76.4		45		30-Aug-07		22:06:20		71		53.5		30-Aug-07		22:07:53		75.2		45		10-Oct-07		22:25:59		73.4		43.5

		31-Aug-07		0:07:10		76.4		44.5		31-Aug-07		0:06:20		71		53.5		31-Aug-07		0:07:53		75.2		44.5		11-Oct-07		0:25:59		72.8		44.5

		31-Aug-07		2:07:10		75.81		44.5		31-Aug-07		2:06:20		71.6		53		31-Aug-07		2:07:53		75.2		45.5		11-Oct-07		2:25:59		72.21		45

		31-Aug-07		4:07:10		75.81		45		31-Aug-07		4:06:20		71.6		53		31-Aug-07		4:07:53		72.8		41.5		11-Oct-07		4:25:59		71.6		45.5

		31-Aug-07		6:07:10		75.81		45.5		31-Aug-07		6:06:20		72.21		54		31-Aug-07		6:07:53		71		54.5		11-Oct-07		6:25:59		72.21		45

		31-Aug-07		8:07:10		75.2		44		31-Aug-07		8:06:20		72.21		43.5		31-Aug-07		8:07:53		71.6		50.5		11-Oct-07		8:25:59		71.6		46.5

		31-Aug-07		10:07:10		74.6		45.5		31-Aug-07		10:06:20		72.21		49.5		31-Aug-07		10:07:53		72.21		44.5		11-Oct-07		10:25:59		72.8		48.5

		31-Aug-07		12:07:10		74.6		49.5		31-Aug-07		12:06:20		71.6		60.5		31-Aug-07		12:07:53		72.21		45		11-Oct-07		12:25:59		74.6		44.5

		31-Aug-07		14:07:10		74.6		45.5		31-Aug-07		14:06:20		71.6		44		31-Aug-07		14:07:53		72.8		47		11-Oct-07		14:25:59		75.81		42.5

		31-Aug-07		16:07:10		74.6		48		31-Aug-07		16:06:20		71.6		56.5		31-Aug-07		16:07:53		72.8		43.5		11-Oct-07		16:25:59		76.4		42.5

		31-Aug-07		18:07:10		75.2		46.5		31-Aug-07		18:06:20		70.41		54.5		31-Aug-07		18:07:53		71		50		11-Oct-07		18:25:59		76.4		41

		31-Aug-07		20:07:10		75.2		46		31-Aug-07		20:06:20		71.6		53		31-Aug-07		20:07:53		74.6		50		11-Oct-07		20:25:59		74.6		41.5

		31-Aug-07		22:07:10		76.4		44		31-Aug-07		22:06:20		71.6		48.5		31-Aug-07		22:07:53		75.2		47		11-Oct-07		22:25:59		74.6		41

		1-Sep-07		0:07:10		76.4		42.5		1-Sep-07		0:06:20		71.6		46.5		1-Sep-07		0:07:53		75.2		45.5		12-Oct-07		0:25:59		73.4		41

		1-Sep-07		2:07:10		76.4		44		1-Sep-07		2:06:20		71.6		53		1-Sep-07		2:07:53		74.6		45.5		12-Oct-07		2:25:59		71.6		41

		1-Sep-07		4:07:10		76.4		44		1-Sep-07		4:06:20		71.6		53		1-Sep-07		4:07:53		72.8		50		12-Oct-07		4:25:59		71		41.5

		1-Sep-07		6:07:10		76.4		45		1-Sep-07		6:06:20		73.4		56.5		1-Sep-07		6:07:53		71.6		45		12-Oct-07		6:25:59		70.41		41.5

		1-Sep-07		8:07:10		75.2		42.5		1-Sep-07		8:06:20		72.21		41		1-Sep-07		8:07:53		71.6		53		12-Oct-07		8:25:59		69.8		41.5

		1-Sep-07		10:07:10		74.6		43.5		1-Sep-07		10:06:20		71.6		42		1-Sep-07		10:07:53		72.21		43.5		12-Oct-07		10:25:59		71.6		44.5

		1-Sep-07		12:07:10		74.6		51.5		1-Sep-07		12:06:20		70.41		64		1-Sep-07		12:07:53		71.6		45.5		12-Oct-07		12:25:59		74.6		43.5

		1-Sep-07		14:07:10		74.6		52		1-Sep-07		14:06:20		70.41		64.5		1-Sep-07		14:07:53		71		50.5		12-Oct-07		14:25:59		75.2		42.5

		1-Sep-07		16:07:10		74.6		46.5		1-Sep-07		16:06:20		70.41		52.5		1-Sep-07		16:07:53		71		57.5		12-Oct-07		16:25:59		75.2		42.5

		1-Sep-07		18:07:10		74.6		45.5		1-Sep-07		18:06:20		70.41		50.5		1-Sep-07		18:07:53		71		58.5		12-Oct-07		18:25:59		74.6		40

		1-Sep-07		20:07:10		74.6		49.5		1-Sep-07		20:06:20		71		56		1-Sep-07		20:07:53		71		55.5		12-Oct-07		20:25:59		74.01		40.5

		1-Sep-07		22:07:10		75.2		47		1-Sep-07		22:06:20		71		56		1-Sep-07		22:07:53		72.21		50.5		12-Oct-07		22:25:59		74.01		40

		2-Sep-07		0:07:10		75.2		45		2-Sep-07		0:06:20		71.6		52.5		2-Sep-07		0:07:53		72.21		50		13-Oct-07		0:25:59		72.8		40.5

		2-Sep-07		2:07:10		75.2		44.5		2-Sep-07		2:06:20		71		51		2-Sep-07		2:07:53		71.6		50		13-Oct-07		2:25:59		71.6		41

		2-Sep-07		4:07:10		74.6		44		2-Sep-07		4:06:20		70.41		51.5		2-Sep-07		4:07:53		70.41		49.5		13-Oct-07		4:25:59		71		42.5

		2-Sep-07		6:07:10		74.01		41.5		2-Sep-07		6:06:20		71		45.5		2-Sep-07		6:07:53		69.2		48.5		13-Oct-07		6:25:59		71.6		43

		2-Sep-07		8:07:10		73.4		44		2-Sep-07		8:06:20		69.8		51		2-Sep-07		8:07:53		69.2		51		13-Oct-07		8:25:59		71		46

		2-Sep-07		10:07:10		74.01		48.5		2-Sep-07		10:06:20		70.41		57.5		2-Sep-07		10:07:53		71		48.5		13-Oct-07		10:25:59		72.21		47.5

		2-Sep-07		12:07:10		74.6		49.5		2-Sep-07		12:06:20		70.41		59.5		2-Sep-07		12:07:53		71		53		13-Oct-07		12:25:59		72.8		47

		2-Sep-07		14:07:10		75.81		49.5		2-Sep-07		14:06:20		70.41		60.5		2-Sep-07		14:07:53		71		60		13-Oct-07		14:25:59		72.21		47.5

		2-Sep-07		16:07:10		76.4		43.5		2-Sep-07		16:06:20		70.41		47.5		2-Sep-07		16:07:53		71		46.5		13-Oct-07		16:25:59		74.01		47

		2-Sep-07		18:07:10		76.4		46.5		2-Sep-07		18:06:20		69.8		55.5		2-Sep-07		18:07:53		71		58		13-Oct-07		18:25:59		74.6		44.5

		2-Sep-07		20:07:10		77		44		2-Sep-07		20:06:20		71		52.5		2-Sep-07		20:07:53		74.01		47		13-Oct-07		20:25:59		72.8		45.5

		2-Sep-07		22:07:10		77		41.5		2-Sep-07		22:06:20		71.6		51		2-Sep-07		22:07:53		74.6		44.5		13-Oct-07		22:25:59		71.6		45

		3-Sep-07		0:07:10		76.4		41		3-Sep-07		0:06:20		71		50.5		3-Sep-07		0:07:53		74.01		44.5		14-Oct-07		0:25:59		71		45

		3-Sep-07		2:07:10		75.81		40		3-Sep-07		2:06:20		71		44		3-Sep-07		2:07:53		72.21		45.5		14-Oct-07		2:25:59		69.8		43.5

		3-Sep-07		4:07:10		75.2		39		3-Sep-07		4:06:20		71		41.5		3-Sep-07		4:07:53		71		46.5		14-Oct-07		4:25:59		69.2		43

		3-Sep-07		6:07:10		75.2		40		3-Sep-07		6:06:20		71.6		46		3-Sep-07		6:07:53		69.2		47.5		14-Oct-07		6:25:59		69.2		42.5

		3-Sep-07		8:07:10		74.01		42		3-Sep-07		8:06:20		69.8		49		3-Sep-07		8:07:53		68.61		49.5		14-Oct-07		8:25:59		69.2		41

		3-Sep-07		10:07:10		74.01		43		3-Sep-07		10:06:20		70.41		48		3-Sep-07		10:07:53		70.41		52		14-Oct-07		10:25:59		71		44

		3-Sep-07		12:07:10		74.6		41.5		3-Sep-07		12:06:20		70.41		43.5		3-Sep-07		12:07:53		71		43.5		14-Oct-07		12:25:59		72.21		45

		3-Sep-07		14:07:10		75.2		43		3-Sep-07		14:06:20		70.41		47		3-Sep-07		14:07:53		71.6		52		14-Oct-07		14:25:59		74.01		44.5

		3-Sep-07		16:07:10		75.81		44.5		3-Sep-07		16:06:20		69.8		49.5		3-Sep-07		16:07:53		71.6		52		14-Oct-07		16:25:59		75.2		44.5

		3-Sep-07		18:07:10		76.4		40.5		3-Sep-07		18:06:20		70.41		47		3-Sep-07		18:07:53		71		45		14-Oct-07		18:25:59		75.81		44

		3-Sep-07		20:07:10		77.61		40		3-Sep-07		20:06:20		71.6		45.5		3-Sep-07		20:07:53		75.81		42		14-Oct-07		20:25:59		74.6		44.5

		3-Sep-07		22:07:10		77		41		3-Sep-07		22:06:20		71.6		50.5		3-Sep-07		22:07:53		74.6		43.5		14-Oct-07		22:25:59		73.4		45

		4-Sep-07		0:07:10		76.4		40.5		4-Sep-07		0:06:20		71		50		4-Sep-07		0:07:53		74.6		43.5		15-Oct-07		0:25:59		72.8		45.5

		4-Sep-07		2:07:10		75.81		40		4-Sep-07		2:06:20		71		49.5		4-Sep-07		2:07:53		72.8		44		15-Oct-07		2:25:59		72.21		46

		4-Sep-07		4:07:10		75.81		39.5		4-Sep-07		4:06:20		71.6		47		4-Sep-07		4:07:53		71.6		45		15-Oct-07		4:25:59		71.6		46

		4-Sep-07		6:07:10		74.6		40		4-Sep-07		6:06:20		71		47.5		4-Sep-07		6:07:53		69.8		46.5		15-Oct-07		6:25:59		71		46.5

		4-Sep-07		8:07:10		74.01		39.5		4-Sep-07		8:06:20		70.41		42		4-Sep-07		8:07:53		69.8		48.5		15-Oct-07		8:25:59		70.41		47

		4-Sep-07		10:07:10		74.01		45.5		4-Sep-07		10:06:20		69.8		53.5		4-Sep-07		10:07:53		71		52		15-Oct-07		10:25:59		69.8		47.5

		4-Sep-07		12:07:10		74.01		48		4-Sep-07		12:06:20		69.8		55		4-Sep-07		12:07:53		71		45.5		15-Oct-07		12:25:59		70.41		48.5

		4-Sep-07		14:07:10		74.01		49		4-Sep-07		14:06:20		70.41		52		4-Sep-07		14:07:53		71		58.5		15-Oct-07		14:25:59		71.6		49

		4-Sep-07		16:07:10		74.6		47.5		4-Sep-07		16:06:20		70.41		50		4-Sep-07		16:07:53		71		49		15-Oct-07		16:25:59		73.4		48

		4-Sep-07		18:07:10		74.6		47.5		4-Sep-07		18:06:20		70.41		50		4-Sep-07		18:07:53		71		49.5		15-Oct-07		18:25:59		74.6		45.5

		4-Sep-07		20:07:10		75.2		50		4-Sep-07		20:06:20		71		58.5		4-Sep-07		20:07:53		71.6		55.5		15-Oct-07		20:25:59		72.8		46

		4-Sep-07		22:07:10		75.81		47.5		4-Sep-07		22:06:20		71.6		56		4-Sep-07		22:07:53		74.01		50		15-Oct-07		22:25:59		71.6		46

		5-Sep-07		0:07:10		75.81		46.5		5-Sep-07		0:06:20		71		56.5		5-Sep-07		0:07:53		74.01		49.5		16-Oct-07		0:25:59		71		46

		5-Sep-07		2:07:10		75.81		44.5		5-Sep-07		2:06:20		71		47.5		5-Sep-07		2:07:53		72.8		50.5		16-Oct-07		2:25:59		70.41		46.5

		5-Sep-07		4:07:10		75.2		45.5		5-Sep-07		4:06:20		71		55		5-Sep-07		4:07:53		71.6		49		16-Oct-07		4:25:59		69.8		46

		5-Sep-07		6:07:10		75.2		47		5-Sep-07		6:06:20		71.6		55		5-Sep-07		6:07:53		70.41		48		16-Oct-07		6:25:59		70.41		46.5

		5-Sep-07		8:07:10		75.2		45		5-Sep-07		8:06:20		72.21		45.5		5-Sep-07		8:07:53		71		53		16-Oct-07		8:25:59		69.8		47.5

		5-Sep-07		10:07:10		74.6		51.5		5-Sep-07		10:06:20		72.21		55		5-Sep-07		10:07:53		72.8		46.5		16-Oct-07		10:25:59		71		49.5

		5-Sep-07		12:07:10		74.01		50.5		5-Sep-07		12:06:20		71		56		5-Sep-07		12:07:53		72.21		57.5		16-Oct-07		12:25:59		72.21		52

		5-Sep-07		14:07:10		74.01		48		5-Sep-07		14:06:20		71.6		54.5		5-Sep-07		14:07:53		72.21		54		16-Oct-07		14:25:59		73.4		52.5

		5-Sep-07		16:07:10		74.01		49		5-Sep-07		16:06:20		71		54		5-Sep-07		16:07:53		72.21		51		16-Oct-07		16:25:59		75.2		47.5

		5-Sep-07		18:07:10		74.6		49		5-Sep-07		18:06:20		70.41		60		5-Sep-07		18:07:53		71.6		48.5		16-Oct-07		18:25:59		75.81		47.5

		5-Sep-07		20:07:10		74.6		48		5-Sep-07		20:06:20		71.6		55		5-Sep-07		20:07:53		71		58		16-Oct-07		20:25:59		74.01		48.5

		5-Sep-07		22:07:10		75.81		46.5		5-Sep-07		22:06:20		71		55.5		5-Sep-07		22:07:53		75.2		47		16-Oct-07		22:25:59		73.4		49

		6-Sep-07		0:07:10		75.81		43.5		6-Sep-07		0:06:20		71.6		50.5		6-Sep-07		0:07:53		74.6		47		17-Oct-07		0:25:59		72.21		49

		6-Sep-07		2:07:10		75.2		44.5		6-Sep-07		2:06:20		71		52.5		6-Sep-07		2:07:53		73.4		47		17-Oct-07		2:25:59		71		48

		6-Sep-07		4:07:10		75.2		43.5		6-Sep-07		4:06:20		71.6		51		6-Sep-07		4:07:53		72.21		48.5		17-Oct-07		4:25:59		70.41		47.5

		6-Sep-07		6:07:10		75.2		42.5		6-Sep-07		6:06:20		71.6		48.5		6-Sep-07		6:07:53		71		50.5		17-Oct-07		6:25:59		69.8		46

		6-Sep-07		8:07:10		75.2		45.5		6-Sep-07		8:06:20		72.21		52		6-Sep-07		8:07:53		71.6		48.5		17-Oct-07		8:25:59		69.2		46.5

		6-Sep-07		10:07:10		75.2		43.5		6-Sep-07		10:06:20		72.21		46		6-Sep-07		10:07:53		72.21		49.5		17-Oct-07		10:25:59		70.41		49

		6-Sep-07		12:07:10		74.6		41.5		6-Sep-07		12:06:20		71.6		42.5		6-Sep-07		12:07:53		72.21		52		17-Oct-07		12:25:59		71.6		51.5

		6-Sep-07		14:07:10		74.01		40		6-Sep-07		14:06:20		71.6		40.5		6-Sep-07		14:07:53		72.21		42		17-Oct-07		14:25:59		72.21		53

		6-Sep-07		16:07:10		74.6		40		6-Sep-07		16:06:20		71.6		43		6-Sep-07		16:07:53		72.21		40		17-Oct-07		16:25:59		72.8		54

		6-Sep-07		18:07:10		74.6		38		6-Sep-07		18:06:20		69.8		42		6-Sep-07		18:07:53		72.21		37.5		17-Oct-07		18:25:59		74.01		50.5

		6-Sep-07		20:07:10		75.2		38		6-Sep-07		20:06:20		71.6		43		6-Sep-07		20:07:53		75.2		39.5		17-Oct-07		20:25:59		72.21		48.5

		6-Sep-07		22:07:10		75.81		38.5		6-Sep-07		22:06:20		71.6		45.5		6-Sep-07		22:07:53		75.2		39.5		17-Oct-07		22:25:59		71		48

		7-Sep-07		0:07:10		75.81		39		7-Sep-07		0:06:20		71.6		46.5		7-Sep-07		0:07:53		75.2		39.5		18-Oct-07		0:25:59		70.41		47

		7-Sep-07		2:07:10		75.81		39		7-Sep-07		2:06:20		71.6		46		7-Sep-07		2:07:53		74.01		41		18-Oct-07		2:25:59		69.2		45.5

		7-Sep-07		4:07:10		75.2		39		7-Sep-07		4:06:20		71		46		7-Sep-07		4:07:53		72.21		37		18-Oct-07		4:25:59		68.61		45

		7-Sep-07		6:07:10		75.81		38		7-Sep-07		6:06:20		71.6		44		7-Sep-07		6:07:53		71		45.5		18-Oct-07		6:25:59		69.2		46

		7-Sep-07		8:07:10		75.81		41		7-Sep-07		8:06:20		71.6		50		7-Sep-07		8:07:53		71.6		39.5		18-Oct-07		8:25:59		69.2		47

		7-Sep-07		10:07:10		75.2		38.5		7-Sep-07		10:06:20		71.6		40.5		7-Sep-07		10:07:53		72.21		40		18-Oct-07		10:25:59		70.41		50

		7-Sep-07		12:07:10		74.6		40		7-Sep-07		12:06:20		71		42.5		7-Sep-07		12:07:53		72.21		51.5		18-Oct-07		12:25:59		72.8		48.5

		7-Sep-07		14:07:10		74.6		43		7-Sep-07		14:06:20		71.6		42		7-Sep-07		14:07:53		71.6		42.5		18-Oct-07		14:25:59		74.6		45

		7-Sep-07		16:07:10		75.81		46		7-Sep-07		16:06:20		71		61		7-Sep-07		16:07:53		71.6		44.5		18-Oct-07		16:25:59		75.81		43

		7-Sep-07		18:07:10		75.2		45.5		7-Sep-07		18:06:20		71		48		7-Sep-07		18:07:53		71		53.5		18-Oct-07		18:25:59		75.81		43

		7-Sep-07		20:07:10		75.81		49		7-Sep-07		20:06:20		71.6		57		7-Sep-07		20:07:53		71.6		55		18-Oct-07		20:25:59		74.6		43.5

		7-Sep-07		22:07:10		75.81		48.5		7-Sep-07		22:06:20		71.6		58		7-Sep-07		22:07:53		72.8		52		18-Oct-07		22:25:59		73.4		44

		8-Sep-07		0:07:10		75.2		47.5		8-Sep-07		0:06:20		71		56.5		8-Sep-07		0:07:53		72.8		51		19-Oct-07		0:25:59		72.21		44.5

		8-Sep-07		2:07:10		75.2		47		8-Sep-07		2:06:20		71.6		55		8-Sep-07		2:07:53		72.21		51.5		19-Oct-07		2:25:59		71		44.5

		8-Sep-07		4:07:10		75.2		47		8-Sep-07		4:06:20		71		55.5		8-Sep-07		4:07:53		71.6		51		19-Oct-07		4:25:59		70.41		45

		8-Sep-07		6:07:10		75.81		47		8-Sep-07		6:06:20		71.6		54.5		8-Sep-07		6:07:53		71		55		19-Oct-07		6:25:59		70.41		45.5

		8-Sep-07		8:07:10		75.2		47.5		8-Sep-07		8:06:20		72.21		56		8-Sep-07		8:07:53		71.6		57		19-Oct-07		8:25:59		70.41		46.5

		8-Sep-07		10:07:10		74.6		44.5		8-Sep-07		10:06:20		72.21		45		8-Sep-07		10:07:53		72.21		46.5		19-Oct-07		10:25:59		71.6		47.5

		8-Sep-07		12:07:10		74.6		50.5		8-Sep-07		12:06:20		71		57		8-Sep-07		12:07:53		72.21		45		19-Oct-07		12:25:59		73.4		46

		8-Sep-07		14:07:10		74.01		46		8-Sep-07		14:06:20		72.21		46		8-Sep-07		14:07:53		71.6		46.5		19-Oct-07		14:25:59		75.2		45.5

		8-Sep-07		16:07:10		74.01		53		8-Sep-07		16:06:20		71		67		8-Sep-07		16:07:53		71.6		50.5		19-Oct-07		16:25:59		74.6		49

		8-Sep-07		18:07:10		74.01		53		8-Sep-07		18:06:20		70.41		63		8-Sep-07		18:07:53		71		53.5		19-Oct-07		18:25:59		74.6		50.5

		8-Sep-07		20:07:10		74.6		51		8-Sep-07		20:06:20		71		58		8-Sep-07		20:07:53		70.41		57		19-Oct-07		20:25:59		74.01		51.5

		8-Sep-07		22:07:10		74.6		48		8-Sep-07		22:06:20		71		55		8-Sep-07		22:07:53		70.41		54		19-Oct-07		22:25:59		74.01		51

		9-Sep-07		0:07:10		74.6		45		9-Sep-07		0:06:20		71		46		9-Sep-07		0:07:53		69.8		53		20-Oct-07		0:25:59		73.4		51.5

		9-Sep-07		2:07:10		74.01		45.5		9-Sep-07		2:06:20		71		52.5		9-Sep-07		2:07:53		69.2		52.5		20-Oct-07		2:25:59		72.8		52.5

		9-Sep-07		4:07:10		74.01		46.5		9-Sep-07		4:06:20		71		53.5		9-Sep-07		4:07:53		69.2		55		20-Oct-07		4:25:59		72.8		53

		9-Sep-07		6:07:10		74.01		48.5		9-Sep-07		6:06:20		71.6		56		9-Sep-07		6:07:53		68.61		56		20-Oct-07		6:25:59		72.8		54

		9-Sep-07		8:07:10		74.01		46		9-Sep-07		8:06:20		71		50		9-Sep-07		8:07:53		68.61		57		20-Oct-07		8:25:59		72.8		56.5

		9-Sep-07		10:07:10		73.4		50.5		9-Sep-07		10:06:20		70.41		57.5		9-Sep-07		10:07:53		68.61		58		20-Oct-07		10:25:59		74.01		57.5

		9-Sep-07		12:07:10		73.4		51.5		9-Sep-07		12:06:20		70.41		56.5		9-Sep-07		12:07:53		69.8		57.5		20-Oct-07		12:25:59		75.2		57.5

		9-Sep-07		14:07:10		73.4		55		9-Sep-07		14:06:20		70.41		63.5		9-Sep-07		14:07:53		70.41		54.5		20-Oct-07		14:25:59		75.81		57

		9-Sep-07		16:07:10		74.6		54		9-Sep-07		16:06:20		70.41		64.5		9-Sep-07		16:07:53		71		51		20-Oct-07		16:25:59		75.81		57

		9-Sep-07		18:07:10		75.2		50		9-Sep-07		18:06:20		70.41		55		9-Sep-07		18:07:53		70.41		60		20-Oct-07		18:25:59		75.81		56

		9-Sep-07		20:07:10		75.2		44.5		9-Sep-07		20:06:20		71.6		47		9-Sep-07		20:07:53		70.41		55		20-Oct-07		20:25:59		74.01		54.5

		9-Sep-07		22:07:10		74.6		47		9-Sep-07		22:06:20		71		54.5		9-Sep-07		22:07:53		69.8		54		20-Oct-07		22:25:59		72.8		53

		10-Sep-07		0:07:10		74.6		46		10-Sep-07		0:06:20		71		52.5		10-Sep-07		0:07:53		69.2		53.5		21-Oct-07		0:25:59		71.6		51

		10-Sep-07		2:07:10		74.6		45.5		10-Sep-07		2:06:20		71.6		51		10-Sep-07		2:07:53		68.61		53.5		21-Oct-07		2:25:59		71		50

		10-Sep-07		4:07:10		74.01		45		10-Sep-07		4:06:20		71.6		50		10-Sep-07		4:07:53		68.61		54		21-Oct-07		4:25:59		70.41		49.5

		10-Sep-07		6:07:10		74.01		45		10-Sep-07		6:06:20		71		51		10-Sep-07		6:07:53		68		54.5		21-Oct-07		6:25:59		69.8		47.5

		10-Sep-07		8:07:10		72.8		44.5		10-Sep-07		8:06:20		69.8		50.5		10-Sep-07		8:07:53		67.4		54.5		21-Oct-07		8:25:59		69.2		45.5

		10-Sep-07		10:07:10		72.8		45.5		10-Sep-07		10:06:20		69.8		46.5		10-Sep-07		10:07:53		67.4		55		21-Oct-07		10:25:59		69.2		48

		10-Sep-07		12:07:10		72.8		46		10-Sep-07		12:06:20		70.41		49.5		10-Sep-07		12:07:53		68.61		56		21-Oct-07		12:25:59		70.41		45.5

		10-Sep-07		14:07:10		73.4		49		10-Sep-07		14:06:20		70.41		56.5		10-Sep-07		14:07:53		69.8		59.5		21-Oct-07		14:25:59		71		42

		10-Sep-07		16:07:10		74.01		53.5		10-Sep-07		16:06:20		70.41		62.5		10-Sep-07		16:07:53		70.41		49		21-Oct-07		16:25:59		72.21		39

		10-Sep-07		18:07:10		74.6		52.5		10-Sep-07		18:06:20		70.41		63		10-Sep-07		18:07:53		71		56		21-Oct-07		18:25:59		73.4		36.5

		10-Sep-07		20:07:10		75.2		49		10-Sep-07		20:06:20		71.6		55.5		10-Sep-07		20:07:53		71.6		54.5		21-Oct-07		20:25:59		72.21		38

		10-Sep-07		22:07:10		74.6		48		10-Sep-07		22:06:20		71		56		10-Sep-07		22:07:53		70.41		54		21-Oct-07		22:25:59		71		40

		11-Sep-07		0:07:10		74.6		47		11-Sep-07		0:06:20		71		54.5		11-Sep-07		0:07:53		69.8		53.5		22-Oct-07		0:25:59		69.8		39.5

		11-Sep-07		2:07:10		74.01		45.5		11-Sep-07		2:06:20		71		52		11-Sep-07		2:07:53		68.61		53.5		22-Oct-07		2:25:59		69.2		39.5

		11-Sep-07		4:07:10		74.01		44.5		11-Sep-07		4:06:20		71.6		48.5		11-Sep-07		4:07:53		68		53.5		22-Oct-07		4:25:59		69.2		39

		11-Sep-07		6:07:10		74.01		43		11-Sep-07		6:06:20		71		48		11-Sep-07		6:07:53		68.61		52		22-Oct-07		6:25:59		68.61		38.5

		11-Sep-07		8:07:10		74.01		43.5		11-Sep-07		8:06:20		70.41		45		11-Sep-07		8:07:53		71.6		51.5		22-Oct-07		8:25:59		68		37.5

		11-Sep-07		10:07:10		74.6		46.5		11-Sep-07		10:06:20		71		45.5		11-Sep-07		10:07:53		71.6		48		22-Oct-07		10:25:59		68		37.5

		11-Sep-07		12:07:10		74.01		52.5		11-Sep-07		12:06:20		71		63		11-Sep-07		12:07:53		72.21		46		22-Oct-07		12:25:59		69.2		36

		11-Sep-07		14:07:10		74.6		46.5		11-Sep-07		14:06:20		71.6		45		11-Sep-07		14:07:53		71.6		45		22-Oct-07		14:25:59		72.21		33

		11-Sep-07		16:07:10		75.2		48.5		11-Sep-07		16:06:20		70.41		52		11-Sep-07		16:07:53		71		63		22-Oct-07		16:25:59		72.8		33

		11-Sep-07		18:07:10		74.6		49.5		11-Sep-07		18:06:20		70.41		54		11-Sep-07		18:07:53		71		60.5		22-Oct-07		18:25:59		72.8		32.5

		11-Sep-07		20:07:10		75.2		50.5		11-Sep-07		20:06:20		71		58.5		11-Sep-07		20:07:53		70.41		57.5		22-Oct-07		20:25:59		72.8		31.5

		11-Sep-07		22:07:10		75.2		45.5		11-Sep-07		22:06:20		71.6		51.5		11-Sep-07		22:07:53		72.21		52		22-Oct-07		22:25:59		72.21		35

		12-Sep-07		0:07:10		74.6		46.5		12-Sep-07		0:06:20		71.6		53		12-Sep-07		0:07:53		71.6		51		23-Oct-07		0:25:59		71.6		36

		12-Sep-07		2:07:10		74.6		45.5		12-Sep-07		2:06:20		71.6		51.5		12-Sep-07		2:07:53		71		51		23-Oct-07		2:25:59		70.41		37

		12-Sep-07		4:07:10		74.01		46.5		12-Sep-07		4:06:20		70.41		53.5		12-Sep-07		4:07:53		70.41		52		23-Oct-07		4:25:59		69.8		36.5

		12-Sep-07		6:07:10		74.6		46.5		12-Sep-07		6:06:20		71		53		12-Sep-07		6:07:53		70.41		50		23-Oct-07		6:25:59		69.8		36.5

		12-Sep-07		8:07:10		74.01		45.5		12-Sep-07		8:06:20		71.6		44.5		12-Sep-07		8:07:53		71		48.5		23-Oct-07		8:25:59		68.61		37.5

		12-Sep-07		10:07:10		74.01		47.5		12-Sep-07		10:06:20		72.21		55		12-Sep-07		10:07:53		71.6		56		23-Oct-07		10:25:59		71.6		39

		12-Sep-07		12:07:10		74.6		47		12-Sep-07		12:06:20		71.6		53		12-Sep-07		12:07:53		72.21		52		23-Oct-07		12:25:59		74.6		37.5

		12-Sep-07		14:07:10		74.01		46		12-Sep-07		14:06:20		71.6		43		12-Sep-07		14:07:53		71.6		54		23-Oct-07		14:25:59		75.2		37

		12-Sep-07		16:07:10		74.6		49		12-Sep-07		16:06:20		71		53		12-Sep-07		16:07:53		71.6		46.5		23-Oct-07		16:25:59		75.81		36.5

		12-Sep-07		18:07:10		74.6		53		12-Sep-07		18:06:20		70.41		65		12-Sep-07		18:07:53		71		62.5		23-Oct-07		18:25:59		75.81		35.5

		12-Sep-07		20:07:10		74.6		52		12-Sep-07		20:06:20		71		60.5		12-Sep-07		20:07:53		71		54.5		23-Oct-07		20:25:59		74.6		36

		12-Sep-07		22:07:10		74.6		49		12-Sep-07		22:06:20		71.6		56.5		12-Sep-07		22:07:53		72.8		52.5		23-Oct-07		22:25:59		74.01		37.5

		13-Sep-07		0:07:10		75.2		49		13-Sep-07		0:06:20		71.6		56.5		13-Sep-07		0:07:53		72.8		53		24-Oct-07		0:25:59		73.4		38.5

		13-Sep-07		2:07:10		75.2		48.5		13-Sep-07		2:06:20		71		57		13-Sep-07		2:07:53		72.21		53		24-Oct-07		2:25:59		72.21		39

		13-Sep-07		4:07:10		74.6		48.5		13-Sep-07		4:06:20		70.41		58.5		13-Sep-07		4:07:53		71.6		56		24-Oct-07		4:25:59		71		39.5

		13-Sep-07		6:07:10		75.2		49		13-Sep-07		6:06:20		71		58		13-Sep-07		6:07:53		70.41		50.5		24-Oct-07		6:25:59		71		39

		13-Sep-07		8:07:10		74.6		50		13-Sep-07		8:06:20		71		52.5		13-Sep-07		8:07:53		71		56		24-Oct-07		8:25:59		69.8		39.5

		13-Sep-07		10:07:10		74.01		45.5		13-Sep-07		10:06:20		71.6		44.5		13-Sep-07		10:07:53		71.6		57		24-Oct-07		10:25:59		72.21		42.5

		13-Sep-07		12:07:10		74.6		48		13-Sep-07		12:06:20		71.6		52.5		13-Sep-07		12:07:53		71.6		48		24-Oct-07		12:25:59		75.2		41

		13-Sep-07		14:07:10		74.6		45.5		13-Sep-07		14:06:20		71.6		44		13-Sep-07		14:07:53		70.41		61.5		24-Oct-07		14:25:59		75.81		40.5

		13-Sep-07		16:07:10		74.6		52.5		13-Sep-07		16:06:20		70.41		58		13-Sep-07		16:07:53		71		61.5		24-Oct-07		16:25:59		76.4		40.5

		13-Sep-07		18:07:10		75.2		47		13-Sep-07		18:06:20		70.41		51		13-Sep-07		18:07:53		70.41		59.5		24-Oct-07		18:25:59		75.81		42.5

		13-Sep-07		20:07:10		75.2		48		13-Sep-07		20:06:20		71.6		55.5		13-Sep-07		20:07:53		71.6		55		24-Oct-07		20:25:59		75.2		45

		13-Sep-07		22:07:10		74.6		47.5		13-Sep-07		22:06:20		71		54.5		13-Sep-07		22:07:53		71.6		52.5		24-Oct-07		22:25:59		75.81		44.5

		14-Sep-07		0:07:10		74.6		46.5		14-Sep-07		0:06:20		71.6		53		14-Sep-07		0:07:53		71.6		51.5		25-Oct-07		0:25:59		74.6		43

		14-Sep-07		2:07:10		74.6		46.5		14-Sep-07		2:06:20		71		51.5		14-Sep-07		2:07:53		71.6		51.5		25-Oct-07		2:25:59		73.4		43

		14-Sep-07		4:07:10		74.6		44.5		14-Sep-07		4:06:20		71.6		50		14-Sep-07		4:07:53		71		45		25-Oct-07		4:25:59		72.21		43

		14-Sep-07		6:07:10		74.6		43.5		14-Sep-07		6:06:20		71		49.5		14-Sep-07		6:07:53		71		51		25-Oct-07		6:25:59		71.6		43

		14-Sep-07		8:07:10		74.01		46		14-Sep-07		8:06:20		71.6		54		14-Sep-07		8:07:53		71		53		25-Oct-07		8:25:59		71		42.5

		14-Sep-07		10:07:10		74.6		46.5		14-Sep-07		10:06:20		71.6		55.5		14-Sep-07		10:07:53		72.21		47.5		25-Oct-07		10:25:59		73.4		44

		14-Sep-07		12:07:10		74.01		47.5		14-Sep-07		12:06:20		70.41		53		14-Sep-07		12:07:53		72.21		43		25-Oct-07		12:25:59		75.2		44

		14-Sep-07		14:07:10		74.6		49		14-Sep-07		14:06:20		71.6		56		14-Sep-07		14:07:53		71.6		48		25-Oct-07		14:25:59		75.81		43

		14-Sep-07		16:07:10		75.2		46.5		14-Sep-07		16:06:20		71		53		14-Sep-07		16:07:53		71.6		58.5		25-Oct-07		16:25:59		75.81		41

		14-Sep-07		18:07:10		75.2		50.5		14-Sep-07		18:06:20		71		64.5		14-Sep-07		18:07:53		71		62		25-Oct-07		18:25:59		75.81		44.5

		14-Sep-07		20:07:10		75.2		50		14-Sep-07		20:06:20		71.6		59		14-Sep-07		20:07:53		72.8		55.5		25-Oct-07		20:25:59		75.2		43.5

		14-Sep-07		22:07:10		75.2		50.5		14-Sep-07		22:06:20		71.6		59.5		14-Sep-07		22:07:53		74.01		52.5		25-Oct-07		22:25:59		74.6		42.5

		15-Sep-07		0:07:10		75.2		48.5		15-Sep-07		0:06:20		71		51.5		15-Sep-07		0:07:53		73.4		52		26-Oct-07		0:25:59		73.4		42.5

		15-Sep-07		2:07:10		74.6		48		15-Sep-07		2:06:20		71.6		56		15-Sep-07		2:07:53		73.4		52		26-Oct-07		2:25:59		72.21		43

		15-Sep-07		4:07:10		74.6		48.5		15-Sep-07		4:06:20		71.6		55.5		15-Sep-07		4:07:53		72.21		54.5		26-Oct-07		4:25:59		71		42.5

		15-Sep-07		6:07:10		75.2		49.5		15-Sep-07		6:06:20		71.6		58.5		15-Sep-07		6:07:53		71		51		26-Oct-07		6:25:59		70.41		41.5

		15-Sep-07		8:07:10		75.2		46		15-Sep-07		8:06:20		72.21		49		15-Sep-07		8:07:53		71.6		56		26-Oct-07		8:25:59		69.2		41

		15-Sep-07		10:07:10		74.6		50		15-Sep-07		10:06:20		71.6		57.5		15-Sep-07		10:07:53		71.6		50		26-Oct-07		10:25:59		71		44.5

		15-Sep-07		12:07:10		74.01		51		15-Sep-07		12:06:20		71		51		15-Sep-07		12:07:53		72.21		49.5		26-Oct-07		12:25:59		74.6		43.5

		15-Sep-07		14:07:10		74.6		46.5		15-Sep-07		14:06:20		71.6		47.5		15-Sep-07		14:07:53		71.6		54		26-Oct-07		14:25:59		75.81		43.5

		15-Sep-07		16:07:10		74.6		45.5		15-Sep-07		16:06:20		69.2		50.5		15-Sep-07		16:07:53		71.6		53		26-Oct-07		16:25:59		76.4		43.5

		15-Sep-07		18:07:10		73.4		46		15-Sep-07		18:06:20		68		50		15-Sep-07		18:07:53		71		48.5		26-Oct-07		18:25:59		75.81		44

		15-Sep-07		20:07:10		74.6		45		15-Sep-07		20:06:20		71		52		15-Sep-07		20:07:53		71		50.5		26-Oct-07		20:25:59		74.6		43

		15-Sep-07		22:07:10		75.2		44.5		15-Sep-07		22:06:20		71.6		52		15-Sep-07		22:07:53		72.8		48		26-Oct-07		22:25:59		73.4		42.5

		16-Sep-07		0:07:10		75.2		44		16-Sep-07		0:06:20		71		51.5		16-Sep-07		0:07:53		72.8		48		27-Oct-07		0:25:59		72.21		43

		16-Sep-07		2:07:10		75.2		43		16-Sep-07		2:06:20		71.6		49.5		16-Sep-07		2:07:53		72.21		47.5		27-Oct-07		2:25:59		71		44

		16-Sep-07		4:07:10		74.6		44		16-Sep-07		4:06:20		71		51		16-Sep-07		4:07:53		71		48.5		27-Oct-07		4:25:59		70.41		44.5

		16-Sep-07		6:07:10		74.01		43		16-Sep-07		6:06:20		69.8		44		16-Sep-07		6:07:53		71		49		27-Oct-07		6:25:59		70.41		45.5

		16-Sep-07		8:07:10		73.4		44		16-Sep-07		8:06:20		68.61		54		16-Sep-07		8:07:53		70.41		48		27-Oct-07		8:25:59		70.41		46

		16-Sep-07		10:07:10		73.4		45.5		16-Sep-07		10:06:20		68.61		57		16-Sep-07		10:07:53		69.8		52.5		27-Oct-07		10:25:59		72.21		45.5

		16-Sep-07		12:07:10		72.8		46		16-Sep-07		12:06:20		68.61		47.5		16-Sep-07		12:07:53		70.41		56		27-Oct-07		12:25:59		74.6		44

		16-Sep-07		14:07:10		73.4		44.5		16-Sep-07		14:06:20		68.61		47		16-Sep-07		14:07:53		71		51		27-Oct-07		14:25:59		75.2		42.5

		16-Sep-07		16:07:10		74.6		45		16-Sep-07		16:06:20		68.61		52		16-Sep-07		16:07:53		71		50.5		27-Oct-07		16:25:59		75.2		43.5

		16-Sep-07		18:07:10		74.6		46		16-Sep-07		18:06:20		68.61		59		16-Sep-07		18:07:53		70.41		53		27-Oct-07		18:25:59		74.6		44

		16-Sep-07		20:07:10		75.81		45		16-Sep-07		20:06:20		71		54		16-Sep-07		20:07:53		71.6		51.5		27-Oct-07		20:25:59		72.21		43.5

		16-Sep-07		22:07:10		75.2		44.5		16-Sep-07		22:06:20		71		52.5		16-Sep-07		22:07:53		72.21		49.5		27-Oct-07		22:25:59		71.6		44

		17-Sep-07		0:07:10		75.2		43		17-Sep-07		0:06:20		71		51.5		17-Sep-07		0:07:53		71.6		49		28-Oct-07		0:25:59		70.41		43.5

		17-Sep-07		2:07:10		74.6		42.5		17-Sep-07		2:06:20		70.41		49.5		17-Sep-07		2:07:53		70.41		48.5		28-Oct-07		2:25:59		69.2		42.5

		17-Sep-07		4:07:10		74.01		41.5		17-Sep-07		4:06:20		70.41		47		17-Sep-07		4:07:53		69.8		48		28-Oct-07		4:25:59		68.61		42

		17-Sep-07		6:07:10		73.4		41.5		17-Sep-07		6:06:20		69.8		42		17-Sep-07		6:07:53		69.2		49		28-Oct-07		6:25:59		68.61		41.5

		17-Sep-07		8:07:10		72.21		44.5		17-Sep-07		8:06:20		68		52.5		17-Sep-07		8:07:53		69.2		50		28-Oct-07		8:25:59		68		42

		17-Sep-07		10:07:10		72.8		47.5		17-Sep-07		10:06:20		68.61		57.5		17-Sep-07		10:07:53		70.41		49.5		28-Oct-07		10:25:59		67.4		44.5

		17-Sep-07		12:07:10		72.8		50.5		17-Sep-07		12:06:20		68.61		61		17-Sep-07		12:07:53		71		49.5		28-Oct-07		12:25:59		68.61		45.5

		17-Sep-07		14:07:10		74.01		45.5		17-Sep-07		14:06:20		69.2		52		17-Sep-07		14:07:53		71		57		28-Oct-07		14:25:59		69.8		46

		17-Sep-07		16:07:10		74.6		49.5		17-Sep-07		16:06:20		68.61		58		17-Sep-07		16:07:53		71		51.5		28-Oct-07		16:25:59		71.6		47

		17-Sep-07		18:07:10		74.6		48.5		17-Sep-07		18:06:20		68.61		61.5		17-Sep-07		18:07:53		71		50		28-Oct-07		18:25:59		71.6		45

		17-Sep-07		20:07:10		75.81		46		17-Sep-07		20:06:20		71		55		17-Sep-07		20:07:53		74.01		48		28-Oct-07		20:25:59		70.41		45

		17-Sep-07		22:07:10		75.81		44		17-Sep-07		22:06:20		71.6		52		17-Sep-07		22:07:53		74.6		46.5		28-Oct-07		22:25:59		69.8		44.5

		18-Sep-07		0:07:10		75.2		42.5		18-Sep-07		0:06:20		71		50		18-Sep-07		0:07:53		73.4		45.5		29-Oct-07		0:25:59		69.2		44

		18-Sep-07		2:07:10		75.2		41.5		18-Sep-07		2:06:20		71.6		48		18-Sep-07		2:07:53		72.21		45.5		29-Oct-07		2:25:59		68.61		44

		18-Sep-07		4:07:10		74.6		40.5		18-Sep-07		4:06:20		71		46.5		18-Sep-07		4:07:53		71		45.5		29-Oct-07		4:25:59		68.61		44

		18-Sep-07		6:07:10		74.6		39.5		18-Sep-07		6:06:20		69.8		45		18-Sep-07		6:07:53		70.41		45.5		29-Oct-07		6:25:59		68		43.5

		18-Sep-07		8:07:10		72.8		40		18-Sep-07		8:06:20		69.2		39.5		18-Sep-07		8:07:53		71		44.5		29-Oct-07		8:25:59		67.4		43

		18-Sep-07		10:07:10		73.4		42.5		18-Sep-07		10:06:20		70.41		46.5		18-Sep-07		10:07:53		71.6		42.5		29-Oct-07		10:25:59		68.61		45.5

		18-Sep-07		12:07:10		73.4		44.5		18-Sep-07		12:06:20		69.8		51		18-Sep-07		12:07:53		72.21		43.5		29-Oct-07		12:25:59		70.41		46.5

		18-Sep-07		14:07:10		73.4		42.5		18-Sep-07		14:06:20		69.8		42		18-Sep-07		14:07:53		71.6		43.5		29-Oct-07		14:25:59		72.21		47.5

		18-Sep-07		16:07:10		74.01		47.5		18-Sep-07		16:06:20		69.2		61		18-Sep-07		16:07:53		71		49.5		29-Oct-07		16:25:59		74.6		47.5

		18-Sep-07		18:07:10		74.01		43.5		18-Sep-07		18:06:20		69.2		49.5		18-Sep-07		18:07:53		71		43		29-Oct-07		18:25:59		75.2		47

		18-Sep-07		20:07:10		74.6		44		18-Sep-07		20:06:20		71.6		50		18-Sep-07		20:07:53		71.6		51.5		29-Oct-07		20:25:59		74.01		46

		18-Sep-07		22:07:10		75.2		42.5		18-Sep-07		22:06:20		71.6		50.5		18-Sep-07		22:07:53		73.4		46		29-Oct-07		22:25:59		72.8		46

		19-Sep-07		0:07:10		75.2		42.5		19-Sep-07		0:06:20		71		49.5		19-Sep-07		0:07:53		73.4		44.5		30-Oct-07		0:25:59		71.6		46

		19-Sep-07		2:07:10		74.6		41		19-Sep-07		2:06:20		71		48		19-Sep-07		2:07:53		72.8		44		30-Oct-07		2:25:59		71		46

		19-Sep-07		4:07:10		74.6		40		19-Sep-07		4:06:20		71		46		19-Sep-07		4:07:53		71		44		30-Oct-07		4:25:59		69.8		45.5

		19-Sep-07		6:07:10		74.01		38.5		19-Sep-07		6:06:20		70.41		41.5		19-Sep-07		6:07:53		70.41		43.5		30-Oct-07		6:25:59		69.8		46

		19-Sep-07		8:07:10		72.8		41		19-Sep-07		8:06:20		69.8		48		19-Sep-07		8:07:53		71		42.5		30-Oct-07		8:25:59		69.2		48

		19-Sep-07		10:07:10		72.8		43.5		19-Sep-07		10:06:20		70.41		51.5		19-Sep-07		10:07:53		71.6		45.5		30-Oct-07		10:25:59		71		48

		19-Sep-07		12:07:10		73.4		45.5		19-Sep-07		12:06:20		70.41		56		19-Sep-07		12:07:53		72.21		53		30-Oct-07		12:25:59		72.8		49

		19-Sep-07		14:07:10		74.6		43.5		19-Sep-07		14:06:20		72.21		49		19-Sep-07		14:07:53		71.6		41		30-Oct-07		14:25:59		74.6		48

		19-Sep-07		16:07:10		73.4		42.5		19-Sep-07		16:06:20		68.61		45		19-Sep-07		16:07:53		72.21		48		30-Oct-07		16:25:59		75.2		47.5

		19-Sep-07		18:07:10		73.4		42		19-Sep-07		18:06:20		68.61		43		19-Sep-07		18:07:53		71		50		30-Oct-07		18:25:59		75.2		45

		19-Sep-07		20:07:10		74.6		42		19-Sep-07		20:06:20		70.41		49		19-Sep-07		20:07:53		71		47.5		30-Oct-07		20:25:59		72.8		45.5

		19-Sep-07		22:07:10		74.6		39.5		19-Sep-07		22:06:20		70.41		46.5		19-Sep-07		22:07:53		72.21		42.5		30-Oct-07		22:25:59		71.6		46.5

		20-Sep-07		0:07:10		74.6		38		20-Sep-07		0:06:20		70.41		44		20-Sep-07		0:07:53		71.6		41		31-Oct-07		0:25:59		71		46.5

		20-Sep-07		2:07:10		74.01		37		20-Sep-07		2:06:20		70.41		42		20-Sep-07		2:07:53		71		40.5		31-Oct-07		2:25:59		70.41		47.5

		20-Sep-07		4:07:10		73.4		36		20-Sep-07		4:06:20		70.41		41		20-Sep-07		4:07:53		69.8		40.5		31-Oct-07		4:25:59		70.41		48

		20-Sep-07		6:07:10		72.8		36		20-Sep-07		6:06:20		69.8		40		20-Sep-07		6:07:53		69.8		40		31-Oct-07		6:25:59		70.41		48.5

		20-Sep-07		8:07:10		72.8		37.5		20-Sep-07		8:06:20		69.8		44		20-Sep-07		8:07:53		71		39.5		31-Oct-07		8:25:59		69.8		48

		20-Sep-07		10:07:10		73.4		37.5		20-Sep-07		10:06:20		70.41		45.5		20-Sep-07		10:07:53		71.6		35.5		31-Oct-07		10:25:59		71.6		48

		20-Sep-07		12:07:10		73.4		36		20-Sep-07		12:06:20		69.2		35.5		20-Sep-07		12:07:53		72.21		34.5		31-Oct-07		12:25:59		72.21		47.5

		20-Sep-07		14:07:10		73.4		34		20-Sep-07		14:06:20		69.8		36		20-Sep-07		14:07:53		71.6		39.5		31-Oct-07		14:25:59		73.4		46.5

		20-Sep-07		16:07:10		73.4		34		20-Sep-07		16:06:20		68.61		37.5		20-Sep-07		16:07:53		71		33		31-Oct-07		16:25:59		74.6		46

		20-Sep-07		18:07:10		74.01		34.5		20-Sep-07		18:06:20		68		41.5		20-Sep-07		18:07:53		70.41		38.5		31-Oct-07		18:25:59		75.2		44.5

		20-Sep-07		20:07:10		74.6		36		20-Sep-07		20:06:20		69.8		41		20-Sep-07		20:07:53		72.8		37.5		31-Oct-07		20:25:59		72.8		44.5

		20-Sep-07		22:07:10		74.6		34		20-Sep-07		22:06:20		70.41		39.5		20-Sep-07		22:07:53		72.21		36.5		31-Oct-07		22:25:59		72.21		45.5

		21-Sep-07		0:07:10		74.01		34.5		21-Sep-07		0:06:20		69.8		40.5		21-Sep-07		0:07:53		71.6		37.5		1-Nov-07		0:25:59		70.41		46

		21-Sep-07		2:07:10		74.01		33.5		21-Sep-07		2:06:20		70.41		36		21-Sep-07		2:07:53		71		37		1-Nov-07		2:25:59		69.8		47

		21-Sep-07		4:07:10		73.4		33		21-Sep-07		4:06:20		70.41		38		21-Sep-07		4:07:53		69.8		37		1-Nov-07		4:25:59		69.8		48

		21-Sep-07		6:07:10		73.4		34.5		21-Sep-07		6:06:20		69.8		39.5		21-Sep-07		6:07:53		69.8		39		1-Nov-07		6:25:59		69.8		48.5

		21-Sep-07		8:07:10		72.8		37.5		21-Sep-07		8:06:20		69.8		44.5		21-Sep-07		8:07:53		71		39		1-Nov-07		8:25:59		69.8		48.5

		21-Sep-07		10:07:10		72.8		38.5		21-Sep-07		10:06:20		69.8		41.5		21-Sep-07		10:07:53		71.6		42		1-Nov-07		10:25:59		72.21		48

		21-Sep-07		12:07:10		74.6		37		21-Sep-07		12:06:20		73.4		36		21-Sep-07		12:07:53		71.6		36.5		1-Nov-07		12:25:59		72.8		48.5

		21-Sep-07		14:07:10		74.6		38.5		21-Sep-07		14:06:20		71.6		45		21-Sep-07		14:07:53		71		41.5		1-Nov-07		14:25:59		73.4		48.5

		21-Sep-07		16:07:10		74.6		38		21-Sep-07		16:06:20		70.41		45.5		21-Sep-07		16:07:53		71		41		1-Nov-07		16:25:59		74.01		49.5

		21-Sep-07		18:07:10		74.6		37.5		21-Sep-07		18:06:20		70.41		44		21-Sep-07		18:07:53		71		40.5		1-Nov-07		18:25:59		74.01		48

		21-Sep-07		20:07:10		75.81		35		21-Sep-07		20:06:20		72.21		39		21-Sep-07		20:07:53		71.6		39		1-Nov-07		20:25:59		72.21		48

		21-Sep-07		22:07:10		75.81		33.5		21-Sep-07		22:06:20		72.8		37.5		21-Sep-07		22:07:53		71		38		1-Nov-07		22:25:59		71.6		49

		22-Sep-07		0:07:10		75.2		33		22-Sep-07		0:06:20		72.21		37		22-Sep-07		0:07:53		70.41		38.5		2-Nov-07		0:25:59		71		49

		22-Sep-07		2:07:10		74.6		32.5		22-Sep-07		2:06:20		71.6		36.5		22-Sep-07		2:07:53		68.61		38.5		2-Nov-07		2:25:59		70.41		49.5

		22-Sep-07		4:07:10		73.4		33		22-Sep-07		4:06:20		70.41		37.5		22-Sep-07		4:07:53		68		39.5		2-Nov-07		4:25:59		69.8		49

		22-Sep-07		6:07:10		72.8		33.5		22-Sep-07		6:06:20		69.8		37.5		22-Sep-07		6:07:53		67.4		40.5		2-Nov-07		6:25:59		69.8		48

		22-Sep-07		8:07:10		72.8		33.5		22-Sep-07		8:06:20		71.6		37.5		22-Sep-07		8:07:53		69.2		40		2-Nov-07		8:25:59		71.6		46.5

		22-Sep-07		10:07:10		73.4		36		22-Sep-07		10:06:20		72.21		39		22-Sep-07		10:07:53		71.6		43.5		2-Nov-07		10:25:59		71.6		48

		22-Sep-07		12:07:10		73.4		36.5		22-Sep-07		12:06:20		71.6		40.5		22-Sep-07		12:07:53		71.6		44.5		2-Nov-07		12:25:59		73.4		48

		22-Sep-07		14:07:10		74.01		38		22-Sep-07		14:06:20		71		40.5		22-Sep-07		14:07:53		72.21		43		2-Nov-07		14:25:59		75.2		48

		22-Sep-07		16:07:10		74.6		40.5		22-Sep-07		16:06:20		70.41		47		22-Sep-07		16:07:53		71.6		47		2-Nov-07		16:25:59		75.2		49.5

		22-Sep-07		18:07:10		74.6		38.5		22-Sep-07		18:06:20		70.41		45		22-Sep-07		18:07:53		71		38.5		2-Nov-07		18:25:59		75.2		50

		22-Sep-07		20:07:10		75.2		37.5		22-Sep-07		20:06:20		72.21		42		22-Sep-07		20:07:53		70.41		44		2-Nov-07		20:25:59		74.6		46

		22-Sep-07		22:07:10		75.81		37.5		22-Sep-07		22:06:20		72.8		42.5		22-Sep-07		22:07:53		71.6		43		2-Nov-07		22:25:59		73.4		45.5

		23-Sep-07		0:07:10		75.81		38.5		23-Sep-07		0:06:20		73.4		43.5		23-Sep-07		0:07:53		71.6		44.5		3-Nov-07		0:25:59		71.6		45

		23-Sep-07		2:07:10		75.2		40		23-Sep-07		2:06:20		72.21		46.5		23-Sep-07		2:07:53		71		46.5		3-Nov-07		2:25:59		69.8		44

		23-Sep-07		4:07:10		75.2		41		23-Sep-07		4:06:20		72.8		46		23-Sep-07		4:07:53		71		47.5		3-Nov-07		4:25:59		69.2		43

		23-Sep-07		6:07:10		74.6		42		23-Sep-07		6:06:20		71.6		44		23-Sep-07		6:07:53		71.6		48		3-Nov-07		6:25:59		69.2		42

		23-Sep-07		8:07:10		74.01		44.5		23-Sep-07		8:06:20		69.8		52		23-Sep-07		8:07:53		71		43.5		3-Nov-07		8:25:59		71.6		39.5

		23-Sep-07		10:07:10		73.4		44.5		23-Sep-07		10:06:20		70.41		50.5		23-Sep-07		10:07:53		71.6		56		3-Nov-07		10:25:59		71.6		42.5

		23-Sep-07		12:07:10		74.01		44.5		23-Sep-07		12:06:20		70.41		48		23-Sep-07		12:07:53		71		49		3-Nov-07		12:25:59		75.2		42.5

		23-Sep-07		14:07:10		73.4		48.5		23-Sep-07		14:06:20		70.41		56.5		23-Sep-07		14:07:53		71		54		3-Nov-07		14:25:59		76.4		42.5

		23-Sep-07		16:07:10		74.01		50.5		23-Sep-07		16:06:20		70.41		60		23-Sep-07		16:07:53		70.41		51		3-Nov-07		16:25:59		75.81		42

		23-Sep-07		18:07:10		73.4		50.5		23-Sep-07		18:06:20		70.41		59		23-Sep-07		18:07:53		69.8		56.5		3-Nov-07		18:25:59		75.81		43.5

		23-Sep-07		20:07:10		74.6		49.5		23-Sep-07		20:06:20		72.21		55		23-Sep-07		20:07:53		69.8		56		3-Nov-07		20:25:59		74.6		43

		23-Sep-07		22:07:10		74.6		48		23-Sep-07		22:06:20		72.21		52.5		23-Sep-07		22:07:53		70.41		55.5		3-Nov-07		22:25:59		73.4		43.5

		24-Sep-07		0:07:10		74.6		47.5		24-Sep-07		0:06:20		72.21		52		24-Sep-07		0:07:53		69.8		54.5		4-Nov-07		0:25:59		71.6		43

		24-Sep-07		2:07:10		74.6		47.5		24-Sep-07		2:06:20		72.21		52		24-Sep-07		2:07:53		69.8		55		4-Nov-07		2:25:59		70.41		42

		24-Sep-07		4:07:10		74.6		47		24-Sep-07		4:06:20		72.21		51.5		24-Sep-07		4:07:53		69.8		54.5		4-Nov-07		4:25:59		69.2		41

		24-Sep-07		6:07:10		74.01		46.5		24-Sep-07		6:06:20		71.6		46		24-Sep-07		6:07:53		69.8		54.5		4-Nov-07		6:25:59		68.61		40

		24-Sep-07		8:07:10		73.4		49		24-Sep-07		8:06:20		70.41		56		24-Sep-07		8:07:53		69.2		55		4-Nov-07		8:25:59		67.4		38.5

		24-Sep-07		10:07:10		72.8		50.5		24-Sep-07		10:06:20		69.8		56.5		24-Sep-07		10:07:53		69.8		55.5		4-Nov-07		10:25:59		68		40.5

		24-Sep-07		12:07:10		72.8		51		24-Sep-07		12:06:20		69.2		55.5		24-Sep-07		12:07:53		69.8		56		4-Nov-07		12:25:59		69.2		42.5

		24-Sep-07		14:07:10		73.4		50		24-Sep-07		14:06:20		69.8		56.5		24-Sep-07		14:07:53		70.41		51.5		4-Nov-07		14:25:59		71		43

		24-Sep-07		16:07:10		74.01		46		24-Sep-07		16:06:20		69.8		44		24-Sep-07		16:07:53		70.41		48		4-Nov-07		16:25:59		72.21		43

		24-Sep-07		18:07:10		74.01		45		24-Sep-07		18:06:20		69.8		51		24-Sep-07		18:07:53		71		46.5		4-Nov-07		18:25:59		72.8		41.5

		24-Sep-07		20:07:10		75.2		40		24-Sep-07		20:06:20		72.8		39.5		24-Sep-07		20:07:53		72.21		45		4-Nov-07		20:25:59		71.6		39

		24-Sep-07		22:07:10		75.81		40		24-Sep-07		22:06:20		73.4		43.5		24-Sep-07		22:07:53		71.6		45.5		4-Nov-07		22:25:59		70.41		39.5

		25-Sep-07		0:07:10		74.6		39		25-Sep-07		0:06:20		72.21		43		25-Sep-07		0:07:53		70.41		45		5-Nov-07		0:25:59		69.8		40

		25-Sep-07		2:07:10		74.01		37.5		25-Sep-07		2:06:20		71.6		41		25-Sep-07		2:07:53		69.2		44		5-Nov-07		2:25:59		68.61		40

		25-Sep-07		4:07:10		73.4		37		25-Sep-07		4:06:20		71		40		25-Sep-07		4:07:53		68		43		5-Nov-07		4:25:59		68		39

		25-Sep-07		6:07:10		72.8		36.5		25-Sep-07		6:06:20		69.8		38.5		25-Sep-07		6:07:53		68.61		42		5-Nov-07		6:25:59		67.4		38.5

		25-Sep-07		8:07:10		72.8		37		25-Sep-07		8:06:20		71		41		25-Sep-07		8:07:53		69.2		41		5-Nov-07		8:25:59		66.2		37.5

		25-Sep-07		10:07:10		74.01		38		25-Sep-07		10:06:20		72.21		40		25-Sep-07		10:07:53		71		48		5-Nov-07		10:25:59		67.4		39.5

		25-Sep-07		12:07:10		74.6		39		25-Sep-07		12:06:20		71.6		43		25-Sep-07		12:07:53		71.6		43		5-Nov-07		12:25:59		69.2		40.5

		25-Sep-07		14:07:10		74.01		34.5		25-Sep-07		14:06:20		71.6		37.5		25-Sep-07		14:07:53		71.6		35		5-Nov-07		14:25:59		71		41.5

		25-Sep-07		16:07:10		74.6		36.5		25-Sep-07		16:06:20		70.41		40.5		25-Sep-07		16:07:53		72.21		39		5-Nov-07		16:25:59		72.21		41.5

		25-Sep-07		18:07:10		74.01		33.5		25-Sep-07		18:06:20		70.41		36		25-Sep-07		18:07:53		71.6		37		5-Nov-07		18:25:59		72.8		41

		25-Sep-07		20:07:10		75.81		36.5		25-Sep-07		20:06:20		72.8		40.5		25-Sep-07		20:07:53		71		42.5		5-Nov-07		20:25:59		71.6		42.5

		25-Sep-07		22:07:10		75.81		36		25-Sep-07		22:06:20		72.8		40		25-Sep-07		22:07:53		72.8		40		5-Nov-07		22:25:59		71		43

		26-Sep-07		0:07:10		75.81		35		26-Sep-07		0:06:20		72.8		39		26-Sep-07		0:07:53		71.6		40		6-Nov-07		0:25:59		69.8		42

		26-Sep-07		2:07:10		75.2		34.5		26-Sep-07		2:06:20		72.21		39		26-Sep-07		2:07:53		69.8		40		6-Nov-07		2:25:59		69.2		41.5

		26-Sep-07		4:07:10		74.01		34		26-Sep-07		4:06:20		71		38		26-Sep-07		4:07:53		68.61		40		6-Nov-07		4:25:59		68		40.5

		26-Sep-07		6:07:10		72.8		33.5		26-Sep-07		6:06:20		70.41		36		26-Sep-07		6:07:53		68.61		39.5		6-Nov-07		6:25:59		68		39.5

		26-Sep-07		8:07:10		73.4		33		26-Sep-07		8:06:20		71.6		36.5		26-Sep-07		8:07:53		70.41		37.5		6-Nov-07		8:25:59		69.8		37

		26-Sep-07		10:07:10		74.01		37		26-Sep-07		10:06:20		71.6		38.5		26-Sep-07		10:07:53		71.6		34.5		6-Nov-07		10:25:59		71		39.5

		26-Sep-07		12:07:10		74.6		34.5		26-Sep-07		12:06:20		71.6		36		26-Sep-07		12:07:53		71.6		35.5		6-Nov-07		12:25:59		73.4		39.5

		26-Sep-07		14:07:10		74.6		33		26-Sep-07		14:06:20		71.6		35.5		26-Sep-07		14:07:53		71.6		34		6-Nov-07		14:25:59		75.2		39.5

		26-Sep-07		16:07:10		75.2		32.5		26-Sep-07		16:06:20		71		35.5		26-Sep-07		16:07:53		71.6		34.5		6-Nov-07		16:25:59		75.81		42.5

		26-Sep-07		18:07:10		74.6		31		26-Sep-07		18:06:20		69.8		34.5		26-Sep-07		18:07:53		71		34.5		6-Nov-07		18:25:59		75.2		41.5

		26-Sep-07		20:07:10		75.81		32		26-Sep-07		20:06:20		72.8		35.5		26-Sep-07		20:07:53		71		33.5		6-Nov-07		20:25:59		72.8		41

		26-Sep-07		22:07:10		76.4		31		26-Sep-07		22:06:20		72.8		35.5		26-Sep-07		22:07:53		73.4		34.5		6-Nov-07		22:25:59		71.6		42

		27-Sep-07		0:07:10		76.4		31		27-Sep-07		0:06:20		72.8		35.5		27-Sep-07		0:07:53		72.8		34.5		7-Nov-07		0:25:59		71		43

		27-Sep-07		2:07:10		75.81		30.5		27-Sep-07		2:06:20		72.21		35		27-Sep-07		2:07:53		71.6		34.5		7-Nov-07		2:25:59		69.8		43

		27-Sep-07		4:07:10		75.2		30		27-Sep-07		4:06:20		72.21		34		27-Sep-07		4:07:53		70.41		35		7-Nov-07		4:25:59		69.2		43.5

		27-Sep-07		6:07:10		75.2		30.5		27-Sep-07		6:06:20		72.21		33		27-Sep-07		6:07:53		70.41		35.5		7-Nov-07		6:25:59		69.2		44

		27-Sep-07		8:07:10		74.6		31.5		27-Sep-07		8:06:20		71.6		35		27-Sep-07		8:07:53		71.6		33		7-Nov-07		8:25:59		71		43

		27-Sep-07		10:07:10		74.6		32		27-Sep-07		10:06:20		72.21		37.5		27-Sep-07		10:07:53		71.6		36.5		7-Nov-07		10:25:59		71.6		42.5

		27-Sep-07		12:07:10		74.6		34		27-Sep-07		12:06:20		71.6		37		27-Sep-07		12:07:53		72.21		39		7-Nov-07		12:25:59		72.8		42

		27-Sep-07		14:07:10		74.6		34		27-Sep-07		14:06:20		71		35.5		27-Sep-07		14:07:53		72.21		34		7-Nov-07		14:25:59		74.01		42.5

		27-Sep-07		16:07:10		75.2		33		27-Sep-07		16:06:20		70.41		37.5		27-Sep-07		16:07:53		71.6		34.5		7-Nov-07		16:25:59		74.6		44

		27-Sep-07		18:07:10		75.2		32.5		27-Sep-07		18:06:20		71		36		27-Sep-07		18:07:53		71.6		35.5		7-Nov-07		18:25:59		74.6		43

		27-Sep-07		20:07:10		76.4		30.5		27-Sep-07		20:06:20		72.8		33.5		27-Sep-07		20:07:53		74.6		31.5		7-Nov-07		20:25:59		72.21		42.5

		27-Sep-07		22:07:10		76.4		30.5		27-Sep-07		22:06:20		72.8		34.5		27-Sep-07		22:07:53		75.2		32		7-Nov-07		22:25:59		71.6		42

		28-Sep-07		0:07:10		76.4		30		28-Sep-07		0:06:20		72.8		34.5		28-Sep-07		0:07:53		74.6		32.5		8-Nov-07		0:25:59		69.8		42.5

		28-Sep-07		2:07:10		75.81		29.5		28-Sep-07		2:06:20		72.8		33		28-Sep-07		2:07:53		72.8		33		8-Nov-07		2:25:59		69.2		43

		28-Sep-07		4:07:10		75.2		30		28-Sep-07		4:06:20		72.8		34		28-Sep-07		4:07:53		71.6		34		8-Nov-07		4:25:59		68.61		42.5

		28-Sep-07		6:07:10		75.2		30.5		28-Sep-07		6:06:20		72.8		32.5		28-Sep-07		6:07:53		70.41		35		8-Nov-07		6:25:59		68.61		43

		28-Sep-07		8:07:10		74.6		31.5		28-Sep-07		8:06:20		71		37		28-Sep-07		8:07:53		71.6		31.5		8-Nov-07		8:25:59		71.6		40.5

		28-Sep-07		10:07:10		74.6		32.5		28-Sep-07		10:06:20		71.6		39		28-Sep-07		10:07:53		71.6		38.5		8-Nov-07		10:25:59		71		41.5

		28-Sep-07		12:07:10		74.6		33		28-Sep-07		12:06:20		71.6		36.5		28-Sep-07		12:07:53		72.21		34.5		8-Nov-07		12:25:59		72.8		43.5

		28-Sep-07		14:07:10		74.01		36		28-Sep-07		14:06:20		71		36		28-Sep-07		14:07:53		71.6		40		8-Nov-07		14:25:59		74.01		42.5

		28-Sep-07		16:07:10		75.2		37.5		28-Sep-07		16:06:20		71		44		28-Sep-07		16:07:53		71.6		41.5		8-Nov-07		16:25:59		75.2		43.5

		28-Sep-07		18:07:10		74.6		39		28-Sep-07		18:06:20		70.41		46.5		28-Sep-07		18:07:53		71		45		8-Nov-07		18:25:59		74.01		43

		28-Sep-07		20:07:10		75.81		37		28-Sep-07		20:06:20		72.8		42		28-Sep-07		20:07:53		71.6		42		8-Nov-07		20:25:59		72.21		43.5

		28-Sep-07		22:07:10		75.81		36.5		28-Sep-07		22:06:20		72.8		42		28-Sep-07		22:07:53		72.21		41		8-Nov-07		22:25:59		72.21		45.5

		29-Sep-07		0:07:10		75.2		36.5		29-Sep-07		0:06:20		72.21		42		29-Sep-07		0:07:53		71.6		42		9-Nov-07		0:25:59		71		44.5

		29-Sep-07		2:07:10		75.2		37		29-Sep-07		2:06:20		72.8		42		29-Sep-07		2:07:53		71		42.5		9-Nov-07		2:25:59		69.8		44.5

		29-Sep-07		4:07:10		75.2		37		29-Sep-07		4:06:20		72.8		41		29-Sep-07		4:07:53		71		42.5		9-Nov-07		4:25:59		69.2		45

		29-Sep-07		6:07:10		75.2		35		29-Sep-07		6:06:20		72.8		35		29-Sep-07		6:07:53		69.8		45.5		9-Nov-07		6:25:59		69.2		46.5

		29-Sep-07		8:07:10		74.6		39		29-Sep-07		8:06:20		71.6		42		29-Sep-07		8:07:53		71		45.5		9-Nov-07		8:25:59		71		45

		29-Sep-07		10:07:10		74.01		40.5		29-Sep-07		10:06:20		71		42		29-Sep-07		10:07:53		71.6		46		9-Nov-07		10:25:59		71		46

		29-Sep-07		12:07:10		74.6		39		29-Sep-07		12:06:20		71.6		38.5		29-Sep-07		12:07:53		71.6		48.5		9-Nov-07		12:25:59		72.21		47

		29-Sep-07		14:07:10		74.01		45		29-Sep-07		14:06:20		71.6		54		29-Sep-07		14:07:53		71.6		47		9-Nov-07		14:25:59		74.01		44.5

		29-Sep-07		16:07:10		74.6		42		29-Sep-07		16:06:20		71.6		48.5		29-Sep-07		16:07:53		71.6		52		9-Nov-07		16:25:59		74.01		44.5

		29-Sep-07		18:07:10		74.6		43.5		29-Sep-07		18:06:20		70.41		53		29-Sep-07		18:07:53		71		52		9-Nov-07		18:25:59		74.01		43.5

		29-Sep-07		20:07:10		75.2		36		29-Sep-07		20:06:20		72.21		38		29-Sep-07		20:07:53		70.41		42		9-Nov-07		20:25:59		73.4		43

		29-Sep-07		22:07:10		75.2		32.5		29-Sep-07		22:06:20		72.8		35		29-Sep-07		22:07:53		71		36.5		9-Nov-07		22:25:59		72.21		45

		30-Sep-07		0:07:10		75.2		31		30-Sep-07		0:06:20		73.4		33.5		30-Sep-07		0:07:53		70.41		35.5		10-Nov-07		0:25:59		71		45

		30-Sep-07		2:07:10		74.6		30.5		30-Sep-07		2:06:20		72.8		32.5		30-Sep-07		2:07:53		69.8		34.5		10-Nov-07		2:25:59		69.8		45.5

		30-Sep-07		4:07:10		74.01		30		30-Sep-07		4:06:20		71.6		32.5		30-Sep-07		4:07:53		68.61		34.5		10-Nov-07		4:25:59		69.2		46

		30-Sep-07		6:07:10		73.4		29.5		30-Sep-07		6:06:20		72.21		32.5		30-Sep-07		6:07:53		68		34.5		10-Nov-07		6:25:59		69.2		45.5

		30-Sep-07		8:07:10		72.21		30.5		30-Sep-07		8:06:20		71		34		30-Sep-07		8:07:53		68		34.5		10-Nov-07		8:25:59		71		42.5

		30-Sep-07		10:07:10		72.8		31		30-Sep-07		10:06:20		71.6		34.5		30-Sep-07		10:07:53		70.41		34.5		10-Nov-07		10:25:59		73.4		43

		30-Sep-07		12:07:10		73.4		31		30-Sep-07		12:06:20		71		33.5		30-Sep-07		12:07:53		70.41		32		10-Nov-07		12:25:59		74.01		43

		30-Sep-07		14:07:10		73.4		29		30-Sep-07		14:06:20		70.41		31.5		30-Sep-07		14:07:53		71		31		10-Nov-07		14:25:59		74.6		42

		30-Sep-07		16:07:10		74.01		30		30-Sep-07		16:06:20		69.8		34.5		30-Sep-07		16:07:53		71		31		10-Nov-07		16:25:59		75.2		43

		30-Sep-07		18:07:10		74.01		29		30-Sep-07		18:06:20		69.8		32.5		30-Sep-07		18:07:53		71		31		10-Nov-07		18:25:59		74.6		44

		30-Sep-07		20:07:10		75.2		28		30-Sep-07		20:06:20		72.21		31		30-Sep-07		20:07:53		71.6		32		10-Nov-07		20:25:59		72.8		44.5

		30-Sep-07		22:07:10		75.81		27.5		30-Sep-07		22:06:20		72.8		31		30-Sep-07		22:07:53		71.6		31.5		10-Nov-07		22:25:59		72.21		45.5

		1-Oct-07		0:07:10		75.2		27		1-Oct-07		0:06:20		72.8		30		1-Oct-07		0:07:53		70.41		32		11-Nov-07		0:25:59		70.41		44

		1-Oct-07		2:07:10		74.01		27.5		1-Oct-07		2:06:20		71.6		30.5		1-Oct-07		2:07:53		68.61		32		11-Nov-07		2:25:59		69.2		43

		1-Oct-07		4:07:10		72.8		27.5		1-Oct-07		4:06:20		70.41		30.5		1-Oct-07		4:07:53		68		32.5		11-Nov-07		4:25:59		68.61		43

		1-Oct-07		6:07:10		72.21		27.5		1-Oct-07		6:06:20		69.8		30		1-Oct-07		6:07:53		66.2		33		11-Nov-07		6:25:59		68		43.5

		1-Oct-07		8:07:10		71		28.5		1-Oct-07		8:06:20		68.61		31.5		1-Oct-07		8:07:53		68		32		11-Nov-07		8:25:59		68		44.5

		1-Oct-07		10:07:10		71.6		30		1-Oct-07		10:06:20		69.8		31.5		1-Oct-07		10:07:53		68.61		33.5		11-Nov-07		10:25:59		69.2		46.5

		1-Oct-07		12:07:10		72.21		30		1-Oct-07		12:06:20		70.41		32		1-Oct-07		12:07:53		70.41		33.5		11-Nov-07		12:25:59		69.2		49

		1-Oct-07		14:07:10		73.4		28.5		1-Oct-07		14:06:20		69.8		30		1-Oct-07		14:07:53		70.41		31.5		11-Nov-07		14:25:59		69.8		50.5

		1-Oct-07		16:07:10		73.4		27		1-Oct-07		16:06:20		69.8		29.5		1-Oct-07		16:07:53		70.41		30.5		11-Nov-07		16:25:59		69.8		52

		1-Oct-07		18:07:10		74.01		30		1-Oct-07		18:06:20		69.8		35.5		1-Oct-07		18:07:53		71		32		11-Nov-07		18:25:59		69.8		53

		1-Oct-07		20:07:10		75.81		33		1-Oct-07		20:06:20		72.8		38		1-Oct-07		20:07:53		72.21		37.5		11-Nov-07		20:25:59		69.2		54

		1-Oct-07		22:07:10		75.2		35.5		1-Oct-07		22:06:20		72.21		41		1-Oct-07		22:07:53		72.21		39.5		11-Nov-07		22:25:59		69.2		55

		2-Oct-07		0:07:10		75.2		35.5		2-Oct-07		0:06:20		72.8		41		2-Oct-07		0:07:53		71.6		41		12-Nov-07		0:25:59		69.2		55.5

		2-Oct-07		2:07:10		75.2		36.5		2-Oct-07		2:06:20		72.8		41		2-Oct-07		2:07:53		71		42.5		12-Nov-07		2:25:59		69.2		55.5

		2-Oct-07		4:07:10		75.2		40		2-Oct-07		4:06:20		72.8		46		2-Oct-07		4:07:53		71		46.5		12-Nov-07		4:25:59		69.2		54

		2-Oct-07		6:07:10		75.2		39		2-Oct-07		6:06:20		72.8		41		2-Oct-07		6:07:53		70.41		53.5		12-Nov-07		6:25:59		68.61		50.5

		2-Oct-07		8:07:10		74.6		44.5		2-Oct-07		8:06:20		71.6		46.5		2-Oct-07		8:07:53		71		51.5		12-Nov-07		8:25:59		68		47.5

		2-Oct-07		10:07:10		74.6		40.5		2-Oct-07		10:06:20		71.6		44.5		2-Oct-07		10:07:53		72.21		41		12-Nov-07		10:25:59		68		47.5

		2-Oct-07		12:07:10		74.6		44.5		2-Oct-07		12:06:20		71		47.5		2-Oct-07		12:07:53		72.21		51.5		12-Nov-07		12:25:59		69.2		46

		2-Oct-07		14:07:10		74.6		42		2-Oct-07		14:06:20		71.6		51		2-Oct-07		14:07:53		71.6		50		12-Nov-07		14:25:59		70.41		44

		2-Oct-07		16:07:10		75.2		38.5		2-Oct-07		16:06:20		71.6		46		2-Oct-07		16:07:53		71		46		12-Nov-07		16:25:59		71		42.5

		2-Oct-07		18:07:10		74.6		34		2-Oct-07		18:06:20		71		39.5		2-Oct-07		18:07:53		71		36		12-Nov-07		18:25:59		71		42.5

		2-Oct-07		20:07:10		75.81		37		2-Oct-07		20:06:20		72.8		41.5		2-Oct-07		20:07:53		70.41		44.5		12-Nov-07		20:25:59		69.8		42.5

		2-Oct-07		22:07:10		76.4		36.5		2-Oct-07		22:06:20		72.8		41.5		2-Oct-07		22:07:53		72.8		41		12-Nov-07		22:25:59		68.61		43

		3-Oct-07		0:07:10		75.81		35.5		3-Oct-07		0:06:20		72.8		40		3-Oct-07		0:07:53		72.21		40		13-Nov-07		0:25:59		68		42.5

		3-Oct-07		2:07:10		75.81		34.5		3-Oct-07		2:06:20		72.8		38		3-Oct-07		2:07:53		71		39.5		13-Nov-07		2:25:59		67.4		42.5

		3-Oct-07		4:07:10		74.6		34.5		3-Oct-07		4:06:20		71.6		38.5		3-Oct-07		4:07:53		69.8		39.5		13-Nov-07		4:25:59		67.4		42

		3-Oct-07		6:07:10		74.01		34.5		3-Oct-07		6:06:20		71.6		37.5		3-Oct-07		6:07:53		69.8		40		13-Nov-07		6:25:59		67.4		42.5

		3-Oct-07		8:07:10		73.4		36.5		3-Oct-07		8:06:20		71.6		42		3-Oct-07		8:07:53		71.6		39.5		13-Nov-07		8:25:59		71		40.5

		3-Oct-07		10:07:10		74.6		39		3-Oct-07		10:06:20		71.6		45		3-Oct-07		10:07:53		71.6		43.5		13-Nov-07		10:25:59		71		41

		3-Oct-07		12:07:10		74.6		38.5		3-Oct-07		12:06:20		71.6		37.5		3-Oct-07		12:07:53		72.21		43		13-Nov-07		12:25:59		74.6		39.5

		3-Oct-07		14:07:10		74.6		39		3-Oct-07		14:06:20		71.6		38		3-Oct-07		14:07:53		72.21		42		13-Nov-07		14:25:59		74.6		38.5

		3-Oct-07		16:07:10		74.6		37		3-Oct-07		16:06:20		71		41.5		3-Oct-07		16:07:53		71		42.5		13-Nov-07		16:25:59		75.2		37.5

		3-Oct-07		18:07:10		74.6		38.5		3-Oct-07		18:06:20		69.8		47.5		3-Oct-07		18:07:53		71		38		13-Nov-07		18:25:59		75.2		35.5

		3-Oct-07		20:07:10		75.81		37.5		3-Oct-07		20:06:20		72.8		43		3-Oct-07		20:07:53		71		44		13-Nov-07		20:25:59		73.4		38.5

		3-Oct-07		22:07:10		76.4		36.5		3-Oct-07		22:06:20		72.8		40		3-Oct-07		22:07:53		71.6		41.5		13-Nov-07		22:25:59		72.21		41

		4-Oct-07		0:07:10		75.81		35		4-Oct-07		0:06:20		72.8		39.5		4-Oct-07		0:07:53		71.6		40.5		14-Nov-07		0:25:59		71.6		43

		4-Oct-07		2:07:10		75.2		34.5		4-Oct-07		2:06:20		72.21		38.5		4-Oct-07		2:07:53		70.41		40.5		14-Nov-07		2:25:59		70.41		44.5

		4-Oct-07		4:07:10		74.01		34		4-Oct-07		4:06:20		71		38.5		4-Oct-07		4:07:53		69.2		40		14-Nov-07		4:25:59		69.8		45

		4-Oct-07		6:07:10		74.01		33.5		4-Oct-07		6:06:20		70.41		37		4-Oct-07		6:07:53		68.61		39.5		14-Nov-07		6:25:59		69.8		47

		4-Oct-07		8:07:10		74.01		34.5		4-Oct-07		8:06:20		71.6		39		4-Oct-07		8:07:53		70.41		38		14-Nov-07		8:25:59		73.4		46

		4-Oct-07		10:07:10		74.6		36		4-Oct-07		10:06:20		72.21		41		4-Oct-07		10:07:53		71.6		35.5		14-Nov-07		10:25:59		74.6		47

		4-Oct-07		12:07:10		76.4		36		4-Oct-07		12:06:20		72.21		41.5		4-Oct-07		12:07:53		71.6		45.5		14-Nov-07		12:25:59		74.6		48.5

		4-Oct-07		14:07:10		75.81		35		4-Oct-07		14:06:20		72.21		36		4-Oct-07		14:07:53		72.21		35.5		14-Nov-07		14:25:59		75.2		49.5

		4-Oct-07		16:07:10		76.4		38.5		4-Oct-07		16:06:20		71		41.5		4-Oct-07		16:07:53		71		49		14-Nov-07		16:25:59		75.2		49.5

		4-Oct-07		18:07:10		76.4		33.5		4-Oct-07		18:06:20		70.41		40		4-Oct-07		18:07:53		70.41		41		14-Nov-07		18:25:59		75.2		49.5

		4-Oct-07		20:07:10		76.4		34		4-Oct-07		20:06:20		72.8		38.5		4-Oct-07		20:07:53		72.8		37.5		14-Nov-07		20:25:59		74.6		49

		4-Oct-07		22:07:10		76.4		31.5		4-Oct-07		22:06:20		72.8		35.5		4-Oct-07		22:07:53		72.8		35		14-Nov-07		22:25:59		74.01		52

		5-Oct-07		0:07:10		75.81		30.5		5-Oct-07		0:06:20		72.8		34.5		5-Oct-07		0:07:53		72.21		34.5		15-Nov-07		0:25:59		72.8		50.5

		5-Oct-07		2:07:10		75.2		29		5-Oct-07		2:06:20		72.8		32.5		5-Oct-07		2:07:53		71		33.5		15-Nov-07		2:25:59		71.6		51

		5-Oct-07		4:07:10		74.6		28.5		5-Oct-07		4:06:20		72.8		31		5-Oct-07		4:07:53		69.8		32.5		15-Nov-07		4:25:59		71		50

		5-Oct-07		6:07:10		74.6		29		5-Oct-07		6:06:20		72.21		31.5		5-Oct-07		6:07:53		69.8		33.5		15-Nov-07		6:25:59		69.8		49

		5-Oct-07		8:07:10		74.01		30.5		5-Oct-07		8:06:20		71.6		33.5		5-Oct-07		8:07:53		71		34		15-Nov-07		8:25:59		72.8		44.5

		5-Oct-07		10:07:10		74.6		31.5		5-Oct-07		10:06:20		72.21		36.5		5-Oct-07		10:07:53		71.6		32.5		15-Nov-07		10:25:59		74.6		47

		5-Oct-07		12:07:10		75.2		32		5-Oct-07		12:06:20		71.6		34		5-Oct-07		12:07:53		71.6		33		15-Nov-07		12:25:59		74.6		48.5

		5-Oct-07		14:07:10		75.2		33		5-Oct-07		14:06:20		72.21		39.5		5-Oct-07		14:07:53		71.6		38.5		15-Nov-07		14:25:59		75.2		48

		5-Oct-07		16:07:10		75.81		32		5-Oct-07		16:06:20		70.41		39.5		5-Oct-07		16:07:53		71		35.5		15-Nov-07		16:25:59		75.2		49

		5-Oct-07		18:07:10		75.2		30		5-Oct-07		18:06:20		69.8		35		5-Oct-07		18:07:53		70.41		34.5		15-Nov-07		18:25:59		74.6		50

		5-Oct-07		20:07:10		75.81		29.5		5-Oct-07		20:06:20		72.21		33.5		5-Oct-07		20:07:53		70.41		34.5		15-Nov-07		20:25:59		74.01		50

		5-Oct-07		22:07:10		75.2		29.5		5-Oct-07		22:06:20		72.21		33.5		5-Oct-07		22:07:53		69.8		34.5		15-Nov-07		22:25:59		74.01		49.5

		6-Oct-07		0:07:10		75.2		29.5		6-Oct-07		0:06:20		72.21		33.5		6-Oct-07		0:07:53		69.2		35		16-Nov-07		0:25:59		72.21		49.5

		6-Oct-07		2:07:10		74.01		30		6-Oct-07		2:06:20		71.6		33.5		6-Oct-07		2:07:53		68		35.5		16-Nov-07		2:25:59		71		48.5

		6-Oct-07		4:07:10		72.8		29.5		6-Oct-07		4:06:20		70.41		33		6-Oct-07		4:07:53		66.81		36		16-Nov-07		4:25:59		69.8		48

		6-Oct-07		6:07:10		72.8		29		6-Oct-07		6:06:20		72.21		30		6-Oct-07		6:07:53		68		34.5		16-Nov-07		6:25:59		69.8		47

		6-Oct-07		8:07:10		72.8		29.5		6-Oct-07		8:06:20		71.6		34.5		6-Oct-07		8:07:53		69.2		33		16-Nov-07		8:25:59		72.8		42.5

		6-Oct-07		10:07:10		73.4		30.5		6-Oct-07		10:06:20		71.6		33.5		6-Oct-07		10:07:53		71.6		31		16-Nov-07		10:25:59		74.01		44

		6-Oct-07		12:07:10		74.01		30.5		6-Oct-07		12:06:20		70.41		36		6-Oct-07		12:07:53		71.6		34.5		16-Nov-07		12:25:59		74.6		47

		6-Oct-07		14:07:10		75.2		28		6-Oct-07		14:06:20		69.2		32.5		6-Oct-07		14:07:53		71		30.5		16-Nov-07		14:25:59		74.6		49.5

		6-Oct-07		16:07:10		75.2		27		6-Oct-07		16:06:20		69.2		31.5		6-Oct-07		16:07:53		70.41		31.5		16-Nov-07		16:25:59		75.81		49.5

		6-Oct-07		18:07:10		75.81		27.5		6-Oct-07		18:06:20		69.2		33		6-Oct-07		18:07:53		71		30		16-Nov-07		18:25:59		75.81		49.5

		6-Oct-07		20:07:10		76.4		27.5		6-Oct-07		20:06:20		72.21		31.5		6-Oct-07		20:07:53		70.41		33.5		16-Nov-07		20:25:59		74.01		50

		6-Oct-07		22:07:10		75.81		27		6-Oct-07		22:06:20		73.4		31.5		6-Oct-07		22:07:53		70.41		33		16-Nov-07		22:25:59		73.4		51.5

		7-Oct-07		0:07:10		75.2		27		7-Oct-07		0:06:20		72.8		30.5		7-Oct-07		0:07:53		69.8		32.5		17-Nov-07		0:25:59		72.21		51

		7-Oct-07		2:07:10		74.6		27		7-Oct-07		2:06:20		72.21		31		7-Oct-07		2:07:53		68.61		33		17-Nov-07		2:25:59		71		51.5

		7-Oct-07		4:07:10		74.01		28		7-Oct-07		4:06:20		71.6		31.5		7-Oct-07		4:07:53		68		34		17-Nov-07		4:25:59		70.41		51.5

		7-Oct-07		6:07:10		72.8		28.5		7-Oct-07		6:06:20		71		32		7-Oct-07		6:07:53		66.81		35		17-Nov-07		6:25:59		70.41		52

		7-Oct-07		8:07:10		72.21		29		7-Oct-07		8:06:20		69.2		32.5		7-Oct-07		8:07:53		67.4		34		17-Nov-07		8:25:59		71		50.5

		7-Oct-07		10:07:10		71.6		31		7-Oct-07		10:06:20		68.61		34.5		7-Oct-07		10:07:53		68.61		35		17-Nov-07		10:25:59		71.6		50.5

		7-Oct-07		12:07:10		72.21		29		7-Oct-07		12:06:20		68.61		31		7-Oct-07		12:07:53		70.41		31.5		17-Nov-07		12:25:59		72.8		50

		7-Oct-07		14:07:10		72.8		26.5		7-Oct-07		14:06:20		69.2		28.5		7-Oct-07		14:07:53		70.41		29		17-Nov-07		14:25:59		75.2		49.5

		7-Oct-07		16:07:10		73.4		27		7-Oct-07		16:06:20		69.2		31		7-Oct-07		16:07:53		70.41		30.5		17-Nov-07		16:25:59		75.2		48

		7-Oct-07		18:07:10		74.01		26		7-Oct-07		18:06:20		69.8		29.5		7-Oct-07		18:07:53		71		29		17-Nov-07		18:25:59		74.6		49

		7-Oct-07		20:07:10		75.2		25		7-Oct-07		20:06:20		72.21		28.5		7-Oct-07		20:07:53		71		29		17-Nov-07		20:25:59		72.8		48.5

		7-Oct-07		22:07:10		75.2		26.5		7-Oct-07		22:06:20		72.8		31		7-Oct-07		22:07:53		70.41		31.5		17-Nov-07		22:25:59		72.21		49

		8-Oct-07		0:07:10		74.6		26.5		8-Oct-07		0:06:20		72.21		30.5		8-Oct-07		0:07:53		69.2		31.5		18-Nov-07		0:25:59		71		52

		8-Oct-07		2:07:10		73.4		25.5		8-Oct-07		2:06:20		71		29		8-Oct-07		2:07:53		68		31		18-Nov-07		2:25:59		70.41		51

		8-Oct-07		4:07:10		72.8		26		8-Oct-07		4:06:20		69.8		29		8-Oct-07		4:07:53		66.81		31.5		18-Nov-07		4:25:59		69.8		50.5

		8-Oct-07		6:07:10		71.6		26		8-Oct-07		6:06:20		69.2		29.5		8-Oct-07		6:07:53		65.6		32		18-Nov-07		6:25:59		69.2		51

		8-Oct-07		8:07:10		71		27		8-Oct-07		8:06:20		68.61		30		8-Oct-07		8:07:53		67.4		31		18-Nov-07		8:25:59		68.61		50.5

		8-Oct-07		10:07:10		71.6		28.5		8-Oct-07		10:06:20		68.61		32		8-Oct-07		10:07:53		68		32.5		18-Nov-07		10:25:59		68.61		51

		8-Oct-07		12:07:10		72.21		29.5		8-Oct-07		12:06:20		69.2		33		8-Oct-07		12:07:53		69.8		33		18-Nov-07		12:25:59		69.2		51.5

		8-Oct-07		14:07:10		72.8		31		8-Oct-07		14:06:20		69.2		34.5		8-Oct-07		14:07:53		70.41		34.5		18-Nov-07		14:25:59		69.8		52

		8-Oct-07		16:07:10		73.4		30.5		8-Oct-07		16:06:20		69.2		35.5		8-Oct-07		16:07:53		70.41		35.5		18-Nov-07		16:25:59		71.6		54

		8-Oct-07		18:07:10		74.01		31.5		8-Oct-07		18:06:20		69.2		35		8-Oct-07		18:07:53		71		34		18-Nov-07		18:25:59		72.21		54

		8-Oct-07		20:07:10		75.2		33.5		8-Oct-07		20:06:20		72.21		36		8-Oct-07		20:07:53		71.6		38.5		18-Nov-07		20:25:59		71		53

		8-Oct-07		22:07:10		75.2		34.5		8-Oct-07		22:06:20		72.21		39.5		8-Oct-07		22:07:53		71		40		18-Nov-07		22:25:59		69.8		53

		9-Oct-07		0:07:10		74.6		34		9-Oct-07		0:06:20		72.21		38.5		9-Oct-07		0:07:53		69.8		40		19-Nov-07		0:25:59		69.2		53

		9-Oct-07		2:07:10		74.01		33.5		9-Oct-07		2:06:20		71.6		37.5		9-Oct-07		2:07:53		68.61		40		19-Nov-07		2:25:59		69.2		53

		9-Oct-07		4:07:10		73.4		33		9-Oct-07		4:06:20		71		36.5		9-Oct-07		4:07:53		67.4		39.5		19-Nov-07		4:25:59		68.61		53

		9-Oct-07		6:07:10		73.4		32.5		9-Oct-07		6:06:20		69.8		36		9-Oct-07		6:07:53		68.61		37.5		19-Nov-07		6:25:59		68.61		53

		9-Oct-07		8:07:10		72.8		33.5		9-Oct-07		8:06:20		69.8		38.5		9-Oct-07		8:07:53		70.41		36		19-Nov-07		8:25:59		68		53

		9-Oct-07		10:07:10		73.4		37.5		9-Oct-07		10:06:20		71		45		9-Oct-07		10:07:53		71.6		37		19-Nov-07		10:25:59		68.61		53

		9-Oct-07		12:07:10		74.6		35.5		9-Oct-07		12:06:20		71		41		9-Oct-07		12:07:53		71.6		42		19-Nov-07		12:25:59		68.61		55

		9-Oct-07		14:07:10		74.6		36		9-Oct-07		14:06:20		71		41		9-Oct-07		14:07:53		71.6		38.5		19-Nov-07		14:25:59		69.8		56

		9-Oct-07		16:07:10		75.2		34		9-Oct-07		16:06:20		69.8		42		9-Oct-07		16:07:53		71.6		37		19-Nov-07		16:25:59		71		57.5

		9-Oct-07		18:07:10		74.01		36.5		9-Oct-07		18:06:20		69.2		44.5		9-Oct-07		18:07:53		71		41.5		19-Nov-07		18:25:59		71.6		56.5

		9-Oct-07		20:07:10		75.81		32		9-Oct-07		20:06:20		72.8		35.5		9-Oct-07		20:07:53		71		37.5		19-Nov-07		20:25:59		71		55

		9-Oct-07		22:07:10		76.4		33.5		9-Oct-07		22:06:20		73.4		38.5		9-Oct-07		22:07:53		71.6		39		19-Nov-07		22:25:59		70.41		54.5

		10-Oct-07		0:07:10		75.81		34.5		10-Oct-07		0:06:20		72.8		39.5		10-Oct-07		0:07:53		70.41		41		20-Nov-07		0:25:59		69.2		53.5

		10-Oct-07		2:07:10		75.2		35.5		10-Oct-07		2:06:20		72.21		40.5		10-Oct-07		2:07:53		69.8		42		20-Nov-07		2:25:59		68.61		52.5

		10-Oct-07		4:07:10		74.6		36		10-Oct-07		4:06:20		72.21		40.5		10-Oct-07		4:07:53		69.2		43		20-Nov-07		4:25:59		68		53

		10-Oct-07		6:07:10		74.6		37.5		10-Oct-07		6:06:20		71		44.5		10-Oct-07		6:07:53		69.2		45		20-Nov-07		6:25:59		68.61		54.5

		10-Oct-07		8:07:10		74.01		39		10-Oct-07		8:06:20		71		38.5		10-Oct-07		8:07:53		71.6		44		20-Nov-07		8:25:59		71.6		54

		10-Oct-07		10:07:10		74.01		43		10-Oct-07		10:06:20		69.8		48.5		10-Oct-07		10:07:53		71		44		20-Nov-07		10:25:59		74.01		55

		10-Oct-07		12:07:10		74.6		42.5		10-Oct-07		12:06:20		70.41		48.5		10-Oct-07		12:07:53		71.6		43		20-Nov-07		12:25:59		74.01		53.5

		10-Oct-07		14:07:10		74.6		44.5		10-Oct-07		14:06:20		71		50.5		10-Oct-07		14:07:53		71		51.5		20-Nov-07		14:25:59		73.4		48.5

		10-Oct-07		16:07:10		74.6		42		10-Oct-07		16:06:20		69.8		57		10-Oct-07		16:07:53		70.41		49		20-Nov-07		16:25:59		74.01		45

		10-Oct-07		18:07:10		74.01		41		10-Oct-07		18:06:20		69.8		51		10-Oct-07		18:07:53		70.41		48		20-Nov-07		18:25:59		74.01		43

		10-Oct-07		20:07:10		75.2		41		10-Oct-07		20:06:20		72.21		47		10-Oct-07		20:07:53		69.8		50		20-Nov-07		20:25:59		72.21		43

		10-Oct-07		22:07:10		75.2		43		10-Oct-07		22:06:20		72.21		50.5		10-Oct-07		22:07:53		69.8		50		20-Nov-07		22:25:59		71		44.5

		11-Oct-07		0:07:10		74.6		44		11-Oct-07		0:06:20		72.21		51		11-Oct-07		0:07:53		69.8		51		21-Nov-07		0:25:59		69.8		44

		11-Oct-07		2:07:10		74.6		44		11-Oct-07		2:06:20		71.6		50.5		11-Oct-07		2:07:53		69.2		51		21-Nov-07		2:25:59		68.61		43

		11-Oct-07		4:07:10		74.01		44		11-Oct-07		4:06:20		71.6		49.5		11-Oct-07		4:07:53		69.2		51.5		21-Nov-07		4:25:59		68		42.5

		11-Oct-07		6:07:10		74.01		44		11-Oct-07		6:06:20		71		50.5		11-Oct-07		6:07:53		69.2		51		21-Nov-07		6:25:59		68		41

		11-Oct-07		8:07:10		73.4		44.5		11-Oct-07		8:06:20		70.41		45		11-Oct-07		8:07:53		71		49		21-Nov-07		8:25:59		71.6		37

		11-Oct-07		10:07:10		73.4		43		11-Oct-07		10:06:20		71.6		45		11-Oct-07		10:07:53		71		48		21-Nov-07		10:25:59		71.6		38

		11-Oct-07		12:07:10		74.01		46		11-Oct-07		12:06:20		70.41		51		11-Oct-07		12:07:53		71.6		49		21-Nov-07		12:25:59		72.21		38.5

		11-Oct-07		14:07:10		74.6		41.5		11-Oct-07		14:06:20		71		41		11-Oct-07		14:07:53		71		49.5		21-Nov-07		14:25:59		72.8		37.5

		11-Oct-07		16:07:10		75.2		46.5		11-Oct-07		16:06:20		69.2		59.5		11-Oct-07		16:07:53		70.41		53		21-Nov-07		16:25:59		73.4		37

		11-Oct-07		18:07:10		74.6		39.5		11-Oct-07		18:06:20		69.8		45		11-Oct-07		18:07:53		70.41		47		21-Nov-07		18:25:59		73.4		38

		11-Oct-07		20:07:10		75.2		40		11-Oct-07		20:06:20		72.21		45		11-Oct-07		20:07:53		70.41		46		21-Nov-07		20:25:59		71.6		38

		11-Oct-07		22:07:10		74.6		39.5		11-Oct-07		22:06:20		72.21		44		11-Oct-07		22:07:53		69.8		45.5		21-Nov-07		22:25:59		69.8		38.5

		12-Oct-07		0:07:10		74.01		38.5		12-Oct-07		0:06:20		72.21		42.5		12-Oct-07		0:07:53		68.61		45		22-Nov-07		0:25:59		68.61		38.5

		12-Oct-07		2:07:10		73.4		38		12-Oct-07		2:06:20		71.6		42		12-Oct-07		2:07:53		67.4		45.5		22-Nov-07		2:25:59		67.4		37.5

		12-Oct-07		4:07:10		72.21		38.5		12-Oct-07		4:06:20		71		42.5		12-Oct-07		4:07:53		66.81		46.5		22-Nov-07		4:25:59		66.81		36.5

		12-Oct-07		6:07:10		72.21		38		12-Oct-07		6:06:20		70.41		41.5		12-Oct-07		6:07:53		68.61		44		22-Nov-07		6:25:59		67.4		35

		12-Oct-07		8:07:10		72.21		38		12-Oct-07		8:06:20		70.41		43.5		12-Oct-07		8:07:53		69.8		42		22-Nov-07		8:25:59		70.41		32.5

		12-Oct-07		10:07:10		72.8		43.5		12-Oct-07		10:06:20		71		51.5		12-Oct-07		10:07:53		71.6		40		22-Nov-07		10:25:59		71.6		33.5

		12-Oct-07		12:07:10		73.4		40.5		12-Oct-07		12:06:20		70.41		45.5		12-Oct-07		12:07:53		71.6		49		22-Nov-07		12:25:59		72.21		35

		12-Oct-07		14:07:10		73.4		43.5		12-Oct-07		14:06:20		69.8		41		12-Oct-07		14:07:53		71		44.5		22-Nov-07		14:25:59		73.4		34

		12-Oct-07		16:07:10		74.01		45		12-Oct-07		16:06:20		69.2		56.5		12-Oct-07		16:07:53		71		46.5		22-Nov-07		16:25:59		72.8		32.5

		12-Oct-07		18:07:10		74.01		39.5		12-Oct-07		18:06:20		69.8		46.5		12-Oct-07		18:07:53		70.41		44.5		22-Nov-07		18:25:59		72.8		34.5

		12-Oct-07		20:07:10		74.6		38.5		12-Oct-07		20:06:20		72.21		42		12-Oct-07		20:07:53		70.41		44		22-Nov-07		20:25:59		71		34

		12-Oct-07		22:07:10		75.2		37		12-Oct-07		22:06:20		72.8		40.5		12-Oct-07		22:07:53		69.8		43.5		22-Nov-07		22:25:59		69.2		35

		13-Oct-07		0:07:10		74.6		36.5		13-Oct-07		0:06:20		72.21		40		13-Oct-07		0:07:53		68.61		44		23-Nov-07		0:25:59		68		35

		13-Oct-07		2:07:10		74.01		38		13-Oct-07		2:06:20		72.21		42		13-Oct-07		2:07:53		68		46		23-Nov-07		2:25:59		66.81		34.5

		13-Oct-07		4:07:10		74.01		39.5		13-Oct-07		4:06:20		72.21		44		13-Oct-07		4:07:53		67.4		48.5		23-Nov-07		4:25:59		66.2		34

		13-Oct-07		6:07:10		73.4		40		13-Oct-07		6:06:20		71		46		13-Oct-07		6:07:53		68.61		48		23-Nov-07		6:25:59		66.81		32.5

		13-Oct-07		8:07:10		72.8		44		13-Oct-07		8:06:20		71		45		13-Oct-07		8:07:53		70.41		48.5		23-Nov-07		8:25:59		69.2		30.5

		13-Oct-07		10:07:10		72.8		44		13-Oct-07		10:06:20		71		43		13-Oct-07		10:07:53		71		50		23-Nov-07		10:25:59		71.6		31

		13-Oct-07		12:07:10		73.4		44		13-Oct-07		12:06:20		70.41		54.5		13-Oct-07		12:07:53		71.6		52		23-Nov-07		12:25:59		70.41		33

		13-Oct-07		14:07:10		73.4		46.5		13-Oct-07		14:06:20		70.41		51		13-Oct-07		14:07:53		71		50		23-Nov-07		14:25:59		71		33.5

		13-Oct-07		16:07:10		72.8		49.5		13-Oct-07		16:06:20		69.2		61		13-Oct-07		16:07:53		71		53		23-Nov-07		16:25:59		71		32.5

		13-Oct-07		18:07:10		72.8		44		13-Oct-07		18:06:20		69.8		50		13-Oct-07		18:07:53		70.41		50.5		23-Nov-07		18:25:59		71		34

		13-Oct-07		20:07:10		73.4		43.5		13-Oct-07		20:06:20		71		48		13-Oct-07		20:07:53		69.8		48.5		23-Nov-07		20:25:59		70.41		34.5

		13-Oct-07		22:07:10		73.4		42.5		13-Oct-07		22:06:20		71.6		46.5		13-Oct-07		22:07:53		68.61		49		23-Nov-07		22:25:59		68.61		34.5

		14-Oct-07		0:07:10		72.21		41.5		14-Oct-07		0:06:20		71		45		14-Oct-07		0:07:53		67.4		49		24-Nov-07		0:25:59		67.4		34.5

		14-Oct-07		2:07:10		71.6		40.5		14-Oct-07		2:06:20		69.8		43.5		14-Oct-07		2:07:53		66.2		48		24-Nov-07		2:25:59		66.81		34

		14-Oct-07		4:07:10		71		40		14-Oct-07		4:06:20		69.2		42.5		14-Oct-07		4:07:53		65.6		47.5		24-Nov-07		4:25:59		66.2		33.5

		14-Oct-07		6:07:10		70.41		39		14-Oct-07		6:06:20		68.61		41		14-Oct-07		6:07:53		65.6		46		24-Nov-07		6:25:59		66.81		32.5

		14-Oct-07		8:07:10		71		37.5		14-Oct-07		8:06:20		68.61		40.5		14-Oct-07		8:07:53		67.4		41.5		24-Nov-07		8:25:59		68.61		29.5

		14-Oct-07		10:07:10		71.6		43.5		14-Oct-07		10:06:20		68.61		49		14-Oct-07		10:07:53		68.61		48.5		24-Nov-07		10:25:59		70.41		25.5

		14-Oct-07		12:07:10		72.21		46		14-Oct-07		12:06:20		68.61		49.5		14-Oct-07		12:07:53		69.8		49.5		24-Nov-07		12:25:59		69.8		24

		14-Oct-07		14:07:10		72.8		47		14-Oct-07		14:06:20		69.2		54		14-Oct-07		14:07:53		70.41		50		24-Nov-07		14:25:59		70.41		23

		14-Oct-07		16:07:10		72.8		45.5		14-Oct-07		16:06:20		69.2		45.5		14-Oct-07		16:07:53		70.41		45.5		24-Nov-07		16:25:59		71.6		22.5

		14-Oct-07		18:07:10		73.4		46		14-Oct-07		18:06:20		69.2		53.5		14-Oct-07		18:07:53		70.41		52.5		24-Nov-07		18:25:59		71		22.5

		14-Oct-07		20:07:10		74.6		44.5		14-Oct-07		20:06:20		71.6		49		14-Oct-07		20:07:53		69.8		50.5		24-Nov-07		20:25:59		69.8		24.5

		14-Oct-07		22:07:10		74.01		43		14-Oct-07		22:06:20		72.21		47		14-Oct-07		22:07:53		69.2		50		24-Nov-07		22:25:59		68.61		27

		15-Oct-07		0:07:10		74.01		43		15-Oct-07		0:06:20		72.21		47		15-Oct-07		0:07:53		68.61		51.5		25-Nov-07		0:25:59		67.4		28

		15-Oct-07		2:07:10		74.01		43.5		15-Oct-07		2:06:20		72.21		47		15-Oct-07		2:07:53		68		52		25-Nov-07		2:25:59		66.81		28.5

		15-Oct-07		4:07:10		73.4		43.5		15-Oct-07		4:06:20		71.6		47		15-Oct-07		4:07:53		67.4		52		25-Nov-07		4:25:59		66.2		28.5

		15-Oct-07		6:07:10		72.8		43.5		15-Oct-07		6:06:20		71		43		15-Oct-07		6:07:53		66.81		52.5		25-Nov-07		6:25:59		65.6		28.5

		15-Oct-07		8:07:10		71.6		45		15-Oct-07		8:06:20		69.2		50		15-Oct-07		8:07:53		68.61		49.5		25-Nov-07		8:25:59		65.6		28

		15-Oct-07		10:07:10		71		46.5		15-Oct-07		10:06:20		68.61		52		15-Oct-07		10:07:53		68		52		25-Nov-07		10:25:59		65.6		29

		15-Oct-07		12:07:10		71		46		15-Oct-07		12:06:20		69.2		52		15-Oct-07		12:07:53		68		53		25-Nov-07		12:25:59		66.2		30.5

		15-Oct-07		14:07:10		71.6		48		15-Oct-07		14:06:20		69.2		45		15-Oct-07		14:07:53		69.2		53		25-Nov-07		14:25:59		68		30

		15-Oct-07		16:07:10		72.21		49.5		15-Oct-07		16:06:20		69.2		49.5		15-Oct-07		16:07:53		69.8		53.5		25-Nov-07		16:25:59		68		30.5

		15-Oct-07		18:07:10		72.8		48		15-Oct-07		18:06:20		69.2		54.5		15-Oct-07		18:07:53		69.8		53.5		25-Nov-07		18:25:59		68		31.5

		15-Oct-07		20:07:10		74.01		44		15-Oct-07		20:06:20		71.6		48		15-Oct-07		20:07:53		69.8		50		25-Nov-07		20:25:59		67.4		32

		15-Oct-07		22:07:10		73.4		42.5		15-Oct-07		22:06:20		71.6		45.5		15-Oct-07		22:07:53		68		50		25-Nov-07		22:25:59		66.81		33

		16-Oct-07		0:07:10		72.8		42		16-Oct-07		0:06:20		71		45.5		16-Oct-07		0:07:53		66.81		50.5		26-Nov-07		0:25:59		66.81		33.5

		16-Oct-07		2:07:10		72.21		42		16-Oct-07		2:06:20		71		45.5		16-Oct-07		2:07:53		66.2		51		26-Nov-07		2:25:59		66.2		33.5

		16-Oct-07		4:07:10		72.21		42.5		16-Oct-07		4:06:20		70.41		46		16-Oct-07		4:07:53		65.6		51.5		26-Nov-07		4:25:59		66.2		34

		16-Oct-07		6:07:10		72.21		43		16-Oct-07		6:06:20		70.41		46.5		16-Oct-07		6:07:53		68.61		48.5		26-Nov-07		6:25:59		66.2		34

		16-Oct-07		8:07:10		72.21		45.5		16-Oct-07		8:06:20		70.41		51.5		16-Oct-07		8:07:53		68.61		49.5		26-Nov-07		8:25:59		65.6		34.5

		16-Oct-07		10:07:10		72.8		45.5		16-Oct-07		10:06:20		71.6		54.5		16-Oct-07		10:07:53		71		49.5		26-Nov-07		10:25:59		65.6		35.5

		16-Oct-07		12:07:10		72.8		48.5		16-Oct-07		12:06:20		69.8		44.5		16-Oct-07		12:07:53		71.6		53		26-Nov-07		12:25:59		66.2		36.5

		16-Oct-07		14:07:10		72.8		53		16-Oct-07		14:06:20		71		54		16-Oct-07		14:07:53		71		57.5		26-Nov-07		14:25:59		66.2		35.5

		16-Oct-07		16:07:10		74.01		48.5		16-Oct-07		16:06:20		69.8		59.5		16-Oct-07		16:07:53		70.41		55.5		26-Nov-07		16:25:59		66.81		35

		16-Oct-07		18:07:10		73.4		47.5		16-Oct-07		18:06:20		70.41		57.5		16-Oct-07		18:07:53		69.8		54.5		26-Nov-07		18:25:59		67.4		35.5

		16-Oct-07		20:07:10		74.6		48		16-Oct-07		20:06:20		72.21		53		16-Oct-07		20:07:53		70.41		54.5		26-Nov-07		20:25:59		66.81		36

		16-Oct-07		22:07:10		74.6		47		16-Oct-07		22:06:20		72.21		51		16-Oct-07		22:07:53		69.8		54		26-Nov-07		22:25:59		66.2		35.5

		17-Oct-07		0:07:10		74.01		45		17-Oct-07		0:06:20		72.8		48.5		17-Oct-07		0:07:53		69.2		52.5		27-Nov-07		0:25:59		65.6		35.5

		17-Oct-07		2:07:10		73.4		43		17-Oct-07		2:06:20		71.6		45.5		17-Oct-07		2:07:53		68		51		27-Nov-07		2:25:59		65.6		34.5

		17-Oct-07		4:07:10		72.8		42.5		17-Oct-07		4:06:20		71		45		17-Oct-07		4:07:53		66.81		50.5		27-Nov-07		4:25:59		65.01		34

		17-Oct-07		6:07:10		72.8		43		17-Oct-07		6:06:20		70.41		44.5		17-Oct-07		6:07:53		68		49		27-Nov-07		6:25:59		66.2		32.5

		17-Oct-07		8:07:10		71.6		43.5		17-Oct-07		8:06:20		69.8		48		17-Oct-07		8:07:53		69.8		46		27-Nov-07		8:25:59		68.61		30.5

		17-Oct-07		10:07:10		72.8		43.5		17-Oct-07		10:06:20		71		52.5		17-Oct-07		10:07:53		71		46		27-Nov-07		10:25:59		70.41		32.5

		17-Oct-07		12:07:10		73.4		46		17-Oct-07		12:06:20		71		55.5		17-Oct-07		12:07:53		71.6		46		27-Nov-07		12:25:59		72.21		33.5

		17-Oct-07		14:07:10		73.4		47		17-Oct-07		14:06:20		71		41		17-Oct-07		14:07:53		71		52.5		27-Nov-07		14:25:59		72.8		34.5

		17-Oct-07		16:07:10		72.8		53		17-Oct-07		16:06:20		69.2		55.5		17-Oct-07		16:07:53		70.41		60.5		27-Nov-07		16:25:59		73.4		35.5

		17-Oct-07		18:07:10		72.8		52		17-Oct-07		18:06:20		69.2		60		17-Oct-07		18:07:53		69.8		55.5		27-Nov-07		18:25:59		72.8		37

		17-Oct-07		20:07:10		72.8		46.5		17-Oct-07		20:06:20		71		49.5		17-Oct-07		20:07:53		69.8		51.5		27-Nov-07		20:25:59		71		37

		17-Oct-07		22:07:10		72.21		44		17-Oct-07		22:06:20		71		46.5		17-Oct-07		22:07:53		68		49.5		27-Nov-07		22:25:59		69.8		36.5

		18-Oct-07		0:07:10		71		42		18-Oct-07		0:06:20		69.8		44		18-Oct-07		0:07:53		66.81		48.5		28-Nov-07		0:25:59		68.61		36.5

		18-Oct-07		2:07:10		70.41		41		18-Oct-07		2:06:20		69.2		43		18-Oct-07		2:07:53		66.2		47.5		28-Nov-07		2:25:59		67.4		36.5

		18-Oct-07		4:07:10		70.41		41.5		18-Oct-07		4:06:20		69.2		44		18-Oct-07		4:07:53		66.2		48.5		28-Nov-07		4:25:59		66.81		36.5

		18-Oct-07		6:07:10		71		43.5		18-Oct-07		6:06:20		69.8		46		18-Oct-07		6:07:53		68		48		28-Nov-07		6:25:59		67.4		36

		18-Oct-07		8:07:10		71.6		44.5		18-Oct-07		8:06:20		71		49.5		18-Oct-07		8:07:53		69.8		46		28-Nov-07		8:25:59		69.8		35

		18-Oct-07		10:07:10		74.01		45.5		18-Oct-07		10:06:20		74.01		41.5		18-Oct-07		10:07:53		71		51.5		28-Nov-07		10:25:59		73.4		36

		18-Oct-07		12:07:10		74.6		44		18-Oct-07		12:06:20		73.4		46.5		18-Oct-07		12:07:53		71.6		50.5		28-Nov-07		12:25:59		72.8		38.5

		18-Oct-07		14:07:10		75.2		41.5		18-Oct-07		14:06:20		74.6		37.5		18-Oct-07		14:07:53		71.6		45		28-Nov-07		14:25:59		73.4		35

		18-Oct-07		16:07:10		75.2		41		18-Oct-07		16:06:20		72.21		41.5		18-Oct-07		16:07:53		70.41		47		28-Nov-07		16:25:59		74.01		34

		18-Oct-07		18:07:10		74.6		41.5		18-Oct-07		18:06:20		71.6		42.5		18-Oct-07		18:07:53		70.41		48.5		28-Nov-07		18:25:59		74.01		35.5

		18-Oct-07		20:07:10		74.6		41		18-Oct-07		20:06:20		72.8		44		18-Oct-07		20:07:53		69.8		47		28-Nov-07		20:25:59		72.21		37

		18-Oct-07		22:07:10		73.4		40.5		18-Oct-07		22:06:20		72.21		43		18-Oct-07		22:07:53		68.61		47.5		28-Nov-07		22:25:59		71		37

		19-Oct-07		0:07:10		72.8		41		19-Oct-07		0:06:20		72.21		43.5		19-Oct-07		0:07:53		67.4		48.5		29-Nov-07		0:25:59		69.8		37

		19-Oct-07		2:07:10		72.21		41.5		19-Oct-07		2:06:20		71		43.5		19-Oct-07		2:07:53		66.81		49.5		29-Nov-07		2:25:59		68.61		37

		19-Oct-07		4:07:10		71.6		42.5		19-Oct-07		4:06:20		71		44.5		19-Oct-07		4:07:53		66.2		52		29-Nov-07		4:25:59		67.4		36.5

		19-Oct-07		6:07:10		71.6		43		19-Oct-07		6:06:20		71		45.5		19-Oct-07		6:07:53		68		49		29-Nov-07		6:25:59		67.4		34.5

		19-Oct-07		8:07:10		72.21		44		19-Oct-07		8:06:20		72.21		47		19-Oct-07		8:07:53		69.2		48		29-Nov-07		8:25:59		69.8		32

		19-Oct-07		10:07:10		72.8		43.5		19-Oct-07		10:06:20		72.21		40		19-Oct-07		10:07:53		71		49.5		29-Nov-07		10:25:59		72.21		33

		19-Oct-07		12:07:10		74.01		44.5		19-Oct-07		12:06:20		72.21		49.5		19-Oct-07		12:07:53		71.6		51		29-Nov-07		12:25:59		72.21		33

		19-Oct-07		14:07:10		75.2		47		19-Oct-07		14:06:20		72.8		47		19-Oct-07		14:07:53		71		54		29-Nov-07		14:25:59		73.4		32.5

		19-Oct-07		16:07:10		74.6		47		19-Oct-07		16:06:20		71.6		45.5		19-Oct-07		16:07:53		71		48		29-Nov-07		16:25:59		73.4		32

		19-Oct-07		18:07:10		74.6		51.5		19-Oct-07		18:06:20		71		56.5		19-Oct-07		18:07:53		70.41		58.5		29-Nov-07		18:25:59		72.8		30.5

		19-Oct-07		20:07:10		74.6		51.5		19-Oct-07		20:06:20		72.8		57		19-Oct-07		20:07:53		70.41		58		29-Nov-07		20:25:59		71		32

		19-Oct-07		22:07:10		74.01		52.5		19-Oct-07		22:06:20		73.4		56		19-Oct-07		22:07:53		70.41		59		29-Nov-07		22:25:59		69.8		32.5

		20-Oct-07		0:07:10		74.01		53		20-Oct-07		0:06:20		72.8		57.5		20-Oct-07		0:07:53		70.41		60.5		30-Nov-07		0:25:59		69.2		33

		20-Oct-07		2:07:10		73.4		55.5		20-Oct-07		2:06:20		72.8		59		20-Oct-07		2:07:53		69.8		61.5		30-Nov-07		2:25:59		68		32.5

		20-Oct-07		4:07:10		73.4		56		20-Oct-07		4:06:20		72.8		59.5		20-Oct-07		4:07:53		69.8		62		30-Nov-07		4:25:59		67.4		32.5

		20-Oct-07		6:07:10		74.01		56		20-Oct-07		6:06:20		72.8		59		20-Oct-07		6:07:53		70.41		65		30-Nov-07		6:25:59		67.4		31.5

		20-Oct-07		8:07:10		73.4		52.5		20-Oct-07		8:06:20		71		55		20-Oct-07		8:07:53		71		63.5		30-Nov-07		8:25:59		69.2		29.5

		20-Oct-07		10:07:10		73.4		54.5		20-Oct-07		10:06:20		71		54		20-Oct-07		10:07:53		71.6		63.5		30-Nov-07		10:25:59		72.21		31.5

		20-Oct-07		12:07:10		74.6		53		20-Oct-07		12:06:20		71		59.5		20-Oct-07		12:07:53		71.6		58		30-Nov-07		12:25:59		71.6		33

		20-Oct-07		14:07:10		75.2		54.5		20-Oct-07		14:06:20		71		48.5		20-Oct-07		14:07:53		71		62		30-Nov-07		14:25:59		74.01		31.5

		20-Oct-07		16:07:10		74.6		56.5		20-Oct-07		16:06:20		69.8		67		20-Oct-07		16:07:53		70.41		70		30-Nov-07		16:25:59		74.6		30.5

		20-Oct-07		18:07:10		73.4		57.5		20-Oct-07		18:06:20		69.2		61		20-Oct-07		18:07:53		70.41		59.5		30-Nov-07		18:25:59		74.01		29

		20-Oct-07		20:07:10		74.6		53.5		20-Oct-07		20:06:20		72.21		58		20-Oct-07		20:07:53		69.8		61.5		30-Nov-07		20:25:59		72.8		27.5

		20-Oct-07		22:07:10		74.01		49		20-Oct-07		22:06:20		72.21		51.5		20-Oct-07		22:07:53		69.2		56.5		30-Nov-07		22:25:59		71		30

		21-Oct-07		0:07:10		73.4		45		21-Oct-07		0:06:20		71.6		46.5		21-Oct-07		0:07:53		68		53		1-Dec-07		0:25:59		69.2		31

		21-Oct-07		2:07:10		72.21		44.5		21-Oct-07		2:06:20		71		47		21-Oct-07		2:07:53		66.81		53.5		1-Dec-07		2:25:59		68		31

		21-Oct-07		4:07:10		71.6		45		21-Oct-07		4:06:20		71		47		21-Oct-07		4:07:53		66.2		54		1-Dec-07		4:25:59		67.4		31

		21-Oct-07		6:07:10		71		43		21-Oct-07		6:06:20		70.41		45		21-Oct-07		6:07:53		65.6		52		1-Dec-07		6:25:59		68		29.5

		21-Oct-07		8:07:10		70.41		42		21-Oct-07		8:06:20		68.61		44		21-Oct-07		8:07:53		68		46		1-Dec-07		8:25:59		71		28

		21-Oct-07		10:07:10		70.41		45		21-Oct-07		10:06:20		69.2		50		21-Oct-07		10:07:53		67.4		52		1-Dec-07		10:25:59		72.8		28

		21-Oct-07		12:07:10		71		41.5		21-Oct-07		12:06:20		68.61		42.5		21-Oct-07		12:07:53		69.2		45		1-Dec-07		12:25:59		74.01		26.5

		21-Oct-07		14:07:10		71		37.5		21-Oct-07		14:06:20		69.2		37		21-Oct-07		14:07:53		69.2		40.5		1-Dec-07		14:25:59		74.01		27

		21-Oct-07		16:07:10		71		36		21-Oct-07		16:06:20		68.61		38		21-Oct-07		16:07:53		69.2		38		1-Dec-07		16:25:59		74.6		26

		21-Oct-07		18:07:10		71.6		35		21-Oct-07		18:06:20		68.61		37		21-Oct-07		18:07:53		69.8		37		1-Dec-07		18:25:59		75.2		26.5

		21-Oct-07		20:07:10		72.21		35.5		21-Oct-07		20:06:20		70.41		38		21-Oct-07		20:07:53		68.61		40		1-Dec-07		20:25:59		74.01		25

		21-Oct-07		22:07:10		72.21		36		21-Oct-07		22:06:20		71		38		21-Oct-07		22:07:53		67.4		42		1-Dec-07		22:25:59		70.41		27

		22-Oct-07		0:07:10		71.6		36		22-Oct-07		0:06:20		70.41		38		22-Oct-07		0:07:53		66.2		42.5		2-Dec-07		0:25:59		68.61		28

		22-Oct-07		2:07:10		71		35.5		22-Oct-07		2:06:20		69.8		37.5		22-Oct-07		2:07:53		65.01		43		2-Dec-07		2:25:59		67.4		27.5

		22-Oct-07		4:07:10		70.41		35.5		22-Oct-07		4:06:20		69.8		37		22-Oct-07		4:07:53		64.4		43		2-Dec-07		4:25:59		66.2		27.5

		22-Oct-07		6:07:10		69.8		34.5		22-Oct-07		6:06:20		69.2		36.5		22-Oct-07		6:07:53		63.8		42.5		2-Dec-07		6:25:59		66.2		27

		22-Oct-07		8:07:10		69.2		34.5		22-Oct-07		8:06:20		68.61		36.5		22-Oct-07		8:07:53		68		37.5		2-Dec-07		8:25:59		66.2		26

		22-Oct-07		10:07:10		69.8		33.5		22-Oct-07		10:06:20		68.61		35		22-Oct-07		10:07:53		67.4		37.5		2-Dec-07		10:25:59		66.2		26.5

		22-Oct-07		12:07:10		69.8		33		22-Oct-07		12:06:20		68.61		34		22-Oct-07		12:07:53		68.61		35.5		2-Dec-07		12:25:59		66.81		29

		22-Oct-07		14:07:10		71		31		22-Oct-07		14:06:20		68.61		32		22-Oct-07		14:07:53		69.8		34		2-Dec-07		14:25:59		67.4		29.5

		22-Oct-07		16:07:10		72.21		30.5		22-Oct-07		16:06:20		68.61		31		22-Oct-07		16:07:53		70.41		33.5		2-Dec-07		16:25:59		68		30

		22-Oct-07		18:07:10		72.21		30.5		22-Oct-07		18:06:20		69.2		32.5		22-Oct-07		18:07:53		70.41		33.5		2-Dec-07		18:25:59		67.4		30

		22-Oct-07		20:07:10		74.01		28		22-Oct-07		20:06:20		72.21		29.5		22-Oct-07		20:07:53		71.6		31		2-Dec-07		20:25:59		66.81		31

		22-Oct-07		22:07:10		74.01		32		22-Oct-07		22:06:20		72.8		35		22-Oct-07		22:07:53		71		36.5		2-Dec-07		22:25:59		66.2		31

		23-Oct-07		0:07:10		73.4		33		23-Oct-07		0:06:20		72.21		36		23-Oct-07		0:07:53		69.2		38		3-Dec-07		0:25:59		66.2		30.5

		23-Oct-07		2:07:10		72.8		33.5		23-Oct-07		2:06:20		71.6		36.5		23-Oct-07		2:07:53		68.61		39		3-Dec-07		2:25:59		66.2		31

		23-Oct-07		4:07:10		72.21		34		23-Oct-07		4:06:20		71		36.5		23-Oct-07		4:07:53		66.81		40		3-Dec-07		4:25:59		66.2		32.5

		23-Oct-07		6:07:10		71.6		34.5		23-Oct-07		6:06:20		69.8		36.5		23-Oct-07		6:07:53		68		39.5		3-Dec-07		6:25:59		66.2		34.5

		23-Oct-07		8:07:10		71.6		35.5		23-Oct-07		8:06:20		69.8		38.5		23-Oct-07		8:07:53		69.2		38		3-Dec-07		8:25:59		66.2		35.5

		23-Oct-07		10:07:10		72.21		37.5		23-Oct-07		10:06:20		70.41		43.5		23-Oct-07		10:07:53		70.41		42		3-Dec-07		10:25:59		66.81		35.5

		23-Oct-07		12:07:10		72.8		35		23-Oct-07		12:06:20		70.41		36.5		23-Oct-07		12:07:53		71.6		34.5		3-Dec-07		12:25:59		67.4		36.5

		23-Oct-07		14:07:10		74.6		38.5		23-Oct-07		14:06:20		69.8		45		23-Oct-07		14:07:53		71.6		41		3-Dec-07		14:25:59		67.4		37.5

		23-Oct-07		16:07:10		75.81		35		23-Oct-07		16:06:20		71		41.5		23-Oct-07		16:07:53		71.6		42.5		3-Dec-07		16:25:59		68		39

		23-Oct-07		18:07:10		75.2		34		23-Oct-07		18:06:20		71.6		36		23-Oct-07		18:07:53		71		36		3-Dec-07		18:25:59		68		39.5

		23-Oct-07		20:07:10		75.81		34.5		23-Oct-07		20:06:20		72.8		38		23-Oct-07		20:07:53		70.41		40.5		3-Dec-07		20:25:59		68		40

		23-Oct-07		22:07:10		75.2		36		23-Oct-07		22:06:20		72.21		40		23-Oct-07		22:07:53		71.6		40.5		3-Dec-07		22:25:59		68		42

		24-Oct-07		0:07:10		74.6		36.5		24-Oct-07		0:06:20		72.21		40.5		24-Oct-07		0:07:53		71		42		4-Dec-07		0:25:59		68		42

		24-Oct-07		2:07:10		74.01		36.5		24-Oct-07		2:06:20		72.21		40		24-Oct-07		2:07:53		69.2		42.5		4-Dec-07		2:25:59		68		41.5

		24-Oct-07		4:07:10		73.4		36.5		24-Oct-07		4:06:20		72.21		39		24-Oct-07		4:07:53		68.61		42.5		4-Dec-07		4:25:59		67.4		41.5

		24-Oct-07		6:07:10		73.4		35.5		24-Oct-07		6:06:20		72.21		38		24-Oct-07		6:07:53		68		42.5		4-Dec-07		6:25:59		68.61		41

		24-Oct-07		8:07:10		73.4		36		24-Oct-07		8:06:20		71.6		40		24-Oct-07		8:07:53		69.8		40		4-Dec-07		8:25:59		72.8		37

		24-Oct-07		10:07:10		75.2		39		24-Oct-07		10:06:20		72.21		40.5		24-Oct-07		10:07:53		71.6		46.5		4-Dec-07		10:25:59		74.6		38

		24-Oct-07		12:07:10		75.81		39.5		24-Oct-07		12:06:20		72.21		38		24-Oct-07		12:07:53		71.6		49		4-Dec-07		12:25:59		75.2		36

		24-Oct-07		14:07:10		75.81		39		24-Oct-07		14:06:20		72.8		46.5		24-Oct-07		14:07:53		71.6		49		4-Dec-07		14:25:59		74.6		37

		24-Oct-07		16:07:10		76.4		40		24-Oct-07		16:06:20		71.6		50		24-Oct-07		16:07:53		71.6		45		4-Dec-07		16:25:59		74.6		38

		24-Oct-07		18:07:10		74.6		41		24-Oct-07		18:06:20		69.8		42		24-Oct-07		18:07:53		71		53.5		4-Dec-07		18:25:59		74.6		39

		24-Oct-07		20:07:10		75.81		43.5		24-Oct-07		20:06:20		73.4		48.5		24-Oct-07		20:07:53		70.41		55.5		4-Dec-07		20:25:59		74.01		39.5

		24-Oct-07		22:07:10		75.81		43.5		24-Oct-07		22:06:20		72.8		48		24-Oct-07		22:07:53		72.8		48		4-Dec-07		22:25:59		72.8		41

		25-Oct-07		0:07:10		75.2		41.5		25-Oct-07		0:06:20		72.8		45.5		25-Oct-07		0:07:53		72.21		46		5-Dec-07		0:25:59		71.6		44.5

		25-Oct-07		2:07:10		74.6		40		25-Oct-07		2:06:20		72.8		43.5		25-Oct-07		2:07:53		71.6		45		5-Dec-07		2:25:59		70.41		45

		25-Oct-07		4:07:10		74.01		39		25-Oct-07		4:06:20		72.8		41.5		25-Oct-07		4:07:53		69.8		44		5-Dec-07		4:25:59		69.8		45.5

		25-Oct-07		6:07:10		73.4		39		25-Oct-07		6:06:20		71.6		42		25-Oct-07		6:07:53		69.2		45		5-Dec-07		6:25:59		70.41		50

		25-Oct-07		8:07:10		72.8		39.5		25-Oct-07		8:06:20		71		45.5		25-Oct-07		8:07:53		71		42.5		5-Dec-07		8:25:59		74.6		47

		25-Oct-07		10:07:10		72.8		43.5		25-Oct-07		10:06:20		70.41		52.5		25-Oct-07		10:07:53		71.6		49.5		5-Dec-07		10:25:59		75.81		48

		25-Oct-07		12:07:10		73.4		43.5		25-Oct-07		12:06:20		70.41		52		25-Oct-07		12:07:53		71.6		44		5-Dec-07		12:25:59		75.2		50

		25-Oct-07		14:07:10		74.01		42		25-Oct-07		14:06:20		71		39.5		25-Oct-07		14:07:53		71.6		47		5-Dec-07		14:25:59		74.6		51.5

		25-Oct-07		16:07:10		74.6		46		25-Oct-07		16:06:20		69.8		54		25-Oct-07		16:07:53		71.6		50.5		5-Dec-07		16:25:59		74.6		50

		25-Oct-07		18:07:10		74.6		47		25-Oct-07		18:06:20		69.2		56.5		25-Oct-07		18:07:53		71		48.5		5-Dec-07		18:25:59		74.6		49.5

		25-Oct-07		20:07:10		75.81		42		25-Oct-07		20:06:20		72.8		46.5		25-Oct-07		20:07:53		72.8		46.5		5-Dec-07		20:25:59		74.6		48.5

		25-Oct-07		22:07:10		75.2		40.5		25-Oct-07		22:06:20		72.8		43.5		25-Oct-07		22:07:53		72.8		44.5		5-Dec-07		22:25:59		72.8		50

		26-Oct-07		0:07:10		74.6		39.5		26-Oct-07		0:06:20		72.8		43.5		26-Oct-07		0:07:53		71.6		44		6-Dec-07		0:25:59		72.21		51.5

		26-Oct-07		2:07:10		74.01		39		26-Oct-07		2:06:20		72.21		42		26-Oct-07		2:07:53		69.8		44		6-Dec-07		2:25:59		71		51.5

		26-Oct-07		4:07:10		72.8		38		26-Oct-07		4:06:20		71		40.5		26-Oct-07		4:07:53		68.61		43.5		6-Dec-07		4:25:59		70.41		52

		26-Oct-07		6:07:10		72.8		37.5		26-Oct-07		6:06:20		70.41		39.5		26-Oct-07		6:07:53		68		43.5		6-Dec-07		6:25:59		70.41		52

		26-Oct-07		8:07:10		72.21		38		26-Oct-07		8:06:20		69.8		42.5		26-Oct-07		8:07:53		69.2		40.5		6-Dec-07		8:25:59		74.6		46.5

		26-Oct-07		10:07:10		72.8		38.5		26-Oct-07		10:06:20		71		40		26-Oct-07		10:07:53		71		47.5		6-Dec-07		10:25:59		75.81		45

		26-Oct-07		12:07:10		73.4		44.5		26-Oct-07		12:06:20		70.41		50.5		26-Oct-07		12:07:53		71.6		44.5		6-Dec-07		12:25:59		75.2		47

		26-Oct-07		14:07:10		74.6		40		26-Oct-07		14:06:20		71		39.5		26-Oct-07		14:07:53		71.6		48.5		6-Dec-07		14:25:59		74.6		49

		26-Oct-07		16:07:10		74.6		47		26-Oct-07		16:06:20		69.8		58.5		26-Oct-07		16:07:53		71		56		6-Dec-07		16:25:59		74.6		47

		26-Oct-07		18:07:10		74.01		47.5		26-Oct-07		18:06:20		69.2		56		26-Oct-07		18:07:53		70.41		52.5		6-Dec-07		18:25:59		74.6		40.5

		26-Oct-07		20:07:10		74.6		41.5		26-Oct-07		20:06:20		71		47.5		26-Oct-07		20:07:53		71		47.5		6-Dec-07		20:25:59		74.01		39.5

		26-Oct-07		22:07:10		74.01		40.5		26-Oct-07		22:06:20		71		40.5		26-Oct-07		22:07:53		70.41		45.5		6-Dec-07		22:25:59		72.21		42

		27-Oct-07		0:07:10		73.4		40.5		27-Oct-07		0:06:20		71.6		44.5		27-Oct-07		0:07:53		69.2		46		7-Dec-07		0:25:59		71		44

		27-Oct-07		2:07:10		72.8		41.5		27-Oct-07		2:06:20		70.41		46.5		27-Oct-07		2:07:53		68		48		7-Dec-07		2:25:59		70.41		43.5

		27-Oct-07		4:07:10		72.21		42		27-Oct-07		4:06:20		70.41		46		27-Oct-07		4:07:53		68		48.5		7-Dec-07		4:25:59		70.41		44

		27-Oct-07		6:07:10		72.8		42		27-Oct-07		6:06:20		71		45.5		27-Oct-07		6:07:53		68		49		7-Dec-07		6:25:59		70.41		44.5

		27-Oct-07		8:07:10		72.21		41		27-Oct-07		8:06:20		71		45.5		27-Oct-07		8:07:53		71		46.5		7-Dec-07		8:25:59		74.6		41

		27-Oct-07		10:07:10		72.8		45		27-Oct-07		10:06:20		71		45.5		27-Oct-07		10:07:53		71		37.5		7-Dec-07		10:25:59		74.6		42

		27-Oct-07		12:07:10		73.4		45		27-Oct-07		12:06:20		70.41		53.5		27-Oct-07		12:07:53		71		52.5		7-Dec-07		12:25:59		72.8		45.5

		27-Oct-07		14:07:10		73.4		42.5		27-Oct-07		14:06:20		71		47.5		27-Oct-07		14:07:53		71		51		7-Dec-07		14:25:59		72.8		46.5

		27-Oct-07		16:07:10		73.4		46		27-Oct-07		16:06:20		68.61		46		27-Oct-07		16:07:53		71		46.5		7-Dec-07		16:25:59		72.8		47.5

		27-Oct-07		18:07:10		73.4		44.5		27-Oct-07		18:06:20		68		46.5		27-Oct-07		18:07:53		69.8		49.5		7-Dec-07		18:25:59		72.8		46

		27-Oct-07		20:07:10		72.8		42		27-Oct-07		20:06:20		69.2		47.5		27-Oct-07		20:07:53		69.8		46.5		7-Dec-07		20:25:59		72.21		46

		27-Oct-07		22:07:10		72.21		41.5		27-Oct-07		22:06:20		69.2		46		27-Oct-07		22:07:53		68.61		46		7-Dec-07		22:25:59		69.8		47.5

		28-Oct-07		0:07:10		71.6		40		28-Oct-07		0:06:20		68.61		44.5		28-Oct-07		0:07:53		67.4		45		8-Dec-07		0:25:59		68.61		48

		28-Oct-07		2:07:10		71		39		28-Oct-07		2:06:20		68.61		43		28-Oct-07		2:07:53		66.2		45		8-Dec-07		2:25:59		68		47

		28-Oct-07		4:07:10		70.41		38.5		28-Oct-07		4:06:20		68.61		41.5		28-Oct-07		4:07:53		65.01		45.5		8-Dec-07		4:25:59		67.4		46.5

		28-Oct-07		6:07:10		69.8		38		28-Oct-07		6:06:20		68		41.5		28-Oct-07		6:07:53		63.8		46		8-Dec-07		6:25:59		68		45.5

		28-Oct-07		8:07:10		69.2		39.5		28-Oct-07		8:06:20		68		43.5		28-Oct-07		8:07:53		66.81		43.5		8-Dec-07		8:25:59		71.6		40

		28-Oct-07		10:07:10		69.2		42		28-Oct-07		10:06:20		68		47		28-Oct-07		10:07:53		66.81		46.5		8-Dec-07		10:25:59		72.21		39.5

		28-Oct-07		12:07:10		69.2		44.5		28-Oct-07		12:06:20		67.4		50		28-Oct-07		12:07:53		67.4		48		8-Dec-07		12:25:59		71.6		40

		28-Oct-07		14:07:10		69.8		47		28-Oct-07		14:06:20		67.4		53		28-Oct-07		14:07:53		68.61		50		8-Dec-07		14:25:59		72.21		39.5

		28-Oct-07		16:07:10		70.41		49.5		28-Oct-07		16:06:20		67.4		49		28-Oct-07		16:07:53		69.2		52		8-Dec-07		16:25:59		72.21		38

		28-Oct-07		18:07:10		71		43		28-Oct-07		18:06:20		68		46.5		28-Oct-07		18:07:53		69.2		47.5		8-Dec-07		18:25:59		71.6		37.5

		28-Oct-07		20:07:10		71		43.5		28-Oct-07		20:06:20		68.61		47		28-Oct-07		20:07:53		68.61		47		8-Dec-07		20:25:59		70.41		36.5

		28-Oct-07		22:07:10		71		41		28-Oct-07		22:06:20		69.2		44.5		28-Oct-07		22:07:53		67.4		46.5		8-Dec-07		22:25:59		69.8		36.5

		29-Oct-07		0:07:10		70.41		41.5		29-Oct-07		0:06:20		68.61		44.5		29-Oct-07		0:07:53		66.2		47		9-Dec-07		0:25:59		68		37

		29-Oct-07		2:07:10		70.41		41.5		29-Oct-07		2:06:20		68.61		44.5		29-Oct-07		2:07:53		65.6		48		9-Dec-07		2:25:59		66.81		37

		29-Oct-07		4:07:10		69.8		40.5		29-Oct-07		4:06:20		68		44		29-Oct-07		4:07:53		65.01		48		9-Dec-07		4:25:59		66.2		36.5

		29-Oct-07		6:07:10		69.8		40.5		29-Oct-07		6:06:20		68		43.5		29-Oct-07		6:07:53		64.4		48		9-Dec-07		6:25:59		66.2		36

		29-Oct-07		8:07:10		69.2		40		29-Oct-07		8:06:20		68		43		29-Oct-07		8:07:53		67.4		43.5		9-Dec-07		8:25:59		66.2		35.5

		29-Oct-07		10:07:10		69.2		43.5		29-Oct-07		10:06:20		68		49.5		29-Oct-07		10:07:53		67.4		48		9-Dec-07		10:25:59		66.2		34

		29-Oct-07		12:07:10		69.8		47.5		29-Oct-07		12:06:20		68		53.5		29-Oct-07		12:07:53		69.2		50		9-Dec-07		12:25:59		66.2		34

		29-Oct-07		14:07:10		71		48.5		29-Oct-07		14:06:20		68		48.5		29-Oct-07		14:07:53		69.8		54.5		9-Dec-07		14:25:59		66.81		33.5

		29-Oct-07		16:07:10		71.6		48.5		29-Oct-07		16:06:20		68.61		55		29-Oct-07		16:07:53		70.41		45.5		9-Dec-07		16:25:59		66.81		33

		29-Oct-07		18:07:10		72.21		50.5		29-Oct-07		18:06:20		68.61		62.5		29-Oct-07		18:07:53		70.41		55.5		9-Dec-07		18:25:59		66.81		31

		29-Oct-07		20:07:10		72.8		48.5		29-Oct-07		20:06:20		69.2		46		29-Oct-07		20:07:53		71.6		50		9-Dec-07		20:25:59		65.6		30.5

		29-Oct-07		22:07:10		72.21		46		29-Oct-07		22:06:20		69.2		51.5		29-Oct-07		22:07:53		70.41		48.5		9-Dec-07		22:25:59		65.01		31.5

		30-Oct-07		0:07:10		71.6		45		30-Oct-07		0:06:20		68.61		50.5		30-Oct-07		0:07:53		69.2		48		10-Dec-07		0:25:59		64.4		31

		30-Oct-07		2:07:10		71.6		44.5		30-Oct-07		2:06:20		68.61		46.5		30-Oct-07		2:07:53		68.61		48.5		10-Dec-07		2:25:59		63.8		31

		30-Oct-07		4:07:10		71		43.5		30-Oct-07		4:06:20		69.2		48		30-Oct-07		4:07:53		67.4		49		10-Dec-07		4:25:59		63.21		31

		30-Oct-07		6:07:10		71.6		43.5		30-Oct-07		6:06:20		69.2		46.5		30-Oct-07		6:07:53		68		49		10-Dec-07		6:25:59		62.6		31

		30-Oct-07		8:07:10		71		46		30-Oct-07		8:06:20		68.61		44.5		30-Oct-07		8:07:53		69.2		47.5		10-Dec-07		8:25:59		63.21		31

		30-Oct-07		10:07:10		72.21		46		30-Oct-07		10:06:20		69.2		55.5		30-Oct-07		10:07:53		71.6		47.5		10-Dec-07		10:25:59		64.4		31

		30-Oct-07		12:07:10		72.21		49		30-Oct-07		12:06:20		69.8		56		30-Oct-07		12:07:53		71		49		10-Dec-07		12:25:59		65.6		31.5

		30-Oct-07		14:07:10		73.4		47		30-Oct-07		14:06:20		70.41		53.5		30-Oct-07		14:07:53		71		55		10-Dec-07		14:25:59		66.2		32

		30-Oct-07		16:07:10		73.4		48.5		30-Oct-07		16:06:20		68.61		61.5		30-Oct-07		16:07:53		70.41		54		10-Dec-07		16:25:59		66.81		32.5

		30-Oct-07		18:07:10		72.8		45		30-Oct-07		18:06:20		69.2		54.5		30-Oct-07		18:07:53		70.41		51.5		10-Dec-07		18:25:59		66.81		33

		30-Oct-07		20:07:10		72.21		46		30-Oct-07		20:06:20		68.61		53		30-Oct-07		20:07:53		69.8		48.5		10-Dec-07		20:25:59		66.2		34

		30-Oct-07		22:07:10		71.6		45.5		30-Oct-07		22:06:20		68.61		51.5		30-Oct-07		22:07:53		69.2		49		10-Dec-07		22:25:59		65.01		35

		31-Oct-07		0:07:10		71.6		45		31-Oct-07		0:06:20		69.2		50		31-Oct-07		0:07:53		68.61		49.5		11-Dec-07		0:25:59		64.4		36.5

		31-Oct-07		2:07:10		71		46.5		31-Oct-07		2:06:20		68.61		52		31-Oct-07		2:07:53		68		51		11-Dec-07		2:25:59		63.21		36.5

		31-Oct-07		4:07:10		71		47		31-Oct-07		4:06:20		68.61		52		31-Oct-07		4:07:53		67.4		52.5		11-Dec-07		4:25:59		63.21		36

		31-Oct-07		6:07:10		71.6		47		31-Oct-07		6:06:20		68.61		52		31-Oct-07		6:07:53		72.21		48		11-Dec-07		6:25:59		64.4		34.5

		31-Oct-07		8:07:10		71.6		47.5		31-Oct-07		8:06:20		69.8		48.5		31-Oct-07		8:07:53		71		43.5		11-Dec-07		8:25:59		66.81		31.5

		31-Oct-07		10:07:10		72.21		48		31-Oct-07		10:06:20		69.8		51.5		31-Oct-07		10:07:53		71.6		49.5		11-Dec-07		10:25:59		69.8		31.5

		31-Oct-07		12:07:10		72.8		46.5		31-Oct-07		12:06:20		69.2		45.5		31-Oct-07		12:07:53		72.21		48		11-Dec-07		12:25:59		74.01		32

		31-Oct-07		14:07:10		72.8		46.5		31-Oct-07		14:06:20		70.41		45.5		31-Oct-07		14:07:53		71		52		11-Dec-07		14:25:59		71.6		33.5

		31-Oct-07		16:07:10		73.4		47		31-Oct-07		16:06:20		68		51		31-Oct-07		16:07:53		71		45.5		11-Dec-07		16:25:59		71.6		34.5

		31-Oct-07		18:07:10		72.8		47		31-Oct-07		18:06:20		68.61		48		31-Oct-07		18:07:53		70.41		51.5		11-Dec-07		18:25:59		71.6		33.5

		31-Oct-07		20:07:10		72.21		45		31-Oct-07		20:06:20		68.61		51.5		31-Oct-07		20:07:53		69.8		48		11-Dec-07		20:25:59		69.8		33.5

		31-Oct-07		22:07:10		72.21		44.5		31-Oct-07		22:06:20		69.2		49.5		31-Oct-07		22:07:53		68.61		49.5		11-Dec-07		22:25:59		67.4		33

		1-Nov-07		0:07:10		71.6		44.5		1-Nov-07		0:06:20		69.2		49.5		1-Nov-07		0:07:53		67.4		50		12-Dec-07		0:25:59		66.2		33.5

		1-Nov-07		2:07:10		71.6		45.5		1-Nov-07		2:06:20		69.2		50		1-Nov-07		2:07:53		66.81		51.5		12-Dec-07		2:25:59		65.01		31

		1-Nov-07		4:07:10		71		46.5		1-Nov-07		4:06:20		68.61		52		1-Nov-07		4:07:53		66.81		53		12-Dec-07		4:25:59		63.8		29

		1-Nov-07		6:07:10		71.6		47.5		1-Nov-07		6:06:20		69.2		53.5		1-Nov-07		6:07:53		68.61		51		12-Dec-07		6:25:59		65.6		24

		1-Nov-07		8:07:10		72.21		44.5		1-Nov-07		8:06:20		69.8		53.5		1-Nov-07		8:07:53		70.41		49		12-Dec-07		8:25:59		69.8		21.5

		1-Nov-07		10:07:10		72.21		47		1-Nov-07		10:06:20		68.61		51.5		1-Nov-07		10:07:53		71		48.5		12-Dec-07		10:25:59		72.21		23

		1-Nov-07		12:07:10		72.8		45.5		1-Nov-07		12:06:20		69.8		44		1-Nov-07		12:07:53		71.6		45.5		12-Dec-07		12:25:59		71.6		22

		1-Nov-07		14:07:10		72.8		46.5		1-Nov-07		14:06:20		68.61		47.5		1-Nov-07		14:07:53		71		51		12-Dec-07		14:25:59		72.21		21

		1-Nov-07		16:07:10		72.8		51.5		1-Nov-07		16:06:20		68.61		60.5		1-Nov-07		16:07:53		70.41		55.5		12-Dec-07		16:25:59		72.21		20.5

		1-Nov-07		18:07:10		72.8		50		1-Nov-07		18:06:20		68.61		59		1-Nov-07		18:07:53		69.8		54.5		12-Dec-07		18:25:59		71.6		23

		1-Nov-07		20:07:10		72.21		47.5		1-Nov-07		20:06:20		68.61		53.5		1-Nov-07		20:07:53		69.8		50.5		12-Dec-07		20:25:59		69.8		24

		1-Nov-07		22:07:10		71.6		47.5		1-Nov-07		22:06:20		69.2		52		1-Nov-07		22:07:53		69.2		51		12-Dec-07		22:25:59		68.61		25.5

		2-Nov-07		0:07:10		71		48		2-Nov-07		0:06:20		68.61		52.5		2-Nov-07		0:07:53		68.61		51.5		13-Dec-07		0:25:59		66.2		26.5

		2-Nov-07		2:07:10		71		48		2-Nov-07		2:06:20		68.61		52.5		2-Nov-07		2:07:53		68		52.5		13-Dec-07		2:25:59		64.4		27

		2-Nov-07		4:07:10		70.41		47.5		2-Nov-07		4:06:20		68.61		52		2-Nov-07		4:07:53		67.4		52.5		13-Dec-07		4:25:59		63.21		27.5

		2-Nov-07		6:07:10		71		46		2-Nov-07		6:06:20		69.2		49		2-Nov-07		6:07:53		68		51.5		13-Dec-07		6:25:59		64.4		28

		2-Nov-07		8:07:10		72.21		46.5		2-Nov-07		8:06:20		68.61		54.5		2-Nov-07		8:07:53		69.8		48		13-Dec-07		8:25:59		68		27.5

		2-Nov-07		10:07:10		73.4		46		2-Nov-07		10:06:20		69.2		53		2-Nov-07		10:07:53		71.6		46.5		13-Dec-07		10:25:59		70.41		28.5

		2-Nov-07		12:07:10		74.01		47		2-Nov-07		12:06:20		69.8		56.5		2-Nov-07		12:07:53		71.6		47.5		13-Dec-07		12:25:59		71.6		29

		2-Nov-07		14:07:10		74.01		44		2-Nov-07		14:06:20		71		48.5		2-Nov-07		14:07:53		71		44		13-Dec-07		14:25:59		71.6		26

		2-Nov-07		16:07:10		74.01		52.5		2-Nov-07		16:06:20		69.2		58		2-Nov-07		16:07:53		71		56.5		13-Dec-07		16:25:59		71.6		25.5

		2-Nov-07		18:07:10		74.01		49.5		2-Nov-07		18:06:20		69.2		49.5		2-Nov-07		18:07:53		70.41		50		13-Dec-07		18:25:59		71.6		26

		2-Nov-07		20:07:10		73.4		46.5		2-Nov-07		20:06:20		69.2		51.5		2-Nov-07		20:07:53		70.41		51		13-Dec-07		20:25:59		71		27.5

		2-Nov-07		22:07:10		72.8		42		2-Nov-07		22:06:20		69.8		47.5		2-Nov-07		22:07:53		69.8		47		13-Dec-07		22:25:59		68		28.5

		3-Nov-07		0:07:10		71.6		42		3-Nov-07		0:06:20		69.2		46		3-Nov-07		0:07:53		68		46.5		14-Dec-07		0:25:59		66.2		29.5

		3-Nov-07		2:07:10		71		40.5		3-Nov-07		2:06:20		69.2		43.5		3-Nov-07		2:07:53		66.81		46.5		14-Dec-07		2:25:59		64.4		29.5

		3-Nov-07		4:07:10		70.41		40		3-Nov-07		4:06:20		68		42.5		3-Nov-07		4:07:53		66.81		45		14-Dec-07		4:25:59		63.8		30

		3-Nov-07		6:07:10		70.41		38		3-Nov-07		6:06:20		67.4		40.5		3-Nov-07		6:07:53		67.4		42.5		14-Dec-07		6:25:59		65.01		29

		3-Nov-07		8:07:10		72.8		36.5		3-Nov-07		8:06:20		69.2		42		3-Nov-07		8:07:53		68.61		39		14-Dec-07		8:25:59		66.81		27

		3-Nov-07		10:07:10		74.01		39.5		3-Nov-07		10:06:20		71.6		46		3-Nov-07		10:07:53		70.41		47		14-Dec-07		10:25:59		70.41		28.5

		3-Nov-07		12:07:10		74.6		40		3-Nov-07		12:06:20		71.6		46.5		3-Nov-07		12:07:53		71.6		45.5		14-Dec-07		12:25:59		72.21		28.5

		3-Nov-07		14:07:10		74.6		42		3-Nov-07		14:06:20		70.41		50		3-Nov-07		14:07:53		71		52		14-Dec-07		14:25:59		72.21		29.5

		3-Nov-07		16:07:10		74.01		42.5		3-Nov-07		16:06:20		69.8		50.5		3-Nov-07		16:07:53		71		49.5		14-Dec-07		16:25:59		72.21		30.5

		3-Nov-07		18:07:10		74.01		47.5		3-Nov-07		18:06:20		69.2		59.5		3-Nov-07		18:07:53		71		47		14-Dec-07		18:25:59		72.8		31.5

		3-Nov-07		20:07:10		74.6		42		3-Nov-07		20:06:20		71		47.5		3-Nov-07		20:07:53		70.41		48.5		14-Dec-07		20:25:59		71		31.5

		3-Nov-07		22:07:10		74.01		40.5		3-Nov-07		22:06:20		71		45		3-Nov-07		22:07:53		69.8		45.5		14-Dec-07		22:25:59		68.61		31

		4-Nov-07		0:07:10		72.8		38.5		4-Nov-07		0:06:20		69.8		42		4-Nov-07		0:07:53		68		44.5		15-Dec-07		0:25:59		66.2		31.5

		4-Nov-07		2:07:10		71.6		37.5		4-Nov-07		2:06:20		69.8		40		4-Nov-07		2:07:53		66.81		44		15-Dec-07		2:25:59		64.4		31.5

		4-Nov-07		4:07:10		71		36.5		4-Nov-07		4:06:20		69.2		39		4-Nov-07		4:07:53		65.01		43.5		15-Dec-07		4:25:59		63.21		31

		4-Nov-07		6:07:10		69.8		35.5		4-Nov-07		6:06:20		68.61		38		4-Nov-07		6:07:53		63.8		43.5		15-Dec-07		6:25:59		64.4		30

		4-Nov-07		8:07:10		69.2		35		4-Nov-07		8:06:20		67.4		38		4-Nov-07		8:07:53		66.81		39		15-Dec-07		8:25:59		66.81		28.5

		4-Nov-07		10:07:10		69.8		37.5		4-Nov-07		10:06:20		68.61		40.5		4-Nov-07		10:07:53		67.4		41		15-Dec-07		10:25:59		69.2		30

		4-Nov-07		12:07:10		70.41		40.5		4-Nov-07		12:06:20		68.61		43		4-Nov-07		12:07:53		68.61		43.5		15-Dec-07		12:25:59		72.21		31

		4-Nov-07		14:07:10		71		41		4-Nov-07		14:06:20		69.2		39.5		4-Nov-07		14:07:53		70.41		41		15-Dec-07		14:25:59		71.6		32

		4-Nov-07		16:07:10		72.21		42.5		4-Nov-07		16:06:20		69.2		41.5		4-Nov-07		16:07:53		70.41		46.5		15-Dec-07		16:25:59		72.21		31.5

		4-Nov-07		18:07:10		72.8		38.5		4-Nov-07		18:06:20		69.2		41		4-Nov-07		18:07:53		69.8		44		15-Dec-07		18:25:59		71.6		34

		4-Nov-07		20:07:10		72.8		36		4-Nov-07		20:06:20		70.41		39		4-Nov-07		20:07:53		70.41		40		15-Dec-07		20:25:59		71		34.5

		4-Nov-07		22:07:10		72.8		35.5		4-Nov-07		22:06:20		70.41		39		4-Nov-07		22:07:53		69.2		40		15-Dec-07		22:25:59		68.61		34

		5-Nov-07		0:07:10		72.21		36.5		5-Nov-07		0:06:20		70.41		40		5-Nov-07		0:07:53		67.4		42		16-Dec-07		0:25:59		67.4		35

		5-Nov-07		2:07:10		71.6		36		5-Nov-07		2:06:20		70.41		38.5		5-Nov-07		2:07:53		65.6		42		16-Dec-07		2:25:59		66.81		35

		5-Nov-07		4:07:10		70.41		35.5		5-Nov-07		4:06:20		69.2		37.5		5-Nov-07		4:07:53		64.4		42.5		16-Dec-07		4:25:59		66.2		35.5

		5-Nov-07		6:07:10		69.8		34.5		5-Nov-07		6:06:20		68.61		37		5-Nov-07		6:07:53		64.4		41.5		16-Dec-07		6:25:59		66.2		35.5

		5-Nov-07		8:07:10		69.2		34		5-Nov-07		8:06:20		67.4		37		5-Nov-07		8:07:53		66.81		37.5		16-Dec-07		8:25:59		65.6		35.5

		5-Nov-07		10:07:10		69.2		37		5-Nov-07		10:06:20		68		40		5-Nov-07		10:07:53		67.4		40.5		16-Dec-07		10:25:59		65.6		36

		5-Nov-07		12:07:10		69.8		39		5-Nov-07		12:06:20		68.61		39		5-Nov-07		12:07:53		68		42		16-Dec-07		12:25:59		66.2		37.5

		5-Nov-07		14:07:10		71		40.5		5-Nov-07		14:06:20		68.61		43		5-Nov-07		14:07:53		69.8		42.5		16-Dec-07		14:25:59		66.2		38.5

		5-Nov-07		16:07:10		71.6		41.5		5-Nov-07		16:06:20		69.2		40.5		5-Nov-07		16:07:53		69.8		45		16-Dec-07		16:25:59		66.2		40

		5-Nov-07		18:07:10		72.21		40.5		5-Nov-07		18:06:20		68.61		45		5-Nov-07		18:07:53		70.41		43.5		16-Dec-07		18:25:59		65.6		41.5

		5-Nov-07		20:07:10		72.8		40		5-Nov-07		20:06:20		71		43		5-Nov-07		20:07:53		70.41		44.5		16-Dec-07		20:25:59		65.01		42

		5-Nov-07		22:07:10		72.21		40.5		5-Nov-07		22:06:20		70.41		44.5		5-Nov-07		22:07:53		69.2		44.5		16-Dec-07		22:25:59		65.01		42

		6-Nov-07		0:07:10		71.6		39		6-Nov-07		0:06:20		70.41		41.5		6-Nov-07		0:07:53		67.4		44		17-Dec-07		0:25:59		64.4		42.5

		6-Nov-07		2:07:10		71		38		6-Nov-07		2:06:20		69.8		40		6-Nov-07		2:07:53		66.2		44		17-Dec-07		2:25:59		63.8		43.5

		6-Nov-07		4:07:10		69.8		36		6-Nov-07		4:06:20		68.61		38		6-Nov-07		4:07:53		65.01		42.5		17-Dec-07		4:25:59		63.8		43.5

		6-Nov-07		6:07:10		69.2		35		6-Nov-07		6:06:20		67.4		37		6-Nov-07		6:07:53		67.4		38		17-Dec-07		6:25:59		63.21		43

		6-Nov-07		8:07:10		71.6		33.5		6-Nov-07		8:06:20		68		36		6-Nov-07		8:07:53		68		37		17-Dec-07		8:25:59		64.4		44

		6-Nov-07		10:07:10		72.8		35.5		6-Nov-07		10:06:20		70.41		42.5		6-Nov-07		10:07:53		70.41		35.5		17-Dec-07		10:25:59		65.6		43.5

		6-Nov-07		12:07:10		74.01		38.5		6-Nov-07		12:06:20		70.41		47.5		6-Nov-07		12:07:53		70.41		46.5		17-Dec-07		12:25:59		66.2		43.5

		6-Nov-07		14:07:10		74.01		37		6-Nov-07		14:06:20		71		39		6-Nov-07		14:07:53		70.41		49.5		17-Dec-07		14:25:59		66.2		42

		6-Nov-07		16:07:10		74.6		44		6-Nov-07		16:06:20		70.41		48.5		6-Nov-07		16:07:53		71		49		17-Dec-07		16:25:59		66.81		41.5

		6-Nov-07		18:07:10		74.6		41.5		6-Nov-07		18:06:20		69.2		43		6-Nov-07		18:07:53		70.41		46.5		17-Dec-07		18:25:59		66.81		41.5

		6-Nov-07		20:07:10		73.4		39.5		6-Nov-07		20:06:20		70.41		44.5		6-Nov-07		20:07:53		69.8		44.5		17-Dec-07		20:25:59		65.6		41.5

		6-Nov-07		22:07:10		72.8		40		6-Nov-07		22:06:20		70.41		44		6-Nov-07		22:07:53		68		46		17-Dec-07		22:25:59		65.01		43.5

		7-Nov-07		0:07:10		72.21		40.5		7-Nov-07		0:06:20		70.41		44.5		7-Nov-07		0:07:53		67.4		47		18-Dec-07		0:25:59		64.4		44.5

		7-Nov-07		2:07:10		71.6		41		7-Nov-07		2:06:20		70.41		44		7-Nov-07		2:07:53		66.2		48		18-Dec-07		2:25:59		63.8		45

		7-Nov-07		4:07:10		71		41		7-Nov-07		4:06:20		69.8		43.5		7-Nov-07		4:07:53		65.6		48.5		18-Dec-07		4:25:59		63.8		44

		7-Nov-07		6:07:10		70.41		41.5		7-Nov-07		6:06:20		69.8		43.5		7-Nov-07		6:07:53		67.4		45		18-Dec-07		6:25:59		65.6		46

		7-Nov-07		8:07:10		71.6		41.5		7-Nov-07		8:06:20		68.61		45		7-Nov-07		8:07:53		70.41		43.5		18-Dec-07		8:25:59		68		45

		7-Nov-07		10:07:10		72.8		41		7-Nov-07		10:06:20		70.41		47.5		7-Nov-07		10:07:53		71		44		18-Dec-07		10:25:59		71		45

		7-Nov-07		12:07:10		72.8		40		7-Nov-07		12:06:20		71		38.5		7-Nov-07		12:07:53		70.41		45.5		18-Dec-07		12:25:59		71.6		44

		7-Nov-07		14:07:10		73.4		42.5		7-Nov-07		14:06:20		71		50.5		7-Nov-07		14:07:53		70.41		45.5		18-Dec-07		14:25:59		71.6		45.5

		7-Nov-07		16:07:10		74.01		46		7-Nov-07		16:06:20		70.41		46		7-Nov-07		16:07:53		71		53		18-Dec-07		16:25:59		71.6		45

		7-Nov-07		18:07:10		74.01		43.5		7-Nov-07		18:06:20		69.2		51.5		7-Nov-07		18:07:53		69.8		50		18-Dec-07		18:25:59		72.21		44

		7-Nov-07		20:07:10		72.8		40.5		7-Nov-07		20:06:20		70.41		44		7-Nov-07		20:07:53		69.2		45.5		18-Dec-07		20:25:59		70.41		43

		7-Nov-07		22:07:10		72.21		39		7-Nov-07		22:06:20		70.41		41		7-Nov-07		22:07:53		68		44		18-Dec-07		22:25:59		68.61		44

		8-Nov-07		0:07:10		71.6		40		8-Nov-07		0:06:20		70.41		42.5		8-Nov-07		0:07:53		66.81		46.5		19-Dec-07		0:25:59		67.4		45

		8-Nov-07		2:07:10		71		40.5		8-Nov-07		2:06:20		70.41		42		8-Nov-07		2:07:53		65.6		47.5		19-Dec-07		2:25:59		66.2		46

		8-Nov-07		4:07:10		70.41		39.5		8-Nov-07		4:06:20		69.8		40.5		8-Nov-07		4:07:53		65.01		47		19-Dec-07		4:25:59		65.01		46.5

		8-Nov-07		6:07:10		69.8		39.5		8-Nov-07		6:06:20		69.8		40		8-Nov-07		6:07:53		67.4		43		19-Dec-07		6:25:59		65.6		49

		8-Nov-07		8:07:10		71.6		38.5		8-Nov-07		8:06:20		68.61		42.5		8-Nov-07		8:07:53		69.2		41.5		19-Dec-07		8:25:59		69.2		46.5

		8-Nov-07		10:07:10		71		40		8-Nov-07		10:06:20		67.4		47		8-Nov-07		10:07:53		71		41		19-Dec-07		10:25:59		71.6		47

		8-Nov-07		12:07:10		72.21		43		8-Nov-07		12:06:20		70.41		46.5		8-Nov-07		12:07:53		70.41		47		19-Dec-07		12:25:59		72.21		46.5

		8-Nov-07		14:07:10		71.6		41		8-Nov-07		14:06:20		68		43		8-Nov-07		14:07:53		71.6		45.5		19-Dec-07		14:25:59		72.21		49.5

		8-Nov-07		16:07:10		74.01		43.5		8-Nov-07		16:06:20		71.6		43		8-Nov-07		16:07:53		70.41		53		19-Dec-07		16:25:59		72.8		46.5

		8-Nov-07		18:07:10		73.4		43		8-Nov-07		18:06:20		71		47.5		8-Nov-07		18:07:53		69.8		48		19-Dec-07		18:25:59		72.21		44.5

		8-Nov-07		20:07:10		71.6		43		8-Nov-07		20:06:20		69.2		46.5		8-Nov-07		20:07:53		69.8		47		19-Dec-07		20:25:59		71.6		42

		8-Nov-07		22:07:10		71.6		44		8-Nov-07		22:06:20		68.61		48		8-Nov-07		22:07:53		68.61		48		19-Dec-07		22:25:59		69.2		43

		9-Nov-07		0:07:10		71		43		9-Nov-07		0:06:20		68.61		46.5		9-Nov-07		0:07:53		68		47		20-Dec-07		0:25:59		68		42.5

		9-Nov-07		2:07:10		70.41		44		9-Nov-07		2:06:20		68.61		47.5		9-Nov-07		2:07:53		67.4		48.5		20-Dec-07		2:25:59		67.4		42.5

		9-Nov-07		4:07:10		70.41		44.5		9-Nov-07		4:06:20		68.61		47.5		9-Nov-07		4:07:53		66.81		49.5		20-Dec-07		4:25:59		66.81		42.5

		9-Nov-07		6:07:10		69.8		44		9-Nov-07		6:06:20		68.61		46.5		9-Nov-07		6:07:53		68		47		20-Dec-07		6:25:59		67.4		42.5

		9-Nov-07		8:07:10		71.6		43		9-Nov-07		8:06:20		69.8		46		9-Nov-07		8:07:53		70.41		47		20-Dec-07		8:25:59		69.8		41.5

		9-Nov-07		10:07:10		71.6		44.5		9-Nov-07		10:06:20		71		48		9-Nov-07		10:07:53		71.6		47.5		20-Dec-07		10:25:59		71.6		41.5

		9-Nov-07		12:07:10		72.21		45		9-Nov-07		12:06:20		71		49		9-Nov-07		12:07:53		70.41		48		20-Dec-07		12:25:59		72.8		41

		9-Nov-07		14:07:10		74.01		42.5		9-Nov-07		14:06:20		71.6		44.5		9-Nov-07		14:07:53		71		49.5		20-Dec-07		14:25:59		72.8		42.5

		9-Nov-07		16:07:10		74.01		44		9-Nov-07		16:06:20		71.6		49		9-Nov-07		16:07:53		69.8		49.5		20-Dec-07		16:25:59		72.8		43.5

		9-Nov-07		18:07:10		72.8		42.5		9-Nov-07		18:06:20		70.41		46.5		9-Nov-07		18:07:53		69.8		50		20-Dec-07		18:25:59		72.8		43

		9-Nov-07		20:07:10		72.8		42.5		9-Nov-07		20:06:20		69.8		46		9-Nov-07		20:07:53		69.2		47		20-Dec-07		20:25:59		71.6		43

		9-Nov-07		22:07:10		71.6		43.5		9-Nov-07		22:06:20		69.2		47		9-Nov-07		22:07:53		69.2		47.5		20-Dec-07		22:25:59		70.41		45

		10-Nov-07		0:07:10		71		44.5		10-Nov-07		0:06:20		69.2		48.5		10-Nov-07		0:07:53		68.61		48.5		21-Dec-07		0:25:59		69.2		45.5

		10-Nov-07		2:07:10		71		45		10-Nov-07		2:06:20		68.61		49.5		10-Nov-07		2:07:53		68		49.5		21-Dec-07		2:25:59		68.61		46.5

		10-Nov-07		4:07:10		70.41		45		10-Nov-07		4:06:20		68.61		48		10-Nov-07		4:07:53		67.4		49.5		21-Dec-07		4:25:59		68.61		46.5

		10-Nov-07		6:07:10		69.8		42		10-Nov-07		6:06:20		68.61		45		10-Nov-07		6:07:53		66.81		47		21-Dec-07		6:25:59		68.61		46

		10-Nov-07		8:07:10		72.21		40		10-Nov-07		8:06:20		68.61		44		10-Nov-07		8:07:53		69.8		44		21-Dec-07		8:25:59		70.41		41

		10-Nov-07		10:07:10		74.01		39.5		10-Nov-07		10:06:20		71		42		10-Nov-07		10:07:53		70.41		47		21-Dec-07		10:25:59		72.8		40.5

		10-Nov-07		12:07:10		73.4		41		10-Nov-07		12:06:20		71		48.5		10-Nov-07		12:07:53		70.41		47		21-Dec-07		12:25:59		72.21		38.5

		10-Nov-07		14:07:10		73.4		40		10-Nov-07		14:06:20		71.6		41		10-Nov-07		14:07:53		71		51		21-Dec-07		14:25:59		72.8		37

		10-Nov-07		16:07:10		74.01		44		10-Nov-07		16:06:20		71		50		10-Nov-07		16:07:53		70.41		41.5		21-Dec-07		16:25:59		72.21		35.5

		10-Nov-07		18:07:10		73.4		44.5		10-Nov-07		18:06:20		69.8		51		10-Nov-07		18:07:53		70.41		52.5		21-Dec-07		18:25:59		71.6		34.5

		10-Nov-07		20:07:10		72.8		44		10-Nov-07		20:06:20		69.2		48.5		10-Nov-07		20:07:53		69.8		48.5		21-Dec-07		20:25:59		69.8		34.5

		10-Nov-07		22:07:10		71.6		42.5		10-Nov-07		22:06:20		68.61		46.5		10-Nov-07		22:07:53		69.2		46.5		21-Dec-07		22:25:59		68.61		35

		11-Nov-07		0:07:10		71		41		11-Nov-07		0:06:20		68.61		44.5		11-Nov-07		0:07:53		68		45		22-Dec-07		0:25:59		68		35

		11-Nov-07		2:07:10		70.41		40		11-Nov-07		2:06:20		68		43		11-Nov-07		2:07:53		66.2		45		22-Dec-07		2:25:59		67.4		34.5

		11-Nov-07		4:07:10		69.8		40		11-Nov-07		4:06:20		68		44		11-Nov-07		4:07:53		65.6		46.5		22-Dec-07		4:25:59		66.2		34

		11-Nov-07		6:07:10		69.8		41		11-Nov-07		6:06:20		68		45.5		11-Nov-07		6:07:53		65.01		48		22-Dec-07		6:25:59		66.81		33

		11-Nov-07		8:07:10		69.8		43		11-Nov-07		8:06:20		68		47.5		11-Nov-07		8:07:53		67.4		47		22-Dec-07		8:25:59		69.2		30.5

		11-Nov-07		10:07:10		69.8		46		11-Nov-07		10:06:20		68		51		11-Nov-07		10:07:53		68		48.5		22-Dec-07		10:25:59		70.41		31

		11-Nov-07		12:07:10		69.8		50		11-Nov-07		12:06:20		68		55		11-Nov-07		12:07:53		67.4		53.5		22-Dec-07		12:25:59		71		30

		11-Nov-07		14:07:10		70.41		52.5		11-Nov-07		14:06:20		68.61		57.5		11-Nov-07		14:07:53		68		54.5		22-Dec-07		14:25:59		70.41		30

		11-Nov-07		16:07:10		70.41		53.5		11-Nov-07		16:06:20		68.61		58.5		11-Nov-07		16:07:53		68		55.5		22-Dec-07		16:25:59		71.6		29.5

		11-Nov-07		18:07:10		70.41		54.5		11-Nov-07		18:06:20		68.61		59		11-Nov-07		18:07:53		68.61		56.5		22-Dec-07		18:25:59		70.41		30

		11-Nov-07		20:07:10		70.41		54.5		11-Nov-07		20:06:20		68.61		59		11-Nov-07		20:07:53		68.61		56		22-Dec-07		20:25:59		69.2		30.5

		11-Nov-07		22:07:10		70.41		55		11-Nov-07		22:06:20		68.61		59.5		11-Nov-07		22:07:53		68		56.5		22-Dec-07		22:25:59		66.81		31.5

		12-Nov-07		0:07:10		70.41		55		12-Nov-07		0:06:20		68.61		59		12-Nov-07		0:07:53		68		57		23-Dec-07		0:25:59		64.4		32

		12-Nov-07		2:07:10		70.41		55		12-Nov-07		2:06:20		68.61		59		12-Nov-07		2:07:53		68		57.5		23-Dec-07		2:25:59		63.21		32.5

		12-Nov-07		4:07:10		69.8		50.5		12-Nov-07		4:06:20		68.61		52		12-Nov-07		4:07:53		67.4		55.5		23-Dec-07		4:25:59		62.6		31.5

		12-Nov-07		6:07:10		69.8		45.5		12-Nov-07		6:06:20		68.61		46		12-Nov-07		6:07:53		66.2		51.5		23-Dec-07		6:25:59		62		31

		12-Nov-07		8:07:10		69.2		43.5		12-Nov-07		8:06:20		68		45.5		12-Nov-07		8:07:53		67.4		47		23-Dec-07		8:25:59		62.6		31

		12-Nov-07		10:07:10		69.2		44		12-Nov-07		10:06:20		68.61		46		12-Nov-07		10:07:53		68		47		23-Dec-07		10:25:59		62.6		32

		12-Nov-07		12:07:10		70.41		43		12-Nov-07		12:06:20		69.2		43.5		12-Nov-07		12:07:53		68		46.5		23-Dec-07		12:25:59		62.6		33.5

		12-Nov-07		14:07:10		71		39.5		12-Nov-07		14:06:20		69.2		39		12-Nov-07		14:07:53		69.2		43		23-Dec-07		14:25:59		65.01		35

		12-Nov-07		16:07:10		71		38.5		12-Nov-07		16:06:20		69.2		38.5		12-Nov-07		16:07:53		69.8		42.5		23-Dec-07		16:25:59		65.01		34

		12-Nov-07		18:07:10		71.6		39		12-Nov-07		18:06:20		69.8		38.5		12-Nov-07		18:07:53		69.8		42.5		23-Dec-07		18:25:59		64.4		34

		12-Nov-07		20:07:10		71		39.5		12-Nov-07		20:06:20		68.61		42		12-Nov-07		20:07:53		69.2		43		23-Dec-07		20:25:59		63.21		35.5

		12-Nov-07		22:07:10		70.41		39		12-Nov-07		22:06:20		68.61		41.5		12-Nov-07		22:07:53		67.4		43		23-Dec-07		22:25:59		62.6		35.5

		13-Nov-07		0:07:10		69.8		38.5		13-Nov-07		0:06:20		68		41		13-Nov-07		0:07:53		65.6		43.5		24-Dec-07		0:25:59		62.6		36

		13-Nov-07		2:07:10		69.2		38		13-Nov-07		2:06:20		68		40.5		13-Nov-07		2:07:53		64.4		44.5		24-Dec-07		2:25:59		62		36

		13-Nov-07		4:07:10		69.2		38		13-Nov-07		4:06:20		68		40.5		13-Nov-07		4:07:53		63.8		45		24-Dec-07		4:25:59		62		36

		13-Nov-07		6:07:10		68.61		39		13-Nov-07		6:06:20		68		41.5		13-Nov-07		6:07:53		66.81		43		24-Dec-07		6:25:59		62		36

		13-Nov-07		8:07:10		71.6		38		13-Nov-07		8:06:20		69.2		41		13-Nov-07		8:07:53		69.2		41.5		24-Dec-07		8:25:59		62		36

		13-Nov-07		10:07:10		72.8		38		13-Nov-07		10:06:20		70.41		42.5		13-Nov-07		10:07:53		71		41		24-Dec-07		10:25:59		62		36.5

		13-Nov-07		12:07:10		75.2		37.5		13-Nov-07		12:06:20		71		40		13-Nov-07		12:07:53		70.41		42.5		24-Dec-07		12:25:59		62		38

		13-Nov-07		14:07:10		74.6		35		13-Nov-07		14:06:20		71.6		38.5		13-Nov-07		14:07:53		71.6		42		24-Dec-07		14:25:59		63.21		41.5

		13-Nov-07		16:07:10		74.01		34.5		13-Nov-07		16:06:20		71.6		37.5		13-Nov-07		16:07:53		70.41		41		24-Dec-07		16:25:59		64.4		42.5

		13-Nov-07		18:07:10		74.01		32		13-Nov-07		18:06:20		69.8		31.5		13-Nov-07		18:07:53		70.41		38		24-Dec-07		18:25:59		65.6		43

		13-Nov-07		20:07:10		73.4		37		13-Nov-07		20:06:20		69.8		42		13-Nov-07		20:07:53		70.41		42		24-Dec-07		20:25:59		65.01		45.5

		13-Nov-07		22:07:10		72.8		40		13-Nov-07		22:06:20		69.8		45		13-Nov-07		22:07:53		69.8		44		24-Dec-07		22:25:59		64.4		44.5

		14-Nov-07		0:07:10		72.21		42		14-Nov-07		0:06:20		69.2		47.5		14-Nov-07		0:07:53		69.8		45		25-Dec-07		0:25:59		63.8		45

		14-Nov-07		2:07:10		72.21		43		14-Nov-07		2:06:20		69.8		48		14-Nov-07		2:07:53		69.2		47.5		25-Dec-07		2:25:59		63.8		45

		14-Nov-07		4:07:10		71.6		44.5		14-Nov-07		4:06:20		69.2		50		14-Nov-07		4:07:53		68.61		48.5		25-Dec-07		4:25:59		63.21		44.5

		14-Nov-07		6:07:10		71		46		14-Nov-07		6:06:20		69.2		51.5		14-Nov-07		6:07:53		68.61		50		25-Dec-07		6:25:59		64.4		44

		14-Nov-07		8:07:10		73.4		45		14-Nov-07		8:06:20		69.8		51.5		14-Nov-07		8:07:53		70.41		44		25-Dec-07		8:25:59		66.81		40.5

		14-Nov-07		10:07:10		74.01		46		14-Nov-07		10:06:20		71.6		54.5		14-Nov-07		10:07:53		70.41		53		25-Dec-07		10:25:59		69.2		36.5

		14-Nov-07		12:07:10		74.01		47.5		14-Nov-07		12:06:20		72.21		54		14-Nov-07		12:07:53		70.41		47		25-Dec-07		12:25:59		70.41		34.5

		14-Nov-07		14:07:10		74.01		48		14-Nov-07		14:06:20		72.21		45		14-Nov-07		14:07:53		70.41		47		25-Dec-07		14:25:59		71		33

		14-Nov-07		16:07:10		74.6		49.5		14-Nov-07		16:06:20		71.6		44.5		14-Nov-07		16:07:53		71		59.5		25-Dec-07		16:25:59		70.41		33.5

		14-Nov-07		18:07:10		74.6		49.5		14-Nov-07		18:06:20		71		49		14-Nov-07		18:07:53		71		53.5		25-Dec-07		18:25:59		68.61		33.5

		14-Nov-07		20:07:10		74.01		49		14-Nov-07		20:06:20		70.41		52.5		14-Nov-07		20:07:53		70.41		57.5		25-Dec-07		20:25:59		66.81		35

		14-Nov-07		22:07:10		73.4		52		14-Nov-07		22:06:20		69.8		61		14-Nov-07		22:07:53		71		55.5		25-Dec-07		22:25:59		64.4		35.5

		15-Nov-07		0:07:10		72.8		52		15-Nov-07		0:06:20		69.8		57		15-Nov-07		0:07:53		71		54		26-Dec-07		0:25:59		63.21		35

		15-Nov-07		2:07:10		72.21		50.5		15-Nov-07		2:06:20		69.8		56		15-Nov-07		2:07:53		70.41		53.5		26-Dec-07		2:25:59		62.6		34

		15-Nov-07		4:07:10		71.6		47		15-Nov-07		4:06:20		68.61		50.5		15-Nov-07		4:07:53		69.8		50.5		26-Dec-07		4:25:59		62		33.5

		15-Nov-07		6:07:10		71		45.5		15-Nov-07		6:06:20		68.61		49		15-Nov-07		6:07:53		68.61		49.5		26-Dec-07		6:25:59		62		33

		15-Nov-07		8:07:10		72.21		43.5		15-Nov-07		8:06:20		69.2		47		15-Nov-07		8:07:53		70.41		47.5		26-Dec-07		8:25:59		62.6		32.5

		15-Nov-07		10:07:10		74.01		44.5		15-Nov-07		10:06:20		71.6		56		15-Nov-07		10:07:53		71		46.5		26-Dec-07		10:25:59		62		32.5

		15-Nov-07		12:07:10		74.01		46.5		15-Nov-07		12:06:20		71.6		54		15-Nov-07		12:07:53		71.6		50.5		26-Dec-07		12:25:59		62		33.5

		15-Nov-07		14:07:10		74.01		47.5		15-Nov-07		14:06:20		71.6		56		15-Nov-07		14:07:53		71		52		26-Dec-07		14:25:59		62.6		34.5

		15-Nov-07		16:07:10		74.6		50		15-Nov-07		16:06:20		71.6		45.5		15-Nov-07		16:07:53		70.41		56		26-Dec-07		16:25:59		63.8		35.5

		15-Nov-07		18:07:10		74.01		51		15-Nov-07		18:06:20		70.41		51		15-Nov-07		18:07:53		70.41		56		26-Dec-07		18:25:59		63.8		37

		15-Nov-07		20:07:10		73.4		50		15-Nov-07		20:06:20		69.8		56.5		15-Nov-07		20:07:53		71		55.5		26-Dec-07		20:25:59		63.21		38

		15-Nov-07		22:07:10		73.4		48.5		15-Nov-07		22:06:20		69.8		54.5		15-Nov-07		22:07:53		71.6		51.5		26-Dec-07		22:25:59		62.6		37.5

		16-Nov-07		0:07:10		72.8		46.5		16-Nov-07		0:06:20		69.8		51		16-Nov-07		0:07:53		71		50		27-Dec-07		0:25:59		62		38.5

		16-Nov-07		2:07:10		71.6		45.5		16-Nov-07		2:06:20		68.61		49.5		16-Nov-07		2:07:53		69.2		49		27-Dec-07		2:25:59		62		39

		16-Nov-07		4:07:10		71		45.5		16-Nov-07		4:06:20		68.61		49.5		16-Nov-07		4:07:53		68.61		49.5		27-Dec-07		4:25:59		62		38

		16-Nov-07		6:07:10		70.41		44		16-Nov-07		6:06:20		68.61		47.5		16-Nov-07		6:07:53		67.4		49		27-Dec-07		6:25:59		62		37.5

		16-Nov-07		8:07:10		71.6		42.5		16-Nov-07		8:06:20		68.61		46		16-Nov-07		8:07:53		70.41		46		27-Dec-07		8:25:59		63.21		36.5

		16-Nov-07		10:07:10		72.8		44.5		16-Nov-07		10:06:20		71		49.5		16-Nov-07		10:07:53		72.21		47		27-Dec-07		10:25:59		67.4		35

		16-Nov-07		12:07:10		73.4		45		16-Nov-07		12:06:20		71.6		50.5		16-Nov-07		12:07:53		71		47		27-Dec-07		12:25:59		72.21		30.5

		16-Nov-07		14:07:10		74.01		46.5		16-Nov-07		14:06:20		71.6		53.5		16-Nov-07		14:07:53		71.6		51.5		27-Dec-07		14:25:59		71		28

		16-Nov-07		16:07:10		74.01		50		16-Nov-07		16:06:20		71.6		52		16-Nov-07		16:07:53		71		60.5		27-Dec-07		16:25:59		71		26

		16-Nov-07		18:07:10		74.01		49.5		16-Nov-07		18:06:20		70.41		62		16-Nov-07		18:07:53		70.41		53.5		27-Dec-07		18:25:59		70.41		26

		16-Nov-07		20:07:10		73.4		51		16-Nov-07		20:06:20		69.8		57.5		16-Nov-07		20:07:53		70.41		57		27-Dec-07		20:25:59		69.2		26.5

		16-Nov-07		22:07:10		72.8		51		16-Nov-07		22:06:20		69.8		56.5		16-Nov-07		22:07:53		70.41		55.5		27-Dec-07		22:25:59		66.2		31.5

		17-Nov-07		0:07:10		72.21		50.5		17-Nov-07		0:06:20		69.8		56		17-Nov-07		0:07:53		70.41		54		28-Dec-07		0:25:59		63.8		29.5

		17-Nov-07		2:07:10		71.6		50.5		17-Nov-07		2:06:20		69.2		56		17-Nov-07		2:07:53		69.8		53.5		28-Dec-07		2:25:59		62.6		29.5

		17-Nov-07		4:07:10		71.6		50.5		17-Nov-07		4:06:20		69.2		55.5		17-Nov-07		4:07:53		69.2		54		28-Dec-07		4:25:59		62.6		29.5

		17-Nov-07		6:07:10		71		49.5		17-Nov-07		6:06:20		68		54		17-Nov-07		6:07:53		68.61		53.5		28-Dec-07		6:25:59		62.6		29

		17-Nov-07		8:07:10		71.6		49.5		17-Nov-07		8:06:20		68		55		17-Nov-07		8:07:53		71		53		28-Dec-07		8:25:59		65.01		28.5

		17-Nov-07		10:07:10		72.21		47.5		17-Nov-07		10:06:20		71		51.5		17-Nov-07		10:07:53		71		49.5		28-Dec-07		10:25:59		68.61		28

		17-Nov-07		12:07:10		73.4		47.5		17-Nov-07		12:06:20		72.21		55		17-Nov-07		12:07:53		71.6		55.5		28-Dec-07		12:25:59		71.6		27

		17-Nov-07		14:07:10		74.01		49.5		17-Nov-07		14:06:20		71		46		17-Nov-07		14:07:53		71		57.5		28-Dec-07		14:25:59		71		28.5

		17-Nov-07		16:07:10		74.6		50		17-Nov-07		16:06:20		71.6		48		17-Nov-07		16:07:53		70.41		58		28-Dec-07		16:25:59		71		28.5

		17-Nov-07		18:07:10		74.6		48.5		17-Nov-07		18:06:20		69.8		55		17-Nov-07		18:07:53		70.41		50		28-Dec-07		18:25:59		72.21		29.5

		17-Nov-07		20:07:10		72.8		47.5		17-Nov-07		20:06:20		69.8		52		17-Nov-07		20:07:53		69.8		52		28-Dec-07		20:25:59		71		32

		17-Nov-07		22:07:10		71.6		48		17-Nov-07		22:06:20		69.2		53.5		17-Nov-07		22:07:53		69.2		51.5		28-Dec-07		22:25:59		68		34.5

		18-Nov-07		0:07:10		71.6		49.5		18-Nov-07		0:06:20		68.61		54		18-Nov-07		0:07:53		69.2		53		29-Dec-07		0:25:59		65.6		35

		18-Nov-07		2:07:10		71		49		18-Nov-07		2:06:20		68		54.5		18-Nov-07		2:07:53		68		53		29-Dec-07		2:25:59		64.4		36

		18-Nov-07		4:07:10		70.41		50		18-Nov-07		4:06:20		68		55		18-Nov-07		4:07:53		67.4		53.5		29-Dec-07		4:25:59		63.21		37

		18-Nov-07		6:07:10		69.8		49.5		18-Nov-07		6:06:20		67.4		54.5		18-Nov-07		6:07:53		66.81		54		29-Dec-07		6:25:59		64.4		37.5

		18-Nov-07		8:07:10		69.8		49.5		18-Nov-07		8:06:20		67.4		54.5		18-Nov-07		8:07:53		67.4		53		29-Dec-07		8:25:59		66.81		36.5

		18-Nov-07		10:07:10		69.2		49.5		18-Nov-07		10:06:20		67.4		54.5		18-Nov-07		10:07:53		67.4		53		29-Dec-07		10:25:59		69.8		36

		18-Nov-07		12:07:10		69.8		51.5		18-Nov-07		12:06:20		67.4		56.5		18-Nov-07		12:07:53		67.4		55.5		29-Dec-07		12:25:59		72.8		34

		18-Nov-07		14:07:10		70.41		52		18-Nov-07		14:06:20		68.61		55.5		18-Nov-07		14:07:53		68		55.5		29-Dec-07		14:25:59		72.8		34

		18-Nov-07		16:07:10		71		53.5		18-Nov-07		16:06:20		69.2		53.5		18-Nov-07		16:07:53		69.8		58		29-Dec-07		16:25:59		73.4		33

		18-Nov-07		18:07:10		71.6		55		18-Nov-07		18:06:20		69.2		56		18-Nov-07		18:07:53		69.8		58.5		29-Dec-07		18:25:59		72.21		33.5

		18-Nov-07		20:07:10		71		52		18-Nov-07		20:06:20		69.2		55.5		18-Nov-07		20:07:53		69.8		54.5		29-Dec-07		20:25:59		71		34

		18-Nov-07		22:07:10		70.41		52		18-Nov-07		22:06:20		68.61		56		18-Nov-07		22:07:53		68.61		55		29-Dec-07		22:25:59		67.4		36

		19-Nov-07		0:07:10		70.41		52		19-Nov-07		0:06:20		68		56		19-Nov-07		0:07:53		68.61		54.5		30-Dec-07		0:25:59		65.01		37.5

		19-Nov-07		2:07:10		69.8		51		19-Nov-07		2:06:20		67.4		56		19-Nov-07		2:07:53		68		55		30-Dec-07		2:25:59		63.8		38

		19-Nov-07		4:07:10		69.8		51		19-Nov-07		4:06:20		67.4		56.5		19-Nov-07		4:07:53		67.4		55.5		30-Dec-07		4:25:59		63.21		39

		19-Nov-07		6:07:10		69.8		51		19-Nov-07		6:06:20		67.4		55.5		19-Nov-07		6:07:53		66.81		56		30-Dec-07		6:25:59		62.6		39.5

		19-Nov-07		8:07:10		69.2		51		19-Nov-07		8:06:20		67.4		55.5		19-Nov-07		8:07:53		67.4		54		30-Dec-07		8:25:59		62.6		40.5

		19-Nov-07		10:07:10		69.2		52		19-Nov-07		10:06:20		67.4		56.5		19-Nov-07		10:07:53		67.4		55.5		30-Dec-07		10:25:59		63.21		42.5

		19-Nov-07		12:07:10		69.8		54.5		19-Nov-07		12:06:20		68		60		19-Nov-07		12:07:53		67.4		58		30-Dec-07		12:25:59		63.21		43.5

		19-Nov-07		14:07:10		70.41		56.5		19-Nov-07		14:06:20		68.61		60		19-Nov-07		14:07:53		68.61		59.5		30-Dec-07		14:25:59		63.8		44.5

		19-Nov-07		16:07:10		71		59		19-Nov-07		16:06:20		69.2		65		19-Nov-07		16:07:53		69.2		61.5		30-Dec-07		16:25:59		63.21		45

		19-Nov-07		18:07:10		71		55		19-Nov-07		18:06:20		69.8		54		19-Nov-07		18:07:53		69.8		59		30-Dec-07		18:25:59		63.21		46

		19-Nov-07		20:07:10		71.6		53		19-Nov-07		20:06:20		69.8		55		19-Nov-07		20:07:53		69.8		56		30-Dec-07		20:25:59		62.6		46.5

		19-Nov-07		22:07:10		71		52		19-Nov-07		22:06:20		69.2		54.5		19-Nov-07		22:07:53		69.2		54.5		30-Dec-07		22:25:59		62.6		47

		20-Nov-07		0:07:10		70.41		50		20-Nov-07		0:06:20		68		53.5		20-Nov-07		0:07:53		68.61		53		31-Dec-07		0:25:59		62.6		47.5

		20-Nov-07		2:07:10		69.8		48.5		20-Nov-07		2:06:20		68		52.5		20-Nov-07		2:07:53		67.4		52.5		31-Dec-07		2:25:59		62.6		48

		20-Nov-07		4:07:10		69.2		50		20-Nov-07		4:06:20		67.4		54.5		20-Nov-07		4:07:53		66.81		54		31-Dec-07		4:25:59		62.6		48.5

		20-Nov-07		6:07:10		69.2		52.5		20-Nov-07		6:06:20		67.4		58		20-Nov-07		6:07:53		67.4		54.5		31-Dec-07		6:25:59		62		48

		20-Nov-07		8:07:10		71		54.5		20-Nov-07		8:06:20		68.61		60		20-Nov-07		8:07:53		69.8		56.5		31-Dec-07		8:25:59		63.21		46

		20-Nov-07		10:07:10		72.8		56		20-Nov-07		10:06:20		70.41		58		20-Nov-07		10:07:53		71		50		31-Dec-07		10:25:59		63.8		44

		20-Nov-07		12:07:10		74.6		50.5		20-Nov-07		12:06:20		71		58.5		20-Nov-07		12:07:53		71.6		58		31-Dec-07		12:25:59		65.01		42.5

		20-Nov-07		14:07:10		74.6		45.5		20-Nov-07		14:06:20		71.6		52		20-Nov-07		14:07:53		71		52		31-Dec-07		14:25:59		65.6		41.5

		20-Nov-07		16:07:10		74.01		41		20-Nov-07		16:06:20		72.21		44		20-Nov-07		16:07:53		70.41		51.5		31-Dec-07		16:25:59		65.6		40.5

		20-Nov-07		18:07:10		73.4		40.5		20-Nov-07		18:06:20		69.8		42.5		20-Nov-07		18:07:53		70.41		48		31-Dec-07		18:25:59		65.6		39

		20-Nov-07		20:07:10		72.8		40		20-Nov-07		20:06:20		69.8		42		20-Nov-07		20:07:53		69.2		45.5		31-Dec-07		20:25:59		64.4		38.5

		20-Nov-07		22:07:10		71.6		39.5		20-Nov-07		22:06:20		68.61		42.5		20-Nov-07		22:07:53		68.61		44		31-Dec-07		22:25:59		62.6		38.5

		21-Nov-07		0:07:10		71		39		21-Nov-07		0:06:20		68.61		40.5		21-Nov-07		0:07:53		68		43		1-Jan-08		0:25:59		62.6		37

		21-Nov-07		2:07:10		70.41		38.5		21-Nov-07		2:06:20		68		40.5		21-Nov-07		2:07:53		66.2		43.5		1-Jan-08		2:25:59		62		36

		21-Nov-07		4:07:10		69.8		37		21-Nov-07		4:06:20		68		39.5		21-Nov-07		4:07:53		65.01		43.5		1-Jan-08		4:25:59		62		35

		21-Nov-07		6:07:10		69.2		36.5		21-Nov-07		6:06:20		68		38.5		21-Nov-07		6:07:53		67.4		39.5		1-Jan-08		6:25:59		62.6		33.5

		21-Nov-07		8:07:10		71		35.5		21-Nov-07		8:06:20		68		37		21-Nov-07		8:07:53		68.61		38		1-Jan-08		8:25:59		65.01		32.5

		21-Nov-07		10:07:10		71.6		35.5		21-Nov-07		10:06:20		69.8		34.5		21-Nov-07		10:07:53		71.6		37		1-Jan-08		10:25:59		68		31

		21-Nov-07		12:07:10		72.8		33.5		21-Nov-07		12:06:20		70.41		34.5		21-Nov-07		12:07:53		70.41		38.5		1-Jan-08		12:25:59		72.21		30.5

		21-Nov-07		14:07:10		73.4		33.5		21-Nov-07		14:06:20		71		35		21-Nov-07		14:07:53		71.6		34.5		1-Jan-08		14:25:59		71.6		31.5

		21-Nov-07		16:07:10		74.6		33.5		21-Nov-07		16:06:20		71		36		21-Nov-07		16:07:53		71		37.5		1-Jan-08		16:25:59		72.21		30.5

		21-Nov-07		18:07:10		74.01		35		21-Nov-07		18:06:20		69.8		37.5		21-Nov-07		18:07:53		70.41		38.5		1-Jan-08		18:25:59		71		31.5

		21-Nov-07		20:07:10		72.8		34		21-Nov-07		20:06:20		69.2		36		21-Nov-07		20:07:53		70.41		38		1-Jan-08		20:25:59		70.41		31.5

		21-Nov-07		22:07:10		71		34		21-Nov-07		22:06:20		68.61		36.5		21-Nov-07		22:07:53		68		37.5		1-Jan-08		22:25:59		66.2		32.5

		22-Nov-07		0:07:10		70.41		33.5		22-Nov-07		0:06:20		68		35.5		22-Nov-07		0:07:53		65.6		38		2-Jan-08		0:25:59		63.8		33

		22-Nov-07		2:07:10		69.8		32		22-Nov-07		2:06:20		68		34		22-Nov-07		2:07:53		64.4		38		2-Jan-08		2:25:59		62.6		33

		22-Nov-07		4:07:10		69.2		31		22-Nov-07		4:06:20		67.4		33		22-Nov-07		4:07:53		63.21		37.5		2-Jan-08		4:25:59		62		32.5

		22-Nov-07		6:07:10		68.61		31		22-Nov-07		6:06:20		68		32.5		22-Nov-07		6:07:53		66.81		33.5		2-Jan-08		6:25:59		62.6		31.5

		22-Nov-07		8:07:10		70.41		30.5		22-Nov-07		8:06:20		69.8		31.5		22-Nov-07		8:07:53		69.2		32		2-Jan-08		8:25:59		63.8		31

		22-Nov-07		10:07:10		71.6		31.5		22-Nov-07		10:06:20		70.41		33.5		22-Nov-07		10:07:53		71.6		33		2-Jan-08		10:25:59		64.4		31

		22-Nov-07		12:07:10		72.21		32.5		22-Nov-07		12:06:20		71		34		22-Nov-07		12:07:53		70.41		35.5		2-Jan-08		12:25:59		66.81		32.5

		22-Nov-07		14:07:10		73.4		31.5		22-Nov-07		14:06:20		71		32.5		22-Nov-07		14:07:53		71.6		33.5		2-Jan-08		14:25:59		68.61		34

		22-Nov-07		16:07:10		73.4		29		22-Nov-07		16:06:20		69.8		29		22-Nov-07		16:07:53		71.6		33		2-Jan-08		16:25:59		70.41		34.5

		22-Nov-07		18:07:10		74.01		31.5		22-Nov-07		18:06:20		69.8		34		22-Nov-07		18:07:53		70.41		36		2-Jan-08		18:25:59		71		33.5

		22-Nov-07		20:07:10		71.6		31		22-Nov-07		20:06:20		68.61		33		22-Nov-07		20:07:53		69.8		34.5		2-Jan-08		20:25:59		70.41		33

		22-Nov-07		22:07:10		70.41		31.5		22-Nov-07		22:06:20		66.81		34.5		22-Nov-07		22:07:53		66.81		35.5		2-Jan-08		22:25:59		66.2		34.5

		23-Nov-07		0:07:10		69.2		31.5		23-Nov-07		0:06:20		66.2		35		23-Nov-07		0:07:53		64.4		37		3-Jan-08		0:25:59		64.4		35.5

		23-Nov-07		2:07:10		68.61		31		23-Nov-07		2:06:20		66.2		34		23-Nov-07		2:07:53		63.21		37		3-Jan-08		2:25:59		62.6		35.5

		23-Nov-07		4:07:10		68		31		23-Nov-07		4:06:20		66.2		33.5		23-Nov-07		4:07:53		62		36.5		3-Jan-08		4:25:59		62		36

		23-Nov-07		6:07:10		67.4		30		23-Nov-07		6:06:20		66.2		31.5		23-Nov-07		6:07:53		66.2		32.5		3-Jan-08		6:25:59		63.8		36

		23-Nov-07		8:07:10		69.2		28.5		23-Nov-07		8:06:20		67.4		30		23-Nov-07		8:07:53		67.4		31		3-Jan-08		8:25:59		65.01		34.5

		23-Nov-07		10:07:10		69.8		30		23-Nov-07		10:06:20		68		33		23-Nov-07		10:07:53		68		32.5		3-Jan-08		10:25:59		67.4		35

		23-Nov-07		12:07:10		70.41		31.5		23-Nov-07		12:06:20		68.61		33		23-Nov-07		12:07:53		68.61		33.5		3-Jan-08		12:25:59		72.8		33.5

		23-Nov-07		14:07:10		71		31		23-Nov-07		14:06:20		69.2		32		23-Nov-07		14:07:53		69.2		34		3-Jan-08		14:25:59		73.4		33

		23-Nov-07		16:07:10		71.6		29.5		23-Nov-07		16:06:20		69.2		29		23-Nov-07		16:07:53		69.8		32.5		3-Jan-08		16:25:59		72.8		34

		23-Nov-07		18:07:10		71.6		31.5		23-Nov-07		18:06:20		69.8		31.5		23-Nov-07		18:07:53		69.8		34		3-Jan-08		18:25:59		72.8		34.5

		23-Nov-07		20:07:10		71.6		32		23-Nov-07		20:06:20		68.61		35		23-Nov-07		20:07:53		68.61		36		3-Jan-08		20:25:59		71.6		35

		23-Nov-07		22:07:10		69.8		32		23-Nov-07		22:06:20		67.4		35.5		23-Nov-07		22:07:53		66.81		36		3-Jan-08		22:25:59		68		36

		24-Nov-07		0:07:10		68.61		32		24-Nov-07		0:06:20		66.2		35.5		24-Nov-07		0:07:53		65.01		36.5		4-Jan-08		0:25:59		65.6		36.5

		24-Nov-07		2:07:10		68		31.5		24-Nov-07		2:06:20		66.2		33.5		24-Nov-07		2:07:53		63.8		36.5		4-Jan-08		2:25:59		64.4		38

		24-Nov-07		4:07:10		67.4		30.5		24-Nov-07		4:06:20		66.2		31.5		24-Nov-07		4:07:53		62.6		35.5		4-Jan-08		4:25:59		63.8		39

		24-Nov-07		6:07:10		67.4		30.5		24-Nov-07		6:06:20		66.2		32.5		24-Nov-07		6:07:53		66.81		32		4-Jan-08		6:25:59		65.01		41

		24-Nov-07		8:07:10		69.2		27		24-Nov-07		8:06:20		68		28		24-Nov-07		8:07:53		68		30		4-Jan-08		8:25:59		68.61		40

		24-Nov-07		10:07:10		70.41		23.5		24-Nov-07		10:06:20		69.2		22		24-Nov-07		10:07:53		68		26		4-Jan-08		10:25:59		71.6		41

		24-Nov-07		12:07:10		71		20.5		24-Nov-07		12:06:20		69.2		18.5		24-Nov-07		12:07:53		68.61		24		4-Jan-08		12:25:59		74.01		40.5

		24-Nov-07		14:07:10		71		19		24-Nov-07		14:06:20		69.2		16		24-Nov-07		14:07:53		69.2		23		4-Jan-08		14:25:59		73.4		42.5

		24-Nov-07		16:07:10		71.6		18.5		24-Nov-07		16:06:20		69.2		16.5		24-Nov-07		16:07:53		69.8		22		4-Jan-08		16:25:59		74.01		41.5

		24-Nov-07		18:07:10		71.6		18.5		24-Nov-07		18:06:20		69.2		17		24-Nov-07		18:07:53		70.41		22		4-Jan-08		18:25:59		73.4		42

		24-Nov-07		20:07:10		71.6		21		24-Nov-07		20:06:20		69.2		22		24-Nov-07		20:07:53		69.2		24.5		4-Jan-08		20:25:59		72.8		43

		24-Nov-07		22:07:10		69.8		24.5		24-Nov-07		22:06:20		67.4		28		24-Nov-07		22:07:53		67.4		28		4-Jan-08		22:25:59		69.8		44

		25-Nov-07		0:07:10		69.2		25.5		25-Nov-07		0:06:20		66.81		29		25-Nov-07		0:07:53		65.6		29.5		5-Jan-08		0:25:59		68		45

		25-Nov-07		2:07:10		68		25.5		25-Nov-07		2:06:20		66.2		28.5		25-Nov-07		2:07:53		63.8		30.5		5-Jan-08		2:25:59		67.4		45.5

		25-Nov-07		4:07:10		67.4		26		25-Nov-07		4:06:20		66.2		28.5		25-Nov-07		4:07:53		62.6		30.5		5-Jan-08		4:25:59		66.81		46

		25-Nov-07		6:07:10		66.81		25.5		25-Nov-07		6:06:20		66.2		28		25-Nov-07		6:07:53		62		31		5-Jan-08		6:25:59		67.4		49

		25-Nov-07		8:07:10		67.4		24.5		25-Nov-07		8:06:20		67.4		26		25-Nov-07		8:07:53		66.81		26.5		5-Jan-08		8:25:59		71.6		48.5

		25-Nov-07		10:07:10		68		26.5		25-Nov-07		10:06:20		68		29		25-Nov-07		10:07:53		67.4		28		5-Jan-08		10:25:59		73.4		48.5

		25-Nov-07		12:07:10		68.61		27.5		25-Nov-07		12:06:20		68		29		25-Nov-07		12:07:53		67.4		30		5-Jan-08		12:25:59		72.8		48.5

		25-Nov-07		14:07:10		69.2		26		25-Nov-07		14:06:20		69.2		26		25-Nov-07		14:07:53		68		29		5-Jan-08		14:25:59		72.21		46

		25-Nov-07		16:07:10		69.8		27.5		25-Nov-07		16:06:20		69.2		28.5		25-Nov-07		16:07:53		68.61		30.5		5-Jan-08		16:25:59		72.8		44.5

		25-Nov-07		18:07:10		70.41		29.5		25-Nov-07		18:06:20		69.2		30.5		25-Nov-07		18:07:53		68.61		31.5		5-Jan-08		18:25:59		73.4		42

		25-Nov-07		20:07:10		69.2		29.5		25-Nov-07		20:06:20		68		32		25-Nov-07		20:07:53		67.4		32.5		5-Jan-08		20:25:59		72.21		41.5

		25-Nov-07		22:07:10		68.61		32		25-Nov-07		22:06:20		66.81		35.5		25-Nov-07		22:07:53		66.2		35		5-Jan-08		22:25:59		68.61		43.5

		26-Nov-07		0:07:10		68		32		26-Nov-07		0:06:20		66.2		35.5		26-Nov-07		0:07:53		65.01		36		6-Jan-08		0:25:59		67.4		44

		26-Nov-07		2:07:10		68		32.5		26-Nov-07		2:06:20		66.2		35.5		26-Nov-07		2:07:53		63.8		37		6-Jan-08		2:25:59		66.2		43.5

		26-Nov-07		4:07:10		67.4		32.5		26-Nov-07		4:06:20		66.2		35.5		26-Nov-07		4:07:53		63.21		37.5		6-Jan-08		4:25:59		65.6		43.5

		26-Nov-07		6:07:10		67.4		33		26-Nov-07		6:06:20		66.2		35.5		26-Nov-07		6:07:53		62.6		38		6-Jan-08		6:25:59		65.01		43.5

		26-Nov-07		8:07:10		68		32.5		26-Nov-07		8:06:20		67.4		34.5		26-Nov-07		8:07:53		67.4		34		6-Jan-08		8:25:59		64.4		43.5

		26-Nov-07		10:07:10		68		34		26-Nov-07		10:06:20		67.4		36.5		26-Nov-07		10:07:53		67.4		36		6-Jan-08		10:25:59		64.4		44.5

		26-Nov-07		12:07:10		68.61		34.5		26-Nov-07		12:06:20		67.4		37		26-Nov-07		12:07:53		68		35.5		6-Jan-08		12:25:59		64.4		45.5

		26-Nov-07		14:07:10		68.61		32		26-Nov-07		14:06:20		68		32		26-Nov-07		14:07:53		68		34		6-Jan-08		14:25:59		64.4		47

		26-Nov-07		16:07:10		69.2		32		26-Nov-07		16:06:20		68.61		33		26-Nov-07		16:07:53		67.4		34.5		6-Jan-08		16:25:59		65.01		47.5

		26-Nov-07		18:07:10		69.2		33		26-Nov-07		18:06:20		68		35		26-Nov-07		18:07:53		68		35.5		6-Jan-08		18:25:59		64.4		47.5

		26-Nov-07		20:07:10		68.61		34		26-Nov-07		20:06:20		67.4		36.5		26-Nov-07		20:07:53		66.81		36.5		6-Jan-08		20:25:59		64.4		47.5

		26-Nov-07		22:07:10		68		33.5		26-Nov-07		22:06:20		66.2		36		26-Nov-07		22:07:53		64.4		37.5		6-Jan-08		22:25:59		64.4		46.5

		27-Nov-07		0:07:10		67.4		33		27-Nov-07		0:06:20		66.2		36		27-Nov-07		0:07:53		63.8		38		7-Jan-08		0:25:59		64.4		46

		27-Nov-07		2:07:10		66.81		32		27-Nov-07		2:06:20		66.2		34		27-Nov-07		2:07:53		62.6		36.5		7-Jan-08		2:25:59		63.8		45

		27-Nov-07		4:07:10		66.81		31.5		27-Nov-07		4:06:20		65.6		32.5		27-Nov-07		4:07:53		62		36.5		7-Jan-08		4:25:59		63.8		44.5

		27-Nov-07		6:07:10		66.81		30.5		27-Nov-07		6:06:20		65.6		32		27-Nov-07		6:07:53		66.81		32		7-Jan-08		6:25:59		63.21		43.5

		27-Nov-07		8:07:10		69.2		28.5		27-Nov-07		8:06:20		67.4		30.5		27-Nov-07		8:07:53		68.61		30.5		7-Jan-08		8:25:59		63.21		43

		27-Nov-07		10:07:10		69.8		31		27-Nov-07		10:06:20		69.8		32.5		27-Nov-07		10:07:53		69.2		32		7-Jan-08		10:25:59		63.8		42

		27-Nov-07		12:07:10		71		32.5		27-Nov-07		12:06:20		71.6		34		27-Nov-07		12:07:53		71		33.5		7-Jan-08		12:25:59		63.8		43

		27-Nov-07		14:07:10		71.6		34		27-Nov-07		14:06:20		71		35.5		27-Nov-07		14:07:53		71		34.5		7-Jan-08		14:25:59		65.01		44.5

		27-Nov-07		16:07:10		72.21		34		27-Nov-07		16:06:20		71.6		37.5		27-Nov-07		16:07:53		70.41		38		7-Jan-08		16:25:59		65.01		44.5

		27-Nov-07		18:07:10		72.21		36.5		27-Nov-07		18:06:20		69.8		39.5		27-Nov-07		18:07:53		69.8		39		7-Jan-08		18:25:59		65.6		44

		27-Nov-07		20:07:10		71.6		36.5		27-Nov-07		20:06:20		68.61		40		27-Nov-07		20:07:53		69.2		39.5		7-Jan-08		20:25:59		64.4		44.5

		27-Nov-07		22:07:10		69.8		35		27-Nov-07		22:06:20		67.4		38.5		27-Nov-07		22:07:53		67.4		38.5		7-Jan-08		22:25:59		63.8		45

		28-Nov-07		0:07:10		69.2		35		28-Nov-07		0:06:20		66.81		38.5		28-Nov-07		0:07:53		66.2		38.5		8-Jan-08		0:25:59		63.8		45.5

		28-Nov-07		2:07:10		68		34.5		28-Nov-07		2:06:20		66.2		38		28-Nov-07		2:07:53		65.01		39		8-Jan-08		2:25:59		63.8		45.5

		28-Nov-07		4:07:10		68		34		28-Nov-07		4:06:20		66.2		37		28-Nov-07		4:07:53		63.8		39		8-Jan-08		4:25:59		63.8		46

		28-Nov-07		6:07:10		67.4		34.5		28-Nov-07		6:06:20		66.2		37.5		28-Nov-07		6:07:53		67.4		35.5		8-Jan-08		6:25:59		65.01		45

		28-Nov-07		8:07:10		69.8		34		28-Nov-07		8:06:20		68		36.5		28-Nov-07		8:07:53		69.2		36.5		8-Jan-08		8:25:59		67.4		40.5

		28-Nov-07		10:07:10		71		34.5		28-Nov-07		10:06:20		70.41		36.5		28-Nov-07		10:07:53		71.6		36		8-Jan-08		10:25:59		69.8		39

		28-Nov-07		12:07:10		72.21		39		28-Nov-07		12:06:20		71		43.5		28-Nov-07		12:07:53		71		41		8-Jan-08		12:25:59		73.4		39

		28-Nov-07		14:07:10		72.8		34		28-Nov-07		14:06:20		71		34		28-Nov-07		14:07:53		71		39		8-Jan-08		14:25:59		72.8		37

		28-Nov-07		16:07:10		72.8		33.5		28-Nov-07		16:06:20		71.6		34.5		28-Nov-07		16:07:53		71		37.5		8-Jan-08		16:25:59		72.21		36

		28-Nov-07		18:07:10		72.8		35		28-Nov-07		18:06:20		70.41		37.5		28-Nov-07		18:07:53		71		37.5		8-Jan-08		18:25:59		72.21		35.5

		28-Nov-07		20:07:10		72.8		35		28-Nov-07		20:06:20		69.8		37.5		28-Nov-07		20:07:53		70.41		38.5		8-Jan-08		20:25:59		71.6		34.5

		28-Nov-07		22:07:10		71.6		35		28-Nov-07		22:06:20		68.61		38		28-Nov-07		22:07:53		69.2		38		8-Jan-08		22:25:59		68		37.5

		29-Nov-07		0:07:10		70.41		35.5		29-Nov-07		0:06:20		67.4		38.5		29-Nov-07		0:07:53		68		38		9-Jan-08		0:25:59		66.81		38

		29-Nov-07		2:07:10		69.2		34		29-Nov-07		2:06:20		66.81		37		29-Nov-07		2:07:53		66.2		38		9-Jan-08		2:25:59		65.6		39

		29-Nov-07		4:07:10		68.61		33		29-Nov-07		4:06:20		66.81		35.5		29-Nov-07		4:07:53		65.01		37.5		9-Jan-08		4:25:59		65.01		39.5

		29-Nov-07		6:07:10		68.61		32		29-Nov-07		6:06:20		66.2		33.5		29-Nov-07		6:07:53		66.81		34.5		9-Jan-08		6:25:59		65.6		39.5

		29-Nov-07		8:07:10		70.41		30.5		29-Nov-07		8:06:20		68		32		29-Nov-07		8:07:53		68		33.5		9-Jan-08		8:25:59		68.61		38

		29-Nov-07		10:07:10		71.6		32.5		29-Nov-07		10:06:20		71		34.5		29-Nov-07		10:07:53		70.41		34		9-Jan-08		10:25:59		71		40

		29-Nov-07		12:07:10		72.8		31		29-Nov-07		12:06:20		71.6		32.5		29-Nov-07		12:07:53		71		33		9-Jan-08		12:25:59		73.4		39

		29-Nov-07		14:07:10		72.8		31		29-Nov-07		14:06:20		71.6		32.5		29-Nov-07		14:07:53		71.6		31		9-Jan-08		14:25:59		74.01		40

		29-Nov-07		16:07:10		72.8		30.5		29-Nov-07		16:06:20		71.6		31.5		29-Nov-07		16:07:53		71		35		9-Jan-08		16:25:59		74.6		41

		29-Nov-07		18:07:10		72.8		28		29-Nov-07		18:06:20		69.2		29		29-Nov-07		18:07:53		71		32		9-Jan-08		18:25:59		75.2		41.5

		29-Nov-07		20:07:10		72.21		30		29-Nov-07		20:06:20		69.2		31		29-Nov-07		20:07:53		69.8		32.5		9-Jan-08		20:25:59		73.4		41.5

		29-Nov-07		22:07:10		70.41		31		29-Nov-07		22:06:20		67.4		34		29-Nov-07		22:07:53		68		34		9-Jan-08		22:25:59		69.8		42.5

		30-Nov-07		0:07:10		69.2		31		30-Nov-07		0:06:20		66.81		34		30-Nov-07		0:07:53		66.2		34.5		10-Jan-08		0:25:59		68		44

		30-Nov-07		2:07:10		68.61		30.5		30-Nov-07		2:06:20		66.2		33.5		30-Nov-07		2:07:53		65.01		35		10-Jan-08		2:25:59		66.81		44.5

		30-Nov-07		4:07:10		68		30		30-Nov-07		4:06:20		65.6		33		30-Nov-07		4:07:53		63.21		35		10-Jan-08		4:25:59		66.2		45

		30-Nov-07		6:07:10		67.4		30		30-Nov-07		6:06:20		66.2		32		30-Nov-07		6:07:53		67.4		31		10-Jan-08		6:25:59		68		45

		30-Nov-07		8:07:10		69.8		28		30-Nov-07		8:06:20		68.61		30.5		30-Nov-07		8:07:53		68		31		10-Jan-08		8:25:59		71.6		41.5

		30-Nov-07		10:07:10		71		30		30-Nov-07		10:06:20		70.41		33		30-Nov-07		10:07:53		70.41		32		10-Jan-08		10:25:59		73.4		40.5

		30-Nov-07		12:07:10		71.6		31.5		30-Nov-07		12:06:20		71		31		30-Nov-07		12:07:53		71.6		31.5		10-Jan-08		12:25:59		74.6		39.5

		30-Nov-07		14:07:10		72.8		30		30-Nov-07		14:06:20		71		31		30-Nov-07		14:07:53		71		35		10-Jan-08		14:25:59		74.6		39

		30-Nov-07		16:07:10		73.4		28		30-Nov-07		16:06:20		71		29		30-Nov-07		16:07:53		71		32.5		10-Jan-08		16:25:59		74.6		39

		30-Nov-07		18:07:10		73.4		26.5		30-Nov-07		18:06:20		69.8		26.5		30-Nov-07		18:07:53		69.8		31		10-Jan-08		18:25:59		73.4		39.5

		30-Nov-07		20:07:10		72.21		26		30-Nov-07		20:06:20		69.2		27.5		30-Nov-07		20:07:53		69.2		29		10-Jan-08		20:25:59		74.01		38.5

		30-Nov-07		22:07:10		71		27.5		30-Nov-07		22:06:20		68		30.5		30-Nov-07		22:07:53		68		31		10-Jan-08		22:25:59		70.41		43

		1-Dec-07		0:07:10		69.8		28.5		1-Dec-07		0:06:20		67.4		32		1-Dec-07		0:07:53		66.81		32.5		11-Jan-08		0:25:59		68.61		42.5

		1-Dec-07		2:07:10		69.2		28.5		1-Dec-07		2:06:20		66.81		31.5		1-Dec-07		2:07:53		65.01		33		11-Jan-08		2:25:59		67.4		43.5

		1-Dec-07		4:07:10		68.61		28		1-Dec-07		4:06:20		66.2		30.5		1-Dec-07		4:07:53		64.4		33		11-Jan-08		4:25:59		66.2		44

		1-Dec-07		6:07:10		68.61		28		1-Dec-07		6:06:20		66.2		30.5		1-Dec-07		6:07:53		66.81		30.5		11-Jan-08		6:25:59		68		44.5

		1-Dec-07		8:07:10		70.41		27		1-Dec-07		8:06:20		68		29		1-Dec-07		8:07:53		69.2		29.5		11-Jan-08		8:25:59		71.6		42

		1-Dec-07		10:07:10		71		27.5		1-Dec-07		10:06:20		70.41		29.5		1-Dec-07		10:07:53		71		29		11-Jan-08		10:25:59		74.01		41.5

		1-Dec-07		12:07:10		72.21		26.5		1-Dec-07		12:06:20		71.6		27		1-Dec-07		12:07:53		71		29.5		11-Jan-08		12:25:59		74.6		41

		1-Dec-07		14:07:10		72.8		24.5		1-Dec-07		14:06:20		71		26		1-Dec-07		14:07:53		70.41		29		11-Jan-08		14:25:59		74.01		43

		1-Dec-07		16:07:10		72.8		24.5		1-Dec-07		16:06:20		71		25.5		1-Dec-07		16:07:53		70.41		28		11-Jan-08		16:25:59		73.4		44.5

		1-Dec-07		18:07:10		72.8		26.5		1-Dec-07		18:06:20		69.8		28.5		1-Dec-07		18:07:53		70.41		30.5		11-Jan-08		18:25:59		71.6		45.5

		1-Dec-07		20:07:10		71.6		24.5		1-Dec-07		20:06:20		68		26		1-Dec-07		20:07:53		68.61		28		11-Jan-08		20:25:59		69.2		46.5

		1-Dec-07		22:07:10		69.8		24.5		1-Dec-07		22:06:20		66.81		27.5		1-Dec-07		22:07:53		66.2		28.5		11-Jan-08		22:25:59		68.61		47

		2-Dec-07		0:07:10		68.61		26		2-Dec-07		0:06:20		66.2		28		2-Dec-07		0:07:53		64.4		31.5		12-Jan-08		0:25:59		67.4		47.5

		2-Dec-07		2:07:10		68		25		2-Dec-07		2:06:20		65.6		28		2-Dec-07		2:07:53		63.21		30.5		12-Jan-08		2:25:59		66.81		48

		2-Dec-07		4:07:10		67.4		24.5		2-Dec-07		4:06:20		65.6		26.5		2-Dec-07		4:07:53		62		29.5		12-Jan-08		4:25:59		66.2		48

		2-Dec-07		6:07:10		66.81		24		2-Dec-07		6:06:20		65.6		26		2-Dec-07		6:07:53		61.41		29		12-Jan-08		6:25:59		66.2		49

		2-Dec-07		8:07:10		67.4		23		2-Dec-07		8:06:20		67.4		24.5		2-Dec-07		8:07:53		66.81		25.5		12-Jan-08		8:25:59		69.8		44.5

		2-Dec-07		10:07:10		67.4		24.5		2-Dec-07		10:06:20		67.4		26		2-Dec-07		10:07:53		68.61		25		12-Jan-08		10:25:59		71.6		43.5

		2-Dec-07		12:07:10		68		27		2-Dec-07		12:06:20		68		28.5		2-Dec-07		12:07:53		68.61		28		12-Jan-08		12:25:59		70.41		45

		2-Dec-07		14:07:10		68.61		27.5		2-Dec-07		14:06:20		68		28.5		2-Dec-07		14:07:53		69.2		29		12-Jan-08		14:25:59		71		44.5

		2-Dec-07		16:07:10		69.2		28		2-Dec-07		16:06:20		68		29.5		2-Dec-07		16:07:53		68		30		12-Jan-08		16:25:59		70.41		44

		2-Dec-07		18:07:10		69.2		28.5		2-Dec-07		18:06:20		68		30		2-Dec-07		18:07:53		67.4		31		12-Jan-08		18:25:59		69.8		44

		2-Dec-07		20:07:10		68		30		2-Dec-07		20:06:20		66.81		33		2-Dec-07		20:07:53		67.4		31		12-Jan-08		20:25:59		68.61		44.5

		2-Dec-07		22:07:10		67.4		29.5		2-Dec-07		22:06:20		66.2		32.5		2-Dec-07		22:07:53		63.8		33.5		12-Jan-08		22:25:59		67.4		46

		3-Dec-07		0:07:10		66.81		29.5		3-Dec-07		0:06:20		65.6		32		3-Dec-07		0:07:53		62.6		33.5		13-Jan-08		0:25:59		66.2		46.5

		3-Dec-07		2:07:10		66.81		30		3-Dec-07		2:06:20		66.2		33		3-Dec-07		2:07:53		62		34.5		13-Jan-08		2:25:59		66.2		47

		3-Dec-07		4:07:10		66.81		32.5		3-Dec-07		4:06:20		66.2		36		3-Dec-07		4:07:53		62.6		37.5		13-Jan-08		4:25:59		65.6		47

		3-Dec-07		6:07:10		66.81		35		3-Dec-07		6:06:20		66.2		39		3-Dec-07		6:07:53		62.6		40		13-Jan-08		6:25:59		65.01		47

		3-Dec-07		8:07:10		68		35.5		3-Dec-07		8:06:20		67.4		38		3-Dec-07		8:07:53		68.61		36		13-Jan-08		8:25:59		65.01		47.5

		3-Dec-07		10:07:10		68		35		3-Dec-07		10:06:20		67.4		37		3-Dec-07		10:07:53		68		36.5		13-Jan-08		10:25:59		65.01		48.5

		3-Dec-07		12:07:10		68		36		3-Dec-07		12:06:20		67.4		38		3-Dec-07		12:07:53		67.4		37.5		13-Jan-08		12:25:59		65.01		50

		3-Dec-07		14:07:10		68.61		36.5		3-Dec-07		14:06:20		68		39		3-Dec-07		14:07:53		68		38		13-Jan-08		14:25:59		65.6		51

		3-Dec-07		16:07:10		69.2		39		3-Dec-07		16:06:20		68		42.5		3-Dec-07		16:07:53		67.4		41		13-Jan-08		16:25:59		66.81		50

		3-Dec-07		18:07:10		69.2		39.5		3-Dec-07		18:06:20		68		42.5		3-Dec-07		18:07:53		67.4		42		13-Jan-08		18:25:59		67.4		49.5

		3-Dec-07		20:07:10		68.61		41		3-Dec-07		20:06:20		67.4		44.5		3-Dec-07		20:07:53		67.4		43		13-Jan-08		20:25:59		66.2		49.5

		3-Dec-07		22:07:10		68.61		44.5		3-Dec-07		22:06:20		66.81		50		3-Dec-07		22:07:53		66.2		47.5		13-Jan-08		22:25:59		65.6		49

		4-Dec-07		0:07:10		68.61		43		4-Dec-07		0:06:20		66.81		47		4-Dec-07		0:07:53		66.2		46.5		14-Jan-08		0:25:59		65.01		48

		4-Dec-07		2:07:10		68.61		42		4-Dec-07		2:06:20		66.81		45.5		4-Dec-07		2:07:53		66.2		45.5		14-Jan-08		2:25:59		64.4		48.5

		4-Dec-07		4:07:10		68.61		40.5		4-Dec-07		4:06:20		67.4		43		4-Dec-07		4:07:53		66.2		44.5		14-Jan-08		4:25:59		64.4		49

		4-Dec-07		6:07:10		68.61		40		4-Dec-07		6:06:20		67.4		42		4-Dec-07		6:07:53		66.2		44		14-Jan-08		6:25:59		64.4		49.5

		4-Dec-07		8:07:10		71.6		37		4-Dec-07		8:06:20		69.2		39		4-Dec-07		8:07:53		69.2		41		14-Jan-08		8:25:59		65.01		50.5

		4-Dec-07		10:07:10		72.8		39		4-Dec-07		10:06:20		71		42		4-Dec-07		10:07:53		70.41		43.5		14-Jan-08		10:25:59		65.6		49.5

		4-Dec-07		12:07:10		74.6		37.5		4-Dec-07		12:06:20		71.6		39		4-Dec-07		12:07:53		71		38.5		14-Jan-08		12:25:59		66.2		49

		4-Dec-07		14:07:10		73.4		38		4-Dec-07		14:06:20		71		42.5		4-Dec-07		14:07:53		71		39.5		14-Jan-08		14:25:59		66.81		48.5

		4-Dec-07		16:07:10		74.01		39.5		4-Dec-07		16:06:20		71.6		41.5		4-Dec-07		16:07:53		70.41		40		14-Jan-08		16:25:59		66.81		49

		4-Dec-07		18:07:10		74.01		40		4-Dec-07		18:06:20		70.41		42		4-Dec-07		18:07:53		71		45		14-Jan-08		18:25:59		66.81		49.5

		4-Dec-07		20:07:10		72.8		40.5		4-Dec-07		20:06:20		69.8		44		4-Dec-07		20:07:53		70.41		44		14-Jan-08		20:25:59		66.2		49

		4-Dec-07		22:07:10		72.21		44		4-Dec-07		22:06:20		69.8		50.5		4-Dec-07		22:07:53		69.8		46.5		14-Jan-08		22:25:59		65.01		49

		5-Dec-07		0:07:10		72.21		47		5-Dec-07		0:06:20		69.2		53.5		5-Dec-07		0:07:53		69.8		49.5		15-Jan-08		0:25:59		64.4		47.5

		5-Dec-07		2:07:10		71.6		48.5		5-Dec-07		2:06:20		69.2		54.5		5-Dec-07		2:07:53		69.2		51		15-Jan-08		2:25:59		63.8		47

		5-Dec-07		4:07:10		71		49.5		5-Dec-07		4:06:20		69.2		55		5-Dec-07		4:07:53		68.61		52.5		15-Jan-08		4:25:59		63.8		46.5

		5-Dec-07		6:07:10		71		50.5		5-Dec-07		6:06:20		68.61		56		5-Dec-07		6:07:53		68		53.5		15-Jan-08		6:25:59		64.4		46.5

		5-Dec-07		8:07:10		73.4		50		5-Dec-07		8:06:20		69.8		57.5		5-Dec-07		8:07:53		71		53		15-Jan-08		8:25:59		67.4		44

		5-Dec-07		10:07:10		74.01		49		5-Dec-07		10:06:20		71		44		5-Dec-07		10:07:53		71		57.5		15-Jan-08		10:25:59		71		43.5

		5-Dec-07		12:07:10		74.01		48		5-Dec-07		12:06:20		71.6		54		5-Dec-07		12:07:53		71		51		15-Jan-08		12:25:59		70.41		43

		5-Dec-07		14:07:10		74.01		49		5-Dec-07		14:06:20		71.6		54		5-Dec-07		14:07:53		71		48.5		15-Jan-08		14:25:59		69.8		44

		5-Dec-07		16:07:10		74.01		51		5-Dec-07		16:06:20		71.6		54		5-Dec-07		16:07:53		71		59.5		15-Jan-08		16:25:59		70.41		45

		5-Dec-07		18:07:10		73.4		50.5		5-Dec-07		18:06:20		69.8		57		5-Dec-07		18:07:53		71		47.5		15-Jan-08		18:25:59		71.6		43.5

		5-Dec-07		20:07:10		73.4		50		5-Dec-07		20:06:20		69.8		56		5-Dec-07		20:07:53		71		54.5		15-Jan-08		20:25:59		69.2		43

		5-Dec-07		22:07:10		72.8		50.5		5-Dec-07		22:06:20		69.8		56.5		5-Dec-07		22:07:53		70.41		55		15-Jan-08		22:25:59		66.81		43.5

		6-Dec-07		0:07:10		72.21		51.5		6-Dec-07		0:06:20		69.2		57		6-Dec-07		0:07:53		70.41		54.5		16-Jan-08		0:25:59		65.01		43.5

		6-Dec-07		2:07:10		71.6		51.5		6-Dec-07		2:06:20		69.2		57		6-Dec-07		2:07:53		69.8		54		16-Jan-08		2:25:59		64.4		43.5

		6-Dec-07		4:07:10		71.6		52		6-Dec-07		4:06:20		68.61		57.5		6-Dec-07		4:07:53		69.8		54		16-Jan-08		4:25:59		63.8		43.5

		6-Dec-07		6:07:10		71		50		6-Dec-07		6:06:20		68		54		6-Dec-07		6:07:53		69.2		53		16-Jan-08		6:25:59		64.4		42.5

		6-Dec-07		8:07:10		72.8		47.5		6-Dec-07		8:06:20		69.8		52		6-Dec-07		8:07:53		71		52		16-Jan-08		8:25:59		66.81		39.5

		6-Dec-07		10:07:10		74.01		45.5		6-Dec-07		10:06:20		71		45		6-Dec-07		10:07:53		71		50		16-Jan-08		10:25:59		70.41		38

		6-Dec-07		12:07:10		74.01		46		6-Dec-07		12:06:20		71		55		6-Dec-07		12:07:53		71		48		16-Jan-08		12:25:59		71		39.5

		6-Dec-07		14:07:10		74.01		46		6-Dec-07		14:06:20		71		57		6-Dec-07		14:07:53		71		54.5		16-Jan-08		14:25:59		72.21		40.5

		6-Dec-07		16:07:10		74.6		47.5		6-Dec-07		16:06:20		71		47.5		6-Dec-07		16:07:53		70.41		51.5		16-Jan-08		16:25:59		72.21		43

		6-Dec-07		18:07:10		74.01		39		6-Dec-07		18:06:20		69.8		41		6-Dec-07		18:07:53		69.8		45		16-Jan-08		18:25:59		72.8		41.5

		6-Dec-07		20:07:10		73.4		38		6-Dec-07		20:06:20		69.8		40		6-Dec-07		20:07:53		69.8		43.5		16-Jan-08		20:25:59		71		41.5

		6-Dec-07		22:07:10		72.21		40		6-Dec-07		22:06:20		69.2		44		6-Dec-07		22:07:53		70.41		44		16-Jan-08		22:25:59		68.61		41.5

		7-Dec-07		0:07:10		71.6		42		7-Dec-07		0:06:20		68		47		7-Dec-07		0:07:53		69.8		44.5		17-Jan-08		0:25:59		66.2		41.5

		7-Dec-07		2:07:10		70.41		42.5		7-Dec-07		2:06:20		67.4		48		7-Dec-07		2:07:53		69.2		45		17-Jan-08		2:25:59		65.01		41.5

		7-Dec-07		4:07:10		69.8		43		7-Dec-07		4:06:20		66.81		48.5		7-Dec-07		4:07:53		68.61		45.5		17-Jan-08		4:25:59		64.4		41.5

		7-Dec-07		6:07:10		69.8		43.5		7-Dec-07		6:06:20		66.81		49		7-Dec-07		6:07:53		68		46.5		17-Jan-08		6:25:59		65.01		39.5

		7-Dec-07		8:07:10		72.21		42		7-Dec-07		8:06:20		68.61		47.5		7-Dec-07		8:07:53		70.41		45		17-Jan-08		8:25:59		66.81		36.5

		7-Dec-07		10:07:10		73.4		42.5		7-Dec-07		10:06:20		71		49.5		7-Dec-07		10:07:53		71		48		17-Jan-08		10:25:59		71		33

		7-Dec-07		12:07:10		72.8		45		7-Dec-07		12:06:20		71		44.5		7-Dec-07		12:07:53		70.41		50.5		17-Jan-08		12:25:59		71.6		27

		7-Dec-07		14:07:10		72.21		47		7-Dec-07		14:06:20		71		47		7-Dec-07		14:07:53		71.6		52.5		17-Jan-08		14:25:59		72.8		25.5

		7-Dec-07		16:07:10		72.21		46		7-Dec-07		16:06:20		71		50		7-Dec-07		16:07:53		70.41		50		17-Jan-08		16:25:59		72.21		23.5

		7-Dec-07		18:07:10		72.21		45.5		7-Dec-07		18:06:20		69.2		50.5		7-Dec-07		18:07:53		70.41		51.5		17-Jan-08		18:25:59		72.21		23

		7-Dec-07		20:07:10		71		47		7-Dec-07		20:06:20		68.61		51		7-Dec-07		20:07:53		69.8		49		17-Jan-08		20:25:59		71.6		23

		7-Dec-07		22:07:10		69.8		47.5		7-Dec-07		22:06:20		67.4		52.5		7-Dec-07		22:07:53		69.8		48.5		17-Jan-08		22:25:59		69.2		24.5

		8-Dec-07		0:07:10		69.2		48		8-Dec-07		0:06:20		66.81		52.5		8-Dec-07		0:07:53		69.2		49		18-Jan-08		0:25:59		67.4		25.5

		8-Dec-07		2:07:10		68.61		44.5		8-Dec-07		2:06:20		66.81		47		8-Dec-07		2:07:53		68		46.5		18-Jan-08		2:25:59		66.2		26

		8-Dec-07		4:07:10		68.61		44		8-Dec-07		4:06:20		66.2		47		8-Dec-07		4:07:53		66.81		47		18-Jan-08		4:25:59		65.01		26

		8-Dec-07		6:07:10		68		43		8-Dec-07		6:06:20		66.2		45.5		8-Dec-07		6:07:53		67.4		45		18-Jan-08		6:25:59		66.2		26.5

		8-Dec-07		8:07:10		71		39		8-Dec-07		8:06:20		68		41		8-Dec-07		8:07:53		69.8		42		18-Jan-08		8:25:59		68.61		26

		8-Dec-07		10:07:10		72.21		37		8-Dec-07		10:06:20		69.8		40.5		8-Dec-07		10:07:53		71.6		40.5		18-Jan-08		10:25:59		72.21		27.5

		8-Dec-07		12:07:10		71.6		37.5		8-Dec-07		12:06:20		71		40.5		8-Dec-07		12:07:53		71		41		18-Jan-08		12:25:59		71.6		28

		8-Dec-07		14:07:10		71.6		36.5		8-Dec-07		14:06:20		71		40		8-Dec-07		14:07:53		71		35		18-Jan-08		14:25:59		72.21		29.5

		8-Dec-07		16:07:10		71.6		35.5		8-Dec-07		16:06:20		71		38		8-Dec-07		16:07:53		70.41		38.5		18-Jan-08		16:25:59		72.8		29

		8-Dec-07		18:07:10		71.6		35.5		8-Dec-07		18:06:20		69.8		35.5		8-Dec-07		18:07:53		69.8		37.5		18-Jan-08		18:25:59		72.21		30

		8-Dec-07		20:07:10		70.41		35		8-Dec-07		20:06:20		67.4		36.5		8-Dec-07		20:07:53		69.2		37		18-Jan-08		20:25:59		71.6		31.5

		8-Dec-07		22:07:10		69.2		33.5		8-Dec-07		22:06:20		66.81		36		8-Dec-07		22:07:53		67.4		37		18-Jan-08		22:25:59		68.61		32

		9-Dec-07		0:07:10		68.61		33.5		9-Dec-07		0:06:20		66.81		35.5		9-Dec-07		0:07:53		66.2		37		19-Jan-08		0:25:59		66.81		32.5

		9-Dec-07		2:07:10		68		33		9-Dec-07		2:06:20		66.2		35		9-Dec-07		2:07:53		65.6		37		19-Jan-08		2:25:59		65.01		33

		9-Dec-07		4:07:10		68		32.5		9-Dec-07		4:06:20		66.2		34		9-Dec-07		4:07:53		64.4		37		19-Jan-08		4:25:59		64.4		33

		9-Dec-07		6:07:10		67.4		32		9-Dec-07		6:06:20		66.2		33.5		9-Dec-07		6:07:53		63.8		36.5		19-Jan-08		6:25:59		66.2		32

		9-Dec-07		8:07:10		68		30.5		9-Dec-07		8:06:20		67.4		31.5		9-Dec-07		8:07:53		67.4		33		19-Jan-08		8:25:59		68.61		30

		9-Dec-07		10:07:10		68.61		30.5		9-Dec-07		10:06:20		68		31		9-Dec-07		10:07:53		68.61		31.5		19-Jan-08		10:25:59		70.41		31

		9-Dec-07		12:07:10		68.61		29.5		9-Dec-07		12:06:20		68.61		29		9-Dec-07		12:07:53		69.8		30		19-Jan-08		12:25:59		71		32.5

		9-Dec-07		14:07:10		68.61		28.5		9-Dec-07		14:06:20		68		28		9-Dec-07		14:07:53		70.41		30		19-Jan-08		14:25:59		71.6		33

		9-Dec-07		16:07:10		69.2		25		9-Dec-07		16:06:20		68		22.5		9-Dec-07		16:07:53		69.2		28.5		19-Jan-08		16:25:59		72.8		32.5

		9-Dec-07		18:07:10		69.2		24		9-Dec-07		18:06:20		68		23		9-Dec-07		18:07:53		68.61		27.5		19-Jan-08		18:25:59		72.8		33

		9-Dec-07		20:07:10		68.61		24		9-Dec-07		20:06:20		67.4		23.5		9-Dec-07		20:07:53		67.4		27		19-Jan-08		20:25:59		72.21		32

		9-Dec-07		22:07:10		68		24		9-Dec-07		22:06:20		66.81		24		9-Dec-07		22:07:53		66.2		27		19-Jan-08		22:25:59		68		34.5

		10-Dec-07		0:07:10		67.4		24		10-Dec-07		0:06:20		66.2		24.5		10-Dec-07		0:07:53		65.6		27.5		20-Jan-08		0:25:59		66.2		34.5

		10-Dec-07		2:07:10		67.4		24.5		10-Dec-07		2:06:20		66.2		25		10-Dec-07		2:07:53		64.4		28		20-Jan-08		2:25:59		65.01		34.5

		10-Dec-07		4:07:10		66.81		25		10-Dec-07		4:06:20		65.6		26.5		10-Dec-07		4:07:53		63.8		28.5		20-Jan-08		4:25:59		63.8		34

		10-Dec-07		6:07:10		66.2		26		10-Dec-07		6:06:20		65.6		28		10-Dec-07		6:07:53		63.21		29.5		20-Jan-08		6:25:59		63.21		33.5

		10-Dec-07		8:07:10		66.81		26		10-Dec-07		8:06:20		67.4		27		10-Dec-07		8:07:53		68.61		26.5		20-Jan-08		8:25:59		63.21		32.5

		10-Dec-07		10:07:10		67.4		26.5		10-Dec-07		10:06:20		67.4		27.5		10-Dec-07		10:07:53		67.4		27.5		20-Jan-08		10:25:59		63.21		33

		10-Dec-07		12:07:10		68		27.5		10-Dec-07		12:06:20		68		28		10-Dec-07		12:07:53		68		29		20-Jan-08		12:25:59		63.8		37

		10-Dec-07		14:07:10		68.61		28.5		10-Dec-07		14:06:20		68		29.5		10-Dec-07		14:07:53		68		30		20-Jan-08		14:25:59		65.01		39

		10-Dec-07		16:07:10		69.2		28.5		10-Dec-07		16:06:20		68.61		29		10-Dec-07		16:07:53		68		31.5		20-Jan-08		16:25:59		66.2		37.5

		10-Dec-07		18:07:10		69.2		30		10-Dec-07		18:06:20		68		31.5		10-Dec-07		18:07:53		67.4		32.5		20-Jan-08		18:25:59		66.81		37

		10-Dec-07		20:07:10		68.61		31		10-Dec-07		20:06:20		66.81		33.5		10-Dec-07		20:07:53		66.81		33.5		20-Jan-08		20:25:59		65.6		37

		10-Dec-07		22:07:10		68		32.5		10-Dec-07		22:06:20		66.2		35.5		10-Dec-07		22:07:53		65.6		35		20-Jan-08		22:25:59		65.01		37

		11-Dec-07		0:07:10		67.4		33.5		11-Dec-07		0:06:20		66.2		36.5		11-Dec-07		0:07:53		65.01		36.5		21-Jan-08		0:25:59		64.4		37

		11-Dec-07		2:07:10		66.81		32		11-Dec-07		2:06:20		66.2		34.5		11-Dec-07		2:07:53		64.4		36		21-Jan-08		2:25:59		63.8		38

		11-Dec-07		4:07:10		66.81		31.5		11-Dec-07		4:06:20		66.2		33		11-Dec-07		4:07:53		63.21		35.5		21-Jan-08		4:25:59		63.8		38.5

		11-Dec-07		6:07:10		66.81		30.5		11-Dec-07		6:06:20		66.2		32		11-Dec-07		6:07:53		67.4		31.5		21-Jan-08		6:25:59		63.21		38

		11-Dec-07		8:07:10		68.61		28.5		11-Dec-07		8:06:20		67.4		30		11-Dec-07		8:07:53		68		30.5		21-Jan-08		8:25:59		63.21		38

		11-Dec-07		10:07:10		69.2		30		11-Dec-07		10:06:20		69.8		31.5		11-Dec-07		10:07:53		69.2		31		21-Jan-08		10:25:59		63.8		38

		11-Dec-07		12:07:10		71.6		31.5		11-Dec-07		12:06:20		70.41		34		11-Dec-07		12:07:53		71.6		32.5		21-Jan-08		12:25:59		65.01		39

		11-Dec-07		14:07:10		71.6		32.5		11-Dec-07		14:06:20		70.41		34		11-Dec-07		14:07:53		71		35.5		21-Jan-08		14:25:59		65.6		36

		11-Dec-07		16:07:10		72.21		32.5		11-Dec-07		16:06:20		69.8		34.5		11-Dec-07		16:07:53		71		35		21-Jan-08		16:25:59		65.6		36

		11-Dec-07		18:07:10		72.21		31		11-Dec-07		18:06:20		69.8		31		11-Dec-07		18:07:53		71		34.5		21-Jan-08		18:25:59		65.6		35.5

		11-Dec-07		20:07:10		70.41		32.5		11-Dec-07		20:06:20		67.4		36		11-Dec-07		20:07:53		70.41		33.5		21-Jan-08		20:25:59		65.01		36

		11-Dec-07		22:07:10		69.2		27		11-Dec-07		22:06:20		66.81		26.5		11-Dec-07		22:07:53		68		31		21-Jan-08		22:25:59		63.8		36.5

		12-Dec-07		0:07:10		68.61		25		12-Dec-07		0:06:20		66.81		24		12-Dec-07		0:07:53		66.81		29		22-Jan-08		0:25:59		63.21		36

		12-Dec-07		2:07:10		68		22		12-Dec-07		2:06:20		66.81		20		12-Dec-07		2:07:53		66.2		26		22-Jan-08		2:25:59		63.21		35

		12-Dec-07		4:07:10		67.4		19.5		12-Dec-07		4:06:20		66.2		17		12-Dec-07		4:07:53		65.6		23.5		22-Jan-08		4:25:59		62.6		33.5

		12-Dec-07		6:07:10		67.4		18.5		12-Dec-07		6:06:20		66.2		16.5		12-Dec-07		6:07:53		65.01		22.5		22-Jan-08		6:25:59		64.4		32.5

		12-Dec-07		8:07:10		69.8		17.5		12-Dec-07		8:06:20		68		16		12-Dec-07		8:07:53		68		20.5		22-Jan-08		8:25:59		66.81		31

		12-Dec-07		10:07:10		71.6		19.5		12-Dec-07		10:06:20		70.41		20		12-Dec-07		10:07:53		71		22		22-Jan-08		10:25:59		69.8		31.5

		12-Dec-07		12:07:10		72.21		18.5		12-Dec-07		12:06:20		71		18		12-Dec-07		12:07:53		71		22.5		22-Jan-08		12:25:59		74.6		30.5

		12-Dec-07		14:07:10		72.21		17.5		12-Dec-07		14:06:20		71		18.5		12-Dec-07		14:07:53		71.6		23		22-Jan-08		14:25:59		72.8		34

		12-Dec-07		16:07:10		72.21		17		12-Dec-07		16:06:20		71		19		12-Dec-07		16:07:53		70.41		22		22-Jan-08		16:25:59		73.4		34.5

		12-Dec-07		18:07:10		72.21		19		12-Dec-07		18:06:20		69.2		19		12-Dec-07		18:07:53		70.41		23.5		22-Jan-08		18:25:59		73.4		33.5

		12-Dec-07		20:07:10		70.41		22		12-Dec-07		20:06:20		67.4		24		12-Dec-07		20:07:53		69.8		24		22-Jan-08		20:25:59		72.21		34

		12-Dec-07		22:07:10		69.2		22.5		12-Dec-07		22:06:20		66.81		26		12-Dec-07		22:07:53		68.61		25		22-Jan-08		22:25:59		67.4		36

		13-Dec-07		0:07:10		68.61		23		13-Dec-07		0:06:20		66.2		26		13-Dec-07		0:07:53		66.81		25.5		23-Jan-08		0:25:59		65.6		37.5

		13-Dec-07		2:07:10		67.4		23		13-Dec-07		2:06:20		66.2		26		13-Dec-07		2:07:53		65.01		26.5		23-Jan-08		2:25:59		64.4		38

		13-Dec-07		4:07:10		66.81		23.5		13-Dec-07		4:06:20		66.2		25.5		13-Dec-07		4:07:53		63.8		27.5		23-Jan-08		4:25:59		63.8		38

		13-Dec-07		6:07:10		67.4		24.5		13-Dec-07		6:06:20		66.2		27		13-Dec-07		6:07:53		67.4		25.5		23-Jan-08		6:25:59		66.2		37.5

		13-Dec-07		8:07:10		70.41		24.5		13-Dec-07		8:06:20		68		27		13-Dec-07		8:07:53		68.61		26.5		23-Jan-08		8:25:59		68.61		34.5

		13-Dec-07		10:07:10		71.6		25		13-Dec-07		10:06:20		70.41		27.5		13-Dec-07		10:07:53		70.41		27.5		23-Jan-08		10:25:59		72.21		33

		13-Dec-07		12:07:10		72.21		26.5		13-Dec-07		12:06:20		71		28.5		13-Dec-07		12:07:53		70.41		30		23-Jan-08		12:25:59		74.01		31.5

		13-Dec-07		14:07:10		72.21		25.5		13-Dec-07		14:06:20		71		27		13-Dec-07		14:07:53		70.41		30.5		23-Jan-08		14:25:59		72.8		31.5

		13-Dec-07		16:07:10		72.21		22.5		13-Dec-07		16:06:20		71		23.5		13-Dec-07		16:07:53		70.41		28		23-Jan-08		16:25:59		72.21		31.5

		13-Dec-07		18:07:10		72.8		23.5		13-Dec-07		18:06:20		69.8		24		13-Dec-07		18:07:53		69.8		27.5		23-Jan-08		18:25:59		72.8		30.5

		13-Dec-07		20:07:10		70.41		25.5		13-Dec-07		20:06:20		67.4		28.5		13-Dec-07		20:07:53		69.2		28		23-Jan-08		20:25:59		72.8		30

		13-Dec-07		22:07:10		69.2		25.5		13-Dec-07		22:06:20		66.81		29		13-Dec-07		22:07:53		68		28.5		23-Jan-08		22:25:59		68		32

		14-Dec-07		0:07:10		68		26		14-Dec-07		0:06:20		66.2		29		14-Dec-07		0:07:53		66.2		29		24-Jan-08		0:25:59		65.6		33

		14-Dec-07		2:07:10		67.4		26.5		14-Dec-07		2:06:20		66.2		29		14-Dec-07		2:07:53		64.4		30		24-Jan-08		2:25:59		64.4		34

		14-Dec-07		4:07:10		66.81		26		14-Dec-07		4:06:20		66.2		28.5		14-Dec-07		4:07:53		63.21		30.5		24-Jan-08		4:25:59		63.8		35

		14-Dec-07		6:07:10		66.81		25.5		14-Dec-07		6:06:20		66.2		27		14-Dec-07		6:07:53		66.2		27		24-Jan-08		6:25:59		65.6		36

		14-Dec-07		8:07:10		69.2		24		14-Dec-07		8:06:20		67.4		26		14-Dec-07		8:07:53		68.61		26.5		24-Jan-08		8:25:59		68		34.5

		14-Dec-07		10:07:10		69.8		26		14-Dec-07		10:06:20		69.8		28		14-Dec-07		10:07:53		69.8		27.5		24-Jan-08		10:25:59		71.6		34.5

		14-Dec-07		12:07:10		71		28		14-Dec-07		12:06:20		70.41		30.5		14-Dec-07		12:07:53		71.6		28.5		24-Jan-08		12:25:59		74.01		33.5

		14-Dec-07		14:07:10		71.6		28		14-Dec-07		14:06:20		71		29.5		14-Dec-07		14:07:53		71		28.5		24-Jan-08		14:25:59		71.6		35

		14-Dec-07		16:07:10		72.21		29		14-Dec-07		16:06:20		71.6		30		14-Dec-07		16:07:53		69.8		32		24-Jan-08		16:25:59		72.21		34.5

		14-Dec-07		18:07:10		73.4		30		14-Dec-07		18:06:20		69.8		33		14-Dec-07		18:07:53		70.41		33.5		24-Jan-08		18:25:59		72.21		33.5

		14-Dec-07		20:07:10		71		30.5		14-Dec-07		20:06:20		69.2		33		14-Dec-07		20:07:53		69.2		32		24-Jan-08		20:25:59		72.21		33.5

		14-Dec-07		22:07:10		69.2		29.5		14-Dec-07		22:06:20		66.81		32.5		14-Dec-07		22:07:53		68		31.5		24-Jan-08		22:25:59		68		36

		15-Dec-07		0:07:10		68		29		15-Dec-07		0:06:20		66.2		32		15-Dec-07		0:07:53		65.6		32		25-Jan-08		0:25:59		65.6		36.5

		15-Dec-07		2:07:10		67.4		28		15-Dec-07		2:06:20		66.2		30.5		15-Dec-07		2:07:53		63.8		32		25-Jan-08		2:25:59		65.01		37.5

		15-Dec-07		4:07:10		66.81		27		15-Dec-07		4:06:20		65.6		29		15-Dec-07		4:07:53		63.21		31.5		25-Jan-08		4:25:59		64.4		38.5

		15-Dec-07		6:07:10		66.81		27		15-Dec-07		6:06:20		66.2		28.5		15-Dec-07		6:07:53		67.4		27.5		25-Jan-08		6:25:59		66.2		38

		15-Dec-07		8:07:10		68.61		25		15-Dec-07		8:06:20		67.4		26		15-Dec-07		8:07:53		68.61		27		25-Jan-08		8:25:59		69.2		36

		15-Dec-07		10:07:10		70.41		27		15-Dec-07		10:06:20		69.8		28.5		15-Dec-07		10:07:53		70.41		28.5		25-Jan-08		10:25:59		72.8		36

		15-Dec-07		12:07:10		71.6		29.5		15-Dec-07		12:06:20		71		29.5		15-Dec-07		12:07:53		71.6		30		25-Jan-08		12:25:59		74.01		34.5

		15-Dec-07		14:07:10		71.6		30.5		15-Dec-07		14:06:20		71		31.5		15-Dec-07		14:07:53		70.41		30		25-Jan-08		14:25:59		73.4		35

		15-Dec-07		16:07:10		71.6		30.5		15-Dec-07		16:06:20		71		31.5		15-Dec-07		16:07:53		71		32.5		25-Jan-08		16:25:59		74.01		35.5

		15-Dec-07		18:07:10		72.8		33		15-Dec-07		18:06:20		69.8		37		15-Dec-07		18:07:53		70.41		35.5		25-Jan-08		18:25:59		72.8		35

		15-Dec-07		20:07:10		71		34.5		15-Dec-07		20:06:20		67.4		39		15-Dec-07		20:07:53		69.2		35.5		25-Jan-08		20:25:59		72.21		34

		15-Dec-07		22:07:10		69.2		33.5		15-Dec-07		22:06:20		66.81		37.5		15-Dec-07		22:07:53		67.4		35.5		25-Jan-08		22:25:59		69.2		36

		16-Dec-07		0:07:10		68.61		34		16-Dec-07		0:06:20		66.2		38		16-Dec-07		0:07:53		66.2		36.5		26-Jan-08		0:25:59		67.4		36.5

		16-Dec-07		2:07:10		68		34		16-Dec-07		2:06:20		66.2		38		16-Dec-07		2:07:53		65.6		37.5		26-Jan-08		2:25:59		66.2		37

		16-Dec-07		4:07:10		68		35		16-Dec-07		4:06:20		66.2		39		16-Dec-07		4:07:53		65.01		38.5		26-Jan-08		4:25:59		65.6		37

		16-Dec-07		6:07:10		67.4		35		16-Dec-07		6:06:20		66.2		38		16-Dec-07		6:07:53		64.4		39		26-Jan-08		6:25:59		66.81		37

		16-Dec-07		8:07:10		68		34		16-Dec-07		8:06:20		67.4		36.5		16-Dec-07		8:07:53		66.81		37		26-Jan-08		8:25:59		70.41		37

		16-Dec-07		10:07:10		68		34.5		16-Dec-07		10:06:20		67.4		36.5		16-Dec-07		10:07:53		66.81		36		26-Jan-08		10:25:59		73.4		38

		16-Dec-07		12:07:10		68		35		16-Dec-07		12:06:20		68		37		16-Dec-07		12:07:53		67.4		36.5		26-Jan-08		12:25:59		72.8		39

		16-Dec-07		14:07:10		68.61		37		16-Dec-07		14:06:20		68		39.5		16-Dec-07		14:07:53		66.81		39		26-Jan-08		14:25:59		73.4		39.5

		16-Dec-07		16:07:10		69.2		39		16-Dec-07		16:06:20		68		42.5		16-Dec-07		16:07:53		67.4		41.5		26-Jan-08		16:25:59		73.4		39.5

		16-Dec-07		18:07:10		69.2		40.5		16-Dec-07		18:06:20		68		44		16-Dec-07		18:07:53		68		42.5		26-Jan-08		18:25:59		73.4		40

		16-Dec-07		20:07:10		68.61		40.5		16-Dec-07		20:06:20		66.81		44		16-Dec-07		20:07:53		67.4		42		26-Jan-08		20:25:59		72.8		41

		16-Dec-07		22:07:10		68		40.5		16-Dec-07		22:06:20		66.81		44		16-Dec-07		22:07:53		66.2		43		26-Jan-08		22:25:59		69.8		43

		17-Dec-07		0:07:10		68		41		17-Dec-07		0:06:20		66.2		44.5		17-Dec-07		0:07:53		66.2		43.5		27-Jan-08		0:25:59		68		44

		17-Dec-07		2:07:10		67.4		41		17-Dec-07		2:06:20		66.2		44.5		17-Dec-07		2:07:53		65.6		44		27-Jan-08		2:25:59		67.4		45.5

		17-Dec-07		4:07:10		67.4		40.5		17-Dec-07		4:06:20		66.2		44.5		17-Dec-07		4:07:53		65.01		44		27-Jan-08		4:25:59		66.81		46.5

		17-Dec-07		6:07:10		66.81		40.5		17-Dec-07		6:06:20		66.2		43.5		17-Dec-07		6:07:53		65.01		43.5		27-Jan-08		6:25:59		66.2		47

		17-Dec-07		8:07:10		68		40		17-Dec-07		8:06:20		67.4		42.5		17-Dec-07		8:07:53		66.81		41.5		27-Jan-08		8:25:59		66.2		46.5

		17-Dec-07		10:07:10		68		40.5		17-Dec-07		10:06:20		67.4		43		17-Dec-07		10:07:53		67.4		42		27-Jan-08		10:25:59		66.2		45.5

		17-Dec-07		12:07:10		68		40.5		17-Dec-07		12:06:20		67.4		42.5		17-Dec-07		12:07:53		67.4		42.5		27-Jan-08		12:25:59		66.81		45

		17-Dec-07		14:07:10		68.61		37		17-Dec-07		14:06:20		68		37		17-Dec-07		14:07:53		67.4		40		27-Jan-08		14:25:59		67.4		46

		17-Dec-07		16:07:10		68.61		37.5		17-Dec-07		16:06:20		67.4		39.5		17-Dec-07		16:07:53		67.4		40.5		27-Jan-08		16:25:59		68		45.5

		17-Dec-07		18:07:10		68.61		38		17-Dec-07		18:06:20		68		39.5		17-Dec-07		18:07:53		67.4		40		27-Jan-08		18:25:59		67.4		44.5

		17-Dec-07		20:07:10		68		40		17-Dec-07		20:06:20		66.81		43.5		17-Dec-07		20:07:53		66.81		42		27-Jan-08		20:25:59		66.81		44

		17-Dec-07		22:07:10		68		42.5		17-Dec-07		22:06:20		66.2		47		17-Dec-07		22:07:53		65.6		45		27-Jan-08		22:25:59		66.2		44

		18-Dec-07		0:07:10		67.4		43.5		18-Dec-07		0:06:20		66.2		48.5		18-Dec-07		0:07:53		65.6		46.5		28-Jan-08		0:25:59		66.2		44.5

		18-Dec-07		2:07:10		67.4		43.5		18-Dec-07		2:06:20		66.81		46.5		18-Dec-07		2:07:53		65.6		46.5		28-Jan-08		2:25:59		66.2		46

		18-Dec-07		4:07:10		67.4		42		18-Dec-07		4:06:20		66.2		44.5		18-Dec-07		4:07:53		65.01		45.5		28-Jan-08		4:25:59		65.6		46.5

		18-Dec-07		6:07:10		67.4		43		18-Dec-07		6:06:20		66.2		46		18-Dec-07		6:07:53		66.81		43.5		28-Jan-08		6:25:59		65.6		47

		18-Dec-07		8:07:10		69.8		41		18-Dec-07		8:06:20		68		44.5		18-Dec-07		8:07:53		69.2		43		28-Jan-08		8:25:59		65.6		47.5

		18-Dec-07		10:07:10		71		42		18-Dec-07		10:06:20		71		39		18-Dec-07		10:07:53		71.6		41.5		28-Jan-08		10:25:59		66.81		47.5

		18-Dec-07		12:07:10		71.6		41		18-Dec-07		12:06:20		71.6		43.5		18-Dec-07		12:07:53		71.6		43.5		28-Jan-08		12:25:59		68		47

		18-Dec-07		14:07:10		71.6		41		18-Dec-07		14:06:20		71		45		18-Dec-07		14:07:53		71		45.5		28-Jan-08		14:25:59		68.61		46.5

		18-Dec-07		16:07:10		72.21		44		18-Dec-07		16:06:20		71		39.5		18-Dec-07		16:07:53		71		46		28-Jan-08		16:25:59		68.61		46.5

		18-Dec-07		18:07:10		72.21		42		18-Dec-07		18:06:20		69.2		45		18-Dec-07		18:07:53		71.6		40.5		28-Jan-08		18:25:59		69.2		46.5

		18-Dec-07		20:07:10		71		41.5		18-Dec-07		20:06:20		68		45		18-Dec-07		20:07:53		70.41		42.5		28-Jan-08		20:25:59		67.4		47.5

		18-Dec-07		22:07:10		69.8		43		18-Dec-07		22:06:20		66.81		48.5		18-Dec-07		22:07:53		68.61		44.5		28-Jan-08		22:25:59		66.2		46

		19-Dec-07		0:07:10		69.2		44		19-Dec-07		0:06:20		66.81		48.5		19-Dec-07		0:07:53		68		45.5		29-Jan-08		0:25:59		65.01		42.5

		19-Dec-07		2:07:10		68.61		44.5		19-Dec-07		2:06:20		66.81		49		19-Dec-07		2:07:53		67.4		46.5		29-Jan-08		2:25:59		64.4		41

		19-Dec-07		4:07:10		68.61		44.5		19-Dec-07		4:06:20		66.81		48.5		19-Dec-07		4:07:53		66.81		47.5		29-Jan-08		4:25:59		64.4		40.5

		19-Dec-07		6:07:10		68		45		19-Dec-07		6:06:20		66.81		48.5		19-Dec-07		6:07:53		68		46		29-Jan-08		6:25:59		66.2		39

		19-Dec-07		8:07:10		70.41		43		19-Dec-07		8:06:20		68.61		46		19-Dec-07		8:07:53		69.8		44.5		29-Jan-08		8:25:59		68.61		37

		19-Dec-07		10:07:10		71.6		42		19-Dec-07		10:06:20		71		48.5		19-Dec-07		10:07:53		71		43.5		29-Jan-08		10:25:59		73.4		35.5

		19-Dec-07		12:07:10		72.21		44		19-Dec-07		12:06:20		71.6		49.5		19-Dec-07		12:07:53		70.41		50		29-Jan-08		12:25:59		71		37

		19-Dec-07		14:07:10		72.21		45.5		19-Dec-07		14:06:20		71		53.5		19-Dec-07		14:07:53		69.8		49.5		29-Jan-08		14:25:59		71.6		36

		19-Dec-07		16:07:10		72.8		45.5		19-Dec-07		16:06:20		71		47		19-Dec-07		16:07:53		70.41		47		29-Jan-08		16:25:59		72.8		35.5

		19-Dec-07		18:07:10		72.21		41.5		19-Dec-07		18:06:20		69.2		44		19-Dec-07		18:07:53		69.8		44.5		29-Jan-08		18:25:59		72.21		35.5

		19-Dec-07		20:07:10		71		41		19-Dec-07		20:06:20		67.4		44.5		19-Dec-07		20:07:53		69.2		43		29-Jan-08		20:25:59		72.21		33.5

		19-Dec-07		22:07:10		69.8		39		19-Dec-07		22:06:20		66.81		42		19-Dec-07		22:07:53		68		42		29-Jan-08		22:25:59		68		36

		20-Dec-07		0:07:10		68.61		38.5		20-Dec-07		0:06:20		66.2		42		20-Dec-07		0:07:53		66.2		42		30-Jan-08		0:25:59		66.2		36

		20-Dec-07		2:07:10		68.61		39		20-Dec-07		2:06:20		66.2		43		20-Dec-07		2:07:53		65.6		43		30-Jan-08		2:25:59		65.01		36

		20-Dec-07		4:07:10		68		40		20-Dec-07		4:06:20		66.2		43.5		20-Dec-07		4:07:53		65.01		44		30-Jan-08		4:25:59		63.8		35

		20-Dec-07		6:07:10		68		40		20-Dec-07		6:06:20		66.2		43.5		20-Dec-07		6:07:53		67.4		41.5		30-Jan-08		6:25:59		66.2		34

		20-Dec-07		8:07:10		70.41		39		20-Dec-07		8:06:20		68		42.5		20-Dec-07		8:07:53		69.8		41		30-Jan-08		8:25:59		69.2		33

		20-Dec-07		10:07:10		72.21		39		20-Dec-07		10:06:20		70.41		42		20-Dec-07		10:07:53		71.6		39.5		30-Jan-08		10:25:59		72.8		33.5

		20-Dec-07		12:07:10		72.21		41		20-Dec-07		12:06:20		71		45.5		20-Dec-07		12:07:53		71.6		43		30-Jan-08		12:25:59		73.4		34

		20-Dec-07		14:07:10		72.8		39.5		20-Dec-07		14:06:20		70.41		47.5		20-Dec-07		14:07:53		71.6		42		30-Jan-08		14:25:59		72.8		37.5

		20-Dec-07		16:07:10		72.21		43		20-Dec-07		16:06:20		70.41		43		20-Dec-07		16:07:53		70.41		46		30-Jan-08		16:25:59		72.8		39.5

		20-Dec-07		18:07:10		72.8		41.5		20-Dec-07		18:06:20		69.2		45.5		20-Dec-07		18:07:53		70.41		44.5		30-Jan-08		18:25:59		72.21		37.5

		20-Dec-07		20:07:10		71.6		42.5		20-Dec-07		20:06:20		68.61		47.5		20-Dec-07		20:07:53		69.8		45		30-Jan-08		20:25:59		72.21		34.5

		20-Dec-07		22:07:10		70.41		44.5		20-Dec-07		22:06:20		68		49.5		20-Dec-07		22:07:53		69.2		46.5		30-Jan-08		22:25:59		69.2		36

		21-Dec-07		0:07:10		69.8		46		21-Dec-07		0:06:20		67.4		51.5		21-Dec-07		0:07:53		68		47.5		31-Jan-08		0:25:59		67.4		36.5

		21-Dec-07		2:07:10		69.2		46		21-Dec-07		2:06:20		67.4		51		21-Dec-07		2:07:53		68		49		31-Jan-08		2:25:59		66.2		36.5

		21-Dec-07		4:07:10		69.2		46.5		21-Dec-07		4:06:20		66.81		51.5		21-Dec-07		4:07:53		67.4		49		31-Jan-08		4:25:59		65.6		37

		21-Dec-07		6:07:10		68.61		44.5		21-Dec-07		6:06:20		66.81		47		21-Dec-07		6:07:53		67.4		47		31-Jan-08		6:25:59		66.81		36

		21-Dec-07		8:07:10		71		38.5		21-Dec-07		8:06:20		68		39		21-Dec-07		8:07:53		69.8		42		31-Jan-08		8:25:59		70.41		34.5

		21-Dec-07		10:07:10		71.6		38.5		21-Dec-07		10:06:20		69.8		38		21-Dec-07		10:07:53		71.6		39.5		31-Jan-08		10:25:59		74.01		34

		21-Dec-07		12:07:10		72.21		37		21-Dec-07		12:06:20		69.8		38.5		21-Dec-07		12:07:53		71		40		31-Jan-08		12:25:59		71		36

		21-Dec-07		14:07:10		72.21		35.5		21-Dec-07		14:06:20		70.41		35		21-Dec-07		14:07:53		71		40.5		31-Jan-08		14:25:59		72.21		35.5

		21-Dec-07		16:07:10		72.21		33		21-Dec-07		16:06:20		70.41		32.5		21-Dec-07		16:07:53		71		35.5		31-Jan-08		16:25:59		72.21		35

		21-Dec-07		18:07:10		71.6		31.5		21-Dec-07		18:06:20		69.2		30.5		21-Dec-07		18:07:53		70.41		34		31-Jan-08		18:25:59		72.21		35.5

		21-Dec-07		20:07:10		69.8		32		21-Dec-07		20:06:20		67.4		34		21-Dec-07		20:07:53		69.2		33.5		31-Jan-08		20:25:59		72.21		35.5

		21-Dec-07		22:07:10		69.2		32		21-Dec-07		22:06:20		66.81		34		21-Dec-07		22:07:53		67.4		34.5		31-Jan-08		22:25:59		69.2		38

		22-Dec-07		0:07:10		68.61		31.5		22-Dec-07		0:06:20		66.2		33.5		22-Dec-07		0:07:53		65.6		35		1-Feb-08		0:25:59		67.4		38.5

		22-Dec-07		2:07:10		68		31		22-Dec-07		2:06:20		66.2		33		22-Dec-07		2:07:53		64.4		35		1-Feb-08		2:25:59		66.2		39

		22-Dec-07		4:07:10		67.4		30		22-Dec-07		4:06:20		66.2		31.5		22-Dec-07		4:07:53		63.21		35		1-Feb-08		4:25:59		65.6		40

		22-Dec-07		6:07:10		67.4		29.5		22-Dec-07		6:06:20		66.2		30.5		22-Dec-07		6:07:53		66.2		31.5		1-Feb-08		6:25:59		66.81		40

		22-Dec-07		8:07:10		69.2		28		22-Dec-07		8:06:20		69.2		29		22-Dec-07		8:07:53		68.61		31.5		1-Feb-08		8:25:59		70.41		39

		22-Dec-07		10:07:10		71		28		22-Dec-07		10:06:20		70.41		30		22-Dec-07		10:07:53		70.41		31		1-Feb-08		10:25:59		73.4		40

		22-Dec-07		12:07:10		71		28.5		22-Dec-07		12:06:20		70.41		29.5		22-Dec-07		12:07:53		71.6		28.5		1-Feb-08		12:25:59		72.21		41

		22-Dec-07		14:07:10		71		26.5		22-Dec-07		14:06:20		69.2		26		22-Dec-07		14:07:53		69.8		30		1-Feb-08		14:25:59		72.8		42.5

		22-Dec-07		16:07:10		71		26.5		22-Dec-07		16:06:20		69.2		26		22-Dec-07		16:07:53		69.2		29.5		1-Feb-08		16:25:59		72.8		44

		22-Dec-07		18:07:10		70.41		26.5		22-Dec-07		18:06:20		69.2		26		22-Dec-07		18:07:53		69.2		29.5		1-Feb-08		18:25:59		72.21		45.5

		22-Dec-07		20:07:10		69.8		28		22-Dec-07		20:06:20		66.81		31		22-Dec-07		20:07:53		68		31.5		1-Feb-08		20:25:59		72.8		41

		22-Dec-07		22:07:10		68.61		28.5		22-Dec-07		22:06:20		66.2		31		22-Dec-07		22:07:53		66.2		31.5		1-Feb-08		22:25:59		69.8		42

		23-Dec-07		0:07:10		68		28		23-Dec-07		0:06:20		65.6		31		23-Dec-07		0:07:53		64.4		31.5		2-Feb-08		0:25:59		67.4		41.5

		23-Dec-07		2:07:10		66.81		27.5		23-Dec-07		2:06:20		65.6		30		23-Dec-07		2:07:53		63.21		32		2-Feb-08		2:25:59		65.6		40.5

		23-Dec-07		4:07:10		66.81		27		23-Dec-07		4:06:20		65.6		29.5		23-Dec-07		4:07:53		62		31.5		2-Feb-08		4:25:59		64.4		39.5

		23-Dec-07		6:07:10		66.2		26.5		23-Dec-07		6:06:20		65.6		28		23-Dec-07		6:07:53		61.41		31.5		2-Feb-08		6:25:59		65.6		37

		23-Dec-07		8:07:10		66.81		26.5		23-Dec-07		8:06:20		66.81		28		23-Dec-07		8:07:53		67.4		28		2-Feb-08		8:25:59		68		34.5

		23-Dec-07		10:07:10		67.4		28		23-Dec-07		10:06:20		67.4		29.5		23-Dec-07		10:07:53		68		28		2-Feb-08		10:25:59		71		38.5

		23-Dec-07		12:07:10		67.4		30		23-Dec-07		12:06:20		67.4		31.5		23-Dec-07		12:07:53		68		30.5		2-Feb-08		12:25:59		71.6		37

		23-Dec-07		14:07:10		68		29.5		23-Dec-07		14:06:20		67.4		30.5		23-Dec-07		14:07:53		68		31		2-Feb-08		14:25:59		71.6		39

		23-Dec-07		16:07:10		68		29.5		23-Dec-07		16:06:20		68		30.5		23-Dec-07		16:07:53		68		31.5		2-Feb-08		16:25:59		71.6		39

		23-Dec-07		18:07:10		68.61		29.5		23-Dec-07		18:06:20		67.4		30		23-Dec-07		18:07:53		68		31.5		2-Feb-08		18:25:59		71.6		39

		23-Dec-07		20:07:10		68		31.5		23-Dec-07		20:06:20		66.2		34		23-Dec-07		20:07:53		68.61		31.5		2-Feb-08		20:25:59		71.6		38.5

		23-Dec-07		22:07:10		67.4		32		23-Dec-07		22:06:20		66.2		34.5		23-Dec-07		22:07:53		68.61		32		2-Feb-08		22:25:59		68.61		39.5

		24-Dec-07		0:07:10		66.81		32		24-Dec-07		0:06:20		65.6		34.5		24-Dec-07		0:07:53		68.61		31.5		3-Feb-08		0:25:59		66.81		40.5

		24-Dec-07		2:07:10		66.81		31.5		24-Dec-07		2:06:20		66.2		33.5		24-Dec-07		2:07:53		68.61		31.5		3-Feb-08		2:25:59		66.2		41

		24-Dec-07		4:07:10		66.81		31.5		24-Dec-07		4:06:20		65.6		34		24-Dec-07		4:07:53		68.61		31.5		3-Feb-08		4:25:59		65.6		42

		24-Dec-07		6:07:10		66.81		31.5		24-Dec-07		6:06:20		65.6		33		24-Dec-07		6:07:53		68		31		3-Feb-08		6:25:59		65.01		42.5

		24-Dec-07		8:07:10		67.4		31		24-Dec-07		8:06:20		67.4		32		24-Dec-07		8:07:53		69.2		30.5		3-Feb-08		8:25:59		65.01		43

		24-Dec-07		10:07:10		67.4		32		24-Dec-07		10:06:20		67.4		33.5		24-Dec-07		10:07:53		69.2		31		3-Feb-08		10:25:59		66.2		43

		24-Dec-07		12:07:10		68		32.5		24-Dec-07		12:06:20		67.4		33.5		24-Dec-07		12:07:53		68.61		32		3-Feb-08		12:25:59		66.81		45

		24-Dec-07		14:07:10		68.61		36		24-Dec-07		14:06:20		68		38.5		24-Dec-07		14:07:53		69.2		35.5		3-Feb-08		14:25:59		67.4		46

		24-Dec-07		16:07:10		69.2		40		24-Dec-07		16:06:20		68.61		44		24-Dec-07		16:07:53		69.8		39.5		3-Feb-08		16:25:59		67.4		48.5

		24-Dec-07		18:07:10		69.8		43		24-Dec-07		18:06:20		68.61		48		24-Dec-07		18:07:53		69.8		43		3-Feb-08		18:25:59		66.81		50.5

		24-Dec-07		20:07:10		68.61		43		24-Dec-07		20:06:20		66.81		47.5		24-Dec-07		20:07:53		69.2		42.5		3-Feb-08		20:25:59		66.81		50

		24-Dec-07		22:07:10		68		41.5		24-Dec-07		22:06:20		66.2		46		24-Dec-07		22:07:53		69.8		40.5		3-Feb-08		22:25:59		66.2		51.5

		25-Dec-07		0:07:10		68		41.5		25-Dec-07		0:06:20		66.2		45		25-Dec-07		0:07:53		69.8		40		4-Feb-08		0:25:59		66.2		52.5

		25-Dec-07		2:07:10		67.4		40.5		25-Dec-07		2:06:20		66.2		44.5		25-Dec-07		2:07:53		69.8		39		4-Feb-08		2:25:59		66.2		51.5

		25-Dec-07		4:07:10		67.4		40.5		25-Dec-07		4:06:20		66.2		43.5		25-Dec-07		4:07:53		69.8		38		4-Feb-08		4:25:59		65.6		49.5

		25-Dec-07		6:07:10		67.4		39.5		25-Dec-07		6:06:20		66.2		42		25-Dec-07		6:07:53		69.8		37		4-Feb-08		6:25:59		65.6		48.5

		25-Dec-07		8:07:10		69.2		37.5		25-Dec-07		8:06:20		67.4		40		25-Dec-07		8:07:53		69.2		38		4-Feb-08		8:25:59		65.6		47

		25-Dec-07		10:07:10		69.8		33.5		25-Dec-07		10:06:20		68		34.5		25-Dec-07		10:07:53		68.61		35		4-Feb-08		10:25:59		66.2		46

		25-Dec-07		12:07:10		71		31.5		25-Dec-07		12:06:20		69.2		31		25-Dec-07		12:07:53		69.2		33.5		4-Feb-08		12:25:59		66.81		46.5

		25-Dec-07		14:07:10		70.41		30		25-Dec-07		14:06:20		69.2		28		25-Dec-07		14:07:53		69.8		31.5		4-Feb-08		14:25:59		67.4		46

		25-Dec-07		16:07:10		70.41		27.5		25-Dec-07		16:06:20		68.61		26		25-Dec-07		16:07:53		70.41		30.5		4-Feb-08		16:25:59		67.4		45.5

		25-Dec-07		18:07:10		70.41		29.5		25-Dec-07		18:06:20		68.61		29		25-Dec-07		18:07:53		70.41		30.5		4-Feb-08		18:25:59		67.4		45

		25-Dec-07		20:07:10		69.2		32		25-Dec-07		20:06:20		66.81		34.5		25-Dec-07		20:07:53		69.2		33		4-Feb-08		20:25:59		66.2		45

		25-Dec-07		22:07:10		68		30		25-Dec-07		22:06:20		66.2		31.5		25-Dec-07		22:07:53		67.4		32		4-Feb-08		22:25:59		65.6		45

		26-Dec-07		0:07:10		67.4		29.5		26-Dec-07		0:06:20		65.6		31		26-Dec-07		0:07:53		65.6		31.5		5-Feb-08		0:25:59		65.6		44.5

		26-Dec-07		2:07:10		66.81		28.5		26-Dec-07		2:06:20		65.6		30		26-Dec-07		2:07:53		64.4		31.5		5-Feb-08		2:25:59		65.01		44.5

		26-Dec-07		4:07:10		66.2		28		26-Dec-07		4:06:20		65.6		29.5		26-Dec-07		4:07:53		62.6		31		5-Feb-08		4:25:59		65.01		44

		26-Dec-07		6:07:10		66.2		27.5		26-Dec-07		6:06:20		65.6		29		26-Dec-07		6:07:53		66.81		28.5		5-Feb-08		6:25:59		66.2		42.5

		26-Dec-07		8:07:10		66.81		26.5		26-Dec-07		8:06:20		66.81		27		26-Dec-07		8:07:53		68		27.5		5-Feb-08		8:25:59		69.8		39.5

		26-Dec-07		10:07:10		67.4		26.5		26-Dec-07		10:06:20		67.4		27.5		26-Dec-07		10:07:53		68.61		27.5		5-Feb-08		10:25:59		72.8		37.5

		26-Dec-07		12:07:10		67.4		27.5		26-Dec-07		12:06:20		67.4		28		26-Dec-07		12:07:53		68.61		28.5		5-Feb-08		12:25:59		71.6		37.5

		26-Dec-07		14:07:10		68		28		26-Dec-07		14:06:20		68		28		26-Dec-07		14:07:53		68.61		29.5		5-Feb-08		14:25:59		71.6		36

		26-Dec-07		16:07:10		68.61		29.5		26-Dec-07		16:06:20		68		30.5		26-Dec-07		16:07:53		68.61		31		5-Feb-08		16:25:59		72.8		34.5

		26-Dec-07		18:07:10		68.61		32.5		26-Dec-07		18:06:20		68		35		26-Dec-07		18:07:53		68.61		34		5-Feb-08		18:25:59		72.8		34.5

		26-Dec-07		20:07:10		68		33.5		26-Dec-07		20:06:20		66.81		36		26-Dec-07		20:07:53		69.2		34		5-Feb-08		20:25:59		72.21		34

		26-Dec-07		22:07:10		67.4		34		26-Dec-07		22:06:20		66.2		36.5		26-Dec-07		22:07:53		67.4		34.5		5-Feb-08		22:25:59		69.2		36

		27-Dec-07		0:07:10		66.81		34.5		27-Dec-07		0:06:20		66.2		38		27-Dec-07		0:07:53		66.2		36		6-Feb-08		0:25:59		67.4		37

		27-Dec-07		2:07:10		66.81		34		27-Dec-07		2:06:20		66.2		36		27-Dec-07		2:07:53		65.01		36		6-Feb-08		2:25:59		66.2		38

		27-Dec-07		4:07:10		66.2		32.5		27-Dec-07		4:06:20		65.6		34		27-Dec-07		4:07:53		63.8		35		6-Feb-08		4:25:59		65.6		38

		27-Dec-07		6:07:10		66.2		31.5		27-Dec-07		6:06:20		65.6		32.5		27-Dec-07		6:07:53		68		31.5		6-Feb-08		6:25:59		66.81		39.5

		27-Dec-07		8:07:10		68		30		27-Dec-07		8:06:20		67.4		31		27-Dec-07		8:07:53		70.41		30.5		6-Feb-08		8:25:59		70.41		36.5

		27-Dec-07		10:07:10		69.2		30.5		27-Dec-07		10:06:20		69.8		31.5		27-Dec-07		10:07:53		71		30.5		6-Feb-08		10:25:59		72.8		35.5

		27-Dec-07		12:07:10		71		28.5		27-Dec-07		12:06:20		70.41		28.5		27-Dec-07		12:07:53		71		29		6-Feb-08		12:25:59		71		37

		27-Dec-07		14:07:10		70.41		25.5		27-Dec-07		14:06:20		70.41		24.5		27-Dec-07		14:07:53		71		25.5		6-Feb-08		14:25:59		72.21		37

		27-Dec-07		16:07:10		71		22.5		27-Dec-07		16:06:20		71		22		27-Dec-07		16:07:53		69.8		24		6-Feb-08		16:25:59		72.8		34.5

		27-Dec-07		18:07:10		70.41		23		27-Dec-07		18:06:20		68.61		23.5		27-Dec-07		18:07:53		69.2		24.5		6-Feb-08		18:25:59		72.8		35

		27-Dec-07		20:07:10		69.8		24		27-Dec-07		20:06:20		66.81		26		27-Dec-07		20:07:53		68		26		6-Feb-08		20:25:59		72.8		37

		27-Dec-07		22:07:10		68		24		27-Dec-07		22:06:20		66.2		26		27-Dec-07		22:07:53		66.2		27		6-Feb-08		22:25:59		69.8		38

		28-Dec-07		0:07:10		67.4		24.5		28-Dec-07		0:06:20		65.6		26		28-Dec-07		0:07:53		65.01		27.5		7-Feb-08		0:25:59		68		38.5

		28-Dec-07		2:07:10		66.81		24		28-Dec-07		2:06:20		65.6		26		28-Dec-07		2:07:53		63.21		28		7-Feb-08		2:25:59		66.81		38.5

		28-Dec-07		4:07:10		66.2		24		28-Dec-07		4:06:20		65.6		25.5		28-Dec-07		4:07:53		62.6		28		7-Feb-08		4:25:59		66.2		38.5

		28-Dec-07		6:07:10		66.2		24.5		28-Dec-07		6:06:20		65.6		25.5		28-Dec-07		6:07:53		66.2		26		7-Feb-08		6:25:59		67.4		38.5

		28-Dec-07		8:07:10		68		23.5		28-Dec-07		8:06:20		67.4		24.5		28-Dec-07		8:07:53		68		25.5		7-Feb-08		8:25:59		71.6		38

		28-Dec-07		10:07:10		69.2		24		28-Dec-07		10:06:20		69.2		25.5		28-Dec-07		10:07:53		69.8		25		7-Feb-08		10:25:59		72.21		37.5

		28-Dec-07		12:07:10		70.41		25		28-Dec-07		12:06:20		70.41		26		28-Dec-07		12:07:53		71		26		7-Feb-08		12:25:59		71.6		40.5

		28-Dec-07		14:07:10		70.41		25.5		28-Dec-07		14:06:20		70.41		26		28-Dec-07		14:07:53		71		27		7-Feb-08		14:25:59		71.6		40

		28-Dec-07		16:07:10		71		26.5		28-Dec-07		16:06:20		70.41		27.5		28-Dec-07		16:07:53		71		25		7-Feb-08		16:25:59		72.8		38

		28-Dec-07		18:07:10		71		28.5		28-Dec-07		18:06:20		68.61		31.5		28-Dec-07		18:07:53		71		29.5		7-Feb-08		18:25:59		72.8		37.5

		28-Dec-07		20:07:10		71		31.5		28-Dec-07		20:06:20		66.81		37		28-Dec-07		20:07:53		69.8		32.5		7-Feb-08		20:25:59		72.21		36

		28-Dec-07		22:07:10		69.8		33		28-Dec-07		22:06:20		66.2		38.5		28-Dec-07		22:07:53		68		34.5		7-Feb-08		22:25:59		69.2		37.5

		29-Dec-07		0:07:10		68.61		34		29-Dec-07		0:06:20		66.2		39		29-Dec-07		0:07:53		66.81		36		8-Feb-08		0:25:59		67.4		38.5

		29-Dec-07		2:07:10		68		34		29-Dec-07		2:06:20		66.2		37.5		29-Dec-07		2:07:53		66.2		36.5		8-Feb-08		2:25:59		66.81		39

		29-Dec-07		4:07:10		67.4		34		29-Dec-07		4:06:20		66.2		38		29-Dec-07		4:07:53		65.01		37		8-Feb-08		4:25:59		65.6		39.5

		29-Dec-07		6:07:10		68		33.5		29-Dec-07		6:06:20		65.6		36.5		29-Dec-07		6:07:53		66.81		35.5		8-Feb-08		6:25:59		67.4		39.5

		29-Dec-07		8:07:10		69.8		32		29-Dec-07		8:06:20		68		34.5		29-Dec-07		8:07:53		68.61		35.5		8-Feb-08		8:25:59		71		37.5

		29-Dec-07		10:07:10		70.41		32		29-Dec-07		10:06:20		69.8		33		29-Dec-07		10:07:53		70.41		33.5		8-Feb-08		10:25:59		71.6		38

		29-Dec-07		12:07:10		72.21		33		29-Dec-07		12:06:20		70.41		35		29-Dec-07		12:07:53		71.6		34		8-Feb-08		12:25:59		71		39

		29-Dec-07		14:07:10		72.8		32.5		29-Dec-07		14:06:20		71		34		29-Dec-07		14:07:53		71.6		34		8-Feb-08		14:25:59		72.21		40

		29-Dec-07		16:07:10		72.8		32		29-Dec-07		16:06:20		71		35		29-Dec-07		16:07:53		70.41		34.5		8-Feb-08		16:25:59		73.4		41

		29-Dec-07		18:07:10		72.21		32		29-Dec-07		18:06:20		69.2		35		29-Dec-07		18:07:53		69.2		35.5		8-Feb-08		18:25:59		74.01		40

		29-Dec-07		20:07:10		71		33		29-Dec-07		20:06:20		67.4		37.5		29-Dec-07		20:07:53		68		36.5		8-Feb-08		20:25:59		72.21		40.5

		29-Dec-07		22:07:10		69.2		34		29-Dec-07		22:06:20		66.81		38.5		29-Dec-07		22:07:53		66.2		37.5		8-Feb-08		22:25:59		70.41		41.5

		30-Dec-07		0:07:10		68		34.5		30-Dec-07		0:06:20		66.2		38.5		30-Dec-07		0:07:53		65.01		38.5		9-Feb-08		0:25:59		69.2		41.5

		30-Dec-07		2:07:10		67.4		35.5		30-Dec-07		2:06:20		65.6		39		30-Dec-07		2:07:53		63.8		40		9-Feb-08		2:25:59		68		41

		30-Dec-07		4:07:10		67.4		36		30-Dec-07		4:06:20		66.2		39.5		30-Dec-07		4:07:53		63.8		41		9-Feb-08		4:25:59		66.2		40.5

		30-Dec-07		6:07:10		66.81		37		30-Dec-07		6:06:20		65.6		40.5		30-Dec-07		6:07:53		63.21		42		9-Feb-08		6:25:59		67.4		39.5

		30-Dec-07		8:07:10		67.4		37		30-Dec-07		8:06:20		67.4		39		30-Dec-07		8:07:53		69.2		37		9-Feb-08		8:25:59		71		36.5

		30-Dec-07		10:07:10		68		37.5		30-Dec-07		10:06:20		67.4		40		30-Dec-07		10:07:53		67.4		39.5		9-Feb-08		10:25:59		71		37.5

		30-Dec-07		12:07:10		68		39		30-Dec-07		12:06:20		67.4		41.5		30-Dec-07		12:07:53		67.4		39.5		9-Feb-08		12:25:59		70.41		39

		30-Dec-07		14:07:10		68		40		30-Dec-07		14:06:20		67.4		42.5		30-Dec-07		14:07:53		67.4		40.5		9-Feb-08		14:25:59		71.6		37.5

		30-Dec-07		16:07:10		68		41		30-Dec-07		16:06:20		67.4		43.5		30-Dec-07		16:07:53		66.81		42.5		9-Feb-08		16:25:59		72.8		34

		30-Dec-07		18:07:10		68		41.5		30-Dec-07		18:06:20		67.4		44		30-Dec-07		18:07:53		66.81		43.5		9-Feb-08		18:25:59		73.4		33.5

		30-Dec-07		20:07:10		67.4		42.5		30-Dec-07		20:06:20		66.2		46		30-Dec-07		20:07:53		67.4		43		9-Feb-08		20:25:59		71.6		37.5

		30-Dec-07		22:07:10		66.81		43		30-Dec-07		22:06:20		66.2		46.5		30-Dec-07		22:07:53		65.01		45.5		9-Feb-08		22:25:59		69.8		38.5

		31-Dec-07		0:07:10		66.81		43.5		31-Dec-07		0:06:20		66.2		46.5		31-Dec-07		0:07:53		64.4		47		10-Feb-08		0:25:59		68		39

		31-Dec-07		2:07:10		66.81		44		31-Dec-07		2:06:20		66.2		47		31-Dec-07		2:07:53		63.8		48		10-Feb-08		2:25:59		66.2		39

		31-Dec-07		4:07:10		66.81		44		31-Dec-07		4:06:20		66.2		47		31-Dec-07		4:07:53		63.21		49		10-Feb-08		4:25:59		65.6		39.5

		31-Dec-07		6:07:10		66.81		42.5		31-Dec-07		6:06:20		65.6		44		31-Dec-07		6:07:53		63.21		48		10-Feb-08		6:25:59		64.4		40

		31-Dec-07		8:07:10		66.81		39.5		31-Dec-07		8:06:20		67.4		40		31-Dec-07		8:07:53		66.2		42		10-Feb-08		8:25:59		64.4		39.5

		31-Dec-07		10:07:10		67.4		38		31-Dec-07		10:06:20		67.4		38.5		31-Dec-07		10:07:53		68		38.5		10-Feb-08		10:25:59		65.01		40.5

		31-Dec-07		12:07:10		67.4		36.5		31-Dec-07		12:06:20		67.4		37		31-Dec-07		12:07:53		66.81		38		10-Feb-08		12:25:59		66.81		43

		31-Dec-07		14:07:10		68		34.5		31-Dec-07		14:06:20		68		34		31-Dec-07		14:07:53		67.4		36.5		10-Feb-08		14:25:59		68.61		44

		31-Dec-07		16:07:10		68		32		31-Dec-07		16:06:20		67.4		31.5		31-Dec-07		16:07:53		67.4		35		10-Feb-08		16:25:59		69.8		42

		31-Dec-07		18:07:10		68		30.5		31-Dec-07		18:06:20		68		30		31-Dec-07		18:07:53		67.4		33.5		10-Feb-08		18:25:59		71		42.5

		31-Dec-07		20:07:10		67.4		31		31-Dec-07		20:06:20		66.2		31.5		31-Dec-07		20:07:53		65.6		33.5		10-Feb-08		20:25:59		69.8		42.5

		31-Dec-07		22:07:10		66.81		31.5		31-Dec-07		22:06:20		65.6		33		31-Dec-07		22:07:53		63.8		35		10-Feb-08		22:25:59		68		43

		1-Jan-08		0:07:10		66.2		30.5		1-Jan-08		0:06:20		65.6		31.5		1-Jan-08		0:07:53		63.21		34.5		11-Feb-08		0:25:59		66.81		43

		1-Jan-08		2:07:10		66.2		29.5		1-Jan-08		2:06:20		65.6		30		1-Jan-08		2:07:53		62		33.5		11-Feb-08		2:25:59		65.6		43

		1-Jan-08		4:07:10		66.2		29		1-Jan-08		4:06:20		65.6		29.5		1-Jan-08		4:07:53		61.41		33.5		11-Feb-08		4:25:59		65.01		43

		1-Jan-08		6:07:10		66.2		28.5		1-Jan-08		6:06:20		65.6		29.5		1-Jan-08		6:07:53		67.4		29		11-Feb-08		6:25:59		64.4		42.5

		1-Jan-08		8:07:10		67.4		27		1-Jan-08		8:06:20		68.61		27.5		1-Jan-08		8:07:53		69.2		28.5		11-Feb-08		8:25:59		64.4		41.5

		1-Jan-08		10:07:10		68.61		27.5		1-Jan-08		10:06:20		69.2		28.5		1-Jan-08		10:07:53		69.8		29		11-Feb-08		10:25:59		65.6		41.5

		1-Jan-08		12:07:10		69.8		29		1-Jan-08		12:06:20		69.2		28.5		1-Jan-08		12:07:53		71.6		29		11-Feb-08		12:25:59		68		45

		1-Jan-08		14:07:10		71		29.5		1-Jan-08		14:06:20		70.41		30.5		1-Jan-08		14:07:53		71		31.5		11-Feb-08		14:25:59		69.2		45

		1-Jan-08		16:07:10		71.6		28.5		1-Jan-08		16:06:20		69.2		29		1-Jan-08		16:07:53		69.8		30.5		11-Feb-08		16:25:59		70.41		44.5

		1-Jan-08		18:07:10		71.6		29		1-Jan-08		18:06:20		69.2		30		1-Jan-08		18:07:53		69.8		31.5		11-Feb-08		18:25:59		71		45

		1-Jan-08		20:07:10		70.41		28.5		1-Jan-08		20:06:20		67.4		31		1-Jan-08		20:07:53		68.61		31.5		11-Feb-08		20:25:59		69.8		45

		1-Jan-08		22:07:10		68.61		28.5		1-Jan-08		22:06:20		66.81		31		1-Jan-08		22:07:53		66.2		31.5		11-Feb-08		22:25:59		68		45.5

		2-Jan-08		0:07:10		67.4		28.5		2-Jan-08		0:06:20		66.2		30.5		2-Jan-08		0:07:53		63.8		32		12-Feb-08		0:25:59		66.81		45.5

		2-Jan-08		2:07:10		66.81		29		2-Jan-08		2:06:20		65.6		31		2-Jan-08		2:07:53		62		33		12-Feb-08		2:25:59		65.6		45

		2-Jan-08		4:07:10		66.2		27.5		2-Jan-08		4:06:20		65.6		29.5		2-Jan-08		4:07:53		60.8		33		12-Feb-08		4:25:59		65.01		45

		2-Jan-08		6:07:10		66.81		27		2-Jan-08		6:06:20		65.6		29		2-Jan-08		6:07:53		66.81		28.5		12-Feb-08		6:25:59		66.2		44

		2-Jan-08		8:07:10		67.4		26		2-Jan-08		8:06:20		66.81		27.5		2-Jan-08		8:07:53		67.4		27.5		12-Feb-08		8:25:59		69.2		40.5

		2-Jan-08		10:07:10		68		26.5		2-Jan-08		10:06:20		67.4		28		2-Jan-08		10:07:53		67.4		28		12-Feb-08		10:25:59		72.8		40

		2-Jan-08		12:07:10		69.2		29.5		2-Jan-08		12:06:20		68		31.5		2-Jan-08		12:07:53		67.4		31		12-Feb-08		12:25:59		71.6		43

		2-Jan-08		14:07:10		70.41		31.5		2-Jan-08		14:06:20		68.61		33.5		2-Jan-08		14:07:53		68		33.5		12-Feb-08		14:25:59		72.8		43.5

		2-Jan-08		16:07:10		71.6		32		2-Jan-08		16:06:20		69.2		34		2-Jan-08		16:07:53		69.2		34.5		12-Feb-08		16:25:59		74.01		43.5

		2-Jan-08		18:07:10		72.21		31		2-Jan-08		18:06:20		69.2		33		2-Jan-08		18:07:53		68.61		34.5		12-Feb-08		18:25:59		74.01		44.5

		2-Jan-08		20:07:10		71.6		31		2-Jan-08		20:06:20		68		34		2-Jan-08		20:07:53		68		34.5		12-Feb-08		20:25:59		71.6		43.5

		2-Jan-08		22:07:10		69.2		31		2-Jan-08		22:06:20		66.81		35.5		2-Jan-08		22:07:53		66.81		34.5		12-Feb-08		22:25:59		70.41		44.5

		3-Jan-08		0:07:10		68		32		3-Jan-08		0:06:20		66.2		35.5		3-Jan-08		0:07:53		64.4		36		13-Feb-08		0:25:59		68.61		44.5

		3-Jan-08		2:07:10		66.81		31.5		3-Jan-08		2:06:20		66.2		34		3-Jan-08		2:07:53		63.21		36.5		13-Feb-08		2:25:59		67.4		44

		3-Jan-08		4:07:10		66.2		31.5		3-Jan-08		4:06:20		66.2		34		3-Jan-08		4:07:53		62		36.5		13-Feb-08		4:25:59		66.2		44

		3-Jan-08		6:07:10		66.81		31.5		3-Jan-08		6:06:20		65.6		34		3-Jan-08		6:07:53		66.81		33.5		13-Feb-08		6:25:59		66.81		43.5

		3-Jan-08		8:07:10		68.61		29.5		3-Jan-08		8:06:20		67.4		31.5		3-Jan-08		8:07:53		68		32.5		13-Feb-08		8:25:59		72.21		39.5

		3-Jan-08		10:07:10		69.2		30.5		3-Jan-08		10:06:20		69.8		32.5		3-Jan-08		10:07:53		69.8		32		13-Feb-08		10:25:59		71.6		40.5

		3-Jan-08		12:07:10		71.6		32		3-Jan-08		12:06:20		71		32.5		3-Jan-08		12:07:53		72.21		32.5		13-Feb-08		12:25:59		72.21		43

		3-Jan-08		14:07:10		72.8		31		3-Jan-08		14:06:20		71		30.5		3-Jan-08		14:07:53		71		35		13-Feb-08		14:25:59		74.01		43.5

		3-Jan-08		16:07:10		72.21		32.5		3-Jan-08		16:06:20		71		34.5		3-Jan-08		16:07:53		70.41		33.5		13-Feb-08		16:25:59		74.6		44.5

		3-Jan-08		18:07:10		72.21		32.5		3-Jan-08		18:06:20		69.2		35		3-Jan-08		18:07:53		70.41		35.5		13-Feb-08		18:25:59		74.01		44

		3-Jan-08		20:07:10		71.6		34		3-Jan-08		20:06:20		68		39		3-Jan-08		20:07:53		69.8		36.5		13-Feb-08		20:25:59		72.21		43.5

		3-Jan-08		22:07:10		70.41		33.5		3-Jan-08		22:06:20		66.81		37.5		3-Jan-08		22:07:53		68		36.5		13-Feb-08		22:25:59		71		43.5

		4-Jan-08		0:07:10		69.2		33		4-Jan-08		0:06:20		66.2		37		4-Jan-08		0:07:53		66.2		36.5		14-Feb-08		0:25:59		68.61		43.5

		4-Jan-08		2:07:10		68.61		34.5		4-Jan-08		2:06:20		66.2		39		4-Jan-08		2:07:53		65.01		38.5		14-Feb-08		2:25:59		67.4		43.5

		4-Jan-08		4:07:10		68		35		4-Jan-08		4:06:20		66.2		39.5		4-Jan-08		4:07:53		65.01		39.5		14-Feb-08		4:25:59		66.2		43.5

		4-Jan-08		6:07:10		68.61		36.5		4-Jan-08		6:06:20		66.2		41		4-Jan-08		6:07:53		66.81		40		14-Feb-08		6:25:59		66.81		44

		4-Jan-08		8:07:10		71		37.5		4-Jan-08		8:06:20		68.61		42		4-Jan-08		8:07:53		70.41		39.5		14-Feb-08		8:25:59		70.41		41

		4-Jan-08		10:07:10		72.21		39		4-Jan-08		10:06:20		70.41		40		4-Jan-08		10:07:53		71.6		40.5		14-Feb-08		10:25:59		71.6		37

		4-Jan-08		12:07:10		73.4		40		4-Jan-08		12:06:20		71		46.5		4-Jan-08		12:07:53		71		45.5		14-Feb-08		12:25:59		71.6		36.5

		4-Jan-08		14:07:10		72.8		42.5		4-Jan-08		14:06:20		71		47.5		4-Jan-08		14:07:53		71		45.5		14-Feb-08		14:25:59		72.8		36

		4-Jan-08		16:07:10		73.4		43.5		4-Jan-08		16:06:20		70.41		49		4-Jan-08		16:07:53		71.6		41.5		14-Feb-08		16:25:59		73.4		32

		4-Jan-08		18:07:10		72.8		42.5		4-Jan-08		18:06:20		69.8		47.5		4-Jan-08		18:07:53		71		42		14-Feb-08		18:25:59		73.4		29

		4-Jan-08		20:07:10		71.6		42.5		4-Jan-08		20:06:20		69.2		48		4-Jan-08		20:07:53		69.8		45.5		14-Feb-08		20:25:59		71.6		28

		4-Jan-08		22:07:10		71		43		4-Jan-08		22:06:20		68		49.5		4-Jan-08		22:07:53		69.2		46.5		14-Feb-08		22:25:59		70.41		31.5

		5-Jan-08		0:07:10		69.8		43.5		5-Jan-08		0:06:20		67.4		50.5		5-Jan-08		0:07:53		69.2		46.5		15-Feb-08		0:25:59		68.61		32.5

		5-Jan-08		2:07:10		69.2		44		5-Jan-08		2:06:20		67.4		51		5-Jan-08		2:07:53		68.61		47		15-Feb-08		2:25:59		67.4		33

		5-Jan-08		4:07:10		69.2		45		5-Jan-08		4:06:20		67.4		52.5		5-Jan-08		4:07:53		68.61		48		15-Feb-08		4:25:59		66.2		33.5

		5-Jan-08		6:07:10		68.61		46		5-Jan-08		6:06:20		67.4		53.5		5-Jan-08		6:07:53		68		49		15-Feb-08		6:25:59		66.81		33.5

		5-Jan-08		8:07:10		69.8		47		5-Jan-08		8:06:20		69.2		53.5		5-Jan-08		8:07:53		70.41		53		15-Feb-08		8:25:59		70.41		32

		5-Jan-08		10:07:10		71		49.5		5-Jan-08		10:06:20		70.41		56.5		5-Jan-08		10:07:53		71		49		15-Feb-08		10:25:59		71.6		30.5

		5-Jan-08		12:07:10		71		49.5		5-Jan-08		12:06:20		71		51		5-Jan-08		12:07:53		71		54.5		15-Feb-08		12:25:59		72.21		30

		5-Jan-08		14:07:10		70.41		46		5-Jan-08		14:06:20		70.41		47		5-Jan-08		14:07:53		72.21		45.5		15-Feb-08		14:25:59		72.8		30.5

		5-Jan-08		16:07:10		69.8		45.5		5-Jan-08		16:06:20		71		46		5-Jan-08		16:07:53		71		46		15-Feb-08		16:25:59		73.4		29.5

		5-Jan-08		18:07:10		73.4		41.5		5-Jan-08		18:06:20		74.01		42		5-Jan-08		18:07:53		74.01		42.5		15-Feb-08		18:25:59		74.01		30

		5-Jan-08		20:07:10		69.2		42.5		5-Jan-08		20:06:20		68		44.5		5-Jan-08		20:07:53		69.2		43.5		15-Feb-08		20:25:59		71		30

		5-Jan-08		22:07:10		68		41.5		5-Jan-08		22:06:20		66.81		43.5		5-Jan-08		22:07:53		68		44		15-Feb-08		22:25:59		69.2		31.5

		6-Jan-08		0:07:10		67.4		41		6-Jan-08		0:06:20		66.81		42.5		6-Jan-08		0:07:53		67.4		43.5		16-Feb-08		0:25:59		68		33

		6-Jan-08		2:07:10		66.81		39.5		6-Jan-08		2:06:20		66.81		39.5		6-Jan-08		2:07:53		66.2		42.5		16-Feb-08		2:25:59		66.2		34

		6-Jan-08		4:07:10		66.2		41		6-Jan-08		4:06:20		66.2		42		6-Jan-08		4:07:53		65.6		43		16-Feb-08		4:25:59		65.6		35

		6-Jan-08		6:07:10		65.6		41		6-Jan-08		6:06:20		66.2		41		6-Jan-08		6:07:53		65.01		43.5		16-Feb-08		6:25:59		66.2		36

		6-Jan-08		8:07:10		65.6		42		6-Jan-08		8:06:20		68		40		6-Jan-08		8:07:53		66.81		41		16-Feb-08		8:25:59		69.2		34

		6-Jan-08		10:07:10		65.6		43.5		6-Jan-08		10:06:20		68		42.5		6-Jan-08		10:07:53		66.81		42.5		16-Feb-08		10:25:59		71.6		34.5

		6-Jan-08		12:07:10		65.6		44.5		6-Jan-08		12:06:20		68		42.5		6-Jan-08		12:07:53		67.4		43		16-Feb-08		12:25:59		72.21		34

		6-Jan-08		14:07:10		65.6		45.5		6-Jan-08		14:06:20		68		44		6-Jan-08		14:07:53		67.4		45		16-Feb-08		14:25:59		72.8		34

		6-Jan-08		16:07:10		66.2		45		6-Jan-08		16:06:20		68		43.5		6-Jan-08		16:07:53		68		44.5		16-Feb-08		16:25:59		74.6		37

		6-Jan-08		18:07:10		66.2		45		6-Jan-08		18:06:20		68		44		6-Jan-08		18:07:53		67.4		45		16-Feb-08		18:25:59		74.01		37

		6-Jan-08		20:07:10		66.2		45		6-Jan-08		20:06:20		66.81		44.5		6-Jan-08		20:07:53		67.4		44		16-Feb-08		20:25:59		71.6		37.5

		6-Jan-08		22:07:10		65.6		43		6-Jan-08		22:06:20		66.81		42.5		6-Jan-08		22:07:53		66.2		43.5		16-Feb-08		22:25:59		69.2		38

		7-Jan-08		0:07:10		65.01		42.5		7-Jan-08		0:06:20		66.2		41.5		7-Jan-08		0:07:53		65.6		43		17-Feb-08		0:25:59		68		39

		7-Jan-08		2:07:10		65.01		42.5		7-Jan-08		2:06:20		66.2		41		7-Jan-08		2:07:53		65.6		43		17-Feb-08		2:25:59		67.4		39.5

		7-Jan-08		4:07:10		64.4		41.5		7-Jan-08		4:06:20		66.2		40		7-Jan-08		4:07:53		65.01		42		17-Feb-08		4:25:59		66.81		40.5

		7-Jan-08		6:07:10		64.4		40		7-Jan-08		6:06:20		66.2		38		7-Jan-08		6:07:53		64.4		41		17-Feb-08		6:25:59		66.81		41

		7-Jan-08		8:07:10		64.4		40.5		7-Jan-08		8:06:20		67.4		37		7-Jan-08		8:07:53		66.81		38.5		17-Feb-08		8:25:59		66.2		41

		7-Jan-08		10:07:10		64.4		39		7-Jan-08		10:06:20		67.4		35.5		7-Jan-08		10:07:53		67.4		36.5		17-Feb-08		10:25:59		66.2		41

		7-Jan-08		12:07:10		64.4		41		7-Jan-08		12:06:20		68		38.5		7-Jan-08		12:07:53		67.4		38.5		17-Feb-08		12:25:59		66.81		42

		7-Jan-08		14:07:10		65.01		43		7-Jan-08		14:06:20		68		41		7-Jan-08		14:07:53		67.4		41		17-Feb-08		14:25:59		67.4		43

		7-Jan-08		16:07:10		65.6		42.5		7-Jan-08		16:06:20		68		39.5		7-Jan-08		16:07:53		68		40.5		17-Feb-08		16:25:59		68.61		42

		7-Jan-08		18:07:10		65.6		41.5		7-Jan-08		18:06:20		68		39.5		7-Jan-08		18:07:53		68		40		17-Feb-08		18:25:59		69.2		41

		7-Jan-08		20:07:10		65.6		42		7-Jan-08		20:06:20		66.81		41.5		7-Jan-08		20:07:53		66.81		41		17-Feb-08		20:25:59		68		41.5

		7-Jan-08		22:07:10		65.01		43.5		7-Jan-08		22:06:20		66.81		42.5		7-Jan-08		22:07:53		65.6		43		17-Feb-08		22:25:59		67.4		42

		8-Jan-08		0:07:10		65.01		44.5		8-Jan-08		0:06:20		66.81		43		8-Jan-08		0:07:53		65.6		44		18-Feb-08		0:25:59		66.2		42

		8-Jan-08		2:07:10		64.4		44		8-Jan-08		2:06:20		66.81		42.5		8-Jan-08		2:07:53		65.01		44		18-Feb-08		2:25:59		65.6		42.5

		8-Jan-08		4:07:10		64.4		44.5		8-Jan-08		4:06:20		66.2		42.5		8-Jan-08		4:07:53		65.01		44		18-Feb-08		4:25:59		65.01		43.5

		8-Jan-08		6:07:10		64.4		44		8-Jan-08		6:06:20		66.2		41.5		8-Jan-08		6:07:53		66.81		41.5		18-Feb-08		6:25:59		65.01		44

		8-Jan-08		8:07:10		65.6		41		8-Jan-08		8:06:20		68		37.5		8-Jan-08		8:07:53		69.2		38.5		18-Feb-08		8:25:59		65.6		43

		8-Jan-08		10:07:10		66.2		39.5		8-Jan-08		10:06:20		69.8		35.5		8-Jan-08		10:07:53		71		36.5		18-Feb-08		10:25:59		66.2		42.5

		8-Jan-08		12:07:10		67.4		42		8-Jan-08		12:06:20		71.6		40.5		8-Jan-08		12:07:53		72.21		39		18-Feb-08		12:25:59		67.4		42

		8-Jan-08		14:07:10		68		38.5		8-Jan-08		14:06:20		71.6		35.5		8-Jan-08		14:07:53		70.41		40.5		18-Feb-08		14:25:59		68		42.5

		8-Jan-08		16:07:10		68.61		35.5		8-Jan-08		16:06:20		71		33.5		8-Jan-08		16:07:53		71		35.5		18-Feb-08		16:25:59		68		43.5

		8-Jan-08		18:07:10		68.61		34		8-Jan-08		18:06:20		69.2		34		8-Jan-08		18:07:53		70.41		36		18-Feb-08		18:25:59		68		43.5

		8-Jan-08		20:07:10		68		34.5		8-Jan-08		20:06:20		67.4		36		8-Jan-08		20:07:53		69.2		36		18-Feb-08		20:25:59		67.4		43.5

		8-Jan-08		22:07:10		67.4		35.5		8-Jan-08		22:06:20		66.81		36.5		8-Jan-08		22:07:53		67.4		38		18-Feb-08		22:25:59		66.2		43.5

		9-Jan-08		0:07:10		66.81		36.5		9-Jan-08		0:06:20		66.81		37		9-Jan-08		0:07:53		65.6		38.5		19-Feb-08		0:25:59		65.6		44.5

		9-Jan-08		2:07:10		65.6		37.5		9-Jan-08		2:06:20		66.81		37.5		9-Jan-08		2:07:53		64.4		39.5		19-Feb-08		2:25:59		65.6		45

		9-Jan-08		4:07:10		65.01		38		9-Jan-08		4:06:20		66.2		38		9-Jan-08		4:07:53		63.21		41		19-Feb-08		4:25:59		65.01		45.5

		9-Jan-08		6:07:10		65.01		39		9-Jan-08		6:06:20		66.2		38.5		9-Jan-08		6:07:53		67.4		38		19-Feb-08		6:25:59		66.2		45

		9-Jan-08		8:07:10		65.6		39		9-Jan-08		8:06:20		68		37.5		9-Jan-08		8:07:53		68.61		39		19-Feb-08		8:25:59		69.8		42.5

		9-Jan-08		10:07:10		66.81		41		9-Jan-08		10:06:20		71		37.5		9-Jan-08		10:07:53		70.41		39.5		19-Feb-08		10:25:59		72.21		40.5

		9-Jan-08		12:07:10		67.4		42.5		9-Jan-08		12:06:20		71		42		9-Jan-08		12:07:53		71		41.5		19-Feb-08		12:25:59		71.6		40.5

		9-Jan-08		14:07:10		68.61		44.5		9-Jan-08		14:06:20		72.8		43.5		9-Jan-08		14:07:53		71.6		42.5		19-Feb-08		14:25:59		71.6		40.5

		9-Jan-08		16:07:10		69.2		46		9-Jan-08		16:06:20		74.01		42.5		9-Jan-08		16:07:53		71		44		19-Feb-08		16:25:59		72.21		40.5

		9-Jan-08		18:07:10		69.8		46		9-Jan-08		18:06:20		71		46		9-Jan-08		18:07:53		71.6		38.5		19-Feb-08		18:25:59		71.6		41

		9-Jan-08		20:07:10		70.41		45		9-Jan-08		20:06:20		69.8		45		9-Jan-08		20:07:53		70.41		44.5		19-Feb-08		20:25:59		71.6		41

		9-Jan-08		22:07:10		69.2		42.5		9-Jan-08		22:06:20		68		44.5		9-Jan-08		22:07:53		68.61		43.5		19-Feb-08		22:25:59		69.2		41.5

		10-Jan-08		0:07:10		68		44		10-Jan-08		0:06:20		66.81		46.5		10-Jan-08		0:07:53		67.4		45		20-Feb-08		0:25:59		67.4		42

		10-Jan-08		2:07:10		67.4		45		10-Jan-08		2:06:20		66.81		47		10-Jan-08		2:07:53		66.2		46.5		20-Feb-08		2:25:59		66.81		42.5

		10-Jan-08		4:07:10		66.81		45.5		10-Jan-08		4:06:20		66.81		46		10-Jan-08		4:07:53		65.6		47		20-Feb-08		4:25:59		66.2		43.5

		10-Jan-08		6:07:10		66.2		46		10-Jan-08		6:06:20		67.4		45.5		10-Jan-08		6:07:53		66.81		45.5		20-Feb-08		6:25:59		66.81		43.5

		10-Jan-08		8:07:10		66.81		45		10-Jan-08		8:06:20		69.8		41.5		10-Jan-08		8:07:53		70.41		43		20-Feb-08		8:25:59		71.6		42

		10-Jan-08		10:07:10		68		44.5		10-Jan-08		10:06:20		70.41		41		10-Jan-08		10:07:53		72.21		41.5		20-Feb-08		10:25:59		72.8		41

		10-Jan-08		12:07:10		68.61		43.5		10-Jan-08		12:06:20		70.41		39		10-Jan-08		12:07:53		71.6		42		20-Feb-08		12:25:59		72.8		41.5

		10-Jan-08		14:07:10		69.2		43.5		10-Jan-08		14:06:20		70.41		45		10-Jan-08		14:07:53		71.6		44		20-Feb-08		14:25:59		72.21		43.5

		10-Jan-08		16:07:10		69.2		43		10-Jan-08		16:06:20		70.41		39.5		10-Jan-08		16:07:53		71		43		20-Feb-08		16:25:59		72.21		45.5

		10-Jan-08		18:07:10		69.2		43		10-Jan-08		18:06:20		68.61		44		10-Jan-08		18:07:53		70.41		43.5		20-Feb-08		18:25:59		71.6		45.5

		10-Jan-08		20:07:10		69.2		42.5		10-Jan-08		20:06:20		68		44.5		10-Jan-08		20:07:53		69.2		42.5		20-Feb-08		20:25:59		71.6		45.5

		10-Jan-08		22:07:10		68.61		43		10-Jan-08		22:06:20		67.4		45		10-Jan-08		22:07:53		68		44		20-Feb-08		22:25:59		70.41		45.5

		11-Jan-08		0:07:10		68		43.5		11-Jan-08		0:06:20		67.4		44.5		11-Jan-08		0:07:53		67.4		44.5		21-Feb-08		0:25:59		68.61		46

		11-Jan-08		2:07:10		67.4		44		11-Jan-08		2:06:20		67.4		45.5		11-Jan-08		2:07:53		66.81		45.5		21-Feb-08		2:25:59		68		46

		11-Jan-08		4:07:10		67.4		44		11-Jan-08		4:06:20		67.4		45		11-Jan-08		4:07:53		65.6		46.5		21-Feb-08		4:25:59		66.81		46.5

		11-Jan-08		6:07:10		66.81		44.5		11-Jan-08		6:06:20		67.4		45		11-Jan-08		6:07:53		68		45		21-Feb-08		6:25:59		66.81		47

		11-Jan-08		8:07:10		67.4		45		11-Jan-08		8:06:20		67.4		45		11-Jan-08		8:07:53		69.8		44		21-Feb-08		8:25:59		71		44.5

		11-Jan-08		10:07:10		68		46		11-Jan-08		10:06:20		72.21		42.5		11-Jan-08		10:07:53		71.6		43		21-Feb-08		10:25:59		72.21		44

		11-Jan-08		12:07:10		69.2		46.5		11-Jan-08		12:06:20		72.8		44		11-Jan-08		12:07:53		71.6		47		21-Feb-08		12:25:59		72.8		43.5

		11-Jan-08		14:07:10		70.41		47.5		11-Jan-08		14:06:20		72.8		46		11-Jan-08		14:07:53		71		41.5		21-Feb-08		14:25:59		73.4		42

		11-Jan-08		16:07:10		70.41		47		11-Jan-08		16:06:20		73.4		40		11-Jan-08		16:07:53		71		48.5		21-Feb-08		16:25:59		74.01		40.5

		11-Jan-08		18:07:10		70.41		47		11-Jan-08		18:06:20		71		46.5		11-Jan-08		18:07:53		70.41		44.5		21-Feb-08		18:25:59		73.4		41

		11-Jan-08		20:07:10		69.8		46		11-Jan-08		20:06:20		69.2		48		11-Jan-08		20:07:53		70.41		44.5		21-Feb-08		20:25:59		72.21		40.5

		11-Jan-08		22:07:10		68.61		47		11-Jan-08		22:06:20		68		49.5		11-Jan-08		22:07:53		69.2		47		21-Feb-08		22:25:59		71		41

		12-Jan-08		0:07:10		68		48		12-Jan-08		0:06:20		68		49.5		12-Jan-08		0:07:53		68		48		22-Feb-08		0:25:59		69.8		41

		12-Jan-08		2:07:10		67.4		49		12-Jan-08		2:06:20		68		50		12-Jan-08		2:07:53		67.4		49		22-Feb-08		2:25:59		68.61		42

		12-Jan-08		4:07:10		66.81		48.5		12-Jan-08		4:06:20		67.4		48.5		12-Jan-08		4:07:53		66.81		49		22-Feb-08		4:25:59		67.4		43

		12-Jan-08		6:07:10		66.81		47.5		12-Jan-08		6:06:20		67.4		46.5		12-Jan-08		6:07:53		67.4		47.5		22-Feb-08		6:25:59		67.4		43.5

		12-Jan-08		8:07:10		66.81		46		12-Jan-08		8:06:20		69.2		43		12-Jan-08		8:07:53		69.8		45		22-Feb-08		8:25:59		71.6		42

		12-Jan-08		10:07:10		68		45.5		12-Jan-08		10:06:20		72.8		38		12-Jan-08		10:07:53		71.6		43		22-Feb-08		10:25:59		72.8		41

		12-Jan-08		12:07:10		68		45.5		12-Jan-08		12:06:20		71		45		12-Jan-08		12:07:53		71		41		22-Feb-08		12:25:59		72.8		42.5

		12-Jan-08		14:07:10		68		44.5		12-Jan-08		14:06:20		70.41		42		12-Jan-08		14:07:53		69.8		44		22-Feb-08		14:25:59		72.21		42

		12-Jan-08		16:07:10		68		45		12-Jan-08		16:06:20		68.61		44		12-Jan-08		16:07:53		70.41		43.5		22-Feb-08		16:25:59		72.21		43.5

		12-Jan-08		18:07:10		67.4		45		12-Jan-08		18:06:20		68.61		44.5		12-Jan-08		18:07:53		69.8		43.5		22-Feb-08		18:25:59		72.21		44

		12-Jan-08		20:07:10		67.4		45.5		12-Jan-08		20:06:20		68		45.5		12-Jan-08		20:07:53		69.2		44		22-Feb-08		20:25:59		72.21		43.5

		12-Jan-08		22:07:10		66.81		45.5		12-Jan-08		22:06:20		66.81		46.5		12-Jan-08		22:07:53		69.2		44.5		22-Feb-08		22:25:59		70.41		44.5

		13-Jan-08		0:07:10		65.6		47		13-Jan-08		0:06:20		66.2		48		13-Jan-08		0:07:53		69.2		43.5		23-Feb-08		0:25:59		68.61		45

		13-Jan-08		2:07:10		65.01		47.5		13-Jan-08		2:06:20		66.2		47.5		13-Jan-08		2:07:53		69.2		43		23-Feb-08		2:25:59		68		45.5

		13-Jan-08		4:07:10		65.01		48		13-Jan-08		4:06:20		66.2		47		13-Jan-08		4:07:53		69.8		42.5		23-Feb-08		4:25:59		67.4		45.5

		13-Jan-08		6:07:10		64.4		49		13-Jan-08		6:06:20		66.2		48		13-Jan-08		6:07:53		69.8		43		23-Feb-08		6:25:59		67.4		45

		13-Jan-08		8:07:10		64.4		49		13-Jan-08		8:06:20		67.4		45.5		13-Jan-08		8:07:53		69.8		42.5		23-Feb-08		8:25:59		72.8		42.5

		13-Jan-08		10:07:10		64.4		49.5		13-Jan-08		10:06:20		68		45.5		13-Jan-08		10:07:53		69.8		42.5		23-Feb-08		10:25:59		72.8		42.5

		13-Jan-08		12:07:10		65.01		50		13-Jan-08		12:06:20		68		47		13-Jan-08		12:07:53		69.8		45		23-Feb-08		12:25:59		71.6		42.5

		13-Jan-08		14:07:10		65.6		49.5		13-Jan-08		14:06:20		68.61		46		13-Jan-08		14:07:53		69.8		44		23-Feb-08		14:25:59		71.6		43

		13-Jan-08		16:07:10		66.2		49.5		13-Jan-08		16:06:20		69.2		46		13-Jan-08		16:07:53		69.8		45.5		23-Feb-08		16:25:59		72.8		41

		13-Jan-08		18:07:10		66.81		49.5		13-Jan-08		18:06:20		69.2		45		13-Jan-08		18:07:53		69.8		46.5		23-Feb-08		18:25:59		72.8		38.5

		13-Jan-08		20:07:10		66.81		48.5		13-Jan-08		20:06:20		68		47.5		13-Jan-08		20:07:53		69.2		45.5		23-Feb-08		20:25:59		71.6		38

		13-Jan-08		22:07:10		66.2		47		13-Jan-08		22:06:20		66.2		46		13-Jan-08		22:07:53		69.2		43		23-Feb-08		22:25:59		69.2		38.5

		14-Jan-08		0:07:10		65.01		46.5		14-Jan-08		0:06:20		65.6		45.5		14-Jan-08		0:07:53		69.2		41		24-Feb-08		0:25:59		66.81		39.5

		14-Jan-08		2:07:10		64.4		48		14-Jan-08		2:06:20		65.6		47		14-Jan-08		2:07:53		69.8		41.5		24-Feb-08		2:25:59		65.6		40

		14-Jan-08		4:07:10		64.4		49.5		14-Jan-08		4:06:20		65.6		48		14-Jan-08		4:07:53		69.8		42		24-Feb-08		4:25:59		64.4		40

		14-Jan-08		6:07:10		64.4		50.5		14-Jan-08		6:06:20		66.2		49		14-Jan-08		6:07:53		69.8		42.5		24-Feb-08		6:25:59		64.4		40.5

		14-Jan-08		8:07:10		64.4		51.5		14-Jan-08		8:06:20		68		47		14-Jan-08		8:07:53		69.8		43		24-Feb-08		8:25:59		65.01		40.5

		14-Jan-08		10:07:10		64.4		50		14-Jan-08		10:06:20		68		45.5		14-Jan-08		10:07:53		69.8		42		24-Feb-08		10:25:59		65.01		41.5

		14-Jan-08		12:07:10		65.01		49		14-Jan-08		12:06:20		68		44.5		14-Jan-08		12:07:53		70.41		39.5		24-Feb-08		12:25:59		65.6		42.5

		14-Jan-08		14:07:10		65.01		49		14-Jan-08		14:06:20		68		45		14-Jan-08		14:07:53		69.8		38.5		24-Feb-08		14:25:59		66.2		43.5

		14-Jan-08		16:07:10		65.6		49.5		14-Jan-08		16:06:20		68.61		46.5		14-Jan-08		16:07:53		69.8		42.5		24-Feb-08		16:25:59		65.6		43.5

		14-Jan-08		18:07:10		66.2		49.5		14-Jan-08		18:06:20		68.61		47		14-Jan-08		18:07:53		69.8		45		24-Feb-08		18:25:59		65.01		44

		14-Jan-08		20:07:10		66.2		48.5		14-Jan-08		20:06:20		67.4		47		14-Jan-08		20:07:53		69.8		44		24-Feb-08		20:25:59		64.4		45

		14-Jan-08		22:07:10		65.6		47		14-Jan-08		22:06:20		66.2		46		14-Jan-08		22:07:53		69.8		41.5		24-Feb-08		22:25:59		64.4		46

		15-Jan-08		0:07:10		64.4		44		15-Jan-08		0:06:20		65.6		42		15-Jan-08		0:07:53		69.2		39		25-Feb-08		0:25:59		64.4		47.5

		15-Jan-08		2:07:10		63.8		45		15-Jan-08		2:06:20		65.6		43		15-Jan-08		2:07:53		69.8		38.5		25-Feb-08		2:25:59		64.4		48

		15-Jan-08		4:07:10		63.8		45		15-Jan-08		4:06:20		65.6		42.5		15-Jan-08		4:07:53		69.8		38		25-Feb-08		4:25:59		64.4		49

		15-Jan-08		6:07:10		63.21		46		15-Jan-08		6:06:20		65.6		44		15-Jan-08		6:07:53		69.8		38.5		25-Feb-08		6:25:59		64.4		49.5

		15-Jan-08		8:07:10		63.8		47		15-Jan-08		8:06:20		67.4		42.5		15-Jan-08		8:07:53		71		39.5		25-Feb-08		8:25:59		65.01		49.5

		15-Jan-08		10:07:10		65.01		47.5		15-Jan-08		10:06:20		70.41		41.5		15-Jan-08		10:07:53		71		37		25-Feb-08		10:25:59		66.2		49.5

		15-Jan-08		12:07:10		65.6		47.5		15-Jan-08		12:06:20		70.41		43		15-Jan-08		12:07:53		71		43.5		25-Feb-08		12:25:59		66.81		49.5

		15-Jan-08		14:07:10		66.2		48		15-Jan-08		14:06:20		70.41		46.5		15-Jan-08		14:07:53		71		43.5		25-Feb-08		14:25:59		67.4		50

		15-Jan-08		16:07:10		66.81		49.5		15-Jan-08		16:06:20		71		44		15-Jan-08		16:07:53		70.41		45		25-Feb-08		16:25:59		67.4		50

		15-Jan-08		18:07:10		66.81		48		15-Jan-08		18:06:20		69.2		44		15-Jan-08		18:07:53		70.41		43.5		25-Feb-08		18:25:59		67.4		49.5

		15-Jan-08		20:07:10		66.81		45.5		15-Jan-08		20:06:20		67.4		44		15-Jan-08		20:07:53		69.8		41.5		25-Feb-08		20:25:59		66.81		49

		15-Jan-08		22:07:10		65.6		43.5		15-Jan-08		22:06:20		65.6		42.5		15-Jan-08		22:07:53		68.61		41		25-Feb-08		22:25:59		66.2		49

		16-Jan-08		0:07:10		65.01		43		16-Jan-08		0:06:20		65.6		41		16-Jan-08		0:07:53		66.81		40		26-Feb-08		0:25:59		65.6		49.5

		16-Jan-08		2:07:10		64.4		42.5		16-Jan-08		2:06:20		65.01		41.5		16-Jan-08		2:07:53		65.6		41		26-Feb-08		2:25:59		65.01		50

		16-Jan-08		4:07:10		63.8		42.5		16-Jan-08		4:06:20		65.6		40		16-Jan-08		4:07:53		64.4		41		26-Feb-08		4:25:59		64.4		49.5

		16-Jan-08		6:07:10		63.21		42		16-Jan-08		6:06:20		65.01		40		16-Jan-08		6:07:53		67.4		38		26-Feb-08		6:25:59		66.2		48

		16-Jan-08		8:07:10		63.8		41		16-Jan-08		8:06:20		67.4		37		16-Jan-08		8:07:53		69.2		36.5		26-Feb-08		8:25:59		69.8		45

		16-Jan-08		10:07:10		65.01		41		16-Jan-08		10:06:20		70.41		36		16-Jan-08		10:07:53		71		36		26-Feb-08		10:25:59		72.21		44

		16-Jan-08		12:07:10		65.6		42.5		16-Jan-08		12:06:20		71		35		16-Jan-08		12:07:53		71.6		36		26-Feb-08		12:25:59		72.21		43.5

		16-Jan-08		14:07:10		66.81		44.5		16-Jan-08		14:06:20		71		39		16-Jan-08		14:07:53		70.41		43.5		26-Feb-08		14:25:59		72.8		43

		16-Jan-08		16:07:10		68		46		16-Jan-08		16:06:20		71.6		40.5		16-Jan-08		16:07:53		69.8		44.5		26-Feb-08		16:25:59		73.4		42

		16-Jan-08		18:07:10		68		44.5		16-Jan-08		18:06:20		69.8		42		16-Jan-08		18:07:53		69.8		43.5		26-Feb-08		18:25:59		73.4		42.5

		16-Jan-08		20:07:10		68		44		16-Jan-08		20:06:20		68.61		43.5		16-Jan-08		20:07:53		69.2		43		26-Feb-08		20:25:59		72.21		42.5

		16-Jan-08		22:07:10		67.4		42		16-Jan-08		22:06:20		66.81		43		16-Jan-08		22:07:53		68.61		40.5		26-Feb-08		22:25:59		70.41		43.5

		17-Jan-08		0:07:10		66.2		40.5		17-Jan-08		0:06:20		65.6		41		17-Jan-08		0:07:53		66.81		39.5		27-Feb-08		0:25:59		68		43.5

		17-Jan-08		2:07:10		65.01		40.5		17-Jan-08		2:06:20		65.6		39		17-Jan-08		2:07:53		65.6		39.5		27-Feb-08		2:25:59		66.81		43.5

		17-Jan-08		4:07:10		63.8		40		17-Jan-08		4:06:20		65.6		38.5		17-Jan-08		4:07:53		64.4		39.5		27-Feb-08		4:25:59		65.6		43.5

		17-Jan-08		6:07:10		63.8		39.5		17-Jan-08		6:06:20		65.6		37		17-Jan-08		6:07:53		66.2		37		27-Feb-08		6:25:59		66.81		43.5

		17-Jan-08		8:07:10		64.4		38.5		17-Jan-08		8:06:20		68		34.5		17-Jan-08		8:07:53		69.2		35.5		27-Feb-08		8:25:59		71.6		41

		17-Jan-08		10:07:10		65.01		35		17-Jan-08		10:06:20		70.41		29.5		17-Jan-08		10:07:53		71.6		31		27-Feb-08		10:25:59		72.21		41

		17-Jan-08		12:07:10		66.2		29		17-Jan-08		12:06:20		71		21.5		17-Jan-08		12:07:53		69.8		23.5		27-Feb-08		12:25:59		72.21		42.5

		17-Jan-08		14:07:10		67.4		27		17-Jan-08		14:06:20		71		22.5		17-Jan-08		14:07:53		71		23.5		27-Feb-08		14:25:59		74.01		40

		17-Jan-08		16:07:10		68		25		17-Jan-08		16:06:20		70.41		21.5		17-Jan-08		16:07:53		70.41		24.5		27-Feb-08		16:25:59		74.01		40

		17-Jan-08		18:07:10		68.61		24		17-Jan-08		18:06:20		69.8		19		17-Jan-08		18:07:53		69.8		22.5		27-Feb-08		18:25:59		74.01		41.5

		17-Jan-08		20:07:10		68.61		22		17-Jan-08		20:06:20		69.8		18		17-Jan-08		20:07:53		70.41		23		27-Feb-08		20:25:59		72.8		42.5

		17-Jan-08		22:07:10		68.61		20.5		17-Jan-08		22:06:20		69.2		17.5		17-Jan-08		22:07:53		70.41		24		27-Feb-08		22:25:59		71.6		43

		18-Jan-08		0:07:10		68		20		18-Jan-08		0:06:20		68		18		18-Jan-08		0:07:53		69.2		23		28-Feb-08		0:25:59		69.8		43

		18-Jan-08		2:07:10		67.4		21.5		18-Jan-08		2:06:20		66.2		22		18-Jan-08		2:07:53		68		24		28-Feb-08		2:25:59		68.61		44

		18-Jan-08		4:07:10		66.2		21		18-Jan-08		4:06:20		66.2		20		18-Jan-08		4:07:53		66.81		23.5		28-Feb-08		4:25:59		67.4		44

		18-Jan-08		6:07:10		65.6		24.5		18-Jan-08		6:06:20		65.6		26		18-Jan-08		6:07:53		65.6		26		28-Feb-08		6:25:59		67.4		43.5

		18-Jan-08		8:07:10		65.6		26.5		18-Jan-08		8:06:20		67.4		26		18-Jan-08		8:07:53		69.8		26		28-Feb-08		8:25:59		71		41

		18-Jan-08		10:07:10		66.81		29		18-Jan-08		10:06:20		70.41		27.5		18-Jan-08		10:07:53		71.6		27		28-Feb-08		10:25:59		72.21		41

		18-Jan-08		12:07:10		67.4		28.5		18-Jan-08		12:06:20		71		26.5		18-Jan-08		12:07:53		71		28		28-Feb-08		12:25:59		72.8		42.5

		18-Jan-08		14:07:10		68		29		18-Jan-08		14:06:20		71		28		18-Jan-08		14:07:53		71		29		28-Feb-08		14:25:59		74.01		42.5

		18-Jan-08		16:07:10		68.61		29		18-Jan-08		16:06:20		70.41		29.5		18-Jan-08		16:07:53		71		31.5		28-Feb-08		16:25:59		75.2		43.5

		18-Jan-08		18:07:10		69.2		30		18-Jan-08		18:06:20		69.8		29.5		18-Jan-08		18:07:53		70.41		31.5		28-Feb-08		18:25:59		74.6		43.5

		18-Jan-08		20:07:10		69.2		32		18-Jan-08		20:06:20		68.61		34		18-Jan-08		20:07:53		71		32.5		28-Feb-08		20:25:59		72.21		44

		18-Jan-08		22:07:10		68		32		18-Jan-08		22:06:20		66.81		34.5		18-Jan-08		22:07:53		69.8		32		28-Feb-08		22:25:59		71.6		44.5

		19-Jan-08		0:07:10		66.81		32.5		19-Jan-08		0:06:20		66.2		34		19-Jan-08		0:07:53		68		32.5		29-Feb-08		0:25:59		69.2		44

		19-Jan-08		2:07:10		66.2		32.5		19-Jan-08		2:06:20		65.6		33		19-Jan-08		2:07:53		66.2		32.5		29-Feb-08		2:25:59		68		43.5

		19-Jan-08		4:07:10		65.01		32.5		19-Jan-08		4:06:20		65.6		32.5		19-Jan-08		4:07:53		65.01		32.5		29-Feb-08		4:25:59		66.81		43

		19-Jan-08		6:07:10		64.4		32.5		19-Jan-08		6:06:20		65.6		32		19-Jan-08		6:07:53		67.4		30		29-Feb-08		6:25:59		67.4		42.5

		19-Jan-08		8:07:10		65.01		32		19-Jan-08		8:06:20		68		29.5		19-Jan-08		8:07:53		69.2		31		29-Feb-08		8:25:59		70.41		40

		19-Jan-08		10:07:10		65.6		33		19-Jan-08		10:06:20		68.61		31		19-Jan-08		10:07:53		71.6		30		29-Feb-08		10:25:59		72.21		40.5

		19-Jan-08		12:07:10		65.6		35.5		19-Jan-08		12:06:20		70.41		33.5		19-Jan-08		12:07:53		71		30.5		29-Feb-08		12:25:59		73.4		42

		19-Jan-08		14:07:10		66.2		35.5		19-Jan-08		14:06:20		70.41		33.5		19-Jan-08		14:07:53		71		34.5		29-Feb-08		14:25:59		74.6		41.5

		19-Jan-08		16:07:10		67.4		35		19-Jan-08		16:06:20		71		32		19-Jan-08		16:07:53		71		34.5		29-Feb-08		16:25:59		74.6		41.5

		19-Jan-08		18:07:10		68		35.5		19-Jan-08		18:06:20		69.8		34		19-Jan-08		18:07:53		70.41		35		29-Feb-08		18:25:59		74.01		43.5

		19-Jan-08		20:07:10		68		34		19-Jan-08		20:06:20		68		34.5		19-Jan-08		20:07:53		69.8		34		29-Feb-08		20:25:59		72.21		42.5

		19-Jan-08		22:07:10		67.4		34.5		19-Jan-08		22:06:20		66.2		36.5		19-Jan-08		22:07:53		68.61		35		29-Feb-08		22:25:59		71		43.5

		20-Jan-08		0:07:10		66.2		34		20-Jan-08		0:06:20		65.6		35		20-Jan-08		0:07:53		67.4		34		1-Mar-08		0:25:59		69.8		43

		20-Jan-08		2:07:10		65.6		34		20-Jan-08		2:06:20		65.6		34		20-Jan-08		2:07:53		65.6		34		1-Mar-08		2:25:59		68.61		43.5

		20-Jan-08		4:07:10		64.4		33		20-Jan-08		4:06:20		65.6		33		20-Jan-08		4:07:53		64.4		33.5		1-Mar-08		4:25:59		68		44

		20-Jan-08		6:07:10		63.8		32.5		20-Jan-08		6:06:20		65.6		31		20-Jan-08		6:07:53		63.21		33.5		1-Mar-08		6:25:59		68		44.5

		20-Jan-08		8:07:10		63.8		31.5		20-Jan-08		8:06:20		67.4		28		20-Jan-08		8:07:53		67.4		29		1-Mar-08		8:25:59		71.6		42

		20-Jan-08		10:07:10		63.8		32		20-Jan-08		10:06:20		68		30		20-Jan-08		10:07:53		66.81		29.5		1-Mar-08		10:25:59		72.8		41.5

		20-Jan-08		12:07:10		64.4		36.5		20-Jan-08		12:06:20		68.61		35		20-Jan-08		12:07:53		67.4		33		1-Mar-08		12:25:59		72.21		43

		20-Jan-08		14:07:10		65.01		37		20-Jan-08		14:06:20		68.61		35		20-Jan-08		14:07:53		67.4		35.5		1-Mar-08		14:25:59		72.8		44

		20-Jan-08		16:07:10		66.2		36.5		20-Jan-08		16:06:20		69.8		33.5		20-Jan-08		16:07:53		68.61		35.5		1-Mar-08		16:25:59		74.01		45

		20-Jan-08		18:07:10		66.81		36.5		20-Jan-08		18:06:20		69.2		34.5		20-Jan-08		18:07:53		69.8		35.5		1-Mar-08		18:25:59		73.4		43.5

		20-Jan-08		20:07:10		66.81		34.5		20-Jan-08		20:06:20		68		33.5		20-Jan-08		20:07:53		69.2		34		1-Mar-08		20:25:59		72.21		43

		20-Jan-08		22:07:10		66.2		35		20-Jan-08		22:06:20		66.2		35.5		20-Jan-08		22:07:53		67.4		34.5		1-Mar-08		22:25:59		71		43

		21-Jan-08		0:07:10		65.01		35		21-Jan-08		0:06:20		65.6		35		21-Jan-08		0:07:53		65.6		34.5		2-Mar-08		0:25:59		69.2		43

		21-Jan-08		2:07:10		64.4		38.5		21-Jan-08		2:06:20		65.6		39		21-Jan-08		2:07:53		65.01		37		2-Mar-08		2:25:59		68.61		44

		21-Jan-08		4:07:10		64.4		38.5		21-Jan-08		4:06:20		65.6		38		21-Jan-08		4:07:53		64.4		38		2-Mar-08		4:25:59		67.4		44.5

		21-Jan-08		6:07:10		63.8		37		21-Jan-08		6:06:20		65.6		36		21-Jan-08		6:07:53		63.8		37.5		2-Mar-08		6:25:59		67.4		44.5

		21-Jan-08		8:07:10		63.8		38		21-Jan-08		8:06:20		67.4		35		21-Jan-08		8:07:53		66.81		34.5		2-Mar-08		8:25:59		67.4		44

		21-Jan-08		10:07:10		63.8		38.5		21-Jan-08		10:06:20		68		35		21-Jan-08		10:07:53		66.81		35.5		2-Mar-08		10:25:59		68		43.5

		21-Jan-08		12:07:10		64.4		40		21-Jan-08		12:06:20		68		36.5		21-Jan-08		12:07:53		67.4		36		2-Mar-08		12:25:59		69.2		42

		21-Jan-08		14:07:10		64.4		35		21-Jan-08		14:06:20		68		31		21-Jan-08		14:07:53		67.4		33.5		2-Mar-08		14:25:59		70.41		40.5

		21-Jan-08		16:07:10		65.01		34.5		21-Jan-08		16:06:20		68		32		21-Jan-08		16:07:53		67.4		34		2-Mar-08		16:25:59		69.8		39

		21-Jan-08		18:07:10		65.6		33.5		21-Jan-08		18:06:20		68		31		21-Jan-08		18:07:53		67.4		33.5		2-Mar-08		18:25:59		69.8		38

		21-Jan-08		20:07:10		65.6		34.5		21-Jan-08		20:06:20		66.2		34		21-Jan-08		20:07:53		66.81		34		2-Mar-08		20:25:59		68.61		39

		21-Jan-08		22:07:10		65.01		34.5		21-Jan-08		22:06:20		65.6		34		21-Jan-08		22:07:53		65.01		34.5		2-Mar-08		22:25:59		67.4		39.5

		22-Jan-08		0:07:10		64.4		34.5		22-Jan-08		0:06:20		65.6		33.5		22-Jan-08		0:07:53		63.8		35		3-Mar-08		0:25:59		66.81		40

		22-Jan-08		2:07:10		63.8		34		22-Jan-08		2:06:20		65.01		32		22-Jan-08		2:07:53		62.6		34		3-Mar-08		2:25:59		65.6		40

		22-Jan-08		4:07:10		63.21		32.5		22-Jan-08		4:06:20		65.01		30.5		22-Jan-08		4:07:53		61.41		33.5		3-Mar-08		4:25:59		65.01		39.5

		22-Jan-08		6:07:10		62.6		31.5		22-Jan-08		6:06:20		65.01		30		22-Jan-08		6:07:53		66.81		29.5		3-Mar-08		6:25:59		64.4		39.5

		22-Jan-08		8:07:10		63.21		32		22-Jan-08		8:06:20		67.4		28.5		22-Jan-08		8:07:53		68		30		3-Mar-08		8:25:59		65.01		38.5

		22-Jan-08		10:07:10		64.4		33.5		22-Jan-08		10:06:20		69.2		30		22-Jan-08		10:07:53		70.41		30.5		3-Mar-08		10:25:59		66.2		38

		22-Jan-08		12:07:10		65.01		36		22-Jan-08		12:06:20		70.41		32.5		22-Jan-08		12:07:53		71.6		31		3-Mar-08		12:25:59		66.81		38

		22-Jan-08		14:07:10		66.2		37.5		22-Jan-08		14:06:20		71		35.5		22-Jan-08		14:07:53		71		36		3-Mar-08		14:25:59		67.4		35.5

		22-Jan-08		16:07:10		66.81		39		22-Jan-08		16:06:20		71		34.5		22-Jan-08		16:07:53		70.41		37		3-Mar-08		16:25:59		68.61		33.5

		22-Jan-08		18:07:10		67.4		37		22-Jan-08		18:06:20		68.61		36		22-Jan-08		18:07:53		69.8		36		3-Mar-08		18:25:59		68.61		31.5

		22-Jan-08		20:07:10		67.4		36.5		22-Jan-08		20:06:20		68		36.5		22-Jan-08		20:07:53		69.8		35		3-Mar-08		20:25:59		68.61		31

		22-Jan-08		22:07:10		66.81		37		22-Jan-08		22:06:20		67.4		36.5		22-Jan-08		22:07:53		67.4		36		3-Mar-08		22:25:59		68		33

		23-Jan-08		0:07:10		65.6		37.5		23-Jan-08		0:06:20		67.4		36.5		23-Jan-08		0:07:53		65.6		37.5		4-Mar-08		0:25:59		66.81		35

		23-Jan-08		2:07:10		65.01		37		23-Jan-08		2:06:20		67.4		35.5		23-Jan-08		2:07:53		65.01		38		4-Mar-08		2:25:59		66.2		37

		23-Jan-08		4:07:10		64.4		37.5		23-Jan-08		4:06:20		66.81		35.5		23-Jan-08		4:07:53		63.8		38.5		4-Mar-08		4:25:59		65.6		37.5

		23-Jan-08		6:07:10		64.4		37		23-Jan-08		6:06:20		66.81		35		23-Jan-08		6:07:53		67.4		35.5		4-Mar-08		6:25:59		66.2		37.5

		23-Jan-08		8:07:10		65.01		36		23-Jan-08		8:06:20		68		33		23-Jan-08		8:07:53		69.2		34		4-Mar-08		8:25:59		69.2		35.5

		23-Jan-08		10:07:10		65.6		36.5		23-Jan-08		10:06:20		69.2		34		23-Jan-08		10:07:53		71		35		4-Mar-08		10:25:59		71.6		36.5

		23-Jan-08		12:07:10		66.2		36		23-Jan-08		12:06:20		69.8		33		23-Jan-08		12:07:53		71		34		4-Mar-08		12:25:59		72.21		36.5

		23-Jan-08		14:07:10		66.81		34.5		23-Jan-08		14:06:20		70.41		32		23-Jan-08		14:07:53		70.41		35		4-Mar-08		14:25:59		73.4		33.5

		23-Jan-08		16:07:10		66.81		33.5		23-Jan-08		16:06:20		69.8		31.5		23-Jan-08		16:07:53		70.41		32		4-Mar-08		16:25:59		74.01		33.5

		23-Jan-08		18:07:10		66.81		33		23-Jan-08		18:06:20		69.2		31		23-Jan-08		18:07:53		69.2		32		4-Mar-08		18:25:59		74.01		33

		23-Jan-08		20:07:10		66.81		32.5		23-Jan-08		20:06:20		68		31		23-Jan-08		20:07:53		68		32.5		4-Mar-08		20:25:59		72.21		32

		23-Jan-08		22:07:10		66.2		32.5		23-Jan-08		22:06:20		67.4		32		23-Jan-08		22:07:53		68		32.5		4-Mar-08		22:25:59		71		33.5

		24-Jan-08		0:07:10		65.6		33.5		24-Jan-08		0:06:20		66.81		32.5		24-Jan-08		0:07:53		66.2		33		5-Mar-08		0:25:59		69.2		34.5

		24-Jan-08		2:07:10		65.01		34		24-Jan-08		2:06:20		67.4		32.5		24-Jan-08		2:07:53		64.4		34.5		5-Mar-08		2:25:59		68		35.5

		24-Jan-08		4:07:10		64.4		35.5		24-Jan-08		4:06:20		67.4		34		24-Jan-08		4:07:53		63.8		36		5-Mar-08		4:25:59		66.81		36

		24-Jan-08		6:07:10		64.4		37		24-Jan-08		6:06:20		66.81		35		24-Jan-08		6:07:53		68		34		5-Mar-08		6:25:59		66.81		36.5

		24-Jan-08		8:07:10		65.01		37		24-Jan-08		8:06:20		68		35		24-Jan-08		8:07:53		69.2		35.5		5-Mar-08		8:25:59		69.8		34

		24-Jan-08		10:07:10		65.6		38		24-Jan-08		10:06:20		71		33.5		24-Jan-08		10:07:53		71		35		5-Mar-08		10:25:59		72.21		36

		24-Jan-08		12:07:10		66.81		39		24-Jan-08		12:06:20		71		36		24-Jan-08		12:07:53		71		37		5-Mar-08		12:25:59		72.8		36.5

		24-Jan-08		14:07:10		68		38		24-Jan-08		14:06:20		71		37		24-Jan-08		14:07:53		71		38.5		5-Mar-08		14:25:59		74.01		36.5

		24-Jan-08		16:07:10		68		36		24-Jan-08		16:06:20		71		34		24-Jan-08		16:07:53		71.6		35		5-Mar-08		16:25:59		74.6		35.5

		24-Jan-08		18:07:10		68.61		34.5		24-Jan-08		18:06:20		68.61		33.5		24-Jan-08		18:07:53		71		34		5-Mar-08		18:25:59		74.6		36.5

		24-Jan-08		20:07:10		68		35.5		24-Jan-08		20:06:20		68		36.5		24-Jan-08		20:07:53		69.8		35		5-Mar-08		20:25:59		72.8		37

		24-Jan-08		22:07:10		67.4		36.5		24-Jan-08		22:06:20		67.4		37		24-Jan-08		22:07:53		68		36		5-Mar-08		22:25:59		71		37

		25-Jan-08		0:07:10		66.2		36.5		25-Jan-08		0:06:20		67.4		36		25-Jan-08		0:07:53		66.2		37		6-Mar-08		0:25:59		69.2		37

		25-Jan-08		2:07:10		65.6		37.5		25-Jan-08		2:06:20		66.81		37		25-Jan-08		2:07:53		65.01		38		6-Mar-08		2:25:59		68		37.5

		25-Jan-08		4:07:10		65.01		39		25-Jan-08		4:06:20		67.4		37.5		25-Jan-08		4:07:53		64.4		39.5		6-Mar-08		4:25:59		66.81		38

		25-Jan-08		6:07:10		64.4		39.5		25-Jan-08		6:06:20		67.4		38		25-Jan-08		6:07:53		66.81		38		6-Mar-08		6:25:59		66.81		37.5

		25-Jan-08		8:07:10		65.01		39		25-Jan-08		8:06:20		68		36.5		25-Jan-08		8:07:53		69.2		36		6-Mar-08		8:25:59		70.41		35.5

		25-Jan-08		10:07:10		65.6		40.5		25-Jan-08		10:06:20		69.8		37		25-Jan-08		10:07:53		71.6		36		6-Mar-08		10:25:59		71.6		36.5

		25-Jan-08		12:07:10		66.81		39.5		25-Jan-08		12:06:20		69.8		37.5		25-Jan-08		12:07:53		72.21		36		6-Mar-08		12:25:59		72.8		35.5

		25-Jan-08		14:07:10		67.4		38		25-Jan-08		14:06:20		69.8		37.5		25-Jan-08		14:07:53		71		37.5		6-Mar-08		14:25:59		74.01		32.5

		25-Jan-08		16:07:10		68.61		37.5		25-Jan-08		16:06:20		70.41		37		25-Jan-08		16:07:53		70.41		38		6-Mar-08		16:25:59		74.6		31

		25-Jan-08		18:07:10		68.61		36		25-Jan-08		18:06:20		68		36.5		25-Jan-08		18:07:53		69.8		36		6-Mar-08		18:25:59		68.61		44.5

		25-Jan-08		20:07:10		68.61		35		25-Jan-08		20:06:20		67.4		37		25-Jan-08		20:07:53		68.61		36		6-Mar-08		20:25:59		68.61		44

		25-Jan-08		22:07:10		68		35.5		25-Jan-08		22:06:20		66.81		37		25-Jan-08		22:07:53		67.4		37.5		6-Mar-08		22:25:59		68.61		42.5

		26-Jan-08		0:07:10		67.4		35.5		26-Jan-08		0:06:20		66.81		36		26-Jan-08		0:07:53		66.81		37.5		7-Mar-08		0:25:59		68.61		44

		26-Jan-08		2:07:10		66.81		36		26-Jan-08		2:06:20		66.81		36.5		26-Jan-08		2:07:53		65.6		37.5		7-Mar-08		2:25:59		68		43

		26-Jan-08		4:07:10		66.2		35		26-Jan-08		4:06:20		66.81		35		26-Jan-08		4:07:53		65.6		37.5		7-Mar-08		4:25:59		69.2		44

		26-Jan-08		6:07:10		65.6		37.5		26-Jan-08		6:06:20		66.81		38		26-Jan-08		6:07:53		68.61		36.5		7-Mar-08		6:25:59		68.61		43.5

		26-Jan-08		8:07:10		66.2		39.5		26-Jan-08		8:06:20		67.4		40		26-Jan-08		8:07:53		69.2		38.5		7-Mar-08		8:25:59		68.61		44.5

		26-Jan-08		10:07:10		67.4		42		26-Jan-08		10:06:20		69.8		42		26-Jan-08		10:07:53		71.6		40.5		7-Mar-08		10:25:59		68.61		44.5

		26-Jan-08		12:07:10		68.61		41		26-Jan-08		12:06:20		69.2		42.5		26-Jan-08		12:07:53		71		43		7-Mar-08		12:25:59		68.61		45

		26-Jan-08		14:07:10		69.8		42		26-Jan-08		14:06:20		71		44		26-Jan-08		14:07:53		71		38.5		7-Mar-08		14:25:59		68.61		45

		26-Jan-08		16:07:10		70.41		43.5		26-Jan-08		16:06:20		70.41		46.5		26-Jan-08		16:07:53		70.41		44.5		7-Mar-08		16:25:59		68.61		44

		26-Jan-08		18:07:10		69.8		42.5		26-Jan-08		18:06:20		68.61		45.5		26-Jan-08		18:07:53		69.2		44		7-Mar-08		18:25:59		68.61		44.5

		26-Jan-08		20:07:10		69.2		44.5		26-Jan-08		20:06:20		68		48		26-Jan-08		20:07:53		68.61		45.5		7-Mar-08		20:25:59		68.61		46.5

		26-Jan-08		22:07:10		68.61		46.5		26-Jan-08		22:06:20		68		49.5		26-Jan-08		22:07:53		68		47.5		7-Mar-08		22:25:59		68.61		45.5

		27-Jan-08		0:07:10		68.61		47.5		27-Jan-08		0:06:20		67.4		51		27-Jan-08		0:07:53		67.4		48		8-Mar-08		0:25:59		68.61		44.5

		27-Jan-08		2:07:10		68		48.5		27-Jan-08		2:06:20		67.4		51.5		27-Jan-08		2:07:53		67.4		48.5		8-Mar-08		2:25:59		68		45

		27-Jan-08		4:07:10		68		49		27-Jan-08		4:06:20		67.4		51		27-Jan-08		4:07:53		67.4		49		8-Mar-08		4:25:59		68		44

		27-Jan-08		6:07:10		67.4		48		27-Jan-08		6:06:20		67.4		49		27-Jan-08		6:07:53		66.81		49		8-Mar-08		6:25:59		68		45

		27-Jan-08		8:07:10		67.4		44.5		27-Jan-08		8:06:20		68		43.5		27-Jan-08		8:07:53		68		45.5		8-Mar-08		8:25:59		68.61		45

		27-Jan-08		10:07:10		67.4		40.5		27-Jan-08		10:06:20		67.4		39.5		27-Jan-08		10:07:53		68		43		8-Mar-08		10:25:59		68.61		45

		27-Jan-08		12:07:10		67.4		39.5		27-Jan-08		12:06:20		67.4		39		27-Jan-08		12:07:53		67.4		42		8-Mar-08		12:25:59		68.61		45

		27-Jan-08		14:07:10		67.4		39		27-Jan-08		14:06:20		68		38.5		27-Jan-08		14:07:53		68		42		8-Mar-08		14:25:59		68.61		45

		27-Jan-08		16:07:10		67.4		39.5		27-Jan-08		16:06:20		68		39		27-Jan-08		16:07:53		68		41		8-Mar-08		16:25:59		68.61		45

		27-Jan-08		18:07:10		68		40		27-Jan-08		18:06:20		68.61		40.5		27-Jan-08		18:07:53		68.61		41.5		8-Mar-08		18:25:59		68.61		44.5

		27-Jan-08		20:07:10		68		39.5		27-Jan-08		20:06:20		67.4		40.5		27-Jan-08		20:07:53		68		42		8-Mar-08		20:25:59		68.61		45.5

		27-Jan-08		22:07:10		67.4		41		27-Jan-08		22:06:20		67.4		42		27-Jan-08		22:07:53		67.4		42.5		8-Mar-08		22:25:59		68.61		45

		28-Jan-08		0:07:10		67.4		43.5		28-Jan-08		0:06:20		67.4		46.5		28-Jan-08		0:07:53		67.4		44		9-Mar-08		0:25:59		68		45

		28-Jan-08		2:07:10		66.81		47.5		28-Jan-08		2:06:20		67.4		49		28-Jan-08		2:07:53		66.81		46.5		9-Mar-08		2:25:59		68		45

		28-Jan-08		4:07:10		66.81		46.5		28-Jan-08		4:06:20		67.4		47		28-Jan-08		4:07:53		66.81		46.5		9-Mar-08		4:25:59		68.61		45

		28-Jan-08		6:07:10		66.81		47.5		28-Jan-08		6:06:20		67.4		48.5		28-Jan-08		6:07:53		66.81		47.5		9-Mar-08		6:25:59		68.61		44.5

		28-Jan-08		8:07:10		66.81		48.5		28-Jan-08		8:06:20		68		48.5		28-Jan-08		8:07:53		67.4		47		9-Mar-08		8:25:59		68.61		45.5

		28-Jan-08		10:07:10		66.81		49.5		28-Jan-08		10:06:20		68		49		28-Jan-08		10:07:53		67.4		47.5		9-Mar-08		10:25:59		68.61		45

		28-Jan-08		12:07:10		66.81		48		28-Jan-08		12:06:20		68		47.5		28-Jan-08		12:07:53		68		47.5		9-Mar-08		12:25:59		68.61		45.5

		28-Jan-08		14:07:10		66.81		45.5		28-Jan-08		14:06:20		68		45		28-Jan-08		14:07:53		68		46		9-Mar-08		14:25:59		68.61		45

		28-Jan-08		16:07:10		67.4		47.5		28-Jan-08		16:06:20		68		49		28-Jan-08		16:07:53		68		47.5		9-Mar-08		16:25:59		68.61		45

		28-Jan-08		18:07:10		68		48.5		28-Jan-08		18:06:20		68		49		28-Jan-08		18:07:53		67.4		48.5		9-Mar-08		18:25:59		68.61		45

		28-Jan-08		20:07:10		68		49		28-Jan-08		20:06:20		67.4		50.5		28-Jan-08		20:07:53		67.4		49		9-Mar-08		20:25:59		68.61		46

		28-Jan-08		22:07:10		67.4		40.5		28-Jan-08		22:06:20		66.81		37.5		28-Jan-08		22:07:53		66.2		41.5		9-Mar-08		22:25:59		68.61		45

		29-Jan-08		0:07:10		66.2		36.5		29-Jan-08		0:06:20		66.2		35		29-Jan-08		0:07:53		63.8		38		10-Mar-08		0:25:59		68		45

		29-Jan-08		2:07:10		65.6		36.5		29-Jan-08		2:06:20		66.81		35.5		29-Jan-08		2:07:53		63.21		39		10-Mar-08		2:25:59		68.61		45

		29-Jan-08		4:07:10		65.6		36.5		29-Jan-08		4:06:20		66.81		35		29-Jan-08		4:07:53		62.6		39.5		10-Mar-08		4:25:59		68.61		45.5

		29-Jan-08		6:07:10		65.6		36		29-Jan-08		6:06:20		66.81		35		29-Jan-08		6:07:53		66.81		36.5		10-Mar-08		6:25:59		68.61		45.5

		29-Jan-08		8:07:10		65.6		36		29-Jan-08		8:06:20		67.4		34.5		29-Jan-08		8:07:53		69.2		35		10-Mar-08		8:25:59		68		45.5

		29-Jan-08		10:07:10		66.2		37.5		29-Jan-08		10:06:20		69.8		34.5		29-Jan-08		10:07:53		70.41		36.5		10-Mar-08		10:25:59		68		45.5

		29-Jan-08		12:07:10		67.4		37.5		29-Jan-08		12:06:20		70.41		35.5		29-Jan-08		12:07:53		71		37		10-Mar-08		12:25:59		68.61		45.5

		29-Jan-08		14:07:10		68.61		35		29-Jan-08		14:06:20		71		31		29-Jan-08		14:07:53		70.41		38		10-Mar-08		14:25:59		68.61		45

		29-Jan-08		16:07:10		69.2		34.5		29-Jan-08		16:06:20		69.8		34		29-Jan-08		16:07:53		70.41		35.5		10-Mar-08		16:25:59		68.61		45.5

		29-Jan-08		18:07:10		69.8		33.5		29-Jan-08		18:06:20		69.2		34		29-Jan-08		18:07:53		69.8		35		10-Mar-08		18:25:59		68.61		45

		29-Jan-08		20:07:10		69.2		32.5		29-Jan-08		20:06:20		67.4		33.5		29-Jan-08		20:07:53		68		35		10-Mar-08		20:25:59		68.61		45

		29-Jan-08		22:07:10		68.61		32.5		29-Jan-08		22:06:20		67.4		33.5		29-Jan-08		22:07:53		66.2		35.5		10-Mar-08		22:25:59		68		45

		30-Jan-08		0:07:10		68		31.5		30-Jan-08		0:06:20		66.81		32.5		30-Jan-08		0:07:53		65.01		35.5		11-Mar-08		0:25:59		68.61		45

		30-Jan-08		2:07:10		67.4		30.5		30-Jan-08		2:06:20		66.81		30.5		30-Jan-08		2:07:53		63.21		34.5		11-Mar-08		2:25:59		68.61		45

		30-Jan-08		4:07:10		66.81		30		30-Jan-08		4:06:20		66.81		30		30-Jan-08		4:07:53		62		34		11-Mar-08		4:25:59		68.61		46

		30-Jan-08		6:07:10		66.81		31		30-Jan-08		6:06:20		66.81		31		30-Jan-08		6:07:53		67.4		31.5		11-Mar-08		6:25:59		68.61		45.5

		30-Jan-08		8:07:10		66.81		31.5		30-Jan-08		8:06:20		67.4		31.5		30-Jan-08		8:07:53		69.2		33		11-Mar-08		8:25:59		68.61		44.5

		30-Jan-08		10:07:10		67.4		33.5		30-Jan-08		10:06:20		69.8		32.5		30-Jan-08		10:07:53		70.41		35		11-Mar-08		10:25:59		68		45

		30-Jan-08		12:07:10		68.61		36		30-Jan-08		12:06:20		71		36		30-Jan-08		12:07:53		71		37.5		11-Mar-08		12:25:59		68.61		46

		30-Jan-08		14:07:10		69.8		39		30-Jan-08		14:06:20		71.6		40.5		30-Jan-08		14:07:53		71		42		11-Mar-08		14:25:59		68		49.5

		30-Jan-08		16:07:10		71.6		40.5		30-Jan-08		16:06:20		71.6		43		30-Jan-08		16:07:53		71		42		11-Mar-08		16:25:59		68.61		46

		30-Jan-08		18:07:10		71		36		30-Jan-08		18:06:20		68.61		36.5		30-Jan-08		18:07:53		69.8		38		11-Mar-08		18:25:59		68		45

		30-Jan-08		20:07:10		70.41		33		30-Jan-08		20:06:20		68		34		30-Jan-08		20:07:53		68.61		36.5		11-Mar-08		20:25:59		68.61		45

		30-Jan-08		22:07:10		69.8		31.5		30-Jan-08		22:06:20		68		32.5		30-Jan-08		22:07:53		67.4		36		11-Mar-08		22:25:59		68.61		45.5

		31-Jan-08		0:07:10		69.2		32		31-Jan-08		0:06:20		68		33.5		31-Jan-08		0:07:53		65.6		36.5		12-Mar-08		0:25:59		68.61		45

		31-Jan-08		2:07:10		68.61		33		31-Jan-08		2:06:20		68		34		31-Jan-08		2:07:53		65.01		37		12-Mar-08		2:25:59		68		45

		31-Jan-08		4:07:10		68.61		33.5		31-Jan-08		4:06:20		68		34.5		31-Jan-08		4:07:53		64.4		38		12-Mar-08		4:25:59		68		46

		31-Jan-08		6:07:10		68		33.5		31-Jan-08		6:06:20		68		34.5		31-Jan-08		6:07:53		66.81		36		12-Mar-08		6:25:59		68		45

		31-Jan-08		8:07:10		69.8		32.5		31-Jan-08		8:06:20		68		34		31-Jan-08		8:07:53		68.61		35.5		12-Mar-08		8:25:59		68.61		46

		31-Jan-08		10:07:10		71.6		33		31-Jan-08		10:06:20		71		34.5		31-Jan-08		10:07:53		71.6		36.5		12-Mar-08		10:25:59		68.61		45.5

		31-Jan-08		12:07:10		71.6		33.5		31-Jan-08		12:06:20		71		33.5		31-Jan-08		12:07:53		70.41		38		12-Mar-08		12:25:59		68		46

		31-Jan-08		14:07:10		71.6		33.5		31-Jan-08		14:06:20		71		36		31-Jan-08		14:07:53		71.6		36		12-Mar-08		14:25:59		68		46.5

		31-Jan-08		16:07:10		71.6		33.5		31-Jan-08		16:06:20		71		35.5		31-Jan-08		16:07:53		69.8		37		12-Mar-08		16:25:59		68.61		48.5

		31-Jan-08		18:07:10		71		34		31-Jan-08		18:06:20		68.61		37		31-Jan-08		18:07:53		71		36.5		12-Mar-08		18:25:59		68.61		47.5

		31-Jan-08		20:07:10		69.2		36		31-Jan-08		20:06:20		68.61		38		31-Jan-08		20:07:53		70.41		37.5		12-Mar-08		20:25:59		68.61		45.5

		31-Jan-08		22:07:10		67.4		37.5		31-Jan-08		22:06:20		68		38		31-Jan-08		22:07:53		69.2		38.5		12-Mar-08		22:25:59		68.61		45.5

		1-Feb-08		0:07:10		66.2		39		1-Feb-08		0:06:20		68		38		1-Feb-08		0:07:53		67.4		39		13-Mar-08		0:25:59		68		46

		1-Feb-08		2:07:10		65.01		40.5		1-Feb-08		2:06:20		68		38		1-Feb-08		2:07:53		66.2		40		13-Mar-08		2:25:59		68		45

		1-Feb-08		4:07:10		64.4		42		1-Feb-08		4:06:20		68		39		1-Feb-08		4:07:53		65.6		41		13-Mar-08		4:25:59		68.61		45

		1-Feb-08		6:07:10		63.8		43		1-Feb-08		6:06:20		68		39		1-Feb-08		6:07:53		66.81		40.5		13-Mar-08		6:25:59		68.61		45

		1-Feb-08		8:07:10		66.2		42		1-Feb-08		8:06:20		68		40.5		1-Feb-08		8:07:53		69.8		40		13-Mar-08		8:25:59		68.61		45.5

		1-Feb-08		10:07:10		68.61		42		1-Feb-08		10:06:20		71		41.5		1-Feb-08		10:07:53		71.6		42		13-Mar-08		10:25:59		68		45.5

		1-Feb-08		12:07:10		69.2		43		1-Feb-08		12:06:20		71		43		1-Feb-08		12:07:53		71		46		13-Mar-08		12:25:59		68.61		45

		1-Feb-08		14:07:10		69.8		45		1-Feb-08		14:06:20		71		44		1-Feb-08		14:07:53		71		40		13-Mar-08		14:25:59		68.61		47

		1-Feb-08		16:07:10		70.41		46.5		1-Feb-08		16:06:20		71		45		1-Feb-08		16:07:53		70.41		48		13-Mar-08		16:25:59		68.61		47

		1-Feb-08		18:07:10		69.2		48.5		1-Feb-08		18:06:20		69.2		50		1-Feb-08		18:07:53		70.41		48		13-Mar-08		18:25:59		68		45.5

		1-Feb-08		20:07:10		68		44.5		1-Feb-08		20:06:20		68.61		43.5		1-Feb-08		20:07:53		70.41		43.5		13-Mar-08		20:25:59		68.61		45

		1-Feb-08		22:07:10		66.81		41.5		1-Feb-08		22:06:20		68		39.5		1-Feb-08		22:07:53		69.2		41		13-Mar-08		22:25:59		68.61		45.5

		2-Feb-08		0:07:10		65.6		40		2-Feb-08		0:06:20		68		37.5		2-Feb-08		0:07:53		66.81		40		14-Mar-08		0:25:59		68.61		47.5

		2-Feb-08		2:07:10		64.4		38		2-Feb-08		2:06:20		68		34		2-Feb-08		2:07:53		64.4		39		14-Mar-08		2:25:59		68		46

		2-Feb-08		4:07:10		63.21		37.5		2-Feb-08		4:06:20		68		33		2-Feb-08		4:07:53		62.6		38		14-Mar-08		4:25:59		68		47

		2-Feb-08		6:07:10		62.6		36.5		2-Feb-08		6:06:20		68		32		2-Feb-08		6:07:53		67.4		33.5		14-Mar-08		6:25:59		68		46.5

		2-Feb-08		8:07:10		63.8		35		2-Feb-08		8:06:20		67.4		31.5		2-Feb-08		8:07:53		68		33.5		14-Mar-08		8:25:59		68.61		47.5

		2-Feb-08		10:07:10		66.2		36		2-Feb-08		10:06:20		71		33		2-Feb-08		10:07:53		70.41		35.5		14-Mar-08		10:25:59		68		48

		2-Feb-08		12:07:10		68.61		38		2-Feb-08		12:06:20		72.8		36		2-Feb-08		12:07:53		71		39.5		14-Mar-08		12:25:59		68.61		45.5

		2-Feb-08		14:07:10		69.2		38		2-Feb-08		14:06:20		71.6		36.5		2-Feb-08		14:07:53		69.8		39.5		14-Mar-08		14:25:59		68.61		45

		2-Feb-08		16:07:10		68.61		38		2-Feb-08		16:06:20		71		36.5		2-Feb-08		16:07:53		69.8		39		14-Mar-08		16:25:59		68.61		45

		2-Feb-08		18:07:10		68		37.5		2-Feb-08		18:06:20		71		35.5		2-Feb-08		18:07:53		71		39		14-Mar-08		18:25:59		68.61		45

		2-Feb-08		20:07:10		67.4		37		2-Feb-08		20:06:20		68.61		35.5		2-Feb-08		20:07:53		69.2		40		14-Mar-08		20:25:59		68.61		45

		2-Feb-08		22:07:10		66.81		36.5		2-Feb-08		22:06:20		68		34		2-Feb-08		22:07:53		67.4		44		14-Mar-08		22:25:59		68.61		45

		3-Feb-08		0:07:10		66.81		35.5		3-Feb-08		0:06:20		68		33		3-Feb-08		0:07:53		66.81		41		15-Mar-08		0:25:59		68.61		45.5

		3-Feb-08		2:07:10		66.2		35		3-Feb-08		2:06:20		68		33		3-Feb-08		2:07:53		65.6		42		15-Mar-08		2:25:59		68.61		46

		3-Feb-08		4:07:10		66.2		34.5		3-Feb-08		4:06:20		68		33		3-Feb-08		4:07:53		65.01		43		15-Mar-08		4:25:59		68.61		45.5

		3-Feb-08		6:07:10		66.2		34.5		3-Feb-08		6:06:20		68		33.5		3-Feb-08		6:07:53		64.4		44		15-Mar-08		6:25:59		68.61		46

		3-Feb-08		8:07:10		66.2		35.5		3-Feb-08		8:06:20		69.8		33		3-Feb-08		8:07:53		67.4		41.5		15-Mar-08		8:25:59		68.61		45.5

		3-Feb-08		10:07:10		66.2		36.5		3-Feb-08		10:06:20		66.81		36.5		3-Feb-08		10:07:53		67.4		42		15-Mar-08		10:25:59		68.61		45

		3-Feb-08		12:07:10		66.81		40		3-Feb-08		12:06:20		65.6		44.5		3-Feb-08		12:07:53		68		47.5		15-Mar-08		12:25:59		68.61		45

		3-Feb-08		14:07:10		66.2		43.5		3-Feb-08		14:06:20		66.2		47.5		3-Feb-08		14:07:53		67.4		49		15-Mar-08		14:25:59		68.61		44.5

		3-Feb-08		16:07:10		66.2		46		3-Feb-08		16:06:20		66.2		49		3-Feb-08		16:07:53		68		49		15-Mar-08		16:25:59		68		44.5

		3-Feb-08		18:07:10		66.2		47.5		3-Feb-08		18:06:20		66.2		50		3-Feb-08		18:07:53		68.61		51		15-Mar-08		18:25:59		68		44.5

		3-Feb-08		20:07:10		66.2		49.5		3-Feb-08		20:06:20		66.81		52		3-Feb-08		20:07:53		67.4		51.5		15-Mar-08		20:25:59		68.61		45

		3-Feb-08		22:07:10		66.2		51.5		3-Feb-08		22:06:20		66.81		53.5		3-Feb-08		22:07:53		68		54		15-Mar-08		22:25:59		68		45

		4-Feb-08		0:07:10		66.2		51.5		4-Feb-08		0:06:20		67.4		52.5		4-Feb-08		0:07:53		68		54		16-Mar-08		0:25:59		68		44.5

		4-Feb-08		2:07:10		66.2		49		4-Feb-08		2:06:20		66.81		48		4-Feb-08		2:07:53		67.4		50.5		16-Mar-08		2:25:59		68.61		44.5

		4-Feb-08		4:07:10		66.2		45		4-Feb-08		4:06:20		65.6		45		4-Feb-08		4:07:53		66.81		47.5		16-Mar-08		4:25:59		68		46

		4-Feb-08		6:07:10		65.6		43		4-Feb-08		6:06:20		65.6		44		4-Feb-08		6:07:53		66.81		47.5		16-Mar-08		6:25:59		68		39

		4-Feb-08		8:07:10		65.6		40.5		4-Feb-08		8:06:20		65.01		41		4-Feb-08		8:07:53		68		45.5		16-Mar-08		8:25:59		68.61		45.5

		4-Feb-08		10:07:10		65.6		41		4-Feb-08		10:06:20		65.6		42.5		4-Feb-08		10:07:53		68.61		45		16-Mar-08		10:25:59		68.61		45.5

		4-Feb-08		12:07:10		65.6		41.5		4-Feb-08		12:06:20		66.2		41		4-Feb-08		12:07:53		68		46		16-Mar-08		12:25:59		68.61		45.5

		4-Feb-08		14:07:10		65.6		40.5		4-Feb-08		14:06:20		66.81		38		4-Feb-08		14:07:53		68		46		16-Mar-08		14:25:59		68.61		35

		4-Feb-08		16:07:10		66.2		39		4-Feb-08		16:06:20		66.81		38		4-Feb-08		16:07:53		68		45		16-Mar-08		16:25:59		68.61		45

		4-Feb-08		18:07:10		66.2		38.5		4-Feb-08		18:06:20		66.81		36.5		4-Feb-08		18:07:53		68		45		16-Mar-08		18:25:59		68.61		45

		4-Feb-08		20:07:10		66.2		37.5		4-Feb-08		20:06:20		65.6		38		4-Feb-08		20:07:53		68		45.5		16-Mar-08		20:25:59		68.61		45

		4-Feb-08		22:07:10		65.6		37.5		4-Feb-08		22:06:20		65.6		38.5		4-Feb-08		22:07:53		67.4		46		16-Mar-08		22:25:59		68		46

		5-Feb-08		0:07:10		65.6		37		5-Feb-08		0:06:20		65.01		38		5-Feb-08		0:07:53		66.81		46.5		17-Mar-08		0:25:59		68.61		44

		5-Feb-08		2:07:10		65.6		36		5-Feb-08		2:06:20		65.6		35.5		5-Feb-08		2:07:53		66.81		46		17-Mar-08		2:25:59		68.61		44

		5-Feb-08		4:07:10		65.6		34.5		5-Feb-08		4:06:20		65.01		35		5-Feb-08		4:07:53		66.2		46		17-Mar-08		4:25:59		68.61		45

		5-Feb-08		6:07:10		65.6		33.5		5-Feb-08		6:06:20		65.01		33		5-Feb-08		6:07:53		66.81		46		17-Mar-08		6:25:59		68		43.5

		5-Feb-08		8:07:10		65.6		33		5-Feb-08		8:06:20		65.01		33.5		5-Feb-08		8:07:53		70.41		39.5		17-Mar-08		8:25:59		68.61		44

		5-Feb-08		10:07:10		65.6		34.5		5-Feb-08		10:06:20		68.61		32.5		5-Feb-08		10:07:53		71		41.5		17-Mar-08		10:25:59		68.61		43

		5-Feb-08		12:07:10		66.2		34.5		5-Feb-08		12:06:20		71		30.5		5-Feb-08		12:07:53		70.41		42.5		17-Mar-08		12:25:59		68		35.5

		5-Feb-08		14:07:10		66.81		32		5-Feb-08		14:06:20		70.41		29.5		5-Feb-08		14:07:53		71		39.5		17-Mar-08		14:25:59		68.61		27.5

		5-Feb-08		16:07:10		67.4		31		5-Feb-08		16:06:20		70.41		28.5		5-Feb-08		16:07:53		71		34.5		17-Mar-08		16:25:59		68.61		26

		5-Feb-08		18:07:10		68		34		5-Feb-08		18:06:20		69.8		29		5-Feb-08		18:07:53		70.41		37.5		17-Mar-08		18:25:59		68		34

		5-Feb-08		20:07:10		67.4		41.5		5-Feb-08		20:06:20		68		32		5-Feb-08		20:07:53		71		36		17-Mar-08		20:25:59		68		44

		5-Feb-08		22:07:10		66.81		35.5		5-Feb-08		22:06:20		67.4		33		5-Feb-08		22:07:53		69.8		39		17-Mar-08		22:25:59		68.61		44

		6-Feb-08		0:07:10		66.81		34.5		6-Feb-08		0:06:20		67.4		33.5		6-Feb-08		0:07:53		68		36.5		18-Mar-08		0:25:59		68.61		37.5

		6-Feb-08		2:07:10		66.81		34		6-Feb-08		2:06:20		67.4		33		6-Feb-08		2:07:53		66.81		36.5		18-Mar-08		2:25:59		68.61		36.5

		6-Feb-08		4:07:10		66.2		34		6-Feb-08		4:06:20		67.4		32.5		6-Feb-08		4:07:53		66.2		37		18-Mar-08		4:25:59		68		44.5

		6-Feb-08		6:07:10		66.2		33		6-Feb-08		6:06:20		68		31.5		6-Feb-08		6:07:53		67.4		36		18-Mar-08		6:25:59		68		42

		6-Feb-08		8:07:10		66.2		32		6-Feb-08		8:06:20		68		30.5		6-Feb-08		8:07:53		68		35		18-Mar-08		8:25:59		68.61		43.5

		6-Feb-08		10:07:10		66.81		34		6-Feb-08		10:06:20		69.8		31.5		6-Feb-08		10:07:53		70.41		36.5		18-Mar-08		10:25:59		68		39.5

		6-Feb-08		12:07:10		67.4		34.5		6-Feb-08		12:06:20		71		31.5		6-Feb-08		12:07:53		69.8		39.5		18-Mar-08		12:25:59		68.61		43.5

		6-Feb-08		14:07:10		67.4		34.5		6-Feb-08		14:06:20		69.2		34.5		6-Feb-08		14:07:53		71		36		18-Mar-08		14:25:59		68		40

		6-Feb-08		16:07:10		68.61		33		6-Feb-08		16:06:20		71		31		6-Feb-08		16:07:53		71		35		18-Mar-08		16:25:59		68.61		46

		6-Feb-08		18:07:10		68		37		6-Feb-08		18:06:20		69.8		33		6-Feb-08		18:07:53		71		38		18-Mar-08		18:25:59		68.61		44.5

		6-Feb-08		20:07:10		66.81		41		6-Feb-08		20:06:20		68		37.5		6-Feb-08		20:07:53		70.41		39		18-Mar-08		20:25:59		68.61		44.5

		6-Feb-08		22:07:10		66.2		44		6-Feb-08		22:06:20		67.4		38		6-Feb-08		22:07:53		69.8		39		18-Mar-08		22:25:59		68.61		44.5

		7-Feb-08		0:07:10		66.2		45		7-Feb-08		0:06:20		68		36		7-Feb-08		0:07:53		68.61		39.5		19-Mar-08		0:25:59		68		41

		7-Feb-08		2:07:10		65.6		46		7-Feb-08		2:06:20		67.4		35.5		7-Feb-08		2:07:53		67.4		40		19-Mar-08		2:25:59		68		45

		7-Feb-08		4:07:10		65.6		46		7-Feb-08		4:06:20		68		34		7-Feb-08		4:07:53		66.81		40		19-Mar-08		4:25:59		68		45

		7-Feb-08		6:07:10		65.6		46.5		7-Feb-08		6:06:20		68		33		7-Feb-08		6:07:53		66.81		39.5		19-Mar-08		6:25:59		68.61		44.5

		7-Feb-08		8:07:10		65.6		47		7-Feb-08		8:06:20		67.4		33		7-Feb-08		8:07:53		69.8		38		19-Mar-08		8:25:59		68.61		44.5

		7-Feb-08		10:07:10		65.6		46.5		7-Feb-08		10:06:20		72.21		33.5		7-Feb-08		10:07:53		71.6		37.5		19-Mar-08		10:25:59		68.61		46.5

		7-Feb-08		12:07:10		66.81		46		7-Feb-08		12:06:20		74.01		36.5		7-Feb-08		12:07:53		69.8		44.5		19-Mar-08		12:25:59		68.61		47.5

		7-Feb-08		14:07:10		67.4		46		7-Feb-08		14:06:20		71.6		34		7-Feb-08		14:07:53		71		47		19-Mar-08		14:25:59		68.61		45

		7-Feb-08		16:07:10		67.4		46		7-Feb-08		16:06:20		69.8		37		7-Feb-08		16:07:53		70.41		43.5		19-Mar-08		16:25:59		68.61		44.5

		7-Feb-08		18:07:10		67.4		46		7-Feb-08		18:06:20		69.2		34		7-Feb-08		18:07:53		70.41		41		19-Mar-08		18:25:59		68.61		47.5

		7-Feb-08		20:07:10		66.2		46.5		7-Feb-08		20:06:20		69.2		34		7-Feb-08		20:07:53		69.8		39		19-Mar-08		20:25:59		68		48

		7-Feb-08		22:07:10		66.2		47		7-Feb-08		22:06:20		66.81		36		7-Feb-08		22:07:53		69.8		38		19-Mar-08		22:25:59		68.61		45

		8-Feb-08		0:07:10		65.6		48		8-Feb-08		0:06:20		65.6		37.5		8-Feb-08		0:07:53		68.61		38.5		20-Mar-08		0:25:59		68.61		45

		8-Feb-08		2:07:10		65.01		48.5		8-Feb-08		2:06:20		65.6		37.5		8-Feb-08		2:07:53		67.4		39		20-Mar-08		2:25:59		68		40

		8-Feb-08		4:07:10		65.01		49		8-Feb-08		4:06:20		65.6		36.5		8-Feb-08		4:07:53		66.81		39.5		20-Mar-08		4:25:59		68		39

		8-Feb-08		6:07:10		65.01		49		8-Feb-08		6:06:20		65.6		36		8-Feb-08		6:07:53		66.81		39		20-Mar-08		6:25:59		68.61		38.5

		8-Feb-08		8:07:10		65.01		48.5		8-Feb-08		8:06:20		68		33.5		8-Feb-08		8:07:53		69.8		37		20-Mar-08		8:25:59		68		44.5

		8-Feb-08		10:07:10		65.01		49		8-Feb-08		10:06:20		70.41		35		8-Feb-08		10:07:53		71.6		38		20-Mar-08		10:25:59		68.61		45

		8-Feb-08		12:07:10		66.2		48		8-Feb-08		12:06:20		70.41		35.5		8-Feb-08		12:07:53		70.41		39		20-Mar-08		12:25:59		68.61		45.5

		8-Feb-08		14:07:10		66.81		48.5		8-Feb-08		14:06:20		71		38.5		8-Feb-08		14:07:53		71.6		46.5		20-Mar-08		14:25:59		68.61		46

		8-Feb-08		16:07:10		68.61		49.5		8-Feb-08		16:06:20		71		39		8-Feb-08		16:07:53		69.8		49		20-Mar-08		16:25:59		68		47

		8-Feb-08		18:07:10		68.61		44.5		8-Feb-08		18:06:20		69.8		41		8-Feb-08		18:07:53		71		47		20-Mar-08		18:25:59		68.61		45

		8-Feb-08		20:07:10		68.61		42.5		8-Feb-08		20:06:20		69.8		40.5		8-Feb-08		20:07:53		69.8		44.5		20-Mar-08		20:25:59		68.61		45

		8-Feb-08		22:07:10		68		45		8-Feb-08		22:06:20		68		44		8-Feb-08		22:07:53		70.41		42.5		20-Mar-08		22:25:59		68.61		44.5

		9-Feb-08		0:07:10		66.81		44		9-Feb-08		0:06:20		66.2		44		9-Feb-08		0:07:53		69.8		41		21-Mar-08		0:25:59		68.61		45

		9-Feb-08		2:07:10		66.2		44		9-Feb-08		2:06:20		66.2		40.5		9-Feb-08		2:07:53		68.61		40		21-Mar-08		2:25:59		68		45.5

		9-Feb-08		4:07:10		66.2		42		9-Feb-08		4:06:20		66.2		37		9-Feb-08		4:07:53		67.4		38.5		21-Mar-08		4:25:59		68		36.5

		9-Feb-08		6:07:10		65.6		40.5		9-Feb-08		6:06:20		66.2		36		9-Feb-08		6:07:53		67.4		37.5		21-Mar-08		6:25:59		68		45.5

		9-Feb-08		8:07:10		65.6		39.5		9-Feb-08		8:06:20		68		32		9-Feb-08		8:07:53		69.2		36		21-Mar-08		8:25:59		68		36

		9-Feb-08		10:07:10		66.2		40		9-Feb-08		10:06:20		71		35		9-Feb-08		10:07:53		71.6		35.5		21-Mar-08		10:25:59		67.4		46.5

		9-Feb-08		12:07:10		67.4		46.5		9-Feb-08		12:06:20		69.2		33.5		9-Feb-08		12:07:53		71		38.5		21-Mar-08		12:25:59		68.61		42

		9-Feb-08		14:07:10		69.8		47.5		9-Feb-08		14:06:20		68.61		33		9-Feb-08		14:07:53		71		34.5		21-Mar-08		14:25:59		68.61		32.5

		9-Feb-08		16:07:10		72.8		42		9-Feb-08		16:06:20		68.61		28.5		9-Feb-08		16:07:53		71		38.5		21-Mar-08		16:25:59		68		32.5

		9-Feb-08		18:07:10		71		48		9-Feb-08		18:06:20		68		29		9-Feb-08		18:07:53		70.41		35.5		21-Mar-08		18:25:59		68		42.5

		9-Feb-08		20:07:10		67.4		48.5		9-Feb-08		20:06:20		68.61		38.5		9-Feb-08		20:07:53		69.8		39.5		21-Mar-08		20:25:59		68.61		37

		9-Feb-08		22:07:10		65.6		51		9-Feb-08		22:06:20		67.4		38.5		9-Feb-08		22:07:53		69.8		38.5		21-Mar-08		22:25:59		68.61		36.5

		10-Feb-08		0:07:10		65.01		49.5		10-Feb-08		0:06:20		66.2		39		10-Feb-08		0:07:53		69.2		37.5		22-Mar-08		0:25:59		68		34.5

		10-Feb-08		2:07:10		65.01		49		10-Feb-08		2:06:20		65.6		38		10-Feb-08		2:07:53		68		37.5		22-Mar-08		2:25:59		68		42.5

		10-Feb-08		4:07:10		65.01		50		10-Feb-08		4:06:20		65.6		36.5		10-Feb-08		4:07:53		66.81		37.5		22-Mar-08		4:25:59		68		38

		10-Feb-08		6:07:10		65.01		51		10-Feb-08		6:06:20		65.6		35.5		10-Feb-08		6:07:53		66.2		38		22-Mar-08		6:25:59		68		35

		10-Feb-08		8:07:10		65.01		50		10-Feb-08		8:06:20		66.2		34		10-Feb-08		8:07:53		66.81		37		22-Mar-08		8:25:59		68		43.5

		10-Feb-08		10:07:10		65.01		49.5		10-Feb-08		10:06:20		67.4		36		10-Feb-08		10:07:53		68		37		22-Mar-08		10:25:59		68		41

		10-Feb-08		12:07:10		66.2		51		10-Feb-08		12:06:20		67.4		40.5		10-Feb-08		12:07:53		69.8		38.5		22-Mar-08		12:25:59		68.61		43.5

		10-Feb-08		14:07:10		68.61		49.5		10-Feb-08		14:06:20		68		41.5		10-Feb-08		14:07:53		70.41		41		22-Mar-08		14:25:59		68		37

		10-Feb-08		16:07:10		69.8		49		10-Feb-08		16:06:20		68		44		10-Feb-08		16:07:53		70.41		45		22-Mar-08		16:25:59		68.61		45

		10-Feb-08		18:07:10		69.8		49.5		10-Feb-08		18:06:20		68		39.5		10-Feb-08		18:07:53		70.41		42		22-Mar-08		18:25:59		68		44.5

		10-Feb-08		20:07:10		67.4		47.5		10-Feb-08		20:06:20		68.61		39.5		10-Feb-08		20:07:53		69.8		46.5		22-Mar-08		20:25:59		68		38.5

		10-Feb-08		22:07:10		66.2		49.5		10-Feb-08		22:06:20		68		39.5		10-Feb-08		22:07:53		70.41		42		22-Mar-08		22:25:59		68		38.5

		11-Feb-08		0:07:10		65.6		49.5		11-Feb-08		0:06:20		66.2		42		11-Feb-08		0:07:53		69.8		41.5		23-Mar-08		0:25:59		68		39

		11-Feb-08		2:07:10		65.01		50		11-Feb-08		2:06:20		66.2		42		11-Feb-08		2:07:53		68.61		42		23-Mar-08		2:25:59		68.61		36.5

		11-Feb-08		4:07:10		65.01		50		11-Feb-08		4:06:20		65.6		40		11-Feb-08		4:07:53		68		41.5		23-Mar-08		4:25:59		68		35.5

		11-Feb-08		6:07:10		65.01		50.5		11-Feb-08		6:06:20		65.6		38		11-Feb-08		6:07:53		67.4		42.5		23-Mar-08		6:25:59		68.61		43.5

		11-Feb-08		8:07:10		65.01		50		11-Feb-08		8:06:20		66.2		36.5		11-Feb-08		8:07:53		68		41.5		23-Mar-08		8:25:59		68		36

		11-Feb-08		10:07:10		65.01		51		11-Feb-08		10:06:20		66.81		39		11-Feb-08		10:07:53		68		42.5		23-Mar-08		10:25:59		68.61		44

		11-Feb-08		12:07:10		66.2		51.5		11-Feb-08		12:06:20		68		41.5		11-Feb-08		12:07:53		69.8		41.5		23-Mar-08		12:25:59		68		40

		11-Feb-08		14:07:10		68		51		11-Feb-08		14:06:20		67.4		43.5		11-Feb-08		14:07:53		69.8		44		23-Mar-08		14:25:59		68.61		44.5

		11-Feb-08		16:07:10		70.41		51		11-Feb-08		16:06:20		68		42		11-Feb-08		16:07:53		70.41		46.5		23-Mar-08		16:25:59		68.61		33

		11-Feb-08		18:07:10		69.8		50.5		11-Feb-08		18:06:20		68		48.5		11-Feb-08		18:07:53		70.41		46		23-Mar-08		18:25:59		68.61		44.5

		11-Feb-08		20:07:10		66.2		52		11-Feb-08		20:06:20		68.61		45.5		11-Feb-08		20:07:53		70.41		46		23-Mar-08		20:25:59		68.61		43.5

		11-Feb-08		22:07:10		65.6		52		11-Feb-08		22:06:20		67.4		44.5		11-Feb-08		22:07:53		70.41		43.5		23-Mar-08		22:25:59		68		45

		12-Feb-08		0:07:10		65.6		51.5		12-Feb-08		0:06:20		66.2		44.5		12-Feb-08		0:07:53		69.2		41.5		24-Mar-08		0:25:59		68		38.5

		12-Feb-08		2:07:10		65.01		50		12-Feb-08		2:06:20		66.2		42		12-Feb-08		2:07:53		68.61		41		24-Mar-08		2:25:59		68.61		39.5

		12-Feb-08		4:07:10		65.01		52		12-Feb-08		4:06:20		65.6		41.5		12-Feb-08		4:07:53		68		41		24-Mar-08		4:25:59		68.61		36

		12-Feb-08		6:07:10		65.01		50		12-Feb-08		6:06:20		65.6		40.5		12-Feb-08		6:07:53		67.4		41		24-Mar-08		6:25:59		68		35.5

		12-Feb-08		8:07:10		65.01		51		12-Feb-08		8:06:20		66.81		37.5		12-Feb-08		8:07:53		69.8		38		24-Mar-08		8:25:59		68.61		33.5

		12-Feb-08		10:07:10		65.6		49.5		12-Feb-08		10:06:20		71		39		12-Feb-08		10:07:53		71		41.5		24-Mar-08		10:25:59		68		37.5

		12-Feb-08		12:07:10		67.4		49.5		12-Feb-08		12:06:20		72.21		42.5		12-Feb-08		12:07:53		70.41		39.5		24-Mar-08		12:25:59		68.61		37.5

		12-Feb-08		14:07:10		70.41		50		12-Feb-08		14:06:20		72.8		41.5		12-Feb-08		14:07:53		71		44		24-Mar-08		14:25:59		68.61		38.5

		12-Feb-08		16:07:10		72.8		49.5		12-Feb-08		16:06:20		71.6		38.5		12-Feb-08		16:07:53		70.41		47.5		24-Mar-08		16:25:59		68		45

		12-Feb-08		18:07:10		71.6		49.5		12-Feb-08		18:06:20		70.41		48.5		12-Feb-08		18:07:53		70.41		50.5		24-Mar-08		18:25:59		68		42.5

		12-Feb-08		20:07:10		67.4		51		12-Feb-08		20:06:20		69.8		43.5		12-Feb-08		20:07:53		69.8		49		24-Mar-08		20:25:59		68		44.5

		12-Feb-08		22:07:10		66.2		52		12-Feb-08		22:06:20		69.2		43.5		12-Feb-08		22:07:53		70.41		45.5		24-Mar-08		22:25:59		68.61		40

		13-Feb-08		0:07:10		66.2		48.5		13-Feb-08		0:06:20		68.61		42.5		13-Feb-08		0:07:53		69.8		42.5		25-Mar-08		0:25:59		68.61		44

		13-Feb-08		2:07:10		65.6		49		13-Feb-08		2:06:20		68.61		40.5		13-Feb-08		2:07:53		69.2		41.5		25-Mar-08		2:25:59		68		38

		13-Feb-08		4:07:10		65.6		48.5		13-Feb-08		4:06:20		68.61		38		13-Feb-08		4:07:53		68.61		40.5		25-Mar-08		4:25:59		68.61		44.5

		13-Feb-08		6:07:10		65.6		50.5		13-Feb-08		6:06:20		68.61		36.5		13-Feb-08		6:07:53		67.4		41		25-Mar-08		6:25:59		68		37.5

		13-Feb-08		8:07:10		65.6		50		13-Feb-08		8:06:20		69.2		36.5		13-Feb-08		8:07:53		69.8		40		25-Mar-08		8:25:59		68		38

		13-Feb-08		10:07:10		66.2		50.5		13-Feb-08		10:06:20		70.41		37.5		13-Feb-08		10:07:53		71.6		42		25-Mar-08		10:25:59		67.4		42.5

		13-Feb-08		12:07:10		67.4		50.5		13-Feb-08		12:06:20		71		43		13-Feb-08		12:07:53		71		47		25-Mar-08		12:25:59		68		44.5

		13-Feb-08		14:07:10		73.4		46		13-Feb-08		14:06:20		71.6		43.5		13-Feb-08		14:07:53		71		52.5		25-Mar-08		14:25:59		68		46

		13-Feb-08		16:07:10		73.4		48.5		13-Feb-08		16:06:20		71.6		40		13-Feb-08		16:07:53		71		50.5		25-Mar-08		16:25:59		68		45.5

		13-Feb-08		18:07:10		71		48		13-Feb-08		18:06:20		70.41		45		13-Feb-08		18:07:53		70.41		47		25-Mar-08		18:25:59		68		44

		13-Feb-08		20:07:10		66.2		53		13-Feb-08		20:06:20		69.8		44		13-Feb-08		20:07:53		70.41		42.5		25-Mar-08		20:25:59		68		42.5

		13-Feb-08		22:07:10		65.6		53		13-Feb-08		22:06:20		69.2		43.5		13-Feb-08		22:07:53		70.41		44		25-Mar-08		22:25:59		68.61		41.5

		14-Feb-08		0:07:10		65.6		50.5		14-Feb-08		0:06:20		68.61		41		14-Feb-08		0:07:53		70.41		42		26-Mar-08		0:25:59		68.61		40.5

		14-Feb-08		2:07:10		65.01		51		14-Feb-08		2:06:20		68.61		39		14-Feb-08		2:07:53		69.2		40		26-Mar-08		2:25:59		68.61		40

		14-Feb-08		4:07:10		65.01		49		14-Feb-08		4:06:20		68.61		39		14-Feb-08		4:07:53		68.61		40.5		26-Mar-08		4:25:59		68.61		39

		14-Feb-08		6:07:10		65.01		51		14-Feb-08		6:06:20		68.61		38.5		14-Feb-08		6:07:53		68		40.5		26-Mar-08		6:25:59		68.61		40

		14-Feb-08		8:07:10		65.6		49.5		14-Feb-08		8:06:20		68.61		37		14-Feb-08		8:07:53		71		40		26-Mar-08		8:25:59		68		41.5

		14-Feb-08		10:07:10		67.4		46.5		14-Feb-08		10:06:20		69.8		30		14-Feb-08		10:07:53		70.41		39		26-Mar-08		10:25:59		68		42.5

		14-Feb-08		12:07:10		68		46.5		14-Feb-08		12:06:20		70.41		30.5		14-Feb-08		12:07:53		71		33		26-Mar-08		12:25:59		68.61		43.5

		14-Feb-08		14:07:10		66.2		46.5		14-Feb-08		14:06:20		72.21		28.5		14-Feb-08		14:07:53		71		38.5		26-Mar-08		14:25:59		68		43

		14-Feb-08		16:07:10		65.6		47		14-Feb-08		16:06:20		72.8		24		14-Feb-08		16:07:53		71		37.5		26-Mar-08		16:25:59		68		42

		14-Feb-08		18:07:10		65.01		49		14-Feb-08		18:06:20		71.6		16.5		14-Feb-08		18:07:53		71		30.5		26-Mar-08		18:25:59		68		40.5

		14-Feb-08		20:07:10		64.4		47		14-Feb-08		20:06:20		71		17		14-Feb-08		20:07:53		70.41		30		26-Mar-08		20:25:59		68.61		38

		14-Feb-08		22:07:10		64.4		49		14-Feb-08		22:06:20		70.41		27.5		14-Feb-08		22:07:53		71		32		26-Mar-08		22:25:59		68		37.5

		15-Feb-08		0:07:10		64.4		49		15-Feb-08		0:06:20		70.41		26		15-Feb-08		0:07:53		70.41		32		27-Mar-08		0:25:59		68		38

		15-Feb-08		2:07:10		64.4		46.5		15-Feb-08		2:06:20		70.41		23.5		15-Feb-08		2:07:53		69.2		31		27-Mar-08		2:25:59		67.4		37.5

		15-Feb-08		4:07:10		64.4		50.5		15-Feb-08		4:06:20		70.41		21		15-Feb-08		4:07:53		68.61		31		27-Mar-08		4:25:59		67.4		36.5

		15-Feb-08		6:07:10		64.4		49		15-Feb-08		6:06:20		70.41		19.5		15-Feb-08		6:07:53		68		30.5		27-Mar-08		6:25:59		67.4		35

		15-Feb-08		8:07:10		64.4		50.5		15-Feb-08		8:06:20		70.41		19.5		15-Feb-08		8:07:53		70.41		31		27-Mar-08		8:25:59		68		35.5

		15-Feb-08		10:07:10		65.01		33.5		15-Feb-08		10:06:20		72.21		19.5		15-Feb-08		10:07:53		71		30.5		27-Mar-08		10:25:59		67.4		37

		15-Feb-08		12:07:10		65.6		48		15-Feb-08		12:06:20		72.8		19		15-Feb-08		12:07:53		71		29.5		27-Mar-08		12:25:59		68		36.5

		15-Feb-08		14:07:10		65.6		49		15-Feb-08		14:06:20		72.8		19.5		15-Feb-08		14:07:53		71		34.5		27-Mar-08		14:25:59		68		39

		15-Feb-08		16:07:10		65.6		48.5		15-Feb-08		16:06:20		73.4		19		15-Feb-08		16:07:53		71		34		27-Mar-08		16:25:59		68		39.5

		15-Feb-08		18:07:10		65.6		49.5		15-Feb-08		18:06:20		71.6		20.5		15-Feb-08		18:07:53		70.41		32		27-Mar-08		18:25:59		68.61		37.5

		15-Feb-08		20:07:10		65.01		43.5		15-Feb-08		20:06:20		71		24.5		15-Feb-08		20:07:53		70.41		31.5		27-Mar-08		20:25:59		68.61		37

		15-Feb-08		22:07:10		65.01		49		15-Feb-08		22:06:20		70.41		26.5		15-Feb-08		22:07:53		69.8		31.5		27-Mar-08		22:25:59		68.61		34.5

		16-Feb-08		0:07:10		65.6		50		16-Feb-08		0:06:20		70.41		26.5		16-Feb-08		0:07:53		69.2		32		28-Mar-08		0:25:59		68		34.5

		16-Feb-08		2:07:10		65.01		50		16-Feb-08		2:06:20		70.41		26.5		16-Feb-08		2:07:53		68.61		33		28-Mar-08		2:25:59		67.4		33

		16-Feb-08		4:07:10		65.01		51		16-Feb-08		4:06:20		70.41		27		16-Feb-08		4:07:53		68		33.5		28-Mar-08		4:25:59		66.81		31.5

		16-Feb-08		6:07:10		65.01		50		16-Feb-08		6:06:20		70.41		26.5		16-Feb-08		6:07:53		66.81		34		28-Mar-08		6:25:59		67.4		31.5

		16-Feb-08		8:07:10		65.01		51		16-Feb-08		8:06:20		70.41		27		16-Feb-08		8:07:53		69.2		33		28-Mar-08		8:25:59		68		30.5

		16-Feb-08		10:07:10		65.6		51		16-Feb-08		10:06:20		71.6		27.5		16-Feb-08		10:07:53		71.6		33.5		28-Mar-08		10:25:59		68		29

		16-Feb-08		12:07:10		65.01		50		16-Feb-08		12:06:20		73.4		28		16-Feb-08		12:07:53		70.41		39		28-Mar-08		12:25:59		68		26

		16-Feb-08		14:07:10		65.6		50		16-Feb-08		14:06:20		73.4		27		16-Feb-08		14:07:53		71		33		28-Mar-08		14:25:59		68.61		25.5

		16-Feb-08		16:07:10		65.6		51.5		16-Feb-08		16:06:20		73.4		37.5		16-Feb-08		16:07:53		71.6		36.5		28-Mar-08		16:25:59		68		23.5

		16-Feb-08		18:07:10		65.01		51		16-Feb-08		18:06:20		67.4		41		16-Feb-08		18:07:53		70.41		40		28-Mar-08		18:25:59		68.61		23.5

		16-Feb-08		20:07:10		65.01		50.5		16-Feb-08		20:06:20		66.2		43		16-Feb-08		20:07:53		71		39.5		28-Mar-08		20:25:59		68		26.5

		16-Feb-08		22:07:10		65.01		52		16-Feb-08		22:06:20		66.81		41		16-Feb-08		22:07:53		70.41		39		28-Mar-08		22:25:59		68		32.5

		17-Feb-08		0:07:10		65.01		52		17-Feb-08		0:06:20		66.2		40		17-Feb-08		0:07:53		69.8		38		29-Mar-08		0:25:59		67.4		33.5

		17-Feb-08		2:07:10		65.01		52.5		17-Feb-08		2:06:20		66.2		40.5		17-Feb-08		2:07:53		69.2		39.5		29-Mar-08		2:25:59		67.4		34

		17-Feb-08		4:07:10		65.01		53		17-Feb-08		4:06:20		66.2		41.5		17-Feb-08		4:07:53		68.61		39.5		29-Mar-08		4:25:59		66.81		34

		17-Feb-08		6:07:10		65.01		53		17-Feb-08		6:06:20		66.2		41		17-Feb-08		6:07:53		68.61		40		29-Mar-08		6:25:59		67.4		33.5

		17-Feb-08		8:07:10		65.01		52		17-Feb-08		8:06:20		65.6		40		17-Feb-08		8:07:53		70.41		39		29-Mar-08		8:25:59		68		34

		17-Feb-08		10:07:10		65.01		52		17-Feb-08		10:06:20		65.6		40.5		17-Feb-08		10:07:53		71		37.5		29-Mar-08		10:25:59		67.4		30.5

		17-Feb-08		12:07:10		65.01		52.5		17-Feb-08		12:06:20		66.81		40.5		17-Feb-08		12:07:53		71		38.5		29-Mar-08		12:25:59		68		37

		17-Feb-08		14:07:10		65.01		52		17-Feb-08		14:06:20		67.4		40.5		17-Feb-08		14:07:53		70.41		41.5		29-Mar-08		14:25:59		68		39.5

		17-Feb-08		16:07:10		65.01		53		17-Feb-08		16:06:20		68		38		17-Feb-08		16:07:53		71		43.5		29-Mar-08		16:25:59		68		42

		17-Feb-08		18:07:10		65.01		52.5		17-Feb-08		18:06:20		66.81		42.5		17-Feb-08		18:07:53		70.41		41.5		29-Mar-08		18:25:59		68		42.5

		17-Feb-08		20:07:10		65.01		52.5		17-Feb-08		20:06:20		66.81		42.5		17-Feb-08		20:07:53		69.8		40.5		29-Mar-08		20:25:59		68		43

		17-Feb-08		22:07:10		65.01		53		17-Feb-08		22:06:20		66.81		40.5		17-Feb-08		22:07:53		69.8		39		29-Mar-08		22:25:59		68		43.5

		18-Feb-08		0:07:10		65.01		52		18-Feb-08		0:06:20		66.2		39.5		18-Feb-08		0:07:53		69.2		38.5		30-Mar-08		0:25:59		68		43.5

		18-Feb-08		2:07:10		65.01		52.5		18-Feb-08		2:06:20		66.2		42.5		18-Feb-08		2:07:53		68.61		40		30-Mar-08		2:25:59		68.61		42.5

		18-Feb-08		4:07:10		65.01		52		18-Feb-08		4:06:20		65.6		41.5		18-Feb-08		4:07:53		68		40.5		30-Mar-08		4:25:59		68.61		41.5

		18-Feb-08		6:07:10		65.01		51.5		18-Feb-08		6:06:20		65.6		41.5		18-Feb-08		6:07:53		68		40.5		30-Mar-08		6:25:59		68.61		40

		18-Feb-08		8:07:10		65.01		52		18-Feb-08		8:06:20		65.6		40		18-Feb-08		8:07:53		67.4		40.5		30-Mar-08		8:25:59		68.61		39

		18-Feb-08		10:07:10		65.01		51.5		18-Feb-08		10:06:20		65.6		41		18-Feb-08		10:07:53		67.4		40.5		30-Mar-08		10:25:59		68.61		39

		18-Feb-08		12:07:10		65.01		52		18-Feb-08		12:06:20		66.2		41.5		18-Feb-08		12:07:53		67.4		41		30-Mar-08		12:25:59		68.61		40

		18-Feb-08		14:07:10		65.01		52.5		18-Feb-08		14:06:20		67.4		42		18-Feb-08		14:07:53		68.61		41.5		30-Mar-08		14:25:59		68.61		40.5

		18-Feb-08		16:07:10		65.01		53.5		18-Feb-08		16:06:20		66.81		45.5		18-Feb-08		16:07:53		69.8		42		30-Mar-08		16:25:59		68.61		40

		18-Feb-08		18:07:10		65.01		54		18-Feb-08		18:06:20		66.2		45		18-Feb-08		18:07:53		69.8		42.5		30-Mar-08		18:25:59		68.61		38.5

		18-Feb-08		20:07:10		65.01		52.5		18-Feb-08		20:06:20		66.81		41.5		18-Feb-08		20:07:53		69.2		41		30-Mar-08		20:25:59		68.61		37

		18-Feb-08		22:07:10		65.01		53		18-Feb-08		22:06:20		66.2		42.5		18-Feb-08		22:07:53		68.61		40.5		30-Mar-08		22:25:59		68.61		32.5

		19-Feb-08		0:07:10		65.01		51		19-Feb-08		0:06:20		66.2		41.5		19-Feb-08		0:07:53		68.61		41		31-Mar-08		0:25:59		68.61		32

		19-Feb-08		2:07:10		65.01		52.5		19-Feb-08		2:06:20		66.2		42.5		19-Feb-08		2:07:53		68		41.5		31-Mar-08		2:25:59		67.4		33

		19-Feb-08		4:07:10		65.01		51		19-Feb-08		4:06:20		66.2		43		19-Feb-08		4:07:53		68		41.5		31-Mar-08		4:25:59		66.81		33.5

		19-Feb-08		6:07:10		65.01		53		19-Feb-08		6:06:20		66.2		43		19-Feb-08		6:07:53		68		42		31-Mar-08		6:25:59		67.4		32.5

		19-Feb-08		8:07:10		65.01		52		19-Feb-08		8:06:20		66.81		42.5		19-Feb-08		8:07:53		68		42.5		31-Mar-08		8:25:59		68		32

		19-Feb-08		10:07:10		65.01		52.5		19-Feb-08		10:06:20		66.2		43.5		19-Feb-08		10:07:53		68.61		42.5		31-Mar-08		10:25:59		68.61		28.5

		19-Feb-08		12:07:10		65.01		52.5		19-Feb-08		12:06:20		66.2		43.5		19-Feb-08		12:07:53		69.2		42.5		31-Mar-08		12:25:59		67.4		25.5

		19-Feb-08		14:07:10		65.01		52		19-Feb-08		14:06:20		66.81		43		19-Feb-08		14:07:53		69.8		42		31-Mar-08		14:25:59		68		24

		19-Feb-08		16:07:10		65.01		52.5		19-Feb-08		16:06:20		66.2		44.5		19-Feb-08		16:07:53		69.8		42.5		31-Mar-08		16:25:59		68.61		24.5

		19-Feb-08		18:07:10		65.01		51.5		19-Feb-08		18:06:20		66.81		43		19-Feb-08		18:07:53		69.8		42		31-Mar-08		18:25:59		68		27.5

		19-Feb-08		20:07:10		65.01		52		19-Feb-08		20:06:20		66.2		43		19-Feb-08		20:07:53		69.8		41.5		31-Mar-08		20:25:59		68		27

		19-Feb-08		22:07:10		65.01		52		19-Feb-08		22:06:20		66.2		42		19-Feb-08		22:07:53		69.8		40.5		31-Mar-08		22:25:59		68		27.5

		20-Feb-08		0:07:10		65.01		52.5		20-Feb-08		0:06:20		66.81		39.5		20-Feb-08		0:07:53		69.8		40		1-Apr-08		0:25:59		67.4		29

		20-Feb-08		2:07:10		65.01		52		20-Feb-08		2:06:20		66.81		40.5		20-Feb-08		2:07:53		69.2		40		1-Apr-08		2:25:59		67.4		29

		20-Feb-08		4:07:10		65.01		52		20-Feb-08		4:06:20		66.81		40.5		20-Feb-08		4:07:53		69.2		40		1-Apr-08		4:25:59		68		28

		20-Feb-08		6:07:10		65.01		52.5		20-Feb-08		6:06:20		66.81		41		20-Feb-08		6:07:53		69.2		40.5		1-Apr-08		6:25:59		68.61		28.5

		20-Feb-08		8:07:10		65.6		51.5		20-Feb-08		8:06:20		67.4		41		20-Feb-08		8:07:53		71		41		1-Apr-08		8:25:59		68		30

		20-Feb-08		10:07:10		65.6		51.5		20-Feb-08		10:06:20		66.81		42		20-Feb-08		10:07:53		71		39.5		1-Apr-08		10:25:59		67.4		31

		20-Feb-08		12:07:10		66.2		51		20-Feb-08		12:06:20		66.81		48.5		20-Feb-08		12:07:53		71		42.5		1-Apr-08		12:25:59		68		25

		20-Feb-08		14:07:10		65.6		52.5		20-Feb-08		14:06:20		66.81		51.5		20-Feb-08		14:07:53		71		39		1-Apr-08		14:25:59		68		29.5

		20-Feb-08		16:07:10		66.81		52.5		20-Feb-08		16:06:20		67.4		48.5		20-Feb-08		16:07:53		70.41		43.5		1-Apr-08		16:25:59		68		31

		20-Feb-08		18:07:10		66.2		52		20-Feb-08		18:06:20		67.4		51.5		20-Feb-08		18:07:53		70.41		48		1-Apr-08		18:25:59		68		29.5

		20-Feb-08		20:07:10		66.2		51		20-Feb-08		20:06:20		66.2		55		20-Feb-08		20:07:53		70.41		47		1-Apr-08		20:25:59		67.4		30.5

		20-Feb-08		22:07:10		66.2		52.5		20-Feb-08		22:06:20		67.4		51.5		20-Feb-08		22:07:53		71		45.5		1-Apr-08		22:25:59		68		29.5

		21-Feb-08		0:07:10		66.2		52.5		21-Feb-08		0:06:20		67.4		50.5		21-Feb-08		0:07:53		70.41		45.5		2-Apr-08		0:25:59		68		32.5

		21-Feb-08		2:07:10		65.6		52.5		21-Feb-08		2:06:20		66.81		47		21-Feb-08		2:07:53		69.8		44		2-Apr-08		2:25:59		68		33.5

		21-Feb-08		4:07:10		65.6		52		21-Feb-08		4:06:20		66.81		47.5		21-Feb-08		4:07:53		69.2		44		2-Apr-08		4:25:59		68		33

		21-Feb-08		6:07:10		65.6		52.5		21-Feb-08		6:06:20		66.81		47		21-Feb-08		6:07:53		68.61		44.5		2-Apr-08		6:25:59		68		31

		21-Feb-08		8:07:10		66.2		52		21-Feb-08		8:06:20		67.4		47		21-Feb-08		8:07:53		71		41.5		2-Apr-08		8:25:59		68		33.5

		21-Feb-08		10:07:10		66.2		52		21-Feb-08		10:06:20		67.4		48.5		21-Feb-08		10:07:53		72.21		44.5		2-Apr-08		10:25:59		68		33

		21-Feb-08		12:07:10		65.6		51.5		21-Feb-08		12:06:20		66.81		49.5		21-Feb-08		12:07:53		70.41		48		2-Apr-08		12:25:59		68.61		33

		21-Feb-08		14:07:10		65.6		51		21-Feb-08		14:06:20		68		41		21-Feb-08		14:07:53		71.6		48.5		2-Apr-08		14:25:59		68		36.5

		21-Feb-08		16:07:10		66.81		50.5		21-Feb-08		16:06:20		68		40.5		21-Feb-08		16:07:53		71		47.5		2-Apr-08		16:25:59		68		34

		21-Feb-08		18:07:10		66.2		52		21-Feb-08		18:06:20		67.4		42.5		21-Feb-08		18:07:53		70.41		45.5		2-Apr-08		18:25:59		68		34

		21-Feb-08		20:07:10		66.2		52.5		21-Feb-08		20:06:20		66.81		44.5		21-Feb-08		20:07:53		70.41		43.5		2-Apr-08		20:25:59		68		37

		21-Feb-08		22:07:10		66.2		51.5		21-Feb-08		22:06:20		67.4		45		21-Feb-08		22:07:53		71		42.5		2-Apr-08		22:25:59		68.61		36.5

		22-Feb-08		0:07:10		66.2		49.5		22-Feb-08		0:06:20		66.81		43		22-Feb-08		0:07:53		70.41		41.5		3-Apr-08		0:25:59		68.61		36.5

		22-Feb-08		2:07:10		65.6		51.5		22-Feb-08		2:06:20		66.81		43.5		22-Feb-08		2:07:53		69.8		41		3-Apr-08		2:25:59		68		36

		22-Feb-08		4:07:10		65.6		52		22-Feb-08		4:06:20		66.81		43.5		22-Feb-08		4:07:53		69.2		41.5		3-Apr-08		4:25:59		67.4		35

		22-Feb-08		6:07:10		66.2		51.5		22-Feb-08		6:06:20		66.81		44		22-Feb-08		6:07:53		69.2		42		3-Apr-08		6:25:59		69.2		34

		22-Feb-08		8:07:10		66.2		51		22-Feb-08		8:06:20		66.2		46		22-Feb-08		8:07:53		71		44		3-Apr-08		8:25:59		67.4		36.5

		22-Feb-08		10:07:10		66.81		48		22-Feb-08		10:06:20		66.2		48		22-Feb-08		10:07:53		71.6		43		3-Apr-08		10:25:59		68		36.5

		22-Feb-08		12:07:10		66.81		48.5		22-Feb-08		12:06:20		67.4		43.5		22-Feb-08		12:07:53		71		39		3-Apr-08		12:25:59		68		37.5

		22-Feb-08		14:07:10		66.81		49		22-Feb-08		14:06:20		68		44.5		22-Feb-08		14:07:53		71		44		3-Apr-08		14:25:59		68		39

		22-Feb-08		16:07:10		66.2		50		22-Feb-08		16:06:20		68		48		22-Feb-08		16:07:53		71		40		3-Apr-08		16:25:59		68		37.5

		22-Feb-08		18:07:10		66.2		51.5		22-Feb-08		18:06:20		66.81		48		22-Feb-08		18:07:53		71		46.5		3-Apr-08		18:25:59		68.61		35

		22-Feb-08		20:07:10		66.2		49		22-Feb-08		20:06:20		67.4		49.5		22-Feb-08		20:07:53		70.41		42		3-Apr-08		20:25:59		68		35.5

		22-Feb-08		22:07:10		66.2		51		22-Feb-08		22:06:20		66.81		51.5		22-Feb-08		22:07:53		70.41		45.5		3-Apr-08		22:25:59		68.61		34

		23-Feb-08		0:07:10		65.6		50.5		23-Feb-08		0:06:20		66.81		49.5		23-Feb-08		0:07:53		70.41		44.5		4-Apr-08		0:25:59		68		34

		23-Feb-08		2:07:10		65.6		49		23-Feb-08		2:06:20		67.4		48		23-Feb-08		2:07:53		69.8		43.5		4-Apr-08		2:25:59		68		33.5

		23-Feb-08		4:07:10		65.6		49		23-Feb-08		4:06:20		67.4		46		23-Feb-08		4:07:53		69.8		43		4-Apr-08		4:25:59		68		35

		23-Feb-08		6:07:10		65.6		46.5		23-Feb-08		6:06:20		66.81		47		23-Feb-08		6:07:53		69.2		43		4-Apr-08		6:25:59		68.61		36.5

		23-Feb-08		8:07:10		66.2		48.5		23-Feb-08		8:06:20		66.2		48		23-Feb-08		8:07:53		71		40.5		4-Apr-08		8:25:59		68		38

		23-Feb-08		10:07:10		66.2		49.5		23-Feb-08		10:06:20		67.4		48		23-Feb-08		10:07:53		71.6		48.5		4-Apr-08		10:25:59		67.4		39

		23-Feb-08		12:07:10		66.81		48.5		23-Feb-08		12:06:20		67.4		47.5		23-Feb-08		12:07:53		71		49.5		4-Apr-08		12:25:59		73.4		36.5

		23-Feb-08		14:07:10		66.81		48.5		23-Feb-08		14:06:20		67.4		47		23-Feb-08		14:07:53		71		45.5		4-Apr-08		14:25:59		74.01		36

		23-Feb-08		16:07:10		66.81		44		23-Feb-08		16:06:20		68		41.5		23-Feb-08		16:07:53		71.6		45.5		4-Apr-08		16:25:59		74.6		37.5

		23-Feb-08		18:07:10		66.2		48		23-Feb-08		18:06:20		67.4		39.5		23-Feb-08		18:07:53		71		42.5		4-Apr-08		18:25:59		74.01		36.5

		23-Feb-08		20:07:10		66.2		48		23-Feb-08		20:06:20		66.81		38		23-Feb-08		20:07:53		70.41		40		4-Apr-08		20:25:59		73.4		36.5

		23-Feb-08		22:07:10		66.2		48.5		23-Feb-08		22:06:20		66.2		38.5		23-Feb-08		22:07:53		69.8		40.5		4-Apr-08		22:25:59		71.6		37

		24-Feb-08		0:07:10		65.6		49.5		24-Feb-08		0:06:20		65.01		38		24-Feb-08		0:07:53		69.2		38		5-Apr-08		0:25:59		70.41		36.5

		24-Feb-08		2:07:10		65.6		41.5		24-Feb-08		2:06:20		64.4		38		24-Feb-08		2:07:53		68		38		5-Apr-08		2:25:59		69.2		36.5

		24-Feb-08		4:07:10		65.6		48		24-Feb-08		4:06:20		63.8		37		24-Feb-08		4:07:53		66.81		37.5		5-Apr-08		4:25:59		68.61		38

		24-Feb-08		6:07:10		65.6		48		24-Feb-08		6:06:20		63.8		38		24-Feb-08		6:07:53		66.2		38.5		5-Apr-08		6:25:59		69.2		37.5

		24-Feb-08		8:07:10		66.2		48		24-Feb-08		8:06:20		64.4		38.5		24-Feb-08		8:07:53		68		38		5-Apr-08		8:25:59		70.41		38.5

		24-Feb-08		10:07:10		66.81		43		24-Feb-08		10:06:20		65.01		42		24-Feb-08		10:07:53		67.4		39.5		5-Apr-08		10:25:59		71.6		38.5

		24-Feb-08		12:07:10		66.81		47		24-Feb-08		12:06:20		66.2		42		24-Feb-08		12:07:53		68		40		5-Apr-08		12:25:59		72.8		38.5

		24-Feb-08		14:07:10		66.2		48		24-Feb-08		14:06:20		66.2		42.5		24-Feb-08		14:07:53		68		41		5-Apr-08		14:25:59		73.4		38.5

		24-Feb-08		16:07:10		66.2		48		24-Feb-08		16:06:20		65.6		44.5		24-Feb-08		16:07:53		68		42		5-Apr-08		16:25:59		74.01		38.5

		24-Feb-08		18:07:10		66.2		49		24-Feb-08		18:06:20		65.01		41.5		24-Feb-08		18:07:53		67.4		41.5		5-Apr-08		18:25:59		73.4		37.5

		24-Feb-08		20:07:10		65.6		45		24-Feb-08		20:06:20		65.6		44		24-Feb-08		20:07:53		66.81		42.5		5-Apr-08		20:25:59		72.8		37

		24-Feb-08		22:07:10		66.2		49		24-Feb-08		22:06:20		65.6		48		24-Feb-08		22:07:53		66.81		44.5		5-Apr-08		22:25:59		71.6		36.5

		25-Feb-08		0:07:10		66.2		49		25-Feb-08		0:06:20		66.2		47.5		25-Feb-08		0:07:53		67.4		45		6-Apr-08		0:25:59		69.8		36

		25-Feb-08		2:07:10		66.2		49		25-Feb-08		2:06:20		66.81		48		25-Feb-08		2:07:53		67.4		45.5		6-Apr-08		2:25:59		68		36.5

		25-Feb-08		4:07:10		66.2		49.5		25-Feb-08		4:06:20		66.81		49		25-Feb-08		4:07:53		67.4		46		6-Apr-08		4:25:59		67.4		37

		25-Feb-08		6:07:10		66.2		48		25-Feb-08		6:06:20		66.81		50		25-Feb-08		6:07:53		67.4		47		6-Apr-08		6:25:59		66.81		36.5

		25-Feb-08		8:07:10		66.2		49.5		25-Feb-08		8:06:20		66.81		51		25-Feb-08		8:07:53		67.4		48		6-Apr-08		8:25:59		66.81		36.5

		25-Feb-08		10:07:10		66.2		51.5		25-Feb-08		10:06:20		67.4		51.5		25-Feb-08		10:07:53		67.4		49.5		6-Apr-08		10:25:59		68.61		38

		25-Feb-08		12:07:10		66.2		52		25-Feb-08		12:06:20		66.81		52.5		25-Feb-08		12:07:53		68		49		6-Apr-08		12:25:59		70.41		38.5

		25-Feb-08		14:07:10		66.2		53		25-Feb-08		14:06:20		67.4		52		25-Feb-08		14:07:53		68		49.5		6-Apr-08		14:25:59		71.6		37.5

		25-Feb-08		16:07:10		66.2		49.5		25-Feb-08		16:06:20		66.2		52.5		25-Feb-08		16:07:53		68		49		6-Apr-08		16:25:59		72.21		37

		25-Feb-08		18:07:10		66.2		50.5		25-Feb-08		18:06:20		67.4		49.5		25-Feb-08		18:07:53		68		48		6-Apr-08		18:25:59		72.8		36.5

		25-Feb-08		20:07:10		66.2		50		25-Feb-08		20:06:20		67.4		47.5		25-Feb-08		20:07:53		68		47.5		6-Apr-08		20:25:59		72.21		36.5

		25-Feb-08		22:07:10		66.2		50		25-Feb-08		22:06:20		66.81		48		25-Feb-08		22:07:53		68		47		6-Apr-08		22:25:59		71		37

		26-Feb-08		0:07:10		66.2		49.5		26-Feb-08		0:06:20		66.81		49.5		26-Feb-08		0:07:53		68		47		7-Apr-08		0:25:59		69.2		37

		26-Feb-08		2:07:10		65.6		50.5		26-Feb-08		2:06:20		66.2		49		26-Feb-08		2:07:53		67.4		47		7-Apr-08		2:25:59		68.61		37.5

		26-Feb-08		4:07:10		65.6		49		26-Feb-08		4:06:20		65.6		47		26-Feb-08		4:07:53		67.4		45.5		7-Apr-08		4:25:59		67.4		37.5

		26-Feb-08		6:07:10		65.6		49		26-Feb-08		6:06:20		65.6		48		26-Feb-08		6:07:53		66.81		45.5		7-Apr-08		6:25:59		66.81		38

		26-Feb-08		8:07:10		66.2		49		26-Feb-08		8:06:20		66.2		46.5		26-Feb-08		8:07:53		69.8		44		7-Apr-08		8:25:59		66.81		38.5

		26-Feb-08		10:07:10		66.81		49		26-Feb-08		10:06:20		66.81		48.5		26-Feb-08		10:07:53		71.6		42		7-Apr-08		10:25:59		68		39.5

		26-Feb-08		12:07:10		66.81		49.5		26-Feb-08		12:06:20		67.4		46.5		26-Feb-08		12:07:53		70.41		49.5		7-Apr-08		12:25:59		68.61		40

		26-Feb-08		14:07:10		66.81		48		26-Feb-08		14:06:20		67.4		45.5		26-Feb-08		14:07:53		71.6		51		7-Apr-08		14:25:59		69.8		39

		26-Feb-08		16:07:10		66.81		47.5		26-Feb-08		16:06:20		67.4		44.5		26-Feb-08		16:07:53		71		50.5		7-Apr-08		16:25:59		70.41		37.5

		26-Feb-08		18:07:10		66.2		49		26-Feb-08		18:06:20		67.4		47		26-Feb-08		18:07:53		71		50.5		7-Apr-08		18:25:59		71		36

		26-Feb-08		20:07:10		66.2		48.5		26-Feb-08		20:06:20		66.2		48.5		26-Feb-08		20:07:53		70.41		46		7-Apr-08		20:25:59		69.8		35

		26-Feb-08		22:07:10		65.6		50		26-Feb-08		22:06:20		66.81		46		26-Feb-08		22:07:53		70.41		44.5		7-Apr-08		22:25:59		68.61		35

		27-Feb-08		0:07:10		65.6		47.5		27-Feb-08		0:06:20		66.2		45		27-Feb-08		0:07:53		69.8		41.5		8-Apr-08		0:25:59		68		35.5

		27-Feb-08		2:07:10		65.6		49		27-Feb-08		2:06:20		65.01		43.5		27-Feb-08		2:07:53		68.61		41		8-Apr-08		2:25:59		66.81		36.5

		27-Feb-08		4:07:10		66.2		49		27-Feb-08		4:06:20		65.01		43.5		27-Feb-08		4:07:53		68		41		8-Apr-08		4:25:59		66.2		37

		27-Feb-08		6:07:10		66.2		48		27-Feb-08		6:06:20		65.01		44		27-Feb-08		6:07:53		67.4		41.5		8-Apr-08		6:25:59		67.4		36

		27-Feb-08		8:07:10		66.2		47.5		27-Feb-08		8:06:20		65.6		41		27-Feb-08		8:07:53		69.8		40		8-Apr-08		8:25:59		68.61		35.5

		27-Feb-08		10:07:10		66.2		47		27-Feb-08		10:06:20		66.81		44.5		27-Feb-08		10:07:53		71.6		38		8-Apr-08		10:25:59		71.6		36

		27-Feb-08		12:07:10		66.81		48.5		27-Feb-08		12:06:20		68		44.5		27-Feb-08		12:07:53		71		40.5		8-Apr-08		12:25:59		72.8		35

		27-Feb-08		14:07:10		66.81		46.5		27-Feb-08		14:06:20		67.4		44		27-Feb-08		14:07:53		70.41		39.5		8-Apr-08		14:25:59		74.01		33.5

		27-Feb-08		16:07:10		66.81		47		27-Feb-08		16:06:20		68.61		42		27-Feb-08		16:07:53		70.41		49.5		8-Apr-08		16:25:59		74.01		35.5

		27-Feb-08		18:07:10		66.2		50		27-Feb-08		18:06:20		68		48.5		27-Feb-08		18:07:53		70.41		42.5		8-Apr-08		18:25:59		73.4		34.5

		27-Feb-08		20:07:10		66.2		49.5		27-Feb-08		20:06:20		66.81		51.5		27-Feb-08		20:07:53		70.41		42.5		8-Apr-08		20:25:59		72.8		34.5

		27-Feb-08		22:07:10		66.2		49.5		27-Feb-08		22:06:20		66.81		50		27-Feb-08		22:07:53		71		46		8-Apr-08		22:25:59		72.21		34

		28-Feb-08		0:07:10		66.2		48.5		28-Feb-08		0:06:20		66.2		49.5		28-Feb-08		0:07:53		71		43		9-Apr-08		0:25:59		70.41		35

		28-Feb-08		2:07:10		66.2		49		28-Feb-08		2:06:20		66.81		47.5		28-Feb-08		2:07:53		70.41		42.5		9-Apr-08		2:25:59		69.2		35

		28-Feb-08		4:07:10		65.6		49		28-Feb-08		4:06:20		66.2		46.5		28-Feb-08		4:07:53		69.8		41.5		9-Apr-08		4:25:59		68.61		35.5

		28-Feb-08		6:07:10		65.6		50		28-Feb-08		6:06:20		65.6		45		28-Feb-08		6:07:53		69.2		41		9-Apr-08		6:25:59		69.2		36

		28-Feb-08		8:07:10		66.2		48		28-Feb-08		8:06:20		65.6		42.5		28-Feb-08		8:07:53		70.41		41.5		9-Apr-08		8:25:59		70.41		36.5

		28-Feb-08		10:07:10		66.2		47.5		28-Feb-08		10:06:20		67.4		46		28-Feb-08		10:07:53		71		39		9-Apr-08		10:25:59		72.8		35.5

		28-Feb-08		12:07:10		66.81		49		28-Feb-08		12:06:20		68		48		28-Feb-08		12:07:53		71		41		9-Apr-08		12:25:59		74.01		35

		28-Feb-08		14:07:10		66.81		49.5		28-Feb-08		14:06:20		68.61		47		28-Feb-08		14:07:53		71		40		9-Apr-08		14:25:59		74.01		34

		28-Feb-08		16:07:10		66.81		51.5		28-Feb-08		16:06:20		67.4		56		28-Feb-08		16:07:53		71		51.5		9-Apr-08		16:25:59		74.01		34.5

		28-Feb-08		18:07:10		66.2		51.5		28-Feb-08		18:06:20		68		49.5		28-Feb-08		18:07:53		71		52		9-Apr-08		18:25:59		74.01		34.5

		28-Feb-08		20:07:10		66.2		48.5		28-Feb-08		20:06:20		66.81		53		28-Feb-08		20:07:53		71.6		47		9-Apr-08		20:25:59		72.8		33.5

		28-Feb-08		22:07:10		66.2		50		28-Feb-08		22:06:20		67.4		49.5		28-Feb-08		22:07:53		72.21		44		9-Apr-08		22:25:59		71		33.5

		29-Feb-08		0:07:10		65.6		49		29-Feb-08		0:06:20		66.81		48		29-Feb-08		0:07:53		71.6		42.5		10-Apr-08		0:25:59		69.2		33.5

		29-Feb-08		2:07:10		65.6		49		29-Feb-08		2:06:20		66.2		46		29-Feb-08		2:07:53		70.41		41.5		10-Apr-08		2:25:59		68		34.5

		29-Feb-08		4:07:10		66.2		49		29-Feb-08		4:06:20		65.01		44.5		29-Feb-08		4:07:53		69.2		40.5		10-Apr-08		4:25:59		66.81		35

		29-Feb-08		6:07:10		65.6		48.5		29-Feb-08		6:06:20		65.01		42		29-Feb-08		6:07:53		68.61		39.5		10-Apr-08		6:25:59		68		34.5

		29-Feb-08		8:07:10		66.2		48		29-Feb-08		8:06:20		65.01		40		29-Feb-08		8:07:53		71		38		10-Apr-08		8:25:59		69.2		35

		29-Feb-08		10:07:10		66.2		48		29-Feb-08		10:06:20		66.81		45.5		29-Feb-08		10:07:53		72.21		42.5		10-Apr-08		10:25:59		72.21		36

		29-Feb-08		12:07:10		66.81		48.5		29-Feb-08		12:06:20		66.81		47.5		29-Feb-08		12:07:53		71.6		47		10-Apr-08		12:25:59		74.01		35.5

		29-Feb-08		14:07:10		66.81		50.5		29-Feb-08		14:06:20		68.61		47.5		29-Feb-08		14:07:53		71		45		10-Apr-08		14:25:59		74.6		36.5

		29-Feb-08		16:07:10		66.81		51.5		29-Feb-08		16:06:20		68		45.5		29-Feb-08		16:07:53		70.41		44		10-Apr-08		16:25:59		74.01		37

		29-Feb-08		18:07:10		66.2		52		29-Feb-08		18:06:20		67.4		54		29-Feb-08		18:07:53		71		52		10-Apr-08		18:25:59		73.4		34.5

		29-Feb-08		20:07:10		66.2		49		29-Feb-08		20:06:20		67.4		48.5		29-Feb-08		20:07:53		69.8		50		10-Apr-08		20:25:59		72.8		35

		29-Feb-08		22:07:10		65.6		50		29-Feb-08		22:06:20		66.81		49.5		29-Feb-08		22:07:53		71.6		44.5		10-Apr-08		22:25:59		71.6		35

		1-Mar-08		0:07:10		65.6		48.5		1-Mar-08		0:06:20		66.81		47		1-Mar-08		0:07:53		71.6		42		11-Apr-08		0:25:59		70.41		35.5

		1-Mar-08		2:07:10		65.6		48.5		1-Mar-08		2:06:20		66.2		49		1-Mar-08		2:07:53		71		42		11-Apr-08		2:25:59		69.2		35

		1-Mar-08		4:07:10		65.6		49.5		1-Mar-08		4:06:20		66.2		48.5		1-Mar-08		4:07:53		70.41		42.5		11-Apr-08		4:25:59		68.61		35.5

		1-Mar-08		6:07:10		65.6		49		1-Mar-08		6:06:20		65.6		48		1-Mar-08		6:07:53		70.41		42.5		11-Apr-08		6:25:59		69.2		35.5

		1-Mar-08		8:07:10		66.2		48.5		1-Mar-08		8:06:20		66.2		46.5		1-Mar-08		8:07:53		71		43.5		11-Apr-08		8:25:59		71		36

		1-Mar-08		10:07:10		66.2		48.5		1-Mar-08		10:06:20		67.4		45		1-Mar-08		10:07:53		71		46		11-Apr-08		10:25:59		72.8		36.5

		1-Mar-08		12:07:10		66.81		49.5		1-Mar-08		12:06:20		66.81		49.5		1-Mar-08		12:07:53		71		48		11-Apr-08		12:25:59		74.6		36.5

		1-Mar-08		14:07:10		66.81		49		1-Mar-08		14:06:20		68		51.5		1-Mar-08		14:07:53		71		40		11-Apr-08		14:25:59		74.6		36

		1-Mar-08		16:07:10		66.81		51.5		1-Mar-08		16:06:20		68		56		1-Mar-08		16:07:53		71		51.5		11-Apr-08		16:25:59		74.6		36.5

		1-Mar-08		18:07:10		66.2		49		1-Mar-08		18:06:20		66.81		50.5		1-Mar-08		18:07:53		70.41		48.5		11-Apr-08		18:25:59		74.01		36

		1-Mar-08		20:07:10		65.6		49.5		1-Mar-08		20:06:20		66.81		49		1-Mar-08		20:07:53		69.8		46.5		11-Apr-08		20:25:59		74.01		36

		1-Mar-08		22:07:10		65.6		49		1-Mar-08		22:06:20		66.81		47		1-Mar-08		22:07:53		69.8		44		11-Apr-08		22:25:59		72.8		36.5

		2-Mar-08		0:07:10		65.6		49		2-Mar-08		0:06:20		66.81		48.5		2-Mar-08		0:07:53		69.8		43.5		12-Apr-08		0:25:59		71.6		37

		2-Mar-08		2:07:10		65.6		49		2-Mar-08		2:06:20		66.81		48.5		2-Mar-08		2:07:53		69.8		43.5		12-Apr-08		2:25:59		69.8		37

		2-Mar-08		4:07:10		65.6		49		2-Mar-08		4:06:20		66.2		48.5		2-Mar-08		4:07:53		69.2		43.5		12-Apr-08		4:25:59		69.2		37.5

		2-Mar-08		6:07:10		65.6		49		2-Mar-08		6:06:20		66.2		48		2-Mar-08		6:07:53		69.2		43.5		12-Apr-08		6:25:59		69.8		37

		2-Mar-08		8:07:10		65.6		49		2-Mar-08		8:06:20		66.81		45		2-Mar-08		8:07:53		71.6		41		12-Apr-08		8:25:59		71		37

		2-Mar-08		10:07:10		66.2		48.5		2-Mar-08		10:06:20		68		42		2-Mar-08		10:07:53		71		36.5		12-Apr-08		10:25:59		73.4		39

		2-Mar-08		12:07:10		66.2		49		2-Mar-08		12:06:20		67.4		35.5		2-Mar-08		12:07:53		70.41		40.5		12-Apr-08		12:25:59		74.6		38.5

		2-Mar-08		14:07:10		65.6		48		2-Mar-08		14:06:20		66.81		34.5		2-Mar-08		14:07:53		71		36.5		12-Apr-08		14:25:59		75.2		36.5

		2-Mar-08		16:07:10		65.6		47		2-Mar-08		16:06:20		67.4		35.5		2-Mar-08		16:07:53		70.41		35		12-Apr-08		16:25:59		74.6		36

		2-Mar-08		18:07:10		65.6		48.5		2-Mar-08		18:06:20		66.2		34.5		2-Mar-08		18:07:53		69.8		34.5		12-Apr-08		18:25:59		74.01		35

		2-Mar-08		20:07:10		65.6		47.5		2-Mar-08		20:06:20		66.2		36.5		2-Mar-08		20:07:53		69.8		35.5		12-Apr-08		20:25:59		73.4		33

		2-Mar-08		22:07:10		65.6		48		2-Mar-08		22:06:20		66.81		37.5		2-Mar-08		22:07:53		69.2		36.5		12-Apr-08		22:25:59		72.8		34.5

		3-Mar-08		0:07:10		65.6		47		3-Mar-08		0:06:20		66.2		37		3-Mar-08		0:07:53		68.61		36.5		13-Apr-08		0:25:59		71.6		35.5

		3-Mar-08		2:07:10		65.6		46.5		3-Mar-08		2:06:20		65.6		35		3-Mar-08		2:07:53		68		36.5		13-Apr-08		2:25:59		70.41		36.5

		3-Mar-08		4:07:10		65.6		49.5		3-Mar-08		4:06:20		65.01		34.5		3-Mar-08		4:07:53		67.4		36		13-Apr-08		4:25:59		69.8		36.5

		3-Mar-08		6:07:10		65.6		48.5		3-Mar-08		6:06:20		65.01		33		3-Mar-08		6:07:53		66.81		36		13-Apr-08		6:25:59		69.8		36.5

		3-Mar-08		8:07:10		66.2		47.5		3-Mar-08		8:06:20		65.01		32.5		3-Mar-08		8:07:53		67.4		34.5		13-Apr-08		8:25:59		69.8		36.5

		3-Mar-08		10:07:10		65.01		47		3-Mar-08		10:06:20		66.2		30.5		3-Mar-08		10:07:53		68		34		13-Apr-08		10:25:59		71.6		38.5

		3-Mar-08		12:07:10		65.6		48		3-Mar-08		12:06:20		67.4		27.5		3-Mar-08		12:07:53		69.2		31.5		13-Apr-08		12:25:59		74.01		37.5

		3-Mar-08		14:07:10		66.2		44.5		3-Mar-08		14:06:20		68		21.5		3-Mar-08		14:07:53		69.8		29		13-Apr-08		14:25:59		74.01		37.5

		3-Mar-08		16:07:10		66.2		44.5		3-Mar-08		16:06:20		68		19		3-Mar-08		16:07:53		69.8		29		13-Apr-08		16:25:59		72.8		38

		3-Mar-08		18:07:10		66.2		45		3-Mar-08		18:06:20		67.4		19		3-Mar-08		18:07:53		69.2		29.5		13-Apr-08		18:25:59		72.8		37.5

		3-Mar-08		20:07:10		65.6		46		3-Mar-08		20:06:20		66.81		19.5		3-Mar-08		20:07:53		70.41		28		13-Apr-08		20:25:59		72.8		37

		3-Mar-08		22:07:10		65.6		47.5		3-Mar-08		22:06:20		67.4		26		3-Mar-08		22:07:53		70.41		29.5		13-Apr-08		22:25:59		72.8		39.5

		4-Mar-08		0:07:10		65.6		48		4-Mar-08		0:06:20		66.2		34		4-Mar-08		0:07:53		69.8		32		14-Apr-08		0:25:59		71.6		39.5

		4-Mar-08		2:07:10		65.6		48.5		4-Mar-08		2:06:20		65.6		35.5		4-Mar-08		2:07:53		69.2		33.5		14-Apr-08		2:25:59		71		39

		4-Mar-08		4:07:10		65.6		46.5		4-Mar-08		4:06:20		65.01		35.5		4-Mar-08		4:07:53		68		34		14-Apr-08		4:25:59		69.8		38.5

		4-Mar-08		6:07:10		66.2		47.5		4-Mar-08		6:06:20		64.4		35		4-Mar-08		6:07:53		67.4		34.5		14-Apr-08		6:25:59		69.2		38.5

		4-Mar-08		8:07:10		66.2		47.5		4-Mar-08		8:06:20		65.01		34		4-Mar-08		8:07:53		69.2		34		14-Apr-08		8:25:59		68.61		39

		4-Mar-08		10:07:10		66.2		46		4-Mar-08		10:06:20		67.4		35.5		4-Mar-08		10:07:53		72.21		36		14-Apr-08		10:25:59		71		40.5

		4-Mar-08		12:07:10		66.81		47		4-Mar-08		12:06:20		68		34.5		4-Mar-08		12:07:53		71		40.5		14-Apr-08		12:25:59		72.8		40

		4-Mar-08		14:07:10		66.81		46		4-Mar-08		14:06:20		68		29		4-Mar-08		14:07:53		71		40		14-Apr-08		14:25:59		74.01		39

		4-Mar-08		16:07:10		66.81		47		4-Mar-08		16:06:20		68.61		31		4-Mar-08		16:07:53		70.41		37		14-Apr-08		16:25:59		74.01		39

		4-Mar-08		18:07:10		66.2		47.5		4-Mar-08		18:06:20		68		30		4-Mar-08		18:07:53		70.41		34.5		14-Apr-08		18:25:59		72.8		39.5

		4-Mar-08		20:07:10		66.2		45.5		4-Mar-08		20:06:20		67.4		30		4-Mar-08		20:07:53		69.8		34		14-Apr-08		20:25:59		72.8		40

		4-Mar-08		22:07:10		65.6		48		4-Mar-08		22:06:20		66.2		32		4-Mar-08		22:07:53		70.41		34		14-Apr-08		22:25:59		71.6		39.5

		5-Mar-08		0:07:10		65.6		47		5-Mar-08		0:06:20		67.4		33		5-Mar-08		0:07:53		71		33.5		15-Apr-08		0:25:59		71		39.5

		5-Mar-08		2:07:10		65.6		47.5		5-Mar-08		2:06:20		65.6		34.5		5-Mar-08		2:07:53		69.8		33.5		15-Apr-08		2:25:59		69.8		39

		5-Mar-08		4:07:10		65.6		48.5		5-Mar-08		4:06:20		65.01		35.5		5-Mar-08		4:07:53		68.61		33.5		15-Apr-08		4:25:59		68.61		39

		5-Mar-08		6:07:10		66.2		49		5-Mar-08		6:06:20		64.4		35		5-Mar-08		6:07:53		67.4		34		15-Apr-08		6:25:59		69.2		39

		5-Mar-08		8:07:10		66.2		47		5-Mar-08		8:06:20		65.01		34.5		5-Mar-08		8:07:53		69.8		33		15-Apr-08		8:25:59		70.41		39.5

		5-Mar-08		10:07:10		66.2		46		5-Mar-08		10:06:20		66.81		37.5		5-Mar-08		10:07:53		72.21		34.5		15-Apr-08		10:25:59		72.8		40.5

		5-Mar-08		12:07:10		66.81		46.5		5-Mar-08		12:06:20		68		38		5-Mar-08		12:07:53		71		42.5		15-Apr-08		12:25:59		74.6		38.5

		5-Mar-08		14:07:10		66.81		47		5-Mar-08		14:06:20		68		38		5-Mar-08		14:07:53		71		36.5		15-Apr-08		14:25:59		74.6		37

		5-Mar-08		16:07:10		66.81		45.5		5-Mar-08		16:06:20		68		35.5		5-Mar-08		16:07:53		70.41		37		15-Apr-08		16:25:59		74.01		36.5

		5-Mar-08		18:07:10		66.81		47.5		5-Mar-08		18:06:20		68		38.5		5-Mar-08		18:07:53		69.8		43		15-Apr-08		18:25:59		73.4		35

		5-Mar-08		20:07:10		66.2		48		5-Mar-08		20:06:20		67.4		42		5-Mar-08		20:07:53		70.41		41.5		15-Apr-08		20:25:59		72.21		34

		5-Mar-08		22:07:10		66.2		48		5-Mar-08		22:06:20		67.4		36.5		5-Mar-08		22:07:53		70.41		39		15-Apr-08		22:25:59		71		33.5

		6-Mar-08		0:07:10		65.6		48.5		6-Mar-08		0:06:20		66.2		38		6-Mar-08		0:07:53		70.41		36.5		16-Apr-08		0:25:59		69.2		33.5

		6-Mar-08		2:07:10		65.6		48.5		6-Mar-08		2:06:20		65.6		38		6-Mar-08		2:07:53		69.8		36		16-Apr-08		2:25:59		68		34

		6-Mar-08		4:07:10		65.6		48.5		6-Mar-08		4:06:20		65.01		37.5		6-Mar-08		4:07:53		68.61		36		16-Apr-08		4:25:59		67.4		35

		6-Mar-08		6:07:10		66.2		48.5		6-Mar-08		6:06:20		65.01		36		6-Mar-08		6:07:53		67.4		36		16-Apr-08		6:25:59		68		34

		6-Mar-08		8:07:10		66.2		47.5		6-Mar-08		8:06:20		65.01		35		6-Mar-08		8:07:53		70.41		34.5		16-Apr-08		8:25:59		70.41		34.5

		6-Mar-08		10:07:10		66.81		46		6-Mar-08		10:06:20		67.4		36.5		6-Mar-08		10:07:53		71.6		35		16-Apr-08		10:25:59		72.8		35

		6-Mar-08		12:07:10		66.81		46.5		6-Mar-08		12:06:20		68		34.5		6-Mar-08		12:07:53		70.41		44.5		16-Apr-08		12:25:59		74.6		34.5

		6-Mar-08		14:07:10		66.81		46.5		6-Mar-08		14:06:20		68.61		28		6-Mar-08		14:07:53		70.41		41		16-Apr-08		14:25:59		74.6		33.5

		6-Mar-08		16:07:10		66.81		43.5		6-Mar-08		16:06:20		68.61		25		6-Mar-08		16:07:53		70.41		39		16-Apr-08		16:25:59		74.01		33.5

		6-Mar-08		18:07:10		66.2		41.5		6-Mar-08		18:06:20		68		29.5		6-Mar-08		18:07:53		69.8		38.5		16-Apr-08		18:25:59		73.4		33

		6-Mar-08		20:07:10		66.2		48.5		6-Mar-08		20:06:20		66.81		37.5		6-Mar-08		20:07:53		71		37.5		16-Apr-08		20:25:59		72.8		32

		6-Mar-08		22:07:10		65.6		47		6-Mar-08		22:06:20		66.81		40		6-Mar-08		22:07:53		71.6		37		16-Apr-08		22:25:59		71.6		32

		7-Mar-08		0:07:10		65.6		48.5		7-Mar-08		0:06:20		66.2		39		7-Mar-08		0:07:53		70.41		36.5		17-Apr-08		0:25:59		69.8		32.5

		7-Mar-08		2:07:10		65.6		48.5		7-Mar-08		2:06:20		65.01		38		7-Mar-08		2:07:53		69.2		36		17-Apr-08		2:25:59		68.61		34

		7-Mar-08		4:07:10		65.6		42.5		7-Mar-08		4:06:20		64.4		37.5		7-Mar-08		4:07:53		68.61		36		17-Apr-08		4:25:59		68		34.5

		7-Mar-08		6:07:10		65.6		47		7-Mar-08		6:06:20		63.8		36.5		7-Mar-08		6:07:53		67.4		36		17-Apr-08		6:25:59		69.2		34

		7-Mar-08		8:07:10		66.2		48		7-Mar-08		8:06:20		65.01		35.5		7-Mar-08		8:07:53		70.41		35		17-Apr-08		8:25:59		71		34.5

		7-Mar-08		10:07:10		65.6		46.5		7-Mar-08		10:06:20		66.81		37.5		7-Mar-08		10:07:53		71.6		33.5		17-Apr-08		10:25:59		74.01		35

		7-Mar-08		12:07:10		66.2		48		7-Mar-08		12:06:20		67.4		39.5		7-Mar-08		12:07:53		71		39.5		17-Apr-08		12:25:59		75.2		34.5

		7-Mar-08		14:07:10		66.2		43.5		7-Mar-08		14:06:20		68		39		7-Mar-08		14:07:53		71.6		38.5		17-Apr-08		14:25:59		75.2		34.5

		7-Mar-08		16:07:10		66.81		47.5		7-Mar-08		16:06:20		68		40		7-Mar-08		16:07:53		70.41		36.5		17-Apr-08		16:25:59		74.6		34.5

		7-Mar-08		18:07:10		66.2		48		7-Mar-08		18:06:20		68		36.5		7-Mar-08		18:07:53		70.41		35		17-Apr-08		18:25:59		74.01		34

		7-Mar-08		20:07:10		66.2		48		7-Mar-08		20:06:20		66.81		40.5		7-Mar-08		20:07:53		69.8		36		17-Apr-08		20:25:59		74.01		35

		7-Mar-08		22:07:10		65.6		48.5		7-Mar-08		22:06:20		66.81		39		7-Mar-08		22:07:53		70.41		38		17-Apr-08		22:25:59		73.4		35

		8-Mar-08		0:07:10		65.6		43		8-Mar-08		0:06:20		66.2		40.5		8-Mar-08		0:07:53		69.8		37		18-Apr-08		0:25:59		71.6		35

		8-Mar-08		2:07:10		65.6		48.5		8-Mar-08		2:06:20		65.01		41.5		8-Mar-08		2:07:53		69.2		37		18-Apr-08		2:25:59		70.41		36

		8-Mar-08		4:07:10		65.6		48		8-Mar-08		4:06:20		64.4		39.5		8-Mar-08		4:07:53		68		37		18-Apr-08		4:25:59		69.2		36

		8-Mar-08		6:07:10		65.6		48.5		8-Mar-08		6:06:20		63.8		38.5		8-Mar-08		6:07:53		67.4		36.5		18-Apr-08		6:25:59		69.8		36

		8-Mar-08		8:07:10		66.2		47.5		8-Mar-08		8:06:20		65.6		37		8-Mar-08		8:07:53		69.2		36		18-Apr-08		8:25:59		71.6		36

		8-Mar-08		10:07:10		66.2		42		8-Mar-08		10:06:20		67.4		39.5		8-Mar-08		10:07:53		71		38.5		18-Apr-08		10:25:59		74.01		37.5

		8-Mar-08		12:07:10		66.2		48		8-Mar-08		12:06:20		68		38.5		8-Mar-08		12:07:53		70.41		43		18-Apr-08		12:25:59		75.2		39

		8-Mar-08		14:07:10		66.2		47		8-Mar-08		14:06:20		67.4		38.5		8-Mar-08		14:07:53		71		36		18-Apr-08		14:25:59		75.2		38

		8-Mar-08		16:07:10		66.2		48		8-Mar-08		16:06:20		67.4		40		8-Mar-08		16:07:53		70.41		42		18-Apr-08		16:25:59		75.2		38

		8-Mar-08		18:07:10		66.2		49		8-Mar-08		18:06:20		67.4		44		8-Mar-08		18:07:53		70.41		42		18-Apr-08		18:25:59		74.6		37

		8-Mar-08		20:07:10		65.6		43.5		8-Mar-08		20:06:20		66.81		41.5		8-Mar-08		20:07:53		69.8		40		18-Apr-08		20:25:59		74.6		38

		8-Mar-08		22:07:10		65.6		48.5		8-Mar-08		22:06:20		66.2		45.5		8-Mar-08		22:07:53		70.41		40.5		18-Apr-08		22:25:59		73.4		37.5

		9-Mar-08		0:07:10		65.6		48.5		9-Mar-08		0:06:20		66.81		44.5		9-Mar-08		0:07:53		70.41		40		19-Apr-08		0:25:59		71.6		37.5

		9-Mar-08		2:07:10		65.6		47		9-Mar-08		2:06:20		66.2		43.5		9-Mar-08		2:07:53		69.8		39		19-Apr-08		2:25:59		71		38.5

		9-Mar-08		4:07:10		65.6		48		9-Mar-08		4:06:20		65.01		42.5		9-Mar-08		4:07:53		69.2		38.5		19-Apr-08		4:25:59		70.41		39.5

		9-Mar-08		6:07:10		65.6		42		9-Mar-08		6:06:20		64.4		42		9-Mar-08		6:07:53		68.61		38.5		19-Apr-08		6:25:59		71.6		39.5

		9-Mar-08		8:07:10		65.6		48		9-Mar-08		8:06:20		65.01		39		9-Mar-08		8:07:53		71		37		19-Apr-08		8:25:59		72.21		39

		9-Mar-08		10:07:10		66.2		48.5		9-Mar-08		10:06:20		66.81		43.5		9-Mar-08		10:07:53		71		34.5		19-Apr-08		10:25:59		73.4		40

		9-Mar-08		12:07:10		66.2		48.5		9-Mar-08		12:06:20		67.4		43		9-Mar-08		12:07:53		71.6		46		19-Apr-08		12:25:59		74.01		40.5

		9-Mar-08		14:07:10		66.2		47.5		9-Mar-08		14:06:20		68		35		9-Mar-08		14:07:53		71		43		19-Apr-08		14:25:59		75.2		41

		9-Mar-08		16:07:10		66.2		44		9-Mar-08		16:06:20		67.4		37.5		9-Mar-08		16:07:53		71		36.5		19-Apr-08		16:25:59		74.6		39.5

		9-Mar-08		18:07:10		66.2		47.5		9-Mar-08		18:06:20		67.4		31.5		9-Mar-08		18:07:53		69.8		36		19-Apr-08		18:25:59		74.01		38.5

		9-Mar-08		20:07:10		66.2		47.5		9-Mar-08		20:06:20		67.4		44.5		9-Mar-08		20:07:53		69.8		42		19-Apr-08		20:25:59		74.01		38.5

		9-Mar-08		22:07:10		65.6		48.5		9-Mar-08		22:06:20		66.2		47.5		9-Mar-08		22:07:53		71.6		40		19-Apr-08		22:25:59		72.8		37.5

		10-Mar-08		0:07:10		65.6		48.5		10-Mar-08		0:06:20		66.81		44.5		10-Mar-08		0:07:53		71		39.5		20-Apr-08		0:25:59		71		38

		10-Mar-08		2:07:10		65.6		48		10-Mar-08		2:06:20		66.2		44.5		10-Mar-08		2:07:53		70.41		39		20-Apr-08		2:25:59		69.8		38

		10-Mar-08		4:07:10		65.6		49		10-Mar-08		4:06:20		65.01		44		10-Mar-08		4:07:53		69.8		38.5		20-Apr-08		4:25:59		68.61		37.5

		10-Mar-08		6:07:10		65.6		49.5		10-Mar-08		6:06:20		64.4		42		10-Mar-08		6:07:53		68.61		38.5		20-Apr-08		6:25:59		68		37.5

		10-Mar-08		8:07:10		65.6		48		10-Mar-08		8:06:20		63.8		40.5		10-Mar-08		8:07:53		68		38		20-Apr-08		8:25:59		67.4		36.5

		10-Mar-08		10:07:10		65.6		48		10-Mar-08		10:06:20		66.2		41.5		10-Mar-08		10:07:53		69.2		39		20-Apr-08		10:25:59		68		37.5

		10-Mar-08		12:07:10		65.6		49		10-Mar-08		12:06:20		66.81		41		10-Mar-08		12:07:53		69.8		40		20-Apr-08		12:25:59		69.2		36.5

		10-Mar-08		14:07:10		66.2		47.5		10-Mar-08		14:06:20		68		37.5		10-Mar-08		14:07:53		70.41		41		20-Apr-08		14:25:59		70.41		33.5

		10-Mar-08		16:07:10		66.2		48		10-Mar-08		16:06:20		68		34.5		10-Mar-08		16:07:53		69.8		41.5		20-Apr-08		16:25:59		70.41		33

		10-Mar-08		18:07:10		66.2		48		10-Mar-08		18:06:20		68		33.5		10-Mar-08		18:07:53		70.41		39.5		20-Apr-08		18:25:59		70.41		32

		10-Mar-08		20:07:10		66.2		48		10-Mar-08		20:06:20		67.4		43		10-Mar-08		20:07:53		71		42		20-Apr-08		20:25:59		69.8		32

		10-Mar-08		22:07:10		65.6		49		10-Mar-08		22:06:20		66.2		45		10-Mar-08		22:07:53		71.6		40.5		20-Apr-08		22:25:59		68.61		33

		11-Mar-08		0:07:10		65.6		49		11-Mar-08		0:06:20		66.81		44.5		11-Mar-08		0:07:53		71		39.5		21-Apr-08		0:25:59		67.4		33.5

		11-Mar-08		2:07:10		65.6		49		11-Mar-08		2:06:20		66.2		45		11-Mar-08		2:07:53		70.41		39.5		21-Apr-08		2:25:59		66.81		34

		11-Mar-08		4:07:10		65.6		48.5		11-Mar-08		4:06:20		65.6		45		11-Mar-08		4:07:53		69.8		39		21-Apr-08		4:25:59		65.6		35

		11-Mar-08		6:07:10		65.6		48		11-Mar-08		6:06:20		65.01		45		11-Mar-08		6:07:53		71		39.5		21-Apr-08		6:25:59		65.01		35.5

		11-Mar-08		8:07:10		66.2		48		11-Mar-08		8:06:20		66.81		43		11-Mar-08		8:07:53		71.6		35.5		21-Apr-08		8:25:59		64.4		36.5

		11-Mar-08		10:07:10		66.81		47.5		11-Mar-08		10:06:20		67.4		43.5		11-Mar-08		10:07:53		71		37		21-Apr-08		10:25:59		65.6		37.5

		11-Mar-08		12:07:10		66.2		48		11-Mar-08		12:06:20		67.4		44		11-Mar-08		12:07:53		71		43		21-Apr-08		12:25:59		66.81		36

		11-Mar-08		14:07:10		66.81		52.5		11-Mar-08		14:06:20		68.61		52		11-Mar-08		14:07:53		70.41		48.5		21-Apr-08		14:25:59		68.61		36

		11-Mar-08		16:07:10		66.2		49.5		11-Mar-08		16:06:20		67.4		49		11-Mar-08		16:07:53		70.41		53		21-Apr-08		16:25:59		69.8		34.5

		11-Mar-08		18:07:10		66.2		49		11-Mar-08		18:06:20		68		45		11-Mar-08		18:07:53		71		42		21-Apr-08		18:25:59		69.8		33

		11-Mar-08		20:07:10		65.6		48.5		11-Mar-08		20:06:20		66.81		46		11-Mar-08		20:07:53		70.41		43		21-Apr-08		20:25:59		69.2		33

		11-Mar-08		22:07:10		65.6		48.5		11-Mar-08		22:06:20		67.4		45.5		11-Mar-08		22:07:53		71		42		21-Apr-08		22:25:59		68.61		34.5

		12-Mar-08		0:07:10		65.6		49		12-Mar-08		0:06:20		66.81		45.5		12-Mar-08		0:07:53		71.6		40.5		22-Apr-08		0:25:59		67.4		34.5

		12-Mar-08		2:07:10		65.6		49		12-Mar-08		2:06:20		66.81		45		12-Mar-08		2:07:53		70.41		40.5		22-Apr-08		2:25:59		66.2		35

		12-Mar-08		4:07:10		65.6		49		12-Mar-08		4:06:20		65.6		44.5		12-Mar-08		4:07:53		69.8		39.5		22-Apr-08		4:25:59		65.6		36

		12-Mar-08		6:07:10		65.6		49		12-Mar-08		6:06:20		65.01		44		12-Mar-08		6:07:53		70.41		39.5		22-Apr-08		6:25:59		66.81		34

		12-Mar-08		8:07:10		66.2		48		12-Mar-08		8:06:20		66.2		42.5		12-Mar-08		8:07:53		71		40.5		22-Apr-08		8:25:59		68		34.5

		12-Mar-08		10:07:10		66.2		49		12-Mar-08		10:06:20		66.81		50		12-Mar-08		10:07:53		70.41		45		22-Apr-08		10:25:59		72.21		36

		12-Mar-08		12:07:10		66.2		50		12-Mar-08		12:06:20		66.81		48		12-Mar-08		12:07:53		71.6		50		22-Apr-08		12:25:59		73.4		35.5

		12-Mar-08		14:07:10		66.2		49.5		12-Mar-08		14:06:20		68		50.5		12-Mar-08		14:07:53		71		41.5		22-Apr-08		14:25:59		73.4		35.5

		12-Mar-08		16:07:10		66.2		51.5		12-Mar-08		16:06:20		66.81		59.5		12-Mar-08		16:07:53		71		50.5		22-Apr-08		16:25:59		73.4		35.5

		12-Mar-08		18:07:10		66.2		51.5		12-Mar-08		18:06:20		67.4		48.5		12-Mar-08		18:07:53		70.41		50		22-Apr-08		18:25:59		72.8		35

		12-Mar-08		20:07:10		65.6		50		12-Mar-08		20:06:20		67.4		51.5		12-Mar-08		20:07:53		70.41		48		22-Apr-08		20:25:59		72.21		34.5

		12-Mar-08		22:07:10		65.6		49		12-Mar-08		22:06:20		67.4		49		12-Mar-08		22:07:53		70.41		44.5		22-Apr-08		22:25:59		71		34

		13-Mar-08		0:07:10		65.6		49		13-Mar-08		0:06:20		66.81		47.5		13-Mar-08		0:07:53		70.41		42		23-Apr-08		0:25:59		69.8		34

		13-Mar-08		2:07:10		65.6		49		13-Mar-08		2:06:20		65.6		46		13-Mar-08		2:07:53		70.41		41		23-Apr-08		2:25:59		68.61		34.5

		13-Mar-08		4:07:10		65.6		49.5		13-Mar-08		4:06:20		65.01		47		13-Mar-08		4:07:53		69.2		41		23-Apr-08		4:25:59		67.4		35

		13-Mar-08		6:07:10		65.6		49		13-Mar-08		6:06:20		65.6		48.5		13-Mar-08		6:07:53		70.41		42.5		23-Apr-08		6:25:59		68.61		34.5

		13-Mar-08		8:07:10		66.2		48		13-Mar-08		8:06:20		67.4		46.5		13-Mar-08		8:07:53		71		44		23-Apr-08		8:25:59		70.41		34.5

		13-Mar-08		10:07:10		66.2		48		13-Mar-08		10:06:20		66.81		46.5		13-Mar-08		10:07:53		71.6		41.5		23-Apr-08		10:25:59		71.6		35.5

		13-Mar-08		12:07:10		66.2		48.5		13-Mar-08		12:06:20		66.81		47.5		13-Mar-08		12:07:53		71		43		23-Apr-08		12:25:59		72.21		37.5

		13-Mar-08		14:07:10		66.81		49		13-Mar-08		14:06:20		67.4		46.5		13-Mar-08		14:07:53		71		46.5		23-Apr-08		14:25:59		72.8		39

		13-Mar-08		16:07:10		66.81		49.5		13-Mar-08		16:06:20		67.4		52		13-Mar-08		16:07:53		70.41		41.5		23-Apr-08		16:25:59		73.4		40.5

		13-Mar-08		18:07:10		66.2		49		13-Mar-08		18:06:20		66.81		49		13-Mar-08		18:07:53		71		44.5		23-Apr-08		18:25:59		73.4		40.5

		13-Mar-08		20:07:10		66.2		48.5		13-Mar-08		20:06:20		66.2		48		13-Mar-08		20:07:53		71		43.5		23-Apr-08		20:25:59		72.8		41.5

		13-Mar-08		22:07:10		66.2		49		13-Mar-08		22:06:20		67.4		46.5		13-Mar-08		22:07:53		72.21		41.5		23-Apr-08		22:25:59		71.6		41.5

		14-Mar-08		0:07:10		66.2		49.5		14-Mar-08		0:06:20		67.4		51		14-Mar-08		0:07:53		71.6		42		24-Apr-08		0:25:59		70.41		42

		14-Mar-08		2:07:10		65.6		50.5		14-Mar-08		2:06:20		67.4		52		14-Mar-08		2:07:53		71.6		43		24-Apr-08		2:25:59		69.2		42

		14-Mar-08		4:07:10		65.6		50.5		14-Mar-08		4:06:20		66.81		53		14-Mar-08		4:07:53		71.6		43.5		24-Apr-08		4:25:59		68.61		42.5

		14-Mar-08		6:07:10		66.2		50.5		14-Mar-08		6:06:20		67.4		53.5		14-Mar-08		6:07:53		71		40.5		24-Apr-08		6:25:59		69.2		42

		14-Mar-08		8:07:10		66.2		49.5		14-Mar-08		8:06:20		66.81		52		14-Mar-08		8:07:53		70.41		50		24-Apr-08		8:25:59		71		42

		14-Mar-08		10:07:10		66.2		51		14-Mar-08		10:06:20		67.4		52.5		14-Mar-08		10:07:53		71		51.5		24-Apr-08		10:25:59		72.8		43

		14-Mar-08		12:07:10		66.2		49.5		14-Mar-08		12:06:20		68		48		14-Mar-08		12:07:53		71		50.5		24-Apr-08		12:25:59		74.01		43

		14-Mar-08		14:07:10		66.81		48.5		14-Mar-08		14:06:20		68.61		47.5		14-Mar-08		14:07:53		71		52.5		24-Apr-08		14:25:59		74.01		40.5

		14-Mar-08		16:07:10		66.2		48		14-Mar-08		16:06:20		68		45.5		14-Mar-08		16:07:53		70.41		44		24-Apr-08		16:25:59		74.01		38.5

		14-Mar-08		18:07:10		65.6		48.5		14-Mar-08		18:06:20		66.81		46		14-Mar-08		18:07:53		70.41		43		24-Apr-08		18:25:59		72.8		36.5

		14-Mar-08		20:07:10		65.6		48.5		14-Mar-08		20:06:20		67.4		45		14-Mar-08		20:07:53		69.8		43		24-Apr-08		20:25:59		72.8		36.5

		14-Mar-08		22:07:10		65.6		48.5		14-Mar-08		22:06:20		67.4		45.5		14-Mar-08		22:07:53		71		41		24-Apr-08		22:25:59		71.6		35

		15-Mar-08		0:07:10		65.6		49		15-Mar-08		0:06:20		66.2		45		15-Mar-08		0:07:53		70.41		40.5		25-Apr-08		0:25:59		69.8		35

		15-Mar-08		2:07:10		65.6		49		15-Mar-08		2:06:20		65.6		44		15-Mar-08		2:07:53		69.8		39.5		25-Apr-08		2:25:59		68		35.5

		15-Mar-08		4:07:10		65.6		49		15-Mar-08		4:06:20		65.01		42.5		15-Mar-08		4:07:53		69.2		39		25-Apr-08		4:25:59		66.81		37

		15-Mar-08		6:07:10		66.2		48.5		15-Mar-08		6:06:20		65.6		44.5		15-Mar-08		6:07:53		69.2		42		25-Apr-08		6:25:59		68		36.5

		15-Mar-08		8:07:10		66.2		47.5		15-Mar-08		8:06:20		66.2		44		15-Mar-08		8:07:53		71		42		25-Apr-08		8:25:59		69.2		36.5

		15-Mar-08		10:07:10		66.81		48		15-Mar-08		10:06:20		67.4		46.5		15-Mar-08		10:07:53		71		47		25-Apr-08		10:25:59		72.8		38.5

		15-Mar-08		12:07:10		66.2		48		15-Mar-08		12:06:20		67.4		46.5		15-Mar-08		12:07:53		71		46.5		25-Apr-08		12:25:59		74.01		37

		15-Mar-08		14:07:10		66.2		48		15-Mar-08		14:06:20		67.4		41		15-Mar-08		14:07:53		71.6		44		25-Apr-08		14:25:59		74.6		36.5

		15-Mar-08		16:07:10		66.2		47.5		15-Mar-08		16:06:20		66.81		38		15-Mar-08		16:07:53		70.41		39.5		25-Apr-08		16:25:59		74.6		37.5

		15-Mar-08		18:07:10		65.6		48		15-Mar-08		18:06:20		66.81		40		15-Mar-08		18:07:53		69.8		38.5		25-Apr-08		18:25:59		74.01		35.5

		15-Mar-08		20:07:10		65.6		42.5		15-Mar-08		20:06:20		65.6		41		15-Mar-08		20:07:53		69.8		37.5		25-Apr-08		20:25:59		74.6		35.5

		15-Mar-08		22:07:10		65.6		49		15-Mar-08		22:06:20		65.01		41.5		15-Mar-08		22:07:53		69.2		37		25-Apr-08		22:25:59		74.01		35.5

		16-Mar-08		0:07:10		65.01		49		16-Mar-08		0:06:20		64.4		42		16-Mar-08		0:07:53		68.61		38		26-Apr-08		0:25:59		72.8		35

		16-Mar-08		2:07:10		65.01		50		16-Mar-08		2:06:20		63.8		43.5		16-Mar-08		2:07:53		68		38.5		26-Apr-08		2:25:59		71		36

		16-Mar-08		4:07:10		65.01		49		16-Mar-08		4:06:20		63.21		44		16-Mar-08		4:07:53		67.4		39		26-Apr-08		4:25:59		69.8		36.5

		16-Mar-08		6:07:10		65.01		49.5		16-Mar-08		6:06:20		63.21		43		16-Mar-08		6:07:53		68		39		26-Apr-08		6:25:59		70.41		37.5

		16-Mar-08		8:07:10		65.6		48		16-Mar-08		8:06:20		62		41.5		16-Mar-08		8:07:53		70.41		36.5		26-Apr-08		8:25:59		72.21		37

		16-Mar-08		10:07:10		65.6		49		16-Mar-08		10:06:20		64.4		44		16-Mar-08		10:07:53		71.6		38.5		26-Apr-08		10:25:59		74.01		38

		16-Mar-08		12:07:10		65.6		44		16-Mar-08		12:06:20		65.6		38		16-Mar-08		12:07:53		71		34		26-Apr-08		12:25:59		75.2		37.5

		16-Mar-08		14:07:10		65.6		38		16-Mar-08		14:06:20		66.2		34.5		16-Mar-08		14:07:53		70.41		33.5		26-Apr-08		14:25:59		73.4		34

		16-Mar-08		16:07:10		65.6		46		16-Mar-08		16:06:20		67.4		33		16-Mar-08		16:07:53		69.8		31.5		26-Apr-08		16:25:59		73.4		35.5

		16-Mar-08		18:07:10		65.6		41		16-Mar-08		18:06:20		66.2		36		16-Mar-08		18:07:53		69.2		34.5		26-Apr-08		18:25:59		73.4		37

		16-Mar-08		20:07:10		65.6		44		16-Mar-08		20:06:20		65.6		40		16-Mar-08		20:07:53		69.2		37		26-Apr-08		20:25:59		73.4		37

		16-Mar-08		22:07:10		65.6		48.5		16-Mar-08		22:06:20		65.6		37.5		16-Mar-08		22:07:53		68.61		36.5		26-Apr-08		22:25:59		72.8		36.5

		17-Mar-08		0:07:10		65.6		47.5		17-Mar-08		0:06:20		65.01		36		17-Mar-08		0:07:53		68		36		27-Apr-08		0:25:59		72.21		36.5

		17-Mar-08		2:07:10		65.6		47		17-Mar-08		2:06:20		64.4		34.5		17-Mar-08		2:07:53		67.4		35		27-Apr-08		2:25:59		71		36

		17-Mar-08		4:07:10		65.6		47.5		17-Mar-08		4:06:20		64.4		34		17-Mar-08		4:07:53		66.81		35		27-Apr-08		4:25:59		70.41		36.5

		17-Mar-08		6:07:10		65.01		38		17-Mar-08		6:06:20		64.4		34.5		17-Mar-08		6:07:53		66.2		35		27-Apr-08		6:25:59		69.8		36

		17-Mar-08		8:07:10		65.01		46.5		17-Mar-08		8:06:20		63.8		34.5		17-Mar-08		8:07:53		67.4		34.5		27-Apr-08		8:25:59		69.8		37.5

		17-Mar-08		10:07:10		65.6		38.5		17-Mar-08		10:06:20		65.01		34		17-Mar-08		10:07:53		68.61		33.5		27-Apr-08		10:25:59		71		40

		17-Mar-08		12:07:10		65.6		33.5		17-Mar-08		12:06:20		67.4		30		17-Mar-08		12:07:53		69.8		31.5		27-Apr-08		12:25:59		72.8		39.5

		17-Mar-08		14:07:10		65.6		42		17-Mar-08		14:06:20		66.81		23		17-Mar-08		14:07:53		69.8		30		27-Apr-08		14:25:59		74.01		38.5

		17-Mar-08		16:07:10		65.6		40		17-Mar-08		16:06:20		66.81		22		17-Mar-08		16:07:53		69.8		29		27-Apr-08		16:25:59		73.4		40.5

		17-Mar-08		18:07:10		65.6		36.5		17-Mar-08		18:06:20		66.2		31.5		17-Mar-08		18:07:53		69.8		31		27-Apr-08		18:25:59		73.4		40.5

		17-Mar-08		20:07:10		65.6		47.5		17-Mar-08		20:06:20		66.2		34.5		17-Mar-08		20:07:53		69.8		33		27-Apr-08		20:25:59		73.4		40.5

		17-Mar-08		22:07:10		65.6		47.5		17-Mar-08		22:06:20		66.81		35		17-Mar-08		22:07:53		70.41		34		27-Apr-08		22:25:59		73.4		38.5

		18-Mar-08		0:07:10		65.6		48		18-Mar-08		0:06:20		66.2		36		18-Mar-08		0:07:53		69.8		33.5		28-Apr-08		0:25:59		72.8		37.5

		18-Mar-08		2:07:10		65.6		39		18-Mar-08		2:06:20		65.01		37		18-Mar-08		2:07:53		68.61		34		28-Apr-08		2:25:59		72.21		39.5

		18-Mar-08		4:07:10		65.6		48		18-Mar-08		4:06:20		65.01		37.5		18-Mar-08		4:07:53		68		35		28-Apr-08		4:25:59		71.6		39.5

		18-Mar-08		6:07:10		66.2		47		18-Mar-08		6:06:20		65.01		37.5		18-Mar-08		6:07:53		69.2		34.5		28-Apr-08		6:25:59		70.41		39.5

		18-Mar-08		8:07:10		66.81		42		18-Mar-08		8:06:20		66.2		36.5		18-Mar-08		8:07:53		71.6		34.5		28-Apr-08		8:25:59		69.8		39.5

		18-Mar-08		10:07:10		66.2		38.5		18-Mar-08		10:06:20		67.4		35.5		18-Mar-08		10:07:53		71.6		39.5		28-Apr-08		10:25:59		71.6		41.5

		18-Mar-08		12:07:10		66.2		42		18-Mar-08		12:06:20		66.81		34.5		18-Mar-08		12:07:53		71.6		37		28-Apr-08		12:25:59		74.01		40

		18-Mar-08		14:07:10		66.81		46		18-Mar-08		14:06:20		66.2		39		18-Mar-08		14:07:53		71.6		34.5		28-Apr-08		14:25:59		74.01		39.5

		18-Mar-08		16:07:10		66.81		47.5		18-Mar-08		16:06:20		65.6		45		18-Mar-08		16:07:53		71.6		40		28-Apr-08		16:25:59		73.4		41.5

		18-Mar-08		18:07:10		66.81		46.5		18-Mar-08		18:06:20		65.6		45.5		18-Mar-08		18:07:53		70.41		37.5		28-Apr-08		18:25:59		73.4		41

		18-Mar-08		20:07:10		66.2		47		18-Mar-08		20:06:20		65.6		47		18-Mar-08		20:07:53		70.41		42.5		28-Apr-08		20:25:59		73.4		40.5

		18-Mar-08		22:07:10		66.2		47.5		18-Mar-08		22:06:20		65.01		47		18-Mar-08		22:07:53		71.6		40.5		28-Apr-08		22:25:59		73.4		39.5

		19-Mar-08		0:07:10		65.6		48		19-Mar-08		0:06:20		65.6		44.5		19-Mar-08		0:07:53		72.21		39		29-Apr-08		0:25:59		72.8		38.5

		19-Mar-08		2:07:10		65.6		48.5		19-Mar-08		2:06:20		64.4		49.5		19-Mar-08		2:07:53		71.6		39		29-Apr-08		2:25:59		71.6		38.5

		19-Mar-08		4:07:10		65.6		48		19-Mar-08		4:06:20		65.6		46.5		19-Mar-08		4:07:53		71		39		29-Apr-08		4:25:59		70.41		38.5

		19-Mar-08		6:07:10		66.2		47		19-Mar-08		6:06:20		65.6		45.5		19-Mar-08		6:07:53		71.6		39.5		29-Apr-08		6:25:59		70.41		38

		19-Mar-08		8:07:10		66.2		47		19-Mar-08		8:06:20		65.01		47		19-Mar-08		8:07:53		70.41		38		29-Apr-08		8:25:59		69.8		39.5

		19-Mar-08		10:07:10		66.2		47		19-Mar-08		10:06:20		66.2		47		19-Mar-08		10:07:53		70.41		37.5		29-Apr-08		10:25:59		72.8		40.5

		19-Mar-08		12:07:10		66.81		48.5		19-Mar-08		12:06:20		66.2		48		19-Mar-08		12:07:53		71.6		50.5		29-Apr-08		12:25:59		73.4		42.5

		19-Mar-08		14:07:10		66.81		49		19-Mar-08		14:06:20		66.2		51		19-Mar-08		14:07:53		71		41		29-Apr-08		14:25:59		73.4		43

		19-Mar-08		16:07:10		66.81		46.5		19-Mar-08		16:06:20		66.2		44		19-Mar-08		16:07:53		71.6		42.5		29-Apr-08		16:25:59		74.01		42.5

		19-Mar-08		18:07:10		66.2		47.5		19-Mar-08		18:06:20		66.2		45		19-Mar-08		18:07:53		70.41		40		29-Apr-08		18:25:59		74.01		41

		19-Mar-08		20:07:10		66.2		49		19-Mar-08		20:06:20		65.01		51.5		19-Mar-08		20:07:53		70.41		45		29-Apr-08		20:25:59		74.6		41

		19-Mar-08		22:07:10		65.6		48		19-Mar-08		22:06:20		65.6		52.5		19-Mar-08		22:07:53		71		44.5		29-Apr-08		22:25:59		74.01		40

		20-Mar-08		0:07:10		65.6		47		20-Mar-08		0:06:20		65.01		50.5		20-Mar-08		0:07:53		71		41.5		30-Apr-08		0:25:59		72.8		36.5

		20-Mar-08		2:07:10		65.6		48.5		20-Mar-08		2:06:20		65.6		47.5		20-Mar-08		2:07:53		71		40		30-Apr-08		2:25:59		71		36

		20-Mar-08		4:07:10		65.6		48.5		20-Mar-08		4:06:20		65.01		44.5		20-Mar-08		4:07:53		70.41		39		30-Apr-08		4:25:59		70.41		36

		20-Mar-08		6:07:10		65.6		41		20-Mar-08		6:06:20		64.4		43.5		20-Mar-08		6:07:53		70.41		38.5		30-Apr-08		6:25:59		70.41		36

		20-Mar-08		8:07:10		66.2		47		20-Mar-08		8:06:20		65.6		45		20-Mar-08		8:07:53		71.6		41		30-Apr-08		8:25:59		71		36

		20-Mar-08		10:07:10		66.2		45		20-Mar-08		10:06:20		65.6		49		20-Mar-08		10:07:53		71		45.5		30-Apr-08		10:25:59		72.8		36

		20-Mar-08		12:07:10		66.2		48		20-Mar-08		12:06:20		65.01		51.5		20-Mar-08		12:07:53		69.8		47		30-Apr-08		12:25:59		72.8		34.5

		20-Mar-08		14:07:10		66.81		47.5		20-Mar-08		14:06:20		65.6		53.5		20-Mar-08		14:07:53		71		51.5		30-Apr-08		14:25:59		73.4		33.5

		20-Mar-08		16:07:10		66.2		50		20-Mar-08		16:06:20		65.6		55.5		20-Mar-08		16:07:53		69.8		50.5		30-Apr-08		16:25:59		73.4		34

		20-Mar-08		18:07:10		66.2		48.5		20-Mar-08		18:06:20		65.6		56		20-Mar-08		18:07:53		69.8		48.5		30-Apr-08		18:25:59		72.8		32

		20-Mar-08		20:07:10		65.6		48.5		20-Mar-08		20:06:20		66.2		46		20-Mar-08		20:07:53		70.41		44		30-Apr-08		20:25:59		73.4		32

		20-Mar-08		22:07:10		65.6		48.5		20-Mar-08		22:06:20		65.6		47.5		20-Mar-08		22:07:53		71		41.5		30-Apr-08		22:25:59		72.21		31

		21-Mar-08		0:07:10		65.6		43		21-Mar-08		0:06:20		65.01		44		21-Mar-08		0:07:53		70.41		40		1-May-08		0:25:59		70.41		31.5

		21-Mar-08		2:07:10		65.6		49		21-Mar-08		2:06:20		65.01		41		21-Mar-08		2:07:53		69.8		38		1-May-08		2:25:59		69.2		31

		21-Mar-08		4:07:10		65.01		39.5		21-Mar-08		4:06:20		64.4		40		21-Mar-08		4:07:53		68.61		37.5		1-May-08		4:25:59		68		31

		21-Mar-08		6:07:10		65.6		48.5		21-Mar-08		6:06:20		64.4		39		21-Mar-08		6:07:53		69.2		37		1-May-08		6:25:59		70.41		30.5

		21-Mar-08		8:07:10		65.6		37.5		21-Mar-08		8:06:20		65.01		37.5		21-Mar-08		8:07:53		71		33		1-May-08		8:25:59		69.2		30

		21-Mar-08		10:07:10		66.2		47		21-Mar-08		10:06:20		66.2		39		21-Mar-08		10:07:53		71		40		1-May-08		10:25:59		71		30

		21-Mar-08		12:07:10		66.2		42.5		21-Mar-08		12:06:20		66.2		32		21-Mar-08		12:07:53		71		37		1-May-08		12:25:59		72.8		29

		21-Mar-08		14:07:10		66.2		46		21-Mar-08		14:06:20		66.81		30.5		21-Mar-08		14:07:53		70.41		31.5		1-May-08		14:25:59		73.4		28

		21-Mar-08		16:07:10		66.2		34.5		21-Mar-08		16:06:20		66.81		33		21-Mar-08		16:07:53		70.41		35.5		1-May-08		16:25:59		72.8		28

		21-Mar-08		18:07:10		66.2		46.5		21-Mar-08		18:06:20		66.2		36		21-Mar-08		18:07:53		70.41		33.5		1-May-08		18:25:59		73.4		29

		21-Mar-08		20:07:10		65.6		40		21-Mar-08		20:06:20		65.6		37		21-Mar-08		20:07:53		70.41		36.5		1-May-08		20:25:59		73.4		29.5

		21-Mar-08		22:07:10		65.6		39		21-Mar-08		22:06:20		65.01		37.5		21-Mar-08		22:07:53		70.41		35		1-May-08		22:25:59		72.8		29.5

		22-Mar-08		0:07:10		65.6		37		22-Mar-08		0:06:20		65.6		35		22-Mar-08		0:07:53		69.8		33.5		2-May-08		0:25:59		71.6		29.5

		22-Mar-08		2:07:10		65.01		36.5		22-Mar-08		2:06:20		65.6		35.5		22-Mar-08		2:07:53		69.2		33.5		2-May-08		2:25:59		70.41		30

		22-Mar-08		4:07:10		65.01		47		22-Mar-08		4:06:20		65.6		35		22-Mar-08		4:07:53		68.61		34		2-May-08		4:25:59		69.2		30

		22-Mar-08		6:07:10		65.6		46		22-Mar-08		6:06:20		65.6		34.5		22-Mar-08		6:07:53		69.2		33.5		2-May-08		6:25:59		71		30.5

		22-Mar-08		8:07:10		65.6		36		22-Mar-08		8:06:20		65.6		34.5		22-Mar-08		8:07:53		71		32.5		2-May-08		8:25:59		69.8		31.5

		22-Mar-08		10:07:10		66.2		41.5		22-Mar-08		10:06:20		65.6		37		22-Mar-08		10:07:53		70.41		34		2-May-08		10:25:59		72.21		32

		22-Mar-08		12:07:10		66.2		42		22-Mar-08		12:06:20		66.81		33.5		22-Mar-08		12:07:53		70.41		32.5		2-May-08		12:25:59		72.8		30.5

		22-Mar-08		14:07:10		66.81		45		22-Mar-08		14:06:20		66.2		33		22-Mar-08		14:07:53		71		33		2-May-08		14:25:59		73.4		28

		22-Mar-08		16:07:10		66.2		41.5		22-Mar-08		16:06:20		65.6		40		22-Mar-08		16:07:53		71		33		2-May-08		16:25:59		74.01		30

		22-Mar-08		18:07:10		66.2		47		22-Mar-08		18:06:20		65.01		40		22-Mar-08		18:07:53		70.41		34.5		2-May-08		18:25:59		72.8		31

		22-Mar-08		20:07:10		65.6		47		22-Mar-08		20:06:20		66.2		43		22-Mar-08		20:07:53		69.8		39.5		2-May-08		20:25:59		74.01		31.5

		22-Mar-08		22:07:10		65.6		47.5		22-Mar-08		22:06:20		65.01		42.5		22-Mar-08		22:07:53		70.41		38.5		2-May-08		22:25:59		74.01		30.5

		23-Mar-08		0:07:10		65.6		47.5		23-Mar-08		0:06:20		65.6		42		23-Mar-08		0:07:53		71		37		3-May-08		0:25:59		73.4		29.5

		23-Mar-08		2:07:10		65.6		40.5		23-Mar-08		2:06:20		65.01		40		23-Mar-08		2:07:53		70.41		36.5		3-May-08		2:25:59		72.21		30.5

		23-Mar-08		4:07:10		65.6		49		23-Mar-08		4:06:20		65.01		38.5		23-Mar-08		4:07:53		69.2		35		3-May-08		4:25:59		70.41		31.5

		23-Mar-08		6:07:10		65.01		38.5		23-Mar-08		6:06:20		65.6		38		23-Mar-08		6:07:53		69.8		35.5		3-May-08		6:25:59		70.41		32

		23-Mar-08		8:07:10		65.6		46		23-Mar-08		8:06:20		65.01		37.5		23-Mar-08		8:07:53		71		34.5		3-May-08		8:25:59		70.41		33.5

		23-Mar-08		10:07:10		65.6		41.5		23-Mar-08		10:06:20		66.2		40.5		23-Mar-08		10:07:53		70.41		34.5		3-May-08		10:25:59		72.8		34.5

		23-Mar-08		12:07:10		66.2		47		23-Mar-08		12:06:20		66.2		42.5		23-Mar-08		12:07:53		69.8		34.5		3-May-08		12:25:59		73.4		34

		23-Mar-08		14:07:10		66.2		42.5		23-Mar-08		14:06:20		65.6		43		23-Mar-08		14:07:53		70.41		43.5		3-May-08		14:25:59		73.4		35.5

		23-Mar-08		16:07:10		66.2		36		23-Mar-08		16:06:20		65.6		36		23-Mar-08		16:07:53		71		38.5		3-May-08		16:25:59		74.01		35

		23-Mar-08		18:07:10		66.2		43.5		23-Mar-08		18:06:20		66.2		42		23-Mar-08		18:07:53		70.41		40		3-May-08		18:25:59		73.4		36.5

		23-Mar-08		20:07:10		65.6		44		23-Mar-08		20:06:20		65.6		45.5		23-Mar-08		20:07:53		69.8		41.5		3-May-08		20:25:59		74.01		36.5

		23-Mar-08		22:07:10		65.6		48		23-Mar-08		22:06:20		65.01		46.5		23-Mar-08		22:07:53		71		39.5		3-May-08		22:25:59		74.01		35

		24-Mar-08		0:07:10		65.6		47.5		24-Mar-08		0:06:20		65.01		44.5		24-Mar-08		0:07:53		71		37.5		4-May-08		0:25:59		72.21		34.5

		24-Mar-08		2:07:10		65.6		43		24-Mar-08		2:06:20		65.6		41		24-Mar-08		2:07:53		69.8		36		4-May-08		2:25:59		70.41		35

		24-Mar-08		4:07:10		65.6		47.5		24-Mar-08		4:06:20		65.01		39.5		24-Mar-08		4:07:53		68.61		36		4-May-08		4:25:59		69.2		34.5

		24-Mar-08		6:07:10		65.01		47.5		24-Mar-08		6:06:20		64.4		38.5		24-Mar-08		6:07:53		68		35.5		4-May-08		6:25:59		69.2		34.5

		24-Mar-08		8:07:10		65.01		36		24-Mar-08		8:06:20		63.8		36.5		24-Mar-08		8:07:53		66.81		35		4-May-08		8:25:59		69.8		35

		24-Mar-08		10:07:10		65.6		47.5		24-Mar-08		10:06:20		65.6		39		24-Mar-08		10:07:53		69.8		35		4-May-08		10:25:59		71.6		37

		24-Mar-08		12:07:10		65.6		39.5		24-Mar-08		12:06:20		66.2		38		24-Mar-08		12:07:53		70.41		36.5		4-May-08		12:25:59		73.4		37

		24-Mar-08		14:07:10		66.2		43.5		24-Mar-08		14:06:20		65.6		39		24-Mar-08		14:07:53		69.8		39		4-May-08		14:25:59		74.6		38

		24-Mar-08		16:07:10		66.2		47.5		24-Mar-08		16:06:20		65.6		45.5		24-Mar-08		16:07:53		70.41		42		4-May-08		16:25:59		74.01		38

		24-Mar-08		18:07:10		66.2		45.5		24-Mar-08		18:06:20		66.2		50		24-Mar-08		18:07:53		69.8		45		4-May-08		18:25:59		73.4		40.5

		24-Mar-08		20:07:10		65.6		47.5		24-Mar-08		20:06:20		66.2		45.5		24-Mar-08		20:07:53		71		42.5		4-May-08		20:25:59		73.4		40

		24-Mar-08		22:07:10		65.6		43		24-Mar-08		22:06:20		65.6		45		24-Mar-08		22:07:53		71.6		39.5		4-May-08		22:25:59		72.8		39

		25-Mar-08		0:07:10		65.6		42.5		25-Mar-08		0:06:20		65.01		46		25-Mar-08		0:07:53		71		38.5		5-May-08		0:25:59		71.6		38.5

		25-Mar-08		2:07:10		65.6		41		25-Mar-08		2:06:20		65.6		42		25-Mar-08		2:07:53		69.8		37.5		5-May-08		2:25:59		71		38

		25-Mar-08		4:07:10		65.6		46		25-Mar-08		4:06:20		65.6		42.5		25-Mar-08		4:07:53		69.2		37		5-May-08		4:25:59		69.8		37.5

		25-Mar-08		6:07:10		65.6		39.5		25-Mar-08		6:06:20		65.6		41		25-Mar-08		6:07:53		69.8		37.5		5-May-08		6:25:59		68.61		37.5

		25-Mar-08		8:07:10		65.6		40		25-Mar-08		8:06:20		65.6		41.5		25-Mar-08		8:07:53		71.6		37		5-May-08		8:25:59		68.61		38

		25-Mar-08		10:07:10		66.2		44.5		25-Mar-08		10:06:20		66.2		49		25-Mar-08		10:07:53		70.41		44.5		5-May-08		10:25:59		69.8		40.5

		25-Mar-08		12:07:10		66.81		46.5		25-Mar-08		12:06:20		66.2		53.5		25-Mar-08		12:07:53		71.6		38.5		5-May-08		12:25:59		71.6		41.5

		25-Mar-08		14:07:10		66.81		47.5		25-Mar-08		14:06:20		66.2		59.5		25-Mar-08		14:07:53		71		46		5-May-08		14:25:59		72.8		41.5

		25-Mar-08		16:07:10		66.81		48.5		25-Mar-08		16:06:20		65.6		53.5		25-Mar-08		16:07:53		71		49		5-May-08		16:25:59		73.4		40.5

		25-Mar-08		18:07:10		66.2		47		25-Mar-08		18:06:20		65.6		57.5		25-Mar-08		18:07:53		70.41		50.5		5-May-08		18:25:59		73.4		39.5

		25-Mar-08		20:07:10		66.2		45.5		25-Mar-08		20:06:20		65.6		55		25-Mar-08		20:07:53		70.41		51		5-May-08		20:25:59		72.8		39

		25-Mar-08		22:07:10		65.6		45		25-Mar-08		22:06:20		65.6		51		25-Mar-08		22:07:53		70.41		46		5-May-08		22:25:59		72.21		38

		26-Mar-08		0:07:10		65.6		44		26-Mar-08		0:06:20		65.6		49		26-Mar-08		0:07:53		69.8		42.5		6-May-08		0:25:59		71.6		37.5

		26-Mar-08		2:07:10		65.6		43		26-Mar-08		2:06:20		65.6		47.5		26-Mar-08		2:07:53		69.8		40.5		6-May-08		2:25:59		70.41		38

		26-Mar-08		4:07:10		65.6		42		26-Mar-08		4:06:20		65.6		45.5		26-Mar-08		4:07:53		69.8		39		6-May-08		4:25:59		69.2		37.5

		26-Mar-08		6:07:10		65.6		43		26-Mar-08		6:06:20		64.4		49.5		26-Mar-08		6:07:53		70.41		40.5		6-May-08		6:25:59		69.8		37.5

		26-Mar-08		8:07:10		66.2		44		26-Mar-08		8:06:20		65.6		50.5		26-Mar-08		8:07:53		71.6		41.5		6-May-08		8:25:59		69.8		40

		26-Mar-08		10:07:10		66.2		45		26-Mar-08		10:06:20		65.01		53		26-Mar-08		10:07:53		71		45.5		6-May-08		10:25:59		72.21		41.5

		26-Mar-08		12:07:10		66.2		46		26-Mar-08		12:06:20		65.6		53.5		26-Mar-08		12:07:53		71		49		6-May-08		12:25:59		73.4		43.5

		26-Mar-08		14:07:10		66.81		45.5		26-Mar-08		14:06:20		65.6		53.5		26-Mar-08		14:07:53		71		48.5		6-May-08		14:25:59		73.4		43

		26-Mar-08		16:07:10		66.2		44		26-Mar-08		16:06:20		66.2		50.5		26-Mar-08		16:07:53		70.41		39.5		6-May-08		16:25:59		74.01		43

		26-Mar-08		18:07:10		65.6		43		26-Mar-08		18:06:20		66.2		45		26-Mar-08		18:07:53		70.41		48		6-May-08		18:25:59		74.01		40

		26-Mar-08		20:07:10		65.6		41		26-Mar-08		20:06:20		65.6		41.5		26-Mar-08		20:07:53		70.41		43.5		6-May-08		20:25:59		73.4		40

		26-Mar-08		22:07:10		65.6		40.5		26-Mar-08		22:06:20		64.4		44		26-Mar-08		22:07:53		72.21		37.5		6-May-08		22:25:59		72.21		39.5

		27-Mar-08		0:07:10		65.6		41		27-Mar-08		0:06:20		65.6		43		27-Mar-08		0:07:53		71.6		36.5		7-May-08		0:25:59		71.6		40

		27-Mar-08		2:07:10		65.01		39.5		27-Mar-08		2:06:20		64.4		42.5		27-Mar-08		2:07:53		70.41		36		7-May-08		2:25:59		71		40

		27-Mar-08		4:07:10		65.01		38		27-Mar-08		4:06:20		63.8		41.5		27-Mar-08		4:07:53		69.8		35		7-May-08		4:25:59		69.8		40

		27-Mar-08		6:07:10		65.01		37		27-Mar-08		6:06:20		63.8		40.5		27-Mar-08		6:07:53		70.41		35		7-May-08		6:25:59		71		40.5

		27-Mar-08		8:07:10		65.6		37		27-Mar-08		8:06:20		63.8		39		27-Mar-08		8:07:53		71.6		34.5		7-May-08		8:25:59		71.6		41.5

		27-Mar-08		10:07:10		65.6		40		27-Mar-08		10:06:20		66.2		41		27-Mar-08		10:07:53		71.6		35		7-May-08		10:25:59		73.4		41

		27-Mar-08		12:07:10		65.6		39		27-Mar-08		12:06:20		69.2		36.5		27-Mar-08		12:07:53		71		42		7-May-08		12:25:59		73.4		43

		27-Mar-08		14:07:10		66.2		40		27-Mar-08		14:06:20		69.2		37		27-Mar-08		14:07:53		71		35.5		7-May-08		14:25:59		73.4		45.5

		27-Mar-08		16:07:10		65.6		43		27-Mar-08		16:06:20		68.61		41.5		27-Mar-08		16:07:53		70.41		37		7-May-08		16:25:59		73.4		44.5

		27-Mar-08		18:07:10		65.6		41		27-Mar-08		18:06:20		68.61		38		27-Mar-08		18:07:53		70.41		42		7-May-08		18:25:59		73.4		43

		27-Mar-08		20:07:10		65.6		40		27-Mar-08		20:06:20		68		38.5		27-Mar-08		20:07:53		72.8		36		7-May-08		20:25:59		74.01		42

		27-Mar-08		22:07:10		65.6		37.5		27-Mar-08		22:06:20		66.81		36		27-Mar-08		22:07:53		74.6		32		7-May-08		22:25:59		74.01		37.5

		28-Mar-08		0:07:10		65.01		36.5		28-Mar-08		0:06:20		65.6		36.5		28-Mar-08		0:07:53		71.6		32.5		8-May-08		0:25:59		73.4		37

		28-Mar-08		2:07:10		65.01		35		28-Mar-08		2:06:20		64.4		35.5		28-Mar-08		2:07:53		69.8		32		8-May-08		2:25:59		71.6		37

		28-Mar-08		4:07:10		65.01		33.5		28-Mar-08		4:06:20		63.8		35		28-Mar-08		4:07:53		68.61		31.5		8-May-08		4:25:59		70.41		37.5

		28-Mar-08		6:07:10		65.01		33		28-Mar-08		6:06:20		63.21		35		28-Mar-08		6:07:53		69.2		32		8-May-08		6:25:59		73.4		35.5

		28-Mar-08		8:07:10		65.6		32		28-Mar-08		8:06:20		64.4		34		28-Mar-08		8:07:53		70.41		32		8-May-08		8:25:59		72.8		35.5

		28-Mar-08		10:07:10		65.6		30.5		28-Mar-08		10:06:20		66.2		31		28-Mar-08		10:07:53		71		33		8-May-08		10:25:59		72.8		37.5

		28-Mar-08		12:07:10		65.6		28		28-Mar-08		12:06:20		68.61		27		28-Mar-08		12:07:53		71		29.5		8-May-08		12:25:59		72.8		38.5

		28-Mar-08		14:07:10		66.2		28		28-Mar-08		14:06:20		69.2		25.5		28-Mar-08		14:07:53		70.41		32.5		8-May-08		14:25:59		73.4		39.5

		28-Mar-08		16:07:10		66.2		23.5		28-Mar-08		16:06:20		69.2		22		28-Mar-08		16:07:53		70.41		28.5		8-May-08		16:25:59		74.01		39.5

		28-Mar-08		18:07:10		65.6		24.5		28-Mar-08		18:06:20		69.2		21		28-Mar-08		18:07:53		71		26.5		8-May-08		18:25:59		73.4		39

		28-Mar-08		20:07:10		65.6		26		28-Mar-08		20:06:20		68.61		23.5		28-Mar-08		20:07:53		71.6		26.5		8-May-08		20:25:59		74.01		39.5

		28-Mar-08		22:07:10		65.01		35		28-Mar-08		22:06:20		67.4		34		28-Mar-08		22:07:53		74.6		28.5		8-May-08		22:25:59		74.01		37.5

		29-Mar-08		0:07:10		65.01		35		29-Mar-08		0:06:20		65.6		35.5		29-Mar-08		0:07:53		72.8		29.5		9-May-08		0:25:59		72.8		37

		29-Mar-08		2:07:10		65.01		36		29-Mar-08		2:06:20		65.01		37.5		29-Mar-08		2:07:53		71		30.5		9-May-08		2:25:59		71		36.5

		29-Mar-08		4:07:10		65.01		35.5		29-Mar-08		4:06:20		64.4		37.5		29-Mar-08		4:07:53		69.8		31		9-May-08		4:25:59		69.2		36.5

		29-Mar-08		6:07:10		65.6		34.5		29-Mar-08		6:06:20		64.4		37		29-Mar-08		6:07:53		70.41		33		9-May-08		6:25:59		72.8		35.5

		29-Mar-08		8:07:10		65.01		36.5		29-Mar-08		8:06:20		65.6		37.5		29-Mar-08		8:07:53		70.41		35		9-May-08		8:25:59		73.4		36.5

		29-Mar-08		10:07:10		65.6		32		29-Mar-08		10:06:20		68		32.5		29-Mar-08		10:07:53		70.41		35.5		9-May-08		10:25:59		73.4		38.5

		29-Mar-08		12:07:10		64.4		39		29-Mar-08		12:06:20		69.2		32		29-Mar-08		12:07:53		71		36.5		9-May-08		12:25:59		72.21		41

		29-Mar-08		14:07:10		66.81		38.5		29-Mar-08		14:06:20		68		38		29-Mar-08		14:07:53		71		44		9-May-08		14:25:59		72.21		41.5

		29-Mar-08		16:07:10		66.81		43		29-Mar-08		16:06:20		65.6		51		29-Mar-08		16:07:53		71		43		9-May-08		16:25:59		73.4		39.5

		29-Mar-08		18:07:10		66.81		44.5		29-Mar-08		18:06:20		64.4		55.5		29-Mar-08		18:07:53		72.21		42.5		9-May-08		18:25:59		72.8		39

		29-Mar-08		20:07:10		66.81		44.5		29-Mar-08		20:06:20		65.01		55		29-Mar-08		20:07:53		71		45.5		9-May-08		20:25:59		73.4		38.5

		29-Mar-08		22:07:10		66.81		45		29-Mar-08		22:06:20		64.4		57		29-Mar-08		22:07:53		70.41		44		9-May-08		22:25:59		72.8		37.5

		30-Mar-08		0:07:10		66.81		45		30-Mar-08		0:06:20		65.01		56		30-Mar-08		0:07:53		70.41		42.5		10-May-08		0:25:59		72.21		36

		30-Mar-08		2:07:10		66.81		44.5		30-Mar-08		2:06:20		65.01		54.5		30-Mar-08		2:07:53		69.8		43		10-May-08		2:25:59		72.21		35

		30-Mar-08		4:07:10		66.81		43.5		30-Mar-08		4:06:20		64.4		53.5		30-Mar-08		4:07:53		69.8		42		10-May-08		4:25:59		72.21		35

		30-Mar-08		6:07:10		66.81		41.5		30-Mar-08		6:06:20		65.01		50		30-Mar-08		6:07:53		69.8		41.5		10-May-08		6:25:59		72.21		34

		30-Mar-08		8:07:10		67.4		40.5		30-Mar-08		8:06:20		65.01		47.5		30-Mar-08		8:07:53		69.8		40		10-May-08		8:25:59		71		36

		30-Mar-08		10:07:10		67.4		39.5		30-Mar-08		10:06:20		64.4		47.5		30-Mar-08		10:07:53		69.8		39.5		10-May-08		10:25:59		73.4		36

		30-Mar-08		12:07:10		68		40.5		30-Mar-08		12:06:20		64.4		48		30-Mar-08		12:07:53		69.8		41		10-May-08		12:25:59		74.6		34.5

		30-Mar-08		14:07:10		67.4		42		30-Mar-08		14:06:20		65.01		51		30-Mar-08		14:07:53		70.41		37.5		10-May-08		14:25:59		75.2		33.5

		30-Mar-08		16:07:10		67.4		40.5		30-Mar-08		16:06:20		65.01		46.5		30-Mar-08		16:07:53		70.41		39		10-May-08		16:25:59		75.2		35.5

		30-Mar-08		18:07:10		67.4		39.5		30-Mar-08		18:06:20		65.01		45.5		30-Mar-08		18:07:53		69.8		43		10-May-08		18:25:59		75.2		35.5

		30-Mar-08		20:07:10		68		37		30-Mar-08		20:06:20		64.4		43		30-Mar-08		20:07:53		70.41		39.5		10-May-08		20:25:59		74.6		36

		30-Mar-08		22:07:10		68		33		30-Mar-08		22:06:20		64.4		37		30-Mar-08		22:07:53		71		35.5		10-May-08		22:25:59		74.6		34.5

		31-Mar-08		0:07:10		68		32		31-Mar-08		0:06:20		65.01		35		31-Mar-08		0:07:53		69.8		33		11-May-08		0:25:59		74.01		34

		31-Mar-08		2:07:10		67.4		32		31-Mar-08		2:06:20		64.4		35.5		31-Mar-08		2:07:53		69.8		32.5		11-May-08		2:25:59		72.21		34

		31-Mar-08		4:07:10		67.4		32.5		31-Mar-08		4:06:20		63.8		37		31-Mar-08		4:07:53		68.61		32.5		11-May-08		4:25:59		71.6		34

		31-Mar-08		6:07:10		68		32.5		31-Mar-08		6:06:20		63.21		38.5		31-Mar-08		6:07:53		68		33		11-May-08		6:25:59		72.21		34

		31-Mar-08		8:07:10		67.4		31		31-Mar-08		8:06:20		63.8		36		31-Mar-08		8:07:53		68		32.5		11-May-08		8:25:59		72.21		34.5

		31-Mar-08		10:07:10		67.4		28.5		31-Mar-08		10:06:20		64.4		32		31-Mar-08		10:07:53		69.2		31		11-May-08		10:25:59		72.8		35

		31-Mar-08		12:07:10		67.4		25.5		31-Mar-08		12:06:20		64.4		29.5		31-Mar-08		12:07:53		69.8		29.5		11-May-08		12:25:59		74.01		35

		31-Mar-08		14:07:10		68		23.5		31-Mar-08		14:06:20		65.01		25.5		31-Mar-08		14:07:53		69.8		27.5		11-May-08		14:25:59		75.81		35.5

		31-Mar-08		16:07:10		67.4		24		31-Mar-08		16:06:20		65.01		26		31-Mar-08		16:07:53		69.2		28		11-May-08		16:25:59		77		34.5

		31-Mar-08		18:07:10		67.4		26.5		31-Mar-08		18:06:20		65.01		29.5		31-Mar-08		18:07:53		69.8		28.5		11-May-08		18:25:59		78.2		35

		31-Mar-08		20:07:10		68		26.5		31-Mar-08		20:06:20		64.4		30		31-Mar-08		20:07:53		71		28.5		11-May-08		20:25:59		77.61		36

		31-Mar-08		22:07:10		67.4		27		31-Mar-08		22:06:20		64.4		30.5		31-Mar-08		22:07:53		70.41		27.5		11-May-08		22:25:59		75.81		37

		1-Apr-08		0:07:10		67.4		27.5		1-Apr-08		0:06:20		64.4		31.5		1-Apr-08		0:07:53		69.2		27.5		12-May-08		0:25:59		74.01		37.5

		1-Apr-08		2:07:10		67.4		28		1-Apr-08		2:06:20		63.8		32.5		1-Apr-08		2:07:53		68.61		28		12-May-08		2:25:59		72.8		38

		1-Apr-08		4:07:10		67.4		28		1-Apr-08		4:06:20		62.6		32.5		1-Apr-08		4:07:53		67.4		28.5		12-May-08		4:25:59		72.21		38

		1-Apr-08		6:07:10		67.4		28.5		1-Apr-08		6:06:20		62		34		1-Apr-08		6:07:53		66.81		29.5		12-May-08		6:25:59		72.21		37.5

		1-Apr-08		8:07:10		68		28.5		1-Apr-08		8:06:20		63.21		34		1-Apr-08		8:07:53		69.8		29.5		12-May-08		8:25:59		72.21		38.5

		1-Apr-08		10:07:10		67.4		30.5		1-Apr-08		10:06:20		65.01		34.5		1-Apr-08		10:07:53		71		31.5		12-May-08		10:25:59		71.6		40

		1-Apr-08		12:07:10		66.81		27		1-Apr-08		12:06:20		65.6		30		1-Apr-08		12:07:53		71		34		12-May-08		12:25:59		72.8		41

		1-Apr-08		14:07:10		66.81		30		1-Apr-08		14:06:20		66.2		31		1-Apr-08		14:07:53		71		35		12-May-08		14:25:59		74.01		36

		1-Apr-08		16:07:10		66.81		31		1-Apr-08		16:06:20		65.6		34		1-Apr-08		16:07:53		71		36.5		12-May-08		16:25:59		74.6		32

		1-Apr-08		18:07:10		66.81		29.5		1-Apr-08		18:06:20		65.01		32.5		1-Apr-08		18:07:53		71		33.5		12-May-08		18:25:59		76.4		31

		1-Apr-08		20:07:10		67.4		30.5		1-Apr-08		20:06:20		65.01		32.5		1-Apr-08		20:07:53		70.41		32		12-May-08		20:25:59		75.81		31.5

		1-Apr-08		22:07:10		67.4		29		1-Apr-08		22:06:20		64.4		32		1-Apr-08		22:07:53		70.41		32		12-May-08		22:25:59		74.01		31

		2-Apr-08		0:07:10		66.81		33		2-Apr-08		0:06:20		65.01		37		2-Apr-08		0:07:53		70.41		31		13-May-08		0:25:59		72.8		31

		2-Apr-08		2:07:10		66.81		34		2-Apr-08		2:06:20		64.4		38.5		2-Apr-08		2:07:53		70.41		31		13-May-08		2:25:59		71.6		31

		2-Apr-08		4:07:10		66.81		33		2-Apr-08		4:06:20		64.4		38		2-Apr-08		4:07:53		70.41		32		13-May-08		4:25:59		71.6		31

		2-Apr-08		6:07:10		66.81		31.5		2-Apr-08		6:06:20		65.01		35		2-Apr-08		6:07:53		71		32		13-May-08		6:25:59		71.6		30

		2-Apr-08		8:07:10		66.81		33.5		2-Apr-08		8:06:20		65.01		37.5		2-Apr-08		8:07:53		71.6		33.5		13-May-08		8:25:59		71.6		30

		2-Apr-08		10:07:10		66.81		33.5		2-Apr-08		10:06:20		66.2		35.5		2-Apr-08		10:07:53		70.41		35		13-May-08		10:25:59		74.01		29.5

		2-Apr-08		12:07:10		66.81		33		2-Apr-08		12:06:20		66.81		33		2-Apr-08		12:07:53		71		36		13-May-08		12:25:59		74.01		29.5

		2-Apr-08		14:07:10		66.81		39		2-Apr-08		14:06:20		67.4		42.5		2-Apr-08		14:07:53		71.6		34.5		13-May-08		14:25:59		75.2		29.5

		2-Apr-08		16:07:10		67.4		34		2-Apr-08		16:06:20		67.4		31.5		2-Apr-08		16:07:53		71.6		36.5		13-May-08		16:25:59		75.2		30

		2-Apr-08		18:07:10		66.81		35		2-Apr-08		18:06:20		66.2		36		2-Apr-08		18:07:53		71		32.5		13-May-08		18:25:59		75.2		30

		2-Apr-08		20:07:10		67.4		36.5		2-Apr-08		20:06:20		66.81		37		2-Apr-08		20:07:53		71		37		13-May-08		20:25:59		74.6		30.5

		2-Apr-08		22:07:10		66.81		37.5		2-Apr-08		22:06:20		65.6		41.5		2-Apr-08		22:07:53		75.2		33		13-May-08		22:25:59		74.01		29.5

		3-Apr-08		0:07:10		66.81		37.5		3-Apr-08		0:06:20		66.2		42		3-Apr-08		0:07:53		71.6		34		14-May-08		0:25:59		73.4		29.5

		3-Apr-08		2:07:10		66.81		36.5		3-Apr-08		2:06:20		65.6		40.5		3-Apr-08		2:07:53		70.41		34.5		14-May-08		2:25:59		72.21		30

		3-Apr-08		4:07:10		67.4		34.5		3-Apr-08		4:06:20		64.4		38.5		3-Apr-08		4:07:53		69.2		33.5		14-May-08		4:25:59		71.6		30.5

		3-Apr-08		6:07:10		67.4		35.5		3-Apr-08		6:06:20		64.4		38		3-Apr-08		6:07:53		69.2		33		14-May-08		6:25:59		72.21		31

		3-Apr-08		8:07:10		67.4		35.5		3-Apr-08		8:06:20		65.01		38.5		3-Apr-08		8:07:53		71		31		14-May-08		8:25:59		71.6		32.5

		3-Apr-08		10:07:10		65.01		39		3-Apr-08		10:06:20		66.2		41		3-Apr-08		10:07:53		71.6		34.5		14-May-08		10:25:59		74.6		33

		3-Apr-08		12:07:10		66.81		38		3-Apr-08		12:06:20		66.81		39		3-Apr-08		12:07:53		71		34.5		14-May-08		12:25:59		74.01		32

		3-Apr-08		14:07:10		66.81		40		3-Apr-08		14:06:20		67.4		41.5		3-Apr-08		14:07:53		71		38		14-May-08		14:25:59		74.01		30.5

		3-Apr-08		16:07:10		66.81		38		3-Apr-08		16:06:20		66.2		40		3-Apr-08		16:07:53		71.6		42.5		14-May-08		16:25:59		74.6		29

		3-Apr-08		18:07:10		66.81		35.5		3-Apr-08		18:06:20		66.81		36		3-Apr-08		18:07:53		71		32		14-May-08		18:25:59		74.01		29

		3-Apr-08		20:07:10		67.4		35.5		3-Apr-08		20:06:20		66.2		37.5		3-Apr-08		20:07:53		71		32.5		14-May-08		20:25:59		74.6		33

		3-Apr-08		22:07:10		67.4		34.5		3-Apr-08		22:06:20		65.6		37		3-Apr-08		22:07:53		72.21		34		14-May-08		22:25:59		75.2		33

		4-Apr-08		0:07:10		67.4		34.5		4-Apr-08		0:06:20		66.2		37.5		4-Apr-08		0:07:53		72.21		33.5		15-May-08		0:25:59		74.6		33.5

		4-Apr-08		2:07:10		66.81		34		4-Apr-08		2:06:20		65.6		36.5		4-Apr-08		2:07:53		70.41		32.5		15-May-08		2:25:59		74.01		34

		4-Apr-08		4:07:10		66.81		35		4-Apr-08		4:06:20		65.01		38		4-Apr-08		4:07:53		69.8		32		15-May-08		4:25:59		73.4		35

		4-Apr-08		6:07:10		66.81		37		4-Apr-08		6:06:20		65.6		40.5		4-Apr-08		6:07:53		69.8		34		15-May-08		6:25:59		73.4		36.5

		4-Apr-08		8:07:10		67.4		37.5		4-Apr-08		8:06:20		66.81		42		4-Apr-08		8:07:53		72.21		33.5		15-May-08		8:25:59		73.4		39

		4-Apr-08		10:07:10		68		38.5		4-Apr-08		10:06:20		66.81		42		4-Apr-08		10:07:53		71.6		36		15-May-08		10:25:59		74.6		40

		4-Apr-08		12:07:10		74.6		35		4-Apr-08		12:06:20		74.6		35.5		4-Apr-08		12:07:53		71.6		42.5		15-May-08		12:25:59		74.01		41.5

		4-Apr-08		14:07:10		66.81		38.5		4-Apr-08		14:06:20		67.4		38.5		4-Apr-08		14:07:53		71.6		45		15-May-08		14:25:59		74.01		38.5

		4-Apr-08		16:07:10		66.81		42		4-Apr-08		16:06:20		66.81		45		4-Apr-08		16:07:53		71		45		15-May-08		16:25:59		74.01		38.5

		4-Apr-08		18:07:10		66.81		40.5		4-Apr-08		18:06:20		66.81		43.5		4-Apr-08		18:07:53		71.6		44		15-May-08		18:25:59		73.4		38.5

		4-Apr-08		20:07:10		66.81		45.5		4-Apr-08		20:06:20		65.6		44		4-Apr-08		20:07:53		71.6		43		15-May-08		20:25:59		75.2		38.5

		4-Apr-08		22:07:10		66.81		45.5		4-Apr-08		22:06:20		66.2		43		4-Apr-08		22:07:53		71.6		35.5		15-May-08		22:25:59		76.4		36

		5-Apr-08		0:07:10		67.4		45		5-Apr-08		0:06:20		65.6		42		5-Apr-08		0:07:53		71		39.5		16-May-08		0:25:59		76.4		35.5

		5-Apr-08		2:07:10		66.81		46.5		5-Apr-08		2:06:20		65.01		43.5		5-Apr-08		2:07:53		70.41		37.5		16-May-08		2:25:59		75.81		35.5

		5-Apr-08		4:07:10		66.81		46.5		5-Apr-08		4:06:20		65.01		44.5		5-Apr-08		4:07:53		69.8		38		16-May-08		4:25:59		75.2		35.5

		5-Apr-08		6:07:10		66.81		46		5-Apr-08		6:06:20		65.01		43		5-Apr-08		6:07:53		70.41		39		16-May-08		6:25:59		75.2		35

		5-Apr-08		8:07:10		68		43.5		5-Apr-08		8:06:20		65.6		43.5		5-Apr-08		8:07:53		71		41		16-May-08		8:25:59		74.6		36.5

		5-Apr-08		10:07:10		67.4		47		5-Apr-08		10:06:20		67.4		40		5-Apr-08		10:07:53		70.41		39		16-May-08		10:25:59		74.01		38.5

		5-Apr-08		12:07:10		67.4		45.5		5-Apr-08		12:06:20		67.4		38.5		5-Apr-08		12:07:53		71		44		16-May-08		12:25:59		73.4		40.5

		5-Apr-08		14:07:10		66.81		47		5-Apr-08		14:06:20		68.61		40.5		5-Apr-08		14:07:53		74.6		35.5		16-May-08		14:25:59		72.8		40.5

		5-Apr-08		16:07:10		66.81		46		5-Apr-08		16:06:20		67.4		43		5-Apr-08		16:07:53		71.6		45.5		16-May-08		16:25:59		73.4		40.5

		5-Apr-08		18:07:10		66.81		46.5		5-Apr-08		18:06:20		66.81		40		5-Apr-08		18:07:53		73.4		40		16-May-08		18:25:59		74.01		40.5

		5-Apr-08		20:07:10		67.4		46.5		5-Apr-08		20:06:20		67.4		40.5		5-Apr-08		20:07:53		75.2		37		16-May-08		20:25:59		75.2		40.5

		5-Apr-08		22:07:10		66.81		46		5-Apr-08		22:06:20		67.4		36.5		5-Apr-08		22:07:53		73.4		36.5		16-May-08		22:25:59		77		40

		6-Apr-08		0:07:10		66.81		46		6-Apr-08		0:06:20		66.81		37		6-Apr-08		0:07:53		71		36		17-May-08		0:25:59		76.4		39

		6-Apr-08		2:07:10		66.81		46.5		6-Apr-08		2:06:20		65.6		37.5		6-Apr-08		2:07:53		69.8		35.5		17-May-08		2:25:59		75.2		39

		6-Apr-08		4:07:10		66.81		47		6-Apr-08		4:06:20		65.01		38		6-Apr-08		4:07:53		68.61		36		17-May-08		4:25:59		74.6		39

		6-Apr-08		6:07:10		67.4		46		6-Apr-08		6:06:20		65.01		37.5		6-Apr-08		6:07:53		67.4		36.5		17-May-08		6:25:59		74.6		40

		6-Apr-08		8:07:10		67.4		47		6-Apr-08		8:06:20		65.01		37.5		6-Apr-08		8:07:53		67.4		36.5		17-May-08		8:25:59		74.6		41.5

		6-Apr-08		10:07:10		67.4		45		6-Apr-08		10:06:20		66.81		37		6-Apr-08		10:07:53		69.2		36.5		17-May-08		10:25:59		74.01		43

		6-Apr-08		12:07:10		67.4		46		6-Apr-08		12:06:20		68		35.5		6-Apr-08		12:07:53		70.41		36.5		17-May-08		12:25:59		73.4		46.5

		6-Apr-08		14:07:10		67.4		46		6-Apr-08		14:06:20		68		37		6-Apr-08		14:07:53		70.41		39		17-May-08		14:25:59		74.01		45.5

		6-Apr-08		16:07:10		68		45.5		6-Apr-08		16:06:20		68		39		6-Apr-08		16:07:53		70.41		40.5		17-May-08		16:25:59		74.01		45

		6-Apr-08		18:07:10		67.4		46.5		6-Apr-08		18:06:20		67.4		38.5		6-Apr-08		18:07:53		71		40		17-May-08		18:25:59		73.4		42.5

		6-Apr-08		20:07:10		68		45.5		6-Apr-08		20:06:20		67.4		39.5		6-Apr-08		20:07:53		72.21		38		17-May-08		20:25:59		75.2		42.5

		6-Apr-08		22:07:10		67.4		43.5		6-Apr-08		22:06:20		67.4		39.5		6-Apr-08		22:07:53		71.6		37		17-May-08		22:25:59		75.81		40

		7-Apr-08		0:07:10		67.4		44		7-Apr-08		0:06:20		66.81		39		7-Apr-08		0:07:53		71		36.5		18-May-08		0:25:59		75.2		39.5

		7-Apr-08		2:07:10		68		46		7-Apr-08		2:06:20		66.2		37.5		7-Apr-08		2:07:53		69.8		36		18-May-08		2:25:59		74.6		40

		7-Apr-08		4:07:10		67.4		45		7-Apr-08		4:06:20		65.6		38		7-Apr-08		4:07:53		69.2		36.5		18-May-08		4:25:59		73.4		40

		7-Apr-08		6:07:10		67.4		45.5		7-Apr-08		6:06:20		65.6		38		7-Apr-08		6:07:53		68.61		37		18-May-08		6:25:59		73.4		39.5

		7-Apr-08		8:07:10		67.4		46.5		7-Apr-08		8:06:20		65.6		39		7-Apr-08		8:07:53		68		37		18-May-08		8:25:59		74.01		40.5

		7-Apr-08		10:07:10		67.4		46		7-Apr-08		10:06:20		66.81		40		7-Apr-08		10:07:53		69.8		37.5		18-May-08		10:25:59		75.81		41.5

		7-Apr-08		12:07:10		68		45		7-Apr-08		12:06:20		66.81		44		7-Apr-08		12:07:53		69.8		39		18-May-08		12:25:59		77.61		42

		7-Apr-08		14:07:10		67.4		45		7-Apr-08		14:06:20		67.4		36		7-Apr-08		14:07:53		71		37		18-May-08		14:25:59		79.41		43

		7-Apr-08		16:07:10		67.4		45.5		7-Apr-08		16:06:20		66.81		35.5		7-Apr-08		16:07:53		71.6		35.5		18-May-08		16:25:59		79.41		41.5

		7-Apr-08		18:07:10		67.4		45.5		7-Apr-08		18:06:20		67.4		33		7-Apr-08		18:07:53		72.21		34.5		18-May-08		18:25:59		78.2		41.5

		7-Apr-08		20:07:10		67.4		44.5		7-Apr-08		20:06:20		66.81		31.5		7-Apr-08		20:07:53		71.6		33		18-May-08		20:25:59		77.61		41

		7-Apr-08		22:07:10		68		46		7-Apr-08		22:06:20		67.4		32.5		7-Apr-08		22:07:53		71		33		18-May-08		22:25:59		76.4		40

		8-Apr-08		0:07:10		67.4		44.5		8-Apr-08		0:06:20		66.81		34		8-Apr-08		0:07:53		69.8		33		19-May-08		0:25:59		74.6		39.5

		8-Apr-08		2:07:10		67.4		46.5		8-Apr-08		2:06:20		66.2		35.5		8-Apr-08		2:07:53		69.2		34		19-May-08		2:25:59		73.4		39

		8-Apr-08		4:07:10		67.4		45.5		8-Apr-08		4:06:20		65.6		35.5		8-Apr-08		4:07:53		68		34.5		19-May-08		4:25:59		72.21		39

		8-Apr-08		6:07:10		67.4		46		8-Apr-08		6:06:20		65.01		35		8-Apr-08		6:07:53		68		35		19-May-08		6:25:59		72.21		39.5

		8-Apr-08		8:07:10		67.4		46.5		8-Apr-08		8:06:20		66.2		35		8-Apr-08		8:07:53		71.6		35		19-May-08		8:25:59		72.21		40

		8-Apr-08		10:07:10		67.4		45		8-Apr-08		10:06:20		68		31.5		8-Apr-08		10:07:53		71.6		33.5		19-May-08		10:25:59		72.8		41.5

		8-Apr-08		12:07:10		66.81		46.5		8-Apr-08		12:06:20		68		29.5		8-Apr-08		12:07:53		71.6		34.5		19-May-08		12:25:59		74.6		41.5

		8-Apr-08		14:07:10		66.81		47		8-Apr-08		14:06:20		67.4		28.5		8-Apr-08		14:07:53		71		34.5		19-May-08		14:25:59		75.81		42

		8-Apr-08		16:07:10		66.81		46.5		8-Apr-08		16:06:20		67.4		35		8-Apr-08		16:07:53		71		37		19-May-08		16:25:59		77		41.5

		8-Apr-08		18:07:10		66.81		46		8-Apr-08		18:06:20		66.81		33		8-Apr-08		18:07:53		71.6		35		19-May-08		18:25:59		77.61		40

		8-Apr-08		20:07:10		66.81		46.5		8-Apr-08		20:06:20		66.81		38.5		8-Apr-08		20:07:53		71		34.5		19-May-08		20:25:59		77		39.5

		8-Apr-08		22:07:10		67.4		47		8-Apr-08		22:06:20		66.2		34		8-Apr-08		22:07:53		71.6		37.5		19-May-08		22:25:59		74.6		39.5

		9-Apr-08		0:07:10		66.81		45.5		9-Apr-08		0:06:20		66.2		38		9-Apr-08		0:07:53		71		35.5		20-May-08		0:25:59		73.4		40

		9-Apr-08		2:07:10		66.81		48		9-Apr-08		2:06:20		66.2		35.5		9-Apr-08		2:07:53		70.41		35		20-May-08		2:25:59		72.21		40

		9-Apr-08		4:07:10		66.81		47.5		9-Apr-08		4:06:20		66.2		36		9-Apr-08		4:07:53		69.8		34.5		20-May-08		4:25:59		72.21		40

		9-Apr-08		6:07:10		66.81		44		9-Apr-08		6:06:20		66.2		37		9-Apr-08		6:07:53		69.8		35.5		20-May-08		6:25:59		72.21		40.5

		9-Apr-08		8:07:10		66.81		47.5		9-Apr-08		8:06:20		66.81		37		9-Apr-08		8:07:53		71		38		20-May-08		8:25:59		71.6		42

		9-Apr-08		10:07:10		66.81		46		9-Apr-08		10:06:20		67.4		34		9-Apr-08		10:07:53		71		34.5		20-May-08		10:25:59		73.4		42.5

		9-Apr-08		12:07:10		66.81		45		9-Apr-08		12:06:20		68		32		9-Apr-08		12:07:53		71		38.5		20-May-08		12:25:59		74.01		43.5

		9-Apr-08		14:07:10		66.81		45		9-Apr-08		14:06:20		68.61		29.5		9-Apr-08		14:07:53		70.41		38.5		20-May-08		14:25:59		74.01		44.5

		9-Apr-08		16:07:10		66.81		47		9-Apr-08		16:06:20		67.4		36		9-Apr-08		16:07:53		71		41.5		20-May-08		16:25:59		74.6		44

		9-Apr-08		18:07:10		66.81		46.5		9-Apr-08		18:06:20		68		34		9-Apr-08		18:07:53		71.6		39.5		20-May-08		18:25:59		74.01		43.5

		9-Apr-08		20:07:10		67.4		47		9-Apr-08		20:06:20		67.4		33.5		9-Apr-08		20:07:53		75.2		35		20-May-08		20:25:59		74.6		43

		9-Apr-08		22:07:10		66.81		47		9-Apr-08		22:06:20		66.81		34.5		9-Apr-08		22:07:53		72.8		34.5		20-May-08		22:25:59		74.01		41

		10-Apr-08		0:07:10		66.81		47.5		10-Apr-08		0:06:20		66.2		33.5		10-Apr-08		0:07:53		70.41		33.5		21-May-08		0:25:59		72.8		41

		10-Apr-08		2:07:10		66.81		47		10-Apr-08		2:06:20		65.6		34.5		10-Apr-08		2:07:53		69.8		33		21-May-08		2:25:59		72.21		41

		10-Apr-08		4:07:10		66.81		47		10-Apr-08		4:06:20		65.01		34.5		10-Apr-08		4:07:53		69.2		33.5		21-May-08		4:25:59		72.21		41

		10-Apr-08		6:07:10		67.4		46		10-Apr-08		6:06:20		65.6		34.5		10-Apr-08		6:07:53		68.61		34.5		21-May-08		6:25:59		72.21		40.5

		10-Apr-08		8:07:10		66.81		47		10-Apr-08		8:06:20		66.2		34.5		10-Apr-08		8:07:53		69.8		35		21-May-08		8:25:59		72.21		42

		10-Apr-08		10:07:10		66.81		47.5		10-Apr-08		10:06:20		68		34		10-Apr-08		10:07:53		70.41		38		21-May-08		10:25:59		73.4		42.5

		10-Apr-08		12:07:10		66.81		47		10-Apr-08		12:06:20		69.2		34		10-Apr-08		12:07:53		70.41		35		21-May-08		12:25:59		73.4		43

		10-Apr-08		14:07:10		66.81		47.5		10-Apr-08		14:06:20		69.8		36		10-Apr-08		14:07:53		71		42.5		21-May-08		14:25:59		74.01		44

		10-Apr-08		16:07:10		66.81		46.5		10-Apr-08		16:06:20		69.2		39.5		10-Apr-08		16:07:53		70.41		47		21-May-08		16:25:59		74.01		41

		10-Apr-08		18:07:10		66.81		47.5		10-Apr-08		18:06:20		68		32		10-Apr-08		18:07:53		69.8		35.5		21-May-08		18:25:59		74.01		35

		10-Apr-08		20:07:10		66.81		46.5		10-Apr-08		20:06:20		67.4		37		10-Apr-08		20:07:53		70.41		41.5		21-May-08		20:25:59		73.4		34.5

		10-Apr-08		22:07:10		66.81		47		10-Apr-08		22:06:20		67.4		37		10-Apr-08		22:07:53		71		37.5		21-May-08		22:25:59		74.01		35

		11-Apr-08		0:07:10		66.81		47.5		11-Apr-08		0:06:20		68		36.5		11-Apr-08		0:07:53		69.2		38		22-May-08		0:25:59		73.4		34.5

		11-Apr-08		2:07:10		66.81		46.5		11-Apr-08		2:06:20		66.81		36.5		11-Apr-08		2:07:53		69.8		36.5		22-May-08		2:25:59		72.21		34.5

		11-Apr-08		4:07:10		66.81		46.5		11-Apr-08		4:06:20		66.2		37.5		11-Apr-08		4:07:53		69.8		35.5		22-May-08		4:25:59		71.6		34

		11-Apr-08		6:07:10		66.81		46.5		11-Apr-08		6:06:20		65.6		37.5		11-Apr-08		6:07:53		69.2		36.5		22-May-08		6:25:59		72.21		32.5

		11-Apr-08		8:07:10		66.81		47.5		11-Apr-08		8:06:20		66.81		38		11-Apr-08		8:07:53		70.41		38.5		22-May-08		8:25:59		71.6		33.5

		11-Apr-08		10:07:10		66.81		48		11-Apr-08		10:06:20		68		36.5		11-Apr-08		10:07:53		70.41		36		22-May-08		10:25:59		73.4		34

		11-Apr-08		12:07:10		66.2		48.5		11-Apr-08		12:06:20		68.61		35		11-Apr-08		12:07:53		71		39.5		22-May-08		12:25:59		73.4		35

		11-Apr-08		14:07:10		66.81		48		11-Apr-08		14:06:20		68.61		34.5		11-Apr-08		14:07:53		70.41		45.5		22-May-08		14:25:59		74.01		35

		11-Apr-08		16:07:10		66.2		45.5		11-Apr-08		16:06:20		68.61		40		11-Apr-08		16:07:53		70.41		47.5		22-May-08		16:25:59		74.01		35

		11-Apr-08		18:07:10		66.81		48		11-Apr-08		18:06:20		68.61		37.5		11-Apr-08		18:07:53		71		45.5		22-May-08		18:25:59		74.01		34.5

		11-Apr-08		20:07:10		66.81		47.5		11-Apr-08		20:06:20		68.61		39.5		11-Apr-08		20:07:53		70.41		42		22-May-08		20:25:59		73.4		34.5

		11-Apr-08		22:07:10		66.81		47		11-Apr-08		22:06:20		67.4		42.5		11-Apr-08		22:07:53		70.41		43		22-May-08		22:25:59		72.8		33.5

		12-Apr-08		0:07:10		66.81		48		12-Apr-08		0:06:20		68		41.5		12-Apr-08		0:07:53		69.8		41.5		23-May-08		0:25:59		72.21		33

		12-Apr-08		2:07:10		66.81		47		12-Apr-08		2:06:20		66.81		42		12-Apr-08		2:07:53		69.8		39		23-May-08		2:25:59		71		32.5

		12-Apr-08		4:07:10		66.81		47.5		12-Apr-08		4:06:20		66.2		41		12-Apr-08		4:07:53		70.41		38.5		23-May-08		4:25:59		71.6		31.5

		12-Apr-08		6:07:10		66.81		47.5		12-Apr-08		6:06:20		66.2		40.5		12-Apr-08		6:07:53		70.41		38		23-May-08		6:25:59		71.6		30.5

		12-Apr-08		8:07:10		66.81		48.5		12-Apr-08		8:06:20		68		39.5		12-Apr-08		8:07:53		69.8		36		23-May-08		8:25:59		71		31.5

		12-Apr-08		10:07:10		66.81		47.5		12-Apr-08		10:06:20		68.61		43		12-Apr-08		10:07:53		70.41		43		23-May-08		10:25:59		73.4		31

		12-Apr-08		12:07:10		66.81		47		12-Apr-08		12:06:20		68		39		12-Apr-08		12:07:53		69.8		47.5		23-May-08		12:25:59		73.4		29.5

		12-Apr-08		14:07:10		67.4		46.5		12-Apr-08		14:06:20		68.61		33.5		12-Apr-08		14:07:53		70.41		40.5		23-May-08		14:25:59		74.01		29

		12-Apr-08		16:07:10		67.4		48		12-Apr-08		16:06:20		67.4		35		12-Apr-08		16:07:53		72.21		40		23-May-08		16:25:59		74.6		30

		12-Apr-08		18:07:10		67.4		45.5		12-Apr-08		18:06:20		67.4		34		12-Apr-08		18:07:53		68		45		23-May-08		18:25:59		74.01		31

		12-Apr-08		20:07:10		67.4		46.5		12-Apr-08		20:06:20		66.81		32.5		12-Apr-08		20:07:53		68		45		23-May-08		20:25:59		74.01		32

		12-Apr-08		22:07:10		67.4		46.5		12-Apr-08		22:06:20		66.2		38.5		12-Apr-08		22:07:53		68		44		23-May-08		22:25:59		74.6		31.5

		13-Apr-08		0:07:10		67.4		46		13-Apr-08		0:06:20		66.81		41		13-Apr-08		0:07:53		66.81		46		24-May-08		0:25:59		73.4		31.5

		13-Apr-08		2:07:10		67.4		46		13-Apr-08		2:06:20		65.6		42		13-Apr-08		2:07:53		66.81		45.5		24-May-08		2:25:59		72.21		32

		13-Apr-08		4:07:10		68		45.5		13-Apr-08		4:06:20		65.6		41		13-Apr-08		4:07:53		66.2		46.5		24-May-08		4:25:59		71.6		32

		13-Apr-08		6:07:10		68		46.5		13-Apr-08		6:06:20		66.81		40		13-Apr-08		6:07:53		66.2		47		24-May-08		6:25:59		72.21		31.5

		13-Apr-08		8:07:10		67.4		46.5		13-Apr-08		8:06:20		66.2		40.5		13-Apr-08		8:07:53		66.2		47.5		24-May-08		8:25:59		71.6		33

		13-Apr-08		10:07:10		68		47		13-Apr-08		10:06:20		66.81		42		13-Apr-08		10:07:53		66.81		47		24-May-08		10:25:59		74.01		33.5

		13-Apr-08		12:07:10		67.4		46		13-Apr-08		12:06:20		67.4		41.5		13-Apr-08		12:07:53		67.4		45.5		24-May-08		12:25:59		73.4		35

		13-Apr-08		14:07:10		67.4		46.5		13-Apr-08		14:06:20		67.4		43		13-Apr-08		14:07:53		67.4		46		24-May-08		14:25:59		74.01		35

		13-Apr-08		16:07:10		67.4		46		13-Apr-08		16:06:20		66.81		40		13-Apr-08		16:07:53		68		45.5		24-May-08		16:25:59		74.01		34.5

		13-Apr-08		18:07:10		67.4		46.5		13-Apr-08		18:06:20		66.81		38.5		13-Apr-08		18:07:53		67.4		45.5		24-May-08		18:25:59		74.01		34.5

		13-Apr-08		20:07:10		68		46		13-Apr-08		20:06:20		66.2		43.5		13-Apr-08		20:07:53		67.4		46		24-May-08		20:25:59		74.01		35.5

		13-Apr-08		22:07:10		67.4		47.5		13-Apr-08		22:06:20		66.2		53.5		13-Apr-08		22:07:53		67.4		46.5		24-May-08		22:25:59		74.01		35

		14-Apr-08		0:07:10		67.4		46		14-Apr-08		0:06:20		66.2		48.5		14-Apr-08		0:07:53		66.81		47		25-May-08		0:25:59		72.8		35.5

		14-Apr-08		2:07:10		67.4		46		14-Apr-08		2:06:20		66.2		46		14-Apr-08		2:07:53		66.81		47		25-May-08		2:25:59		72.21		36

		14-Apr-08		4:07:10		67.4		46		14-Apr-08		4:06:20		65.6		45.5		14-Apr-08		4:07:53		66.2		47.5		25-May-08		4:25:59		71.6		36.5

		14-Apr-08		6:07:10		68.61		46		14-Apr-08		6:06:20		65.6		44		14-Apr-08		6:07:53		66.2		48		25-May-08		6:25:59		71.6		37

		14-Apr-08		8:07:10		67.4		46		14-Apr-08		8:06:20		66.2		41.5		14-Apr-08		8:07:53		66.2		47		25-May-08		8:25:59		71.6		37.5

		14-Apr-08		10:07:10		68		46		14-Apr-08		10:06:20		66.2		43		14-Apr-08		10:07:53		66.2		48		25-May-08		10:25:59		71.6		38.5

		14-Apr-08		12:07:10		67.4		46		14-Apr-08		12:06:20		67.4		43		14-Apr-08		12:07:53		66.81		47		25-May-08		12:25:59		71.6		40

		14-Apr-08		14:07:10		67.4		48		14-Apr-08		14:06:20		67.4		45.5		14-Apr-08		14:07:53		67.4		48.5		25-May-08		14:25:59		71.6		40.5

		14-Apr-08		16:07:10		67.4		46		14-Apr-08		16:06:20		66.81		43		14-Apr-08		16:07:53		66.81		47		25-May-08		16:25:59		71.6		40

		14-Apr-08		18:07:10		67.4		47		14-Apr-08		18:06:20		66.81		46.5		14-Apr-08		18:07:53		66.81		48		25-May-08		18:25:59		71.6		41

		14-Apr-08		20:07:10		67.4		47		14-Apr-08		20:06:20		66.2		50		14-Apr-08		20:07:53		66.2		48		25-May-08		20:25:59		71.6		41

		14-Apr-08		22:07:10		68		45.5		14-Apr-08		22:06:20		66.2		46		14-Apr-08		22:07:53		66.2		48		25-May-08		22:25:59		71.6		41

		15-Apr-08		0:07:10		67.4		46		15-Apr-08		0:06:20		65.6		49		15-Apr-08		0:07:53		66.81		47		26-May-08		0:25:59		71.6		40

		15-Apr-08		2:07:10		67.4		47		15-Apr-08		2:06:20		66.2		46		15-Apr-08		2:07:53		66.81		47.5		26-May-08		2:25:59		71.6		38.5

		15-Apr-08		4:07:10		67.4		44		15-Apr-08		4:06:20		65.6		45		15-Apr-08		4:07:53		66.81		47.5		26-May-08		4:25:59		71.6		37.5

		15-Apr-08		6:07:10		68		46		15-Apr-08		6:06:20		65.01		45		15-Apr-08		6:07:53		66.2		48		26-May-08		6:25:59		71.6		37

		15-Apr-08		8:07:10		67.4		45.5		15-Apr-08		8:06:20		67.4		45		15-Apr-08		8:07:53		65.6		49.5		26-May-08		8:25:59		71.6		37.5

		15-Apr-08		10:07:10		67.4		47		15-Apr-08		10:06:20		69.2		44		15-Apr-08		10:07:53		65.01		49		26-May-08		10:25:59		71.6		39.5

		15-Apr-08		12:07:10		67.4		47		15-Apr-08		12:06:20		69.8		37.5		15-Apr-08		12:07:53		65.6		49		26-May-08		12:25:59		72.21		38.5

		15-Apr-08		14:07:10		67.4		41		15-Apr-08		14:06:20		71		33.5		15-Apr-08		14:07:53		66.2		47.5		26-May-08		14:25:59		72.8		38

		15-Apr-08		16:07:10		67.4		45.5		15-Apr-08		16:06:20		70.41		32.5		15-Apr-08		16:07:53		66.81		47		26-May-08		16:25:59		73.4		36.5

		15-Apr-08		18:07:10		67.4		45.5		15-Apr-08		18:06:20		69.2		31.5		15-Apr-08		18:07:53		68		45.5		26-May-08		18:25:59		74.01		36

		15-Apr-08		20:07:10		67.4		45		15-Apr-08		20:06:20		69.2		29		15-Apr-08		20:07:53		67.4		45		26-May-08		20:25:59		74.01		35.5

		15-Apr-08		22:07:10		68		45.5		15-Apr-08		22:06:20		68		31.5		15-Apr-08		22:07:53		67.4		45		26-May-08		22:25:59		72.21		37

		16-Apr-08		0:07:10		67.4		37		16-Apr-08		0:06:20		66.81		34.5		16-Apr-08		0:07:53		67.4		45.5		27-May-08		0:25:59		72.21		37.5

		16-Apr-08		2:07:10		67.4		46.5		16-Apr-08		2:06:20		65.6		33		16-Apr-08		2:07:53		68		44.5		27-May-08		2:25:59		71.6		37.5

		16-Apr-08		4:07:10		67.4		45		16-Apr-08		4:06:20		65.01		33		16-Apr-08		4:07:53		68		45		27-May-08		4:25:59		71.6		37.5

		16-Apr-08		6:07:10		67.4		45.5		16-Apr-08		6:06:20		65.01		33.5		16-Apr-08		6:07:53		68		44.5		27-May-08		6:25:59		72.21		37.5

		16-Apr-08		8:07:10		67.4		46		16-Apr-08		8:06:20		68		32.5		16-Apr-08		8:07:53		67.4		44		27-May-08		8:25:59		71		39

		16-Apr-08		10:07:10		69.2		34		16-Apr-08		10:06:20		70.41		30		16-Apr-08		10:07:53		66.2		47.5		27-May-08		10:25:59		71		39.5

		16-Apr-08		12:07:10		69.8		44		16-Apr-08		12:06:20		68.61		27.5		16-Apr-08		12:07:53		66.2		48		27-May-08		12:25:59		72.21		40.5

		16-Apr-08		14:07:10		70.41		43		16-Apr-08		14:06:20		69.8		26		16-Apr-08		14:07:53		66.2		49.5		27-May-08		14:25:59		72.8		40

		16-Apr-08		16:07:10		70.41		46		16-Apr-08		16:06:20		69.2		28		16-Apr-08		16:07:53		67.4		47		27-May-08		16:25:59		72.8		39.5

		16-Apr-08		18:07:10		70.41		45.5		16-Apr-08		18:06:20		68.61		31		16-Apr-08		18:07:53		68		48		27-May-08		18:25:59		72.8		41

		16-Apr-08		20:07:10		69.2		44.5		16-Apr-08		20:06:20		68		30		16-Apr-08		20:07:53		67.4		44.5		27-May-08		20:25:59		72.8		40.5

		16-Apr-08		22:07:10		69.2		44.5		16-Apr-08		22:06:20		68		30		16-Apr-08		22:07:53		68		45		27-May-08		22:25:59		72.21		39.5

		17-Apr-08		0:07:10		70.41		46		17-Apr-08		0:06:20		67.4		31.5		17-Apr-08		0:07:53		68		41		28-May-08		0:25:59		72.21		39.5

		17-Apr-08		2:07:10		70.41		43.5		17-Apr-08		2:06:20		66.2		33		17-Apr-08		2:07:53		68		48.5		28-May-08		2:25:59		72.21		40

		17-Apr-08		4:07:10		69.8		46		17-Apr-08		4:06:20		65.6		34		17-Apr-08		4:07:53		68		46.5		28-May-08		4:25:59		71.6		40

		17-Apr-08		6:07:10		69.8		46		17-Apr-08		6:06:20		65.6		34.5		17-Apr-08		6:07:53		68		47		28-May-08		6:25:59		72.21		40.5

		17-Apr-08		8:07:10		71		44.5		17-Apr-08		8:06:20		69.2		33		17-Apr-08		8:07:53		67.4		48		28-May-08		8:25:59		71.6		42.5

		17-Apr-08		10:07:10		70.41		44.5		17-Apr-08		10:06:20		70.41		31.5		17-Apr-08		10:07:53		66.81		45.5		28-May-08		10:25:59		73.4		42

		17-Apr-08		12:07:10		71		45.5		17-Apr-08		12:06:20		71		29		17-Apr-08		12:07:53		68		48.5		28-May-08		12:25:59		74.01		41

		17-Apr-08		14:07:10		71		45.5		17-Apr-08		14:06:20		69.2		29.5		17-Apr-08		14:07:53		67.4		49.5		28-May-08		14:25:59		74.01		41.5

		17-Apr-08		16:07:10		71		45.5		17-Apr-08		16:06:20		68.61		31.5		17-Apr-08		16:07:53		68		48		28-May-08		16:25:59		74.6		39.5

		17-Apr-08		18:07:10		71		46.5		17-Apr-08		18:06:20		70.41		31		17-Apr-08		18:07:53		68.61		48		28-May-08		18:25:59		75.2		38

		17-Apr-08		20:07:10		71		44.5		17-Apr-08		20:06:20		69.8		34.5		17-Apr-08		20:07:53		67.4		46.5		28-May-08		20:25:59		74.6		39.5

		17-Apr-08		22:07:10		69.8		42.5		17-Apr-08		22:06:20		69.8		36.5		17-Apr-08		22:07:53		67.4		46		28-May-08		22:25:59		74.01		38

		18-Apr-08		0:07:10		70.41		45.5		18-Apr-08		0:06:20		68.61		38		18-Apr-08		0:07:53		68		48.5		29-May-08		0:25:59		72.8		38

		18-Apr-08		2:07:10		70.41		42.5		18-Apr-08		2:06:20		67.4		39		18-Apr-08		2:07:53		68		47.5		29-May-08		2:25:59		72.21		38

		18-Apr-08		4:07:10		69.8		46.5		18-Apr-08		4:06:20		66.2		39.5		18-Apr-08		4:07:53		68		47.5		29-May-08		4:25:59		72.21		38.5

		18-Apr-08		6:07:10		69.8		46		18-Apr-08		6:06:20		65.6		40		18-Apr-08		6:07:53		68		42		29-May-08		6:25:59		72.8		38.5

		18-Apr-08		8:07:10		70.41		46.5		18-Apr-08		8:06:20		68.61		39		18-Apr-08		8:07:53		67.4		49		29-May-08		8:25:59		72.8		40

		18-Apr-08		10:07:10		70.41		46		18-Apr-08		10:06:20		71		37.5		18-Apr-08		10:07:53		67.4		47.5		29-May-08		10:25:59		74.01		39

		18-Apr-08		12:07:10		71		44		18-Apr-08		12:06:20		72.21		36.5		18-Apr-08		12:07:53		68		49		29-May-08		12:25:59		74.6		39.5

		18-Apr-08		14:07:10		70.41		44.5		18-Apr-08		14:06:20		71		34.5		18-Apr-08		14:07:53		66.81		49.5		29-May-08		14:25:59		75.2		39

		18-Apr-08		16:07:10		70.41		42.5		18-Apr-08		16:06:20		71		39		18-Apr-08		16:07:53		67.4		49		29-May-08		16:25:59		74.6		39

		18-Apr-08		18:07:10		70.41		45		18-Apr-08		18:06:20		70.41		38		18-Apr-08		18:07:53		68		47.5		29-May-08		18:25:59		74.6		38

		18-Apr-08		20:07:10		70.41		44.5		18-Apr-08		20:06:20		69.8		41		18-Apr-08		20:07:53		67.4		48.5		29-May-08		20:25:59		74.6		39.5

		18-Apr-08		22:07:10		70.41		45.5		18-Apr-08		22:06:20		69.2		41		18-Apr-08		22:07:53		68		48.5		29-May-08		22:25:59		74.6		38.5

		19-Apr-08		0:07:10		69.8		44.5		19-Apr-08		0:06:20		68		42.5		19-Apr-08		0:07:53		67.4		49		30-May-08		0:25:59		74.01		38.5

		19-Apr-08		2:07:10		69.8		45		19-Apr-08		2:06:20		67.4		45		19-Apr-08		2:07:53		67.4		49		30-May-08		2:25:59		72.8		38.5

		19-Apr-08		4:07:10		69.8		40		19-Apr-08		4:06:20		66.81		45		19-Apr-08		4:07:53		68		46.5		30-May-08		4:25:59		72.21		39

		19-Apr-08		6:07:10		69.8		45.5		19-Apr-08		6:06:20		66.81		45		19-Apr-08		6:07:53		68		49		30-May-08		6:25:59		72.21		39.5

		19-Apr-08		8:07:10		69.8		45		19-Apr-08		8:06:20		71		41		19-Apr-08		8:07:53		66.81		50		30-May-08		8:25:59		72.21		41.5

		19-Apr-08		10:07:10		69.8		45		19-Apr-08		10:06:20		71.6		40.5		19-Apr-08		10:07:53		66.81		50		30-May-08		10:25:59		74.6		41.5

		19-Apr-08		12:07:10		70.41		44.5		19-Apr-08		12:06:20		71.6		39		19-Apr-08		12:07:53		66.81		50		30-May-08		12:25:59		74.6		41.5

		19-Apr-08		14:07:10		70.41		42		19-Apr-08		14:06:20		72.8		41		19-Apr-08		14:07:53		66.81		48		30-May-08		14:25:59		74.6		41.5

		19-Apr-08		16:07:10		70.41		45		19-Apr-08		16:06:20		69.8		42.5		19-Apr-08		16:07:53		67.4		48		30-May-08		16:25:59		75.2		40.5

		19-Apr-08		18:07:10		69.8		45		19-Apr-08		18:06:20		69.8		43.5		19-Apr-08		18:07:53		67.4		49.5		30-May-08		18:25:59		74.6		39

		19-Apr-08		20:07:10		69.8		42		19-Apr-08		20:06:20		68.61		41		19-Apr-08		20:07:53		67.4		46		30-May-08		20:25:59		74.6		41

		19-Apr-08		22:07:10		69.8		44.5		19-Apr-08		22:06:20		68.61		39		19-Apr-08		22:07:53		67.4		49.5		30-May-08		22:25:59		74.6		39.5

		20-Apr-08		0:07:10		69.2		44		20-Apr-08		0:06:20		67.4		40		20-Apr-08		0:07:53		67.4		49.5		31-May-08		0:25:59		74.01		39

		20-Apr-08		2:07:10		69.2		44.5		20-Apr-08		2:06:20		66.2		40		20-Apr-08		2:07:53		67.4		48		31-May-08		2:25:59		72.8		39.5

		20-Apr-08		4:07:10		68.61		45.5		20-Apr-08		4:06:20		65.01		38.5		20-Apr-08		4:07:53		66.81		48.5		31-May-08		4:25:59		72.21		40

		20-Apr-08		6:07:10		68.61		46.5		20-Apr-08		6:06:20		65.01		36		20-Apr-08		6:07:53		67.4		48.5		31-May-08		6:25:59		71.6		41

		20-Apr-08		8:07:10		68.61		47		20-Apr-08		8:06:20		65.01		33.5		20-Apr-08		8:07:53		67.4		47.5		31-May-08		8:25:59		71.6		42

		20-Apr-08		10:07:10		68.61		46		20-Apr-08		10:06:20		67.4		30		20-Apr-08		10:07:53		68		47.5		31-May-08		10:25:59		73.4		42.5

		20-Apr-08		12:07:10		69.2		43.5		20-Apr-08		12:06:20		69.2		26		20-Apr-08		12:07:53		67.4		44.5		31-May-08		12:25:59		74.6		42

		20-Apr-08		14:07:10		69.2		43.5		20-Apr-08		14:06:20		69.2		23		20-Apr-08		14:07:53		66.81		36.5		31-May-08		14:25:59		75.2		43.5

		20-Apr-08		16:07:10		69.2		45		20-Apr-08		16:06:20		69.2		23.5		20-Apr-08		16:07:53		67.4		47.5		31-May-08		16:25:59		74.6		43

		20-Apr-08		18:07:10		69.2		44		20-Apr-08		18:06:20		69.8		23		20-Apr-08		18:07:53		67.4		44.5		31-May-08		18:25:59		74.6		44.5

		20-Apr-08		20:07:10		69.2		45.5		20-Apr-08		20:06:20		68		25.5		20-Apr-08		20:07:53		67.4		47		31-May-08		20:25:59		74.6		43

		20-Apr-08		22:07:10		68.61		45		20-Apr-08		22:06:20		66.81		27.5		20-Apr-08		22:07:53		67.4		47.5		31-May-08		22:25:59		74.01		41

		21-Apr-08		0:07:10		68.61		46.5		21-Apr-08		0:06:20		65.6		29		21-Apr-08		0:07:53		67.4		48.5		1-Jun-08		0:25:59		72.8		41

		21-Apr-08		2:07:10		68		44.5		21-Apr-08		2:06:20		65.01		30.5		21-Apr-08		2:07:53		66.81		37.5		1-Jun-08		2:25:59		72.21		40.5

		21-Apr-08		4:07:10		68		46.5		21-Apr-08		4:06:20		63.8		31.5		21-Apr-08		4:07:53		66.81		47.5		1-Jun-08		4:25:59		71.6		40.5

		21-Apr-08		6:07:10		68		47.5		21-Apr-08		6:06:20		63.21		33		21-Apr-08		6:07:53		67.4		47.5		1-Jun-08		6:25:59		72.21		40.5

		21-Apr-08		8:07:10		68		44		21-Apr-08		8:06:20		63.21		33		21-Apr-08		8:07:53		67.4		47.5		1-Jun-08		8:25:59		72.21		40.5

		21-Apr-08		10:07:10		68		47.5		21-Apr-08		10:06:20		65.01		29		21-Apr-08		10:07:53		67.4		47.5		1-Jun-08		10:25:59		72.21		40.5

		21-Apr-08		12:07:10		68		42.5		21-Apr-08		12:06:20		67.4		24.5		21-Apr-08		12:07:53		67.4		42		1-Jun-08		12:25:59		73.4		41

		21-Apr-08		14:07:10		68.61		45.5		21-Apr-08		14:06:20		69.2		27.5		21-Apr-08		14:07:53		67.4		48		1-Jun-08		14:25:59		74.6		41.5

		21-Apr-08		16:07:10		68.61		45		21-Apr-08		16:06:20		69.2		29.5		21-Apr-08		16:07:53		67.4		48		1-Jun-08		16:25:59		75.81		41

		21-Apr-08		18:07:10		68.61		45		21-Apr-08		18:06:20		69.2		27		21-Apr-08		18:07:53		66.81		46.5		1-Jun-08		18:25:59		77		39.5

		21-Apr-08		20:07:10		69.2		45		21-Apr-08		20:06:20		68		30		21-Apr-08		20:07:53		67.4		48		1-Jun-08		20:25:59		76.4		39.5

		21-Apr-08		22:07:10		68.61		46.5		21-Apr-08		22:06:20		66.2		32		21-Apr-08		22:07:53		67.4		48.5		1-Jun-08		22:25:59		74.6		39

		22-Apr-08		0:07:10		68.61		45		22-Apr-08		0:06:20		65.01		30		22-Apr-08		0:07:53		67.4		48		2-Jun-08		0:25:59		72.8		39

		22-Apr-08		2:07:10		68		47		22-Apr-08		2:06:20		64.4		32		22-Apr-08		2:07:53		67.4		48		2-Jun-08		2:25:59		72.21		38.5

		22-Apr-08		4:07:10		67.4		47		22-Apr-08		4:06:20		63.8		32.5		22-Apr-08		4:07:53		66.81		41		2-Jun-08		4:25:59		72.21		38

		22-Apr-08		6:07:10		68		46.5		22-Apr-08		6:06:20		63.21		34		22-Apr-08		6:07:53		67.4		48		2-Jun-08		6:25:59		71.6		37.5

		22-Apr-08		8:07:10		68.61		47		22-Apr-08		8:06:20		66.81		33.5		22-Apr-08		8:07:53		66.81		49		2-Jun-08		8:25:59		71.6		38

		22-Apr-08		10:07:10		69.2		44.5		22-Apr-08		10:06:20		71		29.5		22-Apr-08		10:07:53		66.2		49.5		2-Jun-08		10:25:59		72.21		39

		22-Apr-08		12:07:10		69.8		44		22-Apr-08		12:06:20		71		27.5		22-Apr-08		12:07:53		66.81		48		2-Jun-08		12:25:59		73.4		38.5

		22-Apr-08		14:07:10		69.8		46		22-Apr-08		14:06:20		71		31		22-Apr-08		14:07:53		66.2		49.5		2-Jun-08		14:25:59		75.2		38

		22-Apr-08		16:07:10		69.2		44.5		22-Apr-08		16:06:20		69.8		32.5		22-Apr-08		16:07:53		67.4		47.5		2-Jun-08		16:25:59		75.81		38

		22-Apr-08		18:07:10		69.2		45		22-Apr-08		18:06:20		69.8		32		22-Apr-08		18:07:53		68		46.5		2-Jun-08		18:25:59		76.4		37

		22-Apr-08		20:07:10		69.8		45		22-Apr-08		20:06:20		69.2		31.5		22-Apr-08		20:07:53		68		46.5		2-Jun-08		20:25:59		75.81		37

		22-Apr-08		22:07:10		69.8		43.5		22-Apr-08		22:06:20		68		32		22-Apr-08		22:07:53		68		47		2-Jun-08		22:25:59		74.01		37.5

		23-Apr-08		0:07:10		69.2		45		23-Apr-08		0:06:20		66.81		32		23-Apr-08		0:07:53		67.4		47.5		3-Jun-08		0:25:59		72.21		37

		23-Apr-08		2:07:10		68.61		45		23-Apr-08		2:06:20		65.6		33		23-Apr-08		2:07:53		67.4		47		3-Jun-08		2:25:59		72.21		36.5

		23-Apr-08		4:07:10		68.61		46.5		23-Apr-08		4:06:20		65.01		34.5		23-Apr-08		4:07:53		67.4		47.5		3-Jun-08		4:25:59		71.6		36

		23-Apr-08		6:07:10		68.61		43.5		23-Apr-08		6:06:20		64.4		35.5		23-Apr-08		6:07:53		67.4		47.5		3-Jun-08		6:25:59		72.21		35.5

		23-Apr-08		8:07:10		69.2		42.5		23-Apr-08		8:06:20		66.81		35.5		23-Apr-08		8:07:53		67.4		48		3-Jun-08		8:25:59		71.6		37.5

		23-Apr-08		10:07:10		69.8		46		23-Apr-08		10:06:20		70.41		32.5		23-Apr-08		10:07:53		67.4		48		3-Jun-08		10:25:59		74.01		38

		23-Apr-08		12:07:10		69.2		45.5		23-Apr-08		12:06:20		71		35.5		23-Apr-08		12:07:53		66.81		49.5		3-Jun-08		12:25:59		74.01		39

		23-Apr-08		14:07:10		69.8		45		23-Apr-08		14:06:20		71.6		41		23-Apr-08		14:07:53		66.2		50.5		3-Jun-08		14:25:59		74.6		39.5

		23-Apr-08		16:07:10		70.41		47		23-Apr-08		16:06:20		69.8		49		23-Apr-08		16:07:53		67.4		50.5		3-Jun-08		16:25:59		74.6		39

		23-Apr-08		18:07:10		70.41		44.5		23-Apr-08		18:06:20		69.2		47.5		23-Apr-08		18:07:53		68		50		3-Jun-08		18:25:59		74.6		38.5

		23-Apr-08		20:07:10		70.41		46		23-Apr-08		20:06:20		69.8		49.5		23-Apr-08		20:07:53		68		50		3-Jun-08		20:25:59		74.6		34.5

		23-Apr-08		22:07:10		70.41		46.5		23-Apr-08		22:06:20		69.2		48.5		23-Apr-08		22:07:53		68		50		3-Jun-08		22:25:59		74.6		31.5

		24-Apr-08		0:07:10		70.41		47		24-Apr-08		0:06:20		68		47		24-Apr-08		0:07:53		68		49.5		4-Jun-08		0:25:59		73.4		32.5

		24-Apr-08		2:07:10		69.8		44.5		24-Apr-08		2:06:20		66.81		47.5		24-Apr-08		2:07:53		68		49.5		4-Jun-08		2:25:59		72.8		33.5

		24-Apr-08		4:07:10		69.8		46.5		24-Apr-08		4:06:20		66.2		46		24-Apr-08		4:07:53		68		48.5		4-Jun-08		4:25:59		72.21		34

		24-Apr-08		6:07:10		69.8		46.5		24-Apr-08		6:06:20		65.6		44.5		24-Apr-08		6:07:53		68		49		4-Jun-08		6:25:59		72.21		33.5

		24-Apr-08		8:07:10		70.41		47		24-Apr-08		8:06:20		68		44		24-Apr-08		8:07:53		67.4		50		4-Jun-08		8:25:59		72.21		37

		24-Apr-08		10:07:10		70.41		46		24-Apr-08		10:06:20		70.41		46		24-Apr-08		10:07:53		68		49.5		4-Jun-08		10:25:59		74.01		41.5

		24-Apr-08		12:07:10		70.41		46.5		24-Apr-08		12:06:20		69.8		44.5		24-Apr-08		12:07:53		68		50		4-Jun-08		12:25:59		74.01		44

		24-Apr-08		14:07:10		70.41		46		24-Apr-08		14:06:20		71		36		24-Apr-08		14:07:53		68		49		4-Jun-08		14:25:59		74.01		44.5

		24-Apr-08		16:07:10		70.41		44.5		24-Apr-08		16:06:20		69.8		32		24-Apr-08		16:07:53		68		48		4-Jun-08		16:25:59		73.4		42

		24-Apr-08		18:07:10		69.8		44		24-Apr-08		18:06:20		70.41		31		24-Apr-08		18:07:53		68		45		4-Jun-08		18:25:59		73.4		39

		24-Apr-08		20:07:10		70.41		46		24-Apr-08		20:06:20		69.8		30.5		24-Apr-08		20:07:53		69.2		46.5		4-Jun-08		20:25:59		74.6		39.5

		24-Apr-08		22:07:10		70.41		46		24-Apr-08		22:06:20		68		33		24-Apr-08		22:07:53		68		48.5		4-Jun-08		22:25:59		74.6		38

		25-Apr-08		0:07:10		69.8		45		25-Apr-08		0:06:20		66.2		34		25-Apr-08		0:07:53		68		48.5		5-Jun-08		0:25:59		74.01		37.5

		25-Apr-08		2:07:10		69.2		46		25-Apr-08		2:06:20		65.01		35.5		25-Apr-08		2:07:53		68.61		46		5-Jun-08		2:25:59		72.8		36.5

		25-Apr-08		4:07:10		69.2		45		25-Apr-08		4:06:20		63.8		36		25-Apr-08		4:07:53		68		47.5		5-Jun-08		4:25:59		72.21		36

		25-Apr-08		6:07:10		69.8		45		25-Apr-08		6:06:20		63.21		36		25-Apr-08		6:07:53		68.61		47.5		5-Jun-08		6:25:59		72.21		35.5

		25-Apr-08		8:07:10		69.8		46		25-Apr-08		8:06:20		66.81		35.5		25-Apr-08		8:07:53		68.61		47.5		5-Jun-08		8:25:59		72.21		35.5

		25-Apr-08		10:07:10		69.8		45		25-Apr-08		10:06:20		70.41		32.5		25-Apr-08		10:07:53		67.4		49.5		5-Jun-08		10:25:59		74.01		35.5

		25-Apr-08		12:07:10		70.41		42.5		25-Apr-08		12:06:20		71		28.5		25-Apr-08		12:07:53		68.61		48		5-Jun-08		12:25:59		73.4		35

		25-Apr-08		14:07:10		70.41		45.5		25-Apr-08		14:06:20		71		28		25-Apr-08		14:07:53		68		47.5		5-Jun-08		14:25:59		73.4		34

		25-Apr-08		16:07:10		70.41		46		25-Apr-08		16:06:20		71.6		32.5		25-Apr-08		16:07:53		68.61		48.5		5-Jun-08		16:25:59		74.01		34.5

		25-Apr-08		18:07:10		70.41		45.5		25-Apr-08		18:06:20		70.41		31		25-Apr-08		18:07:53		68		40.5		5-Jun-08		18:25:59		73.4		35

		25-Apr-08		20:07:10		70.41		41.5		25-Apr-08		20:06:20		71		32.5		25-Apr-08		20:07:53		68		48		5-Jun-08		20:25:59		74.01		35.5

		25-Apr-08		22:07:10		69.8		45		25-Apr-08		22:06:20		70.41		35.5		25-Apr-08		22:07:53		68		46		5-Jun-08		22:25:59		74.6		34

		26-Apr-08		0:07:10		70.41		46		26-Apr-08		0:06:20		69.2		36.5		26-Apr-08		0:07:53		68		49		6-Jun-08		0:25:59		74.01		34.5

		26-Apr-08		2:07:10		69.8		45.5		26-Apr-08		2:06:20		67.4		38.5		26-Apr-08		2:07:53		68.61		48		6-Jun-08		2:25:59		72.21		35

		26-Apr-08		4:07:10		69.8		44.5		26-Apr-08		4:06:20		66.2		39		26-Apr-08		4:07:53		68		48		6-Jun-08		4:25:59		71.6		35

		26-Apr-08		6:07:10		69.8		46		26-Apr-08		6:06:20		65.6		38.5		26-Apr-08		6:07:53		68.61		48		6-Jun-08		6:25:59		71.6		35

		26-Apr-08		8:07:10		70.41		46.5		26-Apr-08		8:06:20		68.61		37.5		26-Apr-08		8:07:53		68.61		48.5		6-Jun-08		8:25:59		72.21		37

		26-Apr-08		10:07:10		70.41		45.5		26-Apr-08		10:06:20		71		35.5		26-Apr-08		10:07:53		68		46.5		6-Jun-08		10:25:59		73.4		37.5

		26-Apr-08		12:07:10		71		46.5		26-Apr-08		12:06:20		71		32.5		26-Apr-08		12:07:53		68.61		49		6-Jun-08		12:25:59		73.4		35.5

		26-Apr-08		14:07:10		71		32		26-Apr-08		14:06:20		69.2		31		26-Apr-08		14:07:53		67.4		36		6-Jun-08		14:25:59		74.01		37.5

		26-Apr-08		16:07:10		71		35		26-Apr-08		16:06:20		68.61		36		26-Apr-08		16:07:53		67.4		39.5		6-Jun-08		16:25:59		74.01		38.5

		26-Apr-08		18:07:10		71		39.5		26-Apr-08		18:06:20		69.2		39.5		26-Apr-08		18:07:53		68.61		42.5		6-Jun-08		18:25:59		73.4		38.5

		26-Apr-08		20:07:10		70.41		38		26-Apr-08		20:06:20		69.2		41		26-Apr-08		20:07:53		68.61		41		6-Jun-08		20:25:59		74.01		41

		26-Apr-08		22:07:10		69.8		38		26-Apr-08		22:06:20		68		42		26-Apr-08		22:07:53		68.61		40.5		6-Jun-08		22:25:59		74.6		39

		27-Apr-08		0:07:10		69.8		36.5		27-Apr-08		0:06:20		68		39.5		27-Apr-08		0:07:53		68.61		39.5		7-Jun-08		0:25:59		74.01		38.5

		27-Apr-08		2:07:10		70.41		36.5		27-Apr-08		2:06:20		68		39.5		27-Apr-08		2:07:53		68.61		39.5		7-Jun-08		2:25:59		72.8		39

		27-Apr-08		4:07:10		70.41		37.5		27-Apr-08		4:06:20		66.81		42.5		27-Apr-08		4:07:53		68.61		39.5		7-Jun-08		4:25:59		71.6		38.5

		27-Apr-08		6:07:10		69.8		36		27-Apr-08		6:06:20		67.4		40.5		27-Apr-08		6:07:53		68		39		7-Jun-08		6:25:59		72.21		37.5

		27-Apr-08		8:07:10		69.8		37.5		27-Apr-08		8:06:20		68		42		27-Apr-08		8:07:53		68.61		40.5		7-Jun-08		8:25:59		72.21		38

		27-Apr-08		10:07:10		70.41		40		27-Apr-08		10:06:20		69.2		43		27-Apr-08		10:07:53		68.61		42.5		7-Jun-08		10:25:59		73.4		37.5

		27-Apr-08		12:07:10		71		40		27-Apr-08		12:06:20		69.2		42.5		27-Apr-08		12:07:53		68		44		7-Jun-08		12:25:59		73.4		36

		27-Apr-08		14:07:10		71		40		27-Apr-08		14:06:20		69.2		40.5		27-Apr-08		14:07:53		69.2		42.5		7-Jun-08		14:25:59		73.4		34

		27-Apr-08		16:07:10		71		43		27-Apr-08		16:06:20		69.2		47		27-Apr-08		16:07:53		69.2		46		7-Jun-08		16:25:59		73.4		33.5

		27-Apr-08		18:07:10		71		42.5		27-Apr-08		18:06:20		69.2		43.5		27-Apr-08		18:07:53		69.2		44		7-Jun-08		18:25:59		73.4		34

		27-Apr-08		20:07:10		71.6		38		27-Apr-08		20:06:20		68		43.5		27-Apr-08		20:07:53		68.61		42.5		7-Jun-08		20:25:59		74.01		35

		27-Apr-08		22:07:10		71		37.5		27-Apr-08		22:06:20		68		42.5		27-Apr-08		22:07:53		68.61		41		7-Jun-08		22:25:59		74.01		33.5

		28-Apr-08		0:07:10		70.41		38.5		28-Apr-08		0:06:20		68		40		28-Apr-08		0:07:53		68.61		40		8-Jun-08		0:25:59		73.4		33

		28-Apr-08		2:07:10		69.8		39.5		28-Apr-08		2:06:20		68		45		28-Apr-08		2:07:53		68.61		42		8-Jun-08		2:25:59		72.21		33

		28-Apr-08		4:07:10		69.2		39.5		28-Apr-08		4:06:20		67.4		47.5		28-Apr-08		4:07:53		68		41.5		8-Jun-08		4:25:59		71.6		33

		28-Apr-08		6:07:10		69.2		39.5		28-Apr-08		6:06:20		67.4		45		28-Apr-08		6:07:53		68		41.5		8-Jun-08		6:25:59		71.6		33

		28-Apr-08		8:07:10		70.41		40		28-Apr-08		8:06:20		68		47		28-Apr-08		8:07:53		68.61		42.5		8-Jun-08		8:25:59		71.6		33

		28-Apr-08		10:07:10		70.41		40.5		28-Apr-08		10:06:20		68		47.5		28-Apr-08		10:07:53		68.61		43		8-Jun-08		10:25:59		72.21		34

		28-Apr-08		12:07:10		71		40		28-Apr-08		12:06:20		68.61		44		28-Apr-08		12:07:53		69.2		43		8-Jun-08		12:25:59		74.6		33

		28-Apr-08		14:07:10		71		43		28-Apr-08		14:06:20		69.2		43		28-Apr-08		14:07:53		69.2		45.5		8-Jun-08		14:25:59		75.81		31.5

		28-Apr-08		16:07:10		71		44		28-Apr-08		16:06:20		68.61		52		28-Apr-08		16:07:53		69.2		47		8-Jun-08		16:25:59		77		30.5

		28-Apr-08		18:07:10		71		41.5		28-Apr-08		18:06:20		69.2		46		28-Apr-08		18:07:53		68.61		45		8-Jun-08		18:25:59		77		31.5

		28-Apr-08		20:07:10		71		39		28-Apr-08		20:06:20		68.61		45		28-Apr-08		20:07:53		68.61		43		8-Jun-08		20:25:59		77		33.5

		28-Apr-08		22:07:10		71		38.5		28-Apr-08		22:06:20		68.61		43.5		28-Apr-08		22:07:53		68.61		41.5		8-Jun-08		22:25:59		75.81		34.5

		29-Apr-08		0:07:10		69.2		38.5		29-Apr-08		0:06:20		68		45		29-Apr-08		0:07:53		68		41		9-Jun-08		0:25:59		74.6		34

		29-Apr-08		2:07:10		69.8		38		29-Apr-08		2:06:20		67.4		44.5		29-Apr-08		2:07:53		68.61		40.5		9-Jun-08		2:25:59		74.01		34.5

		29-Apr-08		4:07:10		69.8		37.5		29-Apr-08		4:06:20		66.81		44		29-Apr-08		4:07:53		68.61		40		9-Jun-08		4:25:59		72.8		35

		29-Apr-08		6:07:10		69.2		36.5		29-Apr-08		6:06:20		66.2		44		29-Apr-08		6:07:53		68.61		39		9-Jun-08		6:25:59		72.21		35.5

		29-Apr-08		8:07:10		69.8		38.5		29-Apr-08		8:06:20		68		44.5		29-Apr-08		8:07:53		68		41		9-Jun-08		8:25:59		72.21		36.5

		29-Apr-08		10:07:10		70.41		39.5		29-Apr-08		10:06:20		69.8		45		29-Apr-08		10:07:53		68		43		9-Jun-08		10:25:59		74.01		37

		29-Apr-08		12:07:10		71		42		29-Apr-08		12:06:20		70.41		48.5		29-Apr-08		12:07:53		69.2		44.5		9-Jun-08		12:25:59		76.4		36

		29-Apr-08		14:07:10		71		42.5		29-Apr-08		14:06:20		70.41		48		29-Apr-08		14:07:53		68.61		46.5		9-Jun-08		14:25:59		77.61		35

		29-Apr-08		16:07:10		71		43		29-Apr-08		16:06:20		69.8		49		29-Apr-08		16:07:53		68.61		47		9-Jun-08		16:25:59		78.8		34.5

		29-Apr-08		18:07:10		71.6		41.5		29-Apr-08		18:06:20		69.2		48.5		29-Apr-08		18:07:53		68.61		45.5		9-Jun-08		18:25:59		78.2		35.5

		29-Apr-08		20:07:10		71		40		29-Apr-08		20:06:20		69.2		46.5		29-Apr-08		20:07:53		68.61		43.5		9-Jun-08		20:25:59		78.2		35.5

		29-Apr-08		22:07:10		71		39		29-Apr-08		22:06:20		69.2		47.5		29-Apr-08		22:07:53		68.61		42.5		9-Jun-08		22:25:59		76.4		35.5

		30-Apr-08		0:07:10		69.2		33		30-Apr-08		0:06:20		68		34		30-Apr-08		0:07:53		68		35.5		10-Jun-08		0:25:59		74.6		35.5

		30-Apr-08		2:07:10		69.2		35.5		30-Apr-08		2:06:20		68.61		37.5		30-Apr-08		2:07:53		68.61		37.5		10-Jun-08		2:25:59		73.4		36

		30-Apr-08		4:07:10		69.8		35		30-Apr-08		4:06:20		67.4		38.5		30-Apr-08		4:07:53		68.61		37		10-Jun-08		4:25:59		72.8		36

		30-Apr-08		6:07:10		70.41		35		30-Apr-08		6:06:20		69.2		39		30-Apr-08		6:07:53		68.61		38		10-Jun-08		6:25:59		72.21		37

		30-Apr-08		8:07:10		70.41		34		30-Apr-08		8:06:20		69.8		34		30-Apr-08		8:07:53		68		36.5		10-Jun-08		8:25:59		72.8		39

		30-Apr-08		10:07:10		69.2		34		30-Apr-08		10:06:20		69.8		35		30-Apr-08		10:07:53		67.4		37.5		10-Jun-08		10:25:59		73.4		38.5

		30-Apr-08		12:07:10		69.8		32.5		30-Apr-08		12:06:20		69.8		35		30-Apr-08		12:07:53		68		36		10-Jun-08		12:25:59		72.8		39

		30-Apr-08		14:07:10		69.8		33.5		30-Apr-08		14:06:20		69.2		34		30-Apr-08		14:07:53		68.61		36		10-Jun-08		14:25:59		72.8		39

		30-Apr-08		16:07:10		69.8		34		30-Apr-08		16:06:20		69.2		35		30-Apr-08		16:07:53		68.61		36.5		10-Jun-08		16:25:59		72.21		40

		30-Apr-08		18:07:10		69.8		31		30-Apr-08		18:06:20		69.2		32		30-Apr-08		18:07:53		68		33.5		10-Jun-08		18:25:59		72.8		42.5

		30-Apr-08		20:07:10		68.61		31.5		30-Apr-08		20:06:20		68.61		31.5		30-Apr-08		20:07:53		68		33.5		10-Jun-08		20:25:59		74.6		43

		30-Apr-08		22:07:10		69.2		31		30-Apr-08		22:06:20		68.61		32.5		30-Apr-08		22:07:53		68.61		33.5		10-Jun-08		22:25:59		76.4		40.5

		1-May-08		0:07:10		68.61		31.5		1-May-08		0:06:20		67.4		34		1-May-08		0:07:53		68		34		11-Jun-08		0:25:59		75.81		40.5

		1-May-08		2:07:10		68.61		30.5		1-May-08		2:06:20		66.2		33		1-May-08		2:07:53		68		32.5		11-Jun-08		2:25:59		75.2		39

		1-May-08		4:07:10		68		29.5		1-May-08		4:06:20		65.6		32		1-May-08		4:07:53		68		31		11-Jun-08		4:25:59		74.01		38

		1-May-08		6:07:10		68.61		29		1-May-08		6:06:20		65.6		31.5		1-May-08		6:07:53		68		30.5		11-Jun-08		6:25:59		72.8		37.5

		1-May-08		8:07:10		69.2		28		1-May-08		8:06:20		69.2		30		1-May-08		8:07:53		68.61		30.5		11-Jun-08		8:25:59		72.21		37

		1-May-08		10:07:10		69.8		26		1-May-08		10:06:20		70.41		27.5		1-May-08		10:07:53		68.61		29		11-Jun-08		10:25:59		72.8		33

		1-May-08		12:07:10		69.8		24		1-May-08		12:06:20		70.41		24.5		1-May-08		12:07:53		68.61		27		11-Jun-08		12:25:59		72.8		30.5

		1-May-08		14:07:10		70.41		25		1-May-08		14:06:20		71		26		1-May-08		14:07:53		69.8		27		11-Jun-08		14:25:59		74.01		30.5

		1-May-08		16:07:10		71		25.5		1-May-08		16:06:20		69.8		27.5		1-May-08		16:07:53		69.2		27.5		11-Jun-08		16:25:59		74.01		30.5

		1-May-08		18:07:10		70.41		29		1-May-08		18:06:20		70.41		29.5		1-May-08		18:07:53		69.8		30		11-Jun-08		18:25:59		73.4		32

		1-May-08		20:07:10		69.2		29.5		1-May-08		20:06:20		69.2		30		1-May-08		20:07:53		69.2		31		11-Jun-08		20:25:59		74.6		32.5

		1-May-08		22:07:10		69.2		30.5		1-May-08		22:06:20		69.8		30.5		1-May-08		22:07:53		69.2		32		11-Jun-08		22:25:59		75.2		32

		2-May-08		0:07:10		69.8		30.5		2-May-08		0:06:20		68		33		2-May-08		0:07:53		69.2		32.5		12-Jun-08		0:25:59		74.6		32

		2-May-08		2:07:10		69.8		30.5		2-May-08		2:06:20		67.4		33.5		2-May-08		2:07:53		69.2		32		12-Jun-08		2:25:59		73.4		32.5

		2-May-08		4:07:10		69.2		30.5		2-May-08		4:06:20		66.81		34		2-May-08		4:07:53		69.2		31.5		12-Jun-08		4:25:59		72.21		32.5

		2-May-08		6:07:10		69.2		30		2-May-08		6:06:20		66.81		34		2-May-08		6:07:53		69.2		32		12-Jun-08		6:25:59		71.6		32.5

		2-May-08		8:07:10		69.8		30.5		2-May-08		8:06:20		69.2		33		2-May-08		8:07:53		69.8		32		12-Jun-08		8:25:59		72.21		34.5

		2-May-08		10:07:10		69.8		30		2-May-08		10:06:20		69.8		31.5		2-May-08		10:07:53		69.8		31.5		12-Jun-08		10:25:59		73.4		34.5

		2-May-08		12:07:10		70.41		27		2-May-08		12:06:20		69.8		28		2-May-08		12:07:53		70.41		29.5		12-Jun-08		12:25:59		73.4		32.5

		2-May-08		14:07:10		71		23.5		2-May-08		14:06:20		71		25.5		2-May-08		14:07:53		69.8		26		12-Jun-08		14:25:59		72.8		29

		2-May-08		16:07:10		70.41		29.5		2-May-08		16:06:20		69.8		31		2-May-08		16:07:53		69.2		31		12-Jun-08		16:25:59		73.4		27.5

		2-May-08		18:07:10		70.41		30.5		2-May-08		18:06:20		70.41		31.5		2-May-08		18:07:53		69.8		32		12-Jun-08		18:25:59		73.4		29

		2-May-08		20:07:10		71		34		2-May-08		20:06:20		70.41		34		2-May-08		20:07:53		69.8		34		12-Jun-08		20:25:59		74.6		31.5

		2-May-08		22:07:10		70.41		29		2-May-08		22:06:20		70.41		30		2-May-08		22:07:53		70.41		31		12-Jun-08		22:25:59		75.2		32.5

		3-May-08		0:07:10		69.2		30		3-May-08		0:06:20		69.2		31		3-May-08		0:07:53		69.8		31.5		13-Jun-08		0:25:59		74.6		33

		3-May-08		2:07:10		70.41		33		3-May-08		2:06:20		68.61		36		3-May-08		2:07:53		69.8		34		13-Jun-08		2:25:59		73.4		33.5

		3-May-08		4:07:10		70.41		32.5		3-May-08		4:06:20		67.4		36		3-May-08		4:07:53		69.8		33.5		13-Jun-08		4:25:59		72.8		34

		3-May-08		6:07:10		70.41		32		3-May-08		6:06:20		66.81		36.5		3-May-08		6:07:53		69.8		33.5		13-Jun-08		6:25:59		71.6		35

		3-May-08		8:07:10		70.41		33.5		3-May-08		8:06:20		69.8		35.5		3-May-08		8:07:53		69.2		35		13-Jun-08		8:25:59		72.21		37

		3-May-08		10:07:10		70.41		34		3-May-08		10:06:20		70.41		35.5		3-May-08		10:07:53		69.8		35.5		13-Jun-08		10:25:59		72.21		37

		3-May-08		12:07:10		71		33.5		3-May-08		12:06:20		71		34		3-May-08		12:07:53		69.8		34.5		13-Jun-08		12:25:59		72.21		30.5

		3-May-08		14:07:10		71		36.5		3-May-08		14:06:20		71.6		35		3-May-08		14:07:53		69.8		36.5		13-Jun-08		14:25:59		73.4		27.5

		3-May-08		16:07:10		71		34		3-May-08		16:06:20		70.41		35.5		3-May-08		16:07:53		69.8		36.5		13-Jun-08		16:25:59		73.4		30.5

		3-May-08		18:07:10		71		37.5		3-May-08		18:06:20		71		40		3-May-08		18:07:53		69.8		39		13-Jun-08		18:25:59		73.4		28.5

		3-May-08		20:07:10		71		36.5		3-May-08		20:06:20		70.41		40		3-May-08		20:07:53		69.8		38		13-Jun-08		20:25:59		74.6		29

		3-May-08		22:07:10		71		35.5		3-May-08		22:06:20		69.8		39		3-May-08		22:07:53		69.8		37		13-Jun-08		22:25:59		75.81		29.5

		4-May-08		0:07:10		71		35		4-May-08		0:06:20		68		40		4-May-08		0:07:53		69.2		37		14-Jun-08		0:25:59		75.2		30.5

		4-May-08		2:07:10		70.41		35		4-May-08		2:06:20		66.81		41		4-May-08		2:07:53		69.8		36.5		14-Jun-08		2:25:59		74.01		31.5

		4-May-08		4:07:10		70.41		34.5		4-May-08		4:06:20		66.2		41		4-May-08		4:07:53		69.2		35.5		14-Jun-08		4:25:59		72.8		32

		4-May-08		6:07:10		69.8		33.5		4-May-08		6:06:20		65.6		40		4-May-08		6:07:53		69.8		35		14-Jun-08		6:25:59		72.21		33.5

		4-May-08		8:07:10		70.41		35.5		4-May-08		8:06:20		66.81		41.5		4-May-08		8:07:53		70.41		36		14-Jun-08		8:25:59		72.21		35.5

		4-May-08		10:07:10		70.41		36		4-May-08		10:06:20		69.8		39		4-May-08		10:07:53		70.41		37.5		14-Jun-08		10:25:59		72.8		37

		4-May-08		12:07:10		71		37		4-May-08		12:06:20		71		39.5		4-May-08		12:07:53		70.41		39		14-Jun-08		12:25:59		72.8		39.5

		4-May-08		14:07:10		71		39.5		4-May-08		14:06:20		70.41		45.5		4-May-08		14:07:53		68.61		42.5		14-Jun-08		14:25:59		73.4		38

		4-May-08		16:07:10		71		39.5		4-May-08		16:06:20		70.41		44.5		4-May-08		16:07:53		68.61		43.5		14-Jun-08		16:25:59		72.8		38.5

		4-May-08		18:07:10		71		40		4-May-08		18:06:20		69.8		48		4-May-08		18:07:53		69.2		43		14-Jun-08		18:25:59		73.4		38.5

		4-May-08		20:07:10		71		38.5		4-May-08		20:06:20		69.2		47		4-May-08		20:07:53		68.61		42		14-Jun-08		20:25:59		74.01		37

		4-May-08		22:07:10		71		38		4-May-08		22:06:20		69.8		44		4-May-08		22:07:53		68.61		40.5		14-Jun-08		22:25:59		74.01		37.5

		5-May-08		0:07:10		71		37.5		5-May-08		0:06:20		68.61		44		5-May-08		0:07:53		70.41		39.5		15-Jun-08		0:25:59		72.8		37

		5-May-08		2:07:10		71		37		5-May-08		2:06:20		68		44.5		5-May-08		2:07:53		70.41		38.5		15-Jun-08		2:25:59		72.21		37.5

		5-May-08		4:07:10		70.41		36.5		5-May-08		4:06:20		66.81		44.5		5-May-08		4:07:53		69.8		37.5		15-Jun-08		4:25:59		71.6		37.5

		5-May-08		6:07:10		69.8		35		5-May-08		6:06:20		66.2		43		5-May-08		6:07:53		69.8		37		15-Jun-08		6:25:59		71.6		37.5

		5-May-08		8:07:10		69.8		37		5-May-08		8:06:20		66.2		44.5		5-May-08		8:07:53		69.8		37.5		15-Jun-08		8:25:59		72.21		38

		5-May-08		10:07:10		69.8		38		5-May-08		10:06:20		68.61		44		5-May-08		10:07:53		69.8		39		15-Jun-08		10:25:59		72.21		39

		5-May-08		12:07:10		70.41		40		5-May-08		12:06:20		70.41		45		5-May-08		12:07:53		71		40.5		15-Jun-08		12:25:59		73.4		40

		5-May-08		14:07:10		71		40		5-May-08		14:06:20		71		44.5		5-May-08		14:07:53		71		41.5		15-Jun-08		14:25:59		74.6		41

		5-May-08		16:07:10		71		38		5-May-08		16:06:20		69.8		42		5-May-08		16:07:53		70.41		40		15-Jun-08		16:25:59		75.2		41.5

		5-May-08		18:07:10		71		37.5		5-May-08		18:06:20		70.41		41.5		5-May-08		18:07:53		70.41		39		15-Jun-08		18:25:59		75.81		41

		5-May-08		20:07:10		71		37		5-May-08		20:06:20		70.41		41.5		5-May-08		20:07:53		69.8		38.5		15-Jun-08		20:25:59		75.2		40

		5-May-08		22:07:10		70.41		37		5-May-08		22:06:20		69.8		41		5-May-08		22:07:53		69.8		38.5		15-Jun-08		22:25:59		74.01		39.5

		6-May-08		0:07:10		71		36.5		6-May-08		0:06:20		69.2		42		6-May-08		0:07:53		70.41		38		16-Jun-08		0:25:59		72.8		39

		6-May-08		2:07:10		71		36.5		6-May-08		2:06:20		67.4		43		6-May-08		2:07:53		70.41		37.5		16-Jun-08		2:25:59		72.21		39

		6-May-08		4:07:10		70.41		36		6-May-08		4:06:20		66.81		43		6-May-08		4:07:53		69.8		37		16-Jun-08		4:25:59		71.6		39

		6-May-08		6:07:10		69.8		35.5		6-May-08		6:06:20		65.6		43		6-May-08		6:07:53		69.2		37		16-Jun-08		6:25:59		71		39

		6-May-08		8:07:10		70.41		38		6-May-08		8:06:20		68		43.5		6-May-08		8:07:53		68.61		42		16-Jun-08		8:25:59		70.41		39.5

		6-May-08		10:07:10		70.41		39		6-May-08		10:06:20		71		44		6-May-08		10:07:53		67.4		41.5		16-Jun-08		10:25:59		70.41		40.5

		6-May-08		12:07:10		70.41		40.5		6-May-08		12:06:20		71.6		45		6-May-08		12:07:53		67.4		44		16-Jun-08		12:25:59		72.21		41.5

		6-May-08		14:07:10		71		40.5		6-May-08		14:06:20		71		44.5		6-May-08		14:07:53		67.4		44.5		16-Jun-08		14:25:59		73.4		42.5

		6-May-08		16:07:10		71		40		6-May-08		16:06:20		70.41		46.5		6-May-08		16:07:53		68.61		43.5		16-Jun-08		16:25:59		74.6		41

		6-May-08		18:07:10		70.41		39		6-May-08		18:06:20		69.2		45.5		6-May-08		18:07:53		68.61		41		16-Jun-08		18:25:59		75.2		40

		6-May-08		20:07:10		70.41		39.5		6-May-08		20:06:20		68.61		45		6-May-08		20:07:53		68.61		41.5		16-Jun-08		20:25:59		75.2		39

		6-May-08		22:07:10		70.41		38		6-May-08		22:06:20		69.2		44		6-May-08		22:07:53		68.61		41		16-Jun-08		22:25:59		74.01		38.5

		7-May-08		0:07:10		70.41		38.5		7-May-08		0:06:20		68.61		45		7-May-08		0:07:53		68.61		41		17-Jun-08		0:25:59		72.21		38

		7-May-08		2:07:10		70.41		38.5		7-May-08		2:06:20		68		46.5		7-May-08		2:07:53		68		41.5		17-Jun-08		2:25:59		71		37.5

		7-May-08		4:07:10		69.8		38		7-May-08		4:06:20		67.4		47		7-May-08		4:07:53		68.61		40.5		17-Jun-08		4:25:59		70.41		38.5

		7-May-08		6:07:10		70.41		39		7-May-08		6:06:20		66.81		47.5		7-May-08		6:07:53		68		42		17-Jun-08		6:25:59		70.41		39.5

		7-May-08		8:07:10		70.41		39		7-May-08		8:06:20		69.8		45		7-May-08		8:07:53		68.61		41.5		17-Jun-08		8:25:59		70.41		41.5

		7-May-08		10:07:10		71		38.5		7-May-08		10:06:20		70.41		45		7-May-08		10:07:53		68		42		17-Jun-08		10:25:59		71.6		42.5

		7-May-08		12:07:10		71		40.5		7-May-08		12:06:20		70.41		47		7-May-08		12:07:53		68		43.5		17-Jun-08		12:25:59		73.4		42.5

		7-May-08		14:07:10		71		43.5		7-May-08		14:06:20		69.8		51		7-May-08		14:07:53		68.61		46.5		17-Jun-08		14:25:59		74.01		43.5

		7-May-08		16:07:10		71		43		7-May-08		16:06:20		70.41		56		7-May-08		16:07:53		68.61		46.5		17-Jun-08		16:25:59		74.6		41

		7-May-08		18:07:10		70.41		43.5		7-May-08		18:06:20		71		50		7-May-08		18:07:53		68		46.5		17-Jun-08		18:25:59		74.01		40

		7-May-08		20:07:10		71		36.5		7-May-08		20:06:20		70.41		39		7-May-08		20:07:53		68		41		17-Jun-08		20:25:59		74.01		39.5

		7-May-08		22:07:10		71		34.5		7-May-08		22:06:20		69.8		36		7-May-08		22:07:53		68		38		17-Jun-08		22:25:59		74.01		38.5

		8-May-08		0:07:10		69.8		37		8-May-08		0:06:20		69.8		40.5		8-May-08		0:07:53		68		40		18-Jun-08		0:25:59		72.8		38

		8-May-08		2:07:10		70.41		37		8-May-08		2:06:20		68.61		41		8-May-08		2:07:53		69.2		39		18-Jun-08		2:25:59		71.6		37.5

		8-May-08		4:07:10		70.41		36		8-May-08		4:06:20		68		41.5		8-May-08		4:07:53		69.8		37.5		18-Jun-08		4:25:59		70.41		38.5

		8-May-08		6:07:10		71		34.5		8-May-08		6:06:20		68		39.5		8-May-08		6:07:53		68.61		38		18-Jun-08		6:25:59		70.41		39.5

		8-May-08		8:07:10		71		34.5		8-May-08		8:06:20		69.8		37		8-May-08		8:07:53		68.61		38		18-Jun-08		8:25:59		70.41		41.5

		8-May-08		10:07:10		70.41		36		8-May-08		10:06:20		70.41		38.5		8-May-08		10:07:53		68.61		38		18-Jun-08		10:25:59		72.8		42

		8-May-08		12:07:10		70.41		37		8-May-08		12:06:20		71		38.5		8-May-08		12:07:53		67.4		40.5		18-Jun-08		12:25:59		72.8		41.5

		8-May-08		14:07:10		70.41		39		8-May-08		14:06:20		71		41		8-May-08		14:07:53		67.4		43		18-Jun-08		14:25:59		72.8		42.5

		8-May-08		16:07:10		71		38.5		8-May-08		16:06:20		70.41		43		8-May-08		16:07:53		68		41.5		18-Jun-08		16:25:59		73.4		43

		8-May-08		18:07:10		71		39		8-May-08		18:06:20		71		41.5		8-May-08		18:07:53		68.61		42		18-Jun-08		18:25:59		74.01		34.5

		8-May-08		20:07:10		71		38		8-May-08		20:06:20		70.41		43.5		8-May-08		20:07:53		68		41.5		18-Jun-08		20:25:59		74.6		32

		8-May-08		22:07:10		70.41		37		8-May-08		22:06:20		69.8		41		8-May-08		22:07:53		68		40		18-Jun-08		22:25:59		74.6		30.5

		9-May-08		0:07:10		70.41		37		9-May-08		0:06:20		68.61		41.5		9-May-08		0:07:53		68		40		19-Jun-08		0:25:59		74.01		30.5

		9-May-08		2:07:10		70.41		36.5		9-May-08		2:06:20		67.4		42		9-May-08		2:07:53		68.61		39		19-Jun-08		2:25:59		73.4		31.5

		9-May-08		4:07:10		69.8		35.5		9-May-08		4:06:20		66.81		42.5		9-May-08		4:07:53		69.2		38		19-Jun-08		4:25:59		72.21		33

		9-May-08		6:07:10		71		35.5		9-May-08		6:06:20		66.81		41.5		9-May-08		6:07:53		69.2		37.5		19-Jun-08		6:25:59		71		33.5

		9-May-08		8:07:10		71		37		9-May-08		8:06:20		69.8		42		9-May-08		8:07:53		69.2		39		19-Jun-08		8:25:59		71		35.5

		9-May-08		10:07:10		70.41		38		9-May-08		10:06:20		71		40.5		9-May-08		10:07:53		68.61		40		19-Jun-08		10:25:59		72.8		35.5

		9-May-08		12:07:10		70.41		40		9-May-08		12:06:20		71.6		43		9-May-08		12:07:53		69.2		41.5		19-Jun-08		12:25:59		73.4		33.5

		9-May-08		14:07:10		70.41		39		9-May-08		14:06:20		69.8		45.5		9-May-08		14:07:53		68		42.5		19-Jun-08		14:25:59		72.21		35.5

		9-May-08		16:07:10		70.41		38		9-May-08		16:06:20		69.2		43		9-May-08		16:07:53		67.4		42.5		19-Jun-08		16:25:59		72.21		33.5

		9-May-08		18:07:10		70.41		38.5		9-May-08		18:06:20		68.61		42.5		9-May-08		18:07:53		68.61		41.5		19-Jun-08		18:25:59		74.01		28.5

		9-May-08		20:07:10		70.41		37		9-May-08		20:06:20		68.61		42		9-May-08		20:07:53		68		40		19-Jun-08		20:25:59		74.6		29

		9-May-08		22:07:10		69.8		36.5		9-May-08		22:06:20		68		41.5		9-May-08		22:07:53		68.61		39		19-Jun-08		22:25:59		75.2		27.5

		10-May-08		0:07:10		69.8		35.5		10-May-08		0:06:20		68		40.5		10-May-08		0:07:53		68		39		20-Jun-08		0:25:59		74.6		30

		10-May-08		2:07:10		69.8		34.5		10-May-08		2:06:20		66.81		40.5		10-May-08		2:07:53		68		37.5		20-Jun-08		2:25:59		73.4		31

		10-May-08		4:07:10		69.8		34		10-May-08		4:06:20		66.2		40.5		10-May-08		4:07:53		68.61		37		20-Jun-08		4:25:59		72.8		31.5

		10-May-08		6:07:10		70.41		33.5		10-May-08		6:06:20		65.6		39.5		10-May-08		6:07:53		68.61		35.5		20-Jun-08		6:25:59		71.6		32.5

		10-May-08		8:07:10		70.41		35.5		10-May-08		8:06:20		68		41.5		10-May-08		8:07:53		67.4		38.5		20-Jun-08		8:25:59		72.21		35

		10-May-08		10:07:10		69.8		34		10-May-08		10:06:20		70.41		35		10-May-08		10:07:53		68		37.5		20-Jun-08		10:25:59		73.4		36.5

		10-May-08		12:07:10		71		33.5		10-May-08		12:06:20		71		34.5		10-May-08		12:07:53		68.61		36.5		20-Jun-08		12:25:59		72.8		35

		10-May-08		14:07:10		71.6		32		10-May-08		14:06:20		70.41		34.5		10-May-08		14:07:53		68		35.5		20-Jun-08		14:25:59		72.8		33.5

		10-May-08		16:07:10		71.6		35		10-May-08		16:06:20		69.8		38.5		10-May-08		16:07:53		67.4		40.5		20-Jun-08		16:25:59		72.8		34

		10-May-08		18:07:10		71.6		36		10-May-08		18:06:20		69.2		39.5		10-May-08		18:07:53		67.4		41.5		20-Jun-08		18:25:59		72.8		31

		10-May-08		20:07:10		71		35.5		10-May-08		20:06:20		68.61		40.5		10-May-08		20:07:53		68		39.5		20-Jun-08		20:25:59		74.6		31.5

		10-May-08		22:07:10		70.41		35.5		10-May-08		22:06:20		68.61		39.5		10-May-08		22:07:53		68		38.5		20-Jun-08		22:25:59		75.81		30.5

		11-May-08		0:07:10		70.41		35.5		11-May-08		0:06:20		68.61		39.5		11-May-08		0:07:53		68		38.5		21-Jun-08		0:25:59		75.2		31.5

		11-May-08		2:07:10		70.41		35		11-May-08		2:06:20		67.4		40		11-May-08		2:07:53		68		38		21-Jun-08		2:25:59		74.01		32

		11-May-08		4:07:10		69.8		34		11-May-08		4:06:20		66.81		40.5		11-May-08		4:07:53		68.61		37		21-Jun-08		4:25:59		73.4		32.5

		11-May-08		6:07:10		70.41		34.5		11-May-08		6:06:20		68		39		11-May-08		6:07:53		68.61		36.5		21-Jun-08		6:25:59		72.21		34

		11-May-08		8:07:10		70.41		35.5		11-May-08		8:06:20		69.8		39		11-May-08		8:07:53		68		38.5		21-Jun-08		8:25:59		72.8		35.5

		11-May-08		10:07:10		70.41		35		11-May-08		10:06:20		69.8		36.5		11-May-08		10:07:53		68.61		37.5		21-Jun-08		10:25:59		72.8		35.5

		11-May-08		12:07:10		71		35.5		11-May-08		12:06:20		70.41		38		11-May-08		12:07:53		68.61		39		21-Jun-08		12:25:59		72.8		33.5

		11-May-08		14:07:10		71.6		38		11-May-08		14:06:20		69.2		41		11-May-08		14:07:53		68.61		41.5		21-Jun-08		14:25:59		72.8		32

		11-May-08		16:07:10		71.6		37.5		11-May-08		16:06:20		68.61		40		11-May-08		16:07:53		68.61		40.5		21-Jun-08		16:25:59		73.4		30

		11-May-08		18:07:10		71.6		38.5		11-May-08		18:06:20		69.2		44		11-May-08		18:07:53		68.61		42.5		21-Jun-08		18:25:59		71.6		27

		11-May-08		20:07:10		71.6		39		11-May-08		20:06:20		69.2		50		11-May-08		20:07:53		68.61		43.5		21-Jun-08		20:25:59		74.01		26.5

		11-May-08		22:07:10		71		38.5		11-May-08		22:06:20		68.61		46.5		11-May-08		22:07:53		69.2		41.5		21-Jun-08		22:25:59		75.81		25.5

		12-May-08		0:07:10		69.8		38.5		12-May-08		0:06:20		68.61		47.5		12-May-08		0:07:53		69.2		41		22-Jun-08		0:25:59		75.81		27.5

		12-May-08		2:07:10		70.41		39		12-May-08		2:06:20		68.61		47.5		12-May-08		2:07:53		69.8		41		22-Jun-08		2:25:59		75.2		29

		12-May-08		4:07:10		70.41		38		12-May-08		4:06:20		68		47		12-May-08		4:07:53		69.8		40		22-Jun-08		4:25:59		74.01		29.5

		12-May-08		6:07:10		71		38		12-May-08		6:06:20		67.4		47		12-May-08		6:07:53		69.8		40		22-Jun-08		6:25:59		74.6		30

		12-May-08		8:07:10		71		38.5		12-May-08		8:06:20		67.4		47.5		12-May-08		8:07:53		69.8		40.5		22-Jun-08		8:25:59		75.2		30.5

		12-May-08		10:07:10		70.41		39		12-May-08		10:06:20		68.61		45		12-May-08		10:07:53		69.8		40.5		22-Jun-08		10:25:59		77		31

		12-May-08		12:07:10		70.41		40		12-May-08		12:06:20		69.2		44.5		12-May-08		12:07:53		69.8		41.5		22-Jun-08		12:25:59		78.2		29.5

		12-May-08		14:07:10		71		33		12-May-08		14:06:20		69.2		32		12-May-08		14:07:53		69.8		34.5		22-Jun-08		14:25:59		79.41		28.5

		12-May-08		16:07:10		71		29.5		12-May-08		16:06:20		69.8		29.5		12-May-08		16:07:53		69.8		31		22-Jun-08		16:25:59		79.41		27

		12-May-08		18:07:10		71.6		31.5		12-May-08		18:06:20		69.8		33		12-May-08		18:07:53		69.8		33		22-Jun-08		18:25:59		78.8		25

		12-May-08		20:07:10		71.6		30.5		12-May-08		20:06:20		69.2		33		12-May-08		20:07:53		69.8		33		22-Jun-08		20:25:59		78.8		25

		12-May-08		22:07:10		70.41		30.5		12-May-08		22:06:20		68		33		12-May-08		22:07:53		69.8		32.5		22-Jun-08		22:25:59		77.61		27

		13-May-08		0:07:10		68.61		31		13-May-08		0:06:20		68.61		32.5		13-May-08		0:07:53		68.61		32.5		23-Jun-08		0:25:59		76.4		29

		13-May-08		2:07:10		68		32		13-May-08		2:06:20		68		33		13-May-08		2:07:53		68		33		23-Jun-08		2:25:59		75.2		31

		13-May-08		4:07:10		68		31.5		13-May-08		4:06:20		68.61		32		13-May-08		4:07:53		68		32.5		23-Jun-08		4:25:59		74.01		32

		13-May-08		6:07:10		68		30.5		13-May-08		6:06:20		68.61		31		13-May-08		6:07:53		68		32		23-Jun-08		6:25:59		73.4		32.5

		13-May-08		8:07:10		68.61		29		13-May-08		8:06:20		69.2		31		13-May-08		8:07:53		68.61		31.5		23-Jun-08		8:25:59		72.8		34

		13-May-08		10:07:10		69.8		28		13-May-08		10:06:20		70.41		29.5		13-May-08		10:07:53		68.61		30.5		23-Jun-08		10:25:59		74.01		35.5

		13-May-08		12:07:10		71		27.5		13-May-08		12:06:20		71.6		29		13-May-08		12:07:53		68.61		30.5		23-Jun-08		12:25:59		75.2		35.5

		13-May-08		14:07:10		71.6		28.5		13-May-08		14:06:20		71		30		13-May-08		14:07:53		68.61		31.5		23-Jun-08		14:25:59		76.4		36

		13-May-08		16:07:10		71.6		29.5		13-May-08		16:06:20		69.2		32.5		13-May-08		16:07:53		68.61		33		23-Jun-08		16:25:59		77		36

		13-May-08		18:07:10		71.6		30.5		13-May-08		18:06:20		70.41		33		13-May-08		18:07:53		68.61		34.5		23-Jun-08		18:25:59		77.61		35.5

		13-May-08		20:07:10		71		30		13-May-08		20:06:20		69.8		31.5		13-May-08		20:07:53		68		33.5		23-Jun-08		20:25:59		77.61		34.5

		13-May-08		22:07:10		70.41		30.5		13-May-08		22:06:20		70.41		31.5		13-May-08		22:07:53		68.61		33		23-Jun-08		22:25:59		75.81		34.5

		14-May-08		0:07:10		69.2		31		14-May-08		0:06:20		69.8		32		14-May-08		0:07:53		68		33.5		24-Jun-08		0:25:59		74.6		34.5

		14-May-08		2:07:10		68		32.5		14-May-08		2:06:20		69.2		33.5		14-May-08		2:07:53		68		34.5		24-Jun-08		2:25:59		73.4		34.5

		14-May-08		4:07:10		68		33		14-May-08		4:06:20		69.2		34		14-May-08		4:07:53		68		34.5		24-Jun-08		4:25:59		72.21		34.5

		14-May-08		6:07:10		68.61		33		14-May-08		6:06:20		69.2		34		14-May-08		6:07:53		68		35		24-Jun-08		6:25:59		71		36.5

		14-May-08		8:07:10		69.2		34		14-May-08		8:06:20		70.41		36.5		14-May-08		8:07:53		68		36		24-Jun-08		8:25:59		71		39

		14-May-08		10:07:10		71		34		14-May-08		10:06:20		71		36		14-May-08		10:07:53		67.4		38		24-Jun-08		10:25:59		72.21		40.5

		14-May-08		12:07:10		71.6		28.5		14-May-08		12:06:20		70.41		31.5		14-May-08		12:07:53		68		33		24-Jun-08		12:25:59		72.21		41.5

		14-May-08		14:07:10		71.6		29.5		14-May-08		14:06:20		70.41		32		14-May-08		14:07:53		68		34		24-Jun-08		14:25:59		73.4		39.5

		14-May-08		16:07:10		71.6		26.5		14-May-08		16:06:20		71		28		14-May-08		16:07:53		68		30		24-Jun-08		16:25:59		74.01		39

		14-May-08		18:07:10		71.6		27.5		14-May-08		18:06:20		71		28		14-May-08		18:07:53		68		30.5		24-Jun-08		18:25:59		74.01		38.5

		14-May-08		20:07:10		71.6		35		14-May-08		20:06:20		70.41		39.5		14-May-08		20:07:53		68		39.5		24-Jun-08		20:25:59		74.01		39.5

		14-May-08		22:07:10		71		36		14-May-08		22:06:20		69.8		41		14-May-08		22:07:53		68		40		24-Jun-08		22:25:59		75.2		37

		15-May-08		0:07:10		70.41		36.5		15-May-08		0:06:20		69.8		41		15-May-08		0:07:53		68.61		39.5		25-Jun-08		0:25:59		73.4		37

		15-May-08		2:07:10		69.8		37		15-May-08		2:06:20		69.2		42		15-May-08		2:07:53		68.61		39.5		25-Jun-08		2:25:59		72.21		37

		15-May-08		4:07:10		69.8		38		15-May-08		4:06:20		69.8		42.5		15-May-08		4:07:53		69.2		40.5		25-Jun-08		4:25:59		71		37

		15-May-08		6:07:10		70.41		39		15-May-08		6:06:20		69.8		42.5		15-May-08		6:07:53		68.61		41		25-Jun-08		6:25:59		70.41		38

		15-May-08		8:07:10		71		40		15-May-08		8:06:20		70.41		48.5		15-May-08		8:07:53		68		43.5		25-Jun-08		8:25:59		70.41		40.5

		15-May-08		10:07:10		71.6		40.5		15-May-08		10:06:20		71		46		15-May-08		10:07:53		67.4		46.5		25-Jun-08		10:25:59		72.8		41.5

		15-May-08		12:07:10		71.6		40.5		15-May-08		12:06:20		70.41		46.5		15-May-08		12:07:53		68		46.5		25-Jun-08		12:25:59		73.4		41

		15-May-08		14:07:10		71.6		38		15-May-08		14:06:20		69.8		41		15-May-08		14:07:53		68		43		25-Jun-08		14:25:59		72.8		42

		15-May-08		16:07:10		71.6		37.5		15-May-08		16:06:20		69.8		40.5		15-May-08		16:07:53		68		42.5		25-Jun-08		16:25:59		72.8		41.5

		15-May-08		18:07:10		71.6		39		15-May-08		18:06:20		68.61		42.5		15-May-08		18:07:53		69.2		43		25-Jun-08		18:25:59		74.01		39.5

		15-May-08		20:07:10		71.6		39		15-May-08		20:06:20		68.61		44		15-May-08		20:07:53		68.61		43.5		25-Jun-08		20:25:59		74.01		41

		15-May-08		22:07:10		71.6		37.5		15-May-08		22:06:20		68		44		15-May-08		22:07:53		68.61		42		25-Jun-08		22:25:59		74.6		38.5

		16-May-08		0:07:10		72.21		37		16-May-08		0:06:20		68		42.5		16-May-08		0:07:53		68.61		41.5		26-Jun-08		0:25:59		74.01		37.5

		16-May-08		2:07:10		71.6		37		16-May-08		2:06:20		68		43		16-May-08		2:07:53		69.2		40.5		26-Jun-08		2:25:59		72.8		37.5

		16-May-08		4:07:10		71.6		36.5		16-May-08		4:06:20		68		43		16-May-08		4:07:53		69.2		40.5		26-Jun-08		4:25:59		71.6		38

		16-May-08		6:07:10		71.6		36		16-May-08		6:06:20		68.61		42		16-May-08		6:07:53		69.2		39.5		26-Jun-08		6:25:59		71		38.5

		16-May-08		8:07:10		72.21		36.5		16-May-08		8:06:20		69.8		42		16-May-08		8:07:53		68.61		41		26-Jun-08		8:25:59		71		40.5

		16-May-08		10:07:10		71.6		38		16-May-08		10:06:20		69.2		43		16-May-08		10:07:53		68		43		26-Jun-08		10:25:59		73.4		40.5

		16-May-08		12:07:10		71.6		39.5		16-May-08		12:06:20		70.41		43.5		16-May-08		12:07:53		68		44		26-Jun-08		12:25:59		72.21		43

		16-May-08		14:07:10		71.6		39		16-May-08		14:06:20		70.41		43		16-May-08		14:07:53		68		44		26-Jun-08		14:25:59		72.21		44

		16-May-08		16:07:10		71.6		40		16-May-08		16:06:20		69.2		46		16-May-08		16:07:53		68.61		45		26-Jun-08		16:25:59		72.21		43.5

		16-May-08		18:07:10		71.6		40.5		16-May-08		18:06:20		69.2		45		16-May-08		18:07:53		68.61		45		26-Jun-08		18:25:59		71.6		43

		16-May-08		20:07:10		71.6		42		16-May-08		20:06:20		69.2		48.5		16-May-08		20:07:53		69.2		46.5		26-Jun-08		20:25:59		72.8		40.5

		16-May-08		22:07:10		72.21		41		16-May-08		22:06:20		68.61		54.5		16-May-08		22:07:53		68		46.5		26-Jun-08		22:25:59		73.4		40.5

		17-May-08		0:07:10		72.21		39.5		17-May-08		0:06:20		68.61		50		17-May-08		0:07:53		68.61		44.5		27-Jun-08		0:25:59		72.8		39.5

		17-May-08		2:07:10		72.21		39		17-May-08		2:06:20		68.61		47		17-May-08		2:07:53		68.61		43.5		27-Jun-08		2:25:59		71.6		39

		17-May-08		4:07:10		71.6		39		17-May-08		4:06:20		68		51		17-May-08		4:07:53		68.61		43		27-Jun-08		4:25:59		71		39

		17-May-08		6:07:10		71.6		39		17-May-08		6:06:20		68.61		53		17-May-08		6:07:53		69.2		43		27-Jun-08		6:25:59		70.41		39.5

		17-May-08		8:07:10		72.21		40		17-May-08		8:06:20		69.8		55.5		17-May-08		8:07:53		68		45.5		27-Jun-08		8:25:59		70.41		41

		17-May-08		10:07:10		72.21		40.5		17-May-08		10:06:20		69.8		53.5		17-May-08		10:07:53		68		46		27-Jun-08		10:25:59		72.8		42.5

		17-May-08		12:07:10		71		44.5		17-May-08		12:06:20		69.8		50		17-May-08		12:07:53		68.61		49.5		27-Jun-08		12:25:59		72.21		43

		17-May-08		14:07:10		71.6		45		17-May-08		14:06:20		70.41		52.5		17-May-08		14:07:53		68		51		27-Jun-08		14:25:59		72.21		44.5

		17-May-08		16:07:10		71.6		44.5		17-May-08		16:06:20		69.8		51		17-May-08		16:07:53		68.61		49.5		27-Jun-08		16:25:59		72.8		44

		17-May-08		18:07:10		71.6		41.5		17-May-08		18:06:20		69.2		45.5		17-May-08		18:07:53		68.61		45.5		27-Jun-08		18:25:59		72.8		41

		17-May-08		20:07:10		71.6		41.5		17-May-08		20:06:20		68.61		49		17-May-08		20:07:53		68.61		46		27-Jun-08		20:25:59		73.4		41.5

		17-May-08		22:07:10		72.21		39.5		17-May-08		22:06:20		69.2		48		17-May-08		22:07:53		68		44.5		27-Jun-08		22:25:59		74.01		40

		18-May-08		0:07:10		72.21		39		18-May-08		0:06:20		68		50.5		18-May-08		0:07:53		68.61		43.5		28-Jun-08		0:25:59		73.4		39.5

		18-May-08		2:07:10		71.6		40		18-May-08		2:06:20		68		52		18-May-08		2:07:53		68.61		43.5		28-Jun-08		2:25:59		72.21		39.5

		18-May-08		4:07:10		71		40		18-May-08		4:06:20		68		52.5		18-May-08		4:07:53		69.2		43		28-Jun-08		4:25:59		71.6		39.5

		18-May-08		6:07:10		70.41		39.5		18-May-08		6:06:20		68		50.5		18-May-08		6:07:53		69.2		42		28-Jun-08		6:25:59		71		40

		18-May-08		8:07:10		71		40.5		18-May-08		8:06:20		68.61		53.5		18-May-08		8:07:53		68.61		44		28-Jun-08		8:25:59		71		42

		18-May-08		10:07:10		71.6		42.5		18-May-08		10:06:20		69.2		56.5		18-May-08		10:07:53		68.61		46.5		28-Jun-08		10:25:59		73.4		43

		18-May-08		12:07:10		71.6		44.5		18-May-08		12:06:20		69.2		53.5		18-May-08		12:07:53		68.61		49.5		28-Jun-08		12:25:59		72.8		44

		18-May-08		14:07:10		72.21		48.5		18-May-08		14:06:20		69.2		58.5		18-May-08		14:07:53		68.61		54		28-Jun-08		14:25:59		72.21		45

		18-May-08		16:07:10		72.21		45		18-May-08		16:06:20		68.61		63.5		18-May-08		16:07:53		68.61		51.5		28-Jun-08		16:25:59		72.8		45.5

		18-May-08		18:07:10		72.21		43		18-May-08		18:06:20		68.61		60.5		18-May-08		18:07:53		68.61		49.5		28-Jun-08		18:25:59		72.8		43.5

		18-May-08		20:07:10		72.21		40.5		18-May-08		20:06:20		68.61		52.5		18-May-08		20:07:53		68		46		28-Jun-08		20:25:59		72.8		43.5

		18-May-08		22:07:10		72.21		39		18-May-08		22:06:20		68		51.5		18-May-08		22:07:53		68.61		43.5		28-Jun-08		22:25:59		72.8		42.5

		19-May-08		0:07:10		71		39		19-May-08		0:06:20		68		49.5		19-May-08		0:07:53		69.2		42		29-Jun-08		0:25:59		72.21		42.5

		19-May-08		2:07:10		70.41		39.5		19-May-08		2:06:20		68		49		19-May-08		2:07:53		69.2		42		29-Jun-08		2:25:59		71.6		42.5

		19-May-08		4:07:10		70.41		39		19-May-08		4:06:20		67.4		48		19-May-08		4:07:53		69.2		41.5		29-Jun-08		4:25:59		71		43

		19-May-08		6:07:10		71		39		19-May-08		6:06:20		67.4		49		19-May-08		6:07:53		69.2		41.5		29-Jun-08		6:25:59		71		43.5

		19-May-08		8:07:10		71		39.5		19-May-08		8:06:20		68		49		19-May-08		8:07:53		69.2		42		29-Jun-08		8:25:59		71		44

		19-May-08		10:07:10		70.41		40.5		19-May-08		10:06:20		68		48.5		19-May-08		10:07:53		69.2		43		29-Jun-08		10:25:59		71.6		44.5

		19-May-08		12:07:10		71		41.5		19-May-08		12:06:20		68.61		51		19-May-08		12:07:53		69.2		44.5		29-Jun-08		12:25:59		72.21		45.5

		19-May-08		14:07:10		71.6		41.5		19-May-08		14:06:20		68		54.5		19-May-08		14:07:53		69.8		45		29-Jun-08		14:25:59		74.01		45.5

		19-May-08		16:07:10		72.21		42		19-May-08		16:06:20		68.61		51.5		19-May-08		16:07:53		69.2		46		29-Jun-08		16:25:59		75.2		44.5

		19-May-08		18:07:10		72.21		40		19-May-08		18:06:20		68		55		19-May-08		18:07:53		69.2		44.5		29-Jun-08		18:25:59		75.81		43.5

		19-May-08		20:07:10		72.21		39		19-May-08		20:06:20		68.61		50.5		19-May-08		20:07:53		69.2		43		29-Jun-08		20:25:59		75.2		43

		19-May-08		22:07:10		71		39		19-May-08		22:06:20		67.4		52.5		19-May-08		22:07:53		69.2		42		29-Jun-08		22:25:59		74.01		42.5

		20-May-08		0:07:10		71		39.5		20-May-08		0:06:20		67.4		51		20-May-08		0:07:53		69.2		42		30-Jun-08		0:25:59		72.21		42.5

		20-May-08		2:07:10		71		39.5		20-May-08		2:06:20		68		50		20-May-08		2:07:53		69.2		42		30-Jun-08		2:25:59		71.6		42.5

		20-May-08		4:07:10		70.41		39.5		20-May-08		4:06:20		67.4		49.5		20-May-08		4:07:53		69.2		41.5		30-Jun-08		4:25:59		71		42.5

		20-May-08		6:07:10		71		39.5		20-May-08		6:06:20		68		49.5		20-May-08		6:07:53		69.2		41.5		30-Jun-08		6:25:59		70.41		43

		20-May-08		8:07:10		71		39		20-May-08		8:06:20		68.61		50.5		20-May-08		8:07:53		68.61		44		30-Jun-08		8:25:59		70.41		43.5

		20-May-08		10:07:10		71		39		20-May-08		10:06:20		71		44.5		20-May-08		10:07:53		68.61		43		30-Jun-08		10:25:59		70.41		44

		20-May-08		12:07:10		71		41		20-May-08		12:06:20		71		49.5		20-May-08		12:07:53		68		45		30-Jun-08		12:25:59		72.21		44.5

		20-May-08		14:07:10		71		43		20-May-08		14:06:20		71		55.5		20-May-08		14:07:53		68		48		30-Jun-08		14:25:59		73.4		44.5

		20-May-08		16:07:10		71.6		42		20-May-08		16:06:20		70.41		49.5		20-May-08		16:07:53		68.61		46.5		30-Jun-08		16:25:59		74.6		44.5

		20-May-08		18:07:10		71.6		41		20-May-08		18:06:20		69.8		51		20-May-08		18:07:53		69.2		44.5		30-Jun-08		18:25:59		75.2		43

		20-May-08		20:07:10		71		39		20-May-08		20:06:20		69.8		48.5		20-May-08		20:07:53		69.2		42.5		30-Jun-08		20:25:59		75.2		42.5

		20-May-08		22:07:10		71		39.5		20-May-08		22:06:20		69.8		48		20-May-08		22:07:53		69.8		41.5		30-Jun-08		22:25:59		73.4		42

		21-May-08		0:07:10		70.41		40		21-May-08		0:06:20		69.2		48.5		21-May-08		0:07:53		69.2		42		1-Jul-08		0:25:59		72.21		42

		21-May-08		2:07:10		70.41		40		21-May-08		2:06:20		68.61		48.5		21-May-08		2:07:53		69.8		42		1-Jul-08		2:25:59		71.6		42

		21-May-08		4:07:10		71		39.5		21-May-08		4:06:20		68.61		48		21-May-08		4:07:53		69.2		41.5		1-Jul-08		4:25:59		71		42

		21-May-08		6:07:10		71		39.5		21-May-08		6:06:20		68		48.5		21-May-08		6:07:53		69.8		41		1-Jul-08		6:25:59		71		43

		21-May-08		8:07:10		71		39.5		21-May-08		8:06:20		70.41		48.5		21-May-08		8:07:53		68.61		42		1-Jul-08		8:25:59		70.41		45

		21-May-08		10:07:10		71		40		21-May-08		10:06:20		71		47		21-May-08		10:07:53		68		43		1-Jul-08		10:25:59		72.21		45

		21-May-08		12:07:10		71		41		21-May-08		12:06:20		71		51		21-May-08		12:07:53		68.61		44.5		1-Jul-08		12:25:59		72.21		45

		21-May-08		14:07:10		71		44		21-May-08		14:06:20		71.6		54		21-May-08		14:07:53		68		48.5		1-Jul-08		14:25:59		72.8		46.5

		21-May-08		16:07:10		71		39.5		21-May-08		16:06:20		71		45		21-May-08		16:07:53		69.2		43.5		1-Jul-08		16:25:59		72.8		46.5

		21-May-08		18:07:10		71.6		32		21-May-08		18:06:20		71		34		21-May-08		18:07:53		69.2		36.5		1-Jul-08		18:25:59		72.8		44.5

		21-May-08		20:07:10		71		30		21-May-08		20:06:20		70.41		30		21-May-08		20:07:53		69.8		31.5		1-Jul-08		20:25:59		74.01		42

		21-May-08		22:07:10		70.41		36		21-May-08		22:06:20		70.41		39		21-May-08		22:07:53		69.8		38		1-Jul-08		22:25:59		74.01		43.5

		22-May-08		0:07:10		69.2		35		22-May-08		0:06:20		69.2		37.5		22-May-08		0:07:53		68.61		37		2-Jul-08		0:25:59		73.4		43

		22-May-08		2:07:10		68.61		34.5		22-May-08		2:06:20		69.2		35.5		22-May-08		2:07:53		68.61		36.5		2-Jul-08		2:25:59		72.21		43

		22-May-08		4:07:10		68.61		34		22-May-08		4:06:20		69.2		35		22-May-08		4:07:53		68.61		35		2-Jul-08		4:25:59		72.21		43.5

		22-May-08		6:07:10		69.8		32.5		22-May-08		6:06:20		69.2		34.5		22-May-08		6:07:53		69.2		34.5		2-Jul-08		6:25:59		71.6		44.5

		22-May-08		8:07:10		69.8		32.5		22-May-08		8:06:20		71		34.5		22-May-08		8:07:53		68.61		35		2-Jul-08		8:25:59		71		46.5

		22-May-08		10:07:10		70.41		33.5		22-May-08		10:06:20		71.6		34		22-May-08		10:07:53		68.61		35.5		2-Jul-08		10:25:59		72.21		47.5

		22-May-08		12:07:10		71		33.5		22-May-08		12:06:20		70.41		35.5		22-May-08		12:07:53		69.2		36		2-Jul-08		12:25:59		72.21		46.5

		22-May-08		14:07:10		71		34.5		22-May-08		14:06:20		69.8		37		22-May-08		14:07:53		68.61		38		2-Jul-08		14:25:59		72.21		47.5

		22-May-08		16:07:10		71		35		22-May-08		16:06:20		69.2		38		22-May-08		16:07:53		68.61		38.5		2-Jul-08		16:25:59		72.8		45.5

		22-May-08		18:07:10		71		35		22-May-08		18:06:20		68.61		37.5		22-May-08		18:07:53		68		38		2-Jul-08		18:25:59		72.8		44.5

		22-May-08		20:07:10		70.41		34.5		22-May-08		20:06:20		68.61		37		22-May-08		20:07:53		68		37		2-Jul-08		20:25:59		73.4		42.5

		22-May-08		22:07:10		69.2		33.5		22-May-08		22:06:20		68		36.5		22-May-08		22:07:53		68.61		36		2-Jul-08		22:25:59		74.01		43

		23-May-08		0:07:10		68.61		33.5		23-May-08		0:06:20		68		36		23-May-08		0:07:53		68		35.5		3-Jul-08		0:25:59		72.8		42.5

		23-May-08		2:07:10		68		32.5		23-May-08		2:06:20		68		34.5		23-May-08		2:07:53		68		34.5		3-Jul-08		2:25:59		71.6		42

		23-May-08		4:07:10		68.61		31		23-May-08		4:06:20		68		32.5		23-May-08		4:07:53		68.61		33		3-Jul-08		4:25:59		71		42.5

		23-May-08		6:07:10		69.8		30		23-May-08		6:06:20		68		32		23-May-08		6:07:53		69.2		32		3-Jul-08		6:25:59		70.41		43

		23-May-08		8:07:10		69.8		30		23-May-08		8:06:20		68.61		33		23-May-08		8:07:53		69.2		32		3-Jul-08		8:25:59		71		44.5

		23-May-08		10:07:10		70.41		30		23-May-08		10:06:20		68.61		32.5		23-May-08		10:07:53		68		32		3-Jul-08		10:25:59		72.21		45

		23-May-08		12:07:10		71		25		23-May-08		12:06:20		69.2		27.5		23-May-08		12:07:53		68		28.5		3-Jul-08		12:25:59		71.6		46.5

		23-May-08		14:07:10		71		28.5		23-May-08		14:06:20		68.61		30		23-May-08		14:07:53		67.4		31		3-Jul-08		14:25:59		72.21		46

		23-May-08		16:07:10		71		29.5		23-May-08		16:06:20		68		33		23-May-08		16:07:53		68.61		32.5		3-Jul-08		16:25:59		72.21		45.5

		23-May-08		18:07:10		71		32		23-May-08		18:06:20		68.61		34.5		23-May-08		18:07:53		68.61		35		3-Jul-08		18:25:59		73.4		44

		23-May-08		20:07:10		71		33.5		23-May-08		20:06:20		69.2		36		23-May-08		20:07:53		68.61		36		3-Jul-08		20:25:59		74.01		42

		23-May-08		22:07:10		70.41		33		23-May-08		22:06:20		68.61		37		23-May-08		22:07:53		68.61		36		3-Jul-08		22:25:59		74.6		42

		24-May-08		0:07:10		69.2		33.5		24-May-08		0:06:20		68		37		24-May-08		0:07:53		68.61		36		4-Jul-08		0:25:59		73.4		41.5

		24-May-08		2:07:10		68.61		33.5		24-May-08		2:06:20		68		37		24-May-08		2:07:53		68		36		4-Jul-08		2:25:59		72.21		41.5

		24-May-08		4:07:10		69.2		33		24-May-08		4:06:20		67.4		37		24-May-08		4:07:53		68.61		35		4-Jul-08		4:25:59		71.6		41.5

		24-May-08		6:07:10		70.41		32.5		24-May-08		6:06:20		68		36		24-May-08		6:07:53		69.2		34.5		4-Jul-08		6:25:59		71		42

		24-May-08		8:07:10		70.41		32.5		24-May-08		8:06:20		67.4		38.5		24-May-08		8:07:53		68.61		35.5		4-Jul-08		8:25:59		71		44.5

		24-May-08		10:07:10		70.41		34		24-May-08		10:06:20		70.41		36		24-May-08		10:07:53		68.61		36.5		4-Jul-08		10:25:59		71.6		45

		24-May-08		12:07:10		71		35		24-May-08		12:06:20		71		36		24-May-08		12:07:53		69.2		36.5		4-Jul-08		12:25:59		72.21		48.5

		24-May-08		14:07:10		71		34		24-May-08		14:06:20		71		37		24-May-08		14:07:53		68		37.5		4-Jul-08		14:25:59		73.4		50

		24-May-08		16:07:10		71		34.5		24-May-08		16:06:20		69.8		37		24-May-08		16:07:53		69.2		37		4-Jul-08		16:25:59		72.8		49

		24-May-08		18:07:10		70.41		35.5		24-May-08		18:06:20		70.41		39		24-May-08		18:07:53		69.2		38		4-Jul-08		18:25:59		73.4		48.5

		24-May-08		20:07:10		70.41		36.5		24-May-08		20:06:20		69.8		41		24-May-08		20:07:53		68.61		39		4-Jul-08		20:25:59		74.01		46

		24-May-08		22:07:10		71		36.5		24-May-08		22:06:20		69.2		42.5		24-May-08		22:07:53		68.61		39.5		4-Jul-08		22:25:59		74.01		47

		25-May-08		0:07:10		70.41		37		25-May-08		0:06:20		69.2		42.5		25-May-08		0:07:53		69.2		39.5		5-Jul-08		0:25:59		73.4		46.5

		25-May-08		2:07:10		70.41		37		25-May-08		2:06:20		68.61		42.5		25-May-08		2:07:53		69.2		39		5-Jul-08		2:25:59		72.21		46

		25-May-08		4:07:10		70.41		37.5		25-May-08		4:06:20		68.61		43		25-May-08		4:07:53		69.2		39		5-Jul-08		4:25:59		71.6		45.5

		25-May-08		6:07:10		70.41		37.5		25-May-08		6:06:20		68.61		45		25-May-08		6:07:53		69.2		39.5		5-Jul-08		6:25:59		71		46.5

		25-May-08		8:07:10		70.41		38		25-May-08		8:06:20		68.61		45		25-May-08		8:07:53		69.2		39.5		5-Jul-08		8:25:59		71		48

		25-May-08		10:07:10		70.41		39.5		25-May-08		10:06:20		68.61		48		25-May-08		10:07:53		69.2		41.5		5-Jul-08		10:25:59		72.21		48

		25-May-08		12:07:10		70.41		40		25-May-08		12:06:20		69.2		50		25-May-08		12:07:53		69.8		42		5-Jul-08		12:25:59		72.21		48.5

		25-May-08		14:07:10		69.8		37.5		25-May-08		14:06:20		68.61		46		25-May-08		14:07:53		69.8		40		5-Jul-08		14:25:59		73.4		48

		25-May-08		16:07:10		69.8		38.5		25-May-08		16:06:20		68.61		44.5		25-May-08		16:07:53		69.2		39.5		5-Jul-08		16:25:59		73.4		47.5

		25-May-08		18:07:10		69.8		39.5		25-May-08		18:06:20		69.2		48.5		25-May-08		18:07:53		69.8		41		5-Jul-08		18:25:59		73.4		46.5

		25-May-08		20:07:10		70.41		40		25-May-08		20:06:20		69.2		50		25-May-08		20:07:53		69.2		41.5		5-Jul-08		20:25:59		72.8		45.5

		25-May-08		22:07:10		70.41		40		25-May-08		22:06:20		68.61		48		25-May-08		22:07:53		69.2		41		5-Jul-08		22:25:59		72.8		47

		26-May-08		0:07:10		70.41		39		26-May-08		0:06:20		68		47		26-May-08		0:07:53		69.2		40.5		6-Jul-08		0:25:59		72.21		46

		26-May-08		2:07:10		70.41		37.5		26-May-08		2:06:20		67.4		45		26-May-08		2:07:53		69.2		39		6-Jul-08		2:25:59		72.21		45.5

		26-May-08		4:07:10		70.41		36.5		26-May-08		4:06:20		66.81		44		26-May-08		4:07:53		69.2		38		6-Jul-08		4:25:59		71		45.5

		26-May-08		6:07:10		70.41		36.5		26-May-08		6:06:20		66.81		44.5		26-May-08		6:07:53		69.8		38		6-Jul-08		6:25:59		71		45

		26-May-08		8:07:10		70.41		38.5		26-May-08		8:06:20		67.4		45.5		26-May-08		8:07:53		69.8		39		6-Jul-08		8:25:59		70.41		45.5

		26-May-08		10:07:10		69.8		37		26-May-08		10:06:20		69.2		43		26-May-08		10:07:53		69.2		39.5		6-Jul-08		10:25:59		71.6		47.5

		26-May-08		12:07:10		69.8		37		26-May-08		12:06:20		69.2		40.5		26-May-08		12:07:53		69.2		38.5		6-Jul-08		12:25:59		73.4		48.5

		26-May-08		14:07:10		70.41		37		26-May-08		14:06:20		69.2		40		26-May-08		14:07:53		69.8		38.5		6-Jul-08		14:25:59		75.2		49

		26-May-08		16:07:10		70.41		36		26-May-08		16:06:20		69.2		39		26-May-08		16:07:53		69.2		38		6-Jul-08		16:25:59		77		47.5

		26-May-08		18:07:10		70.41		35.5		26-May-08		18:06:20		68.61		38.5		26-May-08		18:07:53		69.2		37		6-Jul-08		18:25:59		77.61		45.5

		26-May-08		20:07:10		70.41		36		26-May-08		20:06:20		69.2		38.5		26-May-08		20:07:53		69.8		37.5		6-Jul-08		20:25:59		78.2		45

		26-May-08		22:07:10		69.8		37.5		26-May-08		22:06:20		69.2		44		26-May-08		22:07:53		69.2		39.5		6-Jul-08		22:25:59		77		45.5

		27-May-08		0:07:10		70.41		38		27-May-08		0:06:20		68.61		44.5		27-May-08		0:07:53		69.8		39.5		7-Jul-08		0:25:59		75.81		45.5

		27-May-08		2:07:10		70.41		37.5		27-May-08		2:06:20		68		45		27-May-08		2:07:53		69.8		39		7-Jul-08		2:25:59		74.6		44.5

		27-May-08		4:07:10		70.41		37.5		27-May-08		4:06:20		67.4		45.5		27-May-08		4:07:53		69.8		39		7-Jul-08		4:25:59		74.01		44.5

		27-May-08		6:07:10		70.41		37		27-May-08		6:06:20		67.4		45		27-May-08		6:07:53		69.2		38.5		7-Jul-08		6:25:59		72.8		44

		27-May-08		8:07:10		70.41		38		27-May-08		8:06:20		68		45		27-May-08		8:07:53		69.2		39.5		7-Jul-08		8:25:59		72.21		44.5

		27-May-08		10:07:10		69.8		37.5		27-May-08		10:06:20		69.2		42.5		27-May-08		10:07:53		69.2		39		7-Jul-08		10:25:59		73.4		46.5

		27-May-08		12:07:10		70.41		39		27-May-08		12:06:20		69.2		45		27-May-08		12:07:53		69.2		40		7-Jul-08		12:25:59		74.6		48

		27-May-08		14:07:10		70.41		38.5		27-May-08		14:06:20		68.61		45		27-May-08		14:07:53		69.2		40.5		7-Jul-08		14:25:59		76.4		49

		27-May-08		16:07:10		70.41		39		27-May-08		16:06:20		69.2		45.5		27-May-08		16:07:53		69.2		40.5		7-Jul-08		16:25:59		77.61		47.5

		27-May-08		18:07:10		70.41		39		27-May-08		18:06:20		69.2		46		27-May-08		18:07:53		69.2		40.5		7-Jul-08		18:25:59		78.2		46

		27-May-08		20:07:10		70.41		38.5		27-May-08		20:06:20		69.2		46		27-May-08		20:07:53		69.8		40		7-Jul-08		20:25:59		78.2		44.5

		27-May-08		22:07:10		70.41		39		27-May-08		22:06:20		69.2		45		27-May-08		22:07:53		69.8		40		7-Jul-08		22:25:59		76.4		43.5

		28-May-08		0:07:10		70.41		38.5		28-May-08		0:06:20		69.2		46		28-May-08		0:07:53		69.8		40		8-Jul-08		0:25:59		75.2		42.5

		28-May-08		2:07:10		70.41		39		28-May-08		2:06:20		69.2		46.5		28-May-08		2:07:53		69.2		40.5		8-Jul-08		2:25:59		74.01		42.5

		28-May-08		4:07:10		70.41		39		28-May-08		4:06:20		68.61		47		28-May-08		4:07:53		69.8		40.5		8-Jul-08		4:25:59		72.8		42

		28-May-08		6:07:10		70.41		39.5		28-May-08		6:06:20		69.2		47.5		28-May-08		6:07:53		69.2		41		8-Jul-08		6:25:59		72.21		41.5

		28-May-08		8:07:10		70.41		39		28-May-08		8:06:20		69.2		50		28-May-08		8:07:53		69.2		41.5		8-Jul-08		8:25:59		71.6		46

		28-May-08		10:07:10		71		38.5		28-May-08		10:06:20		69.8		45		28-May-08		10:07:53		68.61		41		8-Jul-08		10:25:59		72.8		47

		28-May-08		12:07:10		71		38.5		28-May-08		12:06:20		69.8		44		28-May-08		12:07:53		69.2		41.5		8-Jul-08		12:25:59		72.8		49

		28-May-08		14:07:10		71		39		28-May-08		14:06:20		69.2		43.5		28-May-08		14:07:53		68.61		42.5		8-Jul-08		14:25:59		72.8		49

		28-May-08		16:07:10		71		38		28-May-08		16:06:20		69.8		45.5		28-May-08		16:07:53		68.61		41.5		8-Jul-08		16:25:59		73.4		48.5

		28-May-08		18:07:10		71		37.5		28-May-08		18:06:20		71		41.5		28-May-08		18:07:53		69.2		40.5		8-Jul-08		18:25:59		73.4		47

		28-May-08		20:07:10		71		37.5		28-May-08		20:06:20		70.41		42.5		28-May-08		20:07:53		69.2		40		8-Jul-08		20:25:59		74.6		45.5

		28-May-08		22:07:10		70.41		37.5		28-May-08		22:06:20		71		41.5		28-May-08		22:07:53		69.2		39		8-Jul-08		22:25:59		75.2		45

		29-May-08		0:07:10		70.41		37.5		29-May-08		0:06:20		69.8		43		29-May-08		0:07:53		69.2		39.5		9-Jul-08		0:25:59		75.2		44

		29-May-08		2:07:10		70.41		38		29-May-08		2:06:20		69.2		44		29-May-08		2:07:53		69.8		39.5		9-Jul-08		2:25:59		74.6		44

		29-May-08		4:07:10		70.41		38		29-May-08		4:06:20		68.61		45		29-May-08		4:07:53		69.8		39.5		9-Jul-08		4:25:59		74.01		43.5

		29-May-08		6:07:10		70.41		38.5		29-May-08		6:06:20		68.61		45.5		29-May-08		6:07:53		69.8		40		9-Jul-08		6:25:59		73.4		42

		29-May-08		8:07:10		71		38.5		29-May-08		8:06:20		69.8		46.5		29-May-08		8:07:53		69.2		40.5		9-Jul-08		8:25:59		72.21		45.5

		29-May-08		10:07:10		71		36.5		29-May-08		10:06:20		69.2		41.5		29-May-08		10:07:53		68.61		39.5		9-Jul-08		10:25:59		72.8		50

		29-May-08		12:07:10		71		37.5		29-May-08		12:06:20		69.8		43		29-May-08		12:07:53		69.2		40		9-Jul-08		12:25:59		72.8		50.5

		29-May-08		14:07:10		71		37.5		29-May-08		14:06:20		69.2		41.5		29-May-08		14:07:53		68.61		40.5		9-Jul-08		14:25:59		72.21		49.5

		29-May-08		16:07:10		71		37		29-May-08		16:06:20		69.8		41		29-May-08		16:07:53		68.61		40.5		9-Jul-08		16:25:59		72.8		48.5

		29-May-08		18:07:10		71		38		29-May-08		18:06:20		70.41		42.5		29-May-08		18:07:53		68.61		41		9-Jul-08		18:25:59		73.4		47.5

		29-May-08		20:07:10		71		38		29-May-08		20:06:20		70.41		44.5		29-May-08		20:07:53		69.2		40.5		9-Jul-08		20:25:59		74.01		45

		29-May-08		22:07:10		71		38		29-May-08		22:06:20		70.41		43.5		29-May-08		22:07:53		69.8		40		9-Jul-08		22:25:59		75.81		44

		30-May-08		0:07:10		69.8		38.5		30-May-08		0:06:20		69.2		47		30-May-08		0:07:53		67.4		42.5		10-Jul-08		0:25:59		75.2		44

		30-May-08		2:07:10		70.41		39		30-May-08		2:06:20		68.61		46.5		30-May-08		2:07:53		69.2		41		10-Jul-08		2:25:59		74.6		44

		30-May-08		4:07:10		71		39		30-May-08		4:06:20		68.61		47.5		30-May-08		4:07:53		69.8		40.5		10-Jul-08		4:25:59		74.01		44.5

		30-May-08		6:07:10		71		38.5		30-May-08		6:06:20		68		47.5		30-May-08		6:07:53		69.8		40.5		10-Jul-08		6:25:59		73.4		43

		30-May-08		8:07:10		70.41		39.5		30-May-08		8:06:20		70.41		48.5		30-May-08		8:07:53		68.61		42		10-Jul-08		8:25:59		73.4		46

		30-May-08		10:07:10		71		39		30-May-08		10:06:20		71		44.5		30-May-08		10:07:53		68.61		41.5		10-Jul-08		10:25:59		74.01		47.5

		30-May-08		12:07:10		71.6		39		30-May-08		12:06:20		69.2		49		30-May-08		12:07:53		69.2		41.5		10-Jul-08		12:25:59		72.8		49.5

		30-May-08		14:07:10		71		39.5		30-May-08		14:06:20		69.2		45.5		30-May-08		14:07:53		69.2		42.5		10-Jul-08		14:25:59		72.21		51

		30-May-08		16:07:10		71		39.5		30-May-08		16:06:20		69.2		49		30-May-08		16:07:53		68		44		10-Jul-08		16:25:59		72.8		50.5

		30-May-08		18:07:10		71		39		30-May-08		18:06:20		69.2		47.5		30-May-08		18:07:53		68.61		42		10-Jul-08		18:25:59		73.4		49

		30-May-08		20:07:10		71		38.5		30-May-08		20:06:20		69.2		44		30-May-08		20:07:53		69.2		41		10-Jul-08		20:25:59		74.6		46

		30-May-08		22:07:10		70.41		38.5		30-May-08		22:06:20		68.61		45		30-May-08		22:07:53		69.2		41		10-Jul-08		22:25:59		75.81		47

		31-May-08		0:07:10		71		39.5		31-May-08		0:06:20		68		49.5		31-May-08		0:07:53		69.2		42		11-Jul-08		0:25:59		75.81		46

		31-May-08		2:07:10		70.41		39		31-May-08		2:06:20		68		49.5		31-May-08		2:07:53		69.2		41		11-Jul-08		2:25:59		74.6		46.5

		31-May-08		4:07:10		70.41		39		31-May-08		4:06:20		68		49		31-May-08		4:07:53		69.8		40.5		11-Jul-08		4:25:59		74.01		46.5

		31-May-08		6:07:10		70.41		39		31-May-08		6:06:20		68		51.5		31-May-08		6:07:53		68.61		41.5		11-Jul-08		6:25:59		73.4		44.5

		31-May-08		8:07:10		71		39		31-May-08		8:06:20		68		45.5		31-May-08		8:07:53		68		42.5		11-Jul-08		8:25:59		72.21		47.5

		31-May-08		10:07:10		70.41		39.5		31-May-08		10:06:20		69.2		51		31-May-08		10:07:53		68		42.5		11-Jul-08		10:25:59		73.4		50.5

		31-May-08		12:07:10		71		40		31-May-08		12:06:20		69.2		49		31-May-08		12:07:53		68		44		11-Jul-08		12:25:59		72.8		51

		31-May-08		14:07:10		71		42		31-May-08		14:06:20		69.2		48		31-May-08		14:07:53		68.61		45.5		11-Jul-08		14:25:59		72.8		51.5

		31-May-08		16:07:10		71		40.5		31-May-08		16:06:20		69.2		51		31-May-08		16:07:53		68.61		45		11-Jul-08		16:25:59		72.8		49

		31-May-08		18:07:10		71		40.5		31-May-08		18:06:20		68.61		52.5		31-May-08		18:07:53		68		45		11-Jul-08		18:25:59		73.4		47.5

		31-May-08		20:07:10		71		39.5		31-May-08		20:06:20		68.61		52		31-May-08		20:07:53		68.61		43		11-Jul-08		20:25:59		74.01		46.5

		31-May-08		22:07:10		70.41		39		31-May-08		22:06:20		69.2		48		31-May-08		22:07:53		69.8		41		11-Jul-08		22:25:59		75.2		45

		1-Jun-08		0:07:10		70.41		39.5		1-Jun-08		0:06:20		68.61		47.5		1-Jun-08		0:07:53		68.61		41.5		12-Jul-08		0:25:59		74.6		43.5

		1-Jun-08		2:07:10		70.41		39		1-Jun-08		2:06:20		68.61		47.5		1-Jun-08		2:07:53		69.2		41		12-Jul-08		2:25:59		73.4		44

		1-Jun-08		4:07:10		70.41		39		1-Jun-08		4:06:20		68.61		47.5		1-Jun-08		4:07:53		69.2		41.5		12-Jul-08		4:25:59		72.21		44.5

		1-Jun-08		6:07:10		70.41		39		1-Jun-08		6:06:20		67.4		50.5		1-Jun-08		6:07:53		69.8		41		12-Jul-08		6:25:59		72.21		44

		1-Jun-08		8:07:10		70.41		39.5		1-Jun-08		8:06:20		67.4		51		1-Jun-08		8:07:53		69.2		41.5		12-Jul-08		8:25:59		71.6		46.5

		1-Jun-08		10:07:10		70.41		39.5		1-Jun-08		10:06:20		67.4		50		1-Jun-08		10:07:53		69.8		41		12-Jul-08		10:25:59		72.8		48

		1-Jun-08		12:07:10		70.41		39.5		1-Jun-08		12:06:20		67.4		50.5		1-Jun-08		12:07:53		69.2		42		12-Jul-08		12:25:59		74.6		46.5

		1-Jun-08		14:07:10		71		41		1-Jun-08		14:06:20		68.61		52		1-Jun-08		14:07:53		69.2		43.5		12-Jul-08		14:25:59		74.6		46.5

		1-Jun-08		16:07:10		71		40		1-Jun-08		16:06:20		69.2		50		1-Jun-08		16:07:53		69.2		43.5		12-Jul-08		16:25:59		75.81		45

		1-Jun-08		18:07:10		71.6		39.5		1-Jun-08		18:06:20		69.2		47.5		1-Jun-08		18:07:53		69.2		43		12-Jul-08		18:25:59		75.2		44.5

		1-Jun-08		20:07:10		71.6		38.5		1-Jun-08		20:06:20		68.61		47		1-Jun-08		20:07:53		69.2		42		12-Jul-08		20:25:59		75.81		41.5

		1-Jun-08		22:07:10		70.41		38.5		1-Jun-08		22:06:20		68		47.5		1-Jun-08		22:07:53		68.61		41		12-Jul-08		22:25:59		76.4		43

		2-Jun-08		0:07:10		70.41		38.5		2-Jun-08		0:06:20		68.61		46		2-Jun-08		0:07:53		68.61		41		13-Jul-08		0:25:59		76.4		43

		2-Jun-08		2:07:10		70.41		38		2-Jun-08		2:06:20		68		46		2-Jun-08		2:07:53		68.61		40.5		13-Jul-08		2:25:59		75.81		44

		2-Jun-08		4:07:10		70.41		37		2-Jun-08		4:06:20		67.4		45		2-Jun-08		4:07:53		68.61		39.5		13-Jul-08		4:25:59		75.81		44

		2-Jun-08		6:07:10		69.8		36		2-Jun-08		6:06:20		66.2		44		2-Jun-08		6:07:53		68.61		38.5		13-Jul-08		6:25:59		75.81		44.5

		2-Jun-08		8:07:10		70.41		38		2-Jun-08		8:06:20		66.81		46		2-Jun-08		8:07:53		69.2		40		13-Jul-08		8:25:59		75.81		44.5

		2-Jun-08		10:07:10		69.8		37		2-Jun-08		10:06:20		68.61		40.5		2-Jun-08		10:07:53		68.61		39.5		13-Jul-08		10:25:59		75.81		44.5

		2-Jun-08		12:07:10		70.41		38		2-Jun-08		12:06:20		69.2		41		2-Jun-08		12:07:53		69.2		39.5		13-Jul-08		12:25:59		76.4		44

		2-Jun-08		14:07:10		71		39		2-Jun-08		14:06:20		69.8		42		2-Jun-08		14:07:53		69.2		41.5		13-Jul-08		14:25:59		77.61		44.5

		2-Jun-08		16:07:10		71		38.5		2-Jun-08		16:06:20		69.2		45.5		2-Jun-08		16:07:53		65.01		46		13-Jul-08		16:25:59		78.8		43.5

		2-Jun-08		18:07:10		71		38.5		2-Jun-08		18:06:20		68.61		45		2-Jun-08		18:07:53		67.4		43		13-Jul-08		18:25:59		78.8		43

		2-Jun-08		20:07:10		71		37.5		2-Jun-08		20:06:20		67.4		47		2-Jun-08		20:07:53		66.81		43.5		13-Jul-08		20:25:59		78.8		43.5

		2-Jun-08		22:07:10		69.8		37		2-Jun-08		22:06:20		68		45		2-Jun-08		22:07:53		67.4		42		13-Jul-08		22:25:59		77.61		42.5

		3-Jun-08		0:07:10		69.8		37		3-Jun-08		0:06:20		67.4		44		3-Jun-08		0:07:53		67.4		41		14-Jul-08		0:25:59		77		42.5

		3-Jun-08		2:07:10		70.41		36.5		3-Jun-08		2:06:20		66.81		43.5		3-Jun-08		2:07:53		66.81		40.5		14-Jul-08		2:25:59		76.4		42.5

		3-Jun-08		4:07:10		69.8		35		3-Jun-08		4:06:20		66.2		43		3-Jun-08		4:07:53		67.4		39.5		14-Jul-08		4:25:59		75.81		42.5

		3-Jun-08		6:07:10		70.41		35.5		3-Jun-08		6:06:20		66.2		42.5		3-Jun-08		6:07:53		67.4		38.5		14-Jul-08		6:25:59		75.2		42

		3-Jun-08		8:07:10		70.41		37		3-Jun-08		8:06:20		68		42		3-Jun-08		8:07:53		68.61		39.5		14-Jul-08		8:25:59		74.6		42.5

		3-Jun-08		10:07:10		71		37		3-Jun-08		10:06:20		68		44.5		3-Jun-08		10:07:53		67.4		41.5		14-Jul-08		10:25:59		75.2		42.5

		3-Jun-08		12:07:10		71		37.5		3-Jun-08		12:06:20		71		41		3-Jun-08		12:07:53		68		41.5		14-Jul-08		12:25:59		76.4		43

		3-Jun-08		14:07:10		71		39.5		3-Jun-08		14:06:20		70.41		45.5		3-Jun-08		14:07:53		66.81		45		14-Jul-08		14:25:59		77		43.5

		3-Jun-08		16:07:10		71		39.5		3-Jun-08		16:06:20		69.2		44.5		3-Jun-08		16:07:53		67.4		44.5		14-Jul-08		16:25:59		78.2		43.5

		3-Jun-08		18:07:10		71		39.5		3-Jun-08		18:06:20		69.2		45		3-Jun-08		18:07:53		67.4		44.5		14-Jul-08		18:25:59		78.8		43

		3-Jun-08		20:07:10		71		30.5		3-Jun-08		20:06:20		69.2		31.5		3-Jun-08		20:07:53		67.4		34.5		14-Jul-08		20:25:59		78.8		42.5

		3-Jun-08		22:07:10		70.41		27		3-Jun-08		22:06:20		68.61		29.5		3-Jun-08		22:07:53		68		31		14-Jul-08		22:25:59		77.61		41.5

		4-Jun-08		0:07:10		69.2		34		4-Jun-08		0:06:20		68.61		37		4-Jun-08		0:07:53		68		37		15-Jul-08		0:25:59		77		41

		4-Jun-08		2:07:10		69.2		35.5		4-Jun-08		2:06:20		68		40		4-Jun-08		2:07:53		68		38		15-Jul-08		2:25:59		76.4		41

		4-Jun-08		4:07:10		68.61		35		4-Jun-08		4:06:20		67.4		39.5		4-Jun-08		4:07:53		68		37.5		15-Jul-08		4:25:59		75.81		41.5

		4-Jun-08		6:07:10		69.8		34.5		4-Jun-08		6:06:20		68		39		4-Jun-08		6:07:53		68.61		37		15-Jul-08		6:25:59		75.2		41

		4-Jun-08		8:07:10		69.8		38.5		4-Jun-08		8:06:20		68		46		4-Jun-08		8:07:53		68		40.5		15-Jul-08		8:25:59		74.01		43.5

		4-Jun-08		10:07:10		70.41		41		4-Jun-08		10:06:20		69.8		53		4-Jun-08		10:07:53		68		45		15-Jul-08		10:25:59		74.6		45

		4-Jun-08		12:07:10		71		42.5		4-Jun-08		12:06:20		69.8		50		4-Jun-08		12:07:53		68		46.5		15-Jul-08		12:25:59		75.2		44.5

		4-Jun-08		14:07:10		70.41		41.5		4-Jun-08		14:06:20		69.2		53		4-Jun-08		14:07:53		66.81		47		15-Jul-08		14:25:59		75.81		45

		4-Jun-08		16:07:10		70.41		40		4-Jun-08		16:06:20		70.41		44.5		4-Jun-08		16:07:53		67.4		44.5		15-Jul-08		16:25:59		75.81		44

		4-Jun-08		18:07:10		71		38		4-Jun-08		18:06:20		70.41		38.5		4-Jun-08		18:07:53		67.4		42		15-Jul-08		18:25:59		76.4		42.5

		4-Jun-08		20:07:10		71		38		4-Jun-08		20:06:20		70.41		42		4-Jun-08		20:07:53		67.4		43		15-Jul-08		20:25:59		77		39.5

		4-Jun-08		22:07:10		71		37.5		4-Jun-08		22:06:20		69.8		43		4-Jun-08		22:07:53		67.4		42.5		15-Jul-08		22:25:59		77		41

		5-Jun-08		0:07:10		70.41		38		5-Jun-08		0:06:20		69.2		44		5-Jun-08		0:07:53		68		41.5		16-Jul-08		0:25:59		76.4		41.5

		5-Jun-08		2:07:10		69.8		36		5-Jun-08		2:06:20		69.8		38.5		5-Jun-08		2:07:53		68.61		39		16-Jul-08		2:25:59		75.81		41.5

		5-Jun-08		4:07:10		68.61		36		5-Jun-08		4:06:20		69.2		38.5		5-Jun-08		4:07:53		68		38.5		16-Jul-08		4:25:59		75.81		42

		5-Jun-08		6:07:10		68.61		36		5-Jun-08		6:06:20		68.61		38.5		5-Jun-08		6:07:53		68		38		16-Jul-08		6:25:59		75.2		41

		5-Jun-08		8:07:10		69.2		35		5-Jun-08		8:06:20		69.2		39.5		5-Jun-08		8:07:53		68		38		16-Jul-08		8:25:59		74.6		43.5

		5-Jun-08		10:07:10		70.41		35		5-Jun-08		10:06:20		71		36.5		5-Jun-08		10:07:53		68		38.5		16-Jul-08		10:25:59		75.2		44.5

		5-Jun-08		12:07:10		70.41		34.5		5-Jun-08		12:06:20		69.8		35		5-Jun-08		12:07:53		68.61		37		16-Jul-08		12:25:59		75.2		43.5

		5-Jun-08		14:07:10		70.41		32		5-Jun-08		14:06:20		69.2		34.5		5-Jun-08		14:07:53		68.61		35		16-Jul-08		14:25:59		75.81		45

		5-Jun-08		16:07:10		70.41		34.5		5-Jun-08		16:06:20		70.41		36.5		5-Jun-08		16:07:53		68.61		37.5		16-Jul-08		16:25:59		75.2		43.5

		5-Jun-08		18:07:10		71		35		5-Jun-08		18:06:20		69.8		36		5-Jun-08		18:07:53		68.61		37.5

		5-Jun-08		20:07:10		71		35.5		5-Jun-08		20:06:20		69.2		38.5		5-Jun-08		20:07:53		69.2		38

		5-Jun-08		22:07:10		71		35		5-Jun-08		22:06:20		68.61		39		5-Jun-08		22:07:53		69.2		37.5

		6-Jun-08		0:07:10		69.8		35.5		6-Jun-08		0:06:20		68		41		6-Jun-08		0:07:53		68.61		38.5

		6-Jun-08		2:07:10		69.2		36		6-Jun-08		2:06:20		67.4		41		6-Jun-08		2:07:53		68.61		38

		6-Jun-08		4:07:10		69.2		36		6-Jun-08		4:06:20		67.4		41.5		6-Jun-08		4:07:53		68.61		38.5

		6-Jun-08		6:07:10		69.2		36		6-Jun-08		6:06:20		67.4		41.5		6-Jun-08		6:07:53		68		38.5

		6-Jun-08		8:07:10		69.8		36.5		6-Jun-08		8:06:20		68		42		6-Jun-08		8:07:53		68.61		39.5

		6-Jun-08		10:07:10		70.41		36		6-Jun-08		10:06:20		68		42		6-Jun-08		10:07:53		68		40

		6-Jun-08		12:07:10		70.41		33		6-Jun-08		12:06:20		69.8		36		6-Jun-08		12:07:53		68		37.5

		6-Jun-08		14:07:10		70.41		38.5		6-Jun-08		14:06:20		69.2		40.5		6-Jun-08		14:07:53		67.4		42

		6-Jun-08		16:07:10		70.41		39.5		6-Jun-08		16:06:20		69.8		43		6-Jun-08		16:07:53		68		43

		6-Jun-08		18:07:10		71		38.5		6-Jun-08		18:06:20		69.2		44.5		6-Jun-08		18:07:53		68		42.5

		6-Jun-08		20:07:10		71		39.5		6-Jun-08		20:06:20		69.2		47		6-Jun-08		20:07:53		68.61		43

		6-Jun-08		22:07:10		71		39		6-Jun-08		22:06:20		68.61		51.5		6-Jun-08		22:07:53		68.61		43

		7-Jun-08		0:07:10		70.41		38.5		7-Jun-08		0:06:20		68.61		45		7-Jun-08		0:07:53		69.2		41

		7-Jun-08		2:07:10		69.8		38		7-Jun-08		2:06:20		68		48.5		7-Jun-08		2:07:53		69.2		40.5

		7-Jun-08		4:07:10		69.2		38		7-Jun-08		4:06:20		67.4		45.5		7-Jun-08		4:07:53		68.61		40

		7-Jun-08		6:07:10		69.2		37.5		7-Jun-08		6:06:20		67.4		43.5		7-Jun-08		6:07:53		68.61		39.5

		7-Jun-08		8:07:10		69.8		37.5		7-Jun-08		8:06:20		68.61		44		7-Jun-08		8:07:53		68.61		39.5

		7-Jun-08		10:07:10		70.41		36		7-Jun-08		10:06:20		68.61		40		7-Jun-08		10:07:53		68		39.5

		7-Jun-08		12:07:10		70.41		34.5		7-Jun-08		12:06:20		70.41		36.5		7-Jun-08		12:07:53		69.2		37

		7-Jun-08		14:07:10		70.41		31.5		7-Jun-08		14:06:20		69.8		32.5		7-Jun-08		14:07:53		68.61		33.5

		7-Jun-08		16:07:10		71		32		7-Jun-08		16:06:20		68.61		34.5		7-Jun-08		16:07:53		68		35

		7-Jun-08		18:07:10		70.41		34.5		7-Jun-08		18:06:20		68.61		36.5		7-Jun-08		18:07:53		68.61		36.5

		7-Jun-08		20:07:10		71		34.5		7-Jun-08		20:06:20		69.2		38		7-Jun-08		20:07:53		69.2		37

		7-Jun-08		22:07:10		70.41		34		7-Jun-08		22:06:20		68.61		38		7-Jun-08		22:07:53		68.61		36.5

		8-Jun-08		0:07:10		69.8		34		8-Jun-08		0:06:20		68		38		8-Jun-08		0:07:53		68.61		36.5

		8-Jun-08		2:07:10		69.2		34		8-Jun-08		2:06:20		68		37.5		8-Jun-08		2:07:53		68.61		36

		8-Jun-08		4:07:10		69.2		34		8-Jun-08		4:06:20		68		37		8-Jun-08		4:07:53		68.61		35.5

		8-Jun-08		6:07:10		69.8		33		8-Jun-08		6:06:20		67.4		37		8-Jun-08		6:07:53		68.61		35.5

		8-Jun-08		8:07:10		69.8		33.5		8-Jun-08		8:06:20		68		36.5		8-Jun-08		8:07:53		68.61		35.5

		8-Jun-08		10:07:10		70.41		34.5		8-Jun-08		10:06:20		68		37		8-Jun-08		10:07:53		69.2		35.5

		8-Jun-08		12:07:10		71		33		8-Jun-08		12:06:20		68.61		34.5		8-Jun-08		12:07:53		69.2		35

		8-Jun-08		14:07:10		71		30.5		8-Jun-08		14:06:20		68.61		32		8-Jun-08		14:07:53		69.2		33

		8-Jun-08		16:07:10		71.6		31		8-Jun-08		16:06:20		69.2		33.5		8-Jun-08		16:07:53		68.61		34.5

		8-Jun-08		18:07:10		71.6		34.5		8-Jun-08		18:06:20		68.61		37.5		8-Jun-08		18:07:53		68.61		38

		8-Jun-08		20:07:10		71.6		36.5		8-Jun-08		20:06:20		68.61		45		8-Jun-08		20:07:53		68.61		40.5

		8-Jun-08		22:07:10		71		37		8-Jun-08		22:06:20		68.61		44		8-Jun-08		22:07:53		68.61		40

		9-Jun-08		0:07:10		71		36		9-Jun-08		0:06:20		68.61		40.5		9-Jun-08		0:07:53		69.2		38.5

		9-Jun-08		2:07:10		70.41		36.5		9-Jun-08		2:06:20		68		43		9-Jun-08		2:07:53		69.2		38

		9-Jun-08		4:07:10		69.8		36.5		9-Jun-08		4:06:20		68		43		9-Jun-08		4:07:53		69.2		38.5

		9-Jun-08		6:07:10		69.2		37		9-Jun-08		6:06:20		67.4		43.5		9-Jun-08		6:07:53		69.2		39

		9-Jun-08		8:07:10		69.8		38		9-Jun-08		8:06:20		67.4		45		9-Jun-08		8:07:53		69.2		39

		9-Jun-08		10:07:10		70.41		38.5		9-Jun-08		10:06:20		68.61		43.5		9-Jun-08		10:07:53		69.2		40

		9-Jun-08		12:07:10		71		38		9-Jun-08		12:06:20		68.61		42.5		9-Jun-08		12:07:53		69.8		40.5

		9-Jun-08		14:07:10		71		38		9-Jun-08		14:06:20		68.61		41.5		9-Jun-08		14:07:53		69.2		40.5

		9-Jun-08		16:07:10		72.21		38.5		9-Jun-08		16:06:20		68.61		44.5		9-Jun-08		16:07:53		69.8		42

		9-Jun-08		18:07:10		71.6		39		9-Jun-08		18:06:20		68.61		46.5		9-Jun-08		18:07:53		69.2		43

		9-Jun-08		20:07:10		71.6		38		9-Jun-08		20:06:20		68		48		9-Jun-08		20:07:53		69.2		41.5

		9-Jun-08		22:07:10		71		37.5		9-Jun-08		22:06:20		68		47		9-Jun-08		22:07:53		69.2		40

		10-Jun-08		0:07:10		70.41		37.5		10-Jun-08		0:06:20		68		45.5		10-Jun-08		0:07:53		69.2		39.5

		10-Jun-08		2:07:10		69.8		37		10-Jun-08		2:06:20		67.4		46		10-Jun-08		2:07:53		69.2		39.5

		10-Jun-08		4:07:10		69.8		38		10-Jun-08		4:06:20		68		47		10-Jun-08		4:07:53		69.2		39.5

		10-Jun-08		6:07:10		69.8		38		10-Jun-08		6:06:20		68		44.5		10-Jun-08		6:07:53		69.8		39.5

		10-Jun-08		8:07:10		71		38.5		10-Jun-08		8:06:20		68.61		48		10-Jun-08		8:07:53		69.2		41

		10-Jun-08		10:07:10		71		37.5		10-Jun-08		10:06:20		69.2		43		10-Jun-08		10:07:53		69.2		40.5

		10-Jun-08		12:07:10		71		38		10-Jun-08		12:06:20		70.41		40		10-Jun-08		12:07:53		69.2		40.5

		10-Jun-08		14:07:10		71		37.5		10-Jun-08		14:06:20		71.6		37.5		10-Jun-08		14:07:53		68.61		39.5

		10-Jun-08		16:07:10		70.41		40		10-Jun-08		16:06:20		70.41		41		10-Jun-08		16:07:53		68.61		42

		10-Jun-08		18:07:10		70.41		44		10-Jun-08		18:06:20		71.6		47.5		10-Jun-08		18:07:53		69.2		46.5

		10-Jun-08		20:07:10		71		42		10-Jun-08		20:06:20		71		47		10-Jun-08		20:07:53		68.61		46

		10-Jun-08		22:07:10		71.6		41		10-Jun-08		22:06:20		71		51		10-Jun-08		22:07:53		69.2		44.5

		11-Jun-08		0:07:10		71.6		40.5		11-Jun-08		0:06:20		71		47.5		11-Jun-08		0:07:53		68.61		45

		11-Jun-08		2:07:10		71.6		36.5		11-Jun-08		2:06:20		71		40.5		11-Jun-08		2:07:53		69.2		40

		11-Jun-08		4:07:10		71		37.5		11-Jun-08		4:06:20		69.8		44		11-Jun-08		4:07:53		69.2		40.5

		11-Jun-08		6:07:10		70.41		36.5		11-Jun-08		6:06:20		69.8		41		11-Jun-08		6:07:53		69.2		39

		11-Jun-08		8:07:10		71		35.5		11-Jun-08		8:06:20		70.41		39		11-Jun-08		8:07:53		68		39

		11-Jun-08		10:07:10		71		27.5		11-Jun-08		10:06:20		70.41		29.5		11-Jun-08		10:07:53		67.4		31.5

		11-Jun-08		12:07:10		71		24		11-Jun-08		12:06:20		69.8		24.5		11-Jun-08		12:07:53		68.61		27

		11-Jun-08		14:07:10		71.6		27.5		11-Jun-08		14:06:20		70.41		30.5		11-Jun-08		14:07:53		68		31.5

		11-Jun-08		16:07:10		71		28.5		11-Jun-08		16:06:20		69.8		30		11-Jun-08		16:07:53		68.61		31.5

		11-Jun-08		18:07:10		71		31.5		11-Jun-08		18:06:20		69.8		33		11-Jun-08		18:07:53		68.61		34

		11-Jun-08		20:07:10		71		33.5		11-Jun-08		20:06:20		69.8		35		11-Jun-08		20:07:53		68.61		36

		11-Jun-08		22:07:10		71.6		33.5		11-Jun-08		22:06:20		69.2		37		11-Jun-08		22:07:53		68.61		37

		12-Jun-08		0:07:10		70.41		34		12-Jun-08		0:06:20		69.2		36.5		12-Jun-08		0:07:53		68.61		36.5

		12-Jun-08		2:07:10		69.8		33.5		12-Jun-08		2:06:20		68.61		36.5		12-Jun-08		2:07:53		68.61		36

		12-Jun-08		4:07:10		69.2		34		12-Jun-08		4:06:20		68.61		37		12-Jun-08		4:07:53		68.61		36

		12-Jun-08		6:07:10		68.61		34.5		12-Jun-08		6:06:20		68		37		12-Jun-08		6:07:53		68		36.5

		12-Jun-08		8:07:10		69.8		34.5		12-Jun-08		8:06:20		69.2		37.5		12-Jun-08		8:07:53		68.61		36.5

		12-Jun-08		10:07:10		71		34		12-Jun-08		10:06:20		71		36		12-Jun-08		10:07:53		68.61		37

		12-Jun-08		12:07:10		71		29.5		12-Jun-08		12:06:20		71.6		30		12-Jun-08		12:07:53		69.8		32

		12-Jun-08		14:07:10		71		24.5		12-Jun-08		14:06:20		72.8		26		12-Jun-08		14:07:53		69.8		28.5

		12-Jun-08		16:07:10		71		26.5		12-Jun-08		16:06:20		71.6		20.5		12-Jun-08		16:07:53		69.2		28

		12-Jun-08		18:07:10		70.41		27.5		12-Jun-08		18:06:20		71		27.5		12-Jun-08		18:07:53		69.2		29.5

		12-Jun-08		20:07:10		70.41		35.5		12-Jun-08		20:06:20		71		38.5		12-Jun-08		20:07:53		69.2		38

		12-Jun-08		22:07:10		71		35.5		12-Jun-08		22:06:20		70.41		40		12-Jun-08		22:07:53		69.2		38

		13-Jun-08		0:07:10		70.41		36		13-Jun-08		0:06:20		70.41		39.5		13-Jun-08		0:07:53		69.2		37.5

		13-Jun-08		2:07:10		69.8		36		13-Jun-08		2:06:20		69.8		39.5		13-Jun-08		2:07:53		69.2		37.5

		13-Jun-08		4:07:10		69.8		36.5		13-Jun-08		4:06:20		69.8		40.5		13-Jun-08		4:07:53		69.2		38

		13-Jun-08		6:07:10		69.2		36.5		13-Jun-08		6:06:20		69.8		39.5		13-Jun-08		6:07:53		69.2		37.5

		13-Jun-08		8:07:10		70.41		37		13-Jun-08		8:06:20		70.41		39.5		13-Jun-08		8:07:53		69.2		39

		13-Jun-08		10:07:10		71		36.5		13-Jun-08		10:06:20		70.41		38.5		13-Jun-08		10:07:53		69.2		38.5

		13-Jun-08		12:07:10		71		24		13-Jun-08		12:06:20		71.6		25		13-Jun-08		12:07:53		69.8		28

		13-Jun-08		14:07:10		71		22.5		13-Jun-08		14:06:20		71.6		23.5		13-Jun-08		14:07:53		69.2		25

		13-Jun-08		16:07:10		70.41		29		13-Jun-08		16:06:20		72.21		30		13-Jun-08		16:07:53		69.8		31.5

		13-Jun-08		18:07:10		71		26.5		13-Jun-08		18:06:20		71		27		13-Jun-08		18:07:53		69.8		29

		13-Jun-08		20:07:10		71		29		13-Jun-08		20:06:20		71.6		27.5		13-Jun-08		20:07:53		68.61		29.5

		13-Jun-08		22:07:10		71.6		32.5		13-Jun-08		22:06:20		71		33.5		13-Jun-08		22:07:53		69.2		34.5

		14-Jun-08		0:07:10		71		33		14-Jun-08		0:06:20		70.41		35.5		14-Jun-08		0:07:53		69.2		35.5

		14-Jun-08		2:07:10		70.41		34.5		14-Jun-08		2:06:20		70.41		37		14-Jun-08		2:07:53		69.2		36

		14-Jun-08		4:07:10		69.8		34.5		14-Jun-08		4:06:20		69.8		38.5		14-Jun-08		4:07:53		69.2		36.5

		14-Jun-08		6:07:10		69.8		35.5		14-Jun-08		6:06:20		69.8		38.5		14-Jun-08		6:07:53		68.61		37

		14-Jun-08		8:07:10		70.41		36		14-Jun-08		8:06:20		71		38.5		14-Jun-08		8:07:53		69.2		38

		14-Jun-08		10:07:10		71		36.5		14-Jun-08		10:06:20		71		39.5		14-Jun-08		10:07:53		68.61		39.5

		14-Jun-08		12:07:10		70.41		39		14-Jun-08		12:06:20		71.6		42		14-Jun-08		12:07:53		69.2		41.5

		14-Jun-08		14:07:10		71		37.5		14-Jun-08		14:06:20		72.8		37		14-Jun-08		14:07:53		69.2		39.5

		14-Jun-08		16:07:10		70.41		39		14-Jun-08		16:06:20		71		41		14-Jun-08		16:07:53		69.8		41

		14-Jun-08		18:07:10		70.41		39		14-Jun-08		18:06:20		71		42.5		14-Jun-08		18:07:53		68.61		42

		14-Jun-08		20:07:10		70.41		38		14-Jun-08		20:06:20		70.41		45		14-Jun-08		20:07:53		68.61		41.5

		14-Jun-08		22:07:10		70.41		38		14-Jun-08		22:06:20		71		45		14-Jun-08		22:07:53		68.61		40.5

		15-Jun-08		0:07:10		70.41		38.5		15-Jun-08		0:06:20		69.8		43.5		15-Jun-08		0:07:53		68.61		40.5

		15-Jun-08		2:07:10		70.41		38		15-Jun-08		2:06:20		69.8		44		15-Jun-08		2:07:53		68.61		40.5

		15-Jun-08		4:07:10		69.8		37.5		15-Jun-08		4:06:20		69.2		44		15-Jun-08		4:07:53		68.61		40

		15-Jun-08		6:07:10		69.8		38		15-Jun-08		6:06:20		69.2		45		15-Jun-08		6:07:53		68.61		40.5

		15-Jun-08		8:07:10		70.41		39		15-Jun-08		8:06:20		69.2		45.5		15-Jun-08		8:07:53		68.61		41

		15-Jun-08		10:07:10		70.41		39		15-Jun-08		10:06:20		69.8		45		15-Jun-08		10:07:53		68.61		41

		15-Jun-08		12:07:10		70.41		40		15-Jun-08		12:06:20		70.41		46.5		15-Jun-08		12:07:53		69.2		42

		15-Jun-08		14:07:10		71		41.5		15-Jun-08		14:06:20		71		47.5		15-Jun-08		14:07:53		69.2		44

		15-Jun-08		16:07:10		71		41.5		15-Jun-08		16:06:20		70.41		51.5		15-Jun-08		16:07:53		69.2		44.5

		15-Jun-08		18:07:10		71		40.5		15-Jun-08		18:06:20		70.41		50		15-Jun-08		18:07:53		69.2		43.5

		15-Jun-08		20:07:10		71		38.5		15-Jun-08		20:06:20		69.8		47		15-Jun-08		20:07:53		69.2		41.5

		15-Jun-08		22:07:10		71		38.5		15-Jun-08		22:06:20		70.41		45.5		15-Jun-08		22:07:53		69.2		41

		16-Jun-08		0:07:10		70.41		38.5		16-Jun-08		0:06:20		69.8		44.5		16-Jun-08		0:07:53		69.2		40.5

		16-Jun-08		2:07:10		70.41		38		16-Jun-08		2:06:20		69.2		44.5		16-Jun-08		2:07:53		69.2		40

		16-Jun-08		4:07:10		70.41		38		16-Jun-08		4:06:20		68.61		45		16-Jun-08		4:07:53		69.2		40

		16-Jun-08		6:07:10		69.8		37.5		16-Jun-08		6:06:20		68.61		44.5		16-Jun-08		6:07:53		69.2		39.5

		16-Jun-08		8:07:10		69.8		38		16-Jun-08		8:06:20		68.61		44.5		16-Jun-08		8:07:53		69.2		40

		16-Jun-08		10:07:10		69.8		38.5		16-Jun-08		10:06:20		69.8		44.5		16-Jun-08		10:07:53		69.2		40

		16-Jun-08		12:07:10		70.41		40.5		16-Jun-08		12:06:20		69.8		47		16-Jun-08		12:07:53		69.2		41.5

		16-Jun-08		14:07:10		70.41		42		16-Jun-08		14:06:20		70.41		49.5		16-Jun-08		14:07:53		69.2		43.5

		16-Jun-08		16:07:10		71		40.5		16-Jun-08		16:06:20		71		46		16-Jun-08		16:07:53		69.2		43

		16-Jun-08		18:07:10		71		39.5		16-Jun-08		18:06:20		71		43.5		16-Jun-08		18:07:53		69.2		42.5

		16-Jun-08		20:07:10		71		38		16-Jun-08		20:06:20		70.41		44.5		16-Jun-08		20:07:53		69.2		41

		16-Jun-08		22:07:10		70.41		38		16-Jun-08		22:06:20		70.41		43		16-Jun-08		22:07:53		69.2		40

		17-Jun-08		0:07:10		70.41		37.5		17-Jun-08		0:06:20		69.8		42		17-Jun-08		0:07:53		69.2		39.5

		17-Jun-08		2:07:10		69.8		36.5		17-Jun-08		2:06:20		68.61		43		17-Jun-08		2:07:53		69.2		39

		17-Jun-08		4:07:10		69.8		38		17-Jun-08		4:06:20		68		45.5		17-Jun-08		4:07:53		69.2		40

		17-Jun-08		6:07:10		69.8		38		17-Jun-08		6:06:20		68		45.5		17-Jun-08		6:07:53		69.2		40

		17-Jun-08		8:07:10		70.41		38.5		17-Jun-08		8:06:20		70.41		45		17-Jun-08		8:07:53		68.61		41

		17-Jun-08		10:07:10		70.41		39		17-Jun-08		10:06:20		71		44		17-Jun-08		10:07:53		68.61		41

		17-Jun-08		12:07:10		71		39.5		17-Jun-08		12:06:20		69.8		45.5		17-Jun-08		12:07:53		69.2		42

		17-Jun-08		14:07:10		71		41.5		17-Jun-08		14:06:20		70.41		48.5		17-Jun-08		14:07:53		68		45

		17-Jun-08		16:07:10		71		40		17-Jun-08		16:06:20		70.41		45		17-Jun-08		16:07:53		69.2		43.5

		17-Jun-08		18:07:10		71		39.5		17-Jun-08		18:06:20		70.41		46		17-Jun-08		18:07:53		69.8		41.5

		17-Jun-08		20:07:10		70.41		38.5		17-Jun-08		20:06:20		69.8		44.5		17-Jun-08		20:07:53		69.8		40

		17-Jun-08		22:07:10		70.41		38		17-Jun-08		22:06:20		69.8		43		17-Jun-08		22:07:53		69.8		39.5

		18-Jun-08		0:07:10		70.41		37.5		18-Jun-08		0:06:20		69.2		43		18-Jun-08		0:07:53		69.8		39

		18-Jun-08		2:07:10		70.41		37.5		18-Jun-08		2:06:20		68		43.5		18-Jun-08		2:07:53		69.8		38.5

		18-Jun-08		4:07:10		70.41		38		18-Jun-08		4:06:20		67.4		46		18-Jun-08		4:07:53		69.8		39

		18-Jun-08		6:07:10		70.41		38		18-Jun-08		6:06:20		66.81		46.5		18-Jun-08		6:07:53		69.8		39

		18-Jun-08		8:07:10		70.41		39		18-Jun-08		8:06:20		70.41		43.5		18-Jun-08		8:07:53		69.2		40.5

		18-Jun-08		10:07:10		71		38.5		18-Jun-08		10:06:20		70.41		44.5		18-Jun-08		10:07:53		68.61		41

		18-Jun-08		12:07:10		71		39		18-Jun-08		12:06:20		69.8		44.5		18-Jun-08		12:07:53		69.8		41

		18-Jun-08		14:07:10		71		42		18-Jun-08		14:06:20		69.8		46.5		18-Jun-08		14:07:53		69.2		44.5

		18-Jun-08		16:07:10		71		43.5		18-Jun-08		16:06:20		69.8		51.5		18-Jun-08		16:07:53		69.2		46

		18-Jun-08		18:07:10		71		29		18-Jun-08		18:06:20		69.2		31		18-Jun-08		18:07:53		69.2		32

		18-Jun-08		20:07:10		71		28		18-Jun-08		20:06:20		68.61		29		18-Jun-08		20:07:53		69.2		30

		18-Jun-08		22:07:10		71		29.5		18-Jun-08		22:06:20		68.61		31		18-Jun-08		22:07:53		69.2		31.5

		19-Jun-08		0:07:10		70.41		29		19-Jun-08		0:06:20		68.61		31.5		19-Jun-08		0:07:53		69.2		31

		19-Jun-08		2:07:10		69.8		34		19-Jun-08		2:06:20		68		37		19-Jun-08		2:07:53		69.2		35.5

		19-Jun-08		4:07:10		69.2		35		19-Jun-08		4:06:20		67.4		39.5		19-Jun-08		4:07:53		68.61		36.5

		19-Jun-08		6:07:10		69.8		34		19-Jun-08		6:06:20		67.4		39		19-Jun-08		6:07:53		69.2		35.5

		19-Jun-08		8:07:10		69.8		35.5		19-Jun-08		8:06:20		68		41.5		19-Jun-08		8:07:53		69.2		37.5

		19-Jun-08		10:07:10		71		33.5		19-Jun-08		10:06:20		70.41		36.5		19-Jun-08		10:07:53		69.2		36.5

		19-Jun-08		12:07:10		71		31		19-Jun-08		12:06:20		70.41		33		19-Jun-08		12:07:53		69.8		33

		19-Jun-08		14:07:10		70.41		34.5		19-Jun-08		14:06:20		71		36		19-Jun-08		14:07:53		69.8		36

		19-Jun-08		16:07:10		70.41		31		19-Jun-08		16:06:20		69.2		32.5		19-Jun-08		16:07:53		69.8		32.5

		19-Jun-08		18:07:10		71		25		19-Jun-08		18:06:20		69.2		26		19-Jun-08		18:07:53		69.2		27

		19-Jun-08		20:07:10		71		26		19-Jun-08		20:06:20		69.2		27		19-Jun-08		20:07:53		69.2		27.5

		19-Jun-08		22:07:10		71		30.5		19-Jun-08		22:06:20		68.61		31.5		19-Jun-08		22:07:53		69.2		31.5

		20-Jun-08		0:07:10		71		33		20-Jun-08		0:06:20		68		37		20-Jun-08		0:07:53		68.61		35.5

		20-Jun-08		2:07:10		70.41		33.5		20-Jun-08		2:06:20		68		37.5		20-Jun-08		2:07:53		68.61		35.5

		20-Jun-08		4:07:10		69.8		33.5		20-Jun-08		4:06:20		68		38		20-Jun-08		4:07:53		68.61		36

		20-Jun-08		6:07:10		69.2		34.5		20-Jun-08		6:06:20		67.4		39		20-Jun-08		6:07:53		68		36.5

		20-Jun-08		8:07:10		69.8		35.5		20-Jun-08		8:06:20		68.61		39		20-Jun-08		8:07:53		68.61		37.5

		20-Jun-08		10:07:10		71		35.5		20-Jun-08		10:06:20		70.41		38		20-Jun-08		10:07:53		68.61		38

		20-Jun-08		12:07:10		70.41		34		20-Jun-08		12:06:20		72.21		34.5		20-Jun-08		12:07:53		68.61		36.5

		20-Jun-08		14:07:10		70.41		31		20-Jun-08		14:06:20		69.8		32		20-Jun-08		14:07:53		68		33.5

		20-Jun-08		16:07:10		70.41		32.5		20-Jun-08		16:06:20		71		34.5		20-Jun-08		16:07:53		68.61		35.5

		20-Jun-08		18:07:10		70.41		29		20-Jun-08		18:06:20		69.2		30		20-Jun-08		18:07:53		68.61		31

		20-Jun-08		20:07:10		71		31.5		20-Jun-08		20:06:20		68		34.5		20-Jun-08		20:07:53		68.61		34.5

		20-Jun-08		22:07:10		71		32.5		20-Jun-08		22:06:20		68		36		20-Jun-08		22:07:53		68.61		35

		21-Jun-08		0:07:10		71		34.5		21-Jun-08		0:06:20		68.61		38.5		21-Jun-08		0:07:53		68.61		37

		21-Jun-08		2:07:10		70.41		35		21-Jun-08		2:06:20		67.4		41		21-Jun-08		2:07:53		68.61		37

		21-Jun-08		4:07:10		70.41		36		21-Jun-08		4:06:20		67.4		41		21-Jun-08		4:07:53		69.2		37.5

		21-Jun-08		6:07:10		69.8		36		21-Jun-08		6:06:20		68		43		21-Jun-08		6:07:53		68.61		38.5

		21-Jun-08		8:07:10		71		36		21-Jun-08		8:06:20		68.61		43		21-Jun-08		8:07:53		68.61		39

		21-Jun-08		10:07:10		71		35		21-Jun-08		10:06:20		69.2		37		21-Jun-08		10:07:53		69.2		37

		21-Jun-08		12:07:10		70.41		30.5		21-Jun-08		12:06:20		71		31.5		21-Jun-08		12:07:53		69.2		33

		21-Jun-08		14:07:10		71		30		21-Jun-08		14:06:20		70.41		30.5		21-Jun-08		14:07:53		69.2		31.5

		21-Jun-08		16:07:10		71		26.5		21-Jun-08		16:06:20		71.6		26.5		21-Jun-08		16:07:53		68.61		29

		21-Jun-08		18:07:10		70.41		23		21-Jun-08		18:06:20		70.41		24		21-Jun-08		18:07:53		69.2		26

		21-Jun-08		20:07:10		71		22.5		21-Jun-08		20:06:20		71		22.5		21-Jun-08		20:07:53		69.2		24.5

		21-Jun-08		22:07:10		71		27.5		21-Jun-08		22:06:20		70.41		29		21-Jun-08		22:07:53		69.2		30

		22-Jun-08		0:07:10		71		31		22-Jun-08		0:06:20		70.41		34		22-Jun-08		0:07:53		68.61		34.5

		22-Jun-08		2:07:10		71		31.5		22-Jun-08		2:06:20		69.8		35		22-Jun-08		2:07:53		68.61		35.5

		22-Jun-08		4:07:10		71		32.5		22-Jun-08		4:06:20		69.8		34.5		22-Jun-08		4:07:53		68.61		35.5

		22-Jun-08		6:07:10		70.41		33		22-Jun-08		6:06:20		69.2		35.5		22-Jun-08		6:07:53		68.61		35.5

		22-Jun-08		8:07:10		71		33.5		22-Jun-08		8:06:20		69.2		36.5		22-Jun-08		8:07:53		69.8		35.5

		22-Jun-08		10:07:10		71		34.5		22-Jun-08		10:06:20		70.41		37		22-Jun-08		10:07:53		69.8		37

		22-Jun-08		12:07:10		71.6		32		22-Jun-08		12:06:20		71		34.5		22-Jun-08		12:07:53		69.2		36

		22-Jun-08		14:07:10		71.6		29.5		22-Jun-08		14:06:20		71		32.5		22-Jun-08		14:07:53		69.8		33.5

		22-Jun-08		16:07:10		72.21		26		22-Jun-08		16:06:20		70.41		29		22-Jun-08		16:07:53		69.2		30.5

		22-Jun-08		18:07:10		72.21		22.5		22-Jun-08		18:06:20		70.41		25.5		22-Jun-08		18:07:53		69.2		26.5

		22-Jun-08		20:07:10		72.21		30.5		22-Jun-08		20:06:20		70.41		31.5		22-Jun-08		20:07:53		69.8		31.5

		22-Jun-08		22:07:10		71.6		31		22-Jun-08		22:06:20		70.41		34.5		22-Jun-08		22:07:53		69.2		34

		23-Jun-08		0:07:10		71		34.5		23-Jun-08		0:06:20		69.2		39		23-Jun-08		0:07:53		69.2		36.5

		23-Jun-08		2:07:10		70.41		35.5		23-Jun-08		2:06:20		69.8		41.5		23-Jun-08		2:07:53		69.2		38

		23-Jun-08		4:07:10		70.41		36		23-Jun-08		4:06:20		69.2		42		23-Jun-08		4:07:53		69.8		38

		23-Jun-08		6:07:10		70.41		35.5		23-Jun-08		6:06:20		68.61		42		23-Jun-08		6:07:53		69.8		37.5

		23-Jun-08		8:07:10		70.41		37		23-Jun-08		8:06:20		69.2		44		23-Jun-08		8:07:53		69.8		38.5

		23-Jun-08		10:07:10		71		38		23-Jun-08		10:06:20		69.2		45		23-Jun-08		10:07:53		69.8		39.5

		23-Jun-08		12:07:10		71		38.5		23-Jun-08		12:06:20		69.8		42.5		23-Jun-08		12:07:53		69.8		39.5

		23-Jun-08		14:07:10		71		39		23-Jun-08		14:06:20		70.41		44.5		23-Jun-08		14:07:53		69.8		41

		23-Jun-08		16:07:10		71.6		39.5		23-Jun-08		16:06:20		69.8		46.5		23-Jun-08		16:07:53		69.8		42

		23-Jun-08		18:07:10		71.6		38		23-Jun-08		18:06:20		70.41		42.5		23-Jun-08		18:07:53		69.2		41

		23-Jun-08		20:07:10		71.6		37		23-Jun-08		20:06:20		69.8		43		23-Jun-08		20:07:53		69.8		39.5

		23-Jun-08		22:07:10		71		36		23-Jun-08		22:06:20		69.2		42.5		23-Jun-08		22:07:53		69.8		38.5

		24-Jun-08		0:07:10		69.8		36.5		24-Jun-08		0:06:20		69.2		42		24-Jun-08		0:07:53		69.2		38.5

		24-Jun-08		2:07:10		70.41		36.5		24-Jun-08		2:06:20		68.61		42		24-Jun-08		2:07:53		69.8		38

		24-Jun-08		4:07:10		70.41		36		24-Jun-08		4:06:20		68		42.5		24-Jun-08		4:07:53		69.8		37.5

		24-Jun-08		6:07:10		70.41		37.5		24-Jun-08		6:06:20		67.4		45.5		24-Jun-08		6:07:53		69.8		38.5

		24-Jun-08		8:07:10		70.41		38.5		24-Jun-08		8:06:20		69.8		44.5		24-Jun-08		8:07:53		69.8		40

		24-Jun-08		10:07:10		70.41		38		24-Jun-08		10:06:20		71		44		24-Jun-08		10:07:53		69.2		40.5

		24-Jun-08		12:07:10		70.41		39.5		24-Jun-08		12:06:20		71.6		42.5		24-Jun-08		12:07:53		69.8		41

		24-Jun-08		14:07:10		70.41		38.5		24-Jun-08		14:06:20		71		42.5		24-Jun-08		14:07:53		68		42.5

		24-Jun-08		16:07:10		71		39		24-Jun-08		16:06:20		69.2		47		24-Jun-08		16:07:53		68		42.5

		24-Jun-08		18:07:10		71		38.5		24-Jun-08		18:06:20		69.2		45.5		24-Jun-08		18:07:53		69.2		41.5

		24-Jun-08		20:07:10		70.41		38.5		24-Jun-08		20:06:20		68.61		47		24-Jun-08		20:07:53		69.2		40.5

		24-Jun-08		22:07:10		70.41		38		24-Jun-08		22:06:20		68.61		44		24-Jun-08		22:07:53		69.2		39.5

		25-Jun-08		0:07:10		70.41		38.5		25-Jun-08		0:06:20		68		43.5		25-Jun-08		0:07:53		69.2		40

		25-Jun-08		2:07:10		70.41		37.5		25-Jun-08		2:06:20		67.4		46.5		25-Jun-08		2:07:53		69.8		39

		25-Jun-08		4:07:10		70.41		37.5		25-Jun-08		4:06:20		67.4		45		25-Jun-08		4:07:53		69.8		39

		25-Jun-08		6:07:10		70.41		37		25-Jun-08		6:06:20		66.81		45		25-Jun-08		6:07:53		69.8		38.5

		25-Jun-08		8:07:10		69.8		38.5		25-Jun-08		8:06:20		68		44		25-Jun-08		8:07:53		68.61		40.5

		25-Jun-08		10:07:10		70.41		39		25-Jun-08		10:06:20		69.8		46.5		25-Jun-08		10:07:53		68.61		42

		25-Jun-08		12:07:10		70.41		40.5		25-Jun-08		12:06:20		69.8		44		25-Jun-08		12:07:53		68		43.5

		25-Jun-08		14:07:10		70.41		42		25-Jun-08		14:06:20		69.8		47		25-Jun-08		14:07:53		67.4		46.5

		25-Jun-08		16:07:10		70.41		41.5		25-Jun-08		16:06:20		69.8		50		25-Jun-08		16:07:53		68.61		45

		25-Jun-08		18:07:10		71		39.5		25-Jun-08		18:06:20		69.2		48		25-Jun-08		18:07:53		68.61		43.5

		25-Jun-08		20:07:10		71		38.5		25-Jun-08		20:06:20		69.2		44		25-Jun-08		20:07:53		69.2		42

		25-Jun-08		22:07:10		71		38		25-Jun-08		22:06:20		69.8		43.5		25-Jun-08		22:07:53		69.2		40.5

		26-Jun-08		0:07:10		70.41		38		26-Jun-08		0:06:20		68.61		46		26-Jun-08		0:07:53		69.2		40

		26-Jun-08		2:07:10		69.8		38		26-Jun-08		2:06:20		68.61		44.5		26-Jun-08		2:07:53		68.61		39.5

		26-Jun-08		4:07:10		70.41		38		26-Jun-08		4:06:20		68.61		44		26-Jun-08		4:07:53		69.2		39.5

		26-Jun-08		6:07:10		70.41		37.5		26-Jun-08		6:06:20		68		44.5		26-Jun-08		6:07:53		69.8		39

		26-Jun-08		8:07:10		70.41		39		26-Jun-08		8:06:20		69.2		44		26-Jun-08		8:07:53		68		41.5

		26-Jun-08		10:07:10		70.41		39		26-Jun-08		10:06:20		69.2		45		26-Jun-08		10:07:53		68.61		41.5

		26-Jun-08		12:07:10		70.41		40.5		26-Jun-08		12:06:20		71		43.5		26-Jun-08		12:07:53		68.61		43

		26-Jun-08		14:07:10		70.41		42.5		26-Jun-08		14:06:20		70.41		47.5		26-Jun-08		14:07:53		68		46

		26-Jun-08		16:07:10		70.41		42.5		26-Jun-08		16:06:20		68.61		49.5		26-Jun-08		16:07:53		68.61		45.5

		26-Jun-08		18:07:10		70.41		41.5		26-Jun-08		18:06:20		69.2		47		26-Jun-08		18:07:53		69.2		43.5

		26-Jun-08		20:07:10		70.41		40		26-Jun-08		20:06:20		69.2		47.5		26-Jun-08		20:07:53		69.2		42

		26-Jun-08		22:07:10		70.41		39		26-Jun-08		22:06:20		69.2		46.5		26-Jun-08		22:07:53		69.2		41

		27-Jun-08		0:07:10		69.8		38		27-Jun-08		0:06:20		68		47.5		27-Jun-08		0:07:53		68.61		40.5

		27-Jun-08		2:07:10		69.8		38		27-Jun-08		2:06:20		67.4		46		27-Jun-08		2:07:53		69.2		40

		27-Jun-08		4:07:10		70.41		38		27-Jun-08		4:06:20		68		45		27-Jun-08		4:07:53		69.8		39

		27-Jun-08		6:07:10		69.8		37.5		27-Jun-08		6:06:20		67.4		45		27-Jun-08		6:07:53		69.8		39

		27-Jun-08		8:07:10		70.41		39		27-Jun-08		8:06:20		68.61		49.5		27-Jun-08		8:07:53		69.2		40.5

		27-Jun-08		10:07:10		70.41		39.5		27-Jun-08		10:06:20		69.8		44.5		27-Jun-08		10:07:53		68.61		42

		27-Jun-08		12:07:10		70.41		41		27-Jun-08		12:06:20		70.41		50.5		27-Jun-08		12:07:53		69.2		43

		27-Jun-08		14:07:10		70.41		43		27-Jun-08		14:06:20		71		48.5		27-Jun-08		14:07:53		68		46

		27-Jun-08		16:07:10		70.41		42.5		27-Jun-08		16:06:20		70.41		48.5		27-Jun-08		16:07:53		68		46

		27-Jun-08		18:07:10		70.41		40		27-Jun-08		18:06:20		70.41		44		27-Jun-08		18:07:53		68.61		43

		27-Jun-08		20:07:10		70.41		39		27-Jun-08		20:06:20		70.41		44.5		27-Jun-08		20:07:53		68.61		42

		27-Jun-08		22:07:10		70.41		38.5		27-Jun-08		22:06:20		70.41		45		27-Jun-08		22:07:53		69.2		41

		28-Jun-08		0:07:10		69.8		38.5		28-Jun-08		0:06:20		69.2		46		28-Jun-08		0:07:53		68.61		41

		28-Jun-08		2:07:10		69.8		38.5		28-Jun-08		2:06:20		69.2		45		28-Jun-08		2:07:53		68.61		40.5

		28-Jun-08		4:07:10		69.2		38.5		28-Jun-08		4:06:20		69.2		44.5		28-Jun-08		4:07:53		68.61		40

		28-Jun-08		6:07:10		69.2		39.5		28-Jun-08		6:06:20		69.2		45.5		28-Jun-08		6:07:53		68.61		40.5

		28-Jun-08		8:07:10		69.8		39.5		28-Jun-08		8:06:20		70.41		44		28-Jun-08		8:07:53		68.61		41.5

		28-Jun-08		10:07:10		71		40.5		28-Jun-08		10:06:20		71		50.5		28-Jun-08		10:07:53		68.61		43

		28-Jun-08		12:07:10		70.41		42.5		28-Jun-08		12:06:20		71.6		48		28-Jun-08		12:07:53		69.8		44

		28-Jun-08		14:07:10		70.41		43.5		28-Jun-08		14:06:20		71.6		53.5		28-Jun-08		14:07:53		68.61		46

		28-Jun-08		16:07:10		70.41		44		28-Jun-08		16:06:20		71		50		28-Jun-08		16:07:53		69.2		46.5

		28-Jun-08		18:07:10		71		40.5		28-Jun-08		18:06:20		70.41		51		28-Jun-08		18:07:53		69.2		43.5

		28-Jun-08		20:07:10		71		39.5		28-Jun-08		20:06:20		70.41		49.5		28-Jun-08		20:07:53		69.2		42

		28-Jun-08		22:07:10		70.41		39.5		28-Jun-08		22:06:20		69.8		49		28-Jun-08		22:07:53		69.8		41

		29-Jun-08		0:07:10		69.8		39.5		29-Jun-08		0:06:20		69.8		49.5		29-Jun-08		0:07:53		69.2		41.5

		29-Jun-08		2:07:10		69.8		40		29-Jun-08		2:06:20		69.2		49		29-Jun-08		2:07:53		69.2		41.5

		29-Jun-08		4:07:10		69.8		40		29-Jun-08		4:06:20		69.2		50		29-Jun-08		4:07:53		69.8		41.5

		29-Jun-08		6:07:10		69.8		40		29-Jun-08		6:06:20		69.2		50.5		29-Jun-08		6:07:53		69.8		41

		29-Jun-08		8:07:10		69.8		40		29-Jun-08		8:06:20		69.8		50.5		29-Jun-08		8:07:53		69.8		41.5

		29-Jun-08		10:07:10		70.41		40.5		29-Jun-08		10:06:20		69.2		47		29-Jun-08		10:07:53		69.8		41.5

		29-Jun-08		12:07:10		70.41		41.5		29-Jun-08		12:06:20		69.2		53.5		29-Jun-08		12:07:53		69.8		42.5

		29-Jun-08		14:07:10		70.41		42.5		29-Jun-08		14:06:20		69.8		48		29-Jun-08		14:07:53		70.41		44

		29-Jun-08		16:07:10		71		43		29-Jun-08		16:06:20		69.8		52.5		29-Jun-08		16:07:53		70.41		44.5

		29-Jun-08		18:07:10		71		42		29-Jun-08		18:06:20		70.41		53		29-Jun-08		18:07:53		70.41		44

		29-Jun-08		20:07:10		71		40		29-Jun-08		20:06:20		69.2		52		29-Jun-08		20:07:53		69.8		42

		29-Jun-08		22:07:10		70.41		39.5		29-Jun-08		22:06:20		69.2		50		29-Jun-08		22:07:53		69.8		41

		30-Jun-08		0:07:10		69.2		40		30-Jun-08		0:06:20		69.2		48.5		30-Jun-08		0:07:53		69.2		41

		30-Jun-08		2:07:10		69.2		40		30-Jun-08		2:06:20		69.2		48.5		30-Jun-08		2:07:53		69.8		41

		30-Jun-08		4:07:10		69.2		40		30-Jun-08		4:06:20		69.2		49		30-Jun-08		4:07:53		69.2		41

		30-Jun-08		6:07:10		69.2		40		30-Jun-08		6:06:20		69.2		49		30-Jun-08		6:07:53		69.2		41

		30-Jun-08		8:07:10		69.2		40		30-Jun-08		8:06:20		69.2		49		30-Jun-08		8:07:53		69.8		41

		30-Jun-08		10:07:10		69.2		40		30-Jun-08		10:06:20		69.8		47.5		30-Jun-08		10:07:53		69.8		41

		30-Jun-08		12:07:10		70.41		41.5		30-Jun-08		12:06:20		69.8		49.5		30-Jun-08		12:07:53		70.41		42

		30-Jun-08		14:07:10		70.41		43		30-Jun-08		14:06:20		70.41		48		30-Jun-08		14:07:53		70.41		43.5

		30-Jun-08		16:07:10		71		43		30-Jun-08		16:06:20		70.41		50.5		30-Jun-08		16:07:53		70.41		44.5

		30-Jun-08		18:07:10		71		41.5		30-Jun-08		18:06:20		69.8		50		30-Jun-08		18:07:53		70.41		43.5

		30-Jun-08		20:07:10		71		40		30-Jun-08		20:06:20		69.8		50		30-Jun-08		20:07:53		70.41		42

		30-Jun-08		22:07:10		69.8		39.5		30-Jun-08		22:06:20		69.8		48.5		30-Jun-08		22:07:53		69.8		40.5

		1-Jul-08		0:07:10		69.8		40		1-Jul-08		0:06:20		69.2		48.5		1-Jul-08		0:07:53		69.2		41

		1-Jul-08		2:07:10		69.2		40		1-Jul-08		2:06:20		69.2		48.5		1-Jul-08		2:07:53		69.2		41

		1-Jul-08		4:07:10		69.8		40.5		1-Jul-08		4:06:20		68.61		49		1-Jul-08		4:07:53		69.8		41

		1-Jul-08		6:07:10		69.8		40		1-Jul-08		6:06:20		68.61		49.5		1-Jul-08		6:07:53		69.8		41

		1-Jul-08		8:07:10		70.41		40.5		1-Jul-08		8:06:20		71		48.5		1-Jul-08		8:07:53		69.8		41

		1-Jul-08		10:07:10		70.41		40		1-Jul-08		10:06:20		71		47.5		1-Jul-08		10:07:53		69.8		41.5

		1-Jul-08		12:07:10		70.41		42		1-Jul-08		12:06:20		70.41		46		1-Jul-08		12:07:53		70.41		43.5

		1-Jul-08		14:07:10		71		44		1-Jul-08		14:06:20		70.41		48		1-Jul-08		14:07:53		69.8		45

		1-Jul-08		16:07:10		70.41		44.5		1-Jul-08		16:06:20		70.41		57.5		1-Jul-08		16:07:53		69.2		47

		1-Jul-08		18:07:10		71		43		1-Jul-08		18:06:20		70.41		53		1-Jul-08		18:07:53		69.2		45.5

		1-Jul-08		20:07:10		71		41		1-Jul-08		20:06:20		70.41		53.5		1-Jul-08		20:07:53		69.2		44

		1-Jul-08		22:07:10		71		40		1-Jul-08		22:06:20		69.8		52		1-Jul-08		22:07:53		69.8		42

		2-Jul-08		0:07:10		70.41		40		2-Jul-08		0:06:20		69.2		52		2-Jul-08		0:07:53		69.2		41.5

		2-Jul-08		2:07:10		69.8		40		2-Jul-08		2:06:20		69.2		52		2-Jul-08		2:07:53		69.2		42

		2-Jul-08		4:07:10		69.8		40		2-Jul-08		4:06:20		69.8		51.5		2-Jul-08		4:07:53		69.8		41.5

		2-Jul-08		6:07:10		69.8		40.5		2-Jul-08		6:06:20		69.2		53		2-Jul-08		6:07:53		69.2		42

		2-Jul-08		8:07:10		70.41		41		2-Jul-08		8:06:20		70.41		49		2-Jul-08		8:07:53		69.2		42.5

		2-Jul-08		10:07:10		70.41		40.5		2-Jul-08		10:06:20		69.8		46.5		2-Jul-08		10:07:53		69.8		42

		2-Jul-08		12:07:10		71		42.5		2-Jul-08		12:06:20		70.41		54		2-Jul-08		12:07:53		69.8		43.5

		2-Jul-08		14:07:10		70.41		44.5		2-Jul-08		14:06:20		70.41		50.5		2-Jul-08		14:07:53		69.2		46.5

		2-Jul-08		16:07:10		71		44.5		2-Jul-08		16:06:20		70.41		57.5		2-Jul-08		16:07:53		69.2		47

		2-Jul-08		18:07:10		71		43		2-Jul-08		18:06:20		69.8		49		2-Jul-08		18:07:53		69.8		45

		2-Jul-08		20:07:10		71		41		2-Jul-08		20:06:20		69.8		52		2-Jul-08		20:07:53		69.8		43

		2-Jul-08		22:07:10		70.41		40		2-Jul-08		22:06:20		69.8		49.5		2-Jul-08		22:07:53		69.8		41.5

		3-Jul-08		0:07:10		69.2		40		3-Jul-08		0:06:20		69.8		49		3-Jul-08		0:07:53		69.2		41.5

		3-Jul-08		2:07:10		70.41		40		3-Jul-08		2:06:20		69.2		48		3-Jul-08		2:07:53		69.8		41

		3-Jul-08		4:07:10		70.41		40		3-Jul-08		4:06:20		68.61		49		3-Jul-08		4:07:53		69.8		41

		3-Jul-08		6:07:10		69.8		40		3-Jul-08		6:06:20		68		49.5		3-Jul-08		6:07:53		69.8		41

		3-Jul-08		8:07:10		70.41		40.5		3-Jul-08		8:06:20		69.8		49		3-Jul-08		8:07:53		69.8		41.5

		3-Jul-08		10:07:10		70.41		41		3-Jul-08		10:06:20		70.41		45		3-Jul-08		10:07:53		69.8		41.5

		3-Jul-08		12:07:10		70.41		43		3-Jul-08		12:06:20		71		45.5		3-Jul-08		12:07:53		69.8		43.5

		3-Jul-08		14:07:10		70.41		44.5		3-Jul-08		14:06:20		71		47		3-Jul-08		14:07:53		69.2		46

		3-Jul-08		16:07:10		70.41		44		3-Jul-08		16:06:20		69.8		53		3-Jul-08		16:07:53		69.2		46

		3-Jul-08		18:07:10		70.41		43		3-Jul-08		18:06:20		70.41		49		3-Jul-08		18:07:53		69.8		44.5

		3-Jul-08		20:07:10		70.41		41.5		3-Jul-08		20:06:20		70.41		51.5		3-Jul-08		20:07:53		69.8		43.5

		3-Jul-08		22:07:10		71		40		3-Jul-08		22:06:20		69.2		51		3-Jul-08		22:07:53		69.8		42

		4-Jul-08		0:07:10		69.8		39.5		4-Jul-08		0:06:20		69.2		49.5		4-Jul-08		0:07:53		69.2		41.5

		4-Jul-08		2:07:10		69.2		40.5		4-Jul-08		2:06:20		69.2		47.5		4-Jul-08		2:07:53		69.2		41.5

		4-Jul-08		4:07:10		69.8		40		4-Jul-08		4:06:20		68.61		48		4-Jul-08		4:07:53		69.2		41.5

		4-Jul-08		6:07:10		69.8		39.5		4-Jul-08		6:06:20		69.8		44		4-Jul-08		6:07:53		69.2		41.5

		4-Jul-08		8:07:10		69.8		40		4-Jul-08		8:06:20		69.8		50.5		4-Jul-08		8:07:53		69.2		41.5

		4-Jul-08		10:07:10		71		42		4-Jul-08		10:06:20		69.8		50.5		4-Jul-08		10:07:53		69.2		43

		4-Jul-08		12:07:10		70.41		47		4-Jul-08		12:06:20		71.6		55		4-Jul-08		12:07:53		69.2		48

		4-Jul-08		14:07:10		71		47.5		4-Jul-08		14:06:20		71		55		4-Jul-08		14:07:53		69.2		50

		4-Jul-08		16:07:10		71		48		4-Jul-08		16:06:20		71.6		57		4-Jul-08		16:07:53		69.2		50

		4-Jul-08		18:07:10		71.6		46		4-Jul-08		18:06:20		71.6		54		4-Jul-08		18:07:53		69.2		49.5

		4-Jul-08		20:07:10		71.6		43.5		4-Jul-08		20:06:20		71.6		59		4-Jul-08		20:07:53		69.2		46.5

		4-Jul-08		22:07:10		71		41.5		4-Jul-08		22:06:20		69.8		56.5		4-Jul-08		22:07:53		69.2		45

		5-Jul-08		0:07:10		70.41		42		5-Jul-08		0:06:20		69.8		56.5		5-Jul-08		0:07:53		68.61		44.5

		5-Jul-08		2:07:10		69.8		41		5-Jul-08		2:06:20		69.8		54.5		5-Jul-08		2:07:53		69.2		43.5

		5-Jul-08		4:07:10		69.8		41		5-Jul-08		4:06:20		69.2		53		5-Jul-08		4:07:53		69.2		42.5

		5-Jul-08		6:07:10		69.2		41.5		5-Jul-08		6:06:20		68.61		54.5		5-Jul-08		6:07:53		68.61		43

		5-Jul-08		8:07:10		69.8		42		5-Jul-08		8:06:20		69.2		55		5-Jul-08		8:07:53		69.2		44

		5-Jul-08		10:07:10		71		43		5-Jul-08		10:06:20		69.8		51.5		5-Jul-08		10:07:53		69.2		45

		5-Jul-08		12:07:10		71		45		5-Jul-08		12:06:20		69.8		53.5		5-Jul-08		12:07:53		69.2		47.5

		5-Jul-08		14:07:10		71.6		45.5		5-Jul-08		14:06:20		70.41		55		5-Jul-08		14:07:53		69.2		48.5

		5-Jul-08		16:07:10		71.6		46		5-Jul-08		16:06:20		70.41		55.5		5-Jul-08		16:07:53		69.2		49.5

		5-Jul-08		18:07:10		71.6		45		5-Jul-08		18:06:20		70.41		59.5		5-Jul-08		18:07:53		68.61		48.5

		5-Jul-08		20:07:10		71		42.5		5-Jul-08		20:06:20		69.8		58		5-Jul-08		20:07:53		69.2		46

		5-Jul-08		22:07:10		71		41.5		5-Jul-08		22:06:20		69.2		57.5		5-Jul-08		22:07:53		69.2		45

		6-Jul-08		0:07:10		70.41		41		6-Jul-08		0:06:20		69.2		56		6-Jul-08		0:07:53		69.2		43.5

		6-Jul-08		2:07:10		69.8		40.5		6-Jul-08		2:06:20		68.61		54.5		6-Jul-08		2:07:53		68.61		43

		6-Jul-08		4:07:10		69.8		40.5		6-Jul-08		4:06:20		69.2		52.5		6-Jul-08		4:07:53		68.61		42.5

		6-Jul-08		6:07:10		69.2		41.5		6-Jul-08		6:06:20		69.2		51.5		6-Jul-08		6:07:53		68.61		42.5

		6-Jul-08		8:07:10		69.8		41.5		6-Jul-08		8:06:20		69.2		53		6-Jul-08		8:07:53		68.61		43.5

		6-Jul-08		10:07:10		71		43		6-Jul-08		10:06:20		69.8		55.5		6-Jul-08		10:07:53		69.2		45

		6-Jul-08		12:07:10		71		47		6-Jul-08		12:06:20		70.41		58.5		6-Jul-08		12:07:53		69.2		49

		6-Jul-08		14:07:10		71.6		49		6-Jul-08		14:06:20		70.41		57.5		6-Jul-08		14:07:53		69.2		52

		6-Jul-08		16:07:10		72.21		46		6-Jul-08		16:06:20		70.41		54		6-Jul-08		16:07:53		69.2		51

		6-Jul-08		18:07:10		72.21		47		6-Jul-08		18:06:20		69.8		61		6-Jul-08		18:07:53		69.2		51

		6-Jul-08		20:07:10		72.21		45		6-Jul-08		20:06:20		70.41		54.5		6-Jul-08		20:07:53		69.2		50

		6-Jul-08		22:07:10		72.21		43		6-Jul-08		22:06:20		69.8		62		6-Jul-08		22:07:53		68.61		48

		7-Jul-08		0:07:10		71.6		41.5		7-Jul-08		0:06:20		69.8		57		7-Jul-08		0:07:53		69.2		45

		7-Jul-08		2:07:10		71		41		7-Jul-08		2:06:20		69.8		52		7-Jul-08		2:07:53		69.2		44.5

		7-Jul-08		4:07:10		70.41		41		7-Jul-08		4:06:20		69.2		54		7-Jul-08		4:07:53		69.2		43.5

		7-Jul-08		6:07:10		69.8		40.5		7-Jul-08		6:06:20		69.2		52.5		7-Jul-08		6:07:53		68.61		43

		7-Jul-08		8:07:10		70.41		41.5		7-Jul-08		8:06:20		69.2		53.5		7-Jul-08		8:07:53		69.2		43.5

		7-Jul-08		10:07:10		71		44		7-Jul-08		10:06:20		69.2		58		7-Jul-08		10:07:53		69.2		46

		7-Jul-08		12:07:10		71.6		47.5		7-Jul-08		12:06:20		69.8		62		7-Jul-08		12:07:53		69.2		50

		7-Jul-08		14:07:10		71.6		50.5		7-Jul-08		14:06:20		70.41		59.5		7-Jul-08		14:07:53		69.2		54

		7-Jul-08		16:07:10		72.21		48.5		7-Jul-08		16:06:20		69.8		62		7-Jul-08		16:07:53		69.8		52.5

		7-Jul-08		18:07:10		72.21		46.5		7-Jul-08		18:06:20		70.41		59.5		7-Jul-08		18:07:53		69.2		52

		7-Jul-08		20:07:10		72.21		42.5		7-Jul-08		20:06:20		69.8		55		7-Jul-08		20:07:53		68.61		47.5

		7-Jul-08		22:07:10		72.21		40.5		7-Jul-08		22:06:20		69.8		50		7-Jul-08		22:07:53		69.2		44.5

		8-Jul-08		0:07:10		71		40		8-Jul-08		0:06:20		69.2		52		8-Jul-08		0:07:53		69.2		43.5

		8-Jul-08		2:07:10		70.41		40.5		8-Jul-08		2:06:20		69.2		51		8-Jul-08		2:07:53		69.2		42.5

		8-Jul-08		4:07:10		69.8		40.5		8-Jul-08		4:06:20		68.61		51.5		8-Jul-08		4:07:53		68.61		42.5

		8-Jul-08		6:07:10		69.2		40.5		8-Jul-08		6:06:20		69.2		51.5		8-Jul-08		6:07:53		68.61		42.5

		8-Jul-08		8:07:10		70.41		41.5		8-Jul-08		8:06:20		69.8		53.5		8-Jul-08		8:07:53		68.61		44

		8-Jul-08		10:07:10		71.6		44		8-Jul-08		10:06:20		69.8		50.5		8-Jul-08		10:07:53		68.61		47.5

		8-Jul-08		12:07:10		71		49		8-Jul-08		12:06:20		69.8		54		8-Jul-08		12:07:53		69.2		51

		8-Jul-08		14:07:10		71		49.5		8-Jul-08		14:06:20		70.41		55.5		8-Jul-08		14:07:53		69.2		53.5

		8-Jul-08		16:07:10		71		50		8-Jul-08		16:06:20		70.41		58.5		8-Jul-08		16:07:53		68.61		53.5

		8-Jul-08		18:07:10		71		49		8-Jul-08		18:06:20		70.41		55.5		8-Jul-08		18:07:53		68.61		52.5

		8-Jul-08		20:07:10		71		45		8-Jul-08		20:06:20		71		57.5		8-Jul-08		20:07:53		68		50

		8-Jul-08		22:07:10		71.6		43		8-Jul-08		22:06:20		70.41		53		8-Jul-08		22:07:53		68.61		47.5

		9-Jul-08		0:07:10		71.6		42		9-Jul-08		0:06:20		70.41		52		9-Jul-08		0:07:53		69.2		46

		9-Jul-08		2:07:10		71		41.5		9-Jul-08		2:06:20		69.8		50		9-Jul-08		2:07:53		69.2		44.5

		9-Jul-08		4:07:10		71		41.5		9-Jul-08		4:06:20		69.2		53.5		9-Jul-08		4:07:53		69.2		44

		9-Jul-08		6:07:10		70.41		41		9-Jul-08		6:06:20		69.2		52.5		9-Jul-08		6:07:53		69.2		43.5

		9-Jul-08		8:07:10		71		42.5		9-Jul-08		8:06:20		70.41		56.5		9-Jul-08		8:07:53		68.61		45

		9-Jul-08		10:07:10		71		45.5		9-Jul-08		10:06:20		71		53		9-Jul-08		10:07:53		69.2		48.5

		9-Jul-08		12:07:10		71		49		9-Jul-08		12:06:20		71.6		51		9-Jul-08		12:07:53		69.8		50.5

		9-Jul-08		14:07:10		70.41		47.5		9-Jul-08		14:06:20		71.6		51		9-Jul-08		14:07:53		68.61		51

		9-Jul-08		16:07:10		70.41		49		9-Jul-08		16:06:20		71.6		52.5		9-Jul-08		16:07:53		69.8		50

		9-Jul-08		18:07:10		70.41		48.5		9-Jul-08		18:06:20		70.41		53		9-Jul-08		18:07:53		69.8		50

		9-Jul-08		20:07:10		71		44		9-Jul-08		20:06:20		71		53		9-Jul-08		20:07:53		69.2		47.5

		9-Jul-08		22:07:10		71.6		43		9-Jul-08		22:06:20		70.41		54		9-Jul-08		22:07:53		69.8		46

		10-Jul-08		0:07:10		71.6		42		10-Jul-08		0:06:20		69.8		54.5		10-Jul-08		0:07:53		69.2		45

		10-Jul-08		2:07:10		71.6		41.5		10-Jul-08		2:06:20		69.8		54		10-Jul-08		2:07:53		69.8		44

		10-Jul-08		4:07:10		71		42		10-Jul-08		4:06:20		69.2		58		10-Jul-08		4:07:53		69.8		44

		10-Jul-08		6:07:10		71		41.5		10-Jul-08		6:06:20		69.8		55.5		10-Jul-08		6:07:53		69.8		43.5

		10-Jul-08		8:07:10		71		42.5		10-Jul-08		8:06:20		69.8		58.5		10-Jul-08		8:07:53		69.8		45

		10-Jul-08		10:07:10		71		44.5		10-Jul-08		10:06:20		69.8		58.5		10-Jul-08		10:07:53		68		48.5

		10-Jul-08		12:07:10		70.41		49		10-Jul-08		12:06:20		69.8		56.5		10-Jul-08		12:07:53		69.2		50.5

		10-Jul-08		14:07:10		70.41		52.5		10-Jul-08		14:06:20		71.6		54		10-Jul-08		14:07:53		69.2		54.5

		10-Jul-08		16:07:10		70.41		51		10-Jul-08		16:06:20		71.6		60		10-Jul-08		16:07:53		68.61		54

		10-Jul-08		18:07:10		70.41		49.5		10-Jul-08		18:06:20		70.41		63		10-Jul-08		18:07:53		69.8		51

		10-Jul-08		20:07:10		71		46		10-Jul-08		20:06:20		70.41		58.5		10-Jul-08		20:07:53		69.8		48.5

		10-Jul-08		22:07:10		71.6		43.5		10-Jul-08		22:06:20		70.41		57		10-Jul-08		22:07:53		69.8		47

		11-Jul-08		0:07:10		71.6		42.5		11-Jul-08		0:06:20		69.8		61		11-Jul-08		0:07:53		69.2		46.5

		11-Jul-08		2:07:10		71.6		42.5		11-Jul-08		2:06:20		69.8		53.5		11-Jul-08		2:07:53		69.8		45.5

		11-Jul-08		4:07:10		71		42		11-Jul-08		4:06:20		69.8		53.5		11-Jul-08		4:07:53		69.2		44.5

		11-Jul-08		6:07:10		71		41.5		11-Jul-08		6:06:20		69.8		57		11-Jul-08		6:07:53		69.2		44.5

		11-Jul-08		8:07:10		71		42.5		11-Jul-08		8:06:20		71.6		49		11-Jul-08		8:07:53		69.8		45

		11-Jul-08		10:07:10		71		45.5		11-Jul-08		10:06:20		72.21		56.5		11-Jul-08		10:07:53		68.61		48

		11-Jul-08		12:07:10		71		48.5		11-Jul-08		12:06:20		69.8		63		11-Jul-08		12:07:53		69.2		50.5

		11-Jul-08		14:07:10		71		49.5		11-Jul-08		14:06:20		70.41		55.5		11-Jul-08		14:07:53		69.2		52.5

		11-Jul-08		16:07:10		71		47		11-Jul-08		16:06:20		69.8		63.5		11-Jul-08		16:07:53		69.2		49.5

		11-Jul-08		18:07:10		71		45		11-Jul-08		18:06:20		70.41		54		11-Jul-08		18:07:53		69.2		47.5

		11-Jul-08		20:07:10		71		42.5		11-Jul-08		20:06:20		70.41		53		11-Jul-08		20:07:53		69.2		45.5

		11-Jul-08		22:07:10		71		40.5		11-Jul-08		22:06:20		70.41		52.5		11-Jul-08		22:07:53		69.8		43.5

		12-Jul-08		0:07:10		70.41		41		12-Jul-08		0:06:20		69.2		53		12-Jul-08		0:07:53		69.2		43

		12-Jul-08		2:07:10		70.41		41		12-Jul-08		2:06:20		69.2		52.5		12-Jul-08		2:07:53		69.8		42.5

		12-Jul-08		4:07:10		69.8		40.5		12-Jul-08		4:06:20		69.2		52.5		12-Jul-08		4:07:53		69.2		42.5

		12-Jul-08		6:07:10		69.8		40.5		12-Jul-08		6:06:20		69.2		52.5		12-Jul-08		6:07:53		69.2		42.5

		12-Jul-08		8:07:10		70.41		41.5		12-Jul-08		8:06:20		69.2		55		12-Jul-08		8:07:53		69.2		43

		12-Jul-08		10:07:10		71		42.5		12-Jul-08		10:06:20		69.2		57.5		12-Jul-08		10:07:53		69.2		44.5

		12-Jul-08		12:07:10		71		45.5		12-Jul-08		12:06:20		68.61		53.5		12-Jul-08		12:07:53		69.8		46.5

		12-Jul-08		14:07:10		70.41		45.5		12-Jul-08		14:06:20		69.2		52.5		12-Jul-08		14:07:53		69.8		47.5

		12-Jul-08		16:07:10		70.41		45.5		12-Jul-08		16:06:20		69.2		63.5		12-Jul-08		16:07:53		69.8		47.5

		12-Jul-08		18:07:10		70.41		44.5		12-Jul-08		18:06:20		69.8		54		12-Jul-08		18:07:53		70.41		46.5

		12-Jul-08		20:07:10		71		42.5		12-Jul-08		20:06:20		70.41		54		12-Jul-08		20:07:53		70.41		45

		12-Jul-08		22:07:10		71		42.5		12-Jul-08		22:06:20		69.8		59.5		12-Jul-08		22:07:53		70.41		44.5

		13-Jul-08		0:07:10		71		42.5		13-Jul-08		0:06:20		69.8		60		13-Jul-08		0:07:53		69.8		44

		13-Jul-08		2:07:10		71		42.5		13-Jul-08		2:06:20		69.2		60.5		13-Jul-08		2:07:53		70.41		44.5

		13-Jul-08		4:07:10		71		42.5		13-Jul-08		4:06:20		69.2		60		13-Jul-08		4:07:53		70.41		44.5

		13-Jul-08		6:07:10		71		42.5		13-Jul-08		6:06:20		69.2		61		13-Jul-08		6:07:53		70.41		44.5

		13-Jul-08		8:07:10		71		42.5		13-Jul-08		8:06:20		68.61		59		13-Jul-08		8:07:53		69.8		44

		13-Jul-08		10:07:10		71		43		13-Jul-08		10:06:20		69.2		59.5		13-Jul-08		10:07:53		70.41		44.5

		13-Jul-08		12:07:10		71		45		13-Jul-08		12:06:20		69.2		59		13-Jul-08		12:07:53		69.8		46

		13-Jul-08		14:07:10		71		45		13-Jul-08		14:06:20		70.41		54		13-Jul-08		14:07:53		69.8		47

		13-Jul-08		16:07:10		71.6		44.5		13-Jul-08		16:06:20		69.8		55.5		13-Jul-08		16:07:53		69.8		47

		13-Jul-08		18:07:10		71.6		44		13-Jul-08		18:06:20		69.2		58.5		13-Jul-08		18:07:53		69.2		47

		13-Jul-08		20:07:10		71.6		43		13-Jul-08		20:06:20		69.2		57.5		13-Jul-08		20:07:53		69.8		46.5

		13-Jul-08		22:07:10		71		42.5		13-Jul-08		22:06:20		69.2		60.5		13-Jul-08		22:07:53		70.41		45.5

		14-Jul-08		0:07:10		71		42.5		14-Jul-08		0:06:20		69.2		58		14-Jul-08		0:07:53		70.41		44.5

		14-Jul-08		2:07:10		70.41		42		14-Jul-08		2:06:20		69.2		52		14-Jul-08		2:07:53		70.41		43.5

		14-Jul-08		4:07:10		70.41		42		14-Jul-08		4:06:20		69.2		57.5		14-Jul-08		4:07:53		69.8		43

		14-Jul-08		6:07:10		69.8		41		14-Jul-08		6:06:20		69.2		55.5		14-Jul-08		6:07:53		69.8		42.5

		14-Jul-08		8:07:10		69.8		42		14-Jul-08		8:06:20		69.2		56.5		14-Jul-08		8:07:53		69.8		43

		14-Jul-08		10:07:10		70.41		44		14-Jul-08		10:06:20		69.2		53.5		14-Jul-08		10:07:53		70.41		44.5

		14-Jul-08		12:07:10		70.41		47		14-Jul-08		12:06:20		69.8		62		14-Jul-08		12:07:53		70.41		47

		14-Jul-08		14:07:10		71		47		14-Jul-08		14:06:20		69.8		59.5		14-Jul-08		14:07:53		70.41		48

		14-Jul-08		16:07:10		71		47		14-Jul-08		16:06:20		69.8		60.5		14-Jul-08		16:07:53		70.41		48.5

		14-Jul-08		18:07:10		71		45		14-Jul-08		18:06:20		70.41		57		14-Jul-08		18:07:53		70.41		47

		14-Jul-08		20:07:10		71		43.5		14-Jul-08		20:06:20		69.8		59.5		14-Jul-08		20:07:53		70.41		46

		14-Jul-08		22:07:10		71		42.5		14-Jul-08		22:06:20		69.2		59.5		14-Jul-08		22:07:53		70.41		44.5

		15-Jul-08		0:07:10		70.41		42		15-Jul-08		0:06:20		69.2		57		15-Jul-08		0:07:53		70.41		43.5

		15-Jul-08		2:07:10		70.41		42		15-Jul-08		2:06:20		68.61		56		15-Jul-08		2:07:53		70.41		43.5

		15-Jul-08		4:07:10		69.8		41.5		15-Jul-08		4:06:20		68.61		59		15-Jul-08		4:07:53		69.8		43

		15-Jul-08		6:07:10		69.8		42		15-Jul-08		6:06:20		69.2		56.5		15-Jul-08		6:07:53		69.8		43

		15-Jul-08		8:07:10		70.41		42		15-Jul-08		8:06:20		68		53.5		15-Jul-08		8:07:53		69.8		43.5

		15-Jul-08		10:07:10		71		42		15-Jul-08		10:06:20		69.2		54.5		15-Jul-08		10:07:53		69.8		44

		15-Jul-08		12:07:10		71		44.5		15-Jul-08		12:06:20		69.2		60		15-Jul-08		12:07:53		69.8		45

		15-Jul-08		14:07:10		71		46.5		15-Jul-08		14:06:20		69.2		62		15-Jul-08		14:07:53		69.2		48.5

		15-Jul-08		16:07:10		70.41		45.5		15-Jul-08		16:06:20		69.2		57.5		15-Jul-08		16:07:53		69.8		47.5

		15-Jul-08		18:07:10		70.41		44.5		15-Jul-08		18:06:20		69.8		54.5		15-Jul-08		18:07:53		69.8		46

		15-Jul-08		20:07:10		71		42.5		15-Jul-08		20:06:20		70.41		53.5		15-Jul-08		20:07:53		69.8		44.5

		15-Jul-08		22:07:10		71		41.5		15-Jul-08		22:06:20		69.2		54.5		15-Jul-08		22:07:53		69.8		43.5

		16-Jul-08		0:07:10		70.41		41.5		16-Jul-08		0:06:20		69.2		57		16-Jul-08		0:07:53		69.2		43

		16-Jul-08		2:07:10		69.8		41.5		16-Jul-08		2:06:20		69.8		55.5		16-Jul-08		2:07:53		69.2		43.5

		16-Jul-08		4:07:10		69.8		41.5		16-Jul-08		4:06:20		68.61		56.5		16-Jul-08		4:07:53		69.2		43

		16-Jul-08		6:07:10		69.8		41		16-Jul-08		6:06:20		69.2		56		16-Jul-08		6:07:53		69.2		43

		16-Jul-08		8:07:10		70.41		41.5		16-Jul-08		8:06:20		68.61		58.5		16-Jul-08		8:07:53		69.2		43

		16-Jul-08		10:07:10		70.41		42		16-Jul-08		10:06:20		69.8		55		16-Jul-08		10:07:53		68.61		44.5

		16-Jul-08		12:07:10		71		42.5		16-Jul-08		12:06:20		69.8		51		16-Jul-08		12:07:53		69.2		44.5

		16-Jul-08		14:07:10		71		44.5		16-Jul-08		14:06:20		69.8		51		16-Jul-08		14:07:53		68.61		47.5

		16-Jul-08		16:07:10		71		45		16-Jul-08		16:06:20		70.41		57		16-Jul-08		16:07:53		68.61		48





		



CER 1 Temperature(°F)

CER 2 Temperature(°F)

CER 3 Temperature(°F)

Date

Temperature (Deg. F)

Figure 9.  CER Temperature



		



CER 1 Humidity(%)

CER 3 Humidity(%)

QA Humidity(%)

CER 2 Humidity(%)

Date

Humidity (%)

Figure 10.  CER Relative Humidity



		






_1294660947.xls
Chart5

		39478		39478		39478		39478		39478		39478

		39506		39506		39507		39507		39507		39507

		39537		39538		39538		39538		39538		39538

		39568		39568		39568		39568		39539		39539

		39598		39599		39599		39599		39599		39599

		39629		39629		39629		39629		39629		39629

		39637		39637		39630		39637		39660		39660

		39668		39668		39661		39668		39690		39690

		39692		39699		39692		39699		39721		39721



CER1

CER Change Room

CER 2

CER 3

CER Alert Level

CER Action Level

Date

Diff. Pressure (Water Column In.)

Figure 6.  CER Differential Pressure - Monthly Average

0.0884090909

0.0315909091

0.0402272727

0.015

0.005

0.0345652174

0.0345555556

0.0487272727

0.0402380952

0.015

0.005

0.0413913043

0.03935

0.06315

0.0401923077

0.015

0.005

0.0427272727

0.04

0.0534090909

0.0475

0.015

0.005

0.0410416667

0.04

0.0426086957

0.0397916667

0.015

0.005

0.0386363636

0.0372727273

0.0426086957

0.025

0.015

0.005

0.0266

0.04

0.077

0.0594

0.015

0.005

0.0314

0.0406

0.0614

0.0566

0.015

0.005

0.03

0.0406

0.0594

0.0594

0.015

0.005



Airstrip Count

		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148

		39206		39206		39206		39148		39148

		39230		39230		39230		39167		39167

		39267		39267		39267		39206		39206

		39297		39297		39297		39230		39230

		39349		39349		39349		39267		39267

		39392		39392		39392		39297		39297

		39427		39427		39427		39349		39349

		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713



CER 1

CER 2

CER3

Alert Level

Action Level

Date

Average CER Count

Figure 1.  Average Airstrip Count

3.625

6

29

10

15

5.375

7.5

28

10

15

13.125

13.25

28.75

10

15

13.25

11

27.75

10

15

4.25

5.25

24.5

10

15

4

1.75

11.75

10

15

4.25

9.25

10

15

19.5

5.5

22.5

10

15

5.75

4.25

13

10

15

3.25

1

4.75

10

15

11.625

8

18.25

10

15

3.875

1.75

10.5

10

15

4.125

2

10

35

45

1.125

0.5

3.5

35

45

3

1.25

6.5

35

45

3.25

0.75

5.25

35

45

2

0.75

2.75

35

45

6.375

1.75

8.25

35

45

13.5

1.25

10.25

35

45

2.6666666667

2.6666666667

11.25

35

45

6.2

4

3.75

35

45

6.2666666667

2

3.75

35

45

7.6666666667

3

7.5

35

45

9.4

2.8888888889

9

35

45

8.4

3.4444444444

6.5

35

45

6.5333333333

2.3333333333

8.5

35

45



Contact Plate Count

		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148

		39206		39206		39206		39148		39148

		39230		39230		39230		39167		39167

		39267		39267		39267		39206		39206

		39297		39297		39297		39230		39230

		39349		39349		39349		39267		39267

		39392		39392		39392		39297		39297

		39427		39427		39427		39392		39392

		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

Alert Level

Action Level

Date

Contact Plate Count

Figure 2. Average Contact Plate Count

1.4285714286

0.25

2.5

10

15

3.7142857143

2.75

4

10

15

1.1428571429

1.75

0.8333333333

10

15

2.4285714286

3

2.5

10

15

2.4285714286

0.75

3.1666666667

10

15

5.5714285714

3.25

5

10

15

5.2857142857

5.2

10

15

2.7142857143

1.5

2

10

15

1.1428571429

0

2

10

15

3.1428571429

1

3.25

10

15

3.4285714286

3.25

2.25

10

15

1.5714285714

0.75

1.5

10

15

1.7142857143

1

2.25

6

7

0.5714285714

0.5

2.25

6

7

1.5714285714

0.5

3

6

7

2

0.75

2.5

6

7

0.7142857143

0.25

1.75

6

7

3.4285714286

1.25

3.25

6

7

4

1

3.75

6

7

1.5333333333

1

3

6

7

2

1

2.25

6

7

1.7333333333

0.6666666667

1.5

6

7

0.9333333333

0.4444444444

1.5

6

7

0.9333333333

0.7777777778

2.5

6

7

1.1333333333

0.6666666667

1.75

6

7

0.9333333333

0.6666666667

1.5

6

7



0.5micron Count

		38776		38776		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126		39126		39126

		39148		39167		39167		39148		39148		39148		39148

		39148		39206		39206		39148		39148		39148		39148

		39167		39230		39230		39167		39167		39167		39167

		39206		39267		39267		39206		39206		39206		39206

		39230		39297		39297		39230		39230		39297		39297

		39267		39349		39349		39267		39267		39349		39349

		39297		39392		39392		39297		39297		39392		39392

		39392		39427		39427		39392		39392		39427		39427

		39545		39545		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

CER 1,3 Alert Level

CER 1,3 Action Level

CER 2 Alert Level

CER 2 Action Level

Date

0.5um/cu ft Count

Figure 3.  Average 0.5mm/cu ft Count

194

383

3263.8

5000

10000

5000

10000

339.5

338.3333333333

1210.4

5000

10000

5000

10000

362.75

719.3333333333

2800.4

5000

10000

5000

10000

688.125

416.3333333333

1999.6

5000

10000

5000

10000

618.75

336.6666666667

2033

5000

10000

5000

10000

692.625

1000

1857.4

5000

10000

5000

10000

401.375

1423.2

5000

10000

5000

10000

523.125

842

2313.2

5000

10000

5000

10000

273

292.3333333333

624.4

5000

10000

5000

10000

588.875

620

1580.4

5000

10000

5000

10000

714

474.6666666667

1255.6

5000

10000

5000

10000

755.625

587.3333333333

1139.8

5000

10000

5000

10000

772.875

643

1484

3800

4500

1250

1500

244

896.6666666667

1571.2

3800

4500

1250

1500

551.75

704.3333333333

2714

3800

4500

1250

1500

678.625

553

1781.8

3800

4500

1250

1500

369.625

300

731.6

3800

4500

1250

1500

664

478

1178.6

3800

4500

1250

1500

835.625

525

1260.6

3800

4500

1250

1500

699

83.7777777778

1354.8

3800

4500

1250

1500

635

204.4444444444

620.8

3800

4500

1250

1500

606

181.3333333333

750.8

3800

4500

1250

1500

606

109.5555555556

474.6

3800

4500

1250

1500

612.0666666667

156.7777777778

659.8

3800

4500

1250

1500

285.1333333333

190.5555555556

945.2

3800

4500

1250

1500

474

216.3333333333

768.6

3800

4500

1250

1500



5.0micron Count

		38776		38776		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148		39148		39148

		39206		39206		39206		39148		39148		39148		39148

		39230		39230		39230		39167		39167		39167		39167

		39267		39267		39267		39206		39206		39267		39267

		39297		39297		39297		39230		39230		39297		39297

		39349		39349		39349		39267		39267		39349		39349

		39392		39392		39392		39297		39297		39392		39392

		39427		39427		39427		39392		39392		39427		39427

		39545		39545		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

CER 1,3 Alert Level

CER 1,3 Action Level

CER 2 Alert Level

CER 2 Action Level

Date

5.0um/cu ft Count

Figure 4.  Average 5.0mm/cu ft Count

14.125

48.6666666667

226.8

30

50

30

50

33.625

49.3333333333

104.4

30

50

30

50

36.25

49

211.4

30

50

30

50

126.75

76.6666666667

305.2

30

50

30

50

67.875

37.3333333333

344.6

30

50

30

50

71.75

72.3333333333

166.4

30

50

30

50

43.5

235

30

50

30

50

65.125

37.3333333333

219.4

30

50

30

50

33.125

31.3333333333

50.6

30

50

30

50

47.75

50.6666666667

99.4

30

50

30

50

43.875

32.3333333333

79.2

30

50

30

50

47.125

44.3333333333

92.8

30

50

30

50

49

43.3333333333

92.2

410

500

90

105

30.75

75.6666666667

129.2

410

500

90

105

78.875

89

258.4

410

500

90

105

60

44

147

410

500

90

105

28.375

22.6666666667

53

410

500

90

105

26.125

20.3333333333

58

410

500

90

105

45.125

24.3333333333

80.8

410

500

90

105

37.3333333333

10

69.2

410

500

90

105

34.6

12.5555555556

33.2

410

500

90

105

29

9.3333333333

34

410

500

90

105

29

7.1111111111

33

410

500

90

105

30.0666666667

8.8888888889

27.6

410

500

78

83

18.7333333333

11.5555555556

43.4

410

500

78

83

24.3333333333

9.8888888889

37.6

410

500

78

83



CER 1

				AIRSTRIPS:																																																																																																		CONTACT PLATES:																																																																																																		PARTICLE COUNTS

				A						B						C						D						E						F						G						H						I						J						K						L						M						N						O						Average								A						B						C						D						E						F						G						H						I						J						K						L						M						N						O						Average								A				B				C				D				E				F				G				H				I				J				K				L				M				N				O				Average

		Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 1		Date		Alert Level		Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 1		Date		Alert Level		Action Level		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		CER 1 0.5um/ cu ft		Date		CER 1,3 Alert Level		CER 1,3 Action Level		CER 1 5.0um/cu ft		Date		CER 1,3 Alert Level		CER 1,3 Action Level

		2/28/06		2		0		2		4		0		4		5		0		5		4		0		4		8		0		8		0		0		0		3		0		3		3		0		3																																												4		2/28/06		10		15		0		0		0		0		0		0		1		0		1		0		0		0		2		0		2		0		0		0		3		0		3		4		0		4						0						0						0						0						0						0						0		1		2/28/06		10		15		207		8		291		16		133		12		278		21		134		13		25		5		262		22		222		16																														194		02/28/06		5000		10000		14		2/28/06		30		50

		3/30/06		4		0		4		4		0		4		7		0		7		6		0		6		10		0		10		2		0		2		6		0		6		4		0		4																																												5		3/30/06		10		15		1		0		1		3		0		3		6		0		6		3		0		3		2		0		2		5		0		5		3		0		3		3		0		3						0						0						0						0						0						0						0		4		3/30/06		10		15		310		48		483		69		134		18		263		24		444		31		679		40		199		8		204		31																														340		03/30/06		5000		10000		34		3/30/06		30		50

		4/28/06		4		0		4		12		0		12		12		0		12		15		0		15		17		0		17		6		4		10		12		0		12		23		0		23																																												13		4/28/06		10		15		0		0		0		2		0		2		2		0		2		0		0		0		0		0		0		0		0		0		4		0		4		0		0		0						0						0						0						0						0						0						0		1		4/28/06		10		15		487		81		221		21		261		19		390		32		480		60		287		23		321		19		455		35																														363		04/28/06		5000		10000		36		4/28/06		30		50

		5/30/06		6		0		6		10		0		10		12		0		12		17		0		17		19		0		19		9		0		9		12		0		12		21		0		21																																												13		5/30/06		10		15		1		0		1		4		0		4		3		0		3		0		0		0		1		0		1		0		0		0		7		0		7		1		0		1						0						0						0						0						0						0						0		2		5/30/06		10		15		678		124		1084		137		214		36		113		21		1478		449		220		32		1009		120		709		95																														688		05/30/06		5000		10000		127		5/30/06		30		50

		7/7/06		4		0		4		2		0		2		6		0		6		4		0		4		8		0		8		1		0		1		4		0		4		5		0		5																																												4		7/7/06		10		15		1		0		1		2		0		2		1		0		1		2		0		2		2		0		2		1		0		1		4		0		4		4		0		4						0						0						0						0						0						0						0		2		7/7/06		10		15		631		86		779		72		1234		81		282		38		464		75		694		93		564		65		302		33																														619		07/07/06		5000		10000		68		7/7/06		30		50

		9/5/06		4		0		4		4		0		4		6		0		6		5		0		5		2		0		2		2		0		2		4		0		4		5		0		5																																												4		9/5/06		10		15		4		0		4		6		0		6		4		0		4		3		0		3		6		0		6		5		0		5		5		0		5		6		0		6						0						0						0						0						0						0						0		6		9/5/06		10		15		1056		113		622		73		227		35		828		84		603		57		875		95		545		56		785		61																														693		09/05/06		5000		10000		72		9/5/06		30		50

		10/5/06		5		0		5		4		0		4		4		0		4		5		0		5		6		0		6		4		0		4		3		0		3		3		0		3																																												4		10/5/06		10		15		5		0		5		6		0		6		4		0		4		4		0		4		5		0		5		3		0		3		6		0		6		4		0		4						0						0						0						0						0						0						0		5		10/5/06		10		15		122		14		263		18		352		48		540		69		361		38		421		63		389		41		763		57																														401		10/05/06		5000		10000		44		10/5/06		30		50

		11/14/06		11		0		11		27		0		27		10		0		10		24		0		24		26		0		26		32		0		32		12		0		12		14		0		14																																												20		11/14/06		10		15		1		0		1		1		0		1		0		0		0		0		0		0		5		0		5		1		0		1		2		0		2		9		0		9						0						0						0						0						0						0						0		3		11/14/06		10		15		596		71		455		67		641		77		585		62		991		81		357		52		62		60		498		51																														523		11/14/06		5000		10000		65		11/14/06		30		50

		12/20/06		2		0		2		1		0		1		5		0		5		1		0		1		13		0		13		7		0		7		13		0		13		4		0		4																																												6		12/20/06		10		15		1		0		1		2		0		2		0		0		0		1		0		1		3		0		3		1		0		1		0		0		0		0		0		0						0						0						0						0						0						0						0		1		12/20/06		10		15		367		35		390		46		168		18		321		30		343		32		191		14		90		25		314		65																														273		12/20/06		5000		10000		33		12/20/06		30		50

		1/16/07		3		0		3		2		0		2		4		0		4		6		0		6		2		0		2		2		0		2		3		0		3		4		0		4																																												3		1/16/07		10		15		2		0		2		2		0		2		1		0		1		3		0		3		4		0		4		2		0		2		4		0		4		4		0		4						0						0						0						0						0						0						0		3		1/16/07		10		15		361		21		449		56		304		35		265		31		761		42		804		62		901		64		866		71																														589		01/16/07		5000		10000		48		1/16/07		30		50

		2/13/07		11		0		11		5		0		5		10		0		10		6		0		6		24		0		24		6		0		6		10		0		10		21		0		21																																												12		2/13/07		10		15		1		0		1		8		0		8		3		0		3		2		0		2		0		0		0		4		0		4		2		0		2		4		0		4						0						0						0						0						0						0						0		3		2/13/07		10		15		611		41		862		50		841		42		942		61		744		40		622		33		402		24		688		60																														714		02/13/07		5000		10000		44		2/13/07		30		50

		3/26/07		3		0		3		4		0		4		4		0		4		6		0		6		2		0		2		4		0		4		6		0		6		2		0		2																																												4		3/7/07		10		15		1		0		1		1		0		1		2		0		2		0		0		0		1		0		1		2		0		2		2		0		2		2		0		2						0						0						0						0						0						0						0		2		3/7/07		10		15		721		51		640		42		871		48		901		52		844		48		408		36		799		49		861		51																														756		03/07/07		5000		10000		47		3/7/07		30		50

		5/4/07		4		0		4		4		0		4		3		0		3		4		0		4		6		0		6		2		0		2		6		0		6		4		0		4																																												4		3/7/07		35		45		2		0		2		1		0		1		2		0		2		1		0		1		0		0		0		1		0		1		2		0		2		3		0		3						0						0						0						0						0						0						0		2		3/7/07		6		7		641		41		722		52		699		47		944		61		872		45		698		41		662		37		945		68																														773		03/07/07		3800		4500		49		3/7/07		410		500

		5/28/07		1		0		1		1		0		1		2		0		2		0		0		0		2		0		2		1		0		1		1		0		1		1		0		1																																												1		3/26/07		35		45		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1						0						0						0						0						0						0						0		1		3/26/07		6		7		161		17		200		21		251		36		275		28		320		53		101		15		460		55		184		21																														244		03/26/07		3800		4500		31		3/26/07		410		500

		7/4/07		2		0		2		3		0		3		3		0		3		3		0		3		2		0		2		4		0		4		4		0		4		3		0		3																																												3		5/4/07		35		45		2		0		2		2		0		2		1		0		1		0		0		0		1		0		1		1		0		1		2		0		2		2		0		2						0						0						0						0						0						0						0		2		5/4/07		6		7		346		64		339		37		537		77		301		55		492		86		292		31		896		120		1211		161																														552		05/04/07		3800		4500		79		5/4/07		410		500

		8/3/07		4		0		4		2		0		2		3		0		3		2		0		2		2		0		2		4		0		4		4		0		4		5		0		5																																												3		5/28/07		35		45		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		3		0		3		3		0		3		2		0		2						0						0						0						0						0						0						0		2		5/28/07		6		7		221		20		107		19		647		49		587		37		744		87		907		78		1241		101		975		89																														679		05/28/07		3800		4500		60		5/28/07		410		500

		9/24/07		2		0		2		1		0		1		1		0		1		2		0		2		3		0		3		3		0		3		2		0		2		2		0		2																																												2		7/4/07		35		45		0		0		0		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		2		0		2		2		0		2						0						0						0						0						0						0						0		1		7/4/07		6		7		310		27		488		31		210		20		401		29		121		18		404		31		601		41		422		30																														370		07/04/07		3800		4500		28		7/4/07		410		500

		11/6/07		6		0		6		4		0		4		4		0		4		4		0		4		8		0		8		7		0		7		8		0		8		10		0		10																																												6		8/3/07		35		45		2		0		2		2		0		2		3		0		3		1		0		1		3		0		3		5		0		5		4		0		4		4		0		4						0						0						0						0						0						0						0		3		8/3/07		6		7		523		33		678		25		498		14		671		22		687		23		721		33		856		34		678		25																														664		08/03/07		3800		4500		26		8/3/07		410		500

		12/11/07		10		0		10		9		0		9		11		0		11		12		0		12		12		0		12		15		0		15		21		0		21		18		0		18																																												14		9/24/07		35		45		2		0		2		1		0		1		3		0		3		4		0		4		4		0		4		4		0		4		3		0		3		7		0		7						0						0						0						0						0						0						0		4		11/6/07		6		7		678		36		761		31		734		34		891		44		851		33		781		33		1011		81		978		69																														836		11/06/07		3800		4500		45		11/6/07		410		500

		4/7/08		6		0		6		5		0		5		7		0		7		6		0		6		0		0		0		0		0		0		2		0		2		4		0		4		4		0		4		3		0		3		2		0		2		0		0		0		0		0		0		0		0		0		1		0		1		3		4/7/08		35		45		2		0		2		1		0		1		3		0		3		3		0		3		2		0		2		1		0		1		1		0		1		0		0		0		2		0		2		0		0		0		2		0		2		1		0		1		1		0		1		2		0		2		2		0		2		2		4/7/08		6		7		989		45		1045		58		1349		61		1305		60		689		46		430		30		1027		60		899		42		621		24		318		19		501		24		313		33		295		13		303		21		401		24		699		04/07/08		3800		4500		37		4/7/08		410		500

		5/7/08		9		0		9		8		0		8		7		0		7		8		0		8		3		0		3		3		0		3		3		0		3		7		0		7		7		0		7		4		0		4		8		0		8		4		0		4		8		0		8		9		0		9		5		0		5		6		5/7/08		35		45		3		0		3		2		0		2		2		0		2		2		0		2		3		0		3		3		0		3		2		0		2		1		0		1		1		0		1		1		0		1		2		0		2		2		0		2		2		0		2		2		0		2		2		0		2		2		5/7/08		6		7		782		44		671		39		724		41		454		22		576		33		430		30		671		32		572		28		781		37		671		32		677		33		476		41		672		31		781		43		587		33		635		05/07/08		3800		4500		35		5/7/08		410		500

		6/3/08		8		0		8		8		0		8		4		0		4		5		0		5		6		0		6		6		0		6		5		0		5		5		0		5		5		0		5		4		0		4		7		0		7		8		0		8		8		0		8		9		0		9		6		0		6		6		6/3/08		35		45		3		0		3		1		0		1		1		0		1		2		0		2		1		0		1		3		0		3		1		0		1		2		0		2		2		0		2		0		0		0		2		0		2		1		0		1		2		0		2		2		0		2		3		0		3		2		6/3/08		6		7		621		33		393		22		891		31		671		25		1192		44		671		19		781		22		245		19		1325		44		601		41		418		31		351		29		301		21		290		23		339		31		606		06/03/08		3800		4500		29		6/3/08		410		500

		7/1/08		9		0		9		9		0		9		7		0		7		9		0		9		8		0		8		5		0		5		8		0		8		8		0		8		8		0		8		6		0		6		11		0		11		6		0		6		9		0		9		9		0		9		3		0		3		8		7/1/08		35		45		1		0		1		2		0		2		0		0		0		1		0		1		1		0		1		1		0		1		0		0		0		0		0		0		2		0		2		1		0		1		1		0		1		2		0		2		0		0		0		1		0		1		1		0		1		1		7/1/08		6		7		621		33		393		22		891		31		671		25		1192		44		671		19		781		22		245		19		1325		44		601		41		418		31		351		29		301		21		290		23		339		31		606		07/01/08		3800		4500		29		7/1/08		410		500

		7/21/08		11		0		11		11		0		11		5		0		5		5		0		5		12		0		12		11		0		11		12		0		12		6		0		6		6		0		6		9		0		9		14		0		14		15		0		15		11		0		11		6		0		6		7		0		7		9		7/21/08		35		45		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		7/21/08		6		7		232		23		452		26		337		27		671		33		476		27		501		28		488		28		782		37		561		27		442		28		891		38		590		29		876		31		991		42		891		27		612		07/21/08		3800		4500		30		7/21/08		410		500

		9/4/08		10		0		10		9		0		9		6		0		6		7		0		7		7		0		7		9		0		9		6		0		6		9		0		9		11		0		11		12		0		12		10		0		10		9		0		9		6		0		6		6		0		6		9		0		9		8		9/4/08		35		45		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		9/4/08		6		7		219		19		140		14		275		16		101		9		244		16		301		21		189		19		181		17		176		17		215		21		414		24		409		21		357		21		454		19		602		27		285		09/04/08		3800		4500		19		9/4/08		410		500

		9/22/08		5		0		5		5		0		5		9		0		9		5		0		5		5		0		5		9		0		9		11		0		11		4		0		4		11		0		11		5		0		5		5		0		5		6		0		6		6		0		6		8		0		8		4		0		4		7		9/22/08		35		45		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		0		0		0		2		0		2		1		0		1		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		9/22/08		6		7		332		21		254		19		354		21		548		31		369		22		584		26		651		22		448		26		296		19		489		29		336		21		754		32		565		26		665		29		465		21		474		09/22/08		3800		4500		24		9/22/08		410		500

		11/6/08		3		0		3		3		0		3		5		0		5		4		0		4		4		0		4		3		0		3		4		0		4		4		0		4		4		0		4		5		0		5		5		0		5		3		0		3		3		0		3		3		0		3		4		0		4		4		11/6/08		35		45		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		1		0		1		0		11/6/08		6		7		721		31		867		39		253		12		458		22		357		20		445		28		432		22		685		31		591		28		241		9		219		8		473		19		501		21		765		33		801		36		521		11/06/08		3800		4500		24		11/6/08		410		500

		12/1/08		2		0		2		0		0		0		0		0		0		2		0		2		2		0		2		3		0		3		0		0		0		1		0		1		4		0		4		3		0		3		2		0		2		1		0		1		0		0		0		2		0		2		3		0		3		2		12/1/08		35		45		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		1		12/1/08		6		7		110		9		89		9		122		13		25		6		59		8		131		18		40		7		274		19		157		12		88		6		150		9		114		8		517		32		180		15		234		21		153		12/01/08		3800		4500		13		12/1/08		410		500

		12/16/08		3		0		3		2		0		2		3		0		3		2		0		2		2		0		2		3		0		3		4		0		4		3		0		3		5		0		5		4		0		4		4		0		4		3		0		3		3		0		3		3		0		3		3		0		3		3		12/16/08		35		45		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		1		0		1		1		12/16/08		6		7		291		18		178		11		271		19		189		14		177		14		276		18		198		11		187		14		278		17		91		7		87		6		287		16		376		21		301		17		227		19		228		12/16/08		3800		4500		15		12/16/08		410		500



&L&"Arial Narrow,Bold"&14CER 1&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER 2

										AIRSTRIPS:																																																												CONTACT PLATES:																																																						PARTICLE COUNTS

				A						B						C						D						E						F						G						H						I						Average						A						B						C						D						E						F						G						H						I						Average						A				B				C				D				E				F				G				H				I				Average

		Sample Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 2		Alert Level		Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 2		Total Alert Level		Total Action Level		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		CER 2 0.5um/cu ft		Date		CER 2 Alert Level		CER 2 Action Level		CER 2 5.0um/cu ft		Date		CER 2 Alert Level		CER 2 Action Level

		2/28/06								6		0		6		0		0		0		9		0		9		9		0		9																										6		10		15								0		0		0		0		0		0		1		0		1		0		0		0																										0		10		15		297		39		288		43		0		0		564		64																						383		2/28/06		5000		10000		49		02/28/06		30		50

		3/30/06								9		0		9		1		0		1		8		0		8		12		0		12																										8		10		15								2		0		2		0		0		0		6		0		6		3		0		3																										3		10		15		460		68		264		39		0		0		291		41																						338		3/30/06		5000		10000		49		03/30/06		30		50

		4/28/06								29		0		29		0		0		0		22		0		22		2		0		2																										13		10		15								2		0		2		2		0		2		0		0		0		3		0		3																										2		10		15		1084		67		543		41		0		0		531		39																						719		4/28/06		5000		10000		49		04/28/06		30		50

		5/30/06								21		0		21		0		0		0		19		0		19		4		0		4																										11		10		15								4		0		4		2		0		2		1		0		1		5		0		5																										3		10		15		435		87		354		66		0		0		460		77																						416		5/30/06		5000		10000		77		05/30/06		30		50

		7/7/06								5		0		5		0		0		0		8		0		8		8		0		8																										5		10		15								0		0		0		0		0		0		2		0		2		1		0		1																										1		10		15		232		33		299		39		0		0		479		40																						337		7/7/06		5000		10000		37		07/07/06		30		50

		9/5/06								3		0		3		0		0		0		2		0		2		2		0		2																										2		10		15								4		0		4		0		0		0		4		0		4		5		0		5																										3		10		15		1289		79		289		30		0		0		1422		108																						1000		9/5/06		5000		10000		72		09/05/06		30		50

		10/5/06																																																																																																																																																																10/5/06		5000		10000				10/05/06		30		50

		11/14/06								16		0		16		0		0		0		4		0		4		2		0		2																										6		10		15								1		0		1		0		0		0		4		0		4		1		0		1																										2		10		15		961		41		877		40		0		0		688		31																						842		11/14/06		5000		10000		37		11/14/06		30		50

		12/20/06								5		0		5		4		0		4		6		0		6		2		0		2																										4		10		15								0		0		0		0		0		0		0		0		0		0		0		0																										0		10		15		463		36		141		17		0		0		273		41																						292		12/20/06		5000		10000		31		12/20/06		30		50

		1/16/07								2		0		2		0		0		0		1		0		1		1		0		1																										1		10		15								1		0		1		0		0		0		1		0		1		2		0		2																										1		10		15		781		62		451		32		0		0		628		58																						620		1/16/07		5000		10000		51		01/16/07		30		50

		2/13/07								12		0		12		0		0		0		10		0		10		10		0		10																										8		10		15								4		0		4		0		0		0		4		0		4		4		1		5																										3		10		15		640		31		285		44		0		0		499		22																						475		2/13/07		5000		10000		32		02/13/07		30		50

		3/26/07								2		0		2		0		0		0		2		0		2		3		0		3																										2		35		45								1		0		1		0		0		0		1		0		1		1		0		1																										1		6		7		490		40		684		51		0		0		588		42																						587		3/7/07		5000		10000		44		03/07/07		30		50

		5/4/07								2		0		2		0		0		0		3		0		3		3		0		3																										2		35		45								1		0		1		0		0		0		1		0		1		2		0		2																										1		6		7		640		41		585		37		0		0		704		52																						643		3/7/07		1250		1500		43		03/07/07		90		105

		5/28/07								0		0		0		0		0		0		1		0		1		1		0		1																										1		35		45								1		0		1		0		0		0		0		0		0		1		0		1																										1		6		7		1104		101		944		81		0		0		642		45																						897		3/26/07		1250		1500		76		03/26/07		90		105

		7/4/07								1		0		1		0		0		0		2		0		2		2		0		2																										1		35		45								0		0		0		0		0		0		1		0		1		1		0		1																										1		6		7		10		0		962		123		0		0		1141		132																						704		5/4/07		1250		1500		89		07/04/07		90		105

		8/3/07								0		0		0		0		0		0		1		0		1		2		0		2																										1		35		45								1		0		1		0		0		0		1		0		1		1		0		1																										1		6		7		0		0		784		61		0		0		875		71																						553		8/3/07		1250		1500		44		08/03/07		90		105

		9/24/07								1		0		1		0		0		0		1		0		1		1		0		1																										1		35		45								0		0		0		0		0		0		0		0		0		1		0		1																										0		6		7		0		0		199		19		0		0		701		49																						300		9/24/07		1250		1500		23		09/24/07		90		105

		11/6/07								1		0		1		0		0		0		3		0		3		3		0		3																										2		35		45								1		0		1		0		0		0		2		0		2		2		0		2																										1		6		7		4		0		563		22		0		0		867		39																						478		11/6/07		1250		1500		20		11/06/07		90		105

		12/11/07								0		0		0		0		0		0		2		0		2		3		0		3																										1		35		45								0		0		0		0		0		0		3		0		3		1		0		1																										1		6		7		2		0		672		36		0		0		901		37																						525		12/11/07		1250		1500		24		12/11/07		90		105

		4/7/08		0		0		0		4		0		4		7		0		7		0		0		0		4		0		4		0		0		0		6		0		6		3		0		3		0		0		0		3		35		45		0		0		0		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		2		0		2		2		0		2		0		0		0		1		6		7		0		0		162		23		208		25		0		0		93		19		0		0		90		6		201		17		0		0		84		4/7/08		1250		1500		10		04/07/08		90		105

		5/7/08		0		0		0		3		0		3		9		0		9		0		0		0		8		0		8		0		0		0		8		0		8		8		0		8		0		0		0		4		35		45		0		0		0		2		0		2		3		0		3		0		0		0		2		0		2		0		0		0		1		0		1		1		0		1		0		0		0		1		6		7		0		0		401		24		489		25		0		0		281		22		0		0		187		18		482		24		0		0		204		5/7/08		1250		1500		13		05/07/08		90		105

		6/3/08		0		0		0		3		0		3		3		0		3		0		0		0		5		0		5		0		0		0		5		0		5		2		0		2		0		0		0		2		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		0		1		0		0		0		1		6		7		0		0		267		10		498		22		0		0		268		22		0		0		301		19		298		11		0		0		181		6/3/08		1250		1500		9		06/03/08		90		105

		7/1/08		0		0		0		8		0		8		0		0		0		8		0		8		6		0		6		0		0		0		3		0		3		2		0		2		0		0		0		3		35		45		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		0		6		7		0		0		403		22		0		0		153		11		287		19		1		0		21		1		121		11		0		0		110		7/1/08		1250		1500		7		07/01/08		90		105

		7/21/08		0		0		0		6		0		6		0		0		0		7		0		7		7		0		7		0		0		0		4		0		4		2		0		2		0		0		0		3		35		45		0		0		0		2		0		2		0		0		0		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		0		0		0		1		6		7		0		0		376		19		0		0		298		17		337		21		0		0		109		8		291		15		0		0		157		7/21/08		1250		1500		9		07/21/08		78		83

		9/4/08		0		0		0		7		0		7		9		0		9		0		0		0		4		0		4		0		0		0		4		0		4		4		0		4		3		0		3		3		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		6		7		0		0		210		19		175		11		0		0		361		18		0		0		101		7		162		9		706		40		191		9/4/08		1250		1500		12		09/04/08		78		83

		9/22/08		0		0		0		5		0		5		4		0		4		0		0		0		4		0		4		0		0		0		2		0		2		4		0		4		2		0		2		2		35		45		0		0		0		2		0		2		0		0		0		0		0		0		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		1		6		7		0		0		332		21		296		15		0		0		194		9		0		0		265		11		295		11		565		22		216		9/22/08		1250		1500		10		09/22/08		78		83

		11/6/08		0		0		0		2		0		2		3		0		3		0		0		0		2		0		2		0		0		0		3		0		3		3		0		3		2		0		2		2		35		45		0		0		0		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		6		7		0		0		776		22		409		19		0		0		292		8		0		0		301		16		228		11		220		9		247		11/6/08		1250		1500		9		11/06/08		78		83

		12/1/08		0		0		0		3		0		3		2		0		2		0		0		0		3		0		3		0		0		0		2		0		2		0		0		0		1		0		1		1		35		45		0		0		0		1		0		1		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		6		7		0		0		290		12		203		11		0		0		221		12		0		0		313		21		19		3		148		10		133		12/1/08		1250		1500		8		12/01/08		78		83

		12/16/08		0		0		0		4		0		4		3		0		3		0		0		0		3		0		3		0		0		0		3		0		3		0		0		0		1		0		1		2		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		6		7		0		0		199		9		289		16		0		0		167		7		0		0		267		17		89		6		177		11		132		12/16/08		1250		1500		7		12/16/08		78		83



&L&"Arial Narrow,Bold"&14CER 2&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER 3

				AIRSTRIPS:																														CONTACT PLATES:																																				PARTICLE COUNTS

				A						B						D						E						Average						A						B						C						D						E						Average						A				B				C				D				E				Average

		Sample Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER3		Total Alert Level		Total Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 3		Total Alert Level		Total Action Level		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		CER 3 0.5um/cu ft		0.5um/cu ft Alert Level		0.5um/cu ft Action Level		CER 3 5.0um/cu ft		5.0um/cu ft Alert Level		5.0um/cu ft Action Level

		2/28/06		29		1		30		21		0		21		28		0		28		37		0		37		29		10		15		3		0		3		3		0		3		3		0		3		2		0		2		4		0		4		3		10		15		4411		344		3943		271		3664		229		3068		212		1233		78		3264		5000		10000		227		30		50

		3/30/06		32		1		33		26		0		26		21		0		21		32		0		32		28		10		15		5		0		5		4		0		4		6		0		6		4		0		4		5		0		5		4		10		15		1261		119		979		81		1461		101		1721		120		630		101		1210		5000		10000		104		30		50

		4/28/06		29		2		31		32		0		32		23		0		23		29		0		29		29		10		15		2		0		2		3		0		3		0		0		0		0		0		0		0		0		0		1		10		15		4536		307		3293		245		2424		222		2637		211		1112		72		2800		5000		10000		211		30		50

		5/30/06		31		0		31		29		0		29		21		1		22		29		0		29		28		10		15		4		0		4		5		0		5		2		0		2		1		0		1		3		0		3		3		10		15		1914		327		2122		327		2561		413		1572		207		1829		252		2000		5000		10000		305		30		50

		7/7/06		26		0		26		19		0		19		22		0		22		31		0		31		25		10		15		4		0		4		5		0		5		3		0		3		2		0		2		5		0		5		3		10		15		2150		382		2668		423		2561		401		2022		399		764		118		2033		5000		10000		345		30		50

		9/5/06		10		0		10		12		0		12		11		0		11		14		0		14		12		10		15		6		0		6		4		0		4		4		0		4		6		0		6		5		0		5		5		10		15		2286		180		2142		171		1829		162		1749		171		1281		148		1857		5000		10000		166		30		50

		10/5/06		9		0		9		10		0		10		10		0		10		8		0		8		9		10		15		7		0		7		5		0		5		6		0		6		4		0		4		4		0		4		5		10		15		1679		346		793		137		1841		241		1429		248		1374		203		1423		5000		10000		235		30		50

		11/14/06		19		2		21		26		0		26		26		0		26		17		0		17		23		10		15		2		0		2		1		0		1		0		0		0		1		0		1		6		0		6		2		10		15		2241		243		2301		231		1974		198		2475		224		2575		201		2313		5000		10000		219		30		50

		12/20/06		10		0		10		13		0		13		13		0		13		16		0		16		13		10		15		5		0		5		1		0		1		0		0		0		3		0		3		1		0		1		2		10		15		406		33		727		46		923		94		604		41		462		39		624		5000		10000		51		30		50

		1/16/07		4		0		4		5		0		5		7		0		7		3		0		3		5		10		15		3		0		3		2		0		2		3		0		3		4		0		4		4		0		4		3		10		15		485		41		1785		101		1986		128		1785		109		1861		118		1580		5000		10000		99		30		50

		2/13/07		12		0		12		22		0		22		18		0		18		21		0		21		18		10		15		2		0		2		4		0		4		2		0		2		1		0		1		2		0		2		2		10		15		1261		87		1641		98		901		62		988		61		1487		88		1256		5000		10000		79		30		50

		3/26/07		11		0		11		12		0		12		10		0		10		9		0		9		11		35		45		2		0		2		1		0		1		2		0		2		1		0		1		2		0		2		2		6		7		1421		109		1221		101		866		71		949		82		1242		101		1140		3800		4500		93		410		500

		5/4/07		10		0		10		10		0		10		9		0		9		11		0		11		10		35		45		2		0		2		3		0		3		1		0		1		2		0		2		2		0		2		2		6		7		1741		110		1444		91		1235		81		1479		87		1521		92		1484		3800		4500		92		410		500

		5/28/07		6		0		6		4		0		4		2		0		2		2		0		2		4		35		45		4		0		4		2		0		2		1		0		1		1		0		1		2		0		2		2		6		7		1421		102		1387		100		1842		169		1785		154		1421		121		1571		3800		4500		129		410		500

		7/4/07		7		0		7		6		0		6		6		0		6		7		0		7		7		35		45		4		0		4		3		0		3		2		0		2		1		0		1		4		0		4		3		6		7		3950		375		2745		292		1658		177		2431		201		2786		247		2714		3800		4500		258		410		500

		8/3/07		6		0		6		6		0		6		4		0		4		5		0		5		5		35		45		3		0		3		3		0		3		2		0		2		2		0		2		2		0		2		3		6		7		1672		145		1897		152		1866		149		1987		151		1487		138		1782		3800		4500		147		410		500

		9/24/07		4		0		4		3		0		3		2		0		2		2		0		2		3		35		45		2		0		2		2		0		2		2		0		2		1		0		1		2		0		2		2		6		7		781		61		1011		72		689		49		768		52		409		31		732		3800		4500		53		410		500

		11/6/07		7		0		7		9		0		9		8		0		8		9		0		9		8		35		45		3		0		3		3		0		3		5		0		5		1		0		1		6		0		6		3		6		7		1276		78		1454		65		1109		55		987		45		1067		47		1179		3800		4500		58		410		500

		12/11/07		9		0		9		12		0		12		9		0		9		11		0		11		10		35		45		2		0		2		4		0		4		4		0		4		5		0		5		4		0		4		4		6		7		1853		101		1321		99		901		45		1241		87		987		72		1261		3800		4500		81		410		500

		4/7/08		8		0		8		15		0		15		12		0		12		10		0		10		11		35		45		2		0		2		3		0		3		2		0		2		3		0		3		4		0		4		3		6		7		1047		69		1642		79		1421		67		1677		71		987		60		1355		3800		4500		69		410		500

		5/7/08		3		0		3		4		0		4		4		0		4		4		0		4		4		35		45		4		0		4		3		0		3		4		0		4		1		0		1		1		0		1		2		6		7		561		31		761		44		660		39		451		21		671		31		621		3800		4500		33		410		500

		6/3/08		3		0		3		4		0		4		4		0		4		4		0		4		4		35		45		2		0		2		2		0		2		2		0		2		1		0		1		1		0		1		2		6		7		409		26		391		33		782		34		891		33		1281		44		751		3800		4500		34		410		500

		7/1/08		7		0		7		7		0		7		8		0		8		8		0		8		8		35		45		2		0		2		2		0		2		1		0		1		1		0		1		1		0		1		2		6		7		1121		81		677		42		339		22		125		11		111		9		475		3800		4500		33		410		500

		7/21/08		9		0		9		8		0		8		8		0		8		11		0		11		9		35		45		3		0		3		3		0		3		2		0		2		2		0		2		2		0		2		3		6		7		891		41		781		33		789		31		499		21		339		12		660		3800		4500		28		410		500

		9/4/08		6		0		6		9		0		9		4		0		4		7		0		7		7		35		45		2		0		2		2		0		2		1		0		1		2		0		2		1		0		1		2		6		7		793		37		1044		44		977		39		1011		57		901		40		945		3800		4500		43		410		500

		9/22/08		9		0		9		9		0		9		9		0		9		7		0		7		9		35		45		1		0		1		2		0		2		2		0		2		2		0		2		1		0		1		2		6		7		984		44		564		31		965		33		698		41		632		39		769		3800		4500		38		410		500

		11/6/08		6		0		6		6		0		6		4		0		4		3		0		3		5		35		45		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		1		6		7		1198		81		901		67		789		43		761		41		904		61		911		3800		4500		59		410		500

		12/1/08		7		0		7		7		0		7		6		0		6		7		0		7		7		35		45		2		0		2		1		0		1		2		0		2		1		0		1		1		0		1		1		6		7		1198		81		901		67		789		43		761		41		904		61		911		3800		4500		59		410		500

		12/16/08		8		0		8		8		0		8		6		0		6		9		0		9		8		35		45		1		0		1		2		0		2		1		0		1		1		0		1		1		0		1		1		6		7		892		41		1098		69		892		34		901		44		1167		72		990		3800		4500		52		410		500



&L&"Arial Narrow,Bold"&14CER 3&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER Pressure

		Daily				Monthly				Daily				Monthly				Daily																		Monthly																		Daily								Monthly								Specs

		Date		CER1		Month		CER1		Date		CER Change Room		Month		CER Change Room		Date		CER2		Temp (F)		Relative Humidity (%)		R&D Bio-Safety Cabinet North (left axis)		R&D Bio-Safety Cabinet South (left axis)		Mfg Bio-Safety Cabinet North (left axis)		Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)		Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)		Month		CER 2		Temp (F)		Relative Humidity (%)		R&D Bio-Safety Cabinet North (left axis)		R&D Bio-Safety Cabinet South (left axis)		Mfg Bio-Safety Cabinet North (left axis)		Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)		Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)		Date		CER3		Temp (ºF)		Humidity (%RH)		Month		CER 3		Temp (ºF)		Humidity (%RH)		Date		CER Alert Level		CER Action Level		Bio-Safety Cabinet Alert Level (left axis)		Bio-Safety Cabinet Action  Level (left axis)		Mfg Bio-Safety Cabinet South Alert Level (right axis)		Mfg Bio-Safety Cabinet South Alarm Level (right axis)

		4/24/06		0.05		April-06		0.045		3/31/06		0.05		March-06		0.055		3/31/06		0.09																March-06		0.090																6/19/06		0.05						June-06		0.051						4/30/06		0.05		0.03

		4/24/06		0.05		May-06		0.022		3/31/06		0.06		April-06		0.053		3/31/06		0.09																April-06		0.089																6/19/06		0.06						July-06		0.061						5/31/06		0.05		0.03

		4/25/06		0.05		June-06		0.013		4/4/06		0.05		May-06		0.050		4/4/06		0.09																July-06		0.076																6/28/06		0.03						August-06		0.055						6/30/06		0.05		0.03

		4/25/06		0.04		July-06		0.041		4/4/06		0.05		June-06		0.046		4/4/06		0.09																August-06		0.068																6/28/06		0.06						September-06		0.052						7/31/06		0.05		0.03

		4/26/06		0.06		August-06		0.033		4/5/06		0.05		July-06		0.048		4/5/06		0.09																September-06		0.062																6/29/06		0.03						October-06		0.051						8/31/06		0.05		0.03

		4/26/06		0.04		September-06		0.027		4/5/06		0.06		August-06		0.050		4/5/06		0.09																October-06		0.034																6/29/06		0.06						November-06		0.053						9/30/06		0.05		0.03

		4/27/06		0.04		October-06		0.033		4/6/06		0.05		September-06		0.048		4/6/06		0.09																November-06		0.020																6/30/06		0.06						December-06		0.051						10/31/06		0.05		0.03

		4/27/06		0.045		November-06		0.028		4/6/06		0.06		October-06		0.053		4/6/06		0.09																December-06		0.012																6/30/06		0.06						February-07		0.040						11/30/06		0.05		0.03

		4/28/06		0.05		December-06		0.030		4/7/06		0.055		November-06		0.035		4/7/06		0.09																January-07		0.011																7/5/06		0.03						March-07		0.037						12/31/06		0.05		0.03

		4/28/06		0.04		January-07		0.030		4/7/06		0.05		December-06		0.031		4/7/06		0.09																February-07		0.013																7/5/06		0.03						April-07		0.038						1/31/07		0.05		0.03

		4/29/06		0.035		February-07		0.038		4/10/06		0.055		January-07		0.031		4/10/06		0.095																March-07		0.031																7/6/06		0.06						May-07		0.038						1/28/07		0.05		0.03

		4/29/06		0.035		March-07		0.037		4/10/06		0.055		February-07		0.035		4/10/06		0.09																April-07		0.033																7/6/06		0.06						June-07		0.040						3/7/07		0.05		0.03

		5/1/06		0.025		April-07		0.031		4/11/06		0.055		March-07		0.036		4/11/06		0.095																May-07		0.044																7/7/06		0.06						July-07		0.057						3/7/07		0.03		0.005

		5/1/06		0.03		May-07		0.027		4/11/06		0.055		April-07		0.035		4/11/06		0.095																June-07		0.048																7/7/06		0.06						August-07		0.053						4/30/07		0.03		0.005

		5/2/06		0.025		June-07		0.027		4/12/06		0.055		May-07		0.032		4/12/06		0.09																July-07		0.050																7/10/06		0.06						September-07		0.050						5/16/07		0.03		0.005

		5/2/06		0.03		July-07		0.035		4/12/06		0.055		June-07		0.028		4/12/06		0.09																August-07		0.042																7/10/06		0.06						October-07		0.049						5/16/07		0.015		0.005

		5/3/06		0.015		August-07		0.032		4/13/06		0.055		July-07		0.030		4/13/06		0.09																September-07		0.046						0.610		0.408								7/11/06		0.06						November-07		0.047						5/31/07		0.015		0.005

		5/4/06		0.03		September-07		0.030		4/13/06		0.055		August-07		0.032		4/13/06		0.095																October-07		0.041						0.620		0.420								7/11/06		0.06						December-07		0.043						6/30/07		0.015		0.005

		5/5/06		0.03		October-07		0.030		4/17/06		0.06		September-07		0.029		4/17/06		0.095																November-07		0.035						0.632		0.424								7/12/06		0.06						January-08		0.040						7/31/07		0.015		0.005

		5/5/06		0.03		November-07		0.065		4/17/06		0.055		October-07		0.027		4/17/06		0.09																December-07		0.030						0.643		0.426								7/12/06		0.06						February-08		0.040						8/31/07		0.015		0.005

		5/6/06		0.03		December-07		0.077		4/18/06		0.055		November-07		0.044		4/18/06		0.095																January-08																		7/13/06		0.06						March-08		0.040						9/5/07		0.015		0.005		0.25		0.1

		5/6/06		0.025		January-08		0.088		4/18/06		0.06		December-07		0.043		4/18/06		0.09																February-08		0.049		69.778		46.100		0.281		0.309		0.428		62.091		1180.364		7/13/06		0.06						April-08		0.048		70.864		42.636		9/30/07		0.015		0.005		0.25		0.1

		5/7/06		0.03		February-08		0.035		4/19/06		0.045		January-08		0.032		4/19/06		0.085																March-08		0.063		70.000		39.750		0.272		0.318		0.441		63.000		1193.000		7/14/06		0.06						May-08		0.040		72.696		37.435		10/31/07		0.015		0.005		0.25		0.1

		5/8/06		0.03		March-08		0.041		4/19/06		0.05		February-08		0.035		4/19/06		0.09																April-08		0.053		71.045		41.000		0.276		0.320		0.454		62.333		1196.333		7/14/06		0.06						June-08		0.025		72.136		33.909		11/30/07		0.015		0.005		0.25		0.1

		5/8/06		0.03		April-08		0.043		4/20/06		0.055		March-08		0.039		4/20/06		0.079																May-08		0.043		72.304		35.913		0.282		0.320		0.449		60.652		1194.957		7/17/06		0.06						July-08		0.059		71.920		39.400		12/31/07		0.015		0.005		0.25		0.1

		5/9/06		0.025		May-08		0.041		4/20/06		0.05		April-08		0.040		4/20/06		0.08																June-08		0.043		71.826		33.522		0.288		0.318		0.447		57.913		790.783		7/17/06		0.06						August-08		0.057		71.600		40.040		1/31/08		0.015		0.005		0.25		0.1

		5/9/06		0.025		June-08		0.039		4/24/06		0.06		May-08		0.040		4/21/06		0.085																July-08		0.077		71.800		38.360		0.285		0.320		0.447		59.789		882.526		7/18/06		0.06						September-08		0.059		71.240		38.000		2/29/08		0.015		0.005		0.25		0.1

		5/10/06		0.025		July-08		0.027		4/24/06		0.06		June-08		0.037		4/21/06		0.085																August-08		0.061		71.440		38.480		0.272		0.318		0.448		0.000		0.000		7/18/06		0.06														3/31/08		0.015		0.005		0.25		0.1

		5/10/06		0.025		August-08		0.031		4/25/06		0.06		July-08		0.040		4/25/06		0.086																September-08		0.059		70.640		38.280		0.259		0.319		0.439		0.000		0.000		7/19/06		0.06														4/1/08		0.015		0.005		0.25		0.1

		5/11/06		0.015		September-08		0.030		4/25/06		0.06		August-08		0.041		4/25/06		0.085																																		7/19/06		0.06														5/31/08		0.015		0.005		0.25		0.1

		5/11/06		0.025						4/26/06		0.05		September-08		0.041		4/26/06		0.085																																		7/20/06		0.07														6/30/08		0.015		0.005		0.25		0.1

		5/12/06		0.025						4/26/06		0.02						4/26/06		0.087																																		7/20/06		0.07														7/31/08		0.015		0.005		0.25		0.1

		5/12/06		0.02						4/27/06		0.06						4/27/06		0.085																																		7/21/06		0.07														8/30/08		0.015		0.005		0.25		0.1

		5/15/06		0.02						4/27/06		0.055						4/27/06		0.085																																		7/21/06		0.07														9/30/08		0.015		0.005		0.25		0.1

		5/15/06		0.025						4/28/06		0.04						4/28/06		0.09																																		7/22/06		0.07

		5/16/06		0.01						4/28/06		0.055						4/28/06		0.08																																		7/22/06		0.07

		5/16/06		0.01						4/29/06		0.05						7/25/06		0.085																																		7/24/06		0.07

		5/17/06		0.01						4/29/06		0.05						7/25/06		0.085																																		7/24/06		0.07

		5/17/06		0.025						5/1/06		0.05						7/26/06		0.085																																		7/25/06		0.06

		5/18/06		0.02						5/1/06		0.055						7/26/06		0.075																																		7/25/06		0.06

		5/18/06		0.02						5/2/06		0.05						7/27/06		0.08																																		7/26/06		0.06

		5/19/06		0.03						5/2/06		0.055						7/27/06		0.08																																		7/26/06		0.06

		5/19/06		0.02						5/3/06		0.05						7/28/06		0.075																																		7/27/06		0.06

		5/20/06		0.01						5/4/06		0.045						7/28/06		0.079																																		7/27/06		0.06

		5/20/06		0.02						5/5/06		0.055						7/29/06		0.069																																		8/1/06		0.06

		5/22/06		0.015						5/5/06		0.05						7/29/06		0.07																																		8/1/06		0.06

		5/22/06		0.015						5/6/06		0.065						7/30/06		0.069																																		8/2/06		0.06

		5/23/06		0.015						5/6/06		0.055						7/30/06		0.069																																		8/2/06		0.06

		5/23/06		0.015						5/7/06		0.05						7/31/06		0.075																																		8/3/06		0.06

		5/24/06		0.015						5/8/06		0.05						7/31/06		0.073																																		8/3/06		0.06

		5/24/06		0.015						5/8/06		0.05						8/1/06		0.07																																		8/4/06		0.06

		5/25/06		0.015						5/9/06		0.05						8/1/06		0.075																																		8/4/06		0.06

		5/25/06		0.03						5/9/06		0.055						8/2/06		0.07																																		8/7/06		0.055

		5/30/06		0.015						5/10/06		0.045						8/2/06		0.07																																		8/7/06		0.06

		5/30/06		0.02						5/10/06		0.04						8/3/06		0.07																																		8/8/06		0.06

		6/1/06		0.01						5/11/06		0.045						8/3/06		0.074																																		8/8/06		0.06

		6/1/06		0.01						5/11/06		0.055						8/4/06		0.074																																		8/9/06		0.06

		6/2/06		0.015						5/12/06		0.05						8/4/06		0.074																																		8/9/06		0.06

		6/5/06		0.01						5/12/06		0.06						8/7/06		0.073																																		8/10/06		0.055

		6/5/06		0.013						5/15/06		0.045						8/7/06		0.073																																		8/10/06		0.055

		6/6/06		0.01						5/15/06		0.055						8/8/06		0.073																																		8/11/06		0.055

		6/6/06		0.01						5/16/06		0.05						8/8/06		0.073																																		8/11/06		0.055

		6/7/06		0.01						5/16/06		0.055						8/10/06		0.074																																		8/14/06		0.055

		6/7/06		0.01						5/17/06		0.04						8/10/06		0.071																																		8/14/06		0.055

		6/8/06		0.01						5/17/06		0.045						8/14/06		0.07																																		8/15/06		0.055

		6/8/06		0.01						5/18/06		0.05						8/15/06		0.069																																		8/15/06		0.055

		6/9/06		0.01						5/18/06		0.055						8/16/06		0.069																																		8/16/06		0.055

		6/9/06		0.01						5/19/06		0.04						8/16/06		0.07																																		8/16/06		0.055

		6/12/06		0.03						5/19/06		0.045						8/17/06		0.069																																		8/17/06		0.055

		6/12/06		0.01						5/20/06		0.04						8/17/06		0.069																																		8/17/06		0.06

		6/13/06		0.03						5/20/06		0.043						8/18/06		0.07																																		8/18/06		0.05

		6/13/06		0.01						5/22/06		0.05						8/18/06		0.068																																		8/18/06		0.065

		6/16/06		0.01						5/22/06		0.05						8/21/06		0.065																																		8/19/06		0.05

		6/16/06		0.01						5/23/06		0.05						8/22/06		0.06																																		8/19/06		0.055

		7/6/06		0.05						5/23/06		0.05						8/22/06		0.065																																		8/21/06		0.055

		7/6/06		0.04						5/24/06		0.045						8/23/06		0.065																																		8/21/06		0.05

		7/7/06		0.04						5/24/06		0.05						8/23/06		0.068																																		8/22/06		0.05

		7/8/06		0.04						5/25/06		0.05						8/24/06		0.065																																		8/22/06		0.056

		7/10/06		0.05						5/25/06		0.05						8/24/06		0.055																																		8/23/06		0.055

		7/11/06		0.04						5/30/06		0.045						8/25/06		0.065																																		8/23/06		0.055

		7/12/06		0.05						5/30/06		0.05						8/25/06		0.065																																		8/24/06		0.05

		7/13/06		0.05						6/1/06		0.045						8/28/06		0.065																																		8/24/06		0.05

		7/17/06		0.06						6/1/06		0.05						8/28/06		0.065																																		8/25/06		0.05

		7/18/06		0.04						6/2/06		0.04						8/30/06		0.065																																		8/25/06		0.055

		7/19/06		0.04						6/5/06		0.05						8/30/06		0.063																																		8/26/06		0.05

		7/20/06		0.04						6/5/06		0.055						8/31/06		0.065																																		8/26/06		0.05

		7/21/06		0.033						6/6/06		0.055						8/31/06		0.065																																		8/28/06		0.05

		7/22/06		0.04						6/6/06		0.05						9/1/06		0.06																																		8/28/06		0.05

		7/23/06		0.04						6/7/06		0.055						9/1/06		0.065																																		8/29/06		0.05

		7/24/06		0.04						6/7/06		0.05						9/5/06		0.065																																		8/29/06		0.05

		7/25/06		0.04						6/8/06		0.05						9/5/06		0.065																																		8/30/06		0.05

		7/26/06		0.035						6/8/06		0.05						9/6/06		0.055																																		8/30/06		0.05

		7/26/06		0.04						6/9/06		0.045						9/6/06		0.065																																		8/31/06		0.05

		7/27/06		0.03						6/9/06		0.05						9/7/06		0.055																																		8/31/06		0.05

		7/27/06		0.04						6/12/06		0.01						9/7/06		0.063																																		9/1/06		0.055

		7/28/06		0.04						6/12/06		0.05						9/8/06		0.06																																		9/6/06		0.05

		7/31/06		0.03						6/13/06		0.01						9/8/06		0.063																																		9/6/06		0.05

		8/1/06		0.035						6/13/06		0.05						9/11/06		0.06																																		9/7/06		0.05

		8/2/06		0.03						6/14/06		0.05						9/11/06		0.065																																		9/7/06		0.05

		8/3/06		0.03						6/14/06		0.055						9/12/06		0.06																																		9/8/06		0.05

		8/4/06		0.03						6/15/06		0.055						9/12/06		0.065																																		9/8/06		0.05

		8/7/06		0.03						6/15/06		0.06						9/13/06		0.06																																		9/11/06		0.05

		8/8/06		0.03						6/16/06		0.05						9/13/06		0.065																																		9/11/06		0.05

		8/10/06		0.03						6/16/06		0.04						9/14/06		0.06																																		9/12/06		0.05

		8/10/06		0.05						6/17/06		0.045						9/14/06		0.065																																		9/12/06		0.06

		8/11/06		0.03						6/17/06		0.05						9/15/06		0.06																																		9/13/06		0.05

		8/11/06		0.05						6/19/06		0.05						9/15/06		0.065																																		9/13/06		0.055

		8/14/06		0.03						6/19/06		0.05						9/18/06		0.06																																		9/14/06		0.05

		8/15/06		0.03						6/20/06		0.05						9/18/06		0.063																																		9/14/06		0.04

		8/16/06		0.05						6/20/06		0.05						9/19/06		0.065																																		9/15/06		0.05

		8/16/06		0.03						6/21/06		0.04						9/19/06		0.055																																		9/15/06		0.05

		8/17/06		0.035						6/21/06		0.05						9/20/06		0.065																																		9/18/06		0.055

		8/17/06		0.03						6/22/06		0.04						9/20/06		0.06																																		9/18/06		0.06

		8/18/06		0.03						6/22/06		0.045						9/21/06		0.065																																		9/19/06		0.05

		8/18/06		0.03						6/26/06		0.04						9/21/06		0.062																																		9/19/06		0.055

		8/19/06		0.035						6/27/06		0.04						9/23/06		0.065																																		9/20/06		0.05

		8/19/06		0.03						6/28/06		0.04						9/23/06		0.062																																		9/20/06		0.05

		8/20/06		0.035						6/29/06		0.04						9/25/06		0.059																																		9/21/06		0.055

		8/21/06		0.03						7/5/06		0.04						9/25/06		0.06																																		9/21/06		0.055

		8/21/06		0.03						7/6/06		0.04						10/2/06		0.06																																		9/22/06		0.05

		8/22/06		0.025						7/7/06		0.05						10/2/06		0.05																																		9/22/06		0.055

		8/22/06		0.035						7/8/06		0.05						10/3/06		0.048																																		9/23/06		0.06

		8/23/06		0.035						7/10/06		0.03						10/3/06		0.042																																		9/23/06		0.06

		8/23/06		0.035						7/11/06		0.05						10/4/06		0.048																																		9/25/06		0.05

		8/24/06		0.035						7/12/06		0.04						10/6/06		0.038																																		9/25/06		0.055

		8/24/06		0.035						7/13/06		0.0425						10/9/06		0.055																																		9/26/06		0.05

		8/25/06		0.035						7/17/06		0.04						10/9/06		0.036																																		9/26/06		0.05

		8/25/06		0.035						7/18/06		0.05						10/10/06		0.037																																		9/27/06		0.05

		8/26/06		0.03						7/19/06		0.05						10/10/06		0.032																																		9/27/06		0.05

		8/26/06		0.035						7/20/06		0.05						10/11/06		0.032																																		9/28/06		0.05

		8/28/06		0.03						7/21/06		0.055						10/11/06		0.032																																		9/28/06		0.05

		8/28/06		0.03						7/22/06		0.055						10/12/06		0.033																																		9/29/06		0.05

		8/29/06		0.03						7/23/06		0.055						10/12/06		0.03																																		9/29/06		0.05

		8/29/06		0.03						7/24/06		0.055						10/13/06		0.031																																		10/2/06		0.055

		8/30/06		0.03						7/25/06		0.05						10/13/06		0.03																																		10/2/06		0.06

		8/30/06		0.035						7/26/06		0.055						10/16/06		0.033																																		10/3/06		0.05

		8/31/06		0.03						7/26/06		0.05						10/16/06		0.032																																		10/3/06		0.05

		8/31/06		0.03						7/27/06		0.05						10/17/06		0.032																																		10/4/06		0.055

		9/1/06		0.03						7/27/06		0.05						10/17/06		0.03																																		10/4/06		0.05

		9/5/06		0.03						7/28/06		0.05						10/18/06		0.033																																		10/5/06		0.05

		9/5/06		0.03						7/31/06		0.05						10/18/06		0.03																																		10/5/06		0.05

		9/6/06		0.02						8/1/06		0.05						10/19/06		0.025																																		10/9/06		0.05

		9/7/06		0.02						8/2/06		0.05						10/19/06		0.03																																		10/9/06		0.05

		9/8/06		0.03						8/3/06		0.05						10/20/06		0.03																																		10/10/06		0.05

		9/11/06		0.03						8/4/06		0.05						10/20/06		0.035																																		10/10/06		0.05

		9/11/06		0.03						8/7/06		0.05						10/23/06		0.032																																		10/11/06		0.05

		9/12/06		0.03						8/8/06		0.05						10/23/06		0.026																																		10/11/06		0.05

		9/12/06		0.03						8/11/06		0.03						10/24/06		0.029																																		10/12/06		0.05

		9/13/06		0.025						8/11/06		0.05						10/24/06		0.029																																		10/12/06		0.05

		9/13/06		0.03						8/14/06		0.05						10/26/06		0.03																																		10/13/06		0.05

		9/14/06		0.03						8/15/06		0.035						10/26/06		0.03																																		10/13/06		0.05

		9/15/06		0.03						8/16/06		0.05						10/30/06		0.025																																		10/14/06		0.05

		9/18/06		0.03						8/17/06		0.05						10/30/06		0.023																																		10/14/06		0.05

		9/19/06		0.03						8/17/06		0.05						10/31/06		0.025																																		10/16/06		0.05

		9/19/06		0.03						8/18/06		0.05						10/31/06		0.015																																		10/16/06		0.05

		9/20/06		0.03						8/18/06		0.05						11/1/06		0.026																																		10/17/06		0.05

		9/20/06		0.03						8/19/06		0.05						11/1/06		0.022																																		10/17/06		0.05

		9/21/06		0.02						8/19/06		0.05						11/2/06		0.025																																		10/18/06		0.05

		9/21/06		0.02						8/20/06		0.05						11/2/06		0.015																																		10/18/06		0.05

		9/22/06		0.02						8/21/06		0.05						11/3/06		0.025																																		10/19/06		0.05

		9/22/06		0.02						8/21/06		0.05						11/3/06		0.015																																		10/19/06		0.05

		9/23/06		0.02						8/22/06		0.045						11/6/06		0.025																																		10/20/06		0.05

		9/23/06		0.03						8/22/06		0.05						11/6/06		0.023																																		10/20/06		0.05

		9/25/06		0.02						8/23/06		0.05						11/7/06		0.02																																		10/23/06		0.05

		9/25/06		0.02						8/23/06		0.055						11/7/06		0.018																																		10/23/06		0.055

		9/26/06		0.02						8/24/06		0.05						11/8/06		0.04																																		10/24/06		0.05

		9/26/06		0.02						8/24/06		0.055						11/8/06		0.018																																		10/24/06		0.05

		9/27/06		0.02						8/25/06		0.05						11/9/06		0.02																																		10/25/06		0.05

		9/27/06		0.05						8/25/06		0.055						11/9/06		0.019																																		10/25/06		0.05

		9/28/06		0.03						8/26/06		0.05						11/10/06		0.02																																		10/26/06		0.05

		9/28/06		0.03						8/26/06		0.05						11/10/06		0.015																																		10/26/06		0.05

		9/29/06		0.02						8/28/06		0.05						11/13/06		0.02																																		10/27/06		0.05

		9/29/06		0.03						8/28/06		0.055						11/13/06		0.02																																		10/27/06		0.05

		10/2/06		0.04						8/29/06		0.05						11/14/06		0.02																																		10/28/06		0.05

		10/3/06		0.03						8/29/06		0.05						11/14/06		0.02																																		10/28/06		0.05

		10/3/06		0.03						8/30/06		0.05						11/15/06		0.02																																		10/30/06		0.05

		10/4/06		0.03						8/30/06		0.05						11/15/06		0.02																																		10/30/06		0.05

		10/4/06		0.03						8/31/06		0.05						11/16/06		0.02																																		10/31/06		0.05

		10/5/06		0.04						8/31/06		0.055						11/17/06		0.02																																		10/31/06		0.05

		10/5/06		0.03						9/1/06		0.05						11/17/06		0.018																																		11/1/06		0.05

		10/6/06		0.02						9/5/06		0.045						11/20/06		0.02																																		11/1/06		0.05

		10/7/06		0.05						9/5/06		0.05						11/20/06		0.015																																		11/2/06		0.05

		10/7/06		0.05						9/6/06		0.045						11/21/06		0.02																																		11/2/06		0.055

		10/9/06		0.04						9/7/06		0.05						11/21/06		0.012																																		11/3/06		0.045

		10/9/06		0.04						9/8/06		0.05						11/22/06		0.02																																		11/3/06		0.05

		10/10/06		0.02						9/11/06		0.05						11/22/06		0.02																																		11/6/06		0.05

		10/10/06		0.02						9/11/06		0.05						11/27/06		0.02																																		11/6/06		0.05

		10/11/06		0.03						9/12/06		0.05						11/27/06		0.04																																		11/7/06		0.05

		10/11/06		0.04						9/12/06		0.05						11/28/06		0.02																																		11/7/06		0.055

		10/12/06		0.035						9/13/06		0.05						11/28/06		0.01																																		11/8/06		0.05

		10/12/06		0.035						9/13/06		0.05						11/29/06		0.02																																		11/8/06		0.06

		10/13/06		0.04						9/14/06		0.05						11/29/06		0.015																																		11/9/06		0.05

		10/13/06		0.04						9/15/06		0.05						11/30/06		0.02																																		11/9/06		0.05

		10/14/06		0.04						9/18/06		0.05						11/30/06		0.015																																		11/10/06		0.05

		10/14/06		0.035						9/19/06		0.05						12/1/06		0.01																																		11/10/06		0.05

		10/16/06		0.04						9/19/06		0.05						12/1/06		0.012																																		11/13/06		0.05

		10/16/06		0.035						9/20/06		0.05						12/4/06		0.01																																		11/13/06		0.06

		10/17/06		0.03						9/20/06		0.05						12/4/06		0.015																																		11/14/06		0.06

		10/17/06		0.04						9/21/06		0.05						12/5/06		0.01																																		11/14/06		0.05

		10/18/06		0.03						9/21/06		0.05						12/5/06		0.015																																		11/15/06		0.055

		10/18/06		0.03						9/22/06		0.05						12/6/06		0.01																																		11/15/06		0.05

		10/19/06		0.025						9/22/06		0.05						12/6/06		0.01																																		11/16/06		0.055

		10/19/06		0.02						9/23/06		0.05						12/7/06		0.02																																		11/16/06		0.055

		10/20/06		0.035						9/23/06		0.05						12/7/06		0.01																																		11/17/06		0.05

		10/20/06		0.05						9/25/06		0.05						12/8/06		0.01																																		11/17/06		0.055

		10/21/06		0.04						9/25/06		0.05						12/8/06		0.01																																		11/18/06		0.05

		10/21/06		0.03						9/26/06		0.05						12/11/06		0.01																																		11/18/06		0.065

		10/23/06		0.035						9/26/06		0.05						12/11/06		0.015																																		11/20/06		0.05

		10/23/06		0.04						9/27/06		0.05						12/12/06		0.01																																		11/20/06		0.06

		10/24/06		0.02						9/27/06		0.02						12/12/06		0.015																																		11/21/06		0.05

		10/24/06		0.02						9/28/06		0.03						12/13/06		0.01																																		11/21/06		0.06

		10/25/06		0.035						9/28/06		0.03						12/13/06		0.015																																		11/22/06		0.05

		10/25/06		0.035						9/29/06		0.05						12/14/06		0.02																																		11/22/06		0.05

		10/26/06		0.025						9/29/06		0.05						12/18/06		0.01																																		11/27/06		0.05

		10/26/06		0.045						10/2/06		0.04						12/18/06		0.01																																		11/27/06		0.05

		10/27/06		0.03						10/3/06		0.05						12/19/06		0.01																																		11/28/06		0.055

		10/27/06		0.03						10/3/06		0.05						12/19/06		0.009																																		11/28/06		0.06

		10/28/06		0.03						10/4/06		0.05						12/20/06		0.01																																		11/29/06		0.05

		10/28/06		0.025						10/4/06		0.05						12/20/06		0.01																																		11/29/06		0.055

		10/30/06		0.035						10/5/06		0.04						12/21/06		0.01																																		11/30/06		0.05

		10/30/06		0.035						10/5/06		0.04						12/21/06		0.008																																		11/30/06		0.05

		10/31/06		0.03						10/6/06		0.03						12/22/06		0.01																																		12/1/06		0.05

		11/1/06		0.025						10/7/06		0.03						12/27/06		0.03																																		12/1/06		0.065

		11/2/06		0.035						10/7/06		0.03						12/28/06		0.01																																		12/2/06		0.05

		11/2/06		0.03						10/9/06		0.03						12/28/06		0.01																																		12/2/06		0.065

		11/3/06		0.02						10/9/06		0.03						12/29/06		0.01																																		12/4/06		0.045

		11/6/06		0.015						10/10/06		0.05						12/29/06		0.01																																		12/4/06		0.05

		11/7/06		0.02						10/10/06		0.05						1/2/07		0.01																																		12/5/06		0.045

		11/8/06		0.025						10/11/06		0.03						1/2/07		0.01																																		12/5/06		0.05

		11/9/06		0.03						10/11/06		0.04						1/3/07		0.01																																		12/6/06		0.05

		11/10/06		0.025						10/12/06		0.035						1/3/07		0.01																																		12/6/06		0.05

		11/11/06		0.035						10/12/06		0.035						1/4/07		0.01																																		12/7/06		0.05

		11/13/06		0.035						10/13/06		0.03						1/4/07		0.01																																		12/7/06		0.05

		11/13/06		0.02						10/13/06		0.04						1/5/07		0.01																																		12/8/06		0.05

		11/14/06		0.02						10/14/06		0.03						1/5/07		0.01																																		12/8/06		0.05

		11/14/06		0.02						10/14/06		0.035						1/8/07		0.01																																		12/9/06		0.05

		11/15/06		0.03						10/16/06		0.04						1/8/07		0.01																																		12/9/06		0.05

		11/15/06		0.035						10/16/06		0.04						1/9/07		0.01																																		12/11/06		0.05

		11/16/06		0.035						10/17/06		0.04						1/9/07		0.01																																		12/11/06		0.05

		11/17/06		0.03						10/17/06		0.04						1/10/07		0.01																																		12/12/06		0.05

		11/17/06		0.035						10/18/06		0.04						1/10/07		0.01																																		12/12/06		0.05

		11/18/06		0.03						10/18/06		0.04						1/11/07		0.02																																		12/13/06		0.055

		11/18/06		0.03						10/19/06		0.04						1/11/07		0.01																																		12/13/06		0.055

		11/20/06		0.045						10/19/06		0.04						1/12/07		0.01																																		12/14/06		0.04

		11/21/06		0.035						10/20/06		0.04						1/12/07		0.01																																		12/14/06		0.05

		11/22/06		0.025						10/20/06		0.04						1/15/07		0.02																																		12/15/06		0.05

		11/22/06		0.035						10/21/06		0.03						1/15/07		0.01																																		12/15/06		0.05

		11/27/06		0.03						10/21/06		0.04						1/16/07		0.01																																		2/28/07		0.04

		11/27/06		0.035						10/23/06		0.035						1/16/07		0.015																																		2/28/07		0.04

		11/28/06		0.015						10/23/06		0.04						1/17/07		0.01																																		3/1/07		0.04

		11/29/06		0.015						10/24/06		0.035						1/17/07		0.01																																		3/2/07		0.04

		11/30/06		0.025						10/24/06		0.035						1/18/07		0.01																																		3/3/07		0.04

		12/1/06		0.025						10/25/06		0.03						1/18/07		0.01																																		3/5/07		0.04

		12/2/06		0.025						10/25/06		0.045						1/19/07		0.01																																		3/6/07		0.04

		12/4/06		0.025						10/26/06		0.045						1/19/07		0.01																																		3/7/07		0.04

		12/5/06		0.03						10/26/06		0.04						1/22/07		0.01																																		3/8/07		0.04

		12/6/06		0.03						10/27/06		0.035						1/22/07		0.02																																		3/9/07		0.04

		12/6/06		0.03						10/27/06		0.03						1/23/07		0.01																																		3/12/07		0.045

		12/7/06		0.03						10/28/06		0.03						1/23/07		0.01																																		3/13/07		0.04

		12/7/06		0.035						10/28/06		0.05						1/24/07		0.01																																		3/14/07		0.04

		12/8/06		0.03						10/30/06		0.035						1/24/07		0.005																																		3/15/07		0.03

		12/8/06		0.03						10/30/06		0.035						1/25/07		0.01																																		3/16/07		0.04

		12/9/06		0.03						10/31/06		0.035						1/25/07		0.01																																		3/17/07		0.04

		12/11/06		0.03						11/1/06		0.035						1/26/07		0.01																																		3/19/07		0.03

		12/11/06		0.03						11/2/06		0.035						1/26/07		0.01																																		3/20/07		0.04

		12/12/06		0.03						11/2/06		0.04						1/29/07		0.01																																		3/21/07		0.04

		12/12/06		0.035						11/3/06		0.035						1/29/07		0.01																																		3/22/07		0.03

		12/13/06		0.03						11/6/06		0.05						1/30/07		0.01																																		3/23/07		0.03

		12/13/06		0.03						11/7/06		0.035						1/30/07		0.01																																		3/26/07		0.04

		12/14/06		0.03						11/8/06		0.04						1/31/07		0.01																																		3/27/07		0.03

		12/14/06		0.03						11/9/06		0.035						1/31/07		0.01																																		3/28/07		0.04

		12/15/06		0.03						11/10/06		0.045						2/1/07		0.01																																		3/29/07		0.03

		12/15/06		0.03						11/11/06		0.04						2/1/07		0.005																																		3/30/07		0.04

		12/18/06		0.03						11/13/06		0.04						2/2/07		0.01																																		3/31/07		0.03

		12/18/06		0.03						11/13/06		0.05						2/2/07		0.005																																		4/2/07		0.03

		12/19/06		0.03						11/14/06		0.04						2/5/07		0.01																																		4/3/07		0.045

		12/19/06		0.03						11/14/06		0.04						2/5/07		0.005																																		4/4/07		0.04

		12/20/06		0.03						11/15/06		0.03						2/6/07		0.01																																		4/5/07		0.04

		12/21/06		0.03						11/15/06		0.03						2/6/07		0.005																																		4/6/07		0.04

		12/21/06		0.03						11/16/06		0.03						2/7/07		0.01																																		4/9/07		0.04

		12/22/06		0.02						11/17/06		0.03						2/7/07		0.005																																		4/10/07		0.03

		12/22/06		0.035						11/17/06		0.035						2/8/07		0.01																																		4/11/07		0.04

		12/27/06		0.03						11/18/06		0.03						2/8/07		0.015																																		4/12/07		0.04

		12/27/06		0.03						11/18/06		0.03						2/9/07		0.01																																		4/13/07		0.035

		12/28/06		0.03						11/20/06		0.015						2/9/07		0.018																																		4/16/07		0.035

		12/28/06		0.03						11/21/06		0.03						2/12/07		0.01																																		4/17/07		0.04

		12/29/06		0.03						11/22/06		0.035						2/12/07		0.012																																		4/18/07		0.035

		12/29/06		0.035						11/22/06		0.035						2/13/07		0.01																																		4/19/07		0.04

		1/2/07		0.03						11/27/06		0.035						2/13/07		0.02																																		4/20/07		0.04

		1/2/07		0.03						11/27/06		0.03						2/14/07		0.02																																		4/23/07		0.03

		1/3/07		0.03						11/28/06		0.035						2/14/07		0.015																																		4/24/07		0.04

		1/3/07		0.03						11/29/06		0.035						2/15/07		0.02																																		4/25/07		0.035

		1/4/07		0.03						11/30/06		0.035						2/16/07		0.01																																		4/26/07		0.035

		1/5/07		0.03						12/1/06		0.03						2/20/07		0.015																																		4/27/07		0.035

		1/5/07		0.03						12/2/06		0.03						2/20/07		0.015																																		4/28/07		0.045

		1/8/07		0.03						12/4/06		0.03						2/21/07		0.02																																		4/30/07		0.04

		1/8/07		0.03						12/5/06		0.03						2/21/07		0.015																																		5/1/07		0.04

		1/9/07		0.03						12/6/06		0.03						2/22/07		0.02																																		5/2/07		0.04

		1/9/07		0.03						12/6/06		0.035						2/22/07		0.018																																		5/3/07		0.04

		1/10/07		0.03						12/7/06		0.03						2/23/07		0.02																																		5/4/07		0.04

		1/10/07		0.03						12/7/06		0.03						2/23/07		0.016																																		5/5/07		0.04

		1/11/07		0.03						12/8/06		0.03						2/26/07		0.015																																		5/7/07		0.035

		1/11/07		0.03						12/8/06		0.035						2/26/07		0.014																																		5/8/07		0.04

		1/12/07		0.03						12/9/06		0.03						2/27/07		0.015																																		5/9/07		0.045

		1/13/07		0.03						12/11/06		0.03						2/27/07		0.014																																		5/10/07		0.04

		1/13/07		0.03						12/11/06		0.03						2/28/07		0.01																																		5/11/07		0.035

		1/15/07		0.03						12/12/06		0.03						3/1/07		0.015																																		5/14/07		0.03

		1/15/07		0.03						12/12/06		0.03						3/2/07		0.015																																		5/15/07		0.035

		1/16/07		0.03						12/13/06		0.03						3/5/07		0.01																																		5/16/07		0.045

		1/16/07		0.025						12/13/06		0.03						3/6/07		0.01																																		5/17/07		0.035

		1/17/07		0.02						12/14/06		0.03						3/7/07		0.04																																		5/18/07		0.04

		1/18/07		0.02						12/14/06		0.035						3/8/07		0.04																																		5/19/07		0.04

		1/19/07		0.03						12/15/06		0.03						3/9/07		0.04																																		5/21/07		0.04

		1/19/07		0.03						12/15/06		0.035						3/12/07		0.04																																		5/22/07		0.04

		1/20/07		0.03						12/18/06		0.03						3/13/07		0.04																																		5/23/07		0.045

		1/22/07		0.03						12/18/06		0.03						3/14/07		0.04																																		5/24/07		0.04

		1/23/07		0.03						12/19/06		0.03						3/15/07		0.035																																		5/29/07		0.03

		1/24/07		0.03						12/19/06		0.03						3/16/07		0.04																																		5/30/07		0.03

		1/24/07		0.03						12/20/06		0.03						3/19/07		0.035																																		5/31/07		0.035

		1/25/07		0.03						12/21/06		0.03						3/20/07		0.035																																		6/1/07		0.035

		1/25/07		0.03						12/21/06		0.035						3/21/07		0.035																																		6/2/07		0.05

		1/26/07		0.03						12/22/06		0.03						3/22/07		0.032																																		6/4/07		0.035

		1/26/07		0.035						12/22/06		0.03						3/23/07		0.03																																		6/5/07		0.04

		1/29/07		0.03						12/27/06		0.03						3/26/07		0.03																																		6/6/07		0.04

		1/29/07		0.035						12/27/06		0.03						3/27/07		0.03																																		6/7/07		0.04

		1/30/07		0.035						12/28/06		0.03						3/28/07		0.035																																		6/8/07		0.045

		1/30/07		0.035						12/28/06		0.035						3/29/07		0.035																																		6/9/07		0.04

		1/31/07		0.03						12/29/06		0.03						3/30/07		0.03																																		6/11/07		0.04

		1/31/07		0.035						12/29/06		0.035						4/2/07		0.03																																		6/12/07		0.04

		2/1/07		0.03						1/2/07		0.03						4/3/07		0.025																																		6/13/07		0.04

		2/1/07		0.03						1/2/07		0.03						4/4/07		0.03																																		6/14/07		0.035

		2/2/07		0.03						1/3/07		0.03						4/5/07		0.025																																		6/15/07		0.045

		2/2/07		0.03						1/3/07		0.03						4/6/07		0.03																																		6/16/07		0.05

		2/3/07		0.03						1/4/07		0.03						4/9/07		0.025																																		6/19/07		0.04

		2/3/07		0.035						1/5/07		0.03						4/10/07		0.03																																		6/20/07		0.04

		2/5/07		0.03						1/5/07		0.03						4/11/07		0.03																																		6/21/07		0.035

		2/5/07		0.03						1/8/07		0.03						4/12/07		0.03																																		6/22/07		0.04

		2/6/07		0.03						1/8/07		0.03						4/13/07		0.028																																		6/23/07		0.04

		2/6/07		0.03						1/9/07		0.03						4/16/07		0.032																																		6/25/07		0.04

		2/7/07		0.05						1/9/07		0.03						4/17/07		0.03																																		6/26/07		0.04

		2/7/07		0.04						1/10/07		0.03						4/18/07		0.025																																		6/27/07		0.04

		2/8/07		0.04						1/10/07		0.035						4/19/07		0.025																																		6/28/07		0.04

		2/8/07		0.03						1/11/07		0.03						4/23/07		0.04																																		6/29/07		0.04

		2/10/07		0.03						1/11/07		0.03						4/24/07		0.044																																		7/2/07		0.04

		2/10/07		0.05						1/12/07		0.03						4/25/07		0.049																																		7/3/07		0.045

		2/12/07		0.03						1/13/07		0.03						4/26/07		0.049																																		7/5/07		0.05

		2/13/07		0.035						1/13/07		0.03						4/27/07		0.045																																		7/6/07		0.05

		2/13/07		0.04						1/15/07		0.03						4/30/07		0.045																																		7/9/07		0.045

		2/14/07		0.04						1/15/07		0.03						5/1/07		0.042																																		7/10/07		0.07

		2/14/07		0.04						1/16/07		0.03						5/2/07		0.045																																		7/11/07		0.045

		2/15/07		0.05						1/16/07		0.03						5/3/07		0.042																																		7/12/07		0.055

		2/15/07		0.04						1/17/07		0.03						5/4/07		0.045																																		7/13/07		0.05

		2/16/07		0.04						1/18/07		0.03						5/7/07		0.045																																		7/14/07		0.05

		2/16/07		0.04						1/19/07		0.035						5/8/07		0.045																																		7/16/07		0.055

		2/20/07		0.05						1/19/07		0.03						5/9/07		0.045																																		7/17/07		0.05

		2/20/07		0.05						1/20/07		0.03						5/10/07		0.045																																		7/18/07		0.075

		2/21/07		0.04						1/22/07		0.03						5/11/07		0.045																																		7/19/07		0.07

		2/21/07		0.055						1/23/07		0.03						5/14/07		0.046																																		7/20/07		0.07

		2/22/07		0.04						1/24/07		0.03						5/15/07		0.05																																		7/23/07		0.07

		2/22/07		0.05						1/24/07		0.03						5/16/07		0.055																																		7/24/07		0.07

		2/23/07		0.03						1/25/07		0.03						5/17/07		0.045																																		7/25/07		0.065

		2/23/07		0.05						1/25/07		0.03						5/18/07		0.04																																		7/26/07		0.055

		2/26/07		0.05						1/26/07		0.03						5/21/07		0.044																																		7/27/07		0.06

		2/26/07		0.04						1/26/07		0.035						5/22/07		0.045																																		7/28/07		0.065

		2/27/07		0.03						1/29/07		0.035						5/23/07		0.045																																		7/30/07		0.05

		2/27/07		0.04						1/29/07		0.035						5/24/07		0.04																																		7/31/07		0.06

		2/28/07		0.03						1/30/07		0.03						5/24/07		0.04																																		8/1/07		0.06

		2/28/07		0.03						1/30/07		0.03						5/29/07		0.025																																		8/2/07		0.06

		3/1/07		0.04						1/31/07		0.03						5/30/07		0.045																																		8/3/07		0.06

		3/2/07		0.04						1/31/07		0.035						5/31/07		0.05																																		8/6/07		0.06

		3/5/07		0.04						2/1/07		0.035						6/1/07		0.051																																		8/7/07		0.06

		3/6/07		0.04						2/1/07		0.03						6/4/07		0.044																																		8/8/07		0.05

		3/7/07		0.04						2/2/07		0.03						6/5/07		0.047																																		8/9/07		0.05

		3/8/07		0.04						2/2/07		0.03						6/6/07		0.046																																		8/10/07		0.05

		3/9/07		0.04						2/3/07		0.03						6/7/07		0.05																																		8/11/07		0.05

		3/12/07		0.04						2/3/07		0.03						6/8/07		0.048																																		8/13/07		0.06

		3/13/07		0.03						2/5/07		0.03						6/9/07		0.049																																		8/14/07		0.05

		3/14/07		0.03						2/5/07		0.03						6/11/07		0.049																																		8/15/07		0.05

		3/15/07		0.04						2/6/07		0.03						6/12/07		0.05																																		8/16/07		0.055

		3/16/07		0.04						2/6/07		0.035						6/13/07		0.045																																		8/17/07		0.055

		3/19/07		0.03						2/7/07		0.03						6/14/07		0.048																																		8/20/07		0.05

		3/20/07		0.04						2/7/07		0.03						6/15/07		0.045																																		8/21/07		0.05

		3/21/07		0.035						2/8/07		0.03						6/18/07		0.045																																		8/22/07		0.05

		3/22/07		0.04						2/8/07		0.03						6/19/07		0.045																																		8/23/07		0.05

		3/23/07		0.04						2/10/07		0.03						6/20/07		0.045																																		8/24/07		0.05

		3/26/07		0.035						2/10/07		0.04						6/21/07		0.045																																		8/27/07		0.05

		3/27/07		0.04						2/12/07		0.03						6/25/07		0.042																																		8/28/07		0.05

		3/28/07		0.035						2/13/07		0.035						6/26/07		0.045																																		8/29/07		0.05

		3/29/07		0.035						2/13/07		0.05						6/27/07		0.04																																		8/30/07		0.05

		3/30/07		0.03						2/14/07		0.04						6/28/07		0.063																																		8/31/07		0.05

		3/31/07		0.035						2/14/07		0.04						6/29/07		0.061																																		9/4/07		0.05

		4/2/07		0.04						2/15/07		0.05						7/2/07		0.06																																		9/5/07		0.05

		4/3/07		0.035						2/15/07		0.04						7/3/07		0.062																																		9/6/07		0.05

		4/4/07		0.035						2/16/07		0.04						7/5/07		0.06																																		9/7/07		0.055

		4/5/07		0.035						2/16/07		0.04						7/6/07		0.058																																		9/10/07		0.045

		4/6/07		0.035						2/20/07		0.05						7/9/07		0.06																																		9/11/07		0.05

		4/9/07		0.035						2/20/07		0.05						7/10/07		0.06																																		9/12/07		0.05

		4/10/07		0.03						2/21/07		0.04						7/11/07		0.055																																		9/13/07		0.045

		4/11/07		0.03						2/21/07		0.035						7/12/07		0.056																																		9/14/07		0.05

		4/12/07		0.03						2/22/07		0.04						7/13/07		0.056																																		9/17/07		0.05

		4/13/07		0.03						2/22/07		0.04						7/16/07		0.055																																		9/18/07		0.045

		4/14/07		0.03						2/23/07		0.03						7/17/07		0.05																																		9/19/07		0.05

		4/16/07		0.03						2/23/07		0.04						7/18/07		0.045																																		9/20/07		0.05

		4/17/07		0.03						2/26/07		0.03						7/19/07		0.045																																		9/21/07		0.05

		4/18/07		0.025						2/26/07		0.035						7/20/07		0.04																																		9/22/07		0.05

		4/19/07		0.03						2/27/07		0.03						7/23/07		0.04																																		9/24/07		0.05

		4/20/07		0.035						2/27/07		0.03						7/24/07		0.04																																		9/25/07		0.05

		4/21/07		0.035						2/28/07		0.03						7/25/07		0.04																																		9/26/07		0.05

		4/23/07		0.025						3/1/07		0.03						7/26/07		0.04																																		9/27/07		0.05

		4/24/07		0.02						3/2/07		0.03						7/28/07		0.04																																		9/28/07		0.05

		4/25/07		0.03						3/5/07		0.03						7/30/07		0.044																																		10/1/07		0.05

		4/26/07		0.04						3/6/07		0.03						7/31/07		0.044																																		10/2/07		0.06

		4/27/07		0.025						3/7/07		0.04						8/1/07		0.04																																		10/3/07		0.05

		4/30/07		0.025						3/8/07		0.04						8/2/07		0.04																																		10/4/07		0.05

		5/1/07		0.03						3/9/07		0.04						8/3/07		0.04																																		10/5/07		0.045

		5/2/07		0.02						3/12/07		0.04						8/4/07		0.042																																		10/8/07		0.05

		5/3/07		0.02						3/13/07		0.04						8/6/07		0.04																																		10/9/07		0.05

		5/4/07		0.02						3/14/07		0.03						8/7/07		0.04																																		10/10/07		0.05

		5/5/07		0.02						3/15/07		0.035						8/8/07		0.034																																		10/11/07		0.05

		5/7/07		0.02						3/16/07		0.035						8/9/07		0.032																																		10/12/07		0.05

		5/8/07		0.025						3/19/07		0.035						8/10/07		0.043																																		10/15/07		0.05

		5/9/07		0.03						3/20/07		0.04						8/13/07		0.045																																		10/16/07		0.045

		5/10/07		0.025						3/21/07		0.04						8/14/07		0.045																																		10/17/07		0.05

		5/11/07		0.005						3/22/07		0.04						8/15/07		0.043																																		10/18/07		0.05

		5/14/07		0.035						3/23/07		0.035						8/16/07		0.04																																		10/19/07		0.045

		5/15/07		0.035						3/26/07		0.035						8/17/07		0.04																																		10/22/07		0.05

		5/16/07		0.03						3/27/07		0.04						8/20/07		0.04																																		10/23/07		0.05

		5/17/07		0.03						3/28/07		0.04						8/21/07		0.03																																		10/24/07		0.045

		5/18/07		0.03						3/29/07		0.035						8/22/07		0.04																																		10/25/07		0.045

		5/19/07		0.03						3/30/07		0.03						8/23/07		0.04																																		10/26/07		0.05

		5/21/07		0.025						3/31/07		0.035						8/24/07		0.04																																		10/29/07		0.05

		5/22/07		0.025						4/2/07		0.035						8/27/07		0.045																																		10/30/07		0.045

		5/23/07		0.025						4/3/07		0.035						8/28/07		0.04																																		10/31/07		0.05

		5/24/07		0.02						4/4/07		0.04						8/29/07		0.055																																		11/1/07		0.045

		5/25/07		0.025						4/5/07		0.04						8/30/07		0.055																																		11/2/07		0.05

		5/29/07		0.025						4/6/07		0.04						8/31/07		0.05																																		11/5/07		0.05

		5/30/07		0.048						4/9/07		0.035						9/4/07		0.05																																		11/6/07		0.045

		5/31/07		0.04						4/10/07		0.035						9/5/07		0.04						0.61		0.4																										11/7/07		0.05

		6/1/07		0.025						4/11/07		0.04						9/6/07		0.05						0.61		0.41																										11/8/07		0.05

		6/2/07		0.03						4/12/07		0.035						9/7/07		0.045						0.6		0.41																										11/9/07		0.05

		6/4/07		0.03						4/13/07		0.035						9/8/07		0.04						0.6		0.41																										11/12/07		0.045

		6/5/07		0.0175						4/14/07		0.03						9/10/07		0.055						0.61		0.41																										11/13/07		0.05

		6/6/07		0.03						4/16/07		0.035						9/11/07		0.05						0.61		0.41																										11/14/07		0.045

		6/7/07		0.04						4/17/07		0.035						9/12/07		0.05						0.61		0.41																										11/15/07		0.045

		6/8/07		0.025						4/18/07		0.04						9/13/07		0.05						0.61		0.41																										11/16/07		0.045

		6/9/07		0.02						4/19/07		0.035						9/14/07		0.05						0.6		0.42																										11/19/07		0.045

		6/11/07		0.04						4/20/07		0.04						9/15/07		0.05						0.6		0.4																										11/20/07		0.045

		6/12/07		0.02						4/21/07		0.035						9/17/07		0.054						0.6		0.41																										11/21/07		0.045

		6/13/07		0.03						4/23/07		0.035						9/18/07		0.054						0.61		0.41																										11/26/07		0.045

		6/14/07		0.025						4/24/07		0.02						9/19/07		0.045						0.65		0.4																										11/27/07		0.045

		6/15/07		0.02						4/25/07		0.04						9/20/07		0.045						0.61		0.41																										11/28/07		0.045

		6/18/07		0.025						4/26/07		0.035						9/21/07		0.04						0.6		0.4																										11/29/07		0.045

		6/19/07		0.02						4/27/07		0.04						9/24/07		0.035						0.6		0.4																										11/30/07		0.045

		6/20/07		0.03						4/30/07		0.025						9/25/07		0.04						0.62		0.4																										12/1/07		0.045

		6/21/07		0.016						5/1/07		0.03						9/26/07		0.04						0.62		0.42																										12/3/07		0.045

		6/22/07		0.025						5/2/07		0.03						9/27/07		0.04						0.62		0.42																										12/4/07		0.045

		6/25/07		0.02						5/3/07		0.03						9/28/07		0.05						0.6		0.4																										12/5/07		0.045

		6/26/07		0.025						5/4/07		0.035						10/1/07		0.04						0.62		0.42																										12/6/07		0.045

		6/27/07		0.03						5/5/07		0.035						10/2/07		0.045						0.62		0.42																										12/7/07		0.045

		6/28/07		0.045						5/7/07		0.04						10/3/07		0.045						0.62		0.42																										12/8/07		0.045

		6/29/07		0.025						5/8/07		0.045						10/4/07		0.05						0.61		0.42																										12/10/07		0.045

		7/2/07		0.04						5/9/07		0.03						10/5/07		0.05						0.62		0.42																										12/11/07		0.04

		7/3/07		0.04						5/10/07		0.04						10/8/07		0.05						0.62		0.42																										12/12/07		0.04

		7/5/07		0.04						5/11/07		0.03						10/9/07		0.04						0.62		0.42																										12/13/07		0.04

		7/6/07		0.04						5/14/07		0.03						10/10/07		0.04						0.62		0.42																										12/14/07		0.04

		7/9/07		0.04						5/15/07		0.03						10/11/07		0.05						0.62		0.42																										12/17/07		0.04

		7/10/07		0.03						5/16/07		0.03						10/12/07		0.045						0.62		0.42																										12/18/07		0.045

		7/11/07		0.035						5/17/07		0.03						10/13/07		0.04						0.62		0.42																										12/19/07		0.04

		7/12/07		0.035						5/18/07		0.03						10/15/07		0.04						0.61		0.41																										12/20/07		0.04

		7/13/07		0.03						5/19/07		0.03						10/16/07		0.04						0.62		0.42																										12/26/07		0.04

		7/16/07		0.03						5/21/07		0.03						10/17/07		0.04						0.61		0.41																										12/27/07		0.04

		7/17/07		0.035						5/22/07		0.03						10/18/07		0.04						0.62		0.42																										12/28/07		0.04

		7/18/07		0.03						5/23/07		0.03						10/19/07		0.04						0.62		0.42																										12/31/07		0.05

		7/19/07		0.03						5/24/07		0.03						10/22/07		0.045						0.62		0.42																										1/2/08		0.04

		7/20/07		0.03						5/25/07		0.03						10/23/07		0.05						0.64		0.44																										1/3/08		0.04

		7/23/07		0.04						5/29/07		0.035						10/24/07		0.045						0.62		0.42																										1/4/08		0.04

		7/24/07		0.035						5/30/07		0.02						10/25/07		0.03						0.62		0.42																										1/7/08		0.04

		7/25/07		0.035						5/31/07		0.03						10/26/07		0.035						0.62		0.42																										1/8/08		0.04

		7/26/07		0.04						6/1/07		0.03						10/29/07		0.03						0.62		0.42																										1/9/08		0.04

		7/27/07		0.04						6/2/07		0.03						10/30/07		0.025						0.62		0.42																										1/10/08		0.04

		7/30/07		0.035						6/4/07		0.03						10/31/07		0.03						0.62		0.42																										1/11/08		0.04

		7/31/07		0.035						6/5/07		0.04						11/1/07		0.035						0.62		0.42																										1/14/08		0.04

		8/1/07		0.03						6/6/07		0.025						11/2/07		0.035						0.62		0.42																										1/15/08		0.04

		8/2/07		0.035						6/7/07		0.03						11/5/07		0.025						0.62		0.4																										1/16/08		0.04

		8/3/07		0.04						6/8/07		0.03						11/6/07		0.04						0.62		0.41																										1/17/08		0.04

		8/4/07		0.03						6/9/07		0.025						11/7/07		0.02						0.62		0.42																										1/18/08		0.04

		8/6/07		0.03						6/11/07		0.03						11/8/07		0.03						0.62		0.42																										1/21/08		0.04

		8/7/07		0.035						6/12/07		0.02						11/9/07		0.02						0.62		0.42																										1/22/08		0.04

		8/8/07		0.03						6/13/07		0.03						11/12/07		0.035						0.62		0.42																										1/23/08		0.04

		8/9/07		0.03						6/14/07		0.025						11/13/07		0.04						0.62		0.4																										1/24/08		0.04

		8/10/07		0.04						6/15/07		0.025						11/14/07		0.04						0.62		0.42																										1/25/08		0.045

		8/13/07		0.03						6/18/07		0.03						11/15/07		0.04						0.62		0.42																										1/28/08		0.04

		8/14/07		0.03						6/19/07		0.025						11/16/07		0.035						0.62		0.42																										1/29/08		0.04

		8/15/07		0.03						6/20/07		0.03						11/19/07		0.045						0.66		0.44																										1/30/08		0.04

		8/17/07		0.03						6/21/07		0.03						11/20/07		0.04						0.64		0.42																										1/31/08		0.04

		8/20/07		0.03						6/22/07		0.02						11/21/07		0.04						0.64		0.42																										2/1/08		0.04

		8/21/07		0.03						6/25/07		0.02						11/26/07		0.04						0.66		0.44																										2/4/08		0.04

		8/22/07		0.03						6/26/07		0.02						11/27/07		0.042						0.66		0.44																										2/5/08		0.04

		8/23/07		0.03						6/27/07		0.03						11/28/07		0.04						0.66		0.44																										2/6/08		0.04

		8/24/07		0.03						6/28/07		0.03						11/29/07		0.03						0.64		0.44																										2/7/08		0.04

		8/25/07		0.02						6/29/07		0.04						11/30/07		0.03						0.64		0.44																										2/8/08		0.04

		8/27/07		0.04						7/2/07		0.03						12/3/07		0.04						0.64		0.44																										2/11/08		0.04

		8/28/07		0.035						7/3/07		0.025						12/4/07		0.03						0.64		0.42																										2/12/08		0.04

		8/29/07		0.04						7/5/07		0.03						12/5/07		0.03						0.64		0.44																										2/13/08		0.04

		8/30/07		0.03						7/6/07		0.025						12/6/07		0.03						0.64		0.42																										2/14/08		0.04

		8/31/07		0.03						7/9/07		0.025						12/7/07		0.03						0.64		0.44																										2/15/08		0.04

		9/4/07		0.03						7/10/07		0.03						12/10/07		0.03						0.64		0.44																										2/16/08		0.04

		9/5/07		0.03						7/11/07		0.035						12/11/07		0.03						0.66		0.42																										2/19/08		0.04

		9/6/07		0.035						7/12/07		0.035						12/12/07		0.03						0.6		0.42																										2/20/08		0.045

		9/7/07		0.02						7/13/07		0.03						12/13/07		0.045						0.66		0.42																										2/21/08		0.04

		9/8/07		0.04						7/16/07		0.03						12/14/07		0.03						0.66		0.42																										2/22/08		0.04

		9/10/07		0.025						7/17/07		0.03						12/17/07		0.03						0.64		0.42																										2/25/08		0.04

		9/11/07		0.035						7/18/07		0.025						12/18/07		0.03						0.66		0.4																										2/26/08		0.04

		9/12/07		0.035						7/19/07		0.025						12/19/07		0.02						0.66		0.42																										2/27/08		0.04

		9/13/07		0.03						7/20/07		0.035						12/20/07		0.03						0.64		0.42																										2/28/08		0.04

		9/14/07		0.03						7/23/07		0.03						12/21/07		0.04						0.66		0.42																										2/29/08		0.04

		9/17/07		0.03						7/24/07		0.025						12/26/07		0.03						0.64		0.42																										3/1/08		0.04

		9/18/07		0.025						7/25/07		0.035						12/27/07		0.025						0.62		0.44																										3/2/08		0.04

		9/19/07		0.04						7/26/07		0.03						12/28/07		0.025						0.64		0.44																										3/3/08		0.04

		9/20/07		0.04						7/27/07		0.03						12/31/07		0.02						0.64		0.44																										3/4/08		0.04

		9/21/07		0.03						7/30/07		0.035																																										3/5/08		0.04

		9/24/07		0.025						7/31/07		0.04						2/14/08		0.04						0.292		0.309		0.485		61		1180																				3/6/08		0.04

		9/25/07		0.035						8/1/07		0.03						2/15/08		0.037		69		50		0.28		0.31		0.414		61		1172																				3/7/08		0.04

		9/26/07		0.025						8/2/07		0.035						2/19/08		0.035		69		48		0.293		0.309		0.426		60		1184																				3/8/08		0.04

		9/27/07		0.02						8/3/07		0.03						2/20/08		0.03		70		46		0.26		0.309		0.41		63		1184																				3/10/08		0.04

		9/28/07		0.02						8/4/07		0.03						2/21/08		0.032		70		46		0.29		0.305		0.441		62		1164																				3/11/08		0.04

		9/29/07		0.02						8/6/07		0.03						2/22/08		0.031		70		45		0.281		0.307		0.419		62		1184																				3/12/08		0.04

		10/1/07		0.015						8/7/07		0.025						2/25/08		0.069		70		46		0.288		0.311		0.421		63		1184																				3/13/08		0.04

		10/2/07		0.035						8/8/07		0.03						2/26/08		0.068		70		44		0.281		0.312		0.413		64		1192																				3/14/08		0.04

		10/3/07		0.03						8/9/07		0.045						2/27/08		0.067		70		45		0.288		0.311		0.413		62		1184																				3/15/08		0.04

		10/4/07		0.04						8/10/07		0.04						2/28/08		0.063		70		46		0.283		0.31		0.457		62		1172																				3/17/08		0.04

		10/5/07		0.025						8/13/07		0.04						2/29/08		0.064		70		45		0.256		0.311		0.409		63		1184																				3/18/08		0.04

		10/8/07		0.03						8/14/07		0.04						3/3/08		0.07		70		33		0.285		0.311		0.435		63		1204																				3/19/08		0.04

		10/9/07		0.03						8/15/07		0.04						3/4/08		0.07		70		44		0.261		0.311		0.438		63		1184																				3/20/08		0.04

		10/10/07		0.03						8/17/07		0.04						3/5/08		0.069		70		44		0.291		0.311		0.445		63		1184																				3/21/08		0.04

		10/11/07		0.03						8/20/07		0.03						3/6/08		0.068		70		44		0.281		0.311		0.458		61		1184																				3/22/08		0.04

		10/12/07		0.02						8/21/07		0.03						3/7/08		0.067		70		44		0.282		0.322		0.455		63		1192																				3/24/08		0.04

		10/15/07		0.03						8/22/07		0.035						3/10/08		0.069		70		46		0.264		0.321		0.428		64		1184																				3/25/08		0.04

		10/16/07		0.02						8/23/07		0.03						3/11/08		0.071		70		43		0.285		0.322		0.438		63		1204																				3/26/08		0.045

		10/17/07		0.04						8/24/07		0.035						3/12/08		0.056		70		44		0.261		0.312		0.422		62		1188																				3/27/08		0.04		70		25

		10/18/07		0.04						8/25/07		0.02						3/14/08		0.067		70		43		0.261		0.321		0.451		63		1184																				3/28/08		0.04		70		41

		10/19/07		0.025						8/27/07		0.025						3/17/08		0.069		70		45		0.26		0.32		0.439		63		1196																				3/31/08		0.04		70		28

		10/22/07		0.03						8/28/07		0.025						3/18/08		0.062		70		47		0.279		0.32		0.422		63		1196																				4/1/08		0.04		70		29

		10/23/07		0.03						8/29/07		0.03						3/19/08		0.053		70		44		0.273		0.321		0.419		64		1192																				4/2/08		0.055		70		36

		10/24/07		0.04						8/30/07		0.03						3/20/08		0.064		70		33		0.262		0.321		0.431		64		1192																				4/3/08		0.04		69		40

		10/25/07		0.035						8/31/07		0.03						3/21/08		0.063		70		35		0.277		0.322		0.439		63		1196																				4/4/08		0.045		70		44

		10/26/07		0.045						9/4/07		0.03						3/24/08		0.052		70		42		0.238		0.321		0.418		63		1184																				4/5/08		0.04		70		41

		10/29/07		0.02						9/5/07		0.03						3/25/08		0.057		70		38		0.264		0.319		0.445		63		1192																				4/7/08		0.05		70		44

		10/30/07		0.02						9/6/07		0.03						3/26/08		0.056		70		35		0.276		0.321		0.447		63		1204																				4/8/08		0.05		70		44

		10/31/07		0.02						9/7/07		0.03						3/27/08		0.07		70		24		0.28		0.32		0.46		63		1204																				4/9/08		0.05		70		44

		11/1/07		0.03						9/8/07		0.03						3/28/08		0.05		70		40		0.26		0.32		0.44		63		1192																				4/10/08		0.05		70		44

		11/2/07		0.025						9/10/07		0.02						3/31/08		0.06		70		27		0.3		0.32		0.48		63		1204																				4/11/08		0.05		70		46

		11/5/07		0.03						9/11/07		0.02						4/1/08		0.06		70		28		0.28		0.32		0.46		61		1192																				4/14/08		0.05		72		41

		11/6/07		0.025						9/12/07		0.03						4/2/08		0.06		70		30		0.28		0.32		0.44		63		1204																				4/15/08		0.05		74		42

		11/7/07		0.025						9/13/07		0.02						4/3/08		0.06		70		38		0.28		0.32		0.44		64		1192																				4/16/08		0.05		70		45

		11/8/07		0.085						9/14/07		0.035						4/4/08		0.05		70		44		0.26		0.32		0.44		63		1196																				4/17/08		0.045		72		46

		11/9/07		0.08						9/17/07		0.03						4/5/08		0.05		70		40		0.26		0.32		0.44		63		1196																				4/18/08		0.04		70		48

		11/12/07		0.075						9/18/07		0.03						4/7/08		0.055		70		44		0.26		0.32		0.46		65		1204																				4/19/08		0.05		69		48

		11/13/07		0.08						9/19/07		0.04						4/8/08		0.055		70		44		0.28		0.32		0.44		61		1192																				4/21/08		0.05		73		47

		11/14/07		0.075						9/20/07		0.04						4/9/08		0.055		70		46		0.28		0.32		0.44		63		1196																				4/22/08		0.045		77		46

		11/15/07		0.075						9/21/07		0.03						4/10/08		0.05		70		45		0.28		0.32		0.44		61		1204																				4/23/08		0.05		71		45

		11/16/07		0.07						9/24/07		0.025						4/11/08		0.05		70		42		0.28		0.32		0.44		61		1192																				4/24/08		0.045		73		46

		11/19/07		0.075						9/25/07		0.025						4/14/08		0.05		70		43		0.28		0.32		0.46		61		1196																				4/25/08		0.04		70		46

		11/20/07		0.07						9/26/07		0.03						4/15/08		0.05		73		41		0.28		0.32		0.44		62		1196																				4/30/08		0.06		69		26

		11/21/07		0.075						9/27/07		0.03						4/16/08		0.05		72		43		0.28		0.32		0.48		62		1196																				5/1/08		0.04		75		42

		11/26/07		0.08						9/28/07		0.03						4/17/08		0.05		72		44		0.28		0.32		0.48		62		1196																				5/2/08		0.04		72		35

		11/27/07		0.08						9/29/07		0.025						4/18/08		0.05		72		45		0.28		0.32		0.48		62		1196																				5/3/08		0.04		78		34

		11/28/07		0.08						10/1/07		0.03						4/19/08		0.06		72		44		0.28		0.32		0.48		62		1196																				5/5/08		0.04		71		40

		11/29/07		0.075						10/2/07		0.025						4/21/08		0.055		71		45		0.28		0.32		0.46		64		1196																				5/6/08		0.045		75		40

		11/30/07		0.08						10/3/07		0.03						4/22/08		0.05		72		43		0.28		0.32		0.46		64		1196																				5/7/08		0.05		72		36

		12/3/07		0.07						10/4/07		0.03						4/23/08		0.05		73		42		0.28		0.32		0.48		63		1196																				5/8/08		0.045		72		38

		12/4/07		0.08						10/5/07		0.02						4/24/08		0.055		73		45		0.28		0.32		0.46		63		1196																				5/9/08		0.04		74		34

		12/5/07		0.07						10/8/07		0.03						4/25/08		0.05		73		41		0.26		0.32		0.44		63		1204																				5/10/08		0.045		72		34

		12/6/07		0.08						10/9/07		0.02						4/28/08								0.26		0.32		0.44		63		1204																				5/12/08		0.055		69		28

		12/7/07		0.075						10/10/07		0.025						4/29/08								0.28		0.32		0.44		60		1184																				5/13/08		0.04		75		31

		12/10/07		0.075						10/11/07		0.03						4/30/08		0.06		70		25		0.28		0.32		0.46		60		1192																				5/14/08		0.05		71		38

		12/11/07		0.075						10/12/07		0.02						5/1/08		0.055		73		39		0.28		0.32		0.46		60		1196																				5/15/08		0.04		72		42

		12/12/07		0.075						10/15/07		0.025						5/2/08		0.045		72		34		0.28		0.32		0.46		60		1210																				5/16/08		0.04		71		48

		12/13/07		0.075						10/16/07		0.025						5/3/08		0.05		73		38		0.28		0.32		0.46		60		1210																				5/19/08		0.04		75		42

		12/14/07		0.075						10/17/07		0.03						5/5/08		0.04		72		38		0.28		0.32		0.44		60		1192																				5/20/08		0.04		73		44

		12/17/07		0.08						10/18/07		0.025						5/6/08		0.04		73		42		0.28		0.32		0.44		60		1184																				5/21/08		0.04		71		36

		12/18/07		0.075						10/19/07		0.025						5/7/08		0.04		73		37		0.28		0.32		0.44		62		1196																				5/22/08		0.04		73		30

		12/19/07		0.08						10/22/07		0.025						5/8/08		0.04		73		35		0.28		0.32		0.44		60		1196																				5/23/08		0.04		71		36

		12/20/07		0.08						10/23/07		0.02						5/9/08		0.04		72		34		0.3		0.32		0.46		62		1204																				5/27/08		0.02		73		37

		12/21/07		0.08						10/24/07		0.035						5/10/08		0.04		72		32		0.3		0.32		0.46		62		1204																				5/28/08		0.03		71		39

		12/26/07		0.08						10/25/07		0.025						5/12/08		0.055		68		28		0.26		0.32		0.42		60		1196																				5/29/08		0.03		74		39

		12/27/07		0.08						10/26/07		0.035						5/13/08		0.04		73		31		0.26		0.32		0.46		61		1192																				5/30/08		0.04		72		38

		12/28/07		0.075						10/29/07		0.025						5/14/08		0.045		73		25		0.3		0.32		0.46		60		1184																				5/31/08		0.025		72		39

		12/31/07		0.08						10/30/07		0.03						5/15/08		0.035		73		39		0.3		0.32		0.46		60		1196																				6/2/08		0.025		74		27

		1/2/08		0.09						10/31/07		0.03						5/16/08		0.035		73		45		0.3		0.32		0.44		60		1184																				6/3/08		0.02		71		34

		1/3/08		0.075						11/1/07		0.04						5/19/08		0.045		72		41		0.28		0.32		0.44		60		1204																				6/4/08		0.025		69		33

		1/4/08		0.09						11/2/07		0.03						5/20/08		0.045		73		42		0.28		0.32		0.44		62		1196																				6/5/08		0.025		71		39

		1/7/08		0.125						11/5/07		0.025						5/21/08		0.045		70		35		0.28		0.32		0.46		60		1196																				6/6/08		0.025		71		32

		1/8/08		0.08						11/6/07		0.03						5/22/08		0.045		72		30		0.28		0.32		0.42		61		1176																				6/9/08		0.03		72		43

		1/9/08		0.08						11/7/07		0.035						5/23/08		0.045		73		34		0.28		0.32		0.46		61		1172																				6/10/08		0.03		73		33

		1/10/08		0.08						11/8/07		0.05						5/27/08		0.035		73		36		0.28		0.32		0.44		61		1196																				6/11/08		0.025		70		33

		1/11/08		0.08						11/9/07		0.05						5/28/08		0.04		72		37		0.28		0.32		0.44		61		1204																				6/12/08		0.025		71		35

		1/14/08		0.09						11/12/07		0.03						5/29/08		0.04		73		37		0.26		0.32		0.44		61		1200																				6/13/08		0.025		75		32

		1/15/08		0.085						11/13/07		0.05						5/30/08		0.04		72		37		0.28		0.32		0.48		61		1196																				6/16/08		0.025		72		37

		1/16/08		0.09						11/14/07		0.05						6/2/08		0.04		71		30		0.28		0.28		0.44		60		1200																				6/17/08		0.03		72		26

		1/17/08		0.08						11/15/07		0.05						6/3/08		0.035		72		35		0.28		0.32		0.42		61		1196																				6/18/08		0.025		73		33

		1/18/08		0.09						11/16/07		0.05						6/4/08		0.035		70		33		0.28		0.32		0.44		61		1188																				6/19/08		0.025		71		29

		1/21/08		0.04						11/19/07		0.05						6/5/08		0.035		71		37		0.3		0.32		0.44		61		1192																				6/20/08		0.02		73		33

		1/22/08		0.11						11/20/07		0.05						6/6/08		0.035		71		31		0.28		0.32		0.44		61		1188																				6/21/08		0.025		74		27

		1/23/08		0.09						11/21/07		0.05						6/9/08		0.04		72		40		0.32		0.32		0.48		61		1188																				6/23/08		0.02		72		37

		1/24/08		0.09						11/26/07		0.05						6/10/08		0.04		72		31		0.3		0.32		0.44		55		1172																				6/24/08		0.025		73		35

		1/25/08		0.095						11/27/07		0.05						6/11/08		0.04		70		34		0.3		0.32		0.48		55		1196																				6/25/08		0.03		72		36

		1/28/08		0.09						11/28/07		0.05						6/12/08		0.04		72		31		0.3		0.32		0.48		55		1196																				6/26/08		0.03		74		35

		1/29/08		0.09						11/29/07		0.045						6/13/08		0.05		71		36		0.26		0.32		0.44		55		1208																				6/27/08		0.02		71		39

		1/30/08		0.1						11/30/07		0.05						6/16/08		0.05		73		34		0.3		0.32		0.46		55		1204																				6/30/08		0.02		73		38

		1/31/08		0.105						12/3/07		0.05						6/17/08		0.05		73		24		0.28		0.32		0.44		55		1216																				7/1/08		0.055		73		39

		2/1/08		0.09						12/4/07		0.05						6/18/08		0.05		73		31		0.3		0.32		0.44		55		1196																				7/2/08		0.055		73		38

		2/4/08		0.03						12/5/07		0.045						6/19/08		0.05		71		30		0.28		0.32		0.46		55		1196																				7/3/08		0.065		71		39

		2/5/08		0.04						12/6/07		0.05						6/20/08		0.05		73		28		0.28		0.32		0.46		55		1196																				7/7/08		0.055		75		38

		2/6/08		0.025						12/7/07		0.045						6/21/08		0.045		72		30		0.26		0.32		0.46		55		32																				7/8/08		0.05		72		40

		2/7/08		0.02						12/10/07		0.05						6/23/08		0.05		73		39		0.28		0.32		0.44		57		32																				7/9/08		0.06		73		39

		2/8/08		0.04						12/11/07		0.045						6/24/08		0.05		72		34		0.28		0.32		0.42		60		32																				7/10/08		0.06		74		39

		2/9/08		0.05						12/12/07		0.045						6/25/08		0.04		73		36		0.28		0.32		0.44		60		32																				7/11/08		0.06		71		40

		2/11/08		0.02						12/13/07		0.045						6/26/08		0.04		72		34		0.28		0.32		0.44		60		32																				7/12/08		0.06		73		42

		2/12/08		0.035						12/14/07		0.045						6/27/08		0.04		71		38		0.32		0.32		0.44		60		32																				7/14/08		0.06		72		41

		2/13/08		0.025						12/17/07		0.045						6/30/08		0.04		73		37		0.3		0.32		0.44		60		32																				7/15/08		0.06		71		41

		2/14/08		0.025						12/18/07		0.04						7/1/08		0.035		71		38		0.28		0.32		0.44		60		32																				7/16/08		0.065		72		40

		2/15/08		0.03						12/19/07		0.04						7/2/08		0.07		72		38		0.3		0.32		0.46		60		32																				7/17/08		0.05		71		41

		2/19/08		0.03						12/20/07		0.03						7/3/08		0.08		72		38		0.32		0.32		0.48		57		32																				7/18/08		0.065		72		40

		2/20/08		0.05						12/21/07		0.04						7/7/08		0.06		73		40		0.28		0.32		0.44		57		32																				7/19/08		0.06		72		39

		2/21/08		0.03						12/26/07		0.04						7/8/08		0.06		72		38		0.28		0.32		0.42		60		32																				7/21/08		0.06		71		40

		2/22/08		0.03						12/27/07		0.04						7/9/08		0.06		73		39		0.28		0.32		0.42																								7/22/08		0.05		74		36

		2/23/08		0.035						12/28/07		0.04						7/10/08		0.07		72		40		0.32		0.32		0.48		55		1104																				7/23/08		0.07		72		39

		2/24/08		0.035						12/31/07		0.04						7/11/08		0.065		71		39		0.3		0.32		0.48		55		1104																				7/24/08		0.05		72		37

		2/25/08		0.03						1/2/08		0.04						7/12/08		0.08		73		40																														7/25/08		0.06		71		38

		2/26/08		0.035						1/3/08		0.04						7/14/08		0.08		72		40		0.3		0.32		0.48		61		1200																				7/26/08		0.07		71		38

		2/27/08		0.03						1/4/08		0.04						7/15/08		0.09		71		40		0.28		0.32		0.42		61		1200																				7/28/08		0.06		70		41

		2/28/08		0.03						1/7/08		0.025						7/16/08		0.09		72		39		0.28		0.32		0.42		61		1200																				7/29/08		0.06		70		41

		2/29/08		0.03						1/8/08		0.03						7/17/08		0.08		72		39		0.28		0.32		0.44		61		1200																				7/30/08		0.06		71		39

		3/1/08		0.035						1/9/08		0.03						7/18/08		0.09		72		38		0.3		0.32		0.48		61		1200																				7/31/08		0.065		71		40

		3/3/08		0.03						1/10/08		0.03						7/19/08		0.09		73		37																														8/1/08		0.06		73		36

		3/4/08		0.035						1/11/08		0.03						7/21/08		0.09		72		38		0.28		0.32		0.4		61		1200																				8/2/08		0.06		71		40

		3/5/08		0.043						1/14/08		0.025						7/22/08		0.08		73		37		0.24		0.32		0.42		61		1200																				8/4/08		0.06		72		40

		3/6/08		0.043						1/15/08		0.03						7/23/08		0.09		71		38		0.28		0.32		0.44		61		1200																				8/5/08		0.06		73		39

		3/7/08		0.043						1/16/08		0.03						7/24/08		0.09		72		36		0.26		0.32		0.46		61		1200																				8/6/08		0.06		71		41

		3/10/08		0.043						1/17/08		0.03						7/25/08		0.09		72		36		0.24		0.32		0.42		61		1200																				8/7/08		0.06		72		39

		3/11/08		0.042						1/18/08		0.025						7/26/08		0.09		71		37		0.28		0.32		0.46		61		1200																				8/8/08		0.05		72		40

		3/12/08		0.039						1/21/08		0.035						7/28/08		0.09		71		38		0.3		0.32		0.46		61		1200																				8/9/08		0.055		71		40

		3/13/08		0.03						1/22/08		0.03						7/29/08		0.06		70		40		0.3		0.32		0.44																								8/11/08		0.06		71		39

		3/14/08		0.041						1/23/08		0.035						7/30/08		0.07		71		38		0.3		0.32		0.48																								8/12/08		0.065		71		41

		3/17/08		0.047						1/24/08		0.03						7/31/08		0.075		71		38																														8/13/08		0.055		71		41

		3/18/08		0.048						1/25/08		0.035						8/1/08		0.07		72		37		0.3		0.32		0.48																								8/14/08		0.05		71		41

		3/19/08		0.047						1/28/08		0.035						8/2/08		0.07		72		38																														8/15/08		0.05		72		39

		3/20/08		0.042						1/29/08		0.035						8/4/08		0.07		73		37		0.28		0.32		0.44																								8/16/08		0.06		72		40

		3/21/08		0.043						1/30/08		0.025						8/5/08		0.06		73		37		0.28		0.34		0.48																								8/18/08		0.06		72		41

		3/22/08		0.045						1/31/08		0.03						8/6/08		0.07		71		38		0.28		0.32		0.48																								8/19/08		0.06		72		41

		3/24/08		0.043						2/1/08		0.03						8/7/08		0.06		71		38		0.32		0.32		0.48																								8/20/08		0.06		71		40

		3/25/08		0.045						2/4/08		0.035						8/8/08		0.06		72		38		0.26		0.32		0.44																								8/21/08		0.05		73		44

		3/26/08		0.043						2/5/08		0.025						8/9/08		0.06		71		40																														8/22/08		0.05		72		40

		3/27/08		0.04						2/6/08		0.035						8/11/08		0.07		71		38		0.28		0.32		0.44																								8/23/08		0.05		72		41

		3/28/08		0.04						2/7/08		0.025						8/12/08		0.07		71		40		0.28		0.32		0.44																								8/25/08		0.06		71		40

		3/31/08		0.045						2/8/08		0.02						8/13/08		0.065		71		40		0.28		0.3		0.46																								8/26/08		0.06		70		39

		4/1/08		0.045						2/9/08		0.02						8/14/08		0.05		71		39		0.26		0.32		0.42																								8/27/08		0.05		71		40

		4/2/08		0.045						2/14/08		0.035						8/15/08		0.06		71		38		0.26		0.32		0.42																								8/28/08		0.055		71		40

		4/3/08		0.04						2/15/08		0.033						8/16/08		0.06		71		40																														8/29/08		0.055		72		39

		4/4/08		0.045						2/19/08		0.036						8/18/08		0.065		71		41		0.26		0.32		0.42																								9/2/08		0.055		69		32

		4/5/08		0.045						2/20/08		0.037						8/19/08		0.06		72		40		0.28		0.32		0.44																								9/3/08		0.055		72		39

		4/7/08		0.045						2/21/08		0.037						8/20/08		0.06		71		31		0.26		0.32		0.42																								9/4/08		0.055		70		38

		4/8/08		0.04						2/22/08		0.034						8/21/08		0.05		73		42		0.28		0.32		0.48																								9/5/08		0.06		71		36

		4/9/08		0.04						2/25/08		0.044						8/22/08		0.06		71		38		0.24		0.32		0.44																								9/6/08		0.06		71		39

		4/10/08		0.04						2/26/08		0.043						8/23/08		0.06		72		40																														9/8/08		0.06		74		38

		4/11/08		0.045						2/27/08		0.043						8/25/08		0.06		71		40		0.26		0.32		0.46																								9/9/08		0.06		72		40

		4/14/08		0.045						2/28/08		0.044						8/26/08		0.06		70		38		0.26		0.32		0.44																								9/10/08		0.06		72		40

		4/15/08		0.04						2/29/08		0.046						8/27/08		0.05		71		38		0.26		0.32		0.44																								9/11/08		0.06		71		41

		4/16/08		0.04						3/3/08		0.045						8/28/08		0.05		71		38		0.26		0.3		0.44																								9/12/08		0.06		70		40

		4/17/08		0.04						3/4/08		0.044						8/29/08		0.065		72		38		0.28		0.3		0.44																								9/13/08		0.06		70		41

		4/18/08		0.04						3/5/08		0.039						9/2/08		0.06		69		31		0.24		0.32		0.42																								9/15/08		0.06		70		40

		4/19/08		0.05						3/6/08		0.039						9/3/08		0.06		72		40		0.28		0.32		0.44																								9/16/08		0.06		71		40

		4/21/08		0.05						3/7/08		0.038						9/4/08		0.06		70		37		0.26		0.32		0.44																								9/17/08		0.06		70		30

		4/22/08		0.045						3/10/08		0.037						9/5/08		0.06		70		36		0.26		0.32		0.44																								9/18/08		0.06		71		37

		4/23/08		0.04						3/11/08		0.04						9/6/08		0.06		70		38																														9/19/08		0.06		72		43

		4/24/08		0.04						3/12/08		0.036						9/8/08		0.06		72		41		0.24		0.32		0.42																								9/20/08		0.06		72		42

		4/25/08		0.04						3/14/08		0.039						9/9/08		0.06		71		40		0.24		0.32		0.44																								9/22/08		0.06		71		39

		4/30/08		0.04						3/17/08		0.038						9/10/08		0.06		70		41		0.28		0.32		0.46																								9/23/08		0.065		72		37

		5/1/08		0.04						3/18/08		0.038						9/11/08		0.06		70		41		0.26		0.32		0.42																								9/24/08		0.055		70		33

		5/2/08		0.04						3/19/08		0.037						9/12/08		0.06		70		40		0.28		0.32		0.48																								9/25/08		0.06		72		32

		5/3/08		0.045						3/20/08		0.039						9/13/08		0.06		70		40																														9/26/08		0.06		72		43

		5/5/08		0.04						3/21/08		0.038						9/15/08		0.06		69		41		0.3		0.32		0.44																								9/27/08		0.06		70		37

		5/6/08		0.04						3/24/08		0.038						9/16/08		0.06		69		41		0.24		0.3		0.42																								9/29/08		0.06		71		40

		5/7/08		0.045						3/25/08		0.038						9/17/08		0.07		69		38		0.26		0.32		0.46																								9/30/08		0.06		75		33

		5/8/08		0.04						3/26/08		0.039						9/18/08		0.06		70		38		0.26		0.32		0.42

		5/9/08		0.04						3/27/08		0.045						9/19/08		0.06		73		42		0.26		0.32		0.42

		5/10/08		0.04						3/28/08		0.04						9/20/08		0.05		73		41

		5/12/08		0.04						3/31/08		0.04						9/22/08		0.06		71		38		0.24		0.32		0.44

		5/13/08		0.04						4/1/08		0.04						9/23/08		0.065		71		37		0.26		0.32		0.44

		5/14/08		0.04						4/2/08		0.04						9/24/08		0.055		71		32		0.26		0.32		0.42

		5/15/08		0.04						4/3/08		0.035						9/25/08		0.06		71		32		0.28		0.32		0.48

		5/16/08		0.04						4/4/08		0.04						9/26/08		0.055		73		41		0.24		0.32		0.44

		5/19/08		0.04						4/5/08		0.035						9/27/08		0.06		71		35

		5/20/08		0.04						4/7/08		0.04						9/29/08		0.06		70		40		0.26		0.32		0.44

		5/21/08		0.04						4/8/08		0.04						9/30/08		0.05		71		36		0.24		0.32		0.44

		5/22/08		0.04						4/9/08		0.035						10/1/08								0.24		0.32		0.44

		5/23/08		0.04						4/10/08		0.04						10/2/08								0.24		0.32		0.44

		5/27/08		0.04						4/11/08		0.04

		5/28/08		0.04						4/14/08		0.04

		5/29/08		0.05						4/15/08		0.04

		5/30/08		0.04						4/16/08		0.04

		5/31/08		0.045						4/17/08		0.04

		6/2/08		0.04						4/18/08		0.035

		6/3/08		0.04						4/19/08		0.05

		6/4/08		0.04						4/21/08		0.05

		6/5/08		0.04						4/22/08		0.04

		6/6/08		0.04						4/23/08		0.04

		6/9/08		0.04						4/24/08		0.04

		6/10/08		0.04						4/25/08		0.04

		6/11/08		0.04						4/30/08		0.04

		6/12/08		0.04						5/1/08		0.04

		6/13/08		0.04						5/2/08		0.04

		6/16/08		0.04						5/3/08		0.04

		6/17/08		0.04						5/5/08		0.04

		6/18/08		0.04						5/6/08		0.04

		6/19/08		0.04						5/7/08		0.04

		6/20/08		0.04						5/8/08		0.04

		6/21/08		0.035						5/9/08		0.04

		6/23/08		0.035						5/10/08		0.04

		6/24/08		0.04						5/12/08		0.04

		6/25/08		0.035						5/13/08		0.04

		6/26/08		0.035						5/14/08		0.04

		6/27/08		0.035						5/15/08		0.04

		6/30/08		0.035						5/16/08		0.04

		7/1/08		0.03						5/19/08		0.04

		7/2/08		0.03						5/20/08		0.04

		7/3/08		0.035						5/21/08		0.04

		7/7/08		0.03						5/22/08		0.04

		7/8/08		0.03						5/23/08		0.04

		7/9/08		0.035						5/27/08		0.04

		7/10/08		0.035						5/28/08		0.04

		7/11/08		0.035						5/29/08		0.04

		7/12/08		0.03						5/30/08		0.04

		7/14/08		0.025						6/2/08		0.04

		7/15/08		0.03						6/3/08		0.035

		7/16/08		0.03						6/4/08		0.035

		7/17/08		0.03						6/5/08		0.035

		7/18/08		0.04						6/6/08		0.035

		7/19/08		0.03						6/9/08		0.035

		7/21/08		0.03						6/10/08		0.035

		7/22/08		0.03						6/11/08		0.035

		7/23/08		0.02						6/12/08		0.035

		7/24/08		0.025						6/13/08		0.04

		7/25/08		0.01						6/16/08		0.035

		7/26/08		0.01						6/17/08		0.045

		7/28/08		0.01						6/18/08		0.045

		7/29/08		0.03						6/19/08		0.045

		7/30/08		0.01						6/20/08		0.035

		7/31/08		0.015						6/21/08		0.035

		8/1/08		0.025						6/23/08		0.035

		8/2/08		0.03						6/24/08		0.045

		8/4/08		0.03						6/25/08		0.035

		8/5/08		0.03						6/26/08		0.035

		8/6/08		0.04						6/27/08		0.035

		8/7/08		0.035						6/30/08		0.035

		8/8/08		0.03						7/1/08		0.04

		8/9/08		0.03						7/2/08		0.04

		8/11/08		0.035						7/3/08		0.04

		8/12/08		0.035						7/7/08		0.04

		8/13/08		0.035						7/8/08		0.04

		8/14/08		0.03						7/9/08		0.04

		8/15/08		0.03						7/10/08		0.04

		8/16/08		0.03						7/11/08		0.04

		8/18/08		0.03						7/12/08		0.04

		8/19/08		0.04						7/14/08		0.04

		8/20/08		0.03						7/15/08		0.04

		8/21/08		0.03						7/16/08		0.04

		8/22/08		0.03						7/17/08		0.04

		8/23/08		0.03						7/18/08		0.04

		8/25/08		0.03						7/19/08		0.04

		8/26/08		0.03						7/21/08		0.04

		8/27/08		0.03						7/22/08		0.04

		8/28/08		0.03						7/23/08		0.04

		8/29/08		0.03						7/24/08		0.04

		9/2/08		0.03						7/25/08		0.04

		9/3/08		0.03						7/26/08		0.04

		9/4/08		0.03						7/28/08		0.04

		9/5/08		0.03						7/29/08		0.04

		9/6/08		0.03						7/30/08		0.04

		9/8/08		0.03						7/31/08		0.04

		9/9/08		0.03						8/1/08		0.045

		9/10/08		0.03						8/2/08		0.04

		9/11/08		0.03						8/4/08		0.04

		9/12/08		0.03						8/5/08		0.04

		9/13/08		0.03						8/6/08		0.05

		9/15/08		0.035						8/7/08		0.04

		9/16/08		0.03						8/8/08		0.04

		9/17/08		0.03						8/9/08		0.04

		9/18/08		0.03						8/11/08		0.04

		9/19/08		0.03						8/12/08		0.04

		9/20/08		0.03						8/13/08		0.04

		9/22/08		0.03						8/14/08		0.04

		9/23/08		0.03						8/15/08		0.04

		9/24/08		0.025						8/16/08		0.04

		9/25/08		0.03						8/18/08		0.04

		9/26/08		0.03						8/19/08		0.04

		9/27/08		0.03						8/20/08		0.04

		9/29/08		0.03						8/21/08		0.04

		9/30/08		0.03						8/22/08		0.04

		10/1/08		0.03						8/23/08		0.04

		10/2/08		0.03						8/25/08		0.04

		10/3/08		0.03						8/26/08		0.04

		10/4/08		0.03						8/27/08		0.04

		10/6/08		0.03						8/28/08		0.04

		10/7/08		0.04						8/29/08		0.04

		10/8/08		0.03						9/2/08		0.04

		10/9/08		0.03						9/3/08		0.04

		10/10/08		0.03						9/4/08		0.04

		10/11/08		0.03						9/5/08		0.04

		10/13/08		0.03						9/6/08		0.04

		10/14/08		0.03						9/8/08		0.04

		10/15/08		0.03						9/9/08		0.04

		10/16/08		0.04						9/10/08		0.04

		10/17/08		0.03						9/11/08		0.04

		10/18/08		0.03						9/12/08		0.04

		10/20/08		0.03						9/13/08		0.04

		10/21/08		0.03						9/15/08		0.04

		10/22/08		0.03						9/16/08		0.04

		10/23/08		0.03						9/17/08		0.04

		10/24/08		0.03						9/18/08		0.04

		10/25/08		0.03						9/19/08		0.04

		10/27/08		0.03						9/20/08		0.04

		10/28/08		0.03						9/22/08		0.04

		10/29/08		0.03						9/23/08		0.045

		10/30/08		0.03						9/24/08		0.045

		10/31/08		0.03						9/25/08		0.045

		11/3/08		0.03						9/26/08		0.04

		11/4/08		0.03						9/27/08		0.04

										9/29/08		0.04

										9/30/08		0.04

										10/1/08		0.04

										10/2/08		0.04

										10/3/08		0.04

										10/4/08		0.04

										10/6/08		0.04

										10/7/08		0.05

										10/8/08		0.045

										10/9/08		0.04

										10/10/08		0.04

										10/11/08		0.04

										10/13/08		0.045

										10/14/08		0.04

										10/15/08		0.045

										10/16/08		0.04

										10/17/08		0.04

										10/18/08		0.04

										10/20/08		0.04

										10/21/08		0.04

										10/22/08		0.04

										10/23/08		0.04

										10/24/08		0.04

										10/25/08		0.04

										10/27/08		0.04

										10/28/08		0.04

										10/29/08		0.04

										10/30/08		0.04

										10/31/08		0.04

										11/3/08		0.04

										11/4/08		0.04

										11/5/08		0.05

										11/6/08		0.04

										11/7/08		0.04

										11/8/08		0.045

										11/10/08		0.04

										11/11/08		0.04

										11/12/08		0.04

										11/13/08		0.04

										11/14/08		0.04

										11/15/08		0.04

										11/17/08		0.04

										11/18/08		0.04

										11/19/08		0.04

										11/20/08		0.045

										11/21/08		0.045

										11/22/08		0.04

										11/24/08		0.04

										11/25/08		0.04

										11/26/08		0.04

										12/1/08		0.04





CER Pressure

		



Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)

R&D Bio-Safety Cabinet South (left axis)

Date

Diff. Pressure (Water Column In.)

Mfg Bio-Safety Cabinet South CFM

Figure 7.  CER2 Bio-Safety Cabinet Differential Pressure Daily Run Chart



Conf-Rel

		



Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

R&D Bio-Safety Cabinet South (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)

Date

Diff. Pressure (Water Column In.)

Mfg Bio-Safety Cabinet (cfm)

Figure 8.  Bio-Safety Cabinet Differential Pressure - Monthly Average



Temp-Humid

		



CER1

CER Change Room

CER2

CER3

CER Alert Level

CER Action Level

Date

Diff. Pressure (Water Column In.)

Figure 5.  CER Differential Pressure Daily Run Chart



Sheet1

		



CER1

CER Change Room

CER 2

CER 3

CER Alert Level

CER Action Level

Date

Diff. Pressure (Water Column In.)

Figure 6.  CER Differential Pressure - Monthly Average



		TO:		DCN 0273 File

		FROM:		Andy Pearson

		DATE:		3/3/07

		RE:		Confidence and Reliability Levels for CER Monitoring

		The table below shows 95/95, and 95/99 confidence/reliability levels for  CER and Change Room

		monitoring carried out from Feb 06 to Feb 07.

		Recommended action and alert levels correspond to worst case 95/95 (alert) and 95/99 (action) values.

						95/95 Limit		Recommended Alert Level		95/99 Limit		95/99 Limit		Recommended Action Level

		Airstrips (utl)		CER1		17		35		21		21		45

				CER2		15				20		20

				CER3		34				43		43

		Contact Plates (utl)		CER1		5		6		6		6		7

				CER2		4				5		5

				CER3		6				7		7

		0.5um Particle Counts (utl)		CER1		1092		3800		1324		1324		4500

				CER3		3797				4549		4549

				CER2		1232		1250		1495		1495		1500

		5.0um Particle Counts (utl)		CER1		159		410		200		200		500

				CER3		410				497		497

				CER2		91		90		107		107		105

		Pressure Differential (ltl)		CER1		0.011		0.030		0.003		0.003		0.005

				CER1/2 Chg Rm		0.021				0.013		0.013

				CER2		-0.021				-0.045		-0.045

				CER3		0.040				0.035		0.035

		Andy Pearson

		Sr.Quality Engineer





		CER2								CER1								CER3								QA

		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 2 Temperature(°F)		CER 2 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 1 Temperature(°F)		CER 1 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 3 Temperature(°F)		CER 3 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		QA Temperature(°F)		QA Humidity(%)

		29-Aug-07		16:07:10		75.81		46.5		29-Aug-07		16:06:20		76.4		48		29-Aug-07		16:07:53		75.81		74		9-Oct-07		16:25:59		78.2		33

		29-Aug-07		18:07:10		74.01		40.5		29-Aug-07		18:06:20		70.41		41.5		29-Aug-07		18:07:53		74.6		41.5		9-Oct-07		18:25:59		75.81		35.5

		29-Aug-07		20:07:10		74.6		40.5		29-Aug-07		20:06:20		71.6		43.5		29-Aug-07		20:07:53		73.4		43		9-Oct-07		20:25:59		75.2		34.5

		29-Aug-07		22:07:10		75.81		40.5		29-Aug-07		22:06:20		71.6		46.5		29-Aug-07		22:07:53		74.6		42		9-Oct-07		22:25:59		74.6		35

		30-Aug-07		0:07:10		75.81		40.5		30-Aug-07		0:06:20		71.6		47.5		30-Aug-07		0:07:53		75.2		41.5		10-Oct-07		0:25:59		73.4		36

		30-Aug-07		2:07:10		75.81		41		30-Aug-07		2:06:20		71		49		30-Aug-07		2:07:53		75.81		41.5		10-Oct-07		2:25:59		72.8		37

		30-Aug-07		4:07:10		75.2		42.5		30-Aug-07		4:06:20		71		51		30-Aug-07		4:07:53		75.2		41.5		10-Oct-07		4:25:59		72.21		38

		30-Aug-07		6:07:10		75.81		41		30-Aug-07		6:06:20		71.6		46.5		30-Aug-07		6:07:53		75.2		42		10-Oct-07		6:25:59		72.21		39

		30-Aug-07		8:07:10		75.81		45.5		30-Aug-07		8:06:20		72.21		55.5		30-Aug-07		8:07:53		75.2		44		10-Oct-07		8:25:59		71.6		41.5

		30-Aug-07		10:07:10		74.6		43.5		30-Aug-07		10:06:20		72.21		41.5		30-Aug-07		10:07:53		74.6		45		10-Oct-07		10:25:59		72.8		42.5

		30-Aug-07		12:07:10		74.6		43.5		30-Aug-07		12:06:20		71.6		46		30-Aug-07		12:07:53		72.8		45.5		10-Oct-07		12:25:59		74.01		42.5

		30-Aug-07		14:07:10		74.6		43		30-Aug-07		14:06:20		72.21		43		30-Aug-07		14:07:53		72.21		44.5		10-Oct-07		14:25:59		75.2		43

		30-Aug-07		16:07:10		75.2		43.5		30-Aug-07		16:06:20		72.21		43.5		30-Aug-07		16:07:53		72.8		44.5		10-Oct-07		16:25:59		75.2		42

		30-Aug-07		18:07:10		75.2		45		30-Aug-07		18:06:20		70.41		49.5		30-Aug-07		18:07:53		71.6		46		10-Oct-07		18:25:59		75.2		41

		30-Aug-07		20:07:10		75.2		45.5		30-Aug-07		20:06:20		71.6		52		30-Aug-07		20:07:53		75.81		45		10-Oct-07		20:25:59		74.01		42.5

		30-Aug-07		22:07:10		76.4		45		30-Aug-07		22:06:20		71		53.5		30-Aug-07		22:07:53		75.2		45		10-Oct-07		22:25:59		73.4		43.5

		31-Aug-07		0:07:10		76.4		44.5		31-Aug-07		0:06:20		71		53.5		31-Aug-07		0:07:53		75.2		44.5		11-Oct-07		0:25:59		72.8		44.5

		31-Aug-07		2:07:10		75.81		44.5		31-Aug-07		2:06:20		71.6		53		31-Aug-07		2:07:53		75.2		45.5		11-Oct-07		2:25:59		72.21		45

		31-Aug-07		4:07:10		75.81		45		31-Aug-07		4:06:20		71.6		53		31-Aug-07		4:07:53		72.8		41.5		11-Oct-07		4:25:59		71.6		45.5

		31-Aug-07		6:07:10		75.81		45.5		31-Aug-07		6:06:20		72.21		54		31-Aug-07		6:07:53		71		54.5		11-Oct-07		6:25:59		72.21		45

		31-Aug-07		8:07:10		75.2		44		31-Aug-07		8:06:20		72.21		43.5		31-Aug-07		8:07:53		71.6		50.5		11-Oct-07		8:25:59		71.6		46.5

		31-Aug-07		10:07:10		74.6		45.5		31-Aug-07		10:06:20		72.21		49.5		31-Aug-07		10:07:53		72.21		44.5		11-Oct-07		10:25:59		72.8		48.5

		31-Aug-07		12:07:10		74.6		49.5		31-Aug-07		12:06:20		71.6		60.5		31-Aug-07		12:07:53		72.21		45		11-Oct-07		12:25:59		74.6		44.5

		31-Aug-07		14:07:10		74.6		45.5		31-Aug-07		14:06:20		71.6		44		31-Aug-07		14:07:53		72.8		47		11-Oct-07		14:25:59		75.81		42.5

		31-Aug-07		16:07:10		74.6		48		31-Aug-07		16:06:20		71.6		56.5		31-Aug-07		16:07:53		72.8		43.5		11-Oct-07		16:25:59		76.4		42.5

		31-Aug-07		18:07:10		75.2		46.5		31-Aug-07		18:06:20		70.41		54.5		31-Aug-07		18:07:53		71		50		11-Oct-07		18:25:59		76.4		41

		31-Aug-07		20:07:10		75.2		46		31-Aug-07		20:06:20		71.6		53		31-Aug-07		20:07:53		74.6		50		11-Oct-07		20:25:59		74.6		41.5

		31-Aug-07		22:07:10		76.4		44		31-Aug-07		22:06:20		71.6		48.5		31-Aug-07		22:07:53		75.2		47		11-Oct-07		22:25:59		74.6		41

		1-Sep-07		0:07:10		76.4		42.5		1-Sep-07		0:06:20		71.6		46.5		1-Sep-07		0:07:53		75.2		45.5		12-Oct-07		0:25:59		73.4		41

		1-Sep-07		2:07:10		76.4		44		1-Sep-07		2:06:20		71.6		53		1-Sep-07		2:07:53		74.6		45.5		12-Oct-07		2:25:59		71.6		41

		1-Sep-07		4:07:10		76.4		44		1-Sep-07		4:06:20		71.6		53		1-Sep-07		4:07:53		72.8		50		12-Oct-07		4:25:59		71		41.5

		1-Sep-07		6:07:10		76.4		45		1-Sep-07		6:06:20		73.4		56.5		1-Sep-07		6:07:53		71.6		45		12-Oct-07		6:25:59		70.41		41.5

		1-Sep-07		8:07:10		75.2		42.5		1-Sep-07		8:06:20		72.21		41		1-Sep-07		8:07:53		71.6		53		12-Oct-07		8:25:59		69.8		41.5

		1-Sep-07		10:07:10		74.6		43.5		1-Sep-07		10:06:20		71.6		42		1-Sep-07		10:07:53		72.21		43.5		12-Oct-07		10:25:59		71.6		44.5

		1-Sep-07		12:07:10		74.6		51.5		1-Sep-07		12:06:20		70.41		64		1-Sep-07		12:07:53		71.6		45.5		12-Oct-07		12:25:59		74.6		43.5

		1-Sep-07		14:07:10		74.6		52		1-Sep-07		14:06:20		70.41		64.5		1-Sep-07		14:07:53		71		50.5		12-Oct-07		14:25:59		75.2		42.5

		1-Sep-07		16:07:10		74.6		46.5		1-Sep-07		16:06:20		70.41		52.5		1-Sep-07		16:07:53		71		57.5		12-Oct-07		16:25:59		75.2		42.5

		1-Sep-07		18:07:10		74.6		45.5		1-Sep-07		18:06:20		70.41		50.5		1-Sep-07		18:07:53		71		58.5		12-Oct-07		18:25:59		74.6		40

		1-Sep-07		20:07:10		74.6		49.5		1-Sep-07		20:06:20		71		56		1-Sep-07		20:07:53		71		55.5		12-Oct-07		20:25:59		74.01		40.5

		1-Sep-07		22:07:10		75.2		47		1-Sep-07		22:06:20		71		56		1-Sep-07		22:07:53		72.21		50.5		12-Oct-07		22:25:59		74.01		40

		2-Sep-07		0:07:10		75.2		45		2-Sep-07		0:06:20		71.6		52.5		2-Sep-07		0:07:53		72.21		50		13-Oct-07		0:25:59		72.8		40.5

		2-Sep-07		2:07:10		75.2		44.5		2-Sep-07		2:06:20		71		51		2-Sep-07		2:07:53		71.6		50		13-Oct-07		2:25:59		71.6		41

		2-Sep-07		4:07:10		74.6		44		2-Sep-07		4:06:20		70.41		51.5		2-Sep-07		4:07:53		70.41		49.5		13-Oct-07		4:25:59		71		42.5

		2-Sep-07		6:07:10		74.01		41.5		2-Sep-07		6:06:20		71		45.5		2-Sep-07		6:07:53		69.2		48.5		13-Oct-07		6:25:59		71.6		43

		2-Sep-07		8:07:10		73.4		44		2-Sep-07		8:06:20		69.8		51		2-Sep-07		8:07:53		69.2		51		13-Oct-07		8:25:59		71		46

		2-Sep-07		10:07:10		74.01		48.5		2-Sep-07		10:06:20		70.41		57.5		2-Sep-07		10:07:53		71		48.5		13-Oct-07		10:25:59		72.21		47.5

		2-Sep-07		12:07:10		74.6		49.5		2-Sep-07		12:06:20		70.41		59.5		2-Sep-07		12:07:53		71		53		13-Oct-07		12:25:59		72.8		47

		2-Sep-07		14:07:10		75.81		49.5		2-Sep-07		14:06:20		70.41		60.5		2-Sep-07		14:07:53		71		60		13-Oct-07		14:25:59		72.21		47.5

		2-Sep-07		16:07:10		76.4		43.5		2-Sep-07		16:06:20		70.41		47.5		2-Sep-07		16:07:53		71		46.5		13-Oct-07		16:25:59		74.01		47

		2-Sep-07		18:07:10		76.4		46.5		2-Sep-07		18:06:20		69.8		55.5		2-Sep-07		18:07:53		71		58		13-Oct-07		18:25:59		74.6		44.5

		2-Sep-07		20:07:10		77		44		2-Sep-07		20:06:20		71		52.5		2-Sep-07		20:07:53		74.01		47		13-Oct-07		20:25:59		72.8		45.5

		2-Sep-07		22:07:10		77		41.5		2-Sep-07		22:06:20		71.6		51		2-Sep-07		22:07:53		74.6		44.5		13-Oct-07		22:25:59		71.6		45

		3-Sep-07		0:07:10		76.4		41		3-Sep-07		0:06:20		71		50.5		3-Sep-07		0:07:53		74.01		44.5		14-Oct-07		0:25:59		71		45

		3-Sep-07		2:07:10		75.81		40		3-Sep-07		2:06:20		71		44		3-Sep-07		2:07:53		72.21		45.5		14-Oct-07		2:25:59		69.8		43.5

		3-Sep-07		4:07:10		75.2		39		3-Sep-07		4:06:20		71		41.5		3-Sep-07		4:07:53		71		46.5		14-Oct-07		4:25:59		69.2		43

		3-Sep-07		6:07:10		75.2		40		3-Sep-07		6:06:20		71.6		46		3-Sep-07		6:07:53		69.2		47.5		14-Oct-07		6:25:59		69.2		42.5

		3-Sep-07		8:07:10		74.01		42		3-Sep-07		8:06:20		69.8		49		3-Sep-07		8:07:53		68.61		49.5		14-Oct-07		8:25:59		69.2		41

		3-Sep-07		10:07:10		74.01		43		3-Sep-07		10:06:20		70.41		48		3-Sep-07		10:07:53		70.41		52		14-Oct-07		10:25:59		71		44

		3-Sep-07		12:07:10		74.6		41.5		3-Sep-07		12:06:20		70.41		43.5		3-Sep-07		12:07:53		71		43.5		14-Oct-07		12:25:59		72.21		45

		3-Sep-07		14:07:10		75.2		43		3-Sep-07		14:06:20		70.41		47		3-Sep-07		14:07:53		71.6		52		14-Oct-07		14:25:59		74.01		44.5

		3-Sep-07		16:07:10		75.81		44.5		3-Sep-07		16:06:20		69.8		49.5		3-Sep-07		16:07:53		71.6		52		14-Oct-07		16:25:59		75.2		44.5

		3-Sep-07		18:07:10		76.4		40.5		3-Sep-07		18:06:20		70.41		47		3-Sep-07		18:07:53		71		45		14-Oct-07		18:25:59		75.81		44

		3-Sep-07		20:07:10		77.61		40		3-Sep-07		20:06:20		71.6		45.5		3-Sep-07		20:07:53		75.81		42		14-Oct-07		20:25:59		74.6		44.5

		3-Sep-07		22:07:10		77		41		3-Sep-07		22:06:20		71.6		50.5		3-Sep-07		22:07:53		74.6		43.5		14-Oct-07		22:25:59		73.4		45

		4-Sep-07		0:07:10		76.4		40.5		4-Sep-07		0:06:20		71		50		4-Sep-07		0:07:53		74.6		43.5		15-Oct-07		0:25:59		72.8		45.5

		4-Sep-07		2:07:10		75.81		40		4-Sep-07		2:06:20		71		49.5		4-Sep-07		2:07:53		72.8		44		15-Oct-07		2:25:59		72.21		46

		4-Sep-07		4:07:10		75.81		39.5		4-Sep-07		4:06:20		71.6		47		4-Sep-07		4:07:53		71.6		45		15-Oct-07		4:25:59		71.6		46

		4-Sep-07		6:07:10		74.6		40		4-Sep-07		6:06:20		71		47.5		4-Sep-07		6:07:53		69.8		46.5		15-Oct-07		6:25:59		71		46.5

		4-Sep-07		8:07:10		74.01		39.5		4-Sep-07		8:06:20		70.41		42		4-Sep-07		8:07:53		69.8		48.5		15-Oct-07		8:25:59		70.41		47

		4-Sep-07		10:07:10		74.01		45.5		4-Sep-07		10:06:20		69.8		53.5		4-Sep-07		10:07:53		71		52		15-Oct-07		10:25:59		69.8		47.5

		4-Sep-07		12:07:10		74.01		48		4-Sep-07		12:06:20		69.8		55		4-Sep-07		12:07:53		71		45.5		15-Oct-07		12:25:59		70.41		48.5

		4-Sep-07		14:07:10		74.01		49		4-Sep-07		14:06:20		70.41		52		4-Sep-07		14:07:53		71		58.5		15-Oct-07		14:25:59		71.6		49

		4-Sep-07		16:07:10		74.6		47.5		4-Sep-07		16:06:20		70.41		50		4-Sep-07		16:07:53		71		49		15-Oct-07		16:25:59		73.4		48

		4-Sep-07		18:07:10		74.6		47.5		4-Sep-07		18:06:20		70.41		50		4-Sep-07		18:07:53		71		49.5		15-Oct-07		18:25:59		74.6		45.5

		4-Sep-07		20:07:10		75.2		50		4-Sep-07		20:06:20		71		58.5		4-Sep-07		20:07:53		71.6		55.5		15-Oct-07		20:25:59		72.8		46

		4-Sep-07		22:07:10		75.81		47.5		4-Sep-07		22:06:20		71.6		56		4-Sep-07		22:07:53		74.01		50		15-Oct-07		22:25:59		71.6		46

		5-Sep-07		0:07:10		75.81		46.5		5-Sep-07		0:06:20		71		56.5		5-Sep-07		0:07:53		74.01		49.5		16-Oct-07		0:25:59		71		46

		5-Sep-07		2:07:10		75.81		44.5		5-Sep-07		2:06:20		71		47.5		5-Sep-07		2:07:53		72.8		50.5		16-Oct-07		2:25:59		70.41		46.5

		5-Sep-07		4:07:10		75.2		45.5		5-Sep-07		4:06:20		71		55		5-Sep-07		4:07:53		71.6		49		16-Oct-07		4:25:59		69.8		46

		5-Sep-07		6:07:10		75.2		47		5-Sep-07		6:06:20		71.6		55		5-Sep-07		6:07:53		70.41		48		16-Oct-07		6:25:59		70.41		46.5

		5-Sep-07		8:07:10		75.2		45		5-Sep-07		8:06:20		72.21		45.5		5-Sep-07		8:07:53		71		53		16-Oct-07		8:25:59		69.8		47.5

		5-Sep-07		10:07:10		74.6		51.5		5-Sep-07		10:06:20		72.21		55		5-Sep-07		10:07:53		72.8		46.5		16-Oct-07		10:25:59		71		49.5

		5-Sep-07		12:07:10		74.01		50.5		5-Sep-07		12:06:20		71		56		5-Sep-07		12:07:53		72.21		57.5		16-Oct-07		12:25:59		72.21		52

		5-Sep-07		14:07:10		74.01		48		5-Sep-07		14:06:20		71.6		54.5		5-Sep-07		14:07:53		72.21		54		16-Oct-07		14:25:59		73.4		52.5

		5-Sep-07		16:07:10		74.01		49		5-Sep-07		16:06:20		71		54		5-Sep-07		16:07:53		72.21		51		16-Oct-07		16:25:59		75.2		47.5

		5-Sep-07		18:07:10		74.6		49		5-Sep-07		18:06:20		70.41		60		5-Sep-07		18:07:53		71.6		48.5		16-Oct-07		18:25:59		75.81		47.5

		5-Sep-07		20:07:10		74.6		48		5-Sep-07		20:06:20		71.6		55		5-Sep-07		20:07:53		71		58		16-Oct-07		20:25:59		74.01		48.5

		5-Sep-07		22:07:10		75.81		46.5		5-Sep-07		22:06:20		71		55.5		5-Sep-07		22:07:53		75.2		47		16-Oct-07		22:25:59		73.4		49

		6-Sep-07		0:07:10		75.81		43.5		6-Sep-07		0:06:20		71.6		50.5		6-Sep-07		0:07:53		74.6		47		17-Oct-07		0:25:59		72.21		49

		6-Sep-07		2:07:10		75.2		44.5		6-Sep-07		2:06:20		71		52.5		6-Sep-07		2:07:53		73.4		47		17-Oct-07		2:25:59		71		48

		6-Sep-07		4:07:10		75.2		43.5		6-Sep-07		4:06:20		71.6		51		6-Sep-07		4:07:53		72.21		48.5		17-Oct-07		4:25:59		70.41		47.5

		6-Sep-07		6:07:10		75.2		42.5		6-Sep-07		6:06:20		71.6		48.5		6-Sep-07		6:07:53		71		50.5		17-Oct-07		6:25:59		69.8		46

		6-Sep-07		8:07:10		75.2		45.5		6-Sep-07		8:06:20		72.21		52		6-Sep-07		8:07:53		71.6		48.5		17-Oct-07		8:25:59		69.2		46.5

		6-Sep-07		10:07:10		75.2		43.5		6-Sep-07		10:06:20		72.21		46		6-Sep-07		10:07:53		72.21		49.5		17-Oct-07		10:25:59		70.41		49

		6-Sep-07		12:07:10		74.6		41.5		6-Sep-07		12:06:20		71.6		42.5		6-Sep-07		12:07:53		72.21		52		17-Oct-07		12:25:59		71.6		51.5

		6-Sep-07		14:07:10		74.01		40		6-Sep-07		14:06:20		71.6		40.5		6-Sep-07		14:07:53		72.21		42		17-Oct-07		14:25:59		72.21		53

		6-Sep-07		16:07:10		74.6		40		6-Sep-07		16:06:20		71.6		43		6-Sep-07		16:07:53		72.21		40		17-Oct-07		16:25:59		72.8		54

		6-Sep-07		18:07:10		74.6		38		6-Sep-07		18:06:20		69.8		42		6-Sep-07		18:07:53		72.21		37.5		17-Oct-07		18:25:59		74.01		50.5

		6-Sep-07		20:07:10		75.2		38		6-Sep-07		20:06:20		71.6		43		6-Sep-07		20:07:53		75.2		39.5		17-Oct-07		20:25:59		72.21		48.5

		6-Sep-07		22:07:10		75.81		38.5		6-Sep-07		22:06:20		71.6		45.5		6-Sep-07		22:07:53		75.2		39.5		17-Oct-07		22:25:59		71		48

		7-Sep-07		0:07:10		75.81		39		7-Sep-07		0:06:20		71.6		46.5		7-Sep-07		0:07:53		75.2		39.5		18-Oct-07		0:25:59		70.41		47

		7-Sep-07		2:07:10		75.81		39		7-Sep-07		2:06:20		71.6		46		7-Sep-07		2:07:53		74.01		41		18-Oct-07		2:25:59		69.2		45.5

		7-Sep-07		4:07:10		75.2		39		7-Sep-07		4:06:20		71		46		7-Sep-07		4:07:53		72.21		37		18-Oct-07		4:25:59		68.61		45

		7-Sep-07		6:07:10		75.81		38		7-Sep-07		6:06:20		71.6		44		7-Sep-07		6:07:53		71		45.5		18-Oct-07		6:25:59		69.2		46

		7-Sep-07		8:07:10		75.81		41		7-Sep-07		8:06:20		71.6		50		7-Sep-07		8:07:53		71.6		39.5		18-Oct-07		8:25:59		69.2		47

		7-Sep-07		10:07:10		75.2		38.5		7-Sep-07		10:06:20		71.6		40.5		7-Sep-07		10:07:53		72.21		40		18-Oct-07		10:25:59		70.41		50

		7-Sep-07		12:07:10		74.6		40		7-Sep-07		12:06:20		71		42.5		7-Sep-07		12:07:53		72.21		51.5		18-Oct-07		12:25:59		72.8		48.5

		7-Sep-07		14:07:10		74.6		43		7-Sep-07		14:06:20		71.6		42		7-Sep-07		14:07:53		71.6		42.5		18-Oct-07		14:25:59		74.6		45

		7-Sep-07		16:07:10		75.81		46		7-Sep-07		16:06:20		71		61		7-Sep-07		16:07:53		71.6		44.5		18-Oct-07		16:25:59		75.81		43

		7-Sep-07		18:07:10		75.2		45.5		7-Sep-07		18:06:20		71		48		7-Sep-07		18:07:53		71		53.5		18-Oct-07		18:25:59		75.81		43

		7-Sep-07		20:07:10		75.81		49		7-Sep-07		20:06:20		71.6		57		7-Sep-07		20:07:53		71.6		55		18-Oct-07		20:25:59		74.6		43.5

		7-Sep-07		22:07:10		75.81		48.5		7-Sep-07		22:06:20		71.6		58		7-Sep-07		22:07:53		72.8		52		18-Oct-07		22:25:59		73.4		44

		8-Sep-07		0:07:10		75.2		47.5		8-Sep-07		0:06:20		71		56.5		8-Sep-07		0:07:53		72.8		51		19-Oct-07		0:25:59		72.21		44.5

		8-Sep-07		2:07:10		75.2		47		8-Sep-07		2:06:20		71.6		55		8-Sep-07		2:07:53		72.21		51.5		19-Oct-07		2:25:59		71		44.5

		8-Sep-07		4:07:10		75.2		47		8-Sep-07		4:06:20		71		55.5		8-Sep-07		4:07:53		71.6		51		19-Oct-07		4:25:59		70.41		45

		8-Sep-07		6:07:10		75.81		47		8-Sep-07		6:06:20		71.6		54.5		8-Sep-07		6:07:53		71		55		19-Oct-07		6:25:59		70.41		45.5

		8-Sep-07		8:07:10		75.2		47.5		8-Sep-07		8:06:20		72.21		56		8-Sep-07		8:07:53		71.6		57		19-Oct-07		8:25:59		70.41		46.5

		8-Sep-07		10:07:10		74.6		44.5		8-Sep-07		10:06:20		72.21		45		8-Sep-07		10:07:53		72.21		46.5		19-Oct-07		10:25:59		71.6		47.5

		8-Sep-07		12:07:10		74.6		50.5		8-Sep-07		12:06:20		71		57		8-Sep-07		12:07:53		72.21		45		19-Oct-07		12:25:59		73.4		46

		8-Sep-07		14:07:10		74.01		46		8-Sep-07		14:06:20		72.21		46		8-Sep-07		14:07:53		71.6		46.5		19-Oct-07		14:25:59		75.2		45.5

		8-Sep-07		16:07:10		74.01		53		8-Sep-07		16:06:20		71		67		8-Sep-07		16:07:53		71.6		50.5		19-Oct-07		16:25:59		74.6		49

		8-Sep-07		18:07:10		74.01		53		8-Sep-07		18:06:20		70.41		63		8-Sep-07		18:07:53		71		53.5		19-Oct-07		18:25:59		74.6		50.5

		8-Sep-07		20:07:10		74.6		51		8-Sep-07		20:06:20		71		58		8-Sep-07		20:07:53		70.41		57		19-Oct-07		20:25:59		74.01		51.5

		8-Sep-07		22:07:10		74.6		48		8-Sep-07		22:06:20		71		55		8-Sep-07		22:07:53		70.41		54		19-Oct-07		22:25:59		74.01		51

		9-Sep-07		0:07:10		74.6		45		9-Sep-07		0:06:20		71		46		9-Sep-07		0:07:53		69.8		53		20-Oct-07		0:25:59		73.4		51.5

		9-Sep-07		2:07:10		74.01		45.5		9-Sep-07		2:06:20		71		52.5		9-Sep-07		2:07:53		69.2		52.5		20-Oct-07		2:25:59		72.8		52.5

		9-Sep-07		4:07:10		74.01		46.5		9-Sep-07		4:06:20		71		53.5		9-Sep-07		4:07:53		69.2		55		20-Oct-07		4:25:59		72.8		53

		9-Sep-07		6:07:10		74.01		48.5		9-Sep-07		6:06:20		71.6		56		9-Sep-07		6:07:53		68.61		56		20-Oct-07		6:25:59		72.8		54

		9-Sep-07		8:07:10		74.01		46		9-Sep-07		8:06:20		71		50		9-Sep-07		8:07:53		68.61		57		20-Oct-07		8:25:59		72.8		56.5

		9-Sep-07		10:07:10		73.4		50.5		9-Sep-07		10:06:20		70.41		57.5		9-Sep-07		10:07:53		68.61		58		20-Oct-07		10:25:59		74.01		57.5

		9-Sep-07		12:07:10		73.4		51.5		9-Sep-07		12:06:20		70.41		56.5		9-Sep-07		12:07:53		69.8		57.5		20-Oct-07		12:25:59		75.2		57.5

		9-Sep-07		14:07:10		73.4		55		9-Sep-07		14:06:20		70.41		63.5		9-Sep-07		14:07:53		70.41		54.5		20-Oct-07		14:25:59		75.81		57

		9-Sep-07		16:07:10		74.6		54		9-Sep-07		16:06:20		70.41		64.5		9-Sep-07		16:07:53		71		51		20-Oct-07		16:25:59		75.81		57

		9-Sep-07		18:07:10		75.2		50		9-Sep-07		18:06:20		70.41		55		9-Sep-07		18:07:53		70.41		60		20-Oct-07		18:25:59		75.81		56

		9-Sep-07		20:07:10		75.2		44.5		9-Sep-07		20:06:20		71.6		47		9-Sep-07		20:07:53		70.41		55		20-Oct-07		20:25:59		74.01		54.5

		9-Sep-07		22:07:10		74.6		47		9-Sep-07		22:06:20		71		54.5		9-Sep-07		22:07:53		69.8		54		20-Oct-07		22:25:59		72.8		53

		10-Sep-07		0:07:10		74.6		46		10-Sep-07		0:06:20		71		52.5		10-Sep-07		0:07:53		69.2		53.5		21-Oct-07		0:25:59		71.6		51

		10-Sep-07		2:07:10		74.6		45.5		10-Sep-07		2:06:20		71.6		51		10-Sep-07		2:07:53		68.61		53.5		21-Oct-07		2:25:59		71		50

		10-Sep-07		4:07:10		74.01		45		10-Sep-07		4:06:20		71.6		50		10-Sep-07		4:07:53		68.61		54		21-Oct-07		4:25:59		70.41		49.5

		10-Sep-07		6:07:10		74.01		45		10-Sep-07		6:06:20		71		51		10-Sep-07		6:07:53		68		54.5		21-Oct-07		6:25:59		69.8		47.5

		10-Sep-07		8:07:10		72.8		44.5		10-Sep-07		8:06:20		69.8		50.5		10-Sep-07		8:07:53		67.4		54.5		21-Oct-07		8:25:59		69.2		45.5

		10-Sep-07		10:07:10		72.8		45.5		10-Sep-07		10:06:20		69.8		46.5		10-Sep-07		10:07:53		67.4		55		21-Oct-07		10:25:59		69.2		48

		10-Sep-07		12:07:10		72.8		46		10-Sep-07		12:06:20		70.41		49.5		10-Sep-07		12:07:53		68.61		56		21-Oct-07		12:25:59		70.41		45.5

		10-Sep-07		14:07:10		73.4		49		10-Sep-07		14:06:20		70.41		56.5		10-Sep-07		14:07:53		69.8		59.5		21-Oct-07		14:25:59		71		42

		10-Sep-07		16:07:10		74.01		53.5		10-Sep-07		16:06:20		70.41		62.5		10-Sep-07		16:07:53		70.41		49		21-Oct-07		16:25:59		72.21		39

		10-Sep-07		18:07:10		74.6		52.5		10-Sep-07		18:06:20		70.41		63		10-Sep-07		18:07:53		71		56		21-Oct-07		18:25:59		73.4		36.5

		10-Sep-07		20:07:10		75.2		49		10-Sep-07		20:06:20		71.6		55.5		10-Sep-07		20:07:53		71.6		54.5		21-Oct-07		20:25:59		72.21		38

		10-Sep-07		22:07:10		74.6		48		10-Sep-07		22:06:20		71		56		10-Sep-07		22:07:53		70.41		54		21-Oct-07		22:25:59		71		40

		11-Sep-07		0:07:10		74.6		47		11-Sep-07		0:06:20		71		54.5		11-Sep-07		0:07:53		69.8		53.5		22-Oct-07		0:25:59		69.8		39.5

		11-Sep-07		2:07:10		74.01		45.5		11-Sep-07		2:06:20		71		52		11-Sep-07		2:07:53		68.61		53.5		22-Oct-07		2:25:59		69.2		39.5

		11-Sep-07		4:07:10		74.01		44.5		11-Sep-07		4:06:20		71.6		48.5		11-Sep-07		4:07:53		68		53.5		22-Oct-07		4:25:59		69.2		39

		11-Sep-07		6:07:10		74.01		43		11-Sep-07		6:06:20		71		48		11-Sep-07		6:07:53		68.61		52		22-Oct-07		6:25:59		68.61		38.5

		11-Sep-07		8:07:10		74.01		43.5		11-Sep-07		8:06:20		70.41		45		11-Sep-07		8:07:53		71.6		51.5		22-Oct-07		8:25:59		68		37.5

		11-Sep-07		10:07:10		74.6		46.5		11-Sep-07		10:06:20		71		45.5		11-Sep-07		10:07:53		71.6		48		22-Oct-07		10:25:59		68		37.5

		11-Sep-07		12:07:10		74.01		52.5		11-Sep-07		12:06:20		71		63		11-Sep-07		12:07:53		72.21		46		22-Oct-07		12:25:59		69.2		36

		11-Sep-07		14:07:10		74.6		46.5		11-Sep-07		14:06:20		71.6		45		11-Sep-07		14:07:53		71.6		45		22-Oct-07		14:25:59		72.21		33

		11-Sep-07		16:07:10		75.2		48.5		11-Sep-07		16:06:20		70.41		52		11-Sep-07		16:07:53		71		63		22-Oct-07		16:25:59		72.8		33

		11-Sep-07		18:07:10		74.6		49.5		11-Sep-07		18:06:20		70.41		54		11-Sep-07		18:07:53		71		60.5		22-Oct-07		18:25:59		72.8		32.5

		11-Sep-07		20:07:10		75.2		50.5		11-Sep-07		20:06:20		71		58.5		11-Sep-07		20:07:53		70.41		57.5		22-Oct-07		20:25:59		72.8		31.5

		11-Sep-07		22:07:10		75.2		45.5		11-Sep-07		22:06:20		71.6		51.5		11-Sep-07		22:07:53		72.21		52		22-Oct-07		22:25:59		72.21		35

		12-Sep-07		0:07:10		74.6		46.5		12-Sep-07		0:06:20		71.6		53		12-Sep-07		0:07:53		71.6		51		23-Oct-07		0:25:59		71.6		36

		12-Sep-07		2:07:10		74.6		45.5		12-Sep-07		2:06:20		71.6		51.5		12-Sep-07		2:07:53		71		51		23-Oct-07		2:25:59		70.41		37

		12-Sep-07		4:07:10		74.01		46.5		12-Sep-07		4:06:20		70.41		53.5		12-Sep-07		4:07:53		70.41		52		23-Oct-07		4:25:59		69.8		36.5

		12-Sep-07		6:07:10		74.6		46.5		12-Sep-07		6:06:20		71		53		12-Sep-07		6:07:53		70.41		50		23-Oct-07		6:25:59		69.8		36.5

		12-Sep-07		8:07:10		74.01		45.5		12-Sep-07		8:06:20		71.6		44.5		12-Sep-07		8:07:53		71		48.5		23-Oct-07		8:25:59		68.61		37.5

		12-Sep-07		10:07:10		74.01		47.5		12-Sep-07		10:06:20		72.21		55		12-Sep-07		10:07:53		71.6		56		23-Oct-07		10:25:59		71.6		39

		12-Sep-07		12:07:10		74.6		47		12-Sep-07		12:06:20		71.6		53		12-Sep-07		12:07:53		72.21		52		23-Oct-07		12:25:59		74.6		37.5

		12-Sep-07		14:07:10		74.01		46		12-Sep-07		14:06:20		71.6		43		12-Sep-07		14:07:53		71.6		54		23-Oct-07		14:25:59		75.2		37

		12-Sep-07		16:07:10		74.6		49		12-Sep-07		16:06:20		71		53		12-Sep-07		16:07:53		71.6		46.5		23-Oct-07		16:25:59		75.81		36.5

		12-Sep-07		18:07:10		74.6		53		12-Sep-07		18:06:20		70.41		65		12-Sep-07		18:07:53		71		62.5		23-Oct-07		18:25:59		75.81		35.5

		12-Sep-07		20:07:10		74.6		52		12-Sep-07		20:06:20		71		60.5		12-Sep-07		20:07:53		71		54.5		23-Oct-07		20:25:59		74.6		36

		12-Sep-07		22:07:10		74.6		49		12-Sep-07		22:06:20		71.6		56.5		12-Sep-07		22:07:53		72.8		52.5		23-Oct-07		22:25:59		74.01		37.5

		13-Sep-07		0:07:10		75.2		49		13-Sep-07		0:06:20		71.6		56.5		13-Sep-07		0:07:53		72.8		53		24-Oct-07		0:25:59		73.4		38.5

		13-Sep-07		2:07:10		75.2		48.5		13-Sep-07		2:06:20		71		57		13-Sep-07		2:07:53		72.21		53		24-Oct-07		2:25:59		72.21		39

		13-Sep-07		4:07:10		74.6		48.5		13-Sep-07		4:06:20		70.41		58.5		13-Sep-07		4:07:53		71.6		56		24-Oct-07		4:25:59		71		39.5

		13-Sep-07		6:07:10		75.2		49		13-Sep-07		6:06:20		71		58		13-Sep-07		6:07:53		70.41		50.5		24-Oct-07		6:25:59		71		39

		13-Sep-07		8:07:10		74.6		50		13-Sep-07		8:06:20		71		52.5		13-Sep-07		8:07:53		71		56		24-Oct-07		8:25:59		69.8		39.5

		13-Sep-07		10:07:10		74.01		45.5		13-Sep-07		10:06:20		71.6		44.5		13-Sep-07		10:07:53		71.6		57		24-Oct-07		10:25:59		72.21		42.5

		13-Sep-07		12:07:10		74.6		48		13-Sep-07		12:06:20		71.6		52.5		13-Sep-07		12:07:53		71.6		48		24-Oct-07		12:25:59		75.2		41

		13-Sep-07		14:07:10		74.6		45.5		13-Sep-07		14:06:20		71.6		44		13-Sep-07		14:07:53		70.41		61.5		24-Oct-07		14:25:59		75.81		40.5

		13-Sep-07		16:07:10		74.6		52.5		13-Sep-07		16:06:20		70.41		58		13-Sep-07		16:07:53		71		61.5		24-Oct-07		16:25:59		76.4		40.5

		13-Sep-07		18:07:10		75.2		47		13-Sep-07		18:06:20		70.41		51		13-Sep-07		18:07:53		70.41		59.5		24-Oct-07		18:25:59		75.81		42.5

		13-Sep-07		20:07:10		75.2		48		13-Sep-07		20:06:20		71.6		55.5		13-Sep-07		20:07:53		71.6		55		24-Oct-07		20:25:59		75.2		45

		13-Sep-07		22:07:10		74.6		47.5		13-Sep-07		22:06:20		71		54.5		13-Sep-07		22:07:53		71.6		52.5		24-Oct-07		22:25:59		75.81		44.5

		14-Sep-07		0:07:10		74.6		46.5		14-Sep-07		0:06:20		71.6		53		14-Sep-07		0:07:53		71.6		51.5		25-Oct-07		0:25:59		74.6		43

		14-Sep-07		2:07:10		74.6		46.5		14-Sep-07		2:06:20		71		51.5		14-Sep-07		2:07:53		71.6		51.5		25-Oct-07		2:25:59		73.4		43

		14-Sep-07		4:07:10		74.6		44.5		14-Sep-07		4:06:20		71.6		50		14-Sep-07		4:07:53		71		45		25-Oct-07		4:25:59		72.21		43

		14-Sep-07		6:07:10		74.6		43.5		14-Sep-07		6:06:20		71		49.5		14-Sep-07		6:07:53		71		51		25-Oct-07		6:25:59		71.6		43

		14-Sep-07		8:07:10		74.01		46		14-Sep-07		8:06:20		71.6		54		14-Sep-07		8:07:53		71		53		25-Oct-07		8:25:59		71		42.5

		14-Sep-07		10:07:10		74.6		46.5		14-Sep-07		10:06:20		71.6		55.5		14-Sep-07		10:07:53		72.21		47.5		25-Oct-07		10:25:59		73.4		44

		14-Sep-07		12:07:10		74.01		47.5		14-Sep-07		12:06:20		70.41		53		14-Sep-07		12:07:53		72.21		43		25-Oct-07		12:25:59		75.2		44

		14-Sep-07		14:07:10		74.6		49		14-Sep-07		14:06:20		71.6		56		14-Sep-07		14:07:53		71.6		48		25-Oct-07		14:25:59		75.81		43

		14-Sep-07		16:07:10		75.2		46.5		14-Sep-07		16:06:20		71		53		14-Sep-07		16:07:53		71.6		58.5		25-Oct-07		16:25:59		75.81		41

		14-Sep-07		18:07:10		75.2		50.5		14-Sep-07		18:06:20		71		64.5		14-Sep-07		18:07:53		71		62		25-Oct-07		18:25:59		75.81		44.5

		14-Sep-07		20:07:10		75.2		50		14-Sep-07		20:06:20		71.6		59		14-Sep-07		20:07:53		72.8		55.5		25-Oct-07		20:25:59		75.2		43.5

		14-Sep-07		22:07:10		75.2		50.5		14-Sep-07		22:06:20		71.6		59.5		14-Sep-07		22:07:53		74.01		52.5		25-Oct-07		22:25:59		74.6		42.5

		15-Sep-07		0:07:10		75.2		48.5		15-Sep-07		0:06:20		71		51.5		15-Sep-07		0:07:53		73.4		52		26-Oct-07		0:25:59		73.4		42.5

		15-Sep-07		2:07:10		74.6		48		15-Sep-07		2:06:20		71.6		56		15-Sep-07		2:07:53		73.4		52		26-Oct-07		2:25:59		72.21		43

		15-Sep-07		4:07:10		74.6		48.5		15-Sep-07		4:06:20		71.6		55.5		15-Sep-07		4:07:53		72.21		54.5		26-Oct-07		4:25:59		71		42.5

		15-Sep-07		6:07:10		75.2		49.5		15-Sep-07		6:06:20		71.6		58.5		15-Sep-07		6:07:53		71		51		26-Oct-07		6:25:59		70.41		41.5

		15-Sep-07		8:07:10		75.2		46		15-Sep-07		8:06:20		72.21		49		15-Sep-07		8:07:53		71.6		56		26-Oct-07		8:25:59		69.2		41

		15-Sep-07		10:07:10		74.6		50		15-Sep-07		10:06:20		71.6		57.5		15-Sep-07		10:07:53		71.6		50		26-Oct-07		10:25:59		71		44.5

		15-Sep-07		12:07:10		74.01		51		15-Sep-07		12:06:20		71		51		15-Sep-07		12:07:53		72.21		49.5		26-Oct-07		12:25:59		74.6		43.5

		15-Sep-07		14:07:10		74.6		46.5		15-Sep-07		14:06:20		71.6		47.5		15-Sep-07		14:07:53		71.6		54		26-Oct-07		14:25:59		75.81		43.5

		15-Sep-07		16:07:10		74.6		45.5		15-Sep-07		16:06:20		69.2		50.5		15-Sep-07		16:07:53		71.6		53		26-Oct-07		16:25:59		76.4		43.5

		15-Sep-07		18:07:10		73.4		46		15-Sep-07		18:06:20		68		50		15-Sep-07		18:07:53		71		48.5		26-Oct-07		18:25:59		75.81		44

		15-Sep-07		20:07:10		74.6		45		15-Sep-07		20:06:20		71		52		15-Sep-07		20:07:53		71		50.5		26-Oct-07		20:25:59		74.6		43

		15-Sep-07		22:07:10		75.2		44.5		15-Sep-07		22:06:20		71.6		52		15-Sep-07		22:07:53		72.8		48		26-Oct-07		22:25:59		73.4		42.5

		16-Sep-07		0:07:10		75.2		44		16-Sep-07		0:06:20		71		51.5		16-Sep-07		0:07:53		72.8		48		27-Oct-07		0:25:59		72.21		43

		16-Sep-07		2:07:10		75.2		43		16-Sep-07		2:06:20		71.6		49.5		16-Sep-07		2:07:53		72.21		47.5		27-Oct-07		2:25:59		71		44

		16-Sep-07		4:07:10		74.6		44		16-Sep-07		4:06:20		71		51		16-Sep-07		4:07:53		71		48.5		27-Oct-07		4:25:59		70.41		44.5

		16-Sep-07		6:07:10		74.01		43		16-Sep-07		6:06:20		69.8		44		16-Sep-07		6:07:53		71		49		27-Oct-07		6:25:59		70.41		45.5

		16-Sep-07		8:07:10		73.4		44		16-Sep-07		8:06:20		68.61		54		16-Sep-07		8:07:53		70.41		48		27-Oct-07		8:25:59		70.41		46

		16-Sep-07		10:07:10		73.4		45.5		16-Sep-07		10:06:20		68.61		57		16-Sep-07		10:07:53		69.8		52.5		27-Oct-07		10:25:59		72.21		45.5

		16-Sep-07		12:07:10		72.8		46		16-Sep-07		12:06:20		68.61		47.5		16-Sep-07		12:07:53		70.41		56		27-Oct-07		12:25:59		74.6		44

		16-Sep-07		14:07:10		73.4		44.5		16-Sep-07		14:06:20		68.61		47		16-Sep-07		14:07:53		71		51		27-Oct-07		14:25:59		75.2		42.5

		16-Sep-07		16:07:10		74.6		45		16-Sep-07		16:06:20		68.61		52		16-Sep-07		16:07:53		71		50.5		27-Oct-07		16:25:59		75.2		43.5

		16-Sep-07		18:07:10		74.6		46		16-Sep-07		18:06:20		68.61		59		16-Sep-07		18:07:53		70.41		53		27-Oct-07		18:25:59		74.6		44

		16-Sep-07		20:07:10		75.81		45		16-Sep-07		20:06:20		71		54		16-Sep-07		20:07:53		71.6		51.5		27-Oct-07		20:25:59		72.21		43.5

		16-Sep-07		22:07:10		75.2		44.5		16-Sep-07		22:06:20		71		52.5		16-Sep-07		22:07:53		72.21		49.5		27-Oct-07		22:25:59		71.6		44

		17-Sep-07		0:07:10		75.2		43		17-Sep-07		0:06:20		71		51.5		17-Sep-07		0:07:53		71.6		49		28-Oct-07		0:25:59		70.41		43.5

		17-Sep-07		2:07:10		74.6		42.5		17-Sep-07		2:06:20		70.41		49.5		17-Sep-07		2:07:53		70.41		48.5		28-Oct-07		2:25:59		69.2		42.5

		17-Sep-07		4:07:10		74.01		41.5		17-Sep-07		4:06:20		70.41		47		17-Sep-07		4:07:53		69.8		48		28-Oct-07		4:25:59		68.61		42

		17-Sep-07		6:07:10		73.4		41.5		17-Sep-07		6:06:20		69.8		42		17-Sep-07		6:07:53		69.2		49		28-Oct-07		6:25:59		68.61		41.5

		17-Sep-07		8:07:10		72.21		44.5		17-Sep-07		8:06:20		68		52.5		17-Sep-07		8:07:53		69.2		50		28-Oct-07		8:25:59		68		42

		17-Sep-07		10:07:10		72.8		47.5		17-Sep-07		10:06:20		68.61		57.5		17-Sep-07		10:07:53		70.41		49.5		28-Oct-07		10:25:59		67.4		44.5

		17-Sep-07		12:07:10		72.8		50.5		17-Sep-07		12:06:20		68.61		61		17-Sep-07		12:07:53		71		49.5		28-Oct-07		12:25:59		68.61		45.5

		17-Sep-07		14:07:10		74.01		45.5		17-Sep-07		14:06:20		69.2		52		17-Sep-07		14:07:53		71		57		28-Oct-07		14:25:59		69.8		46

		17-Sep-07		16:07:10		74.6		49.5		17-Sep-07		16:06:20		68.61		58		17-Sep-07		16:07:53		71		51.5		28-Oct-07		16:25:59		71.6		47

		17-Sep-07		18:07:10		74.6		48.5		17-Sep-07		18:06:20		68.61		61.5		17-Sep-07		18:07:53		71		50		28-Oct-07		18:25:59		71.6		45

		17-Sep-07		20:07:10		75.81		46		17-Sep-07		20:06:20		71		55		17-Sep-07		20:07:53		74.01		48		28-Oct-07		20:25:59		70.41		45

		17-Sep-07		22:07:10		75.81		44		17-Sep-07		22:06:20		71.6		52		17-Sep-07		22:07:53		74.6		46.5		28-Oct-07		22:25:59		69.8		44.5

		18-Sep-07		0:07:10		75.2		42.5		18-Sep-07		0:06:20		71		50		18-Sep-07		0:07:53		73.4		45.5		29-Oct-07		0:25:59		69.2		44

		18-Sep-07		2:07:10		75.2		41.5		18-Sep-07		2:06:20		71.6		48		18-Sep-07		2:07:53		72.21		45.5		29-Oct-07		2:25:59		68.61		44

		18-Sep-07		4:07:10		74.6		40.5		18-Sep-07		4:06:20		71		46.5		18-Sep-07		4:07:53		71		45.5		29-Oct-07		4:25:59		68.61		44

		18-Sep-07		6:07:10		74.6		39.5		18-Sep-07		6:06:20		69.8		45		18-Sep-07		6:07:53		70.41		45.5		29-Oct-07		6:25:59		68		43.5

		18-Sep-07		8:07:10		72.8		40		18-Sep-07		8:06:20		69.2		39.5		18-Sep-07		8:07:53		71		44.5		29-Oct-07		8:25:59		67.4		43

		18-Sep-07		10:07:10		73.4		42.5		18-Sep-07		10:06:20		70.41		46.5		18-Sep-07		10:07:53		71.6		42.5		29-Oct-07		10:25:59		68.61		45.5

		18-Sep-07		12:07:10		73.4		44.5		18-Sep-07		12:06:20		69.8		51		18-Sep-07		12:07:53		72.21		43.5		29-Oct-07		12:25:59		70.41		46.5

		18-Sep-07		14:07:10		73.4		42.5		18-Sep-07		14:06:20		69.8		42		18-Sep-07		14:07:53		71.6		43.5		29-Oct-07		14:25:59		72.21		47.5

		18-Sep-07		16:07:10		74.01		47.5		18-Sep-07		16:06:20		69.2		61		18-Sep-07		16:07:53		71		49.5		29-Oct-07		16:25:59		74.6		47.5

		18-Sep-07		18:07:10		74.01		43.5		18-Sep-07		18:06:20		69.2		49.5		18-Sep-07		18:07:53		71		43		29-Oct-07		18:25:59		75.2		47

		18-Sep-07		20:07:10		74.6		44		18-Sep-07		20:06:20		71.6		50		18-Sep-07		20:07:53		71.6		51.5		29-Oct-07		20:25:59		74.01		46

		18-Sep-07		22:07:10		75.2		42.5		18-Sep-07		22:06:20		71.6		50.5		18-Sep-07		22:07:53		73.4		46		29-Oct-07		22:25:59		72.8		46

		19-Sep-07		0:07:10		75.2		42.5		19-Sep-07		0:06:20		71		49.5		19-Sep-07		0:07:53		73.4		44.5		30-Oct-07		0:25:59		71.6		46

		19-Sep-07		2:07:10		74.6		41		19-Sep-07		2:06:20		71		48		19-Sep-07		2:07:53		72.8		44		30-Oct-07		2:25:59		71		46

		19-Sep-07		4:07:10		74.6		40		19-Sep-07		4:06:20		71		46		19-Sep-07		4:07:53		71		44		30-Oct-07		4:25:59		69.8		45.5

		19-Sep-07		6:07:10		74.01		38.5		19-Sep-07		6:06:20		70.41		41.5		19-Sep-07		6:07:53		70.41		43.5		30-Oct-07		6:25:59		69.8		46

		19-Sep-07		8:07:10		72.8		41		19-Sep-07		8:06:20		69.8		48		19-Sep-07		8:07:53		71		42.5		30-Oct-07		8:25:59		69.2		48

		19-Sep-07		10:07:10		72.8		43.5		19-Sep-07		10:06:20		70.41		51.5		19-Sep-07		10:07:53		71.6		45.5		30-Oct-07		10:25:59		71		48

		19-Sep-07		12:07:10		73.4		45.5		19-Sep-07		12:06:20		70.41		56		19-Sep-07		12:07:53		72.21		53		30-Oct-07		12:25:59		72.8		49

		19-Sep-07		14:07:10		74.6		43.5		19-Sep-07		14:06:20		72.21		49		19-Sep-07		14:07:53		71.6		41		30-Oct-07		14:25:59		74.6		48

		19-Sep-07		16:07:10		73.4		42.5		19-Sep-07		16:06:20		68.61		45		19-Sep-07		16:07:53		72.21		48		30-Oct-07		16:25:59		75.2		47.5

		19-Sep-07		18:07:10		73.4		42		19-Sep-07		18:06:20		68.61		43		19-Sep-07		18:07:53		71		50		30-Oct-07		18:25:59		75.2		45

		19-Sep-07		20:07:10		74.6		42		19-Sep-07		20:06:20		70.41		49		19-Sep-07		20:07:53		71		47.5		30-Oct-07		20:25:59		72.8		45.5

		19-Sep-07		22:07:10		74.6		39.5		19-Sep-07		22:06:20		70.41		46.5		19-Sep-07		22:07:53		72.21		42.5		30-Oct-07		22:25:59		71.6		46.5

		20-Sep-07		0:07:10		74.6		38		20-Sep-07		0:06:20		70.41		44		20-Sep-07		0:07:53		71.6		41		31-Oct-07		0:25:59		71		46.5

		20-Sep-07		2:07:10		74.01		37		20-Sep-07		2:06:20		70.41		42		20-Sep-07		2:07:53		71		40.5		31-Oct-07		2:25:59		70.41		47.5

		20-Sep-07		4:07:10		73.4		36		20-Sep-07		4:06:20		70.41		41		20-Sep-07		4:07:53		69.8		40.5		31-Oct-07		4:25:59		70.41		48

		20-Sep-07		6:07:10		72.8		36		20-Sep-07		6:06:20		69.8		40		20-Sep-07		6:07:53		69.8		40		31-Oct-07		6:25:59		70.41		48.5

		20-Sep-07		8:07:10		72.8		37.5		20-Sep-07		8:06:20		69.8		44		20-Sep-07		8:07:53		71		39.5		31-Oct-07		8:25:59		69.8		48

		20-Sep-07		10:07:10		73.4		37.5		20-Sep-07		10:06:20		70.41		45.5		20-Sep-07		10:07:53		71.6		35.5		31-Oct-07		10:25:59		71.6		48

		20-Sep-07		12:07:10		73.4		36		20-Sep-07		12:06:20		69.2		35.5		20-Sep-07		12:07:53		72.21		34.5		31-Oct-07		12:25:59		72.21		47.5

		20-Sep-07		14:07:10		73.4		34		20-Sep-07		14:06:20		69.8		36		20-Sep-07		14:07:53		71.6		39.5		31-Oct-07		14:25:59		73.4		46.5

		20-Sep-07		16:07:10		73.4		34		20-Sep-07		16:06:20		68.61		37.5		20-Sep-07		16:07:53		71		33		31-Oct-07		16:25:59		74.6		46

		20-Sep-07		18:07:10		74.01		34.5		20-Sep-07		18:06:20		68		41.5		20-Sep-07		18:07:53		70.41		38.5		31-Oct-07		18:25:59		75.2		44.5

		20-Sep-07		20:07:10		74.6		36		20-Sep-07		20:06:20		69.8		41		20-Sep-07		20:07:53		72.8		37.5		31-Oct-07		20:25:59		72.8		44.5

		20-Sep-07		22:07:10		74.6		34		20-Sep-07		22:06:20		70.41		39.5		20-Sep-07		22:07:53		72.21		36.5		31-Oct-07		22:25:59		72.21		45.5

		21-Sep-07		0:07:10		74.01		34.5		21-Sep-07		0:06:20		69.8		40.5		21-Sep-07		0:07:53		71.6		37.5		1-Nov-07		0:25:59		70.41		46

		21-Sep-07		2:07:10		74.01		33.5		21-Sep-07		2:06:20		70.41		36		21-Sep-07		2:07:53		71		37		1-Nov-07		2:25:59		69.8		47

		21-Sep-07		4:07:10		73.4		33		21-Sep-07		4:06:20		70.41		38		21-Sep-07		4:07:53		69.8		37		1-Nov-07		4:25:59		69.8		48

		21-Sep-07		6:07:10		73.4		34.5		21-Sep-07		6:06:20		69.8		39.5		21-Sep-07		6:07:53		69.8		39		1-Nov-07		6:25:59		69.8		48.5

		21-Sep-07		8:07:10		72.8		37.5		21-Sep-07		8:06:20		69.8		44.5		21-Sep-07		8:07:53		71		39		1-Nov-07		8:25:59		69.8		48.5

		21-Sep-07		10:07:10		72.8		38.5		21-Sep-07		10:06:20		69.8		41.5		21-Sep-07		10:07:53		71.6		42		1-Nov-07		10:25:59		72.21		48

		21-Sep-07		12:07:10		74.6		37		21-Sep-07		12:06:20		73.4		36		21-Sep-07		12:07:53		71.6		36.5		1-Nov-07		12:25:59		72.8		48.5

		21-Sep-07		14:07:10		74.6		38.5		21-Sep-07		14:06:20		71.6		45		21-Sep-07		14:07:53		71		41.5		1-Nov-07		14:25:59		73.4		48.5

		21-Sep-07		16:07:10		74.6		38		21-Sep-07		16:06:20		70.41		45.5		21-Sep-07		16:07:53		71		41		1-Nov-07		16:25:59		74.01		49.5

		21-Sep-07		18:07:10		74.6		37.5		21-Sep-07		18:06:20		70.41		44		21-Sep-07		18:07:53		71		40.5		1-Nov-07		18:25:59		74.01		48

		21-Sep-07		20:07:10		75.81		35		21-Sep-07		20:06:20		72.21		39		21-Sep-07		20:07:53		71.6		39		1-Nov-07		20:25:59		72.21		48

		21-Sep-07		22:07:10		75.81		33.5		21-Sep-07		22:06:20		72.8		37.5		21-Sep-07		22:07:53		71		38		1-Nov-07		22:25:59		71.6		49

		22-Sep-07		0:07:10		75.2		33		22-Sep-07		0:06:20		72.21		37		22-Sep-07		0:07:53		70.41		38.5		2-Nov-07		0:25:59		71		49

		22-Sep-07		2:07:10		74.6		32.5		22-Sep-07		2:06:20		71.6		36.5		22-Sep-07		2:07:53		68.61		38.5		2-Nov-07		2:25:59		70.41		49.5

		22-Sep-07		4:07:10		73.4		33		22-Sep-07		4:06:20		70.41		37.5		22-Sep-07		4:07:53		68		39.5		2-Nov-07		4:25:59		69.8		49

		22-Sep-07		6:07:10		72.8		33.5		22-Sep-07		6:06:20		69.8		37.5		22-Sep-07		6:07:53		67.4		40.5		2-Nov-07		6:25:59		69.8		48

		22-Sep-07		8:07:10		72.8		33.5		22-Sep-07		8:06:20		71.6		37.5		22-Sep-07		8:07:53		69.2		40		2-Nov-07		8:25:59		71.6		46.5

		22-Sep-07		10:07:10		73.4		36		22-Sep-07		10:06:20		72.21		39		22-Sep-07		10:07:53		71.6		43.5		2-Nov-07		10:25:59		71.6		48

		22-Sep-07		12:07:10		73.4		36.5		22-Sep-07		12:06:20		71.6		40.5		22-Sep-07		12:07:53		71.6		44.5		2-Nov-07		12:25:59		73.4		48

		22-Sep-07		14:07:10		74.01		38		22-Sep-07		14:06:20		71		40.5		22-Sep-07		14:07:53		72.21		43		2-Nov-07		14:25:59		75.2		48

		22-Sep-07		16:07:10		74.6		40.5		22-Sep-07		16:06:20		70.41		47		22-Sep-07		16:07:53		71.6		47		2-Nov-07		16:25:59		75.2		49.5

		22-Sep-07		18:07:10		74.6		38.5		22-Sep-07		18:06:20		70.41		45		22-Sep-07		18:07:53		71		38.5		2-Nov-07		18:25:59		75.2		50

		22-Sep-07		20:07:10		75.2		37.5		22-Sep-07		20:06:20		72.21		42		22-Sep-07		20:07:53		70.41		44		2-Nov-07		20:25:59		74.6		46

		22-Sep-07		22:07:10		75.81		37.5		22-Sep-07		22:06:20		72.8		42.5		22-Sep-07		22:07:53		71.6		43		2-Nov-07		22:25:59		73.4		45.5

		23-Sep-07		0:07:10		75.81		38.5		23-Sep-07		0:06:20		73.4		43.5		23-Sep-07		0:07:53		71.6		44.5		3-Nov-07		0:25:59		71.6		45

		23-Sep-07		2:07:10		75.2		40		23-Sep-07		2:06:20		72.21		46.5		23-Sep-07		2:07:53		71		46.5		3-Nov-07		2:25:59		69.8		44

		23-Sep-07		4:07:10		75.2		41		23-Sep-07		4:06:20		72.8		46		23-Sep-07		4:07:53		71		47.5		3-Nov-07		4:25:59		69.2		43

		23-Sep-07		6:07:10		74.6		42		23-Sep-07		6:06:20		71.6		44		23-Sep-07		6:07:53		71.6		48		3-Nov-07		6:25:59		69.2		42

		23-Sep-07		8:07:10		74.01		44.5		23-Sep-07		8:06:20		69.8		52		23-Sep-07		8:07:53		71		43.5		3-Nov-07		8:25:59		71.6		39.5

		23-Sep-07		10:07:10		73.4		44.5		23-Sep-07		10:06:20		70.41		50.5		23-Sep-07		10:07:53		71.6		56		3-Nov-07		10:25:59		71.6		42.5

		23-Sep-07		12:07:10		74.01		44.5		23-Sep-07		12:06:20		70.41		48		23-Sep-07		12:07:53		71		49		3-Nov-07		12:25:59		75.2		42.5

		23-Sep-07		14:07:10		73.4		48.5		23-Sep-07		14:06:20		70.41		56.5		23-Sep-07		14:07:53		71		54		3-Nov-07		14:25:59		76.4		42.5

		23-Sep-07		16:07:10		74.01		50.5		23-Sep-07		16:06:20		70.41		60		23-Sep-07		16:07:53		70.41		51		3-Nov-07		16:25:59		75.81		42

		23-Sep-07		18:07:10		73.4		50.5		23-Sep-07		18:06:20		70.41		59		23-Sep-07		18:07:53		69.8		56.5		3-Nov-07		18:25:59		75.81		43.5

		23-Sep-07		20:07:10		74.6		49.5		23-Sep-07		20:06:20		72.21		55		23-Sep-07		20:07:53		69.8		56		3-Nov-07		20:25:59		74.6		43

		23-Sep-07		22:07:10		74.6		48		23-Sep-07		22:06:20		72.21		52.5		23-Sep-07		22:07:53		70.41		55.5		3-Nov-07		22:25:59		73.4		43.5

		24-Sep-07		0:07:10		74.6		47.5		24-Sep-07		0:06:20		72.21		52		24-Sep-07		0:07:53		69.8		54.5		4-Nov-07		0:25:59		71.6		43

		24-Sep-07		2:07:10		74.6		47.5		24-Sep-07		2:06:20		72.21		52		24-Sep-07		2:07:53		69.8		55		4-Nov-07		2:25:59		70.41		42

		24-Sep-07		4:07:10		74.6		47		24-Sep-07		4:06:20		72.21		51.5		24-Sep-07		4:07:53		69.8		54.5		4-Nov-07		4:25:59		69.2		41

		24-Sep-07		6:07:10		74.01		46.5		24-Sep-07		6:06:20		71.6		46		24-Sep-07		6:07:53		69.8		54.5		4-Nov-07		6:25:59		68.61		40

		24-Sep-07		8:07:10		73.4		49		24-Sep-07		8:06:20		70.41		56		24-Sep-07		8:07:53		69.2		55		4-Nov-07		8:25:59		67.4		38.5

		24-Sep-07		10:07:10		72.8		50.5		24-Sep-07		10:06:20		69.8		56.5		24-Sep-07		10:07:53		69.8		55.5		4-Nov-07		10:25:59		68		40.5

		24-Sep-07		12:07:10		72.8		51		24-Sep-07		12:06:20		69.2		55.5		24-Sep-07		12:07:53		69.8		56		4-Nov-07		12:25:59		69.2		42.5

		24-Sep-07		14:07:10		73.4		50		24-Sep-07		14:06:20		69.8		56.5		24-Sep-07		14:07:53		70.41		51.5		4-Nov-07		14:25:59		71		43

		24-Sep-07		16:07:10		74.01		46		24-Sep-07		16:06:20		69.8		44		24-Sep-07		16:07:53		70.41		48		4-Nov-07		16:25:59		72.21		43

		24-Sep-07		18:07:10		74.01		45		24-Sep-07		18:06:20		69.8		51		24-Sep-07		18:07:53		71		46.5		4-Nov-07		18:25:59		72.8		41.5

		24-Sep-07		20:07:10		75.2		40		24-Sep-07		20:06:20		72.8		39.5		24-Sep-07		20:07:53		72.21		45		4-Nov-07		20:25:59		71.6		39

		24-Sep-07		22:07:10		75.81		40		24-Sep-07		22:06:20		73.4		43.5		24-Sep-07		22:07:53		71.6		45.5		4-Nov-07		22:25:59		70.41		39.5

		25-Sep-07		0:07:10		74.6		39		25-Sep-07		0:06:20		72.21		43		25-Sep-07		0:07:53		70.41		45		5-Nov-07		0:25:59		69.8		40

		25-Sep-07		2:07:10		74.01		37.5		25-Sep-07		2:06:20		71.6		41		25-Sep-07		2:07:53		69.2		44		5-Nov-07		2:25:59		68.61		40

		25-Sep-07		4:07:10		73.4		37		25-Sep-07		4:06:20		71		40		25-Sep-07		4:07:53		68		43		5-Nov-07		4:25:59		68		39

		25-Sep-07		6:07:10		72.8		36.5		25-Sep-07		6:06:20		69.8		38.5		25-Sep-07		6:07:53		68.61		42		5-Nov-07		6:25:59		67.4		38.5

		25-Sep-07		8:07:10		72.8		37		25-Sep-07		8:06:20		71		41		25-Sep-07		8:07:53		69.2		41		5-Nov-07		8:25:59		66.2		37.5

		25-Sep-07		10:07:10		74.01		38		25-Sep-07		10:06:20		72.21		40		25-Sep-07		10:07:53		71		48		5-Nov-07		10:25:59		67.4		39.5

		25-Sep-07		12:07:10		74.6		39		25-Sep-07		12:06:20		71.6		43		25-Sep-07		12:07:53		71.6		43		5-Nov-07		12:25:59		69.2		40.5

		25-Sep-07		14:07:10		74.01		34.5		25-Sep-07		14:06:20		71.6		37.5		25-Sep-07		14:07:53		71.6		35		5-Nov-07		14:25:59		71		41.5

		25-Sep-07		16:07:10		74.6		36.5		25-Sep-07		16:06:20		70.41		40.5		25-Sep-07		16:07:53		72.21		39		5-Nov-07		16:25:59		72.21		41.5

		25-Sep-07		18:07:10		74.01		33.5		25-Sep-07		18:06:20		70.41		36		25-Sep-07		18:07:53		71.6		37		5-Nov-07		18:25:59		72.8		41

		25-Sep-07		20:07:10		75.81		36.5		25-Sep-07		20:06:20		72.8		40.5		25-Sep-07		20:07:53		71		42.5		5-Nov-07		20:25:59		71.6		42.5

		25-Sep-07		22:07:10		75.81		36		25-Sep-07		22:06:20		72.8		40		25-Sep-07		22:07:53		72.8		40		5-Nov-07		22:25:59		71		43

		26-Sep-07		0:07:10		75.81		35		26-Sep-07		0:06:20		72.8		39		26-Sep-07		0:07:53		71.6		40		6-Nov-07		0:25:59		69.8		42

		26-Sep-07		2:07:10		75.2		34.5		26-Sep-07		2:06:20		72.21		39		26-Sep-07		2:07:53		69.8		40		6-Nov-07		2:25:59		69.2		41.5

		26-Sep-07		4:07:10		74.01		34		26-Sep-07		4:06:20		71		38		26-Sep-07		4:07:53		68.61		40		6-Nov-07		4:25:59		68		40.5

		26-Sep-07		6:07:10		72.8		33.5		26-Sep-07		6:06:20		70.41		36		26-Sep-07		6:07:53		68.61		39.5		6-Nov-07		6:25:59		68		39.5

		26-Sep-07		8:07:10		73.4		33		26-Sep-07		8:06:20		71.6		36.5		26-Sep-07		8:07:53		70.41		37.5		6-Nov-07		8:25:59		69.8		37

		26-Sep-07		10:07:10		74.01		37		26-Sep-07		10:06:20		71.6		38.5		26-Sep-07		10:07:53		71.6		34.5		6-Nov-07		10:25:59		71		39.5

		26-Sep-07		12:07:10		74.6		34.5		26-Sep-07		12:06:20		71.6		36		26-Sep-07		12:07:53		71.6		35.5		6-Nov-07		12:25:59		73.4		39.5

		26-Sep-07		14:07:10		74.6		33		26-Sep-07		14:06:20		71.6		35.5		26-Sep-07		14:07:53		71.6		34		6-Nov-07		14:25:59		75.2		39.5

		26-Sep-07		16:07:10		75.2		32.5		26-Sep-07		16:06:20		71		35.5		26-Sep-07		16:07:53		71.6		34.5		6-Nov-07		16:25:59		75.81		42.5

		26-Sep-07		18:07:10		74.6		31		26-Sep-07		18:06:20		69.8		34.5		26-Sep-07		18:07:53		71		34.5		6-Nov-07		18:25:59		75.2		41.5

		26-Sep-07		20:07:10		75.81		32		26-Sep-07		20:06:20		72.8		35.5		26-Sep-07		20:07:53		71		33.5		6-Nov-07		20:25:59		72.8		41

		26-Sep-07		22:07:10		76.4		31		26-Sep-07		22:06:20		72.8		35.5		26-Sep-07		22:07:53		73.4		34.5		6-Nov-07		22:25:59		71.6		42

		27-Sep-07		0:07:10		76.4		31		27-Sep-07		0:06:20		72.8		35.5		27-Sep-07		0:07:53		72.8		34.5		7-Nov-07		0:25:59		71		43

		27-Sep-07		2:07:10		75.81		30.5		27-Sep-07		2:06:20		72.21		35		27-Sep-07		2:07:53		71.6		34.5		7-Nov-07		2:25:59		69.8		43

		27-Sep-07		4:07:10		75.2		30		27-Sep-07		4:06:20		72.21		34		27-Sep-07		4:07:53		70.41		35		7-Nov-07		4:25:59		69.2		43.5

		27-Sep-07		6:07:10		75.2		30.5		27-Sep-07		6:06:20		72.21		33		27-Sep-07		6:07:53		70.41		35.5		7-Nov-07		6:25:59		69.2		44

		27-Sep-07		8:07:10		74.6		31.5		27-Sep-07		8:06:20		71.6		35		27-Sep-07		8:07:53		71.6		33		7-Nov-07		8:25:59		71		43

		27-Sep-07		10:07:10		74.6		32		27-Sep-07		10:06:20		72.21		37.5		27-Sep-07		10:07:53		71.6		36.5		7-Nov-07		10:25:59		71.6		42.5

		27-Sep-07		12:07:10		74.6		34		27-Sep-07		12:06:20		71.6		37		27-Sep-07		12:07:53		72.21		39		7-Nov-07		12:25:59		72.8		42

		27-Sep-07		14:07:10		74.6		34		27-Sep-07		14:06:20		71		35.5		27-Sep-07		14:07:53		72.21		34		7-Nov-07		14:25:59		74.01		42.5

		27-Sep-07		16:07:10		75.2		33		27-Sep-07		16:06:20		70.41		37.5		27-Sep-07		16:07:53		71.6		34.5		7-Nov-07		16:25:59		74.6		44

		27-Sep-07		18:07:10		75.2		32.5		27-Sep-07		18:06:20		71		36		27-Sep-07		18:07:53		71.6		35.5		7-Nov-07		18:25:59		74.6		43

		27-Sep-07		20:07:10		76.4		30.5		27-Sep-07		20:06:20		72.8		33.5		27-Sep-07		20:07:53		74.6		31.5		7-Nov-07		20:25:59		72.21		42.5

		27-Sep-07		22:07:10		76.4		30.5		27-Sep-07		22:06:20		72.8		34.5		27-Sep-07		22:07:53		75.2		32		7-Nov-07		22:25:59		71.6		42

		28-Sep-07		0:07:10		76.4		30		28-Sep-07		0:06:20		72.8		34.5		28-Sep-07		0:07:53		74.6		32.5		8-Nov-07		0:25:59		69.8		42.5

		28-Sep-07		2:07:10		75.81		29.5		28-Sep-07		2:06:20		72.8		33		28-Sep-07		2:07:53		72.8		33		8-Nov-07		2:25:59		69.2		43

		28-Sep-07		4:07:10		75.2		30		28-Sep-07		4:06:20		72.8		34		28-Sep-07		4:07:53		71.6		34		8-Nov-07		4:25:59		68.61		42.5

		28-Sep-07		6:07:10		75.2		30.5		28-Sep-07		6:06:20		72.8		32.5		28-Sep-07		6:07:53		70.41		35		8-Nov-07		6:25:59		68.61		43

		28-Sep-07		8:07:10		74.6		31.5		28-Sep-07		8:06:20		71		37		28-Sep-07		8:07:53		71.6		31.5		8-Nov-07		8:25:59		71.6		40.5

		28-Sep-07		10:07:10		74.6		32.5		28-Sep-07		10:06:20		71.6		39		28-Sep-07		10:07:53		71.6		38.5		8-Nov-07		10:25:59		71		41.5

		28-Sep-07		12:07:10		74.6		33		28-Sep-07		12:06:20		71.6		36.5		28-Sep-07		12:07:53		72.21		34.5		8-Nov-07		12:25:59		72.8		43.5

		28-Sep-07		14:07:10		74.01		36		28-Sep-07		14:06:20		71		36		28-Sep-07		14:07:53		71.6		40		8-Nov-07		14:25:59		74.01		42.5

		28-Sep-07		16:07:10		75.2		37.5		28-Sep-07		16:06:20		71		44		28-Sep-07		16:07:53		71.6		41.5		8-Nov-07		16:25:59		75.2		43.5

		28-Sep-07		18:07:10		74.6		39		28-Sep-07		18:06:20		70.41		46.5		28-Sep-07		18:07:53		71		45		8-Nov-07		18:25:59		74.01		43

		28-Sep-07		20:07:10		75.81		37		28-Sep-07		20:06:20		72.8		42		28-Sep-07		20:07:53		71.6		42		8-Nov-07		20:25:59		72.21		43.5

		28-Sep-07		22:07:10		75.81		36.5		28-Sep-07		22:06:20		72.8		42		28-Sep-07		22:07:53		72.21		41		8-Nov-07		22:25:59		72.21		45.5

		29-Sep-07		0:07:10		75.2		36.5		29-Sep-07		0:06:20		72.21		42		29-Sep-07		0:07:53		71.6		42		9-Nov-07		0:25:59		71		44.5

		29-Sep-07		2:07:10		75.2		37		29-Sep-07		2:06:20		72.8		42		29-Sep-07		2:07:53		71		42.5		9-Nov-07		2:25:59		69.8		44.5

		29-Sep-07		4:07:10		75.2		37		29-Sep-07		4:06:20		72.8		41		29-Sep-07		4:07:53		71		42.5		9-Nov-07		4:25:59		69.2		45

		29-Sep-07		6:07:10		75.2		35		29-Sep-07		6:06:20		72.8		35		29-Sep-07		6:07:53		69.8		45.5		9-Nov-07		6:25:59		69.2		46.5

		29-Sep-07		8:07:10		74.6		39		29-Sep-07		8:06:20		71.6		42		29-Sep-07		8:07:53		71		45.5		9-Nov-07		8:25:59		71		45

		29-Sep-07		10:07:10		74.01		40.5		29-Sep-07		10:06:20		71		42		29-Sep-07		10:07:53		71.6		46		9-Nov-07		10:25:59		71		46

		29-Sep-07		12:07:10		74.6		39		29-Sep-07		12:06:20		71.6		38.5		29-Sep-07		12:07:53		71.6		48.5		9-Nov-07		12:25:59		72.21		47

		29-Sep-07		14:07:10		74.01		45		29-Sep-07		14:06:20		71.6		54		29-Sep-07		14:07:53		71.6		47		9-Nov-07		14:25:59		74.01		44.5

		29-Sep-07		16:07:10		74.6		42		29-Sep-07		16:06:20		71.6		48.5		29-Sep-07		16:07:53		71.6		52		9-Nov-07		16:25:59		74.01		44.5

		29-Sep-07		18:07:10		74.6		43.5		29-Sep-07		18:06:20		70.41		53		29-Sep-07		18:07:53		71		52		9-Nov-07		18:25:59		74.01		43.5

		29-Sep-07		20:07:10		75.2		36		29-Sep-07		20:06:20		72.21		38		29-Sep-07		20:07:53		70.41		42		9-Nov-07		20:25:59		73.4		43

		29-Sep-07		22:07:10		75.2		32.5		29-Sep-07		22:06:20		72.8		35		29-Sep-07		22:07:53		71		36.5		9-Nov-07		22:25:59		72.21		45

		30-Sep-07		0:07:10		75.2		31		30-Sep-07		0:06:20		73.4		33.5		30-Sep-07		0:07:53		70.41		35.5		10-Nov-07		0:25:59		71		45

		30-Sep-07		2:07:10		74.6		30.5		30-Sep-07		2:06:20		72.8		32.5		30-Sep-07		2:07:53		69.8		34.5		10-Nov-07		2:25:59		69.8		45.5

		30-Sep-07		4:07:10		74.01		30		30-Sep-07		4:06:20		71.6		32.5		30-Sep-07		4:07:53		68.61		34.5		10-Nov-07		4:25:59		69.2		46

		30-Sep-07		6:07:10		73.4		29.5		30-Sep-07		6:06:20		72.21		32.5		30-Sep-07		6:07:53		68		34.5		10-Nov-07		6:25:59		69.2		45.5

		30-Sep-07		8:07:10		72.21		30.5		30-Sep-07		8:06:20		71		34		30-Sep-07		8:07:53		68		34.5		10-Nov-07		8:25:59		71		42.5

		30-Sep-07		10:07:10		72.8		31		30-Sep-07		10:06:20		71.6		34.5		30-Sep-07		10:07:53		70.41		34.5		10-Nov-07		10:25:59		73.4		43

		30-Sep-07		12:07:10		73.4		31		30-Sep-07		12:06:20		71		33.5		30-Sep-07		12:07:53		70.41		32		10-Nov-07		12:25:59		74.01		43

		30-Sep-07		14:07:10		73.4		29		30-Sep-07		14:06:20		70.41		31.5		30-Sep-07		14:07:53		71		31		10-Nov-07		14:25:59		74.6		42

		30-Sep-07		16:07:10		74.01		30		30-Sep-07		16:06:20		69.8		34.5		30-Sep-07		16:07:53		71		31		10-Nov-07		16:25:59		75.2		43

		30-Sep-07		18:07:10		74.01		29		30-Sep-07		18:06:20		69.8		32.5		30-Sep-07		18:07:53		71		31		10-Nov-07		18:25:59		74.6		44

		30-Sep-07		20:07:10		75.2		28		30-Sep-07		20:06:20		72.21		31		30-Sep-07		20:07:53		71.6		32		10-Nov-07		20:25:59		72.8		44.5

		30-Sep-07		22:07:10		75.81		27.5		30-Sep-07		22:06:20		72.8		31		30-Sep-07		22:07:53		71.6		31.5		10-Nov-07		22:25:59		72.21		45.5

		1-Oct-07		0:07:10		75.2		27		1-Oct-07		0:06:20		72.8		30		1-Oct-07		0:07:53		70.41		32		11-Nov-07		0:25:59		70.41		44

		1-Oct-07		2:07:10		74.01		27.5		1-Oct-07		2:06:20		71.6		30.5		1-Oct-07		2:07:53		68.61		32		11-Nov-07		2:25:59		69.2		43

		1-Oct-07		4:07:10		72.8		27.5		1-Oct-07		4:06:20		70.41		30.5		1-Oct-07		4:07:53		68		32.5		11-Nov-07		4:25:59		68.61		43

		1-Oct-07		6:07:10		72.21		27.5		1-Oct-07		6:06:20		69.8		30		1-Oct-07		6:07:53		66.2		33		11-Nov-07		6:25:59		68		43.5

		1-Oct-07		8:07:10		71		28.5		1-Oct-07		8:06:20		68.61		31.5		1-Oct-07		8:07:53		68		32		11-Nov-07		8:25:59		68		44.5

		1-Oct-07		10:07:10		71.6		30		1-Oct-07		10:06:20		69.8		31.5		1-Oct-07		10:07:53		68.61		33.5		11-Nov-07		10:25:59		69.2		46.5

		1-Oct-07		12:07:10		72.21		30		1-Oct-07		12:06:20		70.41		32		1-Oct-07		12:07:53		70.41		33.5		11-Nov-07		12:25:59		69.2		49

		1-Oct-07		14:07:10		73.4		28.5		1-Oct-07		14:06:20		69.8		30		1-Oct-07		14:07:53		70.41		31.5		11-Nov-07		14:25:59		69.8		50.5

		1-Oct-07		16:07:10		73.4		27		1-Oct-07		16:06:20		69.8		29.5		1-Oct-07		16:07:53		70.41		30.5		11-Nov-07		16:25:59		69.8		52

		1-Oct-07		18:07:10		74.01		30		1-Oct-07		18:06:20		69.8		35.5		1-Oct-07		18:07:53		71		32		11-Nov-07		18:25:59		69.8		53

		1-Oct-07		20:07:10		75.81		33		1-Oct-07		20:06:20		72.8		38		1-Oct-07		20:07:53		72.21		37.5		11-Nov-07		20:25:59		69.2		54

		1-Oct-07		22:07:10		75.2		35.5		1-Oct-07		22:06:20		72.21		41		1-Oct-07		22:07:53		72.21		39.5		11-Nov-07		22:25:59		69.2		55

		2-Oct-07		0:07:10		75.2		35.5		2-Oct-07		0:06:20		72.8		41		2-Oct-07		0:07:53		71.6		41		12-Nov-07		0:25:59		69.2		55.5

		2-Oct-07		2:07:10		75.2		36.5		2-Oct-07		2:06:20		72.8		41		2-Oct-07		2:07:53		71		42.5		12-Nov-07		2:25:59		69.2		55.5

		2-Oct-07		4:07:10		75.2		40		2-Oct-07		4:06:20		72.8		46		2-Oct-07		4:07:53		71		46.5		12-Nov-07		4:25:59		69.2		54

		2-Oct-07		6:07:10		75.2		39		2-Oct-07		6:06:20		72.8		41		2-Oct-07		6:07:53		70.41		53.5		12-Nov-07		6:25:59		68.61		50.5

		2-Oct-07		8:07:10		74.6		44.5		2-Oct-07		8:06:20		71.6		46.5		2-Oct-07		8:07:53		71		51.5		12-Nov-07		8:25:59		68		47.5

		2-Oct-07		10:07:10		74.6		40.5		2-Oct-07		10:06:20		71.6		44.5		2-Oct-07		10:07:53		72.21		41		12-Nov-07		10:25:59		68		47.5

		2-Oct-07		12:07:10		74.6		44.5		2-Oct-07		12:06:20		71		47.5		2-Oct-07		12:07:53		72.21		51.5		12-Nov-07		12:25:59		69.2		46

		2-Oct-07		14:07:10		74.6		42		2-Oct-07		14:06:20		71.6		51		2-Oct-07		14:07:53		71.6		50		12-Nov-07		14:25:59		70.41		44

		2-Oct-07		16:07:10		75.2		38.5		2-Oct-07		16:06:20		71.6		46		2-Oct-07		16:07:53		71		46		12-Nov-07		16:25:59		71		42.5

		2-Oct-07		18:07:10		74.6		34		2-Oct-07		18:06:20		71		39.5		2-Oct-07		18:07:53		71		36		12-Nov-07		18:25:59		71		42.5

		2-Oct-07		20:07:10		75.81		37		2-Oct-07		20:06:20		72.8		41.5		2-Oct-07		20:07:53		70.41		44.5		12-Nov-07		20:25:59		69.8		42.5

		2-Oct-07		22:07:10		76.4		36.5		2-Oct-07		22:06:20		72.8		41.5		2-Oct-07		22:07:53		72.8		41		12-Nov-07		22:25:59		68.61		43

		3-Oct-07		0:07:10		75.81		35.5		3-Oct-07		0:06:20		72.8		40		3-Oct-07		0:07:53		72.21		40		13-Nov-07		0:25:59		68		42.5

		3-Oct-07		2:07:10		75.81		34.5		3-Oct-07		2:06:20		72.8		38		3-Oct-07		2:07:53		71		39.5		13-Nov-07		2:25:59		67.4		42.5

		3-Oct-07		4:07:10		74.6		34.5		3-Oct-07		4:06:20		71.6		38.5		3-Oct-07		4:07:53		69.8		39.5		13-Nov-07		4:25:59		67.4		42

		3-Oct-07		6:07:10		74.01		34.5		3-Oct-07		6:06:20		71.6		37.5		3-Oct-07		6:07:53		69.8		40		13-Nov-07		6:25:59		67.4		42.5

		3-Oct-07		8:07:10		73.4		36.5		3-Oct-07		8:06:20		71.6		42		3-Oct-07		8:07:53		71.6		39.5		13-Nov-07		8:25:59		71		40.5

		3-Oct-07		10:07:10		74.6		39		3-Oct-07		10:06:20		71.6		45		3-Oct-07		10:07:53		71.6		43.5		13-Nov-07		10:25:59		71		41

		3-Oct-07		12:07:10		74.6		38.5		3-Oct-07		12:06:20		71.6		37.5		3-Oct-07		12:07:53		72.21		43		13-Nov-07		12:25:59		74.6		39.5

		3-Oct-07		14:07:10		74.6		39		3-Oct-07		14:06:20		71.6		38		3-Oct-07		14:07:53		72.21		42		13-Nov-07		14:25:59		74.6		38.5

		3-Oct-07		16:07:10		74.6		37		3-Oct-07		16:06:20		71		41.5		3-Oct-07		16:07:53		71		42.5		13-Nov-07		16:25:59		75.2		37.5

		3-Oct-07		18:07:10		74.6		38.5		3-Oct-07		18:06:20		69.8		47.5		3-Oct-07		18:07:53		71		38		13-Nov-07		18:25:59		75.2		35.5

		3-Oct-07		20:07:10		75.81		37.5		3-Oct-07		20:06:20		72.8		43		3-Oct-07		20:07:53		71		44		13-Nov-07		20:25:59		73.4		38.5

		3-Oct-07		22:07:10		76.4		36.5		3-Oct-07		22:06:20		72.8		40		3-Oct-07		22:07:53		71.6		41.5		13-Nov-07		22:25:59		72.21		41

		4-Oct-07		0:07:10		75.81		35		4-Oct-07		0:06:20		72.8		39.5		4-Oct-07		0:07:53		71.6		40.5		14-Nov-07		0:25:59		71.6		43

		4-Oct-07		2:07:10		75.2		34.5		4-Oct-07		2:06:20		72.21		38.5		4-Oct-07		2:07:53		70.41		40.5		14-Nov-07		2:25:59		70.41		44.5

		4-Oct-07		4:07:10		74.01		34		4-Oct-07		4:06:20		71		38.5		4-Oct-07		4:07:53		69.2		40		14-Nov-07		4:25:59		69.8		45

		4-Oct-07		6:07:10		74.01		33.5		4-Oct-07		6:06:20		70.41		37		4-Oct-07		6:07:53		68.61		39.5		14-Nov-07		6:25:59		69.8		47

		4-Oct-07		8:07:10		74.01		34.5		4-Oct-07		8:06:20		71.6		39		4-Oct-07		8:07:53		70.41		38		14-Nov-07		8:25:59		73.4		46

		4-Oct-07		10:07:10		74.6		36		4-Oct-07		10:06:20		72.21		41		4-Oct-07		10:07:53		71.6		35.5		14-Nov-07		10:25:59		74.6		47

		4-Oct-07		12:07:10		76.4		36		4-Oct-07		12:06:20		72.21		41.5		4-Oct-07		12:07:53		71.6		45.5		14-Nov-07		12:25:59		74.6		48.5

		4-Oct-07		14:07:10		75.81		35		4-Oct-07		14:06:20		72.21		36		4-Oct-07		14:07:53		72.21		35.5		14-Nov-07		14:25:59		75.2		49.5

		4-Oct-07		16:07:10		76.4		38.5		4-Oct-07		16:06:20		71		41.5		4-Oct-07		16:07:53		71		49		14-Nov-07		16:25:59		75.2		49.5

		4-Oct-07		18:07:10		76.4		33.5		4-Oct-07		18:06:20		70.41		40		4-Oct-07		18:07:53		70.41		41		14-Nov-07		18:25:59		75.2		49.5

		4-Oct-07		20:07:10		76.4		34		4-Oct-07		20:06:20		72.8		38.5		4-Oct-07		20:07:53		72.8		37.5		14-Nov-07		20:25:59		74.6		49

		4-Oct-07		22:07:10		76.4		31.5		4-Oct-07		22:06:20		72.8		35.5		4-Oct-07		22:07:53		72.8		35		14-Nov-07		22:25:59		74.01		52

		5-Oct-07		0:07:10		75.81		30.5		5-Oct-07		0:06:20		72.8		34.5		5-Oct-07		0:07:53		72.21		34.5		15-Nov-07		0:25:59		72.8		50.5

		5-Oct-07		2:07:10		75.2		29		5-Oct-07		2:06:20		72.8		32.5		5-Oct-07		2:07:53		71		33.5		15-Nov-07		2:25:59		71.6		51

		5-Oct-07		4:07:10		74.6		28.5		5-Oct-07		4:06:20		72.8		31		5-Oct-07		4:07:53		69.8		32.5		15-Nov-07		4:25:59		71		50

		5-Oct-07		6:07:10		74.6		29		5-Oct-07		6:06:20		72.21		31.5		5-Oct-07		6:07:53		69.8		33.5		15-Nov-07		6:25:59		69.8		49

		5-Oct-07		8:07:10		74.01		30.5		5-Oct-07		8:06:20		71.6		33.5		5-Oct-07		8:07:53		71		34		15-Nov-07		8:25:59		72.8		44.5

		5-Oct-07		10:07:10		74.6		31.5		5-Oct-07		10:06:20		72.21		36.5		5-Oct-07		10:07:53		71.6		32.5		15-Nov-07		10:25:59		74.6		47

		5-Oct-07		12:07:10		75.2		32		5-Oct-07		12:06:20		71.6		34		5-Oct-07		12:07:53		71.6		33		15-Nov-07		12:25:59		74.6		48.5

		5-Oct-07		14:07:10		75.2		33		5-Oct-07		14:06:20		72.21		39.5		5-Oct-07		14:07:53		71.6		38.5		15-Nov-07		14:25:59		75.2		48

		5-Oct-07		16:07:10		75.81		32		5-Oct-07		16:06:20		70.41		39.5		5-Oct-07		16:07:53		71		35.5		15-Nov-07		16:25:59		75.2		49

		5-Oct-07		18:07:10		75.2		30		5-Oct-07		18:06:20		69.8		35		5-Oct-07		18:07:53		70.41		34.5		15-Nov-07		18:25:59		74.6		50

		5-Oct-07		20:07:10		75.81		29.5		5-Oct-07		20:06:20		72.21		33.5		5-Oct-07		20:07:53		70.41		34.5		15-Nov-07		20:25:59		74.01		50

		5-Oct-07		22:07:10		75.2		29.5		5-Oct-07		22:06:20		72.21		33.5		5-Oct-07		22:07:53		69.8		34.5		15-Nov-07		22:25:59		74.01		49.5

		6-Oct-07		0:07:10		75.2		29.5		6-Oct-07		0:06:20		72.21		33.5		6-Oct-07		0:07:53		69.2		35		16-Nov-07		0:25:59		72.21		49.5

		6-Oct-07		2:07:10		74.01		30		6-Oct-07		2:06:20		71.6		33.5		6-Oct-07		2:07:53		68		35.5		16-Nov-07		2:25:59		71		48.5

		6-Oct-07		4:07:10		72.8		29.5		6-Oct-07		4:06:20		70.41		33		6-Oct-07		4:07:53		66.81		36		16-Nov-07		4:25:59		69.8		48

		6-Oct-07		6:07:10		72.8		29		6-Oct-07		6:06:20		72.21		30		6-Oct-07		6:07:53		68		34.5		16-Nov-07		6:25:59		69.8		47

		6-Oct-07		8:07:10		72.8		29.5		6-Oct-07		8:06:20		71.6		34.5		6-Oct-07		8:07:53		69.2		33		16-Nov-07		8:25:59		72.8		42.5

		6-Oct-07		10:07:10		73.4		30.5		6-Oct-07		10:06:20		71.6		33.5		6-Oct-07		10:07:53		71.6		31		16-Nov-07		10:25:59		74.01		44

		6-Oct-07		12:07:10		74.01		30.5		6-Oct-07		12:06:20		70.41		36		6-Oct-07		12:07:53		71.6		34.5		16-Nov-07		12:25:59		74.6		47

		6-Oct-07		14:07:10		75.2		28		6-Oct-07		14:06:20		69.2		32.5		6-Oct-07		14:07:53		71		30.5		16-Nov-07		14:25:59		74.6		49.5

		6-Oct-07		16:07:10		75.2		27		6-Oct-07		16:06:20		69.2		31.5		6-Oct-07		16:07:53		70.41		31.5		16-Nov-07		16:25:59		75.81		49.5

		6-Oct-07		18:07:10		75.81		27.5		6-Oct-07		18:06:20		69.2		33		6-Oct-07		18:07:53		71		30		16-Nov-07		18:25:59		75.81		49.5

		6-Oct-07		20:07:10		76.4		27.5		6-Oct-07		20:06:20		72.21		31.5		6-Oct-07		20:07:53		70.41		33.5		16-Nov-07		20:25:59		74.01		50

		6-Oct-07		22:07:10		75.81		27		6-Oct-07		22:06:20		73.4		31.5		6-Oct-07		22:07:53		70.41		33		16-Nov-07		22:25:59		73.4		51.5

		7-Oct-07		0:07:10		75.2		27		7-Oct-07		0:06:20		72.8		30.5		7-Oct-07		0:07:53		69.8		32.5		17-Nov-07		0:25:59		72.21		51

		7-Oct-07		2:07:10		74.6		27		7-Oct-07		2:06:20		72.21		31		7-Oct-07		2:07:53		68.61		33		17-Nov-07		2:25:59		71		51.5

		7-Oct-07		4:07:10		74.01		28		7-Oct-07		4:06:20		71.6		31.5		7-Oct-07		4:07:53		68		34		17-Nov-07		4:25:59		70.41		51.5

		7-Oct-07		6:07:10		72.8		28.5		7-Oct-07		6:06:20		71		32		7-Oct-07		6:07:53		66.81		35		17-Nov-07		6:25:59		70.41		52

		7-Oct-07		8:07:10		72.21		29		7-Oct-07		8:06:20		69.2		32.5		7-Oct-07		8:07:53		67.4		34		17-Nov-07		8:25:59		71		50.5

		7-Oct-07		10:07:10		71.6		31		7-Oct-07		10:06:20		68.61		34.5		7-Oct-07		10:07:53		68.61		35		17-Nov-07		10:25:59		71.6		50.5

		7-Oct-07		12:07:10		72.21		29		7-Oct-07		12:06:20		68.61		31		7-Oct-07		12:07:53		70.41		31.5		17-Nov-07		12:25:59		72.8		50

		7-Oct-07		14:07:10		72.8		26.5		7-Oct-07		14:06:20		69.2		28.5		7-Oct-07		14:07:53		70.41		29		17-Nov-07		14:25:59		75.2		49.5

		7-Oct-07		16:07:10		73.4		27		7-Oct-07		16:06:20		69.2		31		7-Oct-07		16:07:53		70.41		30.5		17-Nov-07		16:25:59		75.2		48

		7-Oct-07		18:07:10		74.01		26		7-Oct-07		18:06:20		69.8		29.5		7-Oct-07		18:07:53		71		29		17-Nov-07		18:25:59		74.6		49

		7-Oct-07		20:07:10		75.2		25		7-Oct-07		20:06:20		72.21		28.5		7-Oct-07		20:07:53		71		29		17-Nov-07		20:25:59		72.8		48.5

		7-Oct-07		22:07:10		75.2		26.5		7-Oct-07		22:06:20		72.8		31		7-Oct-07		22:07:53		70.41		31.5		17-Nov-07		22:25:59		72.21		49

		8-Oct-07		0:07:10		74.6		26.5		8-Oct-07		0:06:20		72.21		30.5		8-Oct-07		0:07:53		69.2		31.5		18-Nov-07		0:25:59		71		52

		8-Oct-07		2:07:10		73.4		25.5		8-Oct-07		2:06:20		71		29		8-Oct-07		2:07:53		68		31		18-Nov-07		2:25:59		70.41		51

		8-Oct-07		4:07:10		72.8		26		8-Oct-07		4:06:20		69.8		29		8-Oct-07		4:07:53		66.81		31.5		18-Nov-07		4:25:59		69.8		50.5

		8-Oct-07		6:07:10		71.6		26		8-Oct-07		6:06:20		69.2		29.5		8-Oct-07		6:07:53		65.6		32		18-Nov-07		6:25:59		69.2		51

		8-Oct-07		8:07:10		71		27		8-Oct-07		8:06:20		68.61		30		8-Oct-07		8:07:53		67.4		31		18-Nov-07		8:25:59		68.61		50.5

		8-Oct-07		10:07:10		71.6		28.5		8-Oct-07		10:06:20		68.61		32		8-Oct-07		10:07:53		68		32.5		18-Nov-07		10:25:59		68.61		51

		8-Oct-07		12:07:10		72.21		29.5		8-Oct-07		12:06:20		69.2		33		8-Oct-07		12:07:53		69.8		33		18-Nov-07		12:25:59		69.2		51.5

		8-Oct-07		14:07:10		72.8		31		8-Oct-07		14:06:20		69.2		34.5		8-Oct-07		14:07:53		70.41		34.5		18-Nov-07		14:25:59		69.8		52

		8-Oct-07		16:07:10		73.4		30.5		8-Oct-07		16:06:20		69.2		35.5		8-Oct-07		16:07:53		70.41		35.5		18-Nov-07		16:25:59		71.6		54

		8-Oct-07		18:07:10		74.01		31.5		8-Oct-07		18:06:20		69.2		35		8-Oct-07		18:07:53		71		34		18-Nov-07		18:25:59		72.21		54

		8-Oct-07		20:07:10		75.2		33.5		8-Oct-07		20:06:20		72.21		36		8-Oct-07		20:07:53		71.6		38.5		18-Nov-07		20:25:59		71		53

		8-Oct-07		22:07:10		75.2		34.5		8-Oct-07		22:06:20		72.21		39.5		8-Oct-07		22:07:53		71		40		18-Nov-07		22:25:59		69.8		53

		9-Oct-07		0:07:10		74.6		34		9-Oct-07		0:06:20		72.21		38.5		9-Oct-07		0:07:53		69.8		40		19-Nov-07		0:25:59		69.2		53

		9-Oct-07		2:07:10		74.01		33.5		9-Oct-07		2:06:20		71.6		37.5		9-Oct-07		2:07:53		68.61		40		19-Nov-07		2:25:59		69.2		53

		9-Oct-07		4:07:10		73.4		33		9-Oct-07		4:06:20		71		36.5		9-Oct-07		4:07:53		67.4		39.5		19-Nov-07		4:25:59		68.61		53

		9-Oct-07		6:07:10		73.4		32.5		9-Oct-07		6:06:20		69.8		36		9-Oct-07		6:07:53		68.61		37.5		19-Nov-07		6:25:59		68.61		53

		9-Oct-07		8:07:10		72.8		33.5		9-Oct-07		8:06:20		69.8		38.5		9-Oct-07		8:07:53		70.41		36		19-Nov-07		8:25:59		68		53

		9-Oct-07		10:07:10		73.4		37.5		9-Oct-07		10:06:20		71		45		9-Oct-07		10:07:53		71.6		37		19-Nov-07		10:25:59		68.61		53

		9-Oct-07		12:07:10		74.6		35.5		9-Oct-07		12:06:20		71		41		9-Oct-07		12:07:53		71.6		42		19-Nov-07		12:25:59		68.61		55

		9-Oct-07		14:07:10		74.6		36		9-Oct-07		14:06:20		71		41		9-Oct-07		14:07:53		71.6		38.5		19-Nov-07		14:25:59		69.8		56

		9-Oct-07		16:07:10		75.2		34		9-Oct-07		16:06:20		69.8		42		9-Oct-07		16:07:53		71.6		37		19-Nov-07		16:25:59		71		57.5

		9-Oct-07		18:07:10		74.01		36.5		9-Oct-07		18:06:20		69.2		44.5		9-Oct-07		18:07:53		71		41.5		19-Nov-07		18:25:59		71.6		56.5

		9-Oct-07		20:07:10		75.81		32		9-Oct-07		20:06:20		72.8		35.5		9-Oct-07		20:07:53		71		37.5		19-Nov-07		20:25:59		71		55

		9-Oct-07		22:07:10		76.4		33.5		9-Oct-07		22:06:20		73.4		38.5		9-Oct-07		22:07:53		71.6		39		19-Nov-07		22:25:59		70.41		54.5

		10-Oct-07		0:07:10		75.81		34.5		10-Oct-07		0:06:20		72.8		39.5		10-Oct-07		0:07:53		70.41		41		20-Nov-07		0:25:59		69.2		53.5

		10-Oct-07		2:07:10		75.2		35.5		10-Oct-07		2:06:20		72.21		40.5		10-Oct-07		2:07:53		69.8		42		20-Nov-07		2:25:59		68.61		52.5

		10-Oct-07		4:07:10		74.6		36		10-Oct-07		4:06:20		72.21		40.5		10-Oct-07		4:07:53		69.2		43		20-Nov-07		4:25:59		68		53

		10-Oct-07		6:07:10		74.6		37.5		10-Oct-07		6:06:20		71		44.5		10-Oct-07		6:07:53		69.2		45		20-Nov-07		6:25:59		68.61		54.5

		10-Oct-07		8:07:10		74.01		39		10-Oct-07		8:06:20		71		38.5		10-Oct-07		8:07:53		71.6		44		20-Nov-07		8:25:59		71.6		54

		10-Oct-07		10:07:10		74.01		43		10-Oct-07		10:06:20		69.8		48.5		10-Oct-07		10:07:53		71		44		20-Nov-07		10:25:59		74.01		55

		10-Oct-07		12:07:10		74.6		42.5		10-Oct-07		12:06:20		70.41		48.5		10-Oct-07		12:07:53		71.6		43		20-Nov-07		12:25:59		74.01		53.5

		10-Oct-07		14:07:10		74.6		44.5		10-Oct-07		14:06:20		71		50.5		10-Oct-07		14:07:53		71		51.5		20-Nov-07		14:25:59		73.4		48.5

		10-Oct-07		16:07:10		74.6		42		10-Oct-07		16:06:20		69.8		57		10-Oct-07		16:07:53		70.41		49		20-Nov-07		16:25:59		74.01		45

		10-Oct-07		18:07:10		74.01		41		10-Oct-07		18:06:20		69.8		51		10-Oct-07		18:07:53		70.41		48		20-Nov-07		18:25:59		74.01		43

		10-Oct-07		20:07:10		75.2		41		10-Oct-07		20:06:20		72.21		47		10-Oct-07		20:07:53		69.8		50		20-Nov-07		20:25:59		72.21		43

		10-Oct-07		22:07:10		75.2		43		10-Oct-07		22:06:20		72.21		50.5		10-Oct-07		22:07:53		69.8		50		20-Nov-07		22:25:59		71		44.5

		11-Oct-07		0:07:10		74.6		44		11-Oct-07		0:06:20		72.21		51		11-Oct-07		0:07:53		69.8		51		21-Nov-07		0:25:59		69.8		44

		11-Oct-07		2:07:10		74.6		44		11-Oct-07		2:06:20		71.6		50.5		11-Oct-07		2:07:53		69.2		51		21-Nov-07		2:25:59		68.61		43

		11-Oct-07		4:07:10		74.01		44		11-Oct-07		4:06:20		71.6		49.5		11-Oct-07		4:07:53		69.2		51.5		21-Nov-07		4:25:59		68		42.5

		11-Oct-07		6:07:10		74.01		44		11-Oct-07		6:06:20		71		50.5		11-Oct-07		6:07:53		69.2		51		21-Nov-07		6:25:59		68		41

		11-Oct-07		8:07:10		73.4		44.5		11-Oct-07		8:06:20		70.41		45		11-Oct-07		8:07:53		71		49		21-Nov-07		8:25:59		71.6		37

		11-Oct-07		10:07:10		73.4		43		11-Oct-07		10:06:20		71.6		45		11-Oct-07		10:07:53		71		48		21-Nov-07		10:25:59		71.6		38

		11-Oct-07		12:07:10		74.01		46		11-Oct-07		12:06:20		70.41		51		11-Oct-07		12:07:53		71.6		49		21-Nov-07		12:25:59		72.21		38.5

		11-Oct-07		14:07:10		74.6		41.5		11-Oct-07		14:06:20		71		41		11-Oct-07		14:07:53		71		49.5		21-Nov-07		14:25:59		72.8		37.5

		11-Oct-07		16:07:10		75.2		46.5		11-Oct-07		16:06:20		69.2		59.5		11-Oct-07		16:07:53		70.41		53		21-Nov-07		16:25:59		73.4		37

		11-Oct-07		18:07:10		74.6		39.5		11-Oct-07		18:06:20		69.8		45		11-Oct-07		18:07:53		70.41		47		21-Nov-07		18:25:59		73.4		38

		11-Oct-07		20:07:10		75.2		40		11-Oct-07		20:06:20		72.21		45		11-Oct-07		20:07:53		70.41		46		21-Nov-07		20:25:59		71.6		38

		11-Oct-07		22:07:10		74.6		39.5		11-Oct-07		22:06:20		72.21		44		11-Oct-07		22:07:53		69.8		45.5		21-Nov-07		22:25:59		69.8		38.5

		12-Oct-07		0:07:10		74.01		38.5		12-Oct-07		0:06:20		72.21		42.5		12-Oct-07		0:07:53		68.61		45		22-Nov-07		0:25:59		68.61		38.5

		12-Oct-07		2:07:10		73.4		38		12-Oct-07		2:06:20		71.6		42		12-Oct-07		2:07:53		67.4		45.5		22-Nov-07		2:25:59		67.4		37.5

		12-Oct-07		4:07:10		72.21		38.5		12-Oct-07		4:06:20		71		42.5		12-Oct-07		4:07:53		66.81		46.5		22-Nov-07		4:25:59		66.81		36.5

		12-Oct-07		6:07:10		72.21		38		12-Oct-07		6:06:20		70.41		41.5		12-Oct-07		6:07:53		68.61		44		22-Nov-07		6:25:59		67.4		35

		12-Oct-07		8:07:10		72.21		38		12-Oct-07		8:06:20		70.41		43.5		12-Oct-07		8:07:53		69.8		42		22-Nov-07		8:25:59		70.41		32.5

		12-Oct-07		10:07:10		72.8		43.5		12-Oct-07		10:06:20		71		51.5		12-Oct-07		10:07:53		71.6		40		22-Nov-07		10:25:59		71.6		33.5

		12-Oct-07		12:07:10		73.4		40.5		12-Oct-07		12:06:20		70.41		45.5		12-Oct-07		12:07:53		71.6		49		22-Nov-07		12:25:59		72.21		35

		12-Oct-07		14:07:10		73.4		43.5		12-Oct-07		14:06:20		69.8		41		12-Oct-07		14:07:53		71		44.5		22-Nov-07		14:25:59		73.4		34

		12-Oct-07		16:07:10		74.01		45		12-Oct-07		16:06:20		69.2		56.5		12-Oct-07		16:07:53		71		46.5		22-Nov-07		16:25:59		72.8		32.5

		12-Oct-07		18:07:10		74.01		39.5		12-Oct-07		18:06:20		69.8		46.5		12-Oct-07		18:07:53		70.41		44.5		22-Nov-07		18:25:59		72.8		34.5

		12-Oct-07		20:07:10		74.6		38.5		12-Oct-07		20:06:20		72.21		42		12-Oct-07		20:07:53		70.41		44		22-Nov-07		20:25:59		71		34

		12-Oct-07		22:07:10		75.2		37		12-Oct-07		22:06:20		72.8		40.5		12-Oct-07		22:07:53		69.8		43.5		22-Nov-07		22:25:59		69.2		35

		13-Oct-07		0:07:10		74.6		36.5		13-Oct-07		0:06:20		72.21		40		13-Oct-07		0:07:53		68.61		44		23-Nov-07		0:25:59		68		35

		13-Oct-07		2:07:10		74.01		38		13-Oct-07		2:06:20		72.21		42		13-Oct-07		2:07:53		68		46		23-Nov-07		2:25:59		66.81		34.5

		13-Oct-07		4:07:10		74.01		39.5		13-Oct-07		4:06:20		72.21		44		13-Oct-07		4:07:53		67.4		48.5		23-Nov-07		4:25:59		66.2		34

		13-Oct-07		6:07:10		73.4		40		13-Oct-07		6:06:20		71		46		13-Oct-07		6:07:53		68.61		48		23-Nov-07		6:25:59		66.81		32.5

		13-Oct-07		8:07:10		72.8		44		13-Oct-07		8:06:20		71		45		13-Oct-07		8:07:53		70.41		48.5		23-Nov-07		8:25:59		69.2		30.5

		13-Oct-07		10:07:10		72.8		44		13-Oct-07		10:06:20		71		43		13-Oct-07		10:07:53		71		50		23-Nov-07		10:25:59		71.6		31

		13-Oct-07		12:07:10		73.4		44		13-Oct-07		12:06:20		70.41		54.5		13-Oct-07		12:07:53		71.6		52		23-Nov-07		12:25:59		70.41		33

		13-Oct-07		14:07:10		73.4		46.5		13-Oct-07		14:06:20		70.41		51		13-Oct-07		14:07:53		71		50		23-Nov-07		14:25:59		71		33.5

		13-Oct-07		16:07:10		72.8		49.5		13-Oct-07		16:06:20		69.2		61		13-Oct-07		16:07:53		71		53		23-Nov-07		16:25:59		71		32.5

		13-Oct-07		18:07:10		72.8		44		13-Oct-07		18:06:20		69.8		50		13-Oct-07		18:07:53		70.41		50.5		23-Nov-07		18:25:59		71		34

		13-Oct-07		20:07:10		73.4		43.5		13-Oct-07		20:06:20		71		48		13-Oct-07		20:07:53		69.8		48.5		23-Nov-07		20:25:59		70.41		34.5

		13-Oct-07		22:07:10		73.4		42.5		13-Oct-07		22:06:20		71.6		46.5		13-Oct-07		22:07:53		68.61		49		23-Nov-07		22:25:59		68.61		34.5

		14-Oct-07		0:07:10		72.21		41.5		14-Oct-07		0:06:20		71		45		14-Oct-07		0:07:53		67.4		49		24-Nov-07		0:25:59		67.4		34.5

		14-Oct-07		2:07:10		71.6		40.5		14-Oct-07		2:06:20		69.8		43.5		14-Oct-07		2:07:53		66.2		48		24-Nov-07		2:25:59		66.81		34

		14-Oct-07		4:07:10		71		40		14-Oct-07		4:06:20		69.2		42.5		14-Oct-07		4:07:53		65.6		47.5		24-Nov-07		4:25:59		66.2		33.5

		14-Oct-07		6:07:10		70.41		39		14-Oct-07		6:06:20		68.61		41		14-Oct-07		6:07:53		65.6		46		24-Nov-07		6:25:59		66.81		32.5

		14-Oct-07		8:07:10		71		37.5		14-Oct-07		8:06:20		68.61		40.5		14-Oct-07		8:07:53		67.4		41.5		24-Nov-07		8:25:59		68.61		29.5

		14-Oct-07		10:07:10		71.6		43.5		14-Oct-07		10:06:20		68.61		49		14-Oct-07		10:07:53		68.61		48.5		24-Nov-07		10:25:59		70.41		25.5

		14-Oct-07		12:07:10		72.21		46		14-Oct-07		12:06:20		68.61		49.5		14-Oct-07		12:07:53		69.8		49.5		24-Nov-07		12:25:59		69.8		24

		14-Oct-07		14:07:10		72.8		47		14-Oct-07		14:06:20		69.2		54		14-Oct-07		14:07:53		70.41		50		24-Nov-07		14:25:59		70.41		23

		14-Oct-07		16:07:10		72.8		45.5		14-Oct-07		16:06:20		69.2		45.5		14-Oct-07		16:07:53		70.41		45.5		24-Nov-07		16:25:59		71.6		22.5

		14-Oct-07		18:07:10		73.4		46		14-Oct-07		18:06:20		69.2		53.5		14-Oct-07		18:07:53		70.41		52.5		24-Nov-07		18:25:59		71		22.5

		14-Oct-07		20:07:10		74.6		44.5		14-Oct-07		20:06:20		71.6		49		14-Oct-07		20:07:53		69.8		50.5		24-Nov-07		20:25:59		69.8		24.5

		14-Oct-07		22:07:10		74.01		43		14-Oct-07		22:06:20		72.21		47		14-Oct-07		22:07:53		69.2		50		24-Nov-07		22:25:59		68.61		27

		15-Oct-07		0:07:10		74.01		43		15-Oct-07		0:06:20		72.21		47		15-Oct-07		0:07:53		68.61		51.5		25-Nov-07		0:25:59		67.4		28

		15-Oct-07		2:07:10		74.01		43.5		15-Oct-07		2:06:20		72.21		47		15-Oct-07		2:07:53		68		52		25-Nov-07		2:25:59		66.81		28.5

		15-Oct-07		4:07:10		73.4		43.5		15-Oct-07		4:06:20		71.6		47		15-Oct-07		4:07:53		67.4		52		25-Nov-07		4:25:59		66.2		28.5

		15-Oct-07		6:07:10		72.8		43.5		15-Oct-07		6:06:20		71		43		15-Oct-07		6:07:53		66.81		52.5		25-Nov-07		6:25:59		65.6		28.5

		15-Oct-07		8:07:10		71.6		45		15-Oct-07		8:06:20		69.2		50		15-Oct-07		8:07:53		68.61		49.5		25-Nov-07		8:25:59		65.6		28

		15-Oct-07		10:07:10		71		46.5		15-Oct-07		10:06:20		68.61		52		15-Oct-07		10:07:53		68		52		25-Nov-07		10:25:59		65.6		29

		15-Oct-07		12:07:10		71		46		15-Oct-07		12:06:20		69.2		52		15-Oct-07		12:07:53		68		53		25-Nov-07		12:25:59		66.2		30.5

		15-Oct-07		14:07:10		71.6		48		15-Oct-07		14:06:20		69.2		45		15-Oct-07		14:07:53		69.2		53		25-Nov-07		14:25:59		68		30

		15-Oct-07		16:07:10		72.21		49.5		15-Oct-07		16:06:20		69.2		49.5		15-Oct-07		16:07:53		69.8		53.5		25-Nov-07		16:25:59		68		30.5

		15-Oct-07		18:07:10		72.8		48		15-Oct-07		18:06:20		69.2		54.5		15-Oct-07		18:07:53		69.8		53.5		25-Nov-07		18:25:59		68		31.5

		15-Oct-07		20:07:10		74.01		44		15-Oct-07		20:06:20		71.6		48		15-Oct-07		20:07:53		69.8		50		25-Nov-07		20:25:59		67.4		32

		15-Oct-07		22:07:10		73.4		42.5		15-Oct-07		22:06:20		71.6		45.5		15-Oct-07		22:07:53		68		50		25-Nov-07		22:25:59		66.81		33

		16-Oct-07		0:07:10		72.8		42		16-Oct-07		0:06:20		71		45.5		16-Oct-07		0:07:53		66.81		50.5		26-Nov-07		0:25:59		66.81		33.5

		16-Oct-07		2:07:10		72.21		42		16-Oct-07		2:06:20		71		45.5		16-Oct-07		2:07:53		66.2		51		26-Nov-07		2:25:59		66.2		33.5

		16-Oct-07		4:07:10		72.21		42.5		16-Oct-07		4:06:20		70.41		46		16-Oct-07		4:07:53		65.6		51.5		26-Nov-07		4:25:59		66.2		34

		16-Oct-07		6:07:10		72.21		43		16-Oct-07		6:06:20		70.41		46.5		16-Oct-07		6:07:53		68.61		48.5		26-Nov-07		6:25:59		66.2		34

		16-Oct-07		8:07:10		72.21		45.5		16-Oct-07		8:06:20		70.41		51.5		16-Oct-07		8:07:53		68.61		49.5		26-Nov-07		8:25:59		65.6		34.5

		16-Oct-07		10:07:10		72.8		45.5		16-Oct-07		10:06:20		71.6		54.5		16-Oct-07		10:07:53		71		49.5		26-Nov-07		10:25:59		65.6		35.5

		16-Oct-07		12:07:10		72.8		48.5		16-Oct-07		12:06:20		69.8		44.5		16-Oct-07		12:07:53		71.6		53		26-Nov-07		12:25:59		66.2		36.5

		16-Oct-07		14:07:10		72.8		53		16-Oct-07		14:06:20		71		54		16-Oct-07		14:07:53		71		57.5		26-Nov-07		14:25:59		66.2		35.5

		16-Oct-07		16:07:10		74.01		48.5		16-Oct-07		16:06:20		69.8		59.5		16-Oct-07		16:07:53		70.41		55.5		26-Nov-07		16:25:59		66.81		35

		16-Oct-07		18:07:10		73.4		47.5		16-Oct-07		18:06:20		70.41		57.5		16-Oct-07		18:07:53		69.8		54.5		26-Nov-07		18:25:59		67.4		35.5

		16-Oct-07		20:07:10		74.6		48		16-Oct-07		20:06:20		72.21		53		16-Oct-07		20:07:53		70.41		54.5		26-Nov-07		20:25:59		66.81		36

		16-Oct-07		22:07:10		74.6		47		16-Oct-07		22:06:20		72.21		51		16-Oct-07		22:07:53		69.8		54		26-Nov-07		22:25:59		66.2		35.5

		17-Oct-07		0:07:10		74.01		45		17-Oct-07		0:06:20		72.8		48.5		17-Oct-07		0:07:53		69.2		52.5		27-Nov-07		0:25:59		65.6		35.5

		17-Oct-07		2:07:10		73.4		43		17-Oct-07		2:06:20		71.6		45.5		17-Oct-07		2:07:53		68		51		27-Nov-07		2:25:59		65.6		34.5

		17-Oct-07		4:07:10		72.8		42.5		17-Oct-07		4:06:20		71		45		17-Oct-07		4:07:53		66.81		50.5		27-Nov-07		4:25:59		65.01		34

		17-Oct-07		6:07:10		72.8		43		17-Oct-07		6:06:20		70.41		44.5		17-Oct-07		6:07:53		68		49		27-Nov-07		6:25:59		66.2		32.5

		17-Oct-07		8:07:10		71.6		43.5		17-Oct-07		8:06:20		69.8		48		17-Oct-07		8:07:53		69.8		46		27-Nov-07		8:25:59		68.61		30.5

		17-Oct-07		10:07:10		72.8		43.5		17-Oct-07		10:06:20		71		52.5		17-Oct-07		10:07:53		71		46		27-Nov-07		10:25:59		70.41		32.5

		17-Oct-07		12:07:10		73.4		46		17-Oct-07		12:06:20		71		55.5		17-Oct-07		12:07:53		71.6		46		27-Nov-07		12:25:59		72.21		33.5

		17-Oct-07		14:07:10		73.4		47		17-Oct-07		14:06:20		71		41		17-Oct-07		14:07:53		71		52.5		27-Nov-07		14:25:59		72.8		34.5

		17-Oct-07		16:07:10		72.8		53		17-Oct-07		16:06:20		69.2		55.5		17-Oct-07		16:07:53		70.41		60.5		27-Nov-07		16:25:59		73.4		35.5

		17-Oct-07		18:07:10		72.8		52		17-Oct-07		18:06:20		69.2		60		17-Oct-07		18:07:53		69.8		55.5		27-Nov-07		18:25:59		72.8		37

		17-Oct-07		20:07:10		72.8		46.5		17-Oct-07		20:06:20		71		49.5		17-Oct-07		20:07:53		69.8		51.5		27-Nov-07		20:25:59		71		37

		17-Oct-07		22:07:10		72.21		44		17-Oct-07		22:06:20		71		46.5		17-Oct-07		22:07:53		68		49.5		27-Nov-07		22:25:59		69.8		36.5

		18-Oct-07		0:07:10		71		42		18-Oct-07		0:06:20		69.8		44		18-Oct-07		0:07:53		66.81		48.5		28-Nov-07		0:25:59		68.61		36.5

		18-Oct-07		2:07:10		70.41		41		18-Oct-07		2:06:20		69.2		43		18-Oct-07		2:07:53		66.2		47.5		28-Nov-07		2:25:59		67.4		36.5

		18-Oct-07		4:07:10		70.41		41.5		18-Oct-07		4:06:20		69.2		44		18-Oct-07		4:07:53		66.2		48.5		28-Nov-07		4:25:59		66.81		36.5

		18-Oct-07		6:07:10		71		43.5		18-Oct-07		6:06:20		69.8		46		18-Oct-07		6:07:53		68		48		28-Nov-07		6:25:59		67.4		36

		18-Oct-07		8:07:10		71.6		44.5		18-Oct-07		8:06:20		71		49.5		18-Oct-07		8:07:53		69.8		46		28-Nov-07		8:25:59		69.8		35

		18-Oct-07		10:07:10		74.01		45.5		18-Oct-07		10:06:20		74.01		41.5		18-Oct-07		10:07:53		71		51.5		28-Nov-07		10:25:59		73.4		36

		18-Oct-07		12:07:10		74.6		44		18-Oct-07		12:06:20		73.4		46.5		18-Oct-07		12:07:53		71.6		50.5		28-Nov-07		12:25:59		72.8		38.5

		18-Oct-07		14:07:10		75.2		41.5		18-Oct-07		14:06:20		74.6		37.5		18-Oct-07		14:07:53		71.6		45		28-Nov-07		14:25:59		73.4		35

		18-Oct-07		16:07:10		75.2		41		18-Oct-07		16:06:20		72.21		41.5		18-Oct-07		16:07:53		70.41		47		28-Nov-07		16:25:59		74.01		34

		18-Oct-07		18:07:10		74.6		41.5		18-Oct-07		18:06:20		71.6		42.5		18-Oct-07		18:07:53		70.41		48.5		28-Nov-07		18:25:59		74.01		35.5

		18-Oct-07		20:07:10		74.6		41		18-Oct-07		20:06:20		72.8		44		18-Oct-07		20:07:53		69.8		47		28-Nov-07		20:25:59		72.21		37

		18-Oct-07		22:07:10		73.4		40.5		18-Oct-07		22:06:20		72.21		43		18-Oct-07		22:07:53		68.61		47.5		28-Nov-07		22:25:59		71		37

		19-Oct-07		0:07:10		72.8		41		19-Oct-07		0:06:20		72.21		43.5		19-Oct-07		0:07:53		67.4		48.5		29-Nov-07		0:25:59		69.8		37

		19-Oct-07		2:07:10		72.21		41.5		19-Oct-07		2:06:20		71		43.5		19-Oct-07		2:07:53		66.81		49.5		29-Nov-07		2:25:59		68.61		37

		19-Oct-07		4:07:10		71.6		42.5		19-Oct-07		4:06:20		71		44.5		19-Oct-07		4:07:53		66.2		52		29-Nov-07		4:25:59		67.4		36.5

		19-Oct-07		6:07:10		71.6		43		19-Oct-07		6:06:20		71		45.5		19-Oct-07		6:07:53		68		49		29-Nov-07		6:25:59		67.4		34.5

		19-Oct-07		8:07:10		72.21		44		19-Oct-07		8:06:20		72.21		47		19-Oct-07		8:07:53		69.2		48		29-Nov-07		8:25:59		69.8		32

		19-Oct-07		10:07:10		72.8		43.5		19-Oct-07		10:06:20		72.21		40		19-Oct-07		10:07:53		71		49.5		29-Nov-07		10:25:59		72.21		33

		19-Oct-07		12:07:10		74.01		44.5		19-Oct-07		12:06:20		72.21		49.5		19-Oct-07		12:07:53		71.6		51		29-Nov-07		12:25:59		72.21		33

		19-Oct-07		14:07:10		75.2		47		19-Oct-07		14:06:20		72.8		47		19-Oct-07		14:07:53		71		54		29-Nov-07		14:25:59		73.4		32.5

		19-Oct-07		16:07:10		74.6		47		19-Oct-07		16:06:20		71.6		45.5		19-Oct-07		16:07:53		71		48		29-Nov-07		16:25:59		73.4		32

		19-Oct-07		18:07:10		74.6		51.5		19-Oct-07		18:06:20		71		56.5		19-Oct-07		18:07:53		70.41		58.5		29-Nov-07		18:25:59		72.8		30.5

		19-Oct-07		20:07:10		74.6		51.5		19-Oct-07		20:06:20		72.8		57		19-Oct-07		20:07:53		70.41		58		29-Nov-07		20:25:59		71		32

		19-Oct-07		22:07:10		74.01		52.5		19-Oct-07		22:06:20		73.4		56		19-Oct-07		22:07:53		70.41		59		29-Nov-07		22:25:59		69.8		32.5

		20-Oct-07		0:07:10		74.01		53		20-Oct-07		0:06:20		72.8		57.5		20-Oct-07		0:07:53		70.41		60.5		30-Nov-07		0:25:59		69.2		33

		20-Oct-07		2:07:10		73.4		55.5		20-Oct-07		2:06:20		72.8		59		20-Oct-07		2:07:53		69.8		61.5		30-Nov-07		2:25:59		68		32.5

		20-Oct-07		4:07:10		73.4		56		20-Oct-07		4:06:20		72.8		59.5		20-Oct-07		4:07:53		69.8		62		30-Nov-07		4:25:59		67.4		32.5

		20-Oct-07		6:07:10		74.01		56		20-Oct-07		6:06:20		72.8		59		20-Oct-07		6:07:53		70.41		65		30-Nov-07		6:25:59		67.4		31.5

		20-Oct-07		8:07:10		73.4		52.5		20-Oct-07		8:06:20		71		55		20-Oct-07		8:07:53		71		63.5		30-Nov-07		8:25:59		69.2		29.5

		20-Oct-07		10:07:10		73.4		54.5		20-Oct-07		10:06:20		71		54		20-Oct-07		10:07:53		71.6		63.5		30-Nov-07		10:25:59		72.21		31.5

		20-Oct-07		12:07:10		74.6		53		20-Oct-07		12:06:20		71		59.5		20-Oct-07		12:07:53		71.6		58		30-Nov-07		12:25:59		71.6		33

		20-Oct-07		14:07:10		75.2		54.5		20-Oct-07		14:06:20		71		48.5		20-Oct-07		14:07:53		71		62		30-Nov-07		14:25:59		74.01		31.5

		20-Oct-07		16:07:10		74.6		56.5		20-Oct-07		16:06:20		69.8		67		20-Oct-07		16:07:53		70.41		70		30-Nov-07		16:25:59		74.6		30.5

		20-Oct-07		18:07:10		73.4		57.5		20-Oct-07		18:06:20		69.2		61		20-Oct-07		18:07:53		70.41		59.5		30-Nov-07		18:25:59		74.01		29

		20-Oct-07		20:07:10		74.6		53.5		20-Oct-07		20:06:20		72.21		58		20-Oct-07		20:07:53		69.8		61.5		30-Nov-07		20:25:59		72.8		27.5

		20-Oct-07		22:07:10		74.01		49		20-Oct-07		22:06:20		72.21		51.5		20-Oct-07		22:07:53		69.2		56.5		30-Nov-07		22:25:59		71		30

		21-Oct-07		0:07:10		73.4		45		21-Oct-07		0:06:20		71.6		46.5		21-Oct-07		0:07:53		68		53		1-Dec-07		0:25:59		69.2		31

		21-Oct-07		2:07:10		72.21		44.5		21-Oct-07		2:06:20		71		47		21-Oct-07		2:07:53		66.81		53.5		1-Dec-07		2:25:59		68		31

		21-Oct-07		4:07:10		71.6		45		21-Oct-07		4:06:20		71		47		21-Oct-07		4:07:53		66.2		54		1-Dec-07		4:25:59		67.4		31

		21-Oct-07		6:07:10		71		43		21-Oct-07		6:06:20		70.41		45		21-Oct-07		6:07:53		65.6		52		1-Dec-07		6:25:59		68		29.5

		21-Oct-07		8:07:10		70.41		42		21-Oct-07		8:06:20		68.61		44		21-Oct-07		8:07:53		68		46		1-Dec-07		8:25:59		71		28

		21-Oct-07		10:07:10		70.41		45		21-Oct-07		10:06:20		69.2		50		21-Oct-07		10:07:53		67.4		52		1-Dec-07		10:25:59		72.8		28

		21-Oct-07		12:07:10		71		41.5		21-Oct-07		12:06:20		68.61		42.5		21-Oct-07		12:07:53		69.2		45		1-Dec-07		12:25:59		74.01		26.5

		21-Oct-07		14:07:10		71		37.5		21-Oct-07		14:06:20		69.2		37		21-Oct-07		14:07:53		69.2		40.5		1-Dec-07		14:25:59		74.01		27

		21-Oct-07		16:07:10		71		36		21-Oct-07		16:06:20		68.61		38		21-Oct-07		16:07:53		69.2		38		1-Dec-07		16:25:59		74.6		26

		21-Oct-07		18:07:10		71.6		35		21-Oct-07		18:06:20		68.61		37		21-Oct-07		18:07:53		69.8		37		1-Dec-07		18:25:59		75.2		26.5

		21-Oct-07		20:07:10		72.21		35.5		21-Oct-07		20:06:20		70.41		38		21-Oct-07		20:07:53		68.61		40		1-Dec-07		20:25:59		74.01		25

		21-Oct-07		22:07:10		72.21		36		21-Oct-07		22:06:20		71		38		21-Oct-07		22:07:53		67.4		42		1-Dec-07		22:25:59		70.41		27

		22-Oct-07		0:07:10		71.6		36		22-Oct-07		0:06:20		70.41		38		22-Oct-07		0:07:53		66.2		42.5		2-Dec-07		0:25:59		68.61		28

		22-Oct-07		2:07:10		71		35.5		22-Oct-07		2:06:20		69.8		37.5		22-Oct-07		2:07:53		65.01		43		2-Dec-07		2:25:59		67.4		27.5

		22-Oct-07		4:07:10		70.41		35.5		22-Oct-07		4:06:20		69.8		37		22-Oct-07		4:07:53		64.4		43		2-Dec-07		4:25:59		66.2		27.5

		22-Oct-07		6:07:10		69.8		34.5		22-Oct-07		6:06:20		69.2		36.5		22-Oct-07		6:07:53		63.8		42.5		2-Dec-07		6:25:59		66.2		27

		22-Oct-07		8:07:10		69.2		34.5		22-Oct-07		8:06:20		68.61		36.5		22-Oct-07		8:07:53		68		37.5		2-Dec-07		8:25:59		66.2		26

		22-Oct-07		10:07:10		69.8		33.5		22-Oct-07		10:06:20		68.61		35		22-Oct-07		10:07:53		67.4		37.5		2-Dec-07		10:25:59		66.2		26.5

		22-Oct-07		12:07:10		69.8		33		22-Oct-07		12:06:20		68.61		34		22-Oct-07		12:07:53		68.61		35.5		2-Dec-07		12:25:59		66.81		29

		22-Oct-07		14:07:10		71		31		22-Oct-07		14:06:20		68.61		32		22-Oct-07		14:07:53		69.8		34		2-Dec-07		14:25:59		67.4		29.5

		22-Oct-07		16:07:10		72.21		30.5		22-Oct-07		16:06:20		68.61		31		22-Oct-07		16:07:53		70.41		33.5		2-Dec-07		16:25:59		68		30

		22-Oct-07		18:07:10		72.21		30.5		22-Oct-07		18:06:20		69.2		32.5		22-Oct-07		18:07:53		70.41		33.5		2-Dec-07		18:25:59		67.4		30

		22-Oct-07		20:07:10		74.01		28		22-Oct-07		20:06:20		72.21		29.5		22-Oct-07		20:07:53		71.6		31		2-Dec-07		20:25:59		66.81		31

		22-Oct-07		22:07:10		74.01		32		22-Oct-07		22:06:20		72.8		35		22-Oct-07		22:07:53		71		36.5		2-Dec-07		22:25:59		66.2		31

		23-Oct-07		0:07:10		73.4		33		23-Oct-07		0:06:20		72.21		36		23-Oct-07		0:07:53		69.2		38		3-Dec-07		0:25:59		66.2		30.5

		23-Oct-07		2:07:10		72.8		33.5		23-Oct-07		2:06:20		71.6		36.5		23-Oct-07		2:07:53		68.61		39		3-Dec-07		2:25:59		66.2		31

		23-Oct-07		4:07:10		72.21		34		23-Oct-07		4:06:20		71		36.5		23-Oct-07		4:07:53		66.81		40		3-Dec-07		4:25:59		66.2		32.5

		23-Oct-07		6:07:10		71.6		34.5		23-Oct-07		6:06:20		69.8		36.5		23-Oct-07		6:07:53		68		39.5		3-Dec-07		6:25:59		66.2		34.5

		23-Oct-07		8:07:10		71.6		35.5		23-Oct-07		8:06:20		69.8		38.5		23-Oct-07		8:07:53		69.2		38		3-Dec-07		8:25:59		66.2		35.5

		23-Oct-07		10:07:10		72.21		37.5		23-Oct-07		10:06:20		70.41		43.5		23-Oct-07		10:07:53		70.41		42		3-Dec-07		10:25:59		66.81		35.5

		23-Oct-07		12:07:10		72.8		35		23-Oct-07		12:06:20		70.41		36.5		23-Oct-07		12:07:53		71.6		34.5		3-Dec-07		12:25:59		67.4		36.5

		23-Oct-07		14:07:10		74.6		38.5		23-Oct-07		14:06:20		69.8		45		23-Oct-07		14:07:53		71.6		41		3-Dec-07		14:25:59		67.4		37.5

		23-Oct-07		16:07:10		75.81		35		23-Oct-07		16:06:20		71		41.5		23-Oct-07		16:07:53		71.6		42.5		3-Dec-07		16:25:59		68		39

		23-Oct-07		18:07:10		75.2		34		23-Oct-07		18:06:20		71.6		36		23-Oct-07		18:07:53		71		36		3-Dec-07		18:25:59		68		39.5

		23-Oct-07		20:07:10		75.81		34.5		23-Oct-07		20:06:20		72.8		38		23-Oct-07		20:07:53		70.41		40.5		3-Dec-07		20:25:59		68		40

		23-Oct-07		22:07:10		75.2		36		23-Oct-07		22:06:20		72.21		40		23-Oct-07		22:07:53		71.6		40.5		3-Dec-07		22:25:59		68		42

		24-Oct-07		0:07:10		74.6		36.5		24-Oct-07		0:06:20		72.21		40.5		24-Oct-07		0:07:53		71		42		4-Dec-07		0:25:59		68		42

		24-Oct-07		2:07:10		74.01		36.5		24-Oct-07		2:06:20		72.21		40		24-Oct-07		2:07:53		69.2		42.5		4-Dec-07		2:25:59		68		41.5

		24-Oct-07		4:07:10		73.4		36.5		24-Oct-07		4:06:20		72.21		39		24-Oct-07		4:07:53		68.61		42.5		4-Dec-07		4:25:59		67.4		41.5

		24-Oct-07		6:07:10		73.4		35.5		24-Oct-07		6:06:20		72.21		38		24-Oct-07		6:07:53		68		42.5		4-Dec-07		6:25:59		68.61		41

		24-Oct-07		8:07:10		73.4		36		24-Oct-07		8:06:20		71.6		40		24-Oct-07		8:07:53		69.8		40		4-Dec-07		8:25:59		72.8		37

		24-Oct-07		10:07:10		75.2		39		24-Oct-07		10:06:20		72.21		40.5		24-Oct-07		10:07:53		71.6		46.5		4-Dec-07		10:25:59		74.6		38

		24-Oct-07		12:07:10		75.81		39.5		24-Oct-07		12:06:20		72.21		38		24-Oct-07		12:07:53		71.6		49		4-Dec-07		12:25:59		75.2		36

		24-Oct-07		14:07:10		75.81		39		24-Oct-07		14:06:20		72.8		46.5		24-Oct-07		14:07:53		71.6		49		4-Dec-07		14:25:59		74.6		37

		24-Oct-07		16:07:10		76.4		40		24-Oct-07		16:06:20		71.6		50		24-Oct-07		16:07:53		71.6		45		4-Dec-07		16:25:59		74.6		38

		24-Oct-07		18:07:10		74.6		41		24-Oct-07		18:06:20		69.8		42		24-Oct-07		18:07:53		71		53.5		4-Dec-07		18:25:59		74.6		39

		24-Oct-07		20:07:10		75.81		43.5		24-Oct-07		20:06:20		73.4		48.5		24-Oct-07		20:07:53		70.41		55.5		4-Dec-07		20:25:59		74.01		39.5

		24-Oct-07		22:07:10		75.81		43.5		24-Oct-07		22:06:20		72.8		48		24-Oct-07		22:07:53		72.8		48		4-Dec-07		22:25:59		72.8		41

		25-Oct-07		0:07:10		75.2		41.5		25-Oct-07		0:06:20		72.8		45.5		25-Oct-07		0:07:53		72.21		46		5-Dec-07		0:25:59		71.6		44.5

		25-Oct-07		2:07:10		74.6		40		25-Oct-07		2:06:20		72.8		43.5		25-Oct-07		2:07:53		71.6		45		5-Dec-07		2:25:59		70.41		45

		25-Oct-07		4:07:10		74.01		39		25-Oct-07		4:06:20		72.8		41.5		25-Oct-07		4:07:53		69.8		44		5-Dec-07		4:25:59		69.8		45.5

		25-Oct-07		6:07:10		73.4		39		25-Oct-07		6:06:20		71.6		42		25-Oct-07		6:07:53		69.2		45		5-Dec-07		6:25:59		70.41		50

		25-Oct-07		8:07:10		72.8		39.5		25-Oct-07		8:06:20		71		45.5		25-Oct-07		8:07:53		71		42.5		5-Dec-07		8:25:59		74.6		47

		25-Oct-07		10:07:10		72.8		43.5		25-Oct-07		10:06:20		70.41		52.5		25-Oct-07		10:07:53		71.6		49.5		5-Dec-07		10:25:59		75.81		48

		25-Oct-07		12:07:10		73.4		43.5		25-Oct-07		12:06:20		70.41		52		25-Oct-07		12:07:53		71.6		44		5-Dec-07		12:25:59		75.2		50

		25-Oct-07		14:07:10		74.01		42		25-Oct-07		14:06:20		71		39.5		25-Oct-07		14:07:53		71.6		47		5-Dec-07		14:25:59		74.6		51.5

		25-Oct-07		16:07:10		74.6		46		25-Oct-07		16:06:20		69.8		54		25-Oct-07		16:07:53		71.6		50.5		5-Dec-07		16:25:59		74.6		50

		25-Oct-07		18:07:10		74.6		47		25-Oct-07		18:06:20		69.2		56.5		25-Oct-07		18:07:53		71		48.5		5-Dec-07		18:25:59		74.6		49.5

		25-Oct-07		20:07:10		75.81		42		25-Oct-07		20:06:20		72.8		46.5		25-Oct-07		20:07:53		72.8		46.5		5-Dec-07		20:25:59		74.6		48.5

		25-Oct-07		22:07:10		75.2		40.5		25-Oct-07		22:06:20		72.8		43.5		25-Oct-07		22:07:53		72.8		44.5		5-Dec-07		22:25:59		72.8		50

		26-Oct-07		0:07:10		74.6		39.5		26-Oct-07		0:06:20		72.8		43.5		26-Oct-07		0:07:53		71.6		44		6-Dec-07		0:25:59		72.21		51.5

		26-Oct-07		2:07:10		74.01		39		26-Oct-07		2:06:20		72.21		42		26-Oct-07		2:07:53		69.8		44		6-Dec-07		2:25:59		71		51.5

		26-Oct-07		4:07:10		72.8		38		26-Oct-07		4:06:20		71		40.5		26-Oct-07		4:07:53		68.61		43.5		6-Dec-07		4:25:59		70.41		52

		26-Oct-07		6:07:10		72.8		37.5		26-Oct-07		6:06:20		70.41		39.5		26-Oct-07		6:07:53		68		43.5		6-Dec-07		6:25:59		70.41		52

		26-Oct-07		8:07:10		72.21		38		26-Oct-07		8:06:20		69.8		42.5		26-Oct-07		8:07:53		69.2		40.5		6-Dec-07		8:25:59		74.6		46.5

		26-Oct-07		10:07:10		72.8		38.5		26-Oct-07		10:06:20		71		40		26-Oct-07		10:07:53		71		47.5		6-Dec-07		10:25:59		75.81		45

		26-Oct-07		12:07:10		73.4		44.5		26-Oct-07		12:06:20		70.41		50.5		26-Oct-07		12:07:53		71.6		44.5		6-Dec-07		12:25:59		75.2		47

		26-Oct-07		14:07:10		74.6		40		26-Oct-07		14:06:20		71		39.5		26-Oct-07		14:07:53		71.6		48.5		6-Dec-07		14:25:59		74.6		49

		26-Oct-07		16:07:10		74.6		47		26-Oct-07		16:06:20		69.8		58.5		26-Oct-07		16:07:53		71		56		6-Dec-07		16:25:59		74.6		47

		26-Oct-07		18:07:10		74.01		47.5		26-Oct-07		18:06:20		69.2		56		26-Oct-07		18:07:53		70.41		52.5		6-Dec-07		18:25:59		74.6		40.5

		26-Oct-07		20:07:10		74.6		41.5		26-Oct-07		20:06:20		71		47.5		26-Oct-07		20:07:53		71		47.5		6-Dec-07		20:25:59		74.01		39.5

		26-Oct-07		22:07:10		74.01		40.5		26-Oct-07		22:06:20		71		40.5		26-Oct-07		22:07:53		70.41		45.5		6-Dec-07		22:25:59		72.21		42

		27-Oct-07		0:07:10		73.4		40.5		27-Oct-07		0:06:20		71.6		44.5		27-Oct-07		0:07:53		69.2		46		7-Dec-07		0:25:59		71		44

		27-Oct-07		2:07:10		72.8		41.5		27-Oct-07		2:06:20		70.41		46.5		27-Oct-07		2:07:53		68		48		7-Dec-07		2:25:59		70.41		43.5

		27-Oct-07		4:07:10		72.21		42		27-Oct-07		4:06:20		70.41		46		27-Oct-07		4:07:53		68		48.5		7-Dec-07		4:25:59		70.41		44

		27-Oct-07		6:07:10		72.8		42		27-Oct-07		6:06:20		71		45.5		27-Oct-07		6:07:53		68		49		7-Dec-07		6:25:59		70.41		44.5

		27-Oct-07		8:07:10		72.21		41		27-Oct-07		8:06:20		71		45.5		27-Oct-07		8:07:53		71		46.5		7-Dec-07		8:25:59		74.6		41

		27-Oct-07		10:07:10		72.8		45		27-Oct-07		10:06:20		71		45.5		27-Oct-07		10:07:53		71		37.5		7-Dec-07		10:25:59		74.6		42

		27-Oct-07		12:07:10		73.4		45		27-Oct-07		12:06:20		70.41		53.5		27-Oct-07		12:07:53		71		52.5		7-Dec-07		12:25:59		72.8		45.5

		27-Oct-07		14:07:10		73.4		42.5		27-Oct-07		14:06:20		71		47.5		27-Oct-07		14:07:53		71		51		7-Dec-07		14:25:59		72.8		46.5

		27-Oct-07		16:07:10		73.4		46		27-Oct-07		16:06:20		68.61		46		27-Oct-07		16:07:53		71		46.5		7-Dec-07		16:25:59		72.8		47.5

		27-Oct-07		18:07:10		73.4		44.5		27-Oct-07		18:06:20		68		46.5		27-Oct-07		18:07:53		69.8		49.5		7-Dec-07		18:25:59		72.8		46

		27-Oct-07		20:07:10		72.8		42		27-Oct-07		20:06:20		69.2		47.5		27-Oct-07		20:07:53		69.8		46.5		7-Dec-07		20:25:59		72.21		46

		27-Oct-07		22:07:10		72.21		41.5		27-Oct-07		22:06:20		69.2		46		27-Oct-07		22:07:53		68.61		46		7-Dec-07		22:25:59		69.8		47.5

		28-Oct-07		0:07:10		71.6		40		28-Oct-07		0:06:20		68.61		44.5		28-Oct-07		0:07:53		67.4		45		8-Dec-07		0:25:59		68.61		48

		28-Oct-07		2:07:10		71		39		28-Oct-07		2:06:20		68.61		43		28-Oct-07		2:07:53		66.2		45		8-Dec-07		2:25:59		68		47

		28-Oct-07		4:07:10		70.41		38.5		28-Oct-07		4:06:20		68.61		41.5		28-Oct-07		4:07:53		65.01		45.5		8-Dec-07		4:25:59		67.4		46.5

		28-Oct-07		6:07:10		69.8		38		28-Oct-07		6:06:20		68		41.5		28-Oct-07		6:07:53		63.8		46		8-Dec-07		6:25:59		68		45.5

		28-Oct-07		8:07:10		69.2		39.5		28-Oct-07		8:06:20		68		43.5		28-Oct-07		8:07:53		66.81		43.5		8-Dec-07		8:25:59		71.6		40

		28-Oct-07		10:07:10		69.2		42		28-Oct-07		10:06:20		68		47		28-Oct-07		10:07:53		66.81		46.5		8-Dec-07		10:25:59		72.21		39.5

		28-Oct-07		12:07:10		69.2		44.5		28-Oct-07		12:06:20		67.4		50		28-Oct-07		12:07:53		67.4		48		8-Dec-07		12:25:59		71.6		40

		28-Oct-07		14:07:10		69.8		47		28-Oct-07		14:06:20		67.4		53		28-Oct-07		14:07:53		68.61		50		8-Dec-07		14:25:59		72.21		39.5

		28-Oct-07		16:07:10		70.41		49.5		28-Oct-07		16:06:20		67.4		49		28-Oct-07		16:07:53		69.2		52		8-Dec-07		16:25:59		72.21		38

		28-Oct-07		18:07:10		71		43		28-Oct-07		18:06:20		68		46.5		28-Oct-07		18:07:53		69.2		47.5		8-Dec-07		18:25:59		71.6		37.5

		28-Oct-07		20:07:10		71		43.5		28-Oct-07		20:06:20		68.61		47		28-Oct-07		20:07:53		68.61		47		8-Dec-07		20:25:59		70.41		36.5

		28-Oct-07		22:07:10		71		41		28-Oct-07		22:06:20		69.2		44.5		28-Oct-07		22:07:53		67.4		46.5		8-Dec-07		22:25:59		69.8		36.5

		29-Oct-07		0:07:10		70.41		41.5		29-Oct-07		0:06:20		68.61		44.5		29-Oct-07		0:07:53		66.2		47		9-Dec-07		0:25:59		68		37

		29-Oct-07		2:07:10		70.41		41.5		29-Oct-07		2:06:20		68.61		44.5		29-Oct-07		2:07:53		65.6		48		9-Dec-07		2:25:59		66.81		37

		29-Oct-07		4:07:10		69.8		40.5		29-Oct-07		4:06:20		68		44		29-Oct-07		4:07:53		65.01		48		9-Dec-07		4:25:59		66.2		36.5

		29-Oct-07		6:07:10		69.8		40.5		29-Oct-07		6:06:20		68		43.5		29-Oct-07		6:07:53		64.4		48		9-Dec-07		6:25:59		66.2		36

		29-Oct-07		8:07:10		69.2		40		29-Oct-07		8:06:20		68		43		29-Oct-07		8:07:53		67.4		43.5		9-Dec-07		8:25:59		66.2		35.5

		29-Oct-07		10:07:10		69.2		43.5		29-Oct-07		10:06:20		68		49.5		29-Oct-07		10:07:53		67.4		48		9-Dec-07		10:25:59		66.2		34

		29-Oct-07		12:07:10		69.8		47.5		29-Oct-07		12:06:20		68		53.5		29-Oct-07		12:07:53		69.2		50		9-Dec-07		12:25:59		66.2		34

		29-Oct-07		14:07:10		71		48.5		29-Oct-07		14:06:20		68		48.5		29-Oct-07		14:07:53		69.8		54.5		9-Dec-07		14:25:59		66.81		33.5

		29-Oct-07		16:07:10		71.6		48.5		29-Oct-07		16:06:20		68.61		55		29-Oct-07		16:07:53		70.41		45.5		9-Dec-07		16:25:59		66.81		33

		29-Oct-07		18:07:10		72.21		50.5		29-Oct-07		18:06:20		68.61		62.5		29-Oct-07		18:07:53		70.41		55.5		9-Dec-07		18:25:59		66.81		31

		29-Oct-07		20:07:10		72.8		48.5		29-Oct-07		20:06:20		69.2		46		29-Oct-07		20:07:53		71.6		50		9-Dec-07		20:25:59		65.6		30.5

		29-Oct-07		22:07:10		72.21		46		29-Oct-07		22:06:20		69.2		51.5		29-Oct-07		22:07:53		70.41		48.5		9-Dec-07		22:25:59		65.01		31.5

		30-Oct-07		0:07:10		71.6		45		30-Oct-07		0:06:20		68.61		50.5		30-Oct-07		0:07:53		69.2		48		10-Dec-07		0:25:59		64.4		31

		30-Oct-07		2:07:10		71.6		44.5		30-Oct-07		2:06:20		68.61		46.5		30-Oct-07		2:07:53		68.61		48.5		10-Dec-07		2:25:59		63.8		31

		30-Oct-07		4:07:10		71		43.5		30-Oct-07		4:06:20		69.2		48		30-Oct-07		4:07:53		67.4		49		10-Dec-07		4:25:59		63.21		31

		30-Oct-07		6:07:10		71.6		43.5		30-Oct-07		6:06:20		69.2		46.5		30-Oct-07		6:07:53		68		49		10-Dec-07		6:25:59		62.6		31

		30-Oct-07		8:07:10		71		46		30-Oct-07		8:06:20		68.61		44.5		30-Oct-07		8:07:53		69.2		47.5		10-Dec-07		8:25:59		63.21		31

		30-Oct-07		10:07:10		72.21		46		30-Oct-07		10:06:20		69.2		55.5		30-Oct-07		10:07:53		71.6		47.5		10-Dec-07		10:25:59		64.4		31

		30-Oct-07		12:07:10		72.21		49		30-Oct-07		12:06:20		69.8		56		30-Oct-07		12:07:53		71		49		10-Dec-07		12:25:59		65.6		31.5

		30-Oct-07		14:07:10		73.4		47		30-Oct-07		14:06:20		70.41		53.5		30-Oct-07		14:07:53		71		55		10-Dec-07		14:25:59		66.2		32

		30-Oct-07		16:07:10		73.4		48.5		30-Oct-07		16:06:20		68.61		61.5		30-Oct-07		16:07:53		70.41		54		10-Dec-07		16:25:59		66.81		32.5

		30-Oct-07		18:07:10		72.8		45		30-Oct-07		18:06:20		69.2		54.5		30-Oct-07		18:07:53		70.41		51.5		10-Dec-07		18:25:59		66.81		33

		30-Oct-07		20:07:10		72.21		46		30-Oct-07		20:06:20		68.61		53		30-Oct-07		20:07:53		69.8		48.5		10-Dec-07		20:25:59		66.2		34

		30-Oct-07		22:07:10		71.6		45.5		30-Oct-07		22:06:20		68.61		51.5		30-Oct-07		22:07:53		69.2		49		10-Dec-07		22:25:59		65.01		35

		31-Oct-07		0:07:10		71.6		45		31-Oct-07		0:06:20		69.2		50		31-Oct-07		0:07:53		68.61		49.5		11-Dec-07		0:25:59		64.4		36.5

		31-Oct-07		2:07:10		71		46.5		31-Oct-07		2:06:20		68.61		52		31-Oct-07		2:07:53		68		51		11-Dec-07		2:25:59		63.21		36.5

		31-Oct-07		4:07:10		71		47		31-Oct-07		4:06:20		68.61		52		31-Oct-07		4:07:53		67.4		52.5		11-Dec-07		4:25:59		63.21		36

		31-Oct-07		6:07:10		71.6		47		31-Oct-07		6:06:20		68.61		52		31-Oct-07		6:07:53		72.21		48		11-Dec-07		6:25:59		64.4		34.5

		31-Oct-07		8:07:10		71.6		47.5		31-Oct-07		8:06:20		69.8		48.5		31-Oct-07		8:07:53		71		43.5		11-Dec-07		8:25:59		66.81		31.5

		31-Oct-07		10:07:10		72.21		48		31-Oct-07		10:06:20		69.8		51.5		31-Oct-07		10:07:53		71.6		49.5		11-Dec-07		10:25:59		69.8		31.5

		31-Oct-07		12:07:10		72.8		46.5		31-Oct-07		12:06:20		69.2		45.5		31-Oct-07		12:07:53		72.21		48		11-Dec-07		12:25:59		74.01		32

		31-Oct-07		14:07:10		72.8		46.5		31-Oct-07		14:06:20		70.41		45.5		31-Oct-07		14:07:53		71		52		11-Dec-07		14:25:59		71.6		33.5

		31-Oct-07		16:07:10		73.4		47		31-Oct-07		16:06:20		68		51		31-Oct-07		16:07:53		71		45.5		11-Dec-07		16:25:59		71.6		34.5

		31-Oct-07		18:07:10		72.8		47		31-Oct-07		18:06:20		68.61		48		31-Oct-07		18:07:53		70.41		51.5		11-Dec-07		18:25:59		71.6		33.5

		31-Oct-07		20:07:10		72.21		45		31-Oct-07		20:06:20		68.61		51.5		31-Oct-07		20:07:53		69.8		48		11-Dec-07		20:25:59		69.8		33.5

		31-Oct-07		22:07:10		72.21		44.5		31-Oct-07		22:06:20		69.2		49.5		31-Oct-07		22:07:53		68.61		49.5		11-Dec-07		22:25:59		67.4		33

		1-Nov-07		0:07:10		71.6		44.5		1-Nov-07		0:06:20		69.2		49.5		1-Nov-07		0:07:53		67.4		50		12-Dec-07		0:25:59		66.2		33.5

		1-Nov-07		2:07:10		71.6		45.5		1-Nov-07		2:06:20		69.2		50		1-Nov-07		2:07:53		66.81		51.5		12-Dec-07		2:25:59		65.01		31

		1-Nov-07		4:07:10		71		46.5		1-Nov-07		4:06:20		68.61		52		1-Nov-07		4:07:53		66.81		53		12-Dec-07		4:25:59		63.8		29

		1-Nov-07		6:07:10		71.6		47.5		1-Nov-07		6:06:20		69.2		53.5		1-Nov-07		6:07:53		68.61		51		12-Dec-07		6:25:59		65.6		24

		1-Nov-07		8:07:10		72.21		44.5		1-Nov-07		8:06:20		69.8		53.5		1-Nov-07		8:07:53		70.41		49		12-Dec-07		8:25:59		69.8		21.5

		1-Nov-07		10:07:10		72.21		47		1-Nov-07		10:06:20		68.61		51.5		1-Nov-07		10:07:53		71		48.5		12-Dec-07		10:25:59		72.21		23

		1-Nov-07		12:07:10		72.8		45.5		1-Nov-07		12:06:20		69.8		44		1-Nov-07		12:07:53		71.6		45.5		12-Dec-07		12:25:59		71.6		22

		1-Nov-07		14:07:10		72.8		46.5		1-Nov-07		14:06:20		68.61		47.5		1-Nov-07		14:07:53		71		51		12-Dec-07		14:25:59		72.21		21

		1-Nov-07		16:07:10		72.8		51.5		1-Nov-07		16:06:20		68.61		60.5		1-Nov-07		16:07:53		70.41		55.5		12-Dec-07		16:25:59		72.21		20.5

		1-Nov-07		18:07:10		72.8		50		1-Nov-07		18:06:20		68.61		59		1-Nov-07		18:07:53		69.8		54.5		12-Dec-07		18:25:59		71.6		23

		1-Nov-07		20:07:10		72.21		47.5		1-Nov-07		20:06:20		68.61		53.5		1-Nov-07		20:07:53		69.8		50.5		12-Dec-07		20:25:59		69.8		24

		1-Nov-07		22:07:10		71.6		47.5		1-Nov-07		22:06:20		69.2		52		1-Nov-07		22:07:53		69.2		51		12-Dec-07		22:25:59		68.61		25.5

		2-Nov-07		0:07:10		71		48		2-Nov-07		0:06:20		68.61		52.5		2-Nov-07		0:07:53		68.61		51.5		13-Dec-07		0:25:59		66.2		26.5

		2-Nov-07		2:07:10		71		48		2-Nov-07		2:06:20		68.61		52.5		2-Nov-07		2:07:53		68		52.5		13-Dec-07		2:25:59		64.4		27

		2-Nov-07		4:07:10		70.41		47.5		2-Nov-07		4:06:20		68.61		52		2-Nov-07		4:07:53		67.4		52.5		13-Dec-07		4:25:59		63.21		27.5

		2-Nov-07		6:07:10		71		46		2-Nov-07		6:06:20		69.2		49		2-Nov-07		6:07:53		68		51.5		13-Dec-07		6:25:59		64.4		28

		2-Nov-07		8:07:10		72.21		46.5		2-Nov-07		8:06:20		68.61		54.5		2-Nov-07		8:07:53		69.8		48		13-Dec-07		8:25:59		68		27.5

		2-Nov-07		10:07:10		73.4		46		2-Nov-07		10:06:20		69.2		53		2-Nov-07		10:07:53		71.6		46.5		13-Dec-07		10:25:59		70.41		28.5

		2-Nov-07		12:07:10		74.01		47		2-Nov-07		12:06:20		69.8		56.5		2-Nov-07		12:07:53		71.6		47.5		13-Dec-07		12:25:59		71.6		29

		2-Nov-07		14:07:10		74.01		44		2-Nov-07		14:06:20		71		48.5		2-Nov-07		14:07:53		71		44		13-Dec-07		14:25:59		71.6		26

		2-Nov-07		16:07:10		74.01		52.5		2-Nov-07		16:06:20		69.2		58		2-Nov-07		16:07:53		71		56.5		13-Dec-07		16:25:59		71.6		25.5

		2-Nov-07		18:07:10		74.01		49.5		2-Nov-07		18:06:20		69.2		49.5		2-Nov-07		18:07:53		70.41		50		13-Dec-07		18:25:59		71.6		26

		2-Nov-07		20:07:10		73.4		46.5		2-Nov-07		20:06:20		69.2		51.5		2-Nov-07		20:07:53		70.41		51		13-Dec-07		20:25:59		71		27.5

		2-Nov-07		22:07:10		72.8		42		2-Nov-07		22:06:20		69.8		47.5		2-Nov-07		22:07:53		69.8		47		13-Dec-07		22:25:59		68		28.5

		3-Nov-07		0:07:10		71.6		42		3-Nov-07		0:06:20		69.2		46		3-Nov-07		0:07:53		68		46.5		14-Dec-07		0:25:59		66.2		29.5

		3-Nov-07		2:07:10		71		40.5		3-Nov-07		2:06:20		69.2		43.5		3-Nov-07		2:07:53		66.81		46.5		14-Dec-07		2:25:59		64.4		29.5

		3-Nov-07		4:07:10		70.41		40		3-Nov-07		4:06:20		68		42.5		3-Nov-07		4:07:53		66.81		45		14-Dec-07		4:25:59		63.8		30

		3-Nov-07		6:07:10		70.41		38		3-Nov-07		6:06:20		67.4		40.5		3-Nov-07		6:07:53		67.4		42.5		14-Dec-07		6:25:59		65.01		29

		3-Nov-07		8:07:10		72.8		36.5		3-Nov-07		8:06:20		69.2		42		3-Nov-07		8:07:53		68.61		39		14-Dec-07		8:25:59		66.81		27

		3-Nov-07		10:07:10		74.01		39.5		3-Nov-07		10:06:20		71.6		46		3-Nov-07		10:07:53		70.41		47		14-Dec-07		10:25:59		70.41		28.5

		3-Nov-07		12:07:10		74.6		40		3-Nov-07		12:06:20		71.6		46.5		3-Nov-07		12:07:53		71.6		45.5		14-Dec-07		12:25:59		72.21		28.5

		3-Nov-07		14:07:10		74.6		42		3-Nov-07		14:06:20		70.41		50		3-Nov-07		14:07:53		71		52		14-Dec-07		14:25:59		72.21		29.5

		3-Nov-07		16:07:10		74.01		42.5		3-Nov-07		16:06:20		69.8		50.5		3-Nov-07		16:07:53		71		49.5		14-Dec-07		16:25:59		72.21		30.5

		3-Nov-07		18:07:10		74.01		47.5		3-Nov-07		18:06:20		69.2		59.5		3-Nov-07		18:07:53		71		47		14-Dec-07		18:25:59		72.8		31.5

		3-Nov-07		20:07:10		74.6		42		3-Nov-07		20:06:20		71		47.5		3-Nov-07		20:07:53		70.41		48.5		14-Dec-07		20:25:59		71		31.5

		3-Nov-07		22:07:10		74.01		40.5		3-Nov-07		22:06:20		71		45		3-Nov-07		22:07:53		69.8		45.5		14-Dec-07		22:25:59		68.61		31

		4-Nov-07		0:07:10		72.8		38.5		4-Nov-07		0:06:20		69.8		42		4-Nov-07		0:07:53		68		44.5		15-Dec-07		0:25:59		66.2		31.5

		4-Nov-07		2:07:10		71.6		37.5		4-Nov-07		2:06:20		69.8		40		4-Nov-07		2:07:53		66.81		44		15-Dec-07		2:25:59		64.4		31.5

		4-Nov-07		4:07:10		71		36.5		4-Nov-07		4:06:20		69.2		39		4-Nov-07		4:07:53		65.01		43.5		15-Dec-07		4:25:59		63.21		31

		4-Nov-07		6:07:10		69.8		35.5		4-Nov-07		6:06:20		68.61		38		4-Nov-07		6:07:53		63.8		43.5		15-Dec-07		6:25:59		64.4		30

		4-Nov-07		8:07:10		69.2		35		4-Nov-07		8:06:20		67.4		38		4-Nov-07		8:07:53		66.81		39		15-Dec-07		8:25:59		66.81		28.5

		4-Nov-07		10:07:10		69.8		37.5		4-Nov-07		10:06:20		68.61		40.5		4-Nov-07		10:07:53		67.4		41		15-Dec-07		10:25:59		69.2		30

		4-Nov-07		12:07:10		70.41		40.5		4-Nov-07		12:06:20		68.61		43		4-Nov-07		12:07:53		68.61		43.5		15-Dec-07		12:25:59		72.21		31

		4-Nov-07		14:07:10		71		41		4-Nov-07		14:06:20		69.2		39.5		4-Nov-07		14:07:53		70.41		41		15-Dec-07		14:25:59		71.6		32

		4-Nov-07		16:07:10		72.21		42.5		4-Nov-07		16:06:20		69.2		41.5		4-Nov-07		16:07:53		70.41		46.5		15-Dec-07		16:25:59		72.21		31.5

		4-Nov-07		18:07:10		72.8		38.5		4-Nov-07		18:06:20		69.2		41		4-Nov-07		18:07:53		69.8		44		15-Dec-07		18:25:59		71.6		34

		4-Nov-07		20:07:10		72.8		36		4-Nov-07		20:06:20		70.41		39		4-Nov-07		20:07:53		70.41		40		15-Dec-07		20:25:59		71		34.5

		4-Nov-07		22:07:10		72.8		35.5		4-Nov-07		22:06:20		70.41		39		4-Nov-07		22:07:53		69.2		40		15-Dec-07		22:25:59		68.61		34

		5-Nov-07		0:07:10		72.21		36.5		5-Nov-07		0:06:20		70.41		40		5-Nov-07		0:07:53		67.4		42		16-Dec-07		0:25:59		67.4		35

		5-Nov-07		2:07:10		71.6		36		5-Nov-07		2:06:20		70.41		38.5		5-Nov-07		2:07:53		65.6		42		16-Dec-07		2:25:59		66.81		35

		5-Nov-07		4:07:10		70.41		35.5		5-Nov-07		4:06:20		69.2		37.5		5-Nov-07		4:07:53		64.4		42.5		16-Dec-07		4:25:59		66.2		35.5

		5-Nov-07		6:07:10		69.8		34.5		5-Nov-07		6:06:20		68.61		37		5-Nov-07		6:07:53		64.4		41.5		16-Dec-07		6:25:59		66.2		35.5

		5-Nov-07		8:07:10		69.2		34		5-Nov-07		8:06:20		67.4		37		5-Nov-07		8:07:53		66.81		37.5		16-Dec-07		8:25:59		65.6		35.5

		5-Nov-07		10:07:10		69.2		37		5-Nov-07		10:06:20		68		40		5-Nov-07		10:07:53		67.4		40.5		16-Dec-07		10:25:59		65.6		36

		5-Nov-07		12:07:10		69.8		39		5-Nov-07		12:06:20		68.61		39		5-Nov-07		12:07:53		68		42		16-Dec-07		12:25:59		66.2		37.5

		5-Nov-07		14:07:10		71		40.5		5-Nov-07		14:06:20		68.61		43		5-Nov-07		14:07:53		69.8		42.5		16-Dec-07		14:25:59		66.2		38.5

		5-Nov-07		16:07:10		71.6		41.5		5-Nov-07		16:06:20		69.2		40.5		5-Nov-07		16:07:53		69.8		45		16-Dec-07		16:25:59		66.2		40

		5-Nov-07		18:07:10		72.21		40.5		5-Nov-07		18:06:20		68.61		45		5-Nov-07		18:07:53		70.41		43.5		16-Dec-07		18:25:59		65.6		41.5

		5-Nov-07		20:07:10		72.8		40		5-Nov-07		20:06:20		71		43		5-Nov-07		20:07:53		70.41		44.5		16-Dec-07		20:25:59		65.01		42

		5-Nov-07		22:07:10		72.21		40.5		5-Nov-07		22:06:20		70.41		44.5		5-Nov-07		22:07:53		69.2		44.5		16-Dec-07		22:25:59		65.01		42

		6-Nov-07		0:07:10		71.6		39		6-Nov-07		0:06:20		70.41		41.5		6-Nov-07		0:07:53		67.4		44		17-Dec-07		0:25:59		64.4		42.5

		6-Nov-07		2:07:10		71		38		6-Nov-07		2:06:20		69.8		40		6-Nov-07		2:07:53		66.2		44		17-Dec-07		2:25:59		63.8		43.5

		6-Nov-07		4:07:10		69.8		36		6-Nov-07		4:06:20		68.61		38		6-Nov-07		4:07:53		65.01		42.5		17-Dec-07		4:25:59		63.8		43.5

		6-Nov-07		6:07:10		69.2		35		6-Nov-07		6:06:20		67.4		37		6-Nov-07		6:07:53		67.4		38		17-Dec-07		6:25:59		63.21		43

		6-Nov-07		8:07:10		71.6		33.5		6-Nov-07		8:06:20		68		36		6-Nov-07		8:07:53		68		37		17-Dec-07		8:25:59		64.4		44

		6-Nov-07		10:07:10		72.8		35.5		6-Nov-07		10:06:20		70.41		42.5		6-Nov-07		10:07:53		70.41		35.5		17-Dec-07		10:25:59		65.6		43.5

		6-Nov-07		12:07:10		74.01		38.5		6-Nov-07		12:06:20		70.41		47.5		6-Nov-07		12:07:53		70.41		46.5		17-Dec-07		12:25:59		66.2		43.5

		6-Nov-07		14:07:10		74.01		37		6-Nov-07		14:06:20		71		39		6-Nov-07		14:07:53		70.41		49.5		17-Dec-07		14:25:59		66.2		42

		6-Nov-07		16:07:10		74.6		44		6-Nov-07		16:06:20		70.41		48.5		6-Nov-07		16:07:53		71		49		17-Dec-07		16:25:59		66.81		41.5

		6-Nov-07		18:07:10		74.6		41.5		6-Nov-07		18:06:20		69.2		43		6-Nov-07		18:07:53		70.41		46.5		17-Dec-07		18:25:59		66.81		41.5

		6-Nov-07		20:07:10		73.4		39.5		6-Nov-07		20:06:20		70.41		44.5		6-Nov-07		20:07:53		69.8		44.5		17-Dec-07		20:25:59		65.6		41.5

		6-Nov-07		22:07:10		72.8		40		6-Nov-07		22:06:20		70.41		44		6-Nov-07		22:07:53		68		46		17-Dec-07		22:25:59		65.01		43.5

		7-Nov-07		0:07:10		72.21		40.5		7-Nov-07		0:06:20		70.41		44.5		7-Nov-07		0:07:53		67.4		47		18-Dec-07		0:25:59		64.4		44.5

		7-Nov-07		2:07:10		71.6		41		7-Nov-07		2:06:20		70.41		44		7-Nov-07		2:07:53		66.2		48		18-Dec-07		2:25:59		63.8		45

		7-Nov-07		4:07:10		71		41		7-Nov-07		4:06:20		69.8		43.5		7-Nov-07		4:07:53		65.6		48.5		18-Dec-07		4:25:59		63.8		44

		7-Nov-07		6:07:10		70.41		41.5		7-Nov-07		6:06:20		69.8		43.5		7-Nov-07		6:07:53		67.4		45		18-Dec-07		6:25:59		65.6		46

		7-Nov-07		8:07:10		71.6		41.5		7-Nov-07		8:06:20		68.61		45		7-Nov-07		8:07:53		70.41		43.5		18-Dec-07		8:25:59		68		45

		7-Nov-07		10:07:10		72.8		41		7-Nov-07		10:06:20		70.41		47.5		7-Nov-07		10:07:53		71		44		18-Dec-07		10:25:59		71		45

		7-Nov-07		12:07:10		72.8		40		7-Nov-07		12:06:20		71		38.5		7-Nov-07		12:07:53		70.41		45.5		18-Dec-07		12:25:59		71.6		44

		7-Nov-07		14:07:10		73.4		42.5		7-Nov-07		14:06:20		71		50.5		7-Nov-07		14:07:53		70.41		45.5		18-Dec-07		14:25:59		71.6		45.5

		7-Nov-07		16:07:10		74.01		46		7-Nov-07		16:06:20		70.41		46		7-Nov-07		16:07:53		71		53		18-Dec-07		16:25:59		71.6		45

		7-Nov-07		18:07:10		74.01		43.5		7-Nov-07		18:06:20		69.2		51.5		7-Nov-07		18:07:53		69.8		50		18-Dec-07		18:25:59		72.21		44

		7-Nov-07		20:07:10		72.8		40.5		7-Nov-07		20:06:20		70.41		44		7-Nov-07		20:07:53		69.2		45.5		18-Dec-07		20:25:59		70.41		43

		7-Nov-07		22:07:10		72.21		39		7-Nov-07		22:06:20		70.41		41		7-Nov-07		22:07:53		68		44		18-Dec-07		22:25:59		68.61		44

		8-Nov-07		0:07:10		71.6		40		8-Nov-07		0:06:20		70.41		42.5		8-Nov-07		0:07:53		66.81		46.5		19-Dec-07		0:25:59		67.4		45

		8-Nov-07		2:07:10		71		40.5		8-Nov-07		2:06:20		70.41		42		8-Nov-07		2:07:53		65.6		47.5		19-Dec-07		2:25:59		66.2		46

		8-Nov-07		4:07:10		70.41		39.5		8-Nov-07		4:06:20		69.8		40.5		8-Nov-07		4:07:53		65.01		47		19-Dec-07		4:25:59		65.01		46.5

		8-Nov-07		6:07:10		69.8		39.5		8-Nov-07		6:06:20		69.8		40		8-Nov-07		6:07:53		67.4		43		19-Dec-07		6:25:59		65.6		49

		8-Nov-07		8:07:10		71.6		38.5		8-Nov-07		8:06:20		68.61		42.5		8-Nov-07		8:07:53		69.2		41.5		19-Dec-07		8:25:59		69.2		46.5

		8-Nov-07		10:07:10		71		40		8-Nov-07		10:06:20		67.4		47		8-Nov-07		10:07:53		71		41		19-Dec-07		10:25:59		71.6		47

		8-Nov-07		12:07:10		72.21		43		8-Nov-07		12:06:20		70.41		46.5		8-Nov-07		12:07:53		70.41		47		19-Dec-07		12:25:59		72.21		46.5

		8-Nov-07		14:07:10		71.6		41		8-Nov-07		14:06:20		68		43		8-Nov-07		14:07:53		71.6		45.5		19-Dec-07		14:25:59		72.21		49.5

		8-Nov-07		16:07:10		74.01		43.5		8-Nov-07		16:06:20		71.6		43		8-Nov-07		16:07:53		70.41		53		19-Dec-07		16:25:59		72.8		46.5

		8-Nov-07		18:07:10		73.4		43		8-Nov-07		18:06:20		71		47.5		8-Nov-07		18:07:53		69.8		48		19-Dec-07		18:25:59		72.21		44.5

		8-Nov-07		20:07:10		71.6		43		8-Nov-07		20:06:20		69.2		46.5		8-Nov-07		20:07:53		69.8		47		19-Dec-07		20:25:59		71.6		42

		8-Nov-07		22:07:10		71.6		44		8-Nov-07		22:06:20		68.61		48		8-Nov-07		22:07:53		68.61		48		19-Dec-07		22:25:59		69.2		43

		9-Nov-07		0:07:10		71		43		9-Nov-07		0:06:20		68.61		46.5		9-Nov-07		0:07:53		68		47		20-Dec-07		0:25:59		68		42.5

		9-Nov-07		2:07:10		70.41		44		9-Nov-07		2:06:20		68.61		47.5		9-Nov-07		2:07:53		67.4		48.5		20-Dec-07		2:25:59		67.4		42.5

		9-Nov-07		4:07:10		70.41		44.5		9-Nov-07		4:06:20		68.61		47.5		9-Nov-07		4:07:53		66.81		49.5		20-Dec-07		4:25:59		66.81		42.5

		9-Nov-07		6:07:10		69.8		44		9-Nov-07		6:06:20		68.61		46.5		9-Nov-07		6:07:53		68		47		20-Dec-07		6:25:59		67.4		42.5

		9-Nov-07		8:07:10		71.6		43		9-Nov-07		8:06:20		69.8		46		9-Nov-07		8:07:53		70.41		47		20-Dec-07		8:25:59		69.8		41.5

		9-Nov-07		10:07:10		71.6		44.5		9-Nov-07		10:06:20		71		48		9-Nov-07		10:07:53		71.6		47.5		20-Dec-07		10:25:59		71.6		41.5

		9-Nov-07		12:07:10		72.21		45		9-Nov-07		12:06:20		71		49		9-Nov-07		12:07:53		70.41		48		20-Dec-07		12:25:59		72.8		41

		9-Nov-07		14:07:10		74.01		42.5		9-Nov-07		14:06:20		71.6		44.5		9-Nov-07		14:07:53		71		49.5		20-Dec-07		14:25:59		72.8		42.5

		9-Nov-07		16:07:10		74.01		44		9-Nov-07		16:06:20		71.6		49		9-Nov-07		16:07:53		69.8		49.5		20-Dec-07		16:25:59		72.8		43.5

		9-Nov-07		18:07:10		72.8		42.5		9-Nov-07		18:06:20		70.41		46.5		9-Nov-07		18:07:53		69.8		50		20-Dec-07		18:25:59		72.8		43

		9-Nov-07		20:07:10		72.8		42.5		9-Nov-07		20:06:20		69.8		46		9-Nov-07		20:07:53		69.2		47		20-Dec-07		20:25:59		71.6		43

		9-Nov-07		22:07:10		71.6		43.5		9-Nov-07		22:06:20		69.2		47		9-Nov-07		22:07:53		69.2		47.5		20-Dec-07		22:25:59		70.41		45

		10-Nov-07		0:07:10		71		44.5		10-Nov-07		0:06:20		69.2		48.5		10-Nov-07		0:07:53		68.61		48.5		21-Dec-07		0:25:59		69.2		45.5

		10-Nov-07		2:07:10		71		45		10-Nov-07		2:06:20		68.61		49.5		10-Nov-07		2:07:53		68		49.5		21-Dec-07		2:25:59		68.61		46.5

		10-Nov-07		4:07:10		70.41		45		10-Nov-07		4:06:20		68.61		48		10-Nov-07		4:07:53		67.4		49.5		21-Dec-07		4:25:59		68.61		46.5

		10-Nov-07		6:07:10		69.8		42		10-Nov-07		6:06:20		68.61		45		10-Nov-07		6:07:53		66.81		47		21-Dec-07		6:25:59		68.61		46

		10-Nov-07		8:07:10		72.21		40		10-Nov-07		8:06:20		68.61		44		10-Nov-07		8:07:53		69.8		44		21-Dec-07		8:25:59		70.41		41

		10-Nov-07		10:07:10		74.01		39.5		10-Nov-07		10:06:20		71		42		10-Nov-07		10:07:53		70.41		47		21-Dec-07		10:25:59		72.8		40.5

		10-Nov-07		12:07:10		73.4		41		10-Nov-07		12:06:20		71		48.5		10-Nov-07		12:07:53		70.41		47		21-Dec-07		12:25:59		72.21		38.5

		10-Nov-07		14:07:10		73.4		40		10-Nov-07		14:06:20		71.6		41		10-Nov-07		14:07:53		71		51		21-Dec-07		14:25:59		72.8		37

		10-Nov-07		16:07:10		74.01		44		10-Nov-07		16:06:20		71		50		10-Nov-07		16:07:53		70.41		41.5		21-Dec-07		16:25:59		72.21		35.5

		10-Nov-07		18:07:10		73.4		44.5		10-Nov-07		18:06:20		69.8		51		10-Nov-07		18:07:53		70.41		52.5		21-Dec-07		18:25:59		71.6		34.5

		10-Nov-07		20:07:10		72.8		44		10-Nov-07		20:06:20		69.2		48.5		10-Nov-07		20:07:53		69.8		48.5		21-Dec-07		20:25:59		69.8		34.5

		10-Nov-07		22:07:10		71.6		42.5		10-Nov-07		22:06:20		68.61		46.5		10-Nov-07		22:07:53		69.2		46.5		21-Dec-07		22:25:59		68.61		35

		11-Nov-07		0:07:10		71		41		11-Nov-07		0:06:20		68.61		44.5		11-Nov-07		0:07:53		68		45		22-Dec-07		0:25:59		68		35

		11-Nov-07		2:07:10		70.41		40		11-Nov-07		2:06:20		68		43		11-Nov-07		2:07:53		66.2		45		22-Dec-07		2:25:59		67.4		34.5

		11-Nov-07		4:07:10		69.8		40		11-Nov-07		4:06:20		68		44		11-Nov-07		4:07:53		65.6		46.5		22-Dec-07		4:25:59		66.2		34

		11-Nov-07		6:07:10		69.8		41		11-Nov-07		6:06:20		68		45.5		11-Nov-07		6:07:53		65.01		48		22-Dec-07		6:25:59		66.81		33

		11-Nov-07		8:07:10		69.8		43		11-Nov-07		8:06:20		68		47.5		11-Nov-07		8:07:53		67.4		47		22-Dec-07		8:25:59		69.2		30.5

		11-Nov-07		10:07:10		69.8		46		11-Nov-07		10:06:20		68		51		11-Nov-07		10:07:53		68		48.5		22-Dec-07		10:25:59		70.41		31

		11-Nov-07		12:07:10		69.8		50		11-Nov-07		12:06:20		68		55		11-Nov-07		12:07:53		67.4		53.5		22-Dec-07		12:25:59		71		30

		11-Nov-07		14:07:10		70.41		52.5		11-Nov-07		14:06:20		68.61		57.5		11-Nov-07		14:07:53		68		54.5		22-Dec-07		14:25:59		70.41		30

		11-Nov-07		16:07:10		70.41		53.5		11-Nov-07		16:06:20		68.61		58.5		11-Nov-07		16:07:53		68		55.5		22-Dec-07		16:25:59		71.6		29.5

		11-Nov-07		18:07:10		70.41		54.5		11-Nov-07		18:06:20		68.61		59		11-Nov-07		18:07:53		68.61		56.5		22-Dec-07		18:25:59		70.41		30

		11-Nov-07		20:07:10		70.41		54.5		11-Nov-07		20:06:20		68.61		59		11-Nov-07		20:07:53		68.61		56		22-Dec-07		20:25:59		69.2		30.5

		11-Nov-07		22:07:10		70.41		55		11-Nov-07		22:06:20		68.61		59.5		11-Nov-07		22:07:53		68		56.5		22-Dec-07		22:25:59		66.81		31.5

		12-Nov-07		0:07:10		70.41		55		12-Nov-07		0:06:20		68.61		59		12-Nov-07		0:07:53		68		57		23-Dec-07		0:25:59		64.4		32

		12-Nov-07		2:07:10		70.41		55		12-Nov-07		2:06:20		68.61		59		12-Nov-07		2:07:53		68		57.5		23-Dec-07		2:25:59		63.21		32.5

		12-Nov-07		4:07:10		69.8		50.5		12-Nov-07		4:06:20		68.61		52		12-Nov-07		4:07:53		67.4		55.5		23-Dec-07		4:25:59		62.6		31.5

		12-Nov-07		6:07:10		69.8		45.5		12-Nov-07		6:06:20		68.61		46		12-Nov-07		6:07:53		66.2		51.5		23-Dec-07		6:25:59		62		31

		12-Nov-07		8:07:10		69.2		43.5		12-Nov-07		8:06:20		68		45.5		12-Nov-07		8:07:53		67.4		47		23-Dec-07		8:25:59		62.6		31

		12-Nov-07		10:07:10		69.2		44		12-Nov-07		10:06:20		68.61		46		12-Nov-07		10:07:53		68		47		23-Dec-07		10:25:59		62.6		32

		12-Nov-07		12:07:10		70.41		43		12-Nov-07		12:06:20		69.2		43.5		12-Nov-07		12:07:53		68		46.5		23-Dec-07		12:25:59		62.6		33.5

		12-Nov-07		14:07:10		71		39.5		12-Nov-07		14:06:20		69.2		39		12-Nov-07		14:07:53		69.2		43		23-Dec-07		14:25:59		65.01		35

		12-Nov-07		16:07:10		71		38.5		12-Nov-07		16:06:20		69.2		38.5		12-Nov-07		16:07:53		69.8		42.5		23-Dec-07		16:25:59		65.01		34

		12-Nov-07		18:07:10		71.6		39		12-Nov-07		18:06:20		69.8		38.5		12-Nov-07		18:07:53		69.8		42.5		23-Dec-07		18:25:59		64.4		34

		12-Nov-07		20:07:10		71		39.5		12-Nov-07		20:06:20		68.61		42		12-Nov-07		20:07:53		69.2		43		23-Dec-07		20:25:59		63.21		35.5

		12-Nov-07		22:07:10		70.41		39		12-Nov-07		22:06:20		68.61		41.5		12-Nov-07		22:07:53		67.4		43		23-Dec-07		22:25:59		62.6		35.5

		13-Nov-07		0:07:10		69.8		38.5		13-Nov-07		0:06:20		68		41		13-Nov-07		0:07:53		65.6		43.5		24-Dec-07		0:25:59		62.6		36

		13-Nov-07		2:07:10		69.2		38		13-Nov-07		2:06:20		68		40.5		13-Nov-07		2:07:53		64.4		44.5		24-Dec-07		2:25:59		62		36

		13-Nov-07		4:07:10		69.2		38		13-Nov-07		4:06:20		68		40.5		13-Nov-07		4:07:53		63.8		45		24-Dec-07		4:25:59		62		36

		13-Nov-07		6:07:10		68.61		39		13-Nov-07		6:06:20		68		41.5		13-Nov-07		6:07:53		66.81		43		24-Dec-07		6:25:59		62		36

		13-Nov-07		8:07:10		71.6		38		13-Nov-07		8:06:20		69.2		41		13-Nov-07		8:07:53		69.2		41.5		24-Dec-07		8:25:59		62		36

		13-Nov-07		10:07:10		72.8		38		13-Nov-07		10:06:20		70.41		42.5		13-Nov-07		10:07:53		71		41		24-Dec-07		10:25:59		62		36.5

		13-Nov-07		12:07:10		75.2		37.5		13-Nov-07		12:06:20		71		40		13-Nov-07		12:07:53		70.41		42.5		24-Dec-07		12:25:59		62		38

		13-Nov-07		14:07:10		74.6		35		13-Nov-07		14:06:20		71.6		38.5		13-Nov-07		14:07:53		71.6		42		24-Dec-07		14:25:59		63.21		41.5

		13-Nov-07		16:07:10		74.01		34.5		13-Nov-07		16:06:20		71.6		37.5		13-Nov-07		16:07:53		70.41		41		24-Dec-07		16:25:59		64.4		42.5

		13-Nov-07		18:07:10		74.01		32		13-Nov-07		18:06:20		69.8		31.5		13-Nov-07		18:07:53		70.41		38		24-Dec-07		18:25:59		65.6		43

		13-Nov-07		20:07:10		73.4		37		13-Nov-07		20:06:20		69.8		42		13-Nov-07		20:07:53		70.41		42		24-Dec-07		20:25:59		65.01		45.5

		13-Nov-07		22:07:10		72.8		40		13-Nov-07		22:06:20		69.8		45		13-Nov-07		22:07:53		69.8		44		24-Dec-07		22:25:59		64.4		44.5

		14-Nov-07		0:07:10		72.21		42		14-Nov-07		0:06:20		69.2		47.5		14-Nov-07		0:07:53		69.8		45		25-Dec-07		0:25:59		63.8		45

		14-Nov-07		2:07:10		72.21		43		14-Nov-07		2:06:20		69.8		48		14-Nov-07		2:07:53		69.2		47.5		25-Dec-07		2:25:59		63.8		45

		14-Nov-07		4:07:10		71.6		44.5		14-Nov-07		4:06:20		69.2		50		14-Nov-07		4:07:53		68.61		48.5		25-Dec-07		4:25:59		63.21		44.5

		14-Nov-07		6:07:10		71		46		14-Nov-07		6:06:20		69.2		51.5		14-Nov-07		6:07:53		68.61		50		25-Dec-07		6:25:59		64.4		44

		14-Nov-07		8:07:10		73.4		45		14-Nov-07		8:06:20		69.8		51.5		14-Nov-07		8:07:53		70.41		44		25-Dec-07		8:25:59		66.81		40.5

		14-Nov-07		10:07:10		74.01		46		14-Nov-07		10:06:20		71.6		54.5		14-Nov-07		10:07:53		70.41		53		25-Dec-07		10:25:59		69.2		36.5

		14-Nov-07		12:07:10		74.01		47.5		14-Nov-07		12:06:20		72.21		54		14-Nov-07		12:07:53		70.41		47		25-Dec-07		12:25:59		70.41		34.5

		14-Nov-07		14:07:10		74.01		48		14-Nov-07		14:06:20		72.21		45		14-Nov-07		14:07:53		70.41		47		25-Dec-07		14:25:59		71		33

		14-Nov-07		16:07:10		74.6		49.5		14-Nov-07		16:06:20		71.6		44.5		14-Nov-07		16:07:53		71		59.5		25-Dec-07		16:25:59		70.41		33.5

		14-Nov-07		18:07:10		74.6		49.5		14-Nov-07		18:06:20		71		49		14-Nov-07		18:07:53		71		53.5		25-Dec-07		18:25:59		68.61		33.5

		14-Nov-07		20:07:10		74.01		49		14-Nov-07		20:06:20		70.41		52.5		14-Nov-07		20:07:53		70.41		57.5		25-Dec-07		20:25:59		66.81		35

		14-Nov-07		22:07:10		73.4		52		14-Nov-07		22:06:20		69.8		61		14-Nov-07		22:07:53		71		55.5		25-Dec-07		22:25:59		64.4		35.5

		15-Nov-07		0:07:10		72.8		52		15-Nov-07		0:06:20		69.8		57		15-Nov-07		0:07:53		71		54		26-Dec-07		0:25:59		63.21		35

		15-Nov-07		2:07:10		72.21		50.5		15-Nov-07		2:06:20		69.8		56		15-Nov-07		2:07:53		70.41		53.5		26-Dec-07		2:25:59		62.6		34

		15-Nov-07		4:07:10		71.6		47		15-Nov-07		4:06:20		68.61		50.5		15-Nov-07		4:07:53		69.8		50.5		26-Dec-07		4:25:59		62		33.5

		15-Nov-07		6:07:10		71		45.5		15-Nov-07		6:06:20		68.61		49		15-Nov-07		6:07:53		68.61		49.5		26-Dec-07		6:25:59		62		33

		15-Nov-07		8:07:10		72.21		43.5		15-Nov-07		8:06:20		69.2		47		15-Nov-07		8:07:53		70.41		47.5		26-Dec-07		8:25:59		62.6		32.5

		15-Nov-07		10:07:10		74.01		44.5		15-Nov-07		10:06:20		71.6		56		15-Nov-07		10:07:53		71		46.5		26-Dec-07		10:25:59		62		32.5

		15-Nov-07		12:07:10		74.01		46.5		15-Nov-07		12:06:20		71.6		54		15-Nov-07		12:07:53		71.6		50.5		26-Dec-07		12:25:59		62		33.5

		15-Nov-07		14:07:10		74.01		47.5		15-Nov-07		14:06:20		71.6		56		15-Nov-07		14:07:53		71		52		26-Dec-07		14:25:59		62.6		34.5

		15-Nov-07		16:07:10		74.6		50		15-Nov-07		16:06:20		71.6		45.5		15-Nov-07		16:07:53		70.41		56		26-Dec-07		16:25:59		63.8		35.5

		15-Nov-07		18:07:10		74.01		51		15-Nov-07		18:06:20		70.41		51		15-Nov-07		18:07:53		70.41		56		26-Dec-07		18:25:59		63.8		37

		15-Nov-07		20:07:10		73.4		50		15-Nov-07		20:06:20		69.8		56.5		15-Nov-07		20:07:53		71		55.5		26-Dec-07		20:25:59		63.21		38

		15-Nov-07		22:07:10		73.4		48.5		15-Nov-07		22:06:20		69.8		54.5		15-Nov-07		22:07:53		71.6		51.5		26-Dec-07		22:25:59		62.6		37.5

		16-Nov-07		0:07:10		72.8		46.5		16-Nov-07		0:06:20		69.8		51		16-Nov-07		0:07:53		71		50		27-Dec-07		0:25:59		62		38.5

		16-Nov-07		2:07:10		71.6		45.5		16-Nov-07		2:06:20		68.61		49.5		16-Nov-07		2:07:53		69.2		49		27-Dec-07		2:25:59		62		39

		16-Nov-07		4:07:10		71		45.5		16-Nov-07		4:06:20		68.61		49.5		16-Nov-07		4:07:53		68.61		49.5		27-Dec-07		4:25:59		62		38

		16-Nov-07		6:07:10		70.41		44		16-Nov-07		6:06:20		68.61		47.5		16-Nov-07		6:07:53		67.4		49		27-Dec-07		6:25:59		62		37.5

		16-Nov-07		8:07:10		71.6		42.5		16-Nov-07		8:06:20		68.61		46		16-Nov-07		8:07:53		70.41		46		27-Dec-07		8:25:59		63.21		36.5

		16-Nov-07		10:07:10		72.8		44.5		16-Nov-07		10:06:20		71		49.5		16-Nov-07		10:07:53		72.21		47		27-Dec-07		10:25:59		67.4		35

		16-Nov-07		12:07:10		73.4		45		16-Nov-07		12:06:20		71.6		50.5		16-Nov-07		12:07:53		71		47		27-Dec-07		12:25:59		72.21		30.5

		16-Nov-07		14:07:10		74.01		46.5		16-Nov-07		14:06:20		71.6		53.5		16-Nov-07		14:07:53		71.6		51.5		27-Dec-07		14:25:59		71		28

		16-Nov-07		16:07:10		74.01		50		16-Nov-07		16:06:20		71.6		52		16-Nov-07		16:07:53		71		60.5		27-Dec-07		16:25:59		71		26

		16-Nov-07		18:07:10		74.01		49.5		16-Nov-07		18:06:20		70.41		62		16-Nov-07		18:07:53		70.41		53.5		27-Dec-07		18:25:59		70.41		26

		16-Nov-07		20:07:10		73.4		51		16-Nov-07		20:06:20		69.8		57.5		16-Nov-07		20:07:53		70.41		57		27-Dec-07		20:25:59		69.2		26.5

		16-Nov-07		22:07:10		72.8		51		16-Nov-07		22:06:20		69.8		56.5		16-Nov-07		22:07:53		70.41		55.5		27-Dec-07		22:25:59		66.2		31.5

		17-Nov-07		0:07:10		72.21		50.5		17-Nov-07		0:06:20		69.8		56		17-Nov-07		0:07:53		70.41		54		28-Dec-07		0:25:59		63.8		29.5

		17-Nov-07		2:07:10		71.6		50.5		17-Nov-07		2:06:20		69.2		56		17-Nov-07		2:07:53		69.8		53.5		28-Dec-07		2:25:59		62.6		29.5

		17-Nov-07		4:07:10		71.6		50.5		17-Nov-07		4:06:20		69.2		55.5		17-Nov-07		4:07:53		69.2		54		28-Dec-07		4:25:59		62.6		29.5

		17-Nov-07		6:07:10		71		49.5		17-Nov-07		6:06:20		68		54		17-Nov-07		6:07:53		68.61		53.5		28-Dec-07		6:25:59		62.6		29

		17-Nov-07		8:07:10		71.6		49.5		17-Nov-07		8:06:20		68		55		17-Nov-07		8:07:53		71		53		28-Dec-07		8:25:59		65.01		28.5

		17-Nov-07		10:07:10		72.21		47.5		17-Nov-07		10:06:20		71		51.5		17-Nov-07		10:07:53		71		49.5		28-Dec-07		10:25:59		68.61		28

		17-Nov-07		12:07:10		73.4		47.5		17-Nov-07		12:06:20		72.21		55		17-Nov-07		12:07:53		71.6		55.5		28-Dec-07		12:25:59		71.6		27

		17-Nov-07		14:07:10		74.01		49.5		17-Nov-07		14:06:20		71		46		17-Nov-07		14:07:53		71		57.5		28-Dec-07		14:25:59		71		28.5

		17-Nov-07		16:07:10		74.6		50		17-Nov-07		16:06:20		71.6		48		17-Nov-07		16:07:53		70.41		58		28-Dec-07		16:25:59		71		28.5

		17-Nov-07		18:07:10		74.6		48.5		17-Nov-07		18:06:20		69.8		55		17-Nov-07		18:07:53		70.41		50		28-Dec-07		18:25:59		72.21		29.5

		17-Nov-07		20:07:10		72.8		47.5		17-Nov-07		20:06:20		69.8		52		17-Nov-07		20:07:53		69.8		52		28-Dec-07		20:25:59		71		32

		17-Nov-07		22:07:10		71.6		48		17-Nov-07		22:06:20		69.2		53.5		17-Nov-07		22:07:53		69.2		51.5		28-Dec-07		22:25:59		68		34.5

		18-Nov-07		0:07:10		71.6		49.5		18-Nov-07		0:06:20		68.61		54		18-Nov-07		0:07:53		69.2		53		29-Dec-07		0:25:59		65.6		35

		18-Nov-07		2:07:10		71		49		18-Nov-07		2:06:20		68		54.5		18-Nov-07		2:07:53		68		53		29-Dec-07		2:25:59		64.4		36

		18-Nov-07		4:07:10		70.41		50		18-Nov-07		4:06:20		68		55		18-Nov-07		4:07:53		67.4		53.5		29-Dec-07		4:25:59		63.21		37

		18-Nov-07		6:07:10		69.8		49.5		18-Nov-07		6:06:20		67.4		54.5		18-Nov-07		6:07:53		66.81		54		29-Dec-07		6:25:59		64.4		37.5

		18-Nov-07		8:07:10		69.8		49.5		18-Nov-07		8:06:20		67.4		54.5		18-Nov-07		8:07:53		67.4		53		29-Dec-07		8:25:59		66.81		36.5

		18-Nov-07		10:07:10		69.2		49.5		18-Nov-07		10:06:20		67.4		54.5		18-Nov-07		10:07:53		67.4		53		29-Dec-07		10:25:59		69.8		36

		18-Nov-07		12:07:10		69.8		51.5		18-Nov-07		12:06:20		67.4		56.5		18-Nov-07		12:07:53		67.4		55.5		29-Dec-07		12:25:59		72.8		34

		18-Nov-07		14:07:10		70.41		52		18-Nov-07		14:06:20		68.61		55.5		18-Nov-07		14:07:53		68		55.5		29-Dec-07		14:25:59		72.8		34

		18-Nov-07		16:07:10		71		53.5		18-Nov-07		16:06:20		69.2		53.5		18-Nov-07		16:07:53		69.8		58		29-Dec-07		16:25:59		73.4		33

		18-Nov-07		18:07:10		71.6		55		18-Nov-07		18:06:20		69.2		56		18-Nov-07		18:07:53		69.8		58.5		29-Dec-07		18:25:59		72.21		33.5

		18-Nov-07		20:07:10		71		52		18-Nov-07		20:06:20		69.2		55.5		18-Nov-07		20:07:53		69.8		54.5		29-Dec-07		20:25:59		71		34

		18-Nov-07		22:07:10		70.41		52		18-Nov-07		22:06:20		68.61		56		18-Nov-07		22:07:53		68.61		55		29-Dec-07		22:25:59		67.4		36

		19-Nov-07		0:07:10		70.41		52		19-Nov-07		0:06:20		68		56		19-Nov-07		0:07:53		68.61		54.5		30-Dec-07		0:25:59		65.01		37.5

		19-Nov-07		2:07:10		69.8		51		19-Nov-07		2:06:20		67.4		56		19-Nov-07		2:07:53		68		55		30-Dec-07		2:25:59		63.8		38

		19-Nov-07		4:07:10		69.8		51		19-Nov-07		4:06:20		67.4		56.5		19-Nov-07		4:07:53		67.4		55.5		30-Dec-07		4:25:59		63.21		39

		19-Nov-07		6:07:10		69.8		51		19-Nov-07		6:06:20		67.4		55.5		19-Nov-07		6:07:53		66.81		56		30-Dec-07		6:25:59		62.6		39.5

		19-Nov-07		8:07:10		69.2		51		19-Nov-07		8:06:20		67.4		55.5		19-Nov-07		8:07:53		67.4		54		30-Dec-07		8:25:59		62.6		40.5

		19-Nov-07		10:07:10		69.2		52		19-Nov-07		10:06:20		67.4		56.5		19-Nov-07		10:07:53		67.4		55.5		30-Dec-07		10:25:59		63.21		42.5

		19-Nov-07		12:07:10		69.8		54.5		19-Nov-07		12:06:20		68		60		19-Nov-07		12:07:53		67.4		58		30-Dec-07		12:25:59		63.21		43.5

		19-Nov-07		14:07:10		70.41		56.5		19-Nov-07		14:06:20		68.61		60		19-Nov-07		14:07:53		68.61		59.5		30-Dec-07		14:25:59		63.8		44.5

		19-Nov-07		16:07:10		71		59		19-Nov-07		16:06:20		69.2		65		19-Nov-07		16:07:53		69.2		61.5		30-Dec-07		16:25:59		63.21		45

		19-Nov-07		18:07:10		71		55		19-Nov-07		18:06:20		69.8		54		19-Nov-07		18:07:53		69.8		59		30-Dec-07		18:25:59		63.21		46

		19-Nov-07		20:07:10		71.6		53		19-Nov-07		20:06:20		69.8		55		19-Nov-07		20:07:53		69.8		56		30-Dec-07		20:25:59		62.6		46.5

		19-Nov-07		22:07:10		71		52		19-Nov-07		22:06:20		69.2		54.5		19-Nov-07		22:07:53		69.2		54.5		30-Dec-07		22:25:59		62.6		47

		20-Nov-07		0:07:10		70.41		50		20-Nov-07		0:06:20		68		53.5		20-Nov-07		0:07:53		68.61		53		31-Dec-07		0:25:59		62.6		47.5

		20-Nov-07		2:07:10		69.8		48.5		20-Nov-07		2:06:20		68		52.5		20-Nov-07		2:07:53		67.4		52.5		31-Dec-07		2:25:59		62.6		48

		20-Nov-07		4:07:10		69.2		50		20-Nov-07		4:06:20		67.4		54.5		20-Nov-07		4:07:53		66.81		54		31-Dec-07		4:25:59		62.6		48.5

		20-Nov-07		6:07:10		69.2		52.5		20-Nov-07		6:06:20		67.4		58		20-Nov-07		6:07:53		67.4		54.5		31-Dec-07		6:25:59		62		48

		20-Nov-07		8:07:10		71		54.5		20-Nov-07		8:06:20		68.61		60		20-Nov-07		8:07:53		69.8		56.5		31-Dec-07		8:25:59		63.21		46

		20-Nov-07		10:07:10		72.8		56		20-Nov-07		10:06:20		70.41		58		20-Nov-07		10:07:53		71		50		31-Dec-07		10:25:59		63.8		44

		20-Nov-07		12:07:10		74.6		50.5		20-Nov-07		12:06:20		71		58.5		20-Nov-07		12:07:53		71.6		58		31-Dec-07		12:25:59		65.01		42.5

		20-Nov-07		14:07:10		74.6		45.5		20-Nov-07		14:06:20		71.6		52		20-Nov-07		14:07:53		71		52		31-Dec-07		14:25:59		65.6		41.5

		20-Nov-07		16:07:10		74.01		41		20-Nov-07		16:06:20		72.21		44		20-Nov-07		16:07:53		70.41		51.5		31-Dec-07		16:25:59		65.6		40.5

		20-Nov-07		18:07:10		73.4		40.5		20-Nov-07		18:06:20		69.8		42.5		20-Nov-07		18:07:53		70.41		48		31-Dec-07		18:25:59		65.6		39

		20-Nov-07		20:07:10		72.8		40		20-Nov-07		20:06:20		69.8		42		20-Nov-07		20:07:53		69.2		45.5		31-Dec-07		20:25:59		64.4		38.5

		20-Nov-07		22:07:10		71.6		39.5		20-Nov-07		22:06:20		68.61		42.5		20-Nov-07		22:07:53		68.61		44		31-Dec-07		22:25:59		62.6		38.5

		21-Nov-07		0:07:10		71		39		21-Nov-07		0:06:20		68.61		40.5		21-Nov-07		0:07:53		68		43		1-Jan-08		0:25:59		62.6		37

		21-Nov-07		2:07:10		70.41		38.5		21-Nov-07		2:06:20		68		40.5		21-Nov-07		2:07:53		66.2		43.5		1-Jan-08		2:25:59		62		36

		21-Nov-07		4:07:10		69.8		37		21-Nov-07		4:06:20		68		39.5		21-Nov-07		4:07:53		65.01		43.5		1-Jan-08		4:25:59		62		35

		21-Nov-07		6:07:10		69.2		36.5		21-Nov-07		6:06:20		68		38.5		21-Nov-07		6:07:53		67.4		39.5		1-Jan-08		6:25:59		62.6		33.5

		21-Nov-07		8:07:10		71		35.5		21-Nov-07		8:06:20		68		37		21-Nov-07		8:07:53		68.61		38		1-Jan-08		8:25:59		65.01		32.5

		21-Nov-07		10:07:10		71.6		35.5		21-Nov-07		10:06:20		69.8		34.5		21-Nov-07		10:07:53		71.6		37		1-Jan-08		10:25:59		68		31

		21-Nov-07		12:07:10		72.8		33.5		21-Nov-07		12:06:20		70.41		34.5		21-Nov-07		12:07:53		70.41		38.5		1-Jan-08		12:25:59		72.21		30.5

		21-Nov-07		14:07:10		73.4		33.5		21-Nov-07		14:06:20		71		35		21-Nov-07		14:07:53		71.6		34.5		1-Jan-08		14:25:59		71.6		31.5

		21-Nov-07		16:07:10		74.6		33.5		21-Nov-07		16:06:20		71		36		21-Nov-07		16:07:53		71		37.5		1-Jan-08		16:25:59		72.21		30.5

		21-Nov-07		18:07:10		74.01		35		21-Nov-07		18:06:20		69.8		37.5		21-Nov-07		18:07:53		70.41		38.5		1-Jan-08		18:25:59		71		31.5

		21-Nov-07		20:07:10		72.8		34		21-Nov-07		20:06:20		69.2		36		21-Nov-07		20:07:53		70.41		38		1-Jan-08		20:25:59		70.41		31.5

		21-Nov-07		22:07:10		71		34		21-Nov-07		22:06:20		68.61		36.5		21-Nov-07		22:07:53		68		37.5		1-Jan-08		22:25:59		66.2		32.5

		22-Nov-07		0:07:10		70.41		33.5		22-Nov-07		0:06:20		68		35.5		22-Nov-07		0:07:53		65.6		38		2-Jan-08		0:25:59		63.8		33

		22-Nov-07		2:07:10		69.8		32		22-Nov-07		2:06:20		68		34		22-Nov-07		2:07:53		64.4		38		2-Jan-08		2:25:59		62.6		33

		22-Nov-07		4:07:10		69.2		31		22-Nov-07		4:06:20		67.4		33		22-Nov-07		4:07:53		63.21		37.5		2-Jan-08		4:25:59		62		32.5

		22-Nov-07		6:07:10		68.61		31		22-Nov-07		6:06:20		68		32.5		22-Nov-07		6:07:53		66.81		33.5		2-Jan-08		6:25:59		62.6		31.5

		22-Nov-07		8:07:10		70.41		30.5		22-Nov-07		8:06:20		69.8		31.5		22-Nov-07		8:07:53		69.2		32		2-Jan-08		8:25:59		63.8		31

		22-Nov-07		10:07:10		71.6		31.5		22-Nov-07		10:06:20		70.41		33.5		22-Nov-07		10:07:53		71.6		33		2-Jan-08		10:25:59		64.4		31

		22-Nov-07		12:07:10		72.21		32.5		22-Nov-07		12:06:20		71		34		22-Nov-07		12:07:53		70.41		35.5		2-Jan-08		12:25:59		66.81		32.5

		22-Nov-07		14:07:10		73.4		31.5		22-Nov-07		14:06:20		71		32.5		22-Nov-07		14:07:53		71.6		33.5		2-Jan-08		14:25:59		68.61		34

		22-Nov-07		16:07:10		73.4		29		22-Nov-07		16:06:20		69.8		29		22-Nov-07		16:07:53		71.6		33		2-Jan-08		16:25:59		70.41		34.5

		22-Nov-07		18:07:10		74.01		31.5		22-Nov-07		18:06:20		69.8		34		22-Nov-07		18:07:53		70.41		36		2-Jan-08		18:25:59		71		33.5

		22-Nov-07		20:07:10		71.6		31		22-Nov-07		20:06:20		68.61		33		22-Nov-07		20:07:53		69.8		34.5		2-Jan-08		20:25:59		70.41		33

		22-Nov-07		22:07:10		70.41		31.5		22-Nov-07		22:06:20		66.81		34.5		22-Nov-07		22:07:53		66.81		35.5		2-Jan-08		22:25:59		66.2		34.5

		23-Nov-07		0:07:10		69.2		31.5		23-Nov-07		0:06:20		66.2		35		23-Nov-07		0:07:53		64.4		37		3-Jan-08		0:25:59		64.4		35.5

		23-Nov-07		2:07:10		68.61		31		23-Nov-07		2:06:20		66.2		34		23-Nov-07		2:07:53		63.21		37		3-Jan-08		2:25:59		62.6		35.5

		23-Nov-07		4:07:10		68		31		23-Nov-07		4:06:20		66.2		33.5		23-Nov-07		4:07:53		62		36.5		3-Jan-08		4:25:59		62		36

		23-Nov-07		6:07:10		67.4		30		23-Nov-07		6:06:20		66.2		31.5		23-Nov-07		6:07:53		66.2		32.5		3-Jan-08		6:25:59		63.8		36

		23-Nov-07		8:07:10		69.2		28.5		23-Nov-07		8:06:20		67.4		30		23-Nov-07		8:07:53		67.4		31		3-Jan-08		8:25:59		65.01		34.5

		23-Nov-07		10:07:10		69.8		30		23-Nov-07		10:06:20		68		33		23-Nov-07		10:07:53		68		32.5		3-Jan-08		10:25:59		67.4		35

		23-Nov-07		12:07:10		70.41		31.5		23-Nov-07		12:06:20		68.61		33		23-Nov-07		12:07:53		68.61		33.5		3-Jan-08		12:25:59		72.8		33.5

		23-Nov-07		14:07:10		71		31		23-Nov-07		14:06:20		69.2		32		23-Nov-07		14:07:53		69.2		34		3-Jan-08		14:25:59		73.4		33

		23-Nov-07		16:07:10		71.6		29.5		23-Nov-07		16:06:20		69.2		29		23-Nov-07		16:07:53		69.8		32.5		3-Jan-08		16:25:59		72.8		34

		23-Nov-07		18:07:10		71.6		31.5		23-Nov-07		18:06:20		69.8		31.5		23-Nov-07		18:07:53		69.8		34		3-Jan-08		18:25:59		72.8		34.5

		23-Nov-07		20:07:10		71.6		32		23-Nov-07		20:06:20		68.61		35		23-Nov-07		20:07:53		68.61		36		3-Jan-08		20:25:59		71.6		35

		23-Nov-07		22:07:10		69.8		32		23-Nov-07		22:06:20		67.4		35.5		23-Nov-07		22:07:53		66.81		36		3-Jan-08		22:25:59		68		36

		24-Nov-07		0:07:10		68.61		32		24-Nov-07		0:06:20		66.2		35.5		24-Nov-07		0:07:53		65.01		36.5		4-Jan-08		0:25:59		65.6		36.5

		24-Nov-07		2:07:10		68		31.5		24-Nov-07		2:06:20		66.2		33.5		24-Nov-07		2:07:53		63.8		36.5		4-Jan-08		2:25:59		64.4		38

		24-Nov-07		4:07:10		67.4		30.5		24-Nov-07		4:06:20		66.2		31.5		24-Nov-07		4:07:53		62.6		35.5		4-Jan-08		4:25:59		63.8		39

		24-Nov-07		6:07:10		67.4		30.5		24-Nov-07		6:06:20		66.2		32.5		24-Nov-07		6:07:53		66.81		32		4-Jan-08		6:25:59		65.01		41

		24-Nov-07		8:07:10		69.2		27		24-Nov-07		8:06:20		68		28		24-Nov-07		8:07:53		68		30		4-Jan-08		8:25:59		68.61		40

		24-Nov-07		10:07:10		70.41		23.5		24-Nov-07		10:06:20		69.2		22		24-Nov-07		10:07:53		68		26		4-Jan-08		10:25:59		71.6		41

		24-Nov-07		12:07:10		71		20.5		24-Nov-07		12:06:20		69.2		18.5		24-Nov-07		12:07:53		68.61		24		4-Jan-08		12:25:59		74.01		40.5

		24-Nov-07		14:07:10		71		19		24-Nov-07		14:06:20		69.2		16		24-Nov-07		14:07:53		69.2		23		4-Jan-08		14:25:59		73.4		42.5

		24-Nov-07		16:07:10		71.6		18.5		24-Nov-07		16:06:20		69.2		16.5		24-Nov-07		16:07:53		69.8		22		4-Jan-08		16:25:59		74.01		41.5

		24-Nov-07		18:07:10		71.6		18.5		24-Nov-07		18:06:20		69.2		17		24-Nov-07		18:07:53		70.41		22		4-Jan-08		18:25:59		73.4		42

		24-Nov-07		20:07:10		71.6		21		24-Nov-07		20:06:20		69.2		22		24-Nov-07		20:07:53		69.2		24.5		4-Jan-08		20:25:59		72.8		43

		24-Nov-07		22:07:10		69.8		24.5		24-Nov-07		22:06:20		67.4		28		24-Nov-07		22:07:53		67.4		28		4-Jan-08		22:25:59		69.8		44

		25-Nov-07		0:07:10		69.2		25.5		25-Nov-07		0:06:20		66.81		29		25-Nov-07		0:07:53		65.6		29.5		5-Jan-08		0:25:59		68		45

		25-Nov-07		2:07:10		68		25.5		25-Nov-07		2:06:20		66.2		28.5		25-Nov-07		2:07:53		63.8		30.5		5-Jan-08		2:25:59		67.4		45.5

		25-Nov-07		4:07:10		67.4		26		25-Nov-07		4:06:20		66.2		28.5		25-Nov-07		4:07:53		62.6		30.5		5-Jan-08		4:25:59		66.81		46

		25-Nov-07		6:07:10		66.81		25.5		25-Nov-07		6:06:20		66.2		28		25-Nov-07		6:07:53		62		31		5-Jan-08		6:25:59		67.4		49

		25-Nov-07		8:07:10		67.4		24.5		25-Nov-07		8:06:20		67.4		26		25-Nov-07		8:07:53		66.81		26.5		5-Jan-08		8:25:59		71.6		48.5

		25-Nov-07		10:07:10		68		26.5		25-Nov-07		10:06:20		68		29		25-Nov-07		10:07:53		67.4		28		5-Jan-08		10:25:59		73.4		48.5

		25-Nov-07		12:07:10		68.61		27.5		25-Nov-07		12:06:20		68		29		25-Nov-07		12:07:53		67.4		30		5-Jan-08		12:25:59		72.8		48.5

		25-Nov-07		14:07:10		69.2		26		25-Nov-07		14:06:20		69.2		26		25-Nov-07		14:07:53		68		29		5-Jan-08		14:25:59		72.21		46

		25-Nov-07		16:07:10		69.8		27.5		25-Nov-07		16:06:20		69.2		28.5		25-Nov-07		16:07:53		68.61		30.5		5-Jan-08		16:25:59		72.8		44.5

		25-Nov-07		18:07:10		70.41		29.5		25-Nov-07		18:06:20		69.2		30.5		25-Nov-07		18:07:53		68.61		31.5		5-Jan-08		18:25:59		73.4		42

		25-Nov-07		20:07:10		69.2		29.5		25-Nov-07		20:06:20		68		32		25-Nov-07		20:07:53		67.4		32.5		5-Jan-08		20:25:59		72.21		41.5

		25-Nov-07		22:07:10		68.61		32		25-Nov-07		22:06:20		66.81		35.5		25-Nov-07		22:07:53		66.2		35		5-Jan-08		22:25:59		68.61		43.5

		26-Nov-07		0:07:10		68		32		26-Nov-07		0:06:20		66.2		35.5		26-Nov-07		0:07:53		65.01		36		6-Jan-08		0:25:59		67.4		44

		26-Nov-07		2:07:10		68		32.5		26-Nov-07		2:06:20		66.2		35.5		26-Nov-07		2:07:53		63.8		37		6-Jan-08		2:25:59		66.2		43.5

		26-Nov-07		4:07:10		67.4		32.5		26-Nov-07		4:06:20		66.2		35.5		26-Nov-07		4:07:53		63.21		37.5		6-Jan-08		4:25:59		65.6		43.5

		26-Nov-07		6:07:10		67.4		33		26-Nov-07		6:06:20		66.2		35.5		26-Nov-07		6:07:53		62.6		38		6-Jan-08		6:25:59		65.01		43.5

		26-Nov-07		8:07:10		68		32.5		26-Nov-07		8:06:20		67.4		34.5		26-Nov-07		8:07:53		67.4		34		6-Jan-08		8:25:59		64.4		43.5

		26-Nov-07		10:07:10		68		34		26-Nov-07		10:06:20		67.4		36.5		26-Nov-07		10:07:53		67.4		36		6-Jan-08		10:25:59		64.4		44.5

		26-Nov-07		12:07:10		68.61		34.5		26-Nov-07		12:06:20		67.4		37		26-Nov-07		12:07:53		68		35.5		6-Jan-08		12:25:59		64.4		45.5

		26-Nov-07		14:07:10		68.61		32		26-Nov-07		14:06:20		68		32		26-Nov-07		14:07:53		68		34		6-Jan-08		14:25:59		64.4		47

		26-Nov-07		16:07:10		69.2		32		26-Nov-07		16:06:20		68.61		33		26-Nov-07		16:07:53		67.4		34.5		6-Jan-08		16:25:59		65.01		47.5

		26-Nov-07		18:07:10		69.2		33		26-Nov-07		18:06:20		68		35		26-Nov-07		18:07:53		68		35.5		6-Jan-08		18:25:59		64.4		47.5

		26-Nov-07		20:07:10		68.61		34		26-Nov-07		20:06:20		67.4		36.5		26-Nov-07		20:07:53		66.81		36.5		6-Jan-08		20:25:59		64.4		47.5

		26-Nov-07		22:07:10		68		33.5		26-Nov-07		22:06:20		66.2		36		26-Nov-07		22:07:53		64.4		37.5		6-Jan-08		22:25:59		64.4		46.5

		27-Nov-07		0:07:10		67.4		33		27-Nov-07		0:06:20		66.2		36		27-Nov-07		0:07:53		63.8		38		7-Jan-08		0:25:59		64.4		46

		27-Nov-07		2:07:10		66.81		32		27-Nov-07		2:06:20		66.2		34		27-Nov-07		2:07:53		62.6		36.5		7-Jan-08		2:25:59		63.8		45

		27-Nov-07		4:07:10		66.81		31.5		27-Nov-07		4:06:20		65.6		32.5		27-Nov-07		4:07:53		62		36.5		7-Jan-08		4:25:59		63.8		44.5

		27-Nov-07		6:07:10		66.81		30.5		27-Nov-07		6:06:20		65.6		32		27-Nov-07		6:07:53		66.81		32		7-Jan-08		6:25:59		63.21		43.5

		27-Nov-07		8:07:10		69.2		28.5		27-Nov-07		8:06:20		67.4		30.5		27-Nov-07		8:07:53		68.61		30.5		7-Jan-08		8:25:59		63.21		43

		27-Nov-07		10:07:10		69.8		31		27-Nov-07		10:06:20		69.8		32.5		27-Nov-07		10:07:53		69.2		32		7-Jan-08		10:25:59		63.8		42

		27-Nov-07		12:07:10		71		32.5		27-Nov-07		12:06:20		71.6		34		27-Nov-07		12:07:53		71		33.5		7-Jan-08		12:25:59		63.8		43

		27-Nov-07		14:07:10		71.6		34		27-Nov-07		14:06:20		71		35.5		27-Nov-07		14:07:53		71		34.5		7-Jan-08		14:25:59		65.01		44.5

		27-Nov-07		16:07:10		72.21		34		27-Nov-07		16:06:20		71.6		37.5		27-Nov-07		16:07:53		70.41		38		7-Jan-08		16:25:59		65.01		44.5

		27-Nov-07		18:07:10		72.21		36.5		27-Nov-07		18:06:20		69.8		39.5		27-Nov-07		18:07:53		69.8		39		7-Jan-08		18:25:59		65.6		44

		27-Nov-07		20:07:10		71.6		36.5		27-Nov-07		20:06:20		68.61		40		27-Nov-07		20:07:53		69.2		39.5		7-Jan-08		20:25:59		64.4		44.5

		27-Nov-07		22:07:10		69.8		35		27-Nov-07		22:06:20		67.4		38.5		27-Nov-07		22:07:53		67.4		38.5		7-Jan-08		22:25:59		63.8		45

		28-Nov-07		0:07:10		69.2		35		28-Nov-07		0:06:20		66.81		38.5		28-Nov-07		0:07:53		66.2		38.5		8-Jan-08		0:25:59		63.8		45.5

		28-Nov-07		2:07:10		68		34.5		28-Nov-07		2:06:20		66.2		38		28-Nov-07		2:07:53		65.01		39		8-Jan-08		2:25:59		63.8		45.5

		28-Nov-07		4:07:10		68		34		28-Nov-07		4:06:20		66.2		37		28-Nov-07		4:07:53		63.8		39		8-Jan-08		4:25:59		63.8		46

		28-Nov-07		6:07:10		67.4		34.5		28-Nov-07		6:06:20		66.2		37.5		28-Nov-07		6:07:53		67.4		35.5		8-Jan-08		6:25:59		65.01		45

		28-Nov-07		8:07:10		69.8		34		28-Nov-07		8:06:20		68		36.5		28-Nov-07		8:07:53		69.2		36.5		8-Jan-08		8:25:59		67.4		40.5

		28-Nov-07		10:07:10		71		34.5		28-Nov-07		10:06:20		70.41		36.5		28-Nov-07		10:07:53		71.6		36		8-Jan-08		10:25:59		69.8		39

		28-Nov-07		12:07:10		72.21		39		28-Nov-07		12:06:20		71		43.5		28-Nov-07		12:07:53		71		41		8-Jan-08		12:25:59		73.4		39

		28-Nov-07		14:07:10		72.8		34		28-Nov-07		14:06:20		71		34		28-Nov-07		14:07:53		71		39		8-Jan-08		14:25:59		72.8		37

		28-Nov-07		16:07:10		72.8		33.5		28-Nov-07		16:06:20		71.6		34.5		28-Nov-07		16:07:53		71		37.5		8-Jan-08		16:25:59		72.21		36

		28-Nov-07		18:07:10		72.8		35		28-Nov-07		18:06:20		70.41		37.5		28-Nov-07		18:07:53		71		37.5		8-Jan-08		18:25:59		72.21		35.5

		28-Nov-07		20:07:10		72.8		35		28-Nov-07		20:06:20		69.8		37.5		28-Nov-07		20:07:53		70.41		38.5		8-Jan-08		20:25:59		71.6		34.5

		28-Nov-07		22:07:10		71.6		35		28-Nov-07		22:06:20		68.61		38		28-Nov-07		22:07:53		69.2		38		8-Jan-08		22:25:59		68		37.5

		29-Nov-07		0:07:10		70.41		35.5		29-Nov-07		0:06:20		67.4		38.5		29-Nov-07		0:07:53		68		38		9-Jan-08		0:25:59		66.81		38

		29-Nov-07		2:07:10		69.2		34		29-Nov-07		2:06:20		66.81		37		29-Nov-07		2:07:53		66.2		38		9-Jan-08		2:25:59		65.6		39

		29-Nov-07		4:07:10		68.61		33		29-Nov-07		4:06:20		66.81		35.5		29-Nov-07		4:07:53		65.01		37.5		9-Jan-08		4:25:59		65.01		39.5

		29-Nov-07		6:07:10		68.61		32		29-Nov-07		6:06:20		66.2		33.5		29-Nov-07		6:07:53		66.81		34.5		9-Jan-08		6:25:59		65.6		39.5

		29-Nov-07		8:07:10		70.41		30.5		29-Nov-07		8:06:20		68		32		29-Nov-07		8:07:53		68		33.5		9-Jan-08		8:25:59		68.61		38

		29-Nov-07		10:07:10		71.6		32.5		29-Nov-07		10:06:20		71		34.5		29-Nov-07		10:07:53		70.41		34		9-Jan-08		10:25:59		71		40

		29-Nov-07		12:07:10		72.8		31		29-Nov-07		12:06:20		71.6		32.5		29-Nov-07		12:07:53		71		33		9-Jan-08		12:25:59		73.4		39

		29-Nov-07		14:07:10		72.8		31		29-Nov-07		14:06:20		71.6		32.5		29-Nov-07		14:07:53		71.6		31		9-Jan-08		14:25:59		74.01		40

		29-Nov-07		16:07:10		72.8		30.5		29-Nov-07		16:06:20		71.6		31.5		29-Nov-07		16:07:53		71		35		9-Jan-08		16:25:59		74.6		41

		29-Nov-07		18:07:10		72.8		28		29-Nov-07		18:06:20		69.2		29		29-Nov-07		18:07:53		71		32		9-Jan-08		18:25:59		75.2		41.5

		29-Nov-07		20:07:10		72.21		30		29-Nov-07		20:06:20		69.2		31		29-Nov-07		20:07:53		69.8		32.5		9-Jan-08		20:25:59		73.4		41.5

		29-Nov-07		22:07:10		70.41		31		29-Nov-07		22:06:20		67.4		34		29-Nov-07		22:07:53		68		34		9-Jan-08		22:25:59		69.8		42.5

		30-Nov-07		0:07:10		69.2		31		30-Nov-07		0:06:20		66.81		34		30-Nov-07		0:07:53		66.2		34.5		10-Jan-08		0:25:59		68		44

		30-Nov-07		2:07:10		68.61		30.5		30-Nov-07		2:06:20		66.2		33.5		30-Nov-07		2:07:53		65.01		35		10-Jan-08		2:25:59		66.81		44.5

		30-Nov-07		4:07:10		68		30		30-Nov-07		4:06:20		65.6		33		30-Nov-07		4:07:53		63.21		35		10-Jan-08		4:25:59		66.2		45

		30-Nov-07		6:07:10		67.4		30		30-Nov-07		6:06:20		66.2		32		30-Nov-07		6:07:53		67.4		31		10-Jan-08		6:25:59		68		45

		30-Nov-07		8:07:10		69.8		28		30-Nov-07		8:06:20		68.61		30.5		30-Nov-07		8:07:53		68		31		10-Jan-08		8:25:59		71.6		41.5

		30-Nov-07		10:07:10		71		30		30-Nov-07		10:06:20		70.41		33		30-Nov-07		10:07:53		70.41		32		10-Jan-08		10:25:59		73.4		40.5

		30-Nov-07		12:07:10		71.6		31.5		30-Nov-07		12:06:20		71		31		30-Nov-07		12:07:53		71.6		31.5		10-Jan-08		12:25:59		74.6		39.5

		30-Nov-07		14:07:10		72.8		30		30-Nov-07		14:06:20		71		31		30-Nov-07		14:07:53		71		35		10-Jan-08		14:25:59		74.6		39

		30-Nov-07		16:07:10		73.4		28		30-Nov-07		16:06:20		71		29		30-Nov-07		16:07:53		71		32.5		10-Jan-08		16:25:59		74.6		39

		30-Nov-07		18:07:10		73.4		26.5		30-Nov-07		18:06:20		69.8		26.5		30-Nov-07		18:07:53		69.8		31		10-Jan-08		18:25:59		73.4		39.5

		30-Nov-07		20:07:10		72.21		26		30-Nov-07		20:06:20		69.2		27.5		30-Nov-07		20:07:53		69.2		29		10-Jan-08		20:25:59		74.01		38.5

		30-Nov-07		22:07:10		71		27.5		30-Nov-07		22:06:20		68		30.5		30-Nov-07		22:07:53		68		31		10-Jan-08		22:25:59		70.41		43

		1-Dec-07		0:07:10		69.8		28.5		1-Dec-07		0:06:20		67.4		32		1-Dec-07		0:07:53		66.81		32.5		11-Jan-08		0:25:59		68.61		42.5

		1-Dec-07		2:07:10		69.2		28.5		1-Dec-07		2:06:20		66.81		31.5		1-Dec-07		2:07:53		65.01		33		11-Jan-08		2:25:59		67.4		43.5

		1-Dec-07		4:07:10		68.61		28		1-Dec-07		4:06:20		66.2		30.5		1-Dec-07		4:07:53		64.4		33		11-Jan-08		4:25:59		66.2		44

		1-Dec-07		6:07:10		68.61		28		1-Dec-07		6:06:20		66.2		30.5		1-Dec-07		6:07:53		66.81		30.5		11-Jan-08		6:25:59		68		44.5

		1-Dec-07		8:07:10		70.41		27		1-Dec-07		8:06:20		68		29		1-Dec-07		8:07:53		69.2		29.5		11-Jan-08		8:25:59		71.6		42

		1-Dec-07		10:07:10		71		27.5		1-Dec-07		10:06:20		70.41		29.5		1-Dec-07		10:07:53		71		29		11-Jan-08		10:25:59		74.01		41.5

		1-Dec-07		12:07:10		72.21		26.5		1-Dec-07		12:06:20		71.6		27		1-Dec-07		12:07:53		71		29.5		11-Jan-08		12:25:59		74.6		41

		1-Dec-07		14:07:10		72.8		24.5		1-Dec-07		14:06:20		71		26		1-Dec-07		14:07:53		70.41		29		11-Jan-08		14:25:59		74.01		43

		1-Dec-07		16:07:10		72.8		24.5		1-Dec-07		16:06:20		71		25.5		1-Dec-07		16:07:53		70.41		28		11-Jan-08		16:25:59		73.4		44.5

		1-Dec-07		18:07:10		72.8		26.5		1-Dec-07		18:06:20		69.8		28.5		1-Dec-07		18:07:53		70.41		30.5		11-Jan-08		18:25:59		71.6		45.5

		1-Dec-07		20:07:10		71.6		24.5		1-Dec-07		20:06:20		68		26		1-Dec-07		20:07:53		68.61		28		11-Jan-08		20:25:59		69.2		46.5

		1-Dec-07		22:07:10		69.8		24.5		1-Dec-07		22:06:20		66.81		27.5		1-Dec-07		22:07:53		66.2		28.5		11-Jan-08		22:25:59		68.61		47

		2-Dec-07		0:07:10		68.61		26		2-Dec-07		0:06:20		66.2		28		2-Dec-07		0:07:53		64.4		31.5		12-Jan-08		0:25:59		67.4		47.5

		2-Dec-07		2:07:10		68		25		2-Dec-07		2:06:20		65.6		28		2-Dec-07		2:07:53		63.21		30.5		12-Jan-08		2:25:59		66.81		48

		2-Dec-07		4:07:10		67.4		24.5		2-Dec-07		4:06:20		65.6		26.5		2-Dec-07		4:07:53		62		29.5		12-Jan-08		4:25:59		66.2		48

		2-Dec-07		6:07:10		66.81		24		2-Dec-07		6:06:20		65.6		26		2-Dec-07		6:07:53		61.41		29		12-Jan-08		6:25:59		66.2		49

		2-Dec-07		8:07:10		67.4		23		2-Dec-07		8:06:20		67.4		24.5		2-Dec-07		8:07:53		66.81		25.5		12-Jan-08		8:25:59		69.8		44.5

		2-Dec-07		10:07:10		67.4		24.5		2-Dec-07		10:06:20		67.4		26		2-Dec-07		10:07:53		68.61		25		12-Jan-08		10:25:59		71.6		43.5

		2-Dec-07		12:07:10		68		27		2-Dec-07		12:06:20		68		28.5		2-Dec-07		12:07:53		68.61		28		12-Jan-08		12:25:59		70.41		45

		2-Dec-07		14:07:10		68.61		27.5		2-Dec-07		14:06:20		68		28.5		2-Dec-07		14:07:53		69.2		29		12-Jan-08		14:25:59		71		44.5

		2-Dec-07		16:07:10		69.2		28		2-Dec-07		16:06:20		68		29.5		2-Dec-07		16:07:53		68		30		12-Jan-08		16:25:59		70.41		44

		2-Dec-07		18:07:10		69.2		28.5		2-Dec-07		18:06:20		68		30		2-Dec-07		18:07:53		67.4		31		12-Jan-08		18:25:59		69.8		44

		2-Dec-07		20:07:10		68		30		2-Dec-07		20:06:20		66.81		33		2-Dec-07		20:07:53		67.4		31		12-Jan-08		20:25:59		68.61		44.5

		2-Dec-07		22:07:10		67.4		29.5		2-Dec-07		22:06:20		66.2		32.5		2-Dec-07		22:07:53		63.8		33.5		12-Jan-08		22:25:59		67.4		46

		3-Dec-07		0:07:10		66.81		29.5		3-Dec-07		0:06:20		65.6		32		3-Dec-07		0:07:53		62.6		33.5		13-Jan-08		0:25:59		66.2		46.5

		3-Dec-07		2:07:10		66.81		30		3-Dec-07		2:06:20		66.2		33		3-Dec-07		2:07:53		62		34.5		13-Jan-08		2:25:59		66.2		47

		3-Dec-07		4:07:10		66.81		32.5		3-Dec-07		4:06:20		66.2		36		3-Dec-07		4:07:53		62.6		37.5		13-Jan-08		4:25:59		65.6		47

		3-Dec-07		6:07:10		66.81		35		3-Dec-07		6:06:20		66.2		39		3-Dec-07		6:07:53		62.6		40		13-Jan-08		6:25:59		65.01		47

		3-Dec-07		8:07:10		68		35.5		3-Dec-07		8:06:20		67.4		38		3-Dec-07		8:07:53		68.61		36		13-Jan-08		8:25:59		65.01		47.5

		3-Dec-07		10:07:10		68		35		3-Dec-07		10:06:20		67.4		37		3-Dec-07		10:07:53		68		36.5		13-Jan-08		10:25:59		65.01		48.5

		3-Dec-07		12:07:10		68		36		3-Dec-07		12:06:20		67.4		38		3-Dec-07		12:07:53		67.4		37.5		13-Jan-08		12:25:59		65.01		50

		3-Dec-07		14:07:10		68.61		36.5		3-Dec-07		14:06:20		68		39		3-Dec-07		14:07:53		68		38		13-Jan-08		14:25:59		65.6		51

		3-Dec-07		16:07:10		69.2		39		3-Dec-07		16:06:20		68		42.5		3-Dec-07		16:07:53		67.4		41		13-Jan-08		16:25:59		66.81		50

		3-Dec-07		18:07:10		69.2		39.5		3-Dec-07		18:06:20		68		42.5		3-Dec-07		18:07:53		67.4		42		13-Jan-08		18:25:59		67.4		49.5

		3-Dec-07		20:07:10		68.61		41		3-Dec-07		20:06:20		67.4		44.5		3-Dec-07		20:07:53		67.4		43		13-Jan-08		20:25:59		66.2		49.5

		3-Dec-07		22:07:10		68.61		44.5		3-Dec-07		22:06:20		66.81		50		3-Dec-07		22:07:53		66.2		47.5		13-Jan-08		22:25:59		65.6		49

		4-Dec-07		0:07:10		68.61		43		4-Dec-07		0:06:20		66.81		47		4-Dec-07		0:07:53		66.2		46.5		14-Jan-08		0:25:59		65.01		48

		4-Dec-07		2:07:10		68.61		42		4-Dec-07		2:06:20		66.81		45.5		4-Dec-07		2:07:53		66.2		45.5		14-Jan-08		2:25:59		64.4		48.5

		4-Dec-07		4:07:10		68.61		40.5		4-Dec-07		4:06:20		67.4		43		4-Dec-07		4:07:53		66.2		44.5		14-Jan-08		4:25:59		64.4		49

		4-Dec-07		6:07:10		68.61		40		4-Dec-07		6:06:20		67.4		42		4-Dec-07		6:07:53		66.2		44		14-Jan-08		6:25:59		64.4		49.5

		4-Dec-07		8:07:10		71.6		37		4-Dec-07		8:06:20		69.2		39		4-Dec-07		8:07:53		69.2		41		14-Jan-08		8:25:59		65.01		50.5

		4-Dec-07		10:07:10		72.8		39		4-Dec-07		10:06:20		71		42		4-Dec-07		10:07:53		70.41		43.5		14-Jan-08		10:25:59		65.6		49.5

		4-Dec-07		12:07:10		74.6		37.5		4-Dec-07		12:06:20		71.6		39		4-Dec-07		12:07:53		71		38.5		14-Jan-08		12:25:59		66.2		49

		4-Dec-07		14:07:10		73.4		38		4-Dec-07		14:06:20		71		42.5		4-Dec-07		14:07:53		71		39.5		14-Jan-08		14:25:59		66.81		48.5

		4-Dec-07		16:07:10		74.01		39.5		4-Dec-07		16:06:20		71.6		41.5		4-Dec-07		16:07:53		70.41		40		14-Jan-08		16:25:59		66.81		49

		4-Dec-07		18:07:10		74.01		40		4-Dec-07		18:06:20		70.41		42		4-Dec-07		18:07:53		71		45		14-Jan-08		18:25:59		66.81		49.5

		4-Dec-07		20:07:10		72.8		40.5		4-Dec-07		20:06:20		69.8		44		4-Dec-07		20:07:53		70.41		44		14-Jan-08		20:25:59		66.2		49

		4-Dec-07		22:07:10		72.21		44		4-Dec-07		22:06:20		69.8		50.5		4-Dec-07		22:07:53		69.8		46.5		14-Jan-08		22:25:59		65.01		49

		5-Dec-07		0:07:10		72.21		47		5-Dec-07		0:06:20		69.2		53.5		5-Dec-07		0:07:53		69.8		49.5		15-Jan-08		0:25:59		64.4		47.5

		5-Dec-07		2:07:10		71.6		48.5		5-Dec-07		2:06:20		69.2		54.5		5-Dec-07		2:07:53		69.2		51		15-Jan-08		2:25:59		63.8		47

		5-Dec-07		4:07:10		71		49.5		5-Dec-07		4:06:20		69.2		55		5-Dec-07		4:07:53		68.61		52.5		15-Jan-08		4:25:59		63.8		46.5

		5-Dec-07		6:07:10		71		50.5		5-Dec-07		6:06:20		68.61		56		5-Dec-07		6:07:53		68		53.5		15-Jan-08		6:25:59		64.4		46.5

		5-Dec-07		8:07:10		73.4		50		5-Dec-07		8:06:20		69.8		57.5		5-Dec-07		8:07:53		71		53		15-Jan-08		8:25:59		67.4		44

		5-Dec-07		10:07:10		74.01		49		5-Dec-07		10:06:20		71		44		5-Dec-07		10:07:53		71		57.5		15-Jan-08		10:25:59		71		43.5

		5-Dec-07		12:07:10		74.01		48		5-Dec-07		12:06:20		71.6		54		5-Dec-07		12:07:53		71		51		15-Jan-08		12:25:59		70.41		43

		5-Dec-07		14:07:10		74.01		49		5-Dec-07		14:06:20		71.6		54		5-Dec-07		14:07:53		71		48.5		15-Jan-08		14:25:59		69.8		44

		5-Dec-07		16:07:10		74.01		51		5-Dec-07		16:06:20		71.6		54		5-Dec-07		16:07:53		71		59.5		15-Jan-08		16:25:59		70.41		45

		5-Dec-07		18:07:10		73.4		50.5		5-Dec-07		18:06:20		69.8		57		5-Dec-07		18:07:53		71		47.5		15-Jan-08		18:25:59		71.6		43.5

		5-Dec-07		20:07:10		73.4		50		5-Dec-07		20:06:20		69.8		56		5-Dec-07		20:07:53		71		54.5		15-Jan-08		20:25:59		69.2		43

		5-Dec-07		22:07:10		72.8		50.5		5-Dec-07		22:06:20		69.8		56.5		5-Dec-07		22:07:53		70.41		55		15-Jan-08		22:25:59		66.81		43.5

		6-Dec-07		0:07:10		72.21		51.5		6-Dec-07		0:06:20		69.2		57		6-Dec-07		0:07:53		70.41		54.5		16-Jan-08		0:25:59		65.01		43.5

		6-Dec-07		2:07:10		71.6		51.5		6-Dec-07		2:06:20		69.2		57		6-Dec-07		2:07:53		69.8		54		16-Jan-08		2:25:59		64.4		43.5

		6-Dec-07		4:07:10		71.6		52		6-Dec-07		4:06:20		68.61		57.5		6-Dec-07		4:07:53		69.8		54		16-Jan-08		4:25:59		63.8		43.5

		6-Dec-07		6:07:10		71		50		6-Dec-07		6:06:20		68		54		6-Dec-07		6:07:53		69.2		53		16-Jan-08		6:25:59		64.4		42.5

		6-Dec-07		8:07:10		72.8		47.5		6-Dec-07		8:06:20		69.8		52		6-Dec-07		8:07:53		71		52		16-Jan-08		8:25:59		66.81		39.5

		6-Dec-07		10:07:10		74.01		45.5		6-Dec-07		10:06:20		71		45		6-Dec-07		10:07:53		71		50		16-Jan-08		10:25:59		70.41		38

		6-Dec-07		12:07:10		74.01		46		6-Dec-07		12:06:20		71		55		6-Dec-07		12:07:53		71		48		16-Jan-08		12:25:59		71		39.5

		6-Dec-07		14:07:10		74.01		46		6-Dec-07		14:06:20		71		57		6-Dec-07		14:07:53		71		54.5		16-Jan-08		14:25:59		72.21		40.5

		6-Dec-07		16:07:10		74.6		47.5		6-Dec-07		16:06:20		71		47.5		6-Dec-07		16:07:53		70.41		51.5		16-Jan-08		16:25:59		72.21		43

		6-Dec-07		18:07:10		74.01		39		6-Dec-07		18:06:20		69.8		41		6-Dec-07		18:07:53		69.8		45		16-Jan-08		18:25:59		72.8		41.5

		6-Dec-07		20:07:10		73.4		38		6-Dec-07		20:06:20		69.8		40		6-Dec-07		20:07:53		69.8		43.5		16-Jan-08		20:25:59		71		41.5

		6-Dec-07		22:07:10		72.21		40		6-Dec-07		22:06:20		69.2		44		6-Dec-07		22:07:53		70.41		44		16-Jan-08		22:25:59		68.61		41.5

		7-Dec-07		0:07:10		71.6		42		7-Dec-07		0:06:20		68		47		7-Dec-07		0:07:53		69.8		44.5		17-Jan-08		0:25:59		66.2		41.5

		7-Dec-07		2:07:10		70.41		42.5		7-Dec-07		2:06:20		67.4		48		7-Dec-07		2:07:53		69.2		45		17-Jan-08		2:25:59		65.01		41.5

		7-Dec-07		4:07:10		69.8		43		7-Dec-07		4:06:20		66.81		48.5		7-Dec-07		4:07:53		68.61		45.5		17-Jan-08		4:25:59		64.4		41.5

		7-Dec-07		6:07:10		69.8		43.5		7-Dec-07		6:06:20		66.81		49		7-Dec-07		6:07:53		68		46.5		17-Jan-08		6:25:59		65.01		39.5

		7-Dec-07		8:07:10		72.21		42		7-Dec-07		8:06:20		68.61		47.5		7-Dec-07		8:07:53		70.41		45		17-Jan-08		8:25:59		66.81		36.5

		7-Dec-07		10:07:10		73.4		42.5		7-Dec-07		10:06:20		71		49.5		7-Dec-07		10:07:53		71		48		17-Jan-08		10:25:59		71		33

		7-Dec-07		12:07:10		72.8		45		7-Dec-07		12:06:20		71		44.5		7-Dec-07		12:07:53		70.41		50.5		17-Jan-08		12:25:59		71.6		27

		7-Dec-07		14:07:10		72.21		47		7-Dec-07		14:06:20		71		47		7-Dec-07		14:07:53		71.6		52.5		17-Jan-08		14:25:59		72.8		25.5

		7-Dec-07		16:07:10		72.21		46		7-Dec-07		16:06:20		71		50		7-Dec-07		16:07:53		70.41		50		17-Jan-08		16:25:59		72.21		23.5

		7-Dec-07		18:07:10		72.21		45.5		7-Dec-07		18:06:20		69.2		50.5		7-Dec-07		18:07:53		70.41		51.5		17-Jan-08		18:25:59		72.21		23

		7-Dec-07		20:07:10		71		47		7-Dec-07		20:06:20		68.61		51		7-Dec-07		20:07:53		69.8		49		17-Jan-08		20:25:59		71.6		23

		7-Dec-07		22:07:10		69.8		47.5		7-Dec-07		22:06:20		67.4		52.5		7-Dec-07		22:07:53		69.8		48.5		17-Jan-08		22:25:59		69.2		24.5

		8-Dec-07		0:07:10		69.2		48		8-Dec-07		0:06:20		66.81		52.5		8-Dec-07		0:07:53		69.2		49		18-Jan-08		0:25:59		67.4		25.5

		8-Dec-07		2:07:10		68.61		44.5		8-Dec-07		2:06:20		66.81		47		8-Dec-07		2:07:53		68		46.5		18-Jan-08		2:25:59		66.2		26

		8-Dec-07		4:07:10		68.61		44		8-Dec-07		4:06:20		66.2		47		8-Dec-07		4:07:53		66.81		47		18-Jan-08		4:25:59		65.01		26

		8-Dec-07		6:07:10		68		43		8-Dec-07		6:06:20		66.2		45.5		8-Dec-07		6:07:53		67.4		45		18-Jan-08		6:25:59		66.2		26.5

		8-Dec-07		8:07:10		71		39		8-Dec-07		8:06:20		68		41		8-Dec-07		8:07:53		69.8		42		18-Jan-08		8:25:59		68.61		26

		8-Dec-07		10:07:10		72.21		37		8-Dec-07		10:06:20		69.8		40.5		8-Dec-07		10:07:53		71.6		40.5		18-Jan-08		10:25:59		72.21		27.5

		8-Dec-07		12:07:10		71.6		37.5		8-Dec-07		12:06:20		71		40.5		8-Dec-07		12:07:53		71		41		18-Jan-08		12:25:59		71.6		28

		8-Dec-07		14:07:10		71.6		36.5		8-Dec-07		14:06:20		71		40		8-Dec-07		14:07:53		71		35		18-Jan-08		14:25:59		72.21		29.5

		8-Dec-07		16:07:10		71.6		35.5		8-Dec-07		16:06:20		71		38		8-Dec-07		16:07:53		70.41		38.5		18-Jan-08		16:25:59		72.8		29

		8-Dec-07		18:07:10		71.6		35.5		8-Dec-07		18:06:20		69.8		35.5		8-Dec-07		18:07:53		69.8		37.5		18-Jan-08		18:25:59		72.21		30

		8-Dec-07		20:07:10		70.41		35		8-Dec-07		20:06:20		67.4		36.5		8-Dec-07		20:07:53		69.2		37		18-Jan-08		20:25:59		71.6		31.5

		8-Dec-07		22:07:10		69.2		33.5		8-Dec-07		22:06:20		66.81		36		8-Dec-07		22:07:53		67.4		37		18-Jan-08		22:25:59		68.61		32

		9-Dec-07		0:07:10		68.61		33.5		9-Dec-07		0:06:20		66.81		35.5		9-Dec-07		0:07:53		66.2		37		19-Jan-08		0:25:59		66.81		32.5

		9-Dec-07		2:07:10		68		33		9-Dec-07		2:06:20		66.2		35		9-Dec-07		2:07:53		65.6		37		19-Jan-08		2:25:59		65.01		33

		9-Dec-07		4:07:10		68		32.5		9-Dec-07		4:06:20		66.2		34		9-Dec-07		4:07:53		64.4		37		19-Jan-08		4:25:59		64.4		33

		9-Dec-07		6:07:10		67.4		32		9-Dec-07		6:06:20		66.2		33.5		9-Dec-07		6:07:53		63.8		36.5		19-Jan-08		6:25:59		66.2		32

		9-Dec-07		8:07:10		68		30.5		9-Dec-07		8:06:20		67.4		31.5		9-Dec-07		8:07:53		67.4		33		19-Jan-08		8:25:59		68.61		30

		9-Dec-07		10:07:10		68.61		30.5		9-Dec-07		10:06:20		68		31		9-Dec-07		10:07:53		68.61		31.5		19-Jan-08		10:25:59		70.41		31

		9-Dec-07		12:07:10		68.61		29.5		9-Dec-07		12:06:20		68.61		29		9-Dec-07		12:07:53		69.8		30		19-Jan-08		12:25:59		71		32.5

		9-Dec-07		14:07:10		68.61		28.5		9-Dec-07		14:06:20		68		28		9-Dec-07		14:07:53		70.41		30		19-Jan-08		14:25:59		71.6		33

		9-Dec-07		16:07:10		69.2		25		9-Dec-07		16:06:20		68		22.5		9-Dec-07		16:07:53		69.2		28.5		19-Jan-08		16:25:59		72.8		32.5

		9-Dec-07		18:07:10		69.2		24		9-Dec-07		18:06:20		68		23		9-Dec-07		18:07:53		68.61		27.5		19-Jan-08		18:25:59		72.8		33

		9-Dec-07		20:07:10		68.61		24		9-Dec-07		20:06:20		67.4		23.5		9-Dec-07		20:07:53		67.4		27		19-Jan-08		20:25:59		72.21		32

		9-Dec-07		22:07:10		68		24		9-Dec-07		22:06:20		66.81		24		9-Dec-07		22:07:53		66.2		27		19-Jan-08		22:25:59		68		34.5

		10-Dec-07		0:07:10		67.4		24		10-Dec-07		0:06:20		66.2		24.5		10-Dec-07		0:07:53		65.6		27.5		20-Jan-08		0:25:59		66.2		34.5

		10-Dec-07		2:07:10		67.4		24.5		10-Dec-07		2:06:20		66.2		25		10-Dec-07		2:07:53		64.4		28		20-Jan-08		2:25:59		65.01		34.5

		10-Dec-07		4:07:10		66.81		25		10-Dec-07		4:06:20		65.6		26.5		10-Dec-07		4:07:53		63.8		28.5		20-Jan-08		4:25:59		63.8		34

		10-Dec-07		6:07:10		66.2		26		10-Dec-07		6:06:20		65.6		28		10-Dec-07		6:07:53		63.21		29.5		20-Jan-08		6:25:59		63.21		33.5

		10-Dec-07		8:07:10		66.81		26		10-Dec-07		8:06:20		67.4		27		10-Dec-07		8:07:53		68.61		26.5		20-Jan-08		8:25:59		63.21		32.5

		10-Dec-07		10:07:10		67.4		26.5		10-Dec-07		10:06:20		67.4		27.5		10-Dec-07		10:07:53		67.4		27.5		20-Jan-08		10:25:59		63.21		33

		10-Dec-07		12:07:10		68		27.5		10-Dec-07		12:06:20		68		28		10-Dec-07		12:07:53		68		29		20-Jan-08		12:25:59		63.8		37

		10-Dec-07		14:07:10		68.61		28.5		10-Dec-07		14:06:20		68		29.5		10-Dec-07		14:07:53		68		30		20-Jan-08		14:25:59		65.01		39

		10-Dec-07		16:07:10		69.2		28.5		10-Dec-07		16:06:20		68.61		29		10-Dec-07		16:07:53		68		31.5		20-Jan-08		16:25:59		66.2		37.5

		10-Dec-07		18:07:10		69.2		30		10-Dec-07		18:06:20		68		31.5		10-Dec-07		18:07:53		67.4		32.5		20-Jan-08		18:25:59		66.81		37

		10-Dec-07		20:07:10		68.61		31		10-Dec-07		20:06:20		66.81		33.5		10-Dec-07		20:07:53		66.81		33.5		20-Jan-08		20:25:59		65.6		37

		10-Dec-07		22:07:10		68		32.5		10-Dec-07		22:06:20		66.2		35.5		10-Dec-07		22:07:53		65.6		35		20-Jan-08		22:25:59		65.01		37

		11-Dec-07		0:07:10		67.4		33.5		11-Dec-07		0:06:20		66.2		36.5		11-Dec-07		0:07:53		65.01		36.5		21-Jan-08		0:25:59		64.4		37

		11-Dec-07		2:07:10		66.81		32		11-Dec-07		2:06:20		66.2		34.5		11-Dec-07		2:07:53		64.4		36		21-Jan-08		2:25:59		63.8		38

		11-Dec-07		4:07:10		66.81		31.5		11-Dec-07		4:06:20		66.2		33		11-Dec-07		4:07:53		63.21		35.5		21-Jan-08		4:25:59		63.8		38.5

		11-Dec-07		6:07:10		66.81		30.5		11-Dec-07		6:06:20		66.2		32		11-Dec-07		6:07:53		67.4		31.5		21-Jan-08		6:25:59		63.21		38

		11-Dec-07		8:07:10		68.61		28.5		11-Dec-07		8:06:20		67.4		30		11-Dec-07		8:07:53		68		30.5		21-Jan-08		8:25:59		63.21		38

		11-Dec-07		10:07:10		69.2		30		11-Dec-07		10:06:20		69.8		31.5		11-Dec-07		10:07:53		69.2		31		21-Jan-08		10:25:59		63.8		38

		11-Dec-07		12:07:10		71.6		31.5		11-Dec-07		12:06:20		70.41		34		11-Dec-07		12:07:53		71.6		32.5		21-Jan-08		12:25:59		65.01		39

		11-Dec-07		14:07:10		71.6		32.5		11-Dec-07		14:06:20		70.41		34		11-Dec-07		14:07:53		71		35.5		21-Jan-08		14:25:59		65.6		36

		11-Dec-07		16:07:10		72.21		32.5		11-Dec-07		16:06:20		69.8		34.5		11-Dec-07		16:07:53		71		35		21-Jan-08		16:25:59		65.6		36

		11-Dec-07		18:07:10		72.21		31		11-Dec-07		18:06:20		69.8		31		11-Dec-07		18:07:53		71		34.5		21-Jan-08		18:25:59		65.6		35.5

		11-Dec-07		20:07:10		70.41		32.5		11-Dec-07		20:06:20		67.4		36		11-Dec-07		20:07:53		70.41		33.5		21-Jan-08		20:25:59		65.01		36

		11-Dec-07		22:07:10		69.2		27		11-Dec-07		22:06:20		66.81		26.5		11-Dec-07		22:07:53		68		31		21-Jan-08		22:25:59		63.8		36.5

		12-Dec-07		0:07:10		68.61		25		12-Dec-07		0:06:20		66.81		24		12-Dec-07		0:07:53		66.81		29		22-Jan-08		0:25:59		63.21		36

		12-Dec-07		2:07:10		68		22		12-Dec-07		2:06:20		66.81		20		12-Dec-07		2:07:53		66.2		26		22-Jan-08		2:25:59		63.21		35

		12-Dec-07		4:07:10		67.4		19.5		12-Dec-07		4:06:20		66.2		17		12-Dec-07		4:07:53		65.6		23.5		22-Jan-08		4:25:59		62.6		33.5

		12-Dec-07		6:07:10		67.4		18.5		12-Dec-07		6:06:20		66.2		16.5		12-Dec-07		6:07:53		65.01		22.5		22-Jan-08		6:25:59		64.4		32.5

		12-Dec-07		8:07:10		69.8		17.5		12-Dec-07		8:06:20		68		16		12-Dec-07		8:07:53		68		20.5		22-Jan-08		8:25:59		66.81		31

		12-Dec-07		10:07:10		71.6		19.5		12-Dec-07		10:06:20		70.41		20		12-Dec-07		10:07:53		71		22		22-Jan-08		10:25:59		69.8		31.5

		12-Dec-07		12:07:10		72.21		18.5		12-Dec-07		12:06:20		71		18		12-Dec-07		12:07:53		71		22.5		22-Jan-08		12:25:59		74.6		30.5

		12-Dec-07		14:07:10		72.21		17.5		12-Dec-07		14:06:20		71		18.5		12-Dec-07		14:07:53		71.6		23		22-Jan-08		14:25:59		72.8		34

		12-Dec-07		16:07:10		72.21		17		12-Dec-07		16:06:20		71		19		12-Dec-07		16:07:53		70.41		22		22-Jan-08		16:25:59		73.4		34.5

		12-Dec-07		18:07:10		72.21		19		12-Dec-07		18:06:20		69.2		19		12-Dec-07		18:07:53		70.41		23.5		22-Jan-08		18:25:59		73.4		33.5

		12-Dec-07		20:07:10		70.41		22		12-Dec-07		20:06:20		67.4		24		12-Dec-07		20:07:53		69.8		24		22-Jan-08		20:25:59		72.21		34

		12-Dec-07		22:07:10		69.2		22.5		12-Dec-07		22:06:20		66.81		26		12-Dec-07		22:07:53		68.61		25		22-Jan-08		22:25:59		67.4		36

		13-Dec-07		0:07:10		68.61		23		13-Dec-07		0:06:20		66.2		26		13-Dec-07		0:07:53		66.81		25.5		23-Jan-08		0:25:59		65.6		37.5

		13-Dec-07		2:07:10		67.4		23		13-Dec-07		2:06:20		66.2		26		13-Dec-07		2:07:53		65.01		26.5		23-Jan-08		2:25:59		64.4		38

		13-Dec-07		4:07:10		66.81		23.5		13-Dec-07		4:06:20		66.2		25.5		13-Dec-07		4:07:53		63.8		27.5		23-Jan-08		4:25:59		63.8		38

		13-Dec-07		6:07:10		67.4		24.5		13-Dec-07		6:06:20		66.2		27		13-Dec-07		6:07:53		67.4		25.5		23-Jan-08		6:25:59		66.2		37.5

		13-Dec-07		8:07:10		70.41		24.5		13-Dec-07		8:06:20		68		27		13-Dec-07		8:07:53		68.61		26.5		23-Jan-08		8:25:59		68.61		34.5

		13-Dec-07		10:07:10		71.6		25		13-Dec-07		10:06:20		70.41		27.5		13-Dec-07		10:07:53		70.41		27.5		23-Jan-08		10:25:59		72.21		33

		13-Dec-07		12:07:10		72.21		26.5		13-Dec-07		12:06:20		71		28.5		13-Dec-07		12:07:53		70.41		30		23-Jan-08		12:25:59		74.01		31.5

		13-Dec-07		14:07:10		72.21		25.5		13-Dec-07		14:06:20		71		27		13-Dec-07		14:07:53		70.41		30.5		23-Jan-08		14:25:59		72.8		31.5

		13-Dec-07		16:07:10		72.21		22.5		13-Dec-07		16:06:20		71		23.5		13-Dec-07		16:07:53		70.41		28		23-Jan-08		16:25:59		72.21		31.5

		13-Dec-07		18:07:10		72.8		23.5		13-Dec-07		18:06:20		69.8		24		13-Dec-07		18:07:53		69.8		27.5		23-Jan-08		18:25:59		72.8		30.5

		13-Dec-07		20:07:10		70.41		25.5		13-Dec-07		20:06:20		67.4		28.5		13-Dec-07		20:07:53		69.2		28		23-Jan-08		20:25:59		72.8		30

		13-Dec-07		22:07:10		69.2		25.5		13-Dec-07		22:06:20		66.81		29		13-Dec-07		22:07:53		68		28.5		23-Jan-08		22:25:59		68		32

		14-Dec-07		0:07:10		68		26		14-Dec-07		0:06:20		66.2		29		14-Dec-07		0:07:53		66.2		29		24-Jan-08		0:25:59		65.6		33

		14-Dec-07		2:07:10		67.4		26.5		14-Dec-07		2:06:20		66.2		29		14-Dec-07		2:07:53		64.4		30		24-Jan-08		2:25:59		64.4		34

		14-Dec-07		4:07:10		66.81		26		14-Dec-07		4:06:20		66.2		28.5		14-Dec-07		4:07:53		63.21		30.5		24-Jan-08		4:25:59		63.8		35

		14-Dec-07		6:07:10		66.81		25.5		14-Dec-07		6:06:20		66.2		27		14-Dec-07		6:07:53		66.2		27		24-Jan-08		6:25:59		65.6		36

		14-Dec-07		8:07:10		69.2		24		14-Dec-07		8:06:20		67.4		26		14-Dec-07		8:07:53		68.61		26.5		24-Jan-08		8:25:59		68		34.5

		14-Dec-07		10:07:10		69.8		26		14-Dec-07		10:06:20		69.8		28		14-Dec-07		10:07:53		69.8		27.5		24-Jan-08		10:25:59		71.6		34.5

		14-Dec-07		12:07:10		71		28		14-Dec-07		12:06:20		70.41		30.5		14-Dec-07		12:07:53		71.6		28.5		24-Jan-08		12:25:59		74.01		33.5

		14-Dec-07		14:07:10		71.6		28		14-Dec-07		14:06:20		71		29.5		14-Dec-07		14:07:53		71		28.5		24-Jan-08		14:25:59		71.6		35

		14-Dec-07		16:07:10		72.21		29		14-Dec-07		16:06:20		71.6		30		14-Dec-07		16:07:53		69.8		32		24-Jan-08		16:25:59		72.21		34.5

		14-Dec-07		18:07:10		73.4		30		14-Dec-07		18:06:20		69.8		33		14-Dec-07		18:07:53		70.41		33.5		24-Jan-08		18:25:59		72.21		33.5

		14-Dec-07		20:07:10		71		30.5		14-Dec-07		20:06:20		69.2		33		14-Dec-07		20:07:53		69.2		32		24-Jan-08		20:25:59		72.21		33.5

		14-Dec-07		22:07:10		69.2		29.5		14-Dec-07		22:06:20		66.81		32.5		14-Dec-07		22:07:53		68		31.5		24-Jan-08		22:25:59		68		36

		15-Dec-07		0:07:10		68		29		15-Dec-07		0:06:20		66.2		32		15-Dec-07		0:07:53		65.6		32		25-Jan-08		0:25:59		65.6		36.5

		15-Dec-07		2:07:10		67.4		28		15-Dec-07		2:06:20		66.2		30.5		15-Dec-07		2:07:53		63.8		32		25-Jan-08		2:25:59		65.01		37.5

		15-Dec-07		4:07:10		66.81		27		15-Dec-07		4:06:20		65.6		29		15-Dec-07		4:07:53		63.21		31.5		25-Jan-08		4:25:59		64.4		38.5

		15-Dec-07		6:07:10		66.81		27		15-Dec-07		6:06:20		66.2		28.5		15-Dec-07		6:07:53		67.4		27.5		25-Jan-08		6:25:59		66.2		38

		15-Dec-07		8:07:10		68.61		25		15-Dec-07		8:06:20		67.4		26		15-Dec-07		8:07:53		68.61		27		25-Jan-08		8:25:59		69.2		36

		15-Dec-07		10:07:10		70.41		27		15-Dec-07		10:06:20		69.8		28.5		15-Dec-07		10:07:53		70.41		28.5		25-Jan-08		10:25:59		72.8		36

		15-Dec-07		12:07:10		71.6		29.5		15-Dec-07		12:06:20		71		29.5		15-Dec-07		12:07:53		71.6		30		25-Jan-08		12:25:59		74.01		34.5

		15-Dec-07		14:07:10		71.6		30.5		15-Dec-07		14:06:20		71		31.5		15-Dec-07		14:07:53		70.41		30		25-Jan-08		14:25:59		73.4		35

		15-Dec-07		16:07:10		71.6		30.5		15-Dec-07		16:06:20		71		31.5		15-Dec-07		16:07:53		71		32.5		25-Jan-08		16:25:59		74.01		35.5

		15-Dec-07		18:07:10		72.8		33		15-Dec-07		18:06:20		69.8		37		15-Dec-07		18:07:53		70.41		35.5		25-Jan-08		18:25:59		72.8		35

		15-Dec-07		20:07:10		71		34.5		15-Dec-07		20:06:20		67.4		39		15-Dec-07		20:07:53		69.2		35.5		25-Jan-08		20:25:59		72.21		34

		15-Dec-07		22:07:10		69.2		33.5		15-Dec-07		22:06:20		66.81		37.5		15-Dec-07		22:07:53		67.4		35.5		25-Jan-08		22:25:59		69.2		36

		16-Dec-07		0:07:10		68.61		34		16-Dec-07		0:06:20		66.2		38		16-Dec-07		0:07:53		66.2		36.5		26-Jan-08		0:25:59		67.4		36.5

		16-Dec-07		2:07:10		68		34		16-Dec-07		2:06:20		66.2		38		16-Dec-07		2:07:53		65.6		37.5		26-Jan-08		2:25:59		66.2		37

		16-Dec-07		4:07:10		68		35		16-Dec-07		4:06:20		66.2		39		16-Dec-07		4:07:53		65.01		38.5		26-Jan-08		4:25:59		65.6		37

		16-Dec-07		6:07:10		67.4		35		16-Dec-07		6:06:20		66.2		38		16-Dec-07		6:07:53		64.4		39		26-Jan-08		6:25:59		66.81		37

		16-Dec-07		8:07:10		68		34		16-Dec-07		8:06:20		67.4		36.5		16-Dec-07		8:07:53		66.81		37		26-Jan-08		8:25:59		70.41		37

		16-Dec-07		10:07:10		68		34.5		16-Dec-07		10:06:20		67.4		36.5		16-Dec-07		10:07:53		66.81		36		26-Jan-08		10:25:59		73.4		38

		16-Dec-07		12:07:10		68		35		16-Dec-07		12:06:20		68		37		16-Dec-07		12:07:53		67.4		36.5		26-Jan-08		12:25:59		72.8		39

		16-Dec-07		14:07:10		68.61		37		16-Dec-07		14:06:20		68		39.5		16-Dec-07		14:07:53		66.81		39		26-Jan-08		14:25:59		73.4		39.5

		16-Dec-07		16:07:10		69.2		39		16-Dec-07		16:06:20		68		42.5		16-Dec-07		16:07:53		67.4		41.5		26-Jan-08		16:25:59		73.4		39.5

		16-Dec-07		18:07:10		69.2		40.5		16-Dec-07		18:06:20		68		44		16-Dec-07		18:07:53		68		42.5		26-Jan-08		18:25:59		73.4		40

		16-Dec-07		20:07:10		68.61		40.5		16-Dec-07		20:06:20		66.81		44		16-Dec-07		20:07:53		67.4		42		26-Jan-08		20:25:59		72.8		41

		16-Dec-07		22:07:10		68		40.5		16-Dec-07		22:06:20		66.81		44		16-Dec-07		22:07:53		66.2		43		26-Jan-08		22:25:59		69.8		43

		17-Dec-07		0:07:10		68		41		17-Dec-07		0:06:20		66.2		44.5		17-Dec-07		0:07:53		66.2		43.5		27-Jan-08		0:25:59		68		44

		17-Dec-07		2:07:10		67.4		41		17-Dec-07		2:06:20		66.2		44.5		17-Dec-07		2:07:53		65.6		44		27-Jan-08		2:25:59		67.4		45.5

		17-Dec-07		4:07:10		67.4		40.5		17-Dec-07		4:06:20		66.2		44.5		17-Dec-07		4:07:53		65.01		44		27-Jan-08		4:25:59		66.81		46.5

		17-Dec-07		6:07:10		66.81		40.5		17-Dec-07		6:06:20		66.2		43.5		17-Dec-07		6:07:53		65.01		43.5		27-Jan-08		6:25:59		66.2		47

		17-Dec-07		8:07:10		68		40		17-Dec-07		8:06:20		67.4		42.5		17-Dec-07		8:07:53		66.81		41.5		27-Jan-08		8:25:59		66.2		46.5

		17-Dec-07		10:07:10		68		40.5		17-Dec-07		10:06:20		67.4		43		17-Dec-07		10:07:53		67.4		42		27-Jan-08		10:25:59		66.2		45.5

		17-Dec-07		12:07:10		68		40.5		17-Dec-07		12:06:20		67.4		42.5		17-Dec-07		12:07:53		67.4		42.5		27-Jan-08		12:25:59		66.81		45

		17-Dec-07		14:07:10		68.61		37		17-Dec-07		14:06:20		68		37		17-Dec-07		14:07:53		67.4		40		27-Jan-08		14:25:59		67.4		46

		17-Dec-07		16:07:10		68.61		37.5		17-Dec-07		16:06:20		67.4		39.5		17-Dec-07		16:07:53		67.4		40.5		27-Jan-08		16:25:59		68		45.5

		17-Dec-07		18:07:10		68.61		38		17-Dec-07		18:06:20		68		39.5		17-Dec-07		18:07:53		67.4		40		27-Jan-08		18:25:59		67.4		44.5

		17-Dec-07		20:07:10		68		40		17-Dec-07		20:06:20		66.81		43.5		17-Dec-07		20:07:53		66.81		42		27-Jan-08		20:25:59		66.81		44

		17-Dec-07		22:07:10		68		42.5		17-Dec-07		22:06:20		66.2		47		17-Dec-07		22:07:53		65.6		45		27-Jan-08		22:25:59		66.2		44

		18-Dec-07		0:07:10		67.4		43.5		18-Dec-07		0:06:20		66.2		48.5		18-Dec-07		0:07:53		65.6		46.5		28-Jan-08		0:25:59		66.2		44.5

		18-Dec-07		2:07:10		67.4		43.5		18-Dec-07		2:06:20		66.81		46.5		18-Dec-07		2:07:53		65.6		46.5		28-Jan-08		2:25:59		66.2		46

		18-Dec-07		4:07:10		67.4		42		18-Dec-07		4:06:20		66.2		44.5		18-Dec-07		4:07:53		65.01		45.5		28-Jan-08		4:25:59		65.6		46.5

		18-Dec-07		6:07:10		67.4		43		18-Dec-07		6:06:20		66.2		46		18-Dec-07		6:07:53		66.81		43.5		28-Jan-08		6:25:59		65.6		47

		18-Dec-07		8:07:10		69.8		41		18-Dec-07		8:06:20		68		44.5		18-Dec-07		8:07:53		69.2		43		28-Jan-08		8:25:59		65.6		47.5

		18-Dec-07		10:07:10		71		42		18-Dec-07		10:06:20		71		39		18-Dec-07		10:07:53		71.6		41.5		28-Jan-08		10:25:59		66.81		47.5

		18-Dec-07		12:07:10		71.6		41		18-Dec-07		12:06:20		71.6		43.5		18-Dec-07		12:07:53		71.6		43.5		28-Jan-08		12:25:59		68		47

		18-Dec-07		14:07:10		71.6		41		18-Dec-07		14:06:20		71		45		18-Dec-07		14:07:53		71		45.5		28-Jan-08		14:25:59		68.61		46.5

		18-Dec-07		16:07:10		72.21		44		18-Dec-07		16:06:20		71		39.5		18-Dec-07		16:07:53		71		46		28-Jan-08		16:25:59		68.61		46.5

		18-Dec-07		18:07:10		72.21		42		18-Dec-07		18:06:20		69.2		45		18-Dec-07		18:07:53		71.6		40.5		28-Jan-08		18:25:59		69.2		46.5

		18-Dec-07		20:07:10		71		41.5		18-Dec-07		20:06:20		68		45		18-Dec-07		20:07:53		70.41		42.5		28-Jan-08		20:25:59		67.4		47.5

		18-Dec-07		22:07:10		69.8		43		18-Dec-07		22:06:20		66.81		48.5		18-Dec-07		22:07:53		68.61		44.5		28-Jan-08		22:25:59		66.2		46

		19-Dec-07		0:07:10		69.2		44		19-Dec-07		0:06:20		66.81		48.5		19-Dec-07		0:07:53		68		45.5		29-Jan-08		0:25:59		65.01		42.5

		19-Dec-07		2:07:10		68.61		44.5		19-Dec-07		2:06:20		66.81		49		19-Dec-07		2:07:53		67.4		46.5		29-Jan-08		2:25:59		64.4		41

		19-Dec-07		4:07:10		68.61		44.5		19-Dec-07		4:06:20		66.81		48.5		19-Dec-07		4:07:53		66.81		47.5		29-Jan-08		4:25:59		64.4		40.5

		19-Dec-07		6:07:10		68		45		19-Dec-07		6:06:20		66.81		48.5		19-Dec-07		6:07:53		68		46		29-Jan-08		6:25:59		66.2		39

		19-Dec-07		8:07:10		70.41		43		19-Dec-07		8:06:20		68.61		46		19-Dec-07		8:07:53		69.8		44.5		29-Jan-08		8:25:59		68.61		37

		19-Dec-07		10:07:10		71.6		42		19-Dec-07		10:06:20		71		48.5		19-Dec-07		10:07:53		71		43.5		29-Jan-08		10:25:59		73.4		35.5

		19-Dec-07		12:07:10		72.21		44		19-Dec-07		12:06:20		71.6		49.5		19-Dec-07		12:07:53		70.41		50		29-Jan-08		12:25:59		71		37

		19-Dec-07		14:07:10		72.21		45.5		19-Dec-07		14:06:20		71		53.5		19-Dec-07		14:07:53		69.8		49.5		29-Jan-08		14:25:59		71.6		36

		19-Dec-07		16:07:10		72.8		45.5		19-Dec-07		16:06:20		71		47		19-Dec-07		16:07:53		70.41		47		29-Jan-08		16:25:59		72.8		35.5

		19-Dec-07		18:07:10		72.21		41.5		19-Dec-07		18:06:20		69.2		44		19-Dec-07		18:07:53		69.8		44.5		29-Jan-08		18:25:59		72.21		35.5

		19-Dec-07		20:07:10		71		41		19-Dec-07		20:06:20		67.4		44.5		19-Dec-07		20:07:53		69.2		43		29-Jan-08		20:25:59		72.21		33.5

		19-Dec-07		22:07:10		69.8		39		19-Dec-07		22:06:20		66.81		42		19-Dec-07		22:07:53		68		42		29-Jan-08		22:25:59		68		36

		20-Dec-07		0:07:10		68.61		38.5		20-Dec-07		0:06:20		66.2		42		20-Dec-07		0:07:53		66.2		42		30-Jan-08		0:25:59		66.2		36

		20-Dec-07		2:07:10		68.61		39		20-Dec-07		2:06:20		66.2		43		20-Dec-07		2:07:53		65.6		43		30-Jan-08		2:25:59		65.01		36

		20-Dec-07		4:07:10		68		40		20-Dec-07		4:06:20		66.2		43.5		20-Dec-07		4:07:53		65.01		44		30-Jan-08		4:25:59		63.8		35

		20-Dec-07		6:07:10		68		40		20-Dec-07		6:06:20		66.2		43.5		20-Dec-07		6:07:53		67.4		41.5		30-Jan-08		6:25:59		66.2		34

		20-Dec-07		8:07:10		70.41		39		20-Dec-07		8:06:20		68		42.5		20-Dec-07		8:07:53		69.8		41		30-Jan-08		8:25:59		69.2		33

		20-Dec-07		10:07:10		72.21		39		20-Dec-07		10:06:20		70.41		42		20-Dec-07		10:07:53		71.6		39.5		30-Jan-08		10:25:59		72.8		33.5

		20-Dec-07		12:07:10		72.21		41		20-Dec-07		12:06:20		71		45.5		20-Dec-07		12:07:53		71.6		43		30-Jan-08		12:25:59		73.4		34

		20-Dec-07		14:07:10		72.8		39.5		20-Dec-07		14:06:20		70.41		47.5		20-Dec-07		14:07:53		71.6		42		30-Jan-08		14:25:59		72.8		37.5

		20-Dec-07		16:07:10		72.21		43		20-Dec-07		16:06:20		70.41		43		20-Dec-07		16:07:53		70.41		46		30-Jan-08		16:25:59		72.8		39.5

		20-Dec-07		18:07:10		72.8		41.5		20-Dec-07		18:06:20		69.2		45.5		20-Dec-07		18:07:53		70.41		44.5		30-Jan-08		18:25:59		72.21		37.5

		20-Dec-07		20:07:10		71.6		42.5		20-Dec-07		20:06:20		68.61		47.5		20-Dec-07		20:07:53		69.8		45		30-Jan-08		20:25:59		72.21		34.5

		20-Dec-07		22:07:10		70.41		44.5		20-Dec-07		22:06:20		68		49.5		20-Dec-07		22:07:53		69.2		46.5		30-Jan-08		22:25:59		69.2		36

		21-Dec-07		0:07:10		69.8		46		21-Dec-07		0:06:20		67.4		51.5		21-Dec-07		0:07:53		68		47.5		31-Jan-08		0:25:59		67.4		36.5

		21-Dec-07		2:07:10		69.2		46		21-Dec-07		2:06:20		67.4		51		21-Dec-07		2:07:53		68		49		31-Jan-08		2:25:59		66.2		36.5

		21-Dec-07		4:07:10		69.2		46.5		21-Dec-07		4:06:20		66.81		51.5		21-Dec-07		4:07:53		67.4		49		31-Jan-08		4:25:59		65.6		37

		21-Dec-07		6:07:10		68.61		44.5		21-Dec-07		6:06:20		66.81		47		21-Dec-07		6:07:53		67.4		47		31-Jan-08		6:25:59		66.81		36

		21-Dec-07		8:07:10		71		38.5		21-Dec-07		8:06:20		68		39		21-Dec-07		8:07:53		69.8		42		31-Jan-08		8:25:59		70.41		34.5

		21-Dec-07		10:07:10		71.6		38.5		21-Dec-07		10:06:20		69.8		38		21-Dec-07		10:07:53		71.6		39.5		31-Jan-08		10:25:59		74.01		34

		21-Dec-07		12:07:10		72.21		37		21-Dec-07		12:06:20		69.8		38.5		21-Dec-07		12:07:53		71		40		31-Jan-08		12:25:59		71		36

		21-Dec-07		14:07:10		72.21		35.5		21-Dec-07		14:06:20		70.41		35		21-Dec-07		14:07:53		71		40.5		31-Jan-08		14:25:59		72.21		35.5

		21-Dec-07		16:07:10		72.21		33		21-Dec-07		16:06:20		70.41		32.5		21-Dec-07		16:07:53		71		35.5		31-Jan-08		16:25:59		72.21		35

		21-Dec-07		18:07:10		71.6		31.5		21-Dec-07		18:06:20		69.2		30.5		21-Dec-07		18:07:53		70.41		34		31-Jan-08		18:25:59		72.21		35.5

		21-Dec-07		20:07:10		69.8		32		21-Dec-07		20:06:20		67.4		34		21-Dec-07		20:07:53		69.2		33.5		31-Jan-08		20:25:59		72.21		35.5

		21-Dec-07		22:07:10		69.2		32		21-Dec-07		22:06:20		66.81		34		21-Dec-07		22:07:53		67.4		34.5		31-Jan-08		22:25:59		69.2		38

		22-Dec-07		0:07:10		68.61		31.5		22-Dec-07		0:06:20		66.2		33.5		22-Dec-07		0:07:53		65.6		35		1-Feb-08		0:25:59		67.4		38.5

		22-Dec-07		2:07:10		68		31		22-Dec-07		2:06:20		66.2		33		22-Dec-07		2:07:53		64.4		35		1-Feb-08		2:25:59		66.2		39

		22-Dec-07		4:07:10		67.4		30		22-Dec-07		4:06:20		66.2		31.5		22-Dec-07		4:07:53		63.21		35		1-Feb-08		4:25:59		65.6		40

		22-Dec-07		6:07:10		67.4		29.5		22-Dec-07		6:06:20		66.2		30.5		22-Dec-07		6:07:53		66.2		31.5		1-Feb-08		6:25:59		66.81		40

		22-Dec-07		8:07:10		69.2		28		22-Dec-07		8:06:20		69.2		29		22-Dec-07		8:07:53		68.61		31.5		1-Feb-08		8:25:59		70.41		39

		22-Dec-07		10:07:10		71		28		22-Dec-07		10:06:20		70.41		30		22-Dec-07		10:07:53		70.41		31		1-Feb-08		10:25:59		73.4		40

		22-Dec-07		12:07:10		71		28.5		22-Dec-07		12:06:20		70.41		29.5		22-Dec-07		12:07:53		71.6		28.5		1-Feb-08		12:25:59		72.21		41

		22-Dec-07		14:07:10		71		26.5		22-Dec-07		14:06:20		69.2		26		22-Dec-07		14:07:53		69.8		30		1-Feb-08		14:25:59		72.8		42.5

		22-Dec-07		16:07:10		71		26.5		22-Dec-07		16:06:20		69.2		26		22-Dec-07		16:07:53		69.2		29.5		1-Feb-08		16:25:59		72.8		44

		22-Dec-07		18:07:10		70.41		26.5		22-Dec-07		18:06:20		69.2		26		22-Dec-07		18:07:53		69.2		29.5		1-Feb-08		18:25:59		72.21		45.5

		22-Dec-07		20:07:10		69.8		28		22-Dec-07		20:06:20		66.81		31		22-Dec-07		20:07:53		68		31.5		1-Feb-08		20:25:59		72.8		41

		22-Dec-07		22:07:10		68.61		28.5		22-Dec-07		22:06:20		66.2		31		22-Dec-07		22:07:53		66.2		31.5		1-Feb-08		22:25:59		69.8		42

		23-Dec-07		0:07:10		68		28		23-Dec-07		0:06:20		65.6		31		23-Dec-07		0:07:53		64.4		31.5		2-Feb-08		0:25:59		67.4		41.5

		23-Dec-07		2:07:10		66.81		27.5		23-Dec-07		2:06:20		65.6		30		23-Dec-07		2:07:53		63.21		32		2-Feb-08		2:25:59		65.6		40.5

		23-Dec-07		4:07:10		66.81		27		23-Dec-07		4:06:20		65.6		29.5		23-Dec-07		4:07:53		62		31.5		2-Feb-08		4:25:59		64.4		39.5

		23-Dec-07		6:07:10		66.2		26.5		23-Dec-07		6:06:20		65.6		28		23-Dec-07		6:07:53		61.41		31.5		2-Feb-08		6:25:59		65.6		37

		23-Dec-07		8:07:10		66.81		26.5		23-Dec-07		8:06:20		66.81		28		23-Dec-07		8:07:53		67.4		28		2-Feb-08		8:25:59		68		34.5

		23-Dec-07		10:07:10		67.4		28		23-Dec-07		10:06:20		67.4		29.5		23-Dec-07		10:07:53		68		28		2-Feb-08		10:25:59		71		38.5

		23-Dec-07		12:07:10		67.4		30		23-Dec-07		12:06:20		67.4		31.5		23-Dec-07		12:07:53		68		30.5		2-Feb-08		12:25:59		71.6		37

		23-Dec-07		14:07:10		68		29.5		23-Dec-07		14:06:20		67.4		30.5		23-Dec-07		14:07:53		68		31		2-Feb-08		14:25:59		71.6		39

		23-Dec-07		16:07:10		68		29.5		23-Dec-07		16:06:20		68		30.5		23-Dec-07		16:07:53		68		31.5		2-Feb-08		16:25:59		71.6		39

		23-Dec-07		18:07:10		68.61		29.5		23-Dec-07		18:06:20		67.4		30		23-Dec-07		18:07:53		68		31.5		2-Feb-08		18:25:59		71.6		39

		23-Dec-07		20:07:10		68		31.5		23-Dec-07		20:06:20		66.2		34		23-Dec-07		20:07:53		68.61		31.5		2-Feb-08		20:25:59		71.6		38.5

		23-Dec-07		22:07:10		67.4		32		23-Dec-07		22:06:20		66.2		34.5		23-Dec-07		22:07:53		68.61		32		2-Feb-08		22:25:59		68.61		39.5

		24-Dec-07		0:07:10		66.81		32		24-Dec-07		0:06:20		65.6		34.5		24-Dec-07		0:07:53		68.61		31.5		3-Feb-08		0:25:59		66.81		40.5

		24-Dec-07		2:07:10		66.81		31.5		24-Dec-07		2:06:20		66.2		33.5		24-Dec-07		2:07:53		68.61		31.5		3-Feb-08		2:25:59		66.2		41

		24-Dec-07		4:07:10		66.81		31.5		24-Dec-07		4:06:20		65.6		34		24-Dec-07		4:07:53		68.61		31.5		3-Feb-08		4:25:59		65.6		42

		24-Dec-07		6:07:10		66.81		31.5		24-Dec-07		6:06:20		65.6		33		24-Dec-07		6:07:53		68		31		3-Feb-08		6:25:59		65.01		42.5

		24-Dec-07		8:07:10		67.4		31		24-Dec-07		8:06:20		67.4		32		24-Dec-07		8:07:53		69.2		30.5		3-Feb-08		8:25:59		65.01		43

		24-Dec-07		10:07:10		67.4		32		24-Dec-07		10:06:20		67.4		33.5		24-Dec-07		10:07:53		69.2		31		3-Feb-08		10:25:59		66.2		43

		24-Dec-07		12:07:10		68		32.5		24-Dec-07		12:06:20		67.4		33.5		24-Dec-07		12:07:53		68.61		32		3-Feb-08		12:25:59		66.81		45

		24-Dec-07		14:07:10		68.61		36		24-Dec-07		14:06:20		68		38.5		24-Dec-07		14:07:53		69.2		35.5		3-Feb-08		14:25:59		67.4		46

		24-Dec-07		16:07:10		69.2		40		24-Dec-07		16:06:20		68.61		44		24-Dec-07		16:07:53		69.8		39.5		3-Feb-08		16:25:59		67.4		48.5

		24-Dec-07		18:07:10		69.8		43		24-Dec-07		18:06:20		68.61		48		24-Dec-07		18:07:53		69.8		43		3-Feb-08		18:25:59		66.81		50.5

		24-Dec-07		20:07:10		68.61		43		24-Dec-07		20:06:20		66.81		47.5		24-Dec-07		20:07:53		69.2		42.5		3-Feb-08		20:25:59		66.81		50

		24-Dec-07		22:07:10		68		41.5		24-Dec-07		22:06:20		66.2		46		24-Dec-07		22:07:53		69.8		40.5		3-Feb-08		22:25:59		66.2		51.5

		25-Dec-07		0:07:10		68		41.5		25-Dec-07		0:06:20		66.2		45		25-Dec-07		0:07:53		69.8		40		4-Feb-08		0:25:59		66.2		52.5

		25-Dec-07		2:07:10		67.4		40.5		25-Dec-07		2:06:20		66.2		44.5		25-Dec-07		2:07:53		69.8		39		4-Feb-08		2:25:59		66.2		51.5

		25-Dec-07		4:07:10		67.4		40.5		25-Dec-07		4:06:20		66.2		43.5		25-Dec-07		4:07:53		69.8		38		4-Feb-08		4:25:59		65.6		49.5

		25-Dec-07		6:07:10		67.4		39.5		25-Dec-07		6:06:20		66.2		42		25-Dec-07		6:07:53		69.8		37		4-Feb-08		6:25:59		65.6		48.5

		25-Dec-07		8:07:10		69.2		37.5		25-Dec-07		8:06:20		67.4		40		25-Dec-07		8:07:53		69.2		38		4-Feb-08		8:25:59		65.6		47

		25-Dec-07		10:07:10		69.8		33.5		25-Dec-07		10:06:20		68		34.5		25-Dec-07		10:07:53		68.61		35		4-Feb-08		10:25:59		66.2		46

		25-Dec-07		12:07:10		71		31.5		25-Dec-07		12:06:20		69.2		31		25-Dec-07		12:07:53		69.2		33.5		4-Feb-08		12:25:59		66.81		46.5

		25-Dec-07		14:07:10		70.41		30		25-Dec-07		14:06:20		69.2		28		25-Dec-07		14:07:53		69.8		31.5		4-Feb-08		14:25:59		67.4		46

		25-Dec-07		16:07:10		70.41		27.5		25-Dec-07		16:06:20		68.61		26		25-Dec-07		16:07:53		70.41		30.5		4-Feb-08		16:25:59		67.4		45.5

		25-Dec-07		18:07:10		70.41		29.5		25-Dec-07		18:06:20		68.61		29		25-Dec-07		18:07:53		70.41		30.5		4-Feb-08		18:25:59		67.4		45

		25-Dec-07		20:07:10		69.2		32		25-Dec-07		20:06:20		66.81		34.5		25-Dec-07		20:07:53		69.2		33		4-Feb-08		20:25:59		66.2		45

		25-Dec-07		22:07:10		68		30		25-Dec-07		22:06:20		66.2		31.5		25-Dec-07		22:07:53		67.4		32		4-Feb-08		22:25:59		65.6		45

		26-Dec-07		0:07:10		67.4		29.5		26-Dec-07		0:06:20		65.6		31		26-Dec-07		0:07:53		65.6		31.5		5-Feb-08		0:25:59		65.6		44.5

		26-Dec-07		2:07:10		66.81		28.5		26-Dec-07		2:06:20		65.6		30		26-Dec-07		2:07:53		64.4		31.5		5-Feb-08		2:25:59		65.01		44.5

		26-Dec-07		4:07:10		66.2		28		26-Dec-07		4:06:20		65.6		29.5		26-Dec-07		4:07:53		62.6		31		5-Feb-08		4:25:59		65.01		44

		26-Dec-07		6:07:10		66.2		27.5		26-Dec-07		6:06:20		65.6		29		26-Dec-07		6:07:53		66.81		28.5		5-Feb-08		6:25:59		66.2		42.5

		26-Dec-07		8:07:10		66.81		26.5		26-Dec-07		8:06:20		66.81		27		26-Dec-07		8:07:53		68		27.5		5-Feb-08		8:25:59		69.8		39.5

		26-Dec-07		10:07:10		67.4		26.5		26-Dec-07		10:06:20		67.4		27.5		26-Dec-07		10:07:53		68.61		27.5		5-Feb-08		10:25:59		72.8		37.5

		26-Dec-07		12:07:10		67.4		27.5		26-Dec-07		12:06:20		67.4		28		26-Dec-07		12:07:53		68.61		28.5		5-Feb-08		12:25:59		71.6		37.5

		26-Dec-07		14:07:10		68		28		26-Dec-07		14:06:20		68		28		26-Dec-07		14:07:53		68.61		29.5		5-Feb-08		14:25:59		71.6		36

		26-Dec-07		16:07:10		68.61		29.5		26-Dec-07		16:06:20		68		30.5		26-Dec-07		16:07:53		68.61		31		5-Feb-08		16:25:59		72.8		34.5

		26-Dec-07		18:07:10		68.61		32.5		26-Dec-07		18:06:20		68		35		26-Dec-07		18:07:53		68.61		34		5-Feb-08		18:25:59		72.8		34.5

		26-Dec-07		20:07:10		68		33.5		26-Dec-07		20:06:20		66.81		36		26-Dec-07		20:07:53		69.2		34		5-Feb-08		20:25:59		72.21		34

		26-Dec-07		22:07:10		67.4		34		26-Dec-07		22:06:20		66.2		36.5		26-Dec-07		22:07:53		67.4		34.5		5-Feb-08		22:25:59		69.2		36

		27-Dec-07		0:07:10		66.81		34.5		27-Dec-07		0:06:20		66.2		38		27-Dec-07		0:07:53		66.2		36		6-Feb-08		0:25:59		67.4		37

		27-Dec-07		2:07:10		66.81		34		27-Dec-07		2:06:20		66.2		36		27-Dec-07		2:07:53		65.01		36		6-Feb-08		2:25:59		66.2		38

		27-Dec-07		4:07:10		66.2		32.5		27-Dec-07		4:06:20		65.6		34		27-Dec-07		4:07:53		63.8		35		6-Feb-08		4:25:59		65.6		38

		27-Dec-07		6:07:10		66.2		31.5		27-Dec-07		6:06:20		65.6		32.5		27-Dec-07		6:07:53		68		31.5		6-Feb-08		6:25:59		66.81		39.5

		27-Dec-07		8:07:10		68		30		27-Dec-07		8:06:20		67.4		31		27-Dec-07		8:07:53		70.41		30.5		6-Feb-08		8:25:59		70.41		36.5

		27-Dec-07		10:07:10		69.2		30.5		27-Dec-07		10:06:20		69.8		31.5		27-Dec-07		10:07:53		71		30.5		6-Feb-08		10:25:59		72.8		35.5

		27-Dec-07		12:07:10		71		28.5		27-Dec-07		12:06:20		70.41		28.5		27-Dec-07		12:07:53		71		29		6-Feb-08		12:25:59		71		37

		27-Dec-07		14:07:10		70.41		25.5		27-Dec-07		14:06:20		70.41		24.5		27-Dec-07		14:07:53		71		25.5		6-Feb-08		14:25:59		72.21		37

		27-Dec-07		16:07:10		71		22.5		27-Dec-07		16:06:20		71		22		27-Dec-07		16:07:53		69.8		24		6-Feb-08		16:25:59		72.8		34.5

		27-Dec-07		18:07:10		70.41		23		27-Dec-07		18:06:20		68.61		23.5		27-Dec-07		18:07:53		69.2		24.5		6-Feb-08		18:25:59		72.8		35

		27-Dec-07		20:07:10		69.8		24		27-Dec-07		20:06:20		66.81		26		27-Dec-07		20:07:53		68		26		6-Feb-08		20:25:59		72.8		37

		27-Dec-07		22:07:10		68		24		27-Dec-07		22:06:20		66.2		26		27-Dec-07		22:07:53		66.2		27		6-Feb-08		22:25:59		69.8		38

		28-Dec-07		0:07:10		67.4		24.5		28-Dec-07		0:06:20		65.6		26		28-Dec-07		0:07:53		65.01		27.5		7-Feb-08		0:25:59		68		38.5

		28-Dec-07		2:07:10		66.81		24		28-Dec-07		2:06:20		65.6		26		28-Dec-07		2:07:53		63.21		28		7-Feb-08		2:25:59		66.81		38.5

		28-Dec-07		4:07:10		66.2		24		28-Dec-07		4:06:20		65.6		25.5		28-Dec-07		4:07:53		62.6		28		7-Feb-08		4:25:59		66.2		38.5

		28-Dec-07		6:07:10		66.2		24.5		28-Dec-07		6:06:20		65.6		25.5		28-Dec-07		6:07:53		66.2		26		7-Feb-08		6:25:59		67.4		38.5

		28-Dec-07		8:07:10		68		23.5		28-Dec-07		8:06:20		67.4		24.5		28-Dec-07		8:07:53		68		25.5		7-Feb-08		8:25:59		71.6		38

		28-Dec-07		10:07:10		69.2		24		28-Dec-07		10:06:20		69.2		25.5		28-Dec-07		10:07:53		69.8		25		7-Feb-08		10:25:59		72.21		37.5

		28-Dec-07		12:07:10		70.41		25		28-Dec-07		12:06:20		70.41		26		28-Dec-07		12:07:53		71		26		7-Feb-08		12:25:59		71.6		40.5

		28-Dec-07		14:07:10		70.41		25.5		28-Dec-07		14:06:20		70.41		26		28-Dec-07		14:07:53		71		27		7-Feb-08		14:25:59		71.6		40

		28-Dec-07		16:07:10		71		26.5		28-Dec-07		16:06:20		70.41		27.5		28-Dec-07		16:07:53		71		25		7-Feb-08		16:25:59		72.8		38

		28-Dec-07		18:07:10		71		28.5		28-Dec-07		18:06:20		68.61		31.5		28-Dec-07		18:07:53		71		29.5		7-Feb-08		18:25:59		72.8		37.5

		28-Dec-07		20:07:10		71		31.5		28-Dec-07		20:06:20		66.81		37		28-Dec-07		20:07:53		69.8		32.5		7-Feb-08		20:25:59		72.21		36

		28-Dec-07		22:07:10		69.8		33		28-Dec-07		22:06:20		66.2		38.5		28-Dec-07		22:07:53		68		34.5		7-Feb-08		22:25:59		69.2		37.5

		29-Dec-07		0:07:10		68.61		34		29-Dec-07		0:06:20		66.2		39		29-Dec-07		0:07:53		66.81		36		8-Feb-08		0:25:59		67.4		38.5

		29-Dec-07		2:07:10		68		34		29-Dec-07		2:06:20		66.2		37.5		29-Dec-07		2:07:53		66.2		36.5		8-Feb-08		2:25:59		66.81		39

		29-Dec-07		4:07:10		67.4		34		29-Dec-07		4:06:20		66.2		38		29-Dec-07		4:07:53		65.01		37		8-Feb-08		4:25:59		65.6		39.5

		29-Dec-07		6:07:10		68		33.5		29-Dec-07		6:06:20		65.6		36.5		29-Dec-07		6:07:53		66.81		35.5		8-Feb-08		6:25:59		67.4		39.5

		29-Dec-07		8:07:10		69.8		32		29-Dec-07		8:06:20		68		34.5		29-Dec-07		8:07:53		68.61		35.5		8-Feb-08		8:25:59		71		37.5

		29-Dec-07		10:07:10		70.41		32		29-Dec-07		10:06:20		69.8		33		29-Dec-07		10:07:53		70.41		33.5		8-Feb-08		10:25:59		71.6		38

		29-Dec-07		12:07:10		72.21		33		29-Dec-07		12:06:20		70.41		35		29-Dec-07		12:07:53		71.6		34		8-Feb-08		12:25:59		71		39

		29-Dec-07		14:07:10		72.8		32.5		29-Dec-07		14:06:20		71		34		29-Dec-07		14:07:53		71.6		34		8-Feb-08		14:25:59		72.21		40

		29-Dec-07		16:07:10		72.8		32		29-Dec-07		16:06:20		71		35		29-Dec-07		16:07:53		70.41		34.5		8-Feb-08		16:25:59		73.4		41

		29-Dec-07		18:07:10		72.21		32		29-Dec-07		18:06:20		69.2		35		29-Dec-07		18:07:53		69.2		35.5		8-Feb-08		18:25:59		74.01		40

		29-Dec-07		20:07:10		71		33		29-Dec-07		20:06:20		67.4		37.5		29-Dec-07		20:07:53		68		36.5		8-Feb-08		20:25:59		72.21		40.5

		29-Dec-07		22:07:10		69.2		34		29-Dec-07		22:06:20		66.81		38.5		29-Dec-07		22:07:53		66.2		37.5		8-Feb-08		22:25:59		70.41		41.5

		30-Dec-07		0:07:10		68		34.5		30-Dec-07		0:06:20		66.2		38.5		30-Dec-07		0:07:53		65.01		38.5		9-Feb-08		0:25:59		69.2		41.5

		30-Dec-07		2:07:10		67.4		35.5		30-Dec-07		2:06:20		65.6		39		30-Dec-07		2:07:53		63.8		40		9-Feb-08		2:25:59		68		41

		30-Dec-07		4:07:10		67.4		36		30-Dec-07		4:06:20		66.2		39.5		30-Dec-07		4:07:53		63.8		41		9-Feb-08		4:25:59		66.2		40.5

		30-Dec-07		6:07:10		66.81		37		30-Dec-07		6:06:20		65.6		40.5		30-Dec-07		6:07:53		63.21		42		9-Feb-08		6:25:59		67.4		39.5

		30-Dec-07		8:07:10		67.4		37		30-Dec-07		8:06:20		67.4		39		30-Dec-07		8:07:53		69.2		37		9-Feb-08		8:25:59		71		36.5

		30-Dec-07		10:07:10		68		37.5		30-Dec-07		10:06:20		67.4		40		30-Dec-07		10:07:53		67.4		39.5		9-Feb-08		10:25:59		71		37.5

		30-Dec-07		12:07:10		68		39		30-Dec-07		12:06:20		67.4		41.5		30-Dec-07		12:07:53		67.4		39.5		9-Feb-08		12:25:59		70.41		39

		30-Dec-07		14:07:10		68		40		30-Dec-07		14:06:20		67.4		42.5		30-Dec-07		14:07:53		67.4		40.5		9-Feb-08		14:25:59		71.6		37.5

		30-Dec-07		16:07:10		68		41		30-Dec-07		16:06:20		67.4		43.5		30-Dec-07		16:07:53		66.81		42.5		9-Feb-08		16:25:59		72.8		34

		30-Dec-07		18:07:10		68		41.5		30-Dec-07		18:06:20		67.4		44		30-Dec-07		18:07:53		66.81		43.5		9-Feb-08		18:25:59		73.4		33.5

		30-Dec-07		20:07:10		67.4		42.5		30-Dec-07		20:06:20		66.2		46		30-Dec-07		20:07:53		67.4		43		9-Feb-08		20:25:59		71.6		37.5

		30-Dec-07		22:07:10		66.81		43		30-Dec-07		22:06:20		66.2		46.5		30-Dec-07		22:07:53		65.01		45.5		9-Feb-08		22:25:59		69.8		38.5

		31-Dec-07		0:07:10		66.81		43.5		31-Dec-07		0:06:20		66.2		46.5		31-Dec-07		0:07:53		64.4		47		10-Feb-08		0:25:59		68		39

		31-Dec-07		2:07:10		66.81		44		31-Dec-07		2:06:20		66.2		47		31-Dec-07		2:07:53		63.8		48		10-Feb-08		2:25:59		66.2		39

		31-Dec-07		4:07:10		66.81		44		31-Dec-07		4:06:20		66.2		47		31-Dec-07		4:07:53		63.21		49		10-Feb-08		4:25:59		65.6		39.5

		31-Dec-07		6:07:10		66.81		42.5		31-Dec-07		6:06:20		65.6		44		31-Dec-07		6:07:53		63.21		48		10-Feb-08		6:25:59		64.4		40

		31-Dec-07		8:07:10		66.81		39.5		31-Dec-07		8:06:20		67.4		40		31-Dec-07		8:07:53		66.2		42		10-Feb-08		8:25:59		64.4		39.5

		31-Dec-07		10:07:10		67.4		38		31-Dec-07		10:06:20		67.4		38.5		31-Dec-07		10:07:53		68		38.5		10-Feb-08		10:25:59		65.01		40.5

		31-Dec-07		12:07:10		67.4		36.5		31-Dec-07		12:06:20		67.4		37		31-Dec-07		12:07:53		66.81		38		10-Feb-08		12:25:59		66.81		43

		31-Dec-07		14:07:10		68		34.5		31-Dec-07		14:06:20		68		34		31-Dec-07		14:07:53		67.4		36.5		10-Feb-08		14:25:59		68.61		44

		31-Dec-07		16:07:10		68		32		31-Dec-07		16:06:20		67.4		31.5		31-Dec-07		16:07:53		67.4		35		10-Feb-08		16:25:59		69.8		42

		31-Dec-07		18:07:10		68		30.5		31-Dec-07		18:06:20		68		30		31-Dec-07		18:07:53		67.4		33.5		10-Feb-08		18:25:59		71		42.5

		31-Dec-07		20:07:10		67.4		31		31-Dec-07		20:06:20		66.2		31.5		31-Dec-07		20:07:53		65.6		33.5		10-Feb-08		20:25:59		69.8		42.5

		31-Dec-07		22:07:10		66.81		31.5		31-Dec-07		22:06:20		65.6		33		31-Dec-07		22:07:53		63.8		35		10-Feb-08		22:25:59		68		43

		1-Jan-08		0:07:10		66.2		30.5		1-Jan-08		0:06:20		65.6		31.5		1-Jan-08		0:07:53		63.21		34.5		11-Feb-08		0:25:59		66.81		43

		1-Jan-08		2:07:10		66.2		29.5		1-Jan-08		2:06:20		65.6		30		1-Jan-08		2:07:53		62		33.5		11-Feb-08		2:25:59		65.6		43

		1-Jan-08		4:07:10		66.2		29		1-Jan-08		4:06:20		65.6		29.5		1-Jan-08		4:07:53		61.41		33.5		11-Feb-08		4:25:59		65.01		43

		1-Jan-08		6:07:10		66.2		28.5		1-Jan-08		6:06:20		65.6		29.5		1-Jan-08		6:07:53		67.4		29		11-Feb-08		6:25:59		64.4		42.5

		1-Jan-08		8:07:10		67.4		27		1-Jan-08		8:06:20		68.61		27.5		1-Jan-08		8:07:53		69.2		28.5		11-Feb-08		8:25:59		64.4		41.5

		1-Jan-08		10:07:10		68.61		27.5		1-Jan-08		10:06:20		69.2		28.5		1-Jan-08		10:07:53		69.8		29		11-Feb-08		10:25:59		65.6		41.5

		1-Jan-08		12:07:10		69.8		29		1-Jan-08		12:06:20		69.2		28.5		1-Jan-08		12:07:53		71.6		29		11-Feb-08		12:25:59		68		45

		1-Jan-08		14:07:10		71		29.5		1-Jan-08		14:06:20		70.41		30.5		1-Jan-08		14:07:53		71		31.5		11-Feb-08		14:25:59		69.2		45

		1-Jan-08		16:07:10		71.6		28.5		1-Jan-08		16:06:20		69.2		29		1-Jan-08		16:07:53		69.8		30.5		11-Feb-08		16:25:59		70.41		44.5

		1-Jan-08		18:07:10		71.6		29		1-Jan-08		18:06:20		69.2		30		1-Jan-08		18:07:53		69.8		31.5		11-Feb-08		18:25:59		71		45

		1-Jan-08		20:07:10		70.41		28.5		1-Jan-08		20:06:20		67.4		31		1-Jan-08		20:07:53		68.61		31.5		11-Feb-08		20:25:59		69.8		45

		1-Jan-08		22:07:10		68.61		28.5		1-Jan-08		22:06:20		66.81		31		1-Jan-08		22:07:53		66.2		31.5		11-Feb-08		22:25:59		68		45.5

		2-Jan-08		0:07:10		67.4		28.5		2-Jan-08		0:06:20		66.2		30.5		2-Jan-08		0:07:53		63.8		32		12-Feb-08		0:25:59		66.81		45.5

		2-Jan-08		2:07:10		66.81		29		2-Jan-08		2:06:20		65.6		31		2-Jan-08		2:07:53		62		33		12-Feb-08		2:25:59		65.6		45

		2-Jan-08		4:07:10		66.2		27.5		2-Jan-08		4:06:20		65.6		29.5		2-Jan-08		4:07:53		60.8		33		12-Feb-08		4:25:59		65.01		45

		2-Jan-08		6:07:10		66.81		27		2-Jan-08		6:06:20		65.6		29		2-Jan-08		6:07:53		66.81		28.5		12-Feb-08		6:25:59		66.2		44

		2-Jan-08		8:07:10		67.4		26		2-Jan-08		8:06:20		66.81		27.5		2-Jan-08		8:07:53		67.4		27.5		12-Feb-08		8:25:59		69.2		40.5

		2-Jan-08		10:07:10		68		26.5		2-Jan-08		10:06:20		67.4		28		2-Jan-08		10:07:53		67.4		28		12-Feb-08		10:25:59		72.8		40

		2-Jan-08		12:07:10		69.2		29.5		2-Jan-08		12:06:20		68		31.5		2-Jan-08		12:07:53		67.4		31		12-Feb-08		12:25:59		71.6		43

		2-Jan-08		14:07:10		70.41		31.5		2-Jan-08		14:06:20		68.61		33.5		2-Jan-08		14:07:53		68		33.5		12-Feb-08		14:25:59		72.8		43.5

		2-Jan-08		16:07:10		71.6		32		2-Jan-08		16:06:20		69.2		34		2-Jan-08		16:07:53		69.2		34.5		12-Feb-08		16:25:59		74.01		43.5

		2-Jan-08		18:07:10		72.21		31		2-Jan-08		18:06:20		69.2		33		2-Jan-08		18:07:53		68.61		34.5		12-Feb-08		18:25:59		74.01		44.5

		2-Jan-08		20:07:10		71.6		31		2-Jan-08		20:06:20		68		34		2-Jan-08		20:07:53		68		34.5		12-Feb-08		20:25:59		71.6		43.5

		2-Jan-08		22:07:10		69.2		31		2-Jan-08		22:06:20		66.81		35.5		2-Jan-08		22:07:53		66.81		34.5		12-Feb-08		22:25:59		70.41		44.5

		3-Jan-08		0:07:10		68		32		3-Jan-08		0:06:20		66.2		35.5		3-Jan-08		0:07:53		64.4		36		13-Feb-08		0:25:59		68.61		44.5

		3-Jan-08		2:07:10		66.81		31.5		3-Jan-08		2:06:20		66.2		34		3-Jan-08		2:07:53		63.21		36.5		13-Feb-08		2:25:59		67.4		44

		3-Jan-08		4:07:10		66.2		31.5		3-Jan-08		4:06:20		66.2		34		3-Jan-08		4:07:53		62		36.5		13-Feb-08		4:25:59		66.2		44

		3-Jan-08		6:07:10		66.81		31.5		3-Jan-08		6:06:20		65.6		34		3-Jan-08		6:07:53		66.81		33.5		13-Feb-08		6:25:59		66.81		43.5

		3-Jan-08		8:07:10		68.61		29.5		3-Jan-08		8:06:20		67.4		31.5		3-Jan-08		8:07:53		68		32.5		13-Feb-08		8:25:59		72.21		39.5

		3-Jan-08		10:07:10		69.2		30.5		3-Jan-08		10:06:20		69.8		32.5		3-Jan-08		10:07:53		69.8		32		13-Feb-08		10:25:59		71.6		40.5

		3-Jan-08		12:07:10		71.6		32		3-Jan-08		12:06:20		71		32.5		3-Jan-08		12:07:53		72.21		32.5		13-Feb-08		12:25:59		72.21		43

		3-Jan-08		14:07:10		72.8		31		3-Jan-08		14:06:20		71		30.5		3-Jan-08		14:07:53		71		35		13-Feb-08		14:25:59		74.01		43.5

		3-Jan-08		16:07:10		72.21		32.5		3-Jan-08		16:06:20		71		34.5		3-Jan-08		16:07:53		70.41		33.5		13-Feb-08		16:25:59		74.6		44.5

		3-Jan-08		18:07:10		72.21		32.5		3-Jan-08		18:06:20		69.2		35		3-Jan-08		18:07:53		70.41		35.5		13-Feb-08		18:25:59		74.01		44

		3-Jan-08		20:07:10		71.6		34		3-Jan-08		20:06:20		68		39		3-Jan-08		20:07:53		69.8		36.5		13-Feb-08		20:25:59		72.21		43.5

		3-Jan-08		22:07:10		70.41		33.5		3-Jan-08		22:06:20		66.81		37.5		3-Jan-08		22:07:53		68		36.5		13-Feb-08		22:25:59		71		43.5

		4-Jan-08		0:07:10		69.2		33		4-Jan-08		0:06:20		66.2		37		4-Jan-08		0:07:53		66.2		36.5		14-Feb-08		0:25:59		68.61		43.5

		4-Jan-08		2:07:10		68.61		34.5		4-Jan-08		2:06:20		66.2		39		4-Jan-08		2:07:53		65.01		38.5		14-Feb-08		2:25:59		67.4		43.5

		4-Jan-08		4:07:10		68		35		4-Jan-08		4:06:20		66.2		39.5		4-Jan-08		4:07:53		65.01		39.5		14-Feb-08		4:25:59		66.2		43.5

		4-Jan-08		6:07:10		68.61		36.5		4-Jan-08		6:06:20		66.2		41		4-Jan-08		6:07:53		66.81		40		14-Feb-08		6:25:59		66.81		44

		4-Jan-08		8:07:10		71		37.5		4-Jan-08		8:06:20		68.61		42		4-Jan-08		8:07:53		70.41		39.5		14-Feb-08		8:25:59		70.41		41

		4-Jan-08		10:07:10		72.21		39		4-Jan-08		10:06:20		70.41		40		4-Jan-08		10:07:53		71.6		40.5		14-Feb-08		10:25:59		71.6		37

		4-Jan-08		12:07:10		73.4		40		4-Jan-08		12:06:20		71		46.5		4-Jan-08		12:07:53		71		45.5		14-Feb-08		12:25:59		71.6		36.5

		4-Jan-08		14:07:10		72.8		42.5		4-Jan-08		14:06:20		71		47.5		4-Jan-08		14:07:53		71		45.5		14-Feb-08		14:25:59		72.8		36

		4-Jan-08		16:07:10		73.4		43.5		4-Jan-08		16:06:20		70.41		49		4-Jan-08		16:07:53		71.6		41.5		14-Feb-08		16:25:59		73.4		32

		4-Jan-08		18:07:10		72.8		42.5		4-Jan-08		18:06:20		69.8		47.5		4-Jan-08		18:07:53		71		42		14-Feb-08		18:25:59		73.4		29

		4-Jan-08		20:07:10		71.6		42.5		4-Jan-08		20:06:20		69.2		48		4-Jan-08		20:07:53		69.8		45.5		14-Feb-08		20:25:59		71.6		28

		4-Jan-08		22:07:10		71		43		4-Jan-08		22:06:20		68		49.5		4-Jan-08		22:07:53		69.2		46.5		14-Feb-08		22:25:59		70.41		31.5

		5-Jan-08		0:07:10		69.8		43.5		5-Jan-08		0:06:20		67.4		50.5		5-Jan-08		0:07:53		69.2		46.5		15-Feb-08		0:25:59		68.61		32.5

		5-Jan-08		2:07:10		69.2		44		5-Jan-08		2:06:20		67.4		51		5-Jan-08		2:07:53		68.61		47		15-Feb-08		2:25:59		67.4		33

		5-Jan-08		4:07:10		69.2		45		5-Jan-08		4:06:20		67.4		52.5		5-Jan-08		4:07:53		68.61		48		15-Feb-08		4:25:59		66.2		33.5

		5-Jan-08		6:07:10		68.61		46		5-Jan-08		6:06:20		67.4		53.5		5-Jan-08		6:07:53		68		49		15-Feb-08		6:25:59		66.81		33.5

		5-Jan-08		8:07:10		69.8		47		5-Jan-08		8:06:20		69.2		53.5		5-Jan-08		8:07:53		70.41		53		15-Feb-08		8:25:59		70.41		32

		5-Jan-08		10:07:10		71		49.5		5-Jan-08		10:06:20		70.41		56.5		5-Jan-08		10:07:53		71		49		15-Feb-08		10:25:59		71.6		30.5

		5-Jan-08		12:07:10		71		49.5		5-Jan-08		12:06:20		71		51		5-Jan-08		12:07:53		71		54.5		15-Feb-08		12:25:59		72.21		30

		5-Jan-08		14:07:10		70.41		46		5-Jan-08		14:06:20		70.41		47		5-Jan-08		14:07:53		72.21		45.5		15-Feb-08		14:25:59		72.8		30.5

		5-Jan-08		16:07:10		69.8		45.5		5-Jan-08		16:06:20		71		46		5-Jan-08		16:07:53		71		46		15-Feb-08		16:25:59		73.4		29.5

		5-Jan-08		18:07:10		73.4		41.5		5-Jan-08		18:06:20		74.01		42		5-Jan-08		18:07:53		74.01		42.5		15-Feb-08		18:25:59		74.01		30

		5-Jan-08		20:07:10		69.2		42.5		5-Jan-08		20:06:20		68		44.5		5-Jan-08		20:07:53		69.2		43.5		15-Feb-08		20:25:59		71		30

		5-Jan-08		22:07:10		68		41.5		5-Jan-08		22:06:20		66.81		43.5		5-Jan-08		22:07:53		68		44		15-Feb-08		22:25:59		69.2		31.5

		6-Jan-08		0:07:10		67.4		41		6-Jan-08		0:06:20		66.81		42.5		6-Jan-08		0:07:53		67.4		43.5		16-Feb-08		0:25:59		68		33

		6-Jan-08		2:07:10		66.81		39.5		6-Jan-08		2:06:20		66.81		39.5		6-Jan-08		2:07:53		66.2		42.5		16-Feb-08		2:25:59		66.2		34

		6-Jan-08		4:07:10		66.2		41		6-Jan-08		4:06:20		66.2		42		6-Jan-08		4:07:53		65.6		43		16-Feb-08		4:25:59		65.6		35

		6-Jan-08		6:07:10		65.6		41		6-Jan-08		6:06:20		66.2		41		6-Jan-08		6:07:53		65.01		43.5		16-Feb-08		6:25:59		66.2		36

		6-Jan-08		8:07:10		65.6		42		6-Jan-08		8:06:20		68		40		6-Jan-08		8:07:53		66.81		41		16-Feb-08		8:25:59		69.2		34

		6-Jan-08		10:07:10		65.6		43.5		6-Jan-08		10:06:20		68		42.5		6-Jan-08		10:07:53		66.81		42.5		16-Feb-08		10:25:59		71.6		34.5

		6-Jan-08		12:07:10		65.6		44.5		6-Jan-08		12:06:20		68		42.5		6-Jan-08		12:07:53		67.4		43		16-Feb-08		12:25:59		72.21		34

		6-Jan-08		14:07:10		65.6		45.5		6-Jan-08		14:06:20		68		44		6-Jan-08		14:07:53		67.4		45		16-Feb-08		14:25:59		72.8		34

		6-Jan-08		16:07:10		66.2		45		6-Jan-08		16:06:20		68		43.5		6-Jan-08		16:07:53		68		44.5		16-Feb-08		16:25:59		74.6		37

		6-Jan-08		18:07:10		66.2		45		6-Jan-08		18:06:20		68		44		6-Jan-08		18:07:53		67.4		45		16-Feb-08		18:25:59		74.01		37

		6-Jan-08		20:07:10		66.2		45		6-Jan-08		20:06:20		66.81		44.5		6-Jan-08		20:07:53		67.4		44		16-Feb-08		20:25:59		71.6		37.5

		6-Jan-08		22:07:10		65.6		43		6-Jan-08		22:06:20		66.81		42.5		6-Jan-08		22:07:53		66.2		43.5		16-Feb-08		22:25:59		69.2		38

		7-Jan-08		0:07:10		65.01		42.5		7-Jan-08		0:06:20		66.2		41.5		7-Jan-08		0:07:53		65.6		43		17-Feb-08		0:25:59		68		39

		7-Jan-08		2:07:10		65.01		42.5		7-Jan-08		2:06:20		66.2		41		7-Jan-08		2:07:53		65.6		43		17-Feb-08		2:25:59		67.4		39.5

		7-Jan-08		4:07:10		64.4		41.5		7-Jan-08		4:06:20		66.2		40		7-Jan-08		4:07:53		65.01		42		17-Feb-08		4:25:59		66.81		40.5

		7-Jan-08		6:07:10		64.4		40		7-Jan-08		6:06:20		66.2		38		7-Jan-08		6:07:53		64.4		41		17-Feb-08		6:25:59		66.81		41

		7-Jan-08		8:07:10		64.4		40.5		7-Jan-08		8:06:20		67.4		37		7-Jan-08		8:07:53		66.81		38.5		17-Feb-08		8:25:59		66.2		41

		7-Jan-08		10:07:10		64.4		39		7-Jan-08		10:06:20		67.4		35.5		7-Jan-08		10:07:53		67.4		36.5		17-Feb-08		10:25:59		66.2		41

		7-Jan-08		12:07:10		64.4		41		7-Jan-08		12:06:20		68		38.5		7-Jan-08		12:07:53		67.4		38.5		17-Feb-08		12:25:59		66.81		42

		7-Jan-08		14:07:10		65.01		43		7-Jan-08		14:06:20		68		41		7-Jan-08		14:07:53		67.4		41		17-Feb-08		14:25:59		67.4		43

		7-Jan-08		16:07:10		65.6		42.5		7-Jan-08		16:06:20		68		39.5		7-Jan-08		16:07:53		68		40.5		17-Feb-08		16:25:59		68.61		42

		7-Jan-08		18:07:10		65.6		41.5		7-Jan-08		18:06:20		68		39.5		7-Jan-08		18:07:53		68		40		17-Feb-08		18:25:59		69.2		41

		7-Jan-08		20:07:10		65.6		42		7-Jan-08		20:06:20		66.81		41.5		7-Jan-08		20:07:53		66.81		41		17-Feb-08		20:25:59		68		41.5

		7-Jan-08		22:07:10		65.01		43.5		7-Jan-08		22:06:20		66.81		42.5		7-Jan-08		22:07:53		65.6		43		17-Feb-08		22:25:59		67.4		42

		8-Jan-08		0:07:10		65.01		44.5		8-Jan-08		0:06:20		66.81		43		8-Jan-08		0:07:53		65.6		44		18-Feb-08		0:25:59		66.2		42

		8-Jan-08		2:07:10		64.4		44		8-Jan-08		2:06:20		66.81		42.5		8-Jan-08		2:07:53		65.01		44		18-Feb-08		2:25:59		65.6		42.5

		8-Jan-08		4:07:10		64.4		44.5		8-Jan-08		4:06:20		66.2		42.5		8-Jan-08		4:07:53		65.01		44		18-Feb-08		4:25:59		65.01		43.5

		8-Jan-08		6:07:10		64.4		44		8-Jan-08		6:06:20		66.2		41.5		8-Jan-08		6:07:53		66.81		41.5		18-Feb-08		6:25:59		65.01		44

		8-Jan-08		8:07:10		65.6		41		8-Jan-08		8:06:20		68		37.5		8-Jan-08		8:07:53		69.2		38.5		18-Feb-08		8:25:59		65.6		43

		8-Jan-08		10:07:10		66.2		39.5		8-Jan-08		10:06:20		69.8		35.5		8-Jan-08		10:07:53		71		36.5		18-Feb-08		10:25:59		66.2		42.5

		8-Jan-08		12:07:10		67.4		42		8-Jan-08		12:06:20		71.6		40.5		8-Jan-08		12:07:53		72.21		39		18-Feb-08		12:25:59		67.4		42

		8-Jan-08		14:07:10		68		38.5		8-Jan-08		14:06:20		71.6		35.5		8-Jan-08		14:07:53		70.41		40.5		18-Feb-08		14:25:59		68		42.5

		8-Jan-08		16:07:10		68.61		35.5		8-Jan-08		16:06:20		71		33.5		8-Jan-08		16:07:53		71		35.5		18-Feb-08		16:25:59		68		43.5

		8-Jan-08		18:07:10		68.61		34		8-Jan-08		18:06:20		69.2		34		8-Jan-08		18:07:53		70.41		36		18-Feb-08		18:25:59		68		43.5

		8-Jan-08		20:07:10		68		34.5		8-Jan-08		20:06:20		67.4		36		8-Jan-08		20:07:53		69.2		36		18-Feb-08		20:25:59		67.4		43.5

		8-Jan-08		22:07:10		67.4		35.5		8-Jan-08		22:06:20		66.81		36.5		8-Jan-08		22:07:53		67.4		38		18-Feb-08		22:25:59		66.2		43.5

		9-Jan-08		0:07:10		66.81		36.5		9-Jan-08		0:06:20		66.81		37		9-Jan-08		0:07:53		65.6		38.5		19-Feb-08		0:25:59		65.6		44.5

		9-Jan-08		2:07:10		65.6		37.5		9-Jan-08		2:06:20		66.81		37.5		9-Jan-08		2:07:53		64.4		39.5		19-Feb-08		2:25:59		65.6		45

		9-Jan-08		4:07:10		65.01		38		9-Jan-08		4:06:20		66.2		38		9-Jan-08		4:07:53		63.21		41		19-Feb-08		4:25:59		65.01		45.5

		9-Jan-08		6:07:10		65.01		39		9-Jan-08		6:06:20		66.2		38.5		9-Jan-08		6:07:53		67.4		38		19-Feb-08		6:25:59		66.2		45

		9-Jan-08		8:07:10		65.6		39		9-Jan-08		8:06:20		68		37.5		9-Jan-08		8:07:53		68.61		39		19-Feb-08		8:25:59		69.8		42.5

		9-Jan-08		10:07:10		66.81		41		9-Jan-08		10:06:20		71		37.5		9-Jan-08		10:07:53		70.41		39.5		19-Feb-08		10:25:59		72.21		40.5

		9-Jan-08		12:07:10		67.4		42.5		9-Jan-08		12:06:20		71		42		9-Jan-08		12:07:53		71		41.5		19-Feb-08		12:25:59		71.6		40.5

		9-Jan-08		14:07:10		68.61		44.5		9-Jan-08		14:06:20		72.8		43.5		9-Jan-08		14:07:53		71.6		42.5		19-Feb-08		14:25:59		71.6		40.5

		9-Jan-08		16:07:10		69.2		46		9-Jan-08		16:06:20		74.01		42.5		9-Jan-08		16:07:53		71		44		19-Feb-08		16:25:59		72.21		40.5

		9-Jan-08		18:07:10		69.8		46		9-Jan-08		18:06:20		71		46		9-Jan-08		18:07:53		71.6		38.5		19-Feb-08		18:25:59		71.6		41

		9-Jan-08		20:07:10		70.41		45		9-Jan-08		20:06:20		69.8		45		9-Jan-08		20:07:53		70.41		44.5		19-Feb-08		20:25:59		71.6		41

		9-Jan-08		22:07:10		69.2		42.5		9-Jan-08		22:06:20		68		44.5		9-Jan-08		22:07:53		68.61		43.5		19-Feb-08		22:25:59		69.2		41.5

		10-Jan-08		0:07:10		68		44		10-Jan-08		0:06:20		66.81		46.5		10-Jan-08		0:07:53		67.4		45		20-Feb-08		0:25:59		67.4		42

		10-Jan-08		2:07:10		67.4		45		10-Jan-08		2:06:20		66.81		47		10-Jan-08		2:07:53		66.2		46.5		20-Feb-08		2:25:59		66.81		42.5

		10-Jan-08		4:07:10		66.81		45.5		10-Jan-08		4:06:20		66.81		46		10-Jan-08		4:07:53		65.6		47		20-Feb-08		4:25:59		66.2		43.5

		10-Jan-08		6:07:10		66.2		46		10-Jan-08		6:06:20		67.4		45.5		10-Jan-08		6:07:53		66.81		45.5		20-Feb-08		6:25:59		66.81		43.5

		10-Jan-08		8:07:10		66.81		45		10-Jan-08		8:06:20		69.8		41.5		10-Jan-08		8:07:53		70.41		43		20-Feb-08		8:25:59		71.6		42

		10-Jan-08		10:07:10		68		44.5		10-Jan-08		10:06:20		70.41		41		10-Jan-08		10:07:53		72.21		41.5		20-Feb-08		10:25:59		72.8		41

		10-Jan-08		12:07:10		68.61		43.5		10-Jan-08		12:06:20		70.41		39		10-Jan-08		12:07:53		71.6		42		20-Feb-08		12:25:59		72.8		41.5

		10-Jan-08		14:07:10		69.2		43.5		10-Jan-08		14:06:20		70.41		45		10-Jan-08		14:07:53		71.6		44		20-Feb-08		14:25:59		72.21		43.5

		10-Jan-08		16:07:10		69.2		43		10-Jan-08		16:06:20		70.41		39.5		10-Jan-08		16:07:53		71		43		20-Feb-08		16:25:59		72.21		45.5

		10-Jan-08		18:07:10		69.2		43		10-Jan-08		18:06:20		68.61		44		10-Jan-08		18:07:53		70.41		43.5		20-Feb-08		18:25:59		71.6		45.5

		10-Jan-08		20:07:10		69.2		42.5		10-Jan-08		20:06:20		68		44.5		10-Jan-08		20:07:53		69.2		42.5		20-Feb-08		20:25:59		71.6		45.5

		10-Jan-08		22:07:10		68.61		43		10-Jan-08		22:06:20		67.4		45		10-Jan-08		22:07:53		68		44		20-Feb-08		22:25:59		70.41		45.5

		11-Jan-08		0:07:10		68		43.5		11-Jan-08		0:06:20		67.4		44.5		11-Jan-08		0:07:53		67.4		44.5		21-Feb-08		0:25:59		68.61		46

		11-Jan-08		2:07:10		67.4		44		11-Jan-08		2:06:20		67.4		45.5		11-Jan-08		2:07:53		66.81		45.5		21-Feb-08		2:25:59		68		46

		11-Jan-08		4:07:10		67.4		44		11-Jan-08		4:06:20		67.4		45		11-Jan-08		4:07:53		65.6		46.5		21-Feb-08		4:25:59		66.81		46.5

		11-Jan-08		6:07:10		66.81		44.5		11-Jan-08		6:06:20		67.4		45		11-Jan-08		6:07:53		68		45		21-Feb-08		6:25:59		66.81		47

		11-Jan-08		8:07:10		67.4		45		11-Jan-08		8:06:20		67.4		45		11-Jan-08		8:07:53		69.8		44		21-Feb-08		8:25:59		71		44.5

		11-Jan-08		10:07:10		68		46		11-Jan-08		10:06:20		72.21		42.5		11-Jan-08		10:07:53		71.6		43		21-Feb-08		10:25:59		72.21		44

		11-Jan-08		12:07:10		69.2		46.5		11-Jan-08		12:06:20		72.8		44		11-Jan-08		12:07:53		71.6		47		21-Feb-08		12:25:59		72.8		43.5

		11-Jan-08		14:07:10		70.41		47.5		11-Jan-08		14:06:20		72.8		46		11-Jan-08		14:07:53		71		41.5		21-Feb-08		14:25:59		73.4		42

		11-Jan-08		16:07:10		70.41		47		11-Jan-08		16:06:20		73.4		40		11-Jan-08		16:07:53		71		48.5		21-Feb-08		16:25:59		74.01		40.5

		11-Jan-08		18:07:10		70.41		47		11-Jan-08		18:06:20		71		46.5		11-Jan-08		18:07:53		70.41		44.5		21-Feb-08		18:25:59		73.4		41

		11-Jan-08		20:07:10		69.8		46		11-Jan-08		20:06:20		69.2		48		11-Jan-08		20:07:53		70.41		44.5		21-Feb-08		20:25:59		72.21		40.5

		11-Jan-08		22:07:10		68.61		47		11-Jan-08		22:06:20		68		49.5		11-Jan-08		22:07:53		69.2		47		21-Feb-08		22:25:59		71		41

		12-Jan-08		0:07:10		68		48		12-Jan-08		0:06:20		68		49.5		12-Jan-08		0:07:53		68		48		22-Feb-08		0:25:59		69.8		41

		12-Jan-08		2:07:10		67.4		49		12-Jan-08		2:06:20		68		50		12-Jan-08		2:07:53		67.4		49		22-Feb-08		2:25:59		68.61		42

		12-Jan-08		4:07:10		66.81		48.5		12-Jan-08		4:06:20		67.4		48.5		12-Jan-08		4:07:53		66.81		49		22-Feb-08		4:25:59		67.4		43

		12-Jan-08		6:07:10		66.81		47.5		12-Jan-08		6:06:20		67.4		46.5		12-Jan-08		6:07:53		67.4		47.5		22-Feb-08		6:25:59		67.4		43.5

		12-Jan-08		8:07:10		66.81		46		12-Jan-08		8:06:20		69.2		43		12-Jan-08		8:07:53		69.8		45		22-Feb-08		8:25:59		71.6		42

		12-Jan-08		10:07:10		68		45.5		12-Jan-08		10:06:20		72.8		38		12-Jan-08		10:07:53		71.6		43		22-Feb-08		10:25:59		72.8		41

		12-Jan-08		12:07:10		68		45.5		12-Jan-08		12:06:20		71		45		12-Jan-08		12:07:53		71		41		22-Feb-08		12:25:59		72.8		42.5

		12-Jan-08		14:07:10		68		44.5		12-Jan-08		14:06:20		70.41		42		12-Jan-08		14:07:53		69.8		44		22-Feb-08		14:25:59		72.21		42

		12-Jan-08		16:07:10		68		45		12-Jan-08		16:06:20		68.61		44		12-Jan-08		16:07:53		70.41		43.5		22-Feb-08		16:25:59		72.21		43.5

		12-Jan-08		18:07:10		67.4		45		12-Jan-08		18:06:20		68.61		44.5		12-Jan-08		18:07:53		69.8		43.5		22-Feb-08		18:25:59		72.21		44

		12-Jan-08		20:07:10		67.4		45.5		12-Jan-08		20:06:20		68		45.5		12-Jan-08		20:07:53		69.2		44		22-Feb-08		20:25:59		72.21		43.5

		12-Jan-08		22:07:10		66.81		45.5		12-Jan-08		22:06:20		66.81		46.5		12-Jan-08		22:07:53		69.2		44.5		22-Feb-08		22:25:59		70.41		44.5

		13-Jan-08		0:07:10		65.6		47		13-Jan-08		0:06:20		66.2		48		13-Jan-08		0:07:53		69.2		43.5		23-Feb-08		0:25:59		68.61		45

		13-Jan-08		2:07:10		65.01		47.5		13-Jan-08		2:06:20		66.2		47.5		13-Jan-08		2:07:53		69.2		43		23-Feb-08		2:25:59		68		45.5

		13-Jan-08		4:07:10		65.01		48		13-Jan-08		4:06:20		66.2		47		13-Jan-08		4:07:53		69.8		42.5		23-Feb-08		4:25:59		67.4		45.5

		13-Jan-08		6:07:10		64.4		49		13-Jan-08		6:06:20		66.2		48		13-Jan-08		6:07:53		69.8		43		23-Feb-08		6:25:59		67.4		45

		13-Jan-08		8:07:10		64.4		49		13-Jan-08		8:06:20		67.4		45.5		13-Jan-08		8:07:53		69.8		42.5		23-Feb-08		8:25:59		72.8		42.5

		13-Jan-08		10:07:10		64.4		49.5		13-Jan-08		10:06:20		68		45.5		13-Jan-08		10:07:53		69.8		42.5		23-Feb-08		10:25:59		72.8		42.5

		13-Jan-08		12:07:10		65.01		50		13-Jan-08		12:06:20		68		47		13-Jan-08		12:07:53		69.8		45		23-Feb-08		12:25:59		71.6		42.5

		13-Jan-08		14:07:10		65.6		49.5		13-Jan-08		14:06:20		68.61		46		13-Jan-08		14:07:53		69.8		44		23-Feb-08		14:25:59		71.6		43

		13-Jan-08		16:07:10		66.2		49.5		13-Jan-08		16:06:20		69.2		46		13-Jan-08		16:07:53		69.8		45.5		23-Feb-08		16:25:59		72.8		41

		13-Jan-08		18:07:10		66.81		49.5		13-Jan-08		18:06:20		69.2		45		13-Jan-08		18:07:53		69.8		46.5		23-Feb-08		18:25:59		72.8		38.5

		13-Jan-08		20:07:10		66.81		48.5		13-Jan-08		20:06:20		68		47.5		13-Jan-08		20:07:53		69.2		45.5		23-Feb-08		20:25:59		71.6		38

		13-Jan-08		22:07:10		66.2		47		13-Jan-08		22:06:20		66.2		46		13-Jan-08		22:07:53		69.2		43		23-Feb-08		22:25:59		69.2		38.5

		14-Jan-08		0:07:10		65.01		46.5		14-Jan-08		0:06:20		65.6		45.5		14-Jan-08		0:07:53		69.2		41		24-Feb-08		0:25:59		66.81		39.5

		14-Jan-08		2:07:10		64.4		48		14-Jan-08		2:06:20		65.6		47		14-Jan-08		2:07:53		69.8		41.5		24-Feb-08		2:25:59		65.6		40

		14-Jan-08		4:07:10		64.4		49.5		14-Jan-08		4:06:20		65.6		48		14-Jan-08		4:07:53		69.8		42		24-Feb-08		4:25:59		64.4		40

		14-Jan-08		6:07:10		64.4		50.5		14-Jan-08		6:06:20		66.2		49		14-Jan-08		6:07:53		69.8		42.5		24-Feb-08		6:25:59		64.4		40.5

		14-Jan-08		8:07:10		64.4		51.5		14-Jan-08		8:06:20		68		47		14-Jan-08		8:07:53		69.8		43		24-Feb-08		8:25:59		65.01		40.5

		14-Jan-08		10:07:10		64.4		50		14-Jan-08		10:06:20		68		45.5		14-Jan-08		10:07:53		69.8		42		24-Feb-08		10:25:59		65.01		41.5

		14-Jan-08		12:07:10		65.01		49		14-Jan-08		12:06:20		68		44.5		14-Jan-08		12:07:53		70.41		39.5		24-Feb-08		12:25:59		65.6		42.5

		14-Jan-08		14:07:10		65.01		49		14-Jan-08		14:06:20		68		45		14-Jan-08		14:07:53		69.8		38.5		24-Feb-08		14:25:59		66.2		43.5

		14-Jan-08		16:07:10		65.6		49.5		14-Jan-08		16:06:20		68.61		46.5		14-Jan-08		16:07:53		69.8		42.5		24-Feb-08		16:25:59		65.6		43.5

		14-Jan-08		18:07:10		66.2		49.5		14-Jan-08		18:06:20		68.61		47		14-Jan-08		18:07:53		69.8		45		24-Feb-08		18:25:59		65.01		44

		14-Jan-08		20:07:10		66.2		48.5		14-Jan-08		20:06:20		67.4		47		14-Jan-08		20:07:53		69.8		44		24-Feb-08		20:25:59		64.4		45

		14-Jan-08		22:07:10		65.6		47		14-Jan-08		22:06:20		66.2		46		14-Jan-08		22:07:53		69.8		41.5		24-Feb-08		22:25:59		64.4		46

		15-Jan-08		0:07:10		64.4		44		15-Jan-08		0:06:20		65.6		42		15-Jan-08		0:07:53		69.2		39		25-Feb-08		0:25:59		64.4		47.5

		15-Jan-08		2:07:10		63.8		45		15-Jan-08		2:06:20		65.6		43		15-Jan-08		2:07:53		69.8		38.5		25-Feb-08		2:25:59		64.4		48

		15-Jan-08		4:07:10		63.8		45		15-Jan-08		4:06:20		65.6		42.5		15-Jan-08		4:07:53		69.8		38		25-Feb-08		4:25:59		64.4		49

		15-Jan-08		6:07:10		63.21		46		15-Jan-08		6:06:20		65.6		44		15-Jan-08		6:07:53		69.8		38.5		25-Feb-08		6:25:59		64.4		49.5

		15-Jan-08		8:07:10		63.8		47		15-Jan-08		8:06:20		67.4		42.5		15-Jan-08		8:07:53		71		39.5		25-Feb-08		8:25:59		65.01		49.5

		15-Jan-08		10:07:10		65.01		47.5		15-Jan-08		10:06:20		70.41		41.5		15-Jan-08		10:07:53		71		37		25-Feb-08		10:25:59		66.2		49.5

		15-Jan-08		12:07:10		65.6		47.5		15-Jan-08		12:06:20		70.41		43		15-Jan-08		12:07:53		71		43.5		25-Feb-08		12:25:59		66.81		49.5

		15-Jan-08		14:07:10		66.2		48		15-Jan-08		14:06:20		70.41		46.5		15-Jan-08		14:07:53		71		43.5		25-Feb-08		14:25:59		67.4		50

		15-Jan-08		16:07:10		66.81		49.5		15-Jan-08		16:06:20		71		44		15-Jan-08		16:07:53		70.41		45		25-Feb-08		16:25:59		67.4		50

		15-Jan-08		18:07:10		66.81		48		15-Jan-08		18:06:20		69.2		44		15-Jan-08		18:07:53		70.41		43.5		25-Feb-08		18:25:59		67.4		49.5

		15-Jan-08		20:07:10		66.81		45.5		15-Jan-08		20:06:20		67.4		44		15-Jan-08		20:07:53		69.8		41.5		25-Feb-08		20:25:59		66.81		49

		15-Jan-08		22:07:10		65.6		43.5		15-Jan-08		22:06:20		65.6		42.5		15-Jan-08		22:07:53		68.61		41		25-Feb-08		22:25:59		66.2		49

		16-Jan-08		0:07:10		65.01		43		16-Jan-08		0:06:20		65.6		41		16-Jan-08		0:07:53		66.81		40		26-Feb-08		0:25:59		65.6		49.5

		16-Jan-08		2:07:10		64.4		42.5		16-Jan-08		2:06:20		65.01		41.5		16-Jan-08		2:07:53		65.6		41		26-Feb-08		2:25:59		65.01		50

		16-Jan-08		4:07:10		63.8		42.5		16-Jan-08		4:06:20		65.6		40		16-Jan-08		4:07:53		64.4		41		26-Feb-08		4:25:59		64.4		49.5

		16-Jan-08		6:07:10		63.21		42		16-Jan-08		6:06:20		65.01		40		16-Jan-08		6:07:53		67.4		38		26-Feb-08		6:25:59		66.2		48

		16-Jan-08		8:07:10		63.8		41		16-Jan-08		8:06:20		67.4		37		16-Jan-08		8:07:53		69.2		36.5		26-Feb-08		8:25:59		69.8		45

		16-Jan-08		10:07:10		65.01		41		16-Jan-08		10:06:20		70.41		36		16-Jan-08		10:07:53		71		36		26-Feb-08		10:25:59		72.21		44

		16-Jan-08		12:07:10		65.6		42.5		16-Jan-08		12:06:20		71		35		16-Jan-08		12:07:53		71.6		36		26-Feb-08		12:25:59		72.21		43.5

		16-Jan-08		14:07:10		66.81		44.5		16-Jan-08		14:06:20		71		39		16-Jan-08		14:07:53		70.41		43.5		26-Feb-08		14:25:59		72.8		43

		16-Jan-08		16:07:10		68		46		16-Jan-08		16:06:20		71.6		40.5		16-Jan-08		16:07:53		69.8		44.5		26-Feb-08		16:25:59		73.4		42

		16-Jan-08		18:07:10		68		44.5		16-Jan-08		18:06:20		69.8		42		16-Jan-08		18:07:53		69.8		43.5		26-Feb-08		18:25:59		73.4		42.5

		16-Jan-08		20:07:10		68		44		16-Jan-08		20:06:20		68.61		43.5		16-Jan-08		20:07:53		69.2		43		26-Feb-08		20:25:59		72.21		42.5

		16-Jan-08		22:07:10		67.4		42		16-Jan-08		22:06:20		66.81		43		16-Jan-08		22:07:53		68.61		40.5		26-Feb-08		22:25:59		70.41		43.5

		17-Jan-08		0:07:10		66.2		40.5		17-Jan-08		0:06:20		65.6		41		17-Jan-08		0:07:53		66.81		39.5		27-Feb-08		0:25:59		68		43.5

		17-Jan-08		2:07:10		65.01		40.5		17-Jan-08		2:06:20		65.6		39		17-Jan-08		2:07:53		65.6		39.5		27-Feb-08		2:25:59		66.81		43.5

		17-Jan-08		4:07:10		63.8		40		17-Jan-08		4:06:20		65.6		38.5		17-Jan-08		4:07:53		64.4		39.5		27-Feb-08		4:25:59		65.6		43.5

		17-Jan-08		6:07:10		63.8		39.5		17-Jan-08		6:06:20		65.6		37		17-Jan-08		6:07:53		66.2		37		27-Feb-08		6:25:59		66.81		43.5

		17-Jan-08		8:07:10		64.4		38.5		17-Jan-08		8:06:20		68		34.5		17-Jan-08		8:07:53		69.2		35.5		27-Feb-08		8:25:59		71.6		41

		17-Jan-08		10:07:10		65.01		35		17-Jan-08		10:06:20		70.41		29.5		17-Jan-08		10:07:53		71.6		31		27-Feb-08		10:25:59		72.21		41

		17-Jan-08		12:07:10		66.2		29		17-Jan-08		12:06:20		71		21.5		17-Jan-08		12:07:53		69.8		23.5		27-Feb-08		12:25:59		72.21		42.5

		17-Jan-08		14:07:10		67.4		27		17-Jan-08		14:06:20		71		22.5		17-Jan-08		14:07:53		71		23.5		27-Feb-08		14:25:59		74.01		40

		17-Jan-08		16:07:10		68		25		17-Jan-08		16:06:20		70.41		21.5		17-Jan-08		16:07:53		70.41		24.5		27-Feb-08		16:25:59		74.01		40

		17-Jan-08		18:07:10		68.61		24		17-Jan-08		18:06:20		69.8		19		17-Jan-08		18:07:53		69.8		22.5		27-Feb-08		18:25:59		74.01		41.5

		17-Jan-08		20:07:10		68.61		22		17-Jan-08		20:06:20		69.8		18		17-Jan-08		20:07:53		70.41		23		27-Feb-08		20:25:59		72.8		42.5

		17-Jan-08		22:07:10		68.61		20.5		17-Jan-08		22:06:20		69.2		17.5		17-Jan-08		22:07:53		70.41		24		27-Feb-08		22:25:59		71.6		43

		18-Jan-08		0:07:10		68		20		18-Jan-08		0:06:20		68		18		18-Jan-08		0:07:53		69.2		23		28-Feb-08		0:25:59		69.8		43

		18-Jan-08		2:07:10		67.4		21.5		18-Jan-08		2:06:20		66.2		22		18-Jan-08		2:07:53		68		24		28-Feb-08		2:25:59		68.61		44

		18-Jan-08		4:07:10		66.2		21		18-Jan-08		4:06:20		66.2		20		18-Jan-08		4:07:53		66.81		23.5		28-Feb-08		4:25:59		67.4		44

		18-Jan-08		6:07:10		65.6		24.5		18-Jan-08		6:06:20		65.6		26		18-Jan-08		6:07:53		65.6		26		28-Feb-08		6:25:59		67.4		43.5

		18-Jan-08		8:07:10		65.6		26.5		18-Jan-08		8:06:20		67.4		26		18-Jan-08		8:07:53		69.8		26		28-Feb-08		8:25:59		71		41

		18-Jan-08		10:07:10		66.81		29		18-Jan-08		10:06:20		70.41		27.5		18-Jan-08		10:07:53		71.6		27		28-Feb-08		10:25:59		72.21		41

		18-Jan-08		12:07:10		67.4		28.5		18-Jan-08		12:06:20		71		26.5		18-Jan-08		12:07:53		71		28		28-Feb-08		12:25:59		72.8		42.5

		18-Jan-08		14:07:10		68		29		18-Jan-08		14:06:20		71		28		18-Jan-08		14:07:53		71		29		28-Feb-08		14:25:59		74.01		42.5

		18-Jan-08		16:07:10		68.61		29		18-Jan-08		16:06:20		70.41		29.5		18-Jan-08		16:07:53		71		31.5		28-Feb-08		16:25:59		75.2		43.5

		18-Jan-08		18:07:10		69.2		30		18-Jan-08		18:06:20		69.8		29.5		18-Jan-08		18:07:53		70.41		31.5		28-Feb-08		18:25:59		74.6		43.5

		18-Jan-08		20:07:10		69.2		32		18-Jan-08		20:06:20		68.61		34		18-Jan-08		20:07:53		71		32.5		28-Feb-08		20:25:59		72.21		44

		18-Jan-08		22:07:10		68		32		18-Jan-08		22:06:20		66.81		34.5		18-Jan-08		22:07:53		69.8		32		28-Feb-08		22:25:59		71.6		44.5

		19-Jan-08		0:07:10		66.81		32.5		19-Jan-08		0:06:20		66.2		34		19-Jan-08		0:07:53		68		32.5		29-Feb-08		0:25:59		69.2		44

		19-Jan-08		2:07:10		66.2		32.5		19-Jan-08		2:06:20		65.6		33		19-Jan-08		2:07:53		66.2		32.5		29-Feb-08		2:25:59		68		43.5

		19-Jan-08		4:07:10		65.01		32.5		19-Jan-08		4:06:20		65.6		32.5		19-Jan-08		4:07:53		65.01		32.5		29-Feb-08		4:25:59		66.81		43

		19-Jan-08		6:07:10		64.4		32.5		19-Jan-08		6:06:20		65.6		32		19-Jan-08		6:07:53		67.4		30		29-Feb-08		6:25:59		67.4		42.5

		19-Jan-08		8:07:10		65.01		32		19-Jan-08		8:06:20		68		29.5		19-Jan-08		8:07:53		69.2		31		29-Feb-08		8:25:59		70.41		40

		19-Jan-08		10:07:10		65.6		33		19-Jan-08		10:06:20		68.61		31		19-Jan-08		10:07:53		71.6		30		29-Feb-08		10:25:59		72.21		40.5

		19-Jan-08		12:07:10		65.6		35.5		19-Jan-08		12:06:20		70.41		33.5		19-Jan-08		12:07:53		71		30.5		29-Feb-08		12:25:59		73.4		42

		19-Jan-08		14:07:10		66.2		35.5		19-Jan-08		14:06:20		70.41		33.5		19-Jan-08		14:07:53		71		34.5		29-Feb-08		14:25:59		74.6		41.5

		19-Jan-08		16:07:10		67.4		35		19-Jan-08		16:06:20		71		32		19-Jan-08		16:07:53		71		34.5		29-Feb-08		16:25:59		74.6		41.5

		19-Jan-08		18:07:10		68		35.5		19-Jan-08		18:06:20		69.8		34		19-Jan-08		18:07:53		70.41		35		29-Feb-08		18:25:59		74.01		43.5

		19-Jan-08		20:07:10		68		34		19-Jan-08		20:06:20		68		34.5		19-Jan-08		20:07:53		69.8		34		29-Feb-08		20:25:59		72.21		42.5

		19-Jan-08		22:07:10		67.4		34.5		19-Jan-08		22:06:20		66.2		36.5		19-Jan-08		22:07:53		68.61		35		29-Feb-08		22:25:59		71		43.5

		20-Jan-08		0:07:10		66.2		34		20-Jan-08		0:06:20		65.6		35		20-Jan-08		0:07:53		67.4		34		1-Mar-08		0:25:59		69.8		43

		20-Jan-08		2:07:10		65.6		34		20-Jan-08		2:06:20		65.6		34		20-Jan-08		2:07:53		65.6		34		1-Mar-08		2:25:59		68.61		43.5

		20-Jan-08		4:07:10		64.4		33		20-Jan-08		4:06:20		65.6		33		20-Jan-08		4:07:53		64.4		33.5		1-Mar-08		4:25:59		68		44

		20-Jan-08		6:07:10		63.8		32.5		20-Jan-08		6:06:20		65.6		31		20-Jan-08		6:07:53		63.21		33.5		1-Mar-08		6:25:59		68		44.5

		20-Jan-08		8:07:10		63.8		31.5		20-Jan-08		8:06:20		67.4		28		20-Jan-08		8:07:53		67.4		29		1-Mar-08		8:25:59		71.6		42

		20-Jan-08		10:07:10		63.8		32		20-Jan-08		10:06:20		68		30		20-Jan-08		10:07:53		66.81		29.5		1-Mar-08		10:25:59		72.8		41.5

		20-Jan-08		12:07:10		64.4		36.5		20-Jan-08		12:06:20		68.61		35		20-Jan-08		12:07:53		67.4		33		1-Mar-08		12:25:59		72.21		43

		20-Jan-08		14:07:10		65.01		37		20-Jan-08		14:06:20		68.61		35		20-Jan-08		14:07:53		67.4		35.5		1-Mar-08		14:25:59		72.8		44

		20-Jan-08		16:07:10		66.2		36.5		20-Jan-08		16:06:20		69.8		33.5		20-Jan-08		16:07:53		68.61		35.5		1-Mar-08		16:25:59		74.01		45

		20-Jan-08		18:07:10		66.81		36.5		20-Jan-08		18:06:20		69.2		34.5		20-Jan-08		18:07:53		69.8		35.5		1-Mar-08		18:25:59		73.4		43.5

		20-Jan-08		20:07:10		66.81		34.5		20-Jan-08		20:06:20		68		33.5		20-Jan-08		20:07:53		69.2		34		1-Mar-08		20:25:59		72.21		43

		20-Jan-08		22:07:10		66.2		35		20-Jan-08		22:06:20		66.2		35.5		20-Jan-08		22:07:53		67.4		34.5		1-Mar-08		22:25:59		71		43

		21-Jan-08		0:07:10		65.01		35		21-Jan-08		0:06:20		65.6		35		21-Jan-08		0:07:53		65.6		34.5		2-Mar-08		0:25:59		69.2		43

		21-Jan-08		2:07:10		64.4		38.5		21-Jan-08		2:06:20		65.6		39		21-Jan-08		2:07:53		65.01		37		2-Mar-08		2:25:59		68.61		44

		21-Jan-08		4:07:10		64.4		38.5		21-Jan-08		4:06:20		65.6		38		21-Jan-08		4:07:53		64.4		38		2-Mar-08		4:25:59		67.4		44.5

		21-Jan-08		6:07:10		63.8		37		21-Jan-08		6:06:20		65.6		36		21-Jan-08		6:07:53		63.8		37.5		2-Mar-08		6:25:59		67.4		44.5

		21-Jan-08		8:07:10		63.8		38		21-Jan-08		8:06:20		67.4		35		21-Jan-08		8:07:53		66.81		34.5		2-Mar-08		8:25:59		67.4		44

		21-Jan-08		10:07:10		63.8		38.5		21-Jan-08		10:06:20		68		35		21-Jan-08		10:07:53		66.81		35.5		2-Mar-08		10:25:59		68		43.5

		21-Jan-08		12:07:10		64.4		40		21-Jan-08		12:06:20		68		36.5		21-Jan-08		12:07:53		67.4		36		2-Mar-08		12:25:59		69.2		42

		21-Jan-08		14:07:10		64.4		35		21-Jan-08		14:06:20		68		31		21-Jan-08		14:07:53		67.4		33.5		2-Mar-08		14:25:59		70.41		40.5

		21-Jan-08		16:07:10		65.01		34.5		21-Jan-08		16:06:20		68		32		21-Jan-08		16:07:53		67.4		34		2-Mar-08		16:25:59		69.8		39

		21-Jan-08		18:07:10		65.6		33.5		21-Jan-08		18:06:20		68		31		21-Jan-08		18:07:53		67.4		33.5		2-Mar-08		18:25:59		69.8		38

		21-Jan-08		20:07:10		65.6		34.5		21-Jan-08		20:06:20		66.2		34		21-Jan-08		20:07:53		66.81		34		2-Mar-08		20:25:59		68.61		39

		21-Jan-08		22:07:10		65.01		34.5		21-Jan-08		22:06:20		65.6		34		21-Jan-08		22:07:53		65.01		34.5		2-Mar-08		22:25:59		67.4		39.5

		22-Jan-08		0:07:10		64.4		34.5		22-Jan-08		0:06:20		65.6		33.5		22-Jan-08		0:07:53		63.8		35		3-Mar-08		0:25:59		66.81		40

		22-Jan-08		2:07:10		63.8		34		22-Jan-08		2:06:20		65.01		32		22-Jan-08		2:07:53		62.6		34		3-Mar-08		2:25:59		65.6		40

		22-Jan-08		4:07:10		63.21		32.5		22-Jan-08		4:06:20		65.01		30.5		22-Jan-08		4:07:53		61.41		33.5		3-Mar-08		4:25:59		65.01		39.5

		22-Jan-08		6:07:10		62.6		31.5		22-Jan-08		6:06:20		65.01		30		22-Jan-08		6:07:53		66.81		29.5		3-Mar-08		6:25:59		64.4		39.5

		22-Jan-08		8:07:10		63.21		32		22-Jan-08		8:06:20		67.4		28.5		22-Jan-08		8:07:53		68		30		3-Mar-08		8:25:59		65.01		38.5

		22-Jan-08		10:07:10		64.4		33.5		22-Jan-08		10:06:20		69.2		30		22-Jan-08		10:07:53		70.41		30.5		3-Mar-08		10:25:59		66.2		38

		22-Jan-08		12:07:10		65.01		36		22-Jan-08		12:06:20		70.41		32.5		22-Jan-08		12:07:53		71.6		31		3-Mar-08		12:25:59		66.81		38

		22-Jan-08		14:07:10		66.2		37.5		22-Jan-08		14:06:20		71		35.5		22-Jan-08		14:07:53		71		36		3-Mar-08		14:25:59		67.4		35.5

		22-Jan-08		16:07:10		66.81		39		22-Jan-08		16:06:20		71		34.5		22-Jan-08		16:07:53		70.41		37		3-Mar-08		16:25:59		68.61		33.5

		22-Jan-08		18:07:10		67.4		37		22-Jan-08		18:06:20		68.61		36		22-Jan-08		18:07:53		69.8		36		3-Mar-08		18:25:59		68.61		31.5

		22-Jan-08		20:07:10		67.4		36.5		22-Jan-08		20:06:20		68		36.5		22-Jan-08		20:07:53		69.8		35		3-Mar-08		20:25:59		68.61		31

		22-Jan-08		22:07:10		66.81		37		22-Jan-08		22:06:20		67.4		36.5		22-Jan-08		22:07:53		67.4		36		3-Mar-08		22:25:59		68		33

		23-Jan-08		0:07:10		65.6		37.5		23-Jan-08		0:06:20		67.4		36.5		23-Jan-08		0:07:53		65.6		37.5		4-Mar-08		0:25:59		66.81		35

		23-Jan-08		2:07:10		65.01		37		23-Jan-08		2:06:20		67.4		35.5		23-Jan-08		2:07:53		65.01		38		4-Mar-08		2:25:59		66.2		37

		23-Jan-08		4:07:10		64.4		37.5		23-Jan-08		4:06:20		66.81		35.5		23-Jan-08		4:07:53		63.8		38.5		4-Mar-08		4:25:59		65.6		37.5

		23-Jan-08		6:07:10		64.4		37		23-Jan-08		6:06:20		66.81		35		23-Jan-08		6:07:53		67.4		35.5		4-Mar-08		6:25:59		66.2		37.5

		23-Jan-08		8:07:10		65.01		36		23-Jan-08		8:06:20		68		33		23-Jan-08		8:07:53		69.2		34		4-Mar-08		8:25:59		69.2		35.5

		23-Jan-08		10:07:10		65.6		36.5		23-Jan-08		10:06:20		69.2		34		23-Jan-08		10:07:53		71		35		4-Mar-08		10:25:59		71.6		36.5

		23-Jan-08		12:07:10		66.2		36		23-Jan-08		12:06:20		69.8		33		23-Jan-08		12:07:53		71		34		4-Mar-08		12:25:59		72.21		36.5

		23-Jan-08		14:07:10		66.81		34.5		23-Jan-08		14:06:20		70.41		32		23-Jan-08		14:07:53		70.41		35		4-Mar-08		14:25:59		73.4		33.5

		23-Jan-08		16:07:10		66.81		33.5		23-Jan-08		16:06:20		69.8		31.5		23-Jan-08		16:07:53		70.41		32		4-Mar-08		16:25:59		74.01		33.5

		23-Jan-08		18:07:10		66.81		33		23-Jan-08		18:06:20		69.2		31		23-Jan-08		18:07:53		69.2		32		4-Mar-08		18:25:59		74.01		33

		23-Jan-08		20:07:10		66.81		32.5		23-Jan-08		20:06:20		68		31		23-Jan-08		20:07:53		68		32.5		4-Mar-08		20:25:59		72.21		32

		23-Jan-08		22:07:10		66.2		32.5		23-Jan-08		22:06:20		67.4		32		23-Jan-08		22:07:53		68		32.5		4-Mar-08		22:25:59		71		33.5

		24-Jan-08		0:07:10		65.6		33.5		24-Jan-08		0:06:20		66.81		32.5		24-Jan-08		0:07:53		66.2		33		5-Mar-08		0:25:59		69.2		34.5

		24-Jan-08		2:07:10		65.01		34		24-Jan-08		2:06:20		67.4		32.5		24-Jan-08		2:07:53		64.4		34.5		5-Mar-08		2:25:59		68		35.5

		24-Jan-08		4:07:10		64.4		35.5		24-Jan-08		4:06:20		67.4		34		24-Jan-08		4:07:53		63.8		36		5-Mar-08		4:25:59		66.81		36

		24-Jan-08		6:07:10		64.4		37		24-Jan-08		6:06:20		66.81		35		24-Jan-08		6:07:53		68		34		5-Mar-08		6:25:59		66.81		36.5

		24-Jan-08		8:07:10		65.01		37		24-Jan-08		8:06:20		68		35		24-Jan-08		8:07:53		69.2		35.5		5-Mar-08		8:25:59		69.8		34

		24-Jan-08		10:07:10		65.6		38		24-Jan-08		10:06:20		71		33.5		24-Jan-08		10:07:53		71		35		5-Mar-08		10:25:59		72.21		36

		24-Jan-08		12:07:10		66.81		39		24-Jan-08		12:06:20		71		36		24-Jan-08		12:07:53		71		37		5-Mar-08		12:25:59		72.8		36.5

		24-Jan-08		14:07:10		68		38		24-Jan-08		14:06:20		71		37		24-Jan-08		14:07:53		71		38.5		5-Mar-08		14:25:59		74.01		36.5

		24-Jan-08		16:07:10		68		36		24-Jan-08		16:06:20		71		34		24-Jan-08		16:07:53		71.6		35		5-Mar-08		16:25:59		74.6		35.5

		24-Jan-08		18:07:10		68.61		34.5		24-Jan-08		18:06:20		68.61		33.5		24-Jan-08		18:07:53		71		34		5-Mar-08		18:25:59		74.6		36.5

		24-Jan-08		20:07:10		68		35.5		24-Jan-08		20:06:20		68		36.5		24-Jan-08		20:07:53		69.8		35		5-Mar-08		20:25:59		72.8		37

		24-Jan-08		22:07:10		67.4		36.5		24-Jan-08		22:06:20		67.4		37		24-Jan-08		22:07:53		68		36		5-Mar-08		22:25:59		71		37

		25-Jan-08		0:07:10		66.2		36.5		25-Jan-08		0:06:20		67.4		36		25-Jan-08		0:07:53		66.2		37		6-Mar-08		0:25:59		69.2		37

		25-Jan-08		2:07:10		65.6		37.5		25-Jan-08		2:06:20		66.81		37		25-Jan-08		2:07:53		65.01		38		6-Mar-08		2:25:59		68		37.5

		25-Jan-08		4:07:10		65.01		39		25-Jan-08		4:06:20		67.4		37.5		25-Jan-08		4:07:53		64.4		39.5		6-Mar-08		4:25:59		66.81		38

		25-Jan-08		6:07:10		64.4		39.5		25-Jan-08		6:06:20		67.4		38		25-Jan-08		6:07:53		66.81		38		6-Mar-08		6:25:59		66.81		37.5

		25-Jan-08		8:07:10		65.01		39		25-Jan-08		8:06:20		68		36.5		25-Jan-08		8:07:53		69.2		36		6-Mar-08		8:25:59		70.41		35.5

		25-Jan-08		10:07:10		65.6		40.5		25-Jan-08		10:06:20		69.8		37		25-Jan-08		10:07:53		71.6		36		6-Mar-08		10:25:59		71.6		36.5

		25-Jan-08		12:07:10		66.81		39.5		25-Jan-08		12:06:20		69.8		37.5		25-Jan-08		12:07:53		72.21		36		6-Mar-08		12:25:59		72.8		35.5

		25-Jan-08		14:07:10		67.4		38		25-Jan-08		14:06:20		69.8		37.5		25-Jan-08		14:07:53		71		37.5		6-Mar-08		14:25:59		74.01		32.5

		25-Jan-08		16:07:10		68.61		37.5		25-Jan-08		16:06:20		70.41		37		25-Jan-08		16:07:53		70.41		38		6-Mar-08		16:25:59		74.6		31

		25-Jan-08		18:07:10		68.61		36		25-Jan-08		18:06:20		68		36.5		25-Jan-08		18:07:53		69.8		36		6-Mar-08		18:25:59		68.61		44.5

		25-Jan-08		20:07:10		68.61		35		25-Jan-08		20:06:20		67.4		37		25-Jan-08		20:07:53		68.61		36		6-Mar-08		20:25:59		68.61		44

		25-Jan-08		22:07:10		68		35.5		25-Jan-08		22:06:20		66.81		37		25-Jan-08		22:07:53		67.4		37.5		6-Mar-08		22:25:59		68.61		42.5

		26-Jan-08		0:07:10		67.4		35.5		26-Jan-08		0:06:20		66.81		36		26-Jan-08		0:07:53		66.81		37.5		7-Mar-08		0:25:59		68.61		44

		26-Jan-08		2:07:10		66.81		36		26-Jan-08		2:06:20		66.81		36.5		26-Jan-08		2:07:53		65.6		37.5		7-Mar-08		2:25:59		68		43

		26-Jan-08		4:07:10		66.2		35		26-Jan-08		4:06:20		66.81		35		26-Jan-08		4:07:53		65.6		37.5		7-Mar-08		4:25:59		69.2		44

		26-Jan-08		6:07:10		65.6		37.5		26-Jan-08		6:06:20		66.81		38		26-Jan-08		6:07:53		68.61		36.5		7-Mar-08		6:25:59		68.61		43.5

		26-Jan-08		8:07:10		66.2		39.5		26-Jan-08		8:06:20		67.4		40		26-Jan-08		8:07:53		69.2		38.5		7-Mar-08		8:25:59		68.61		44.5

		26-Jan-08		10:07:10		67.4		42		26-Jan-08		10:06:20		69.8		42		26-Jan-08		10:07:53		71.6		40.5		7-Mar-08		10:25:59		68.61		44.5

		26-Jan-08		12:07:10		68.61		41		26-Jan-08		12:06:20		69.2		42.5		26-Jan-08		12:07:53		71		43		7-Mar-08		12:25:59		68.61		45

		26-Jan-08		14:07:10		69.8		42		26-Jan-08		14:06:20		71		44		26-Jan-08		14:07:53		71		38.5		7-Mar-08		14:25:59		68.61		45

		26-Jan-08		16:07:10		70.41		43.5		26-Jan-08		16:06:20		70.41		46.5		26-Jan-08		16:07:53		70.41		44.5		7-Mar-08		16:25:59		68.61		44

		26-Jan-08		18:07:10		69.8		42.5		26-Jan-08		18:06:20		68.61		45.5		26-Jan-08		18:07:53		69.2		44		7-Mar-08		18:25:59		68.61		44.5

		26-Jan-08		20:07:10		69.2		44.5		26-Jan-08		20:06:20		68		48		26-Jan-08		20:07:53		68.61		45.5		7-Mar-08		20:25:59		68.61		46.5

		26-Jan-08		22:07:10		68.61		46.5		26-Jan-08		22:06:20		68		49.5		26-Jan-08		22:07:53		68		47.5		7-Mar-08		22:25:59		68.61		45.5

		27-Jan-08		0:07:10		68.61		47.5		27-Jan-08		0:06:20		67.4		51		27-Jan-08		0:07:53		67.4		48		8-Mar-08		0:25:59		68.61		44.5

		27-Jan-08		2:07:10		68		48.5		27-Jan-08		2:06:20		67.4		51.5		27-Jan-08		2:07:53		67.4		48.5		8-Mar-08		2:25:59		68		45

		27-Jan-08		4:07:10		68		49		27-Jan-08		4:06:20		67.4		51		27-Jan-08		4:07:53		67.4		49		8-Mar-08		4:25:59		68		44

		27-Jan-08		6:07:10		67.4		48		27-Jan-08		6:06:20		67.4		49		27-Jan-08		6:07:53		66.81		49		8-Mar-08		6:25:59		68		45

		27-Jan-08		8:07:10		67.4		44.5		27-Jan-08		8:06:20		68		43.5		27-Jan-08		8:07:53		68		45.5		8-Mar-08		8:25:59		68.61		45

		27-Jan-08		10:07:10		67.4		40.5		27-Jan-08		10:06:20		67.4		39.5		27-Jan-08		10:07:53		68		43		8-Mar-08		10:25:59		68.61		45

		27-Jan-08		12:07:10		67.4		39.5		27-Jan-08		12:06:20		67.4		39		27-Jan-08		12:07:53		67.4		42		8-Mar-08		12:25:59		68.61		45

		27-Jan-08		14:07:10		67.4		39		27-Jan-08		14:06:20		68		38.5		27-Jan-08		14:07:53		68		42		8-Mar-08		14:25:59		68.61		45

		27-Jan-08		16:07:10		67.4		39.5		27-Jan-08		16:06:20		68		39		27-Jan-08		16:07:53		68		41		8-Mar-08		16:25:59		68.61		45

		27-Jan-08		18:07:10		68		40		27-Jan-08		18:06:20		68.61		40.5		27-Jan-08		18:07:53		68.61		41.5		8-Mar-08		18:25:59		68.61		44.5

		27-Jan-08		20:07:10		68		39.5		27-Jan-08		20:06:20		67.4		40.5		27-Jan-08		20:07:53		68		42		8-Mar-08		20:25:59		68.61		45.5

		27-Jan-08		22:07:10		67.4		41		27-Jan-08		22:06:20		67.4		42		27-Jan-08		22:07:53		67.4		42.5		8-Mar-08		22:25:59		68.61		45

		28-Jan-08		0:07:10		67.4		43.5		28-Jan-08		0:06:20		67.4		46.5		28-Jan-08		0:07:53		67.4		44		9-Mar-08		0:25:59		68		45

		28-Jan-08		2:07:10		66.81		47.5		28-Jan-08		2:06:20		67.4		49		28-Jan-08		2:07:53		66.81		46.5		9-Mar-08		2:25:59		68		45

		28-Jan-08		4:07:10		66.81		46.5		28-Jan-08		4:06:20		67.4		47		28-Jan-08		4:07:53		66.81		46.5		9-Mar-08		4:25:59		68.61		45

		28-Jan-08		6:07:10		66.81		47.5		28-Jan-08		6:06:20		67.4		48.5		28-Jan-08		6:07:53		66.81		47.5		9-Mar-08		6:25:59		68.61		44.5

		28-Jan-08		8:07:10		66.81		48.5		28-Jan-08		8:06:20		68		48.5		28-Jan-08		8:07:53		67.4		47		9-Mar-08		8:25:59		68.61		45.5

		28-Jan-08		10:07:10		66.81		49.5		28-Jan-08		10:06:20		68		49		28-Jan-08		10:07:53		67.4		47.5		9-Mar-08		10:25:59		68.61		45

		28-Jan-08		12:07:10		66.81		48		28-Jan-08		12:06:20		68		47.5		28-Jan-08		12:07:53		68		47.5		9-Mar-08		12:25:59		68.61		45.5

		28-Jan-08		14:07:10		66.81		45.5		28-Jan-08		14:06:20		68		45		28-Jan-08		14:07:53		68		46		9-Mar-08		14:25:59		68.61		45

		28-Jan-08		16:07:10		67.4		47.5		28-Jan-08		16:06:20		68		49		28-Jan-08		16:07:53		68		47.5		9-Mar-08		16:25:59		68.61		45

		28-Jan-08		18:07:10		68		48.5		28-Jan-08		18:06:20		68		49		28-Jan-08		18:07:53		67.4		48.5		9-Mar-08		18:25:59		68.61		45

		28-Jan-08		20:07:10		68		49		28-Jan-08		20:06:20		67.4		50.5		28-Jan-08		20:07:53		67.4		49		9-Mar-08		20:25:59		68.61		46

		28-Jan-08		22:07:10		67.4		40.5		28-Jan-08		22:06:20		66.81		37.5		28-Jan-08		22:07:53		66.2		41.5		9-Mar-08		22:25:59		68.61		45

		29-Jan-08		0:07:10		66.2		36.5		29-Jan-08		0:06:20		66.2		35		29-Jan-08		0:07:53		63.8		38		10-Mar-08		0:25:59		68		45

		29-Jan-08		2:07:10		65.6		36.5		29-Jan-08		2:06:20		66.81		35.5		29-Jan-08		2:07:53		63.21		39		10-Mar-08		2:25:59		68.61		45

		29-Jan-08		4:07:10		65.6		36.5		29-Jan-08		4:06:20		66.81		35		29-Jan-08		4:07:53		62.6		39.5		10-Mar-08		4:25:59		68.61		45.5

		29-Jan-08		6:07:10		65.6		36		29-Jan-08		6:06:20		66.81		35		29-Jan-08		6:07:53		66.81		36.5		10-Mar-08		6:25:59		68.61		45.5

		29-Jan-08		8:07:10		65.6		36		29-Jan-08		8:06:20		67.4		34.5		29-Jan-08		8:07:53		69.2		35		10-Mar-08		8:25:59		68		45.5

		29-Jan-08		10:07:10		66.2		37.5		29-Jan-08		10:06:20		69.8		34.5		29-Jan-08		10:07:53		70.41		36.5		10-Mar-08		10:25:59		68		45.5

		29-Jan-08		12:07:10		67.4		37.5		29-Jan-08		12:06:20		70.41		35.5		29-Jan-08		12:07:53		71		37		10-Mar-08		12:25:59		68.61		45.5

		29-Jan-08		14:07:10		68.61		35		29-Jan-08		14:06:20		71		31		29-Jan-08		14:07:53		70.41		38		10-Mar-08		14:25:59		68.61		45

		29-Jan-08		16:07:10		69.2		34.5		29-Jan-08		16:06:20		69.8		34		29-Jan-08		16:07:53		70.41		35.5		10-Mar-08		16:25:59		68.61		45.5

		29-Jan-08		18:07:10		69.8		33.5		29-Jan-08		18:06:20		69.2		34		29-Jan-08		18:07:53		69.8		35		10-Mar-08		18:25:59		68.61		45

		29-Jan-08		20:07:10		69.2		32.5		29-Jan-08		20:06:20		67.4		33.5		29-Jan-08		20:07:53		68		35		10-Mar-08		20:25:59		68.61		45

		29-Jan-08		22:07:10		68.61		32.5		29-Jan-08		22:06:20		67.4		33.5		29-Jan-08		22:07:53		66.2		35.5		10-Mar-08		22:25:59		68		45

		30-Jan-08		0:07:10		68		31.5		30-Jan-08		0:06:20		66.81		32.5		30-Jan-08		0:07:53		65.01		35.5		11-Mar-08		0:25:59		68.61		45

		30-Jan-08		2:07:10		67.4		30.5		30-Jan-08		2:06:20		66.81		30.5		30-Jan-08		2:07:53		63.21		34.5		11-Mar-08		2:25:59		68.61		45

		30-Jan-08		4:07:10		66.81		30		30-Jan-08		4:06:20		66.81		30		30-Jan-08		4:07:53		62		34		11-Mar-08		4:25:59		68.61		46

		30-Jan-08		6:07:10		66.81		31		30-Jan-08		6:06:20		66.81		31		30-Jan-08		6:07:53		67.4		31.5		11-Mar-08		6:25:59		68.61		45.5

		30-Jan-08		8:07:10		66.81		31.5		30-Jan-08		8:06:20		67.4		31.5		30-Jan-08		8:07:53		69.2		33		11-Mar-08		8:25:59		68.61		44.5

		30-Jan-08		10:07:10		67.4		33.5		30-Jan-08		10:06:20		69.8		32.5		30-Jan-08		10:07:53		70.41		35		11-Mar-08		10:25:59		68		45

		30-Jan-08		12:07:10		68.61		36		30-Jan-08		12:06:20		71		36		30-Jan-08		12:07:53		71		37.5		11-Mar-08		12:25:59		68.61		46

		30-Jan-08		14:07:10		69.8		39		30-Jan-08		14:06:20		71.6		40.5		30-Jan-08		14:07:53		71		42		11-Mar-08		14:25:59		68		49.5

		30-Jan-08		16:07:10		71.6		40.5		30-Jan-08		16:06:20		71.6		43		30-Jan-08		16:07:53		71		42		11-Mar-08		16:25:59		68.61		46

		30-Jan-08		18:07:10		71		36		30-Jan-08		18:06:20		68.61		36.5		30-Jan-08		18:07:53		69.8		38		11-Mar-08		18:25:59		68		45

		30-Jan-08		20:07:10		70.41		33		30-Jan-08		20:06:20		68		34		30-Jan-08		20:07:53		68.61		36.5		11-Mar-08		20:25:59		68.61		45

		30-Jan-08		22:07:10		69.8		31.5		30-Jan-08		22:06:20		68		32.5		30-Jan-08		22:07:53		67.4		36		11-Mar-08		22:25:59		68.61		45.5

		31-Jan-08		0:07:10		69.2		32		31-Jan-08		0:06:20		68		33.5		31-Jan-08		0:07:53		65.6		36.5		12-Mar-08		0:25:59		68.61		45

		31-Jan-08		2:07:10		68.61		33		31-Jan-08		2:06:20		68		34		31-Jan-08		2:07:53		65.01		37		12-Mar-08		2:25:59		68		45

		31-Jan-08		4:07:10		68.61		33.5		31-Jan-08		4:06:20		68		34.5		31-Jan-08		4:07:53		64.4		38		12-Mar-08		4:25:59		68		46

		31-Jan-08		6:07:10		68		33.5		31-Jan-08		6:06:20		68		34.5		31-Jan-08		6:07:53		66.81		36		12-Mar-08		6:25:59		68		45

		31-Jan-08		8:07:10		69.8		32.5		31-Jan-08		8:06:20		68		34		31-Jan-08		8:07:53		68.61		35.5		12-Mar-08		8:25:59		68.61		46

		31-Jan-08		10:07:10		71.6		33		31-Jan-08		10:06:20		71		34.5		31-Jan-08		10:07:53		71.6		36.5		12-Mar-08		10:25:59		68.61		45.5

		31-Jan-08		12:07:10		71.6		33.5		31-Jan-08		12:06:20		71		33.5		31-Jan-08		12:07:53		70.41		38		12-Mar-08		12:25:59		68		46

		31-Jan-08		14:07:10		71.6		33.5		31-Jan-08		14:06:20		71		36		31-Jan-08		14:07:53		71.6		36		12-Mar-08		14:25:59		68		46.5

		31-Jan-08		16:07:10		71.6		33.5		31-Jan-08		16:06:20		71		35.5		31-Jan-08		16:07:53		69.8		37		12-Mar-08		16:25:59		68.61		48.5

		31-Jan-08		18:07:10		71		34		31-Jan-08		18:06:20		68.61		37		31-Jan-08		18:07:53		71		36.5		12-Mar-08		18:25:59		68.61		47.5

		31-Jan-08		20:07:10		69.2		36		31-Jan-08		20:06:20		68.61		38		31-Jan-08		20:07:53		70.41		37.5		12-Mar-08		20:25:59		68.61		45.5

		31-Jan-08		22:07:10		67.4		37.5		31-Jan-08		22:06:20		68		38		31-Jan-08		22:07:53		69.2		38.5		12-Mar-08		22:25:59		68.61		45.5

		1-Feb-08		0:07:10		66.2		39		1-Feb-08		0:06:20		68		38		1-Feb-08		0:07:53		67.4		39		13-Mar-08		0:25:59		68		46

		1-Feb-08		2:07:10		65.01		40.5		1-Feb-08		2:06:20		68		38		1-Feb-08		2:07:53		66.2		40		13-Mar-08		2:25:59		68		45

		1-Feb-08		4:07:10		64.4		42		1-Feb-08		4:06:20		68		39		1-Feb-08		4:07:53		65.6		41		13-Mar-08		4:25:59		68.61		45

		1-Feb-08		6:07:10		63.8		43		1-Feb-08		6:06:20		68		39		1-Feb-08		6:07:53		66.81		40.5		13-Mar-08		6:25:59		68.61		45

		1-Feb-08		8:07:10		66.2		42		1-Feb-08		8:06:20		68		40.5		1-Feb-08		8:07:53		69.8		40		13-Mar-08		8:25:59		68.61		45.5

		1-Feb-08		10:07:10		68.61		42		1-Feb-08		10:06:20		71		41.5		1-Feb-08		10:07:53		71.6		42		13-Mar-08		10:25:59		68		45.5

		1-Feb-08		12:07:10		69.2		43		1-Feb-08		12:06:20		71		43		1-Feb-08		12:07:53		71		46		13-Mar-08		12:25:59		68.61		45

		1-Feb-08		14:07:10		69.8		45		1-Feb-08		14:06:20		71		44		1-Feb-08		14:07:53		71		40		13-Mar-08		14:25:59		68.61		47

		1-Feb-08		16:07:10		70.41		46.5		1-Feb-08		16:06:20		71		45		1-Feb-08		16:07:53		70.41		48		13-Mar-08		16:25:59		68.61		47

		1-Feb-08		18:07:10		69.2		48.5		1-Feb-08		18:06:20		69.2		50		1-Feb-08		18:07:53		70.41		48		13-Mar-08		18:25:59		68		45.5

		1-Feb-08		20:07:10		68		44.5		1-Feb-08		20:06:20		68.61		43.5		1-Feb-08		20:07:53		70.41		43.5		13-Mar-08		20:25:59		68.61		45

		1-Feb-08		22:07:10		66.81		41.5		1-Feb-08		22:06:20		68		39.5		1-Feb-08		22:07:53		69.2		41		13-Mar-08		22:25:59		68.61		45.5

		2-Feb-08		0:07:10		65.6		40		2-Feb-08		0:06:20		68		37.5		2-Feb-08		0:07:53		66.81		40		14-Mar-08		0:25:59		68.61		47.5

		2-Feb-08		2:07:10		64.4		38		2-Feb-08		2:06:20		68		34		2-Feb-08		2:07:53		64.4		39		14-Mar-08		2:25:59		68		46

		2-Feb-08		4:07:10		63.21		37.5		2-Feb-08		4:06:20		68		33		2-Feb-08		4:07:53		62.6		38		14-Mar-08		4:25:59		68		47

		2-Feb-08		6:07:10		62.6		36.5		2-Feb-08		6:06:20		68		32		2-Feb-08		6:07:53		67.4		33.5		14-Mar-08		6:25:59		68		46.5

		2-Feb-08		8:07:10		63.8		35		2-Feb-08		8:06:20		67.4		31.5		2-Feb-08		8:07:53		68		33.5		14-Mar-08		8:25:59		68.61		47.5

		2-Feb-08		10:07:10		66.2		36		2-Feb-08		10:06:20		71		33		2-Feb-08		10:07:53		70.41		35.5		14-Mar-08		10:25:59		68		48

		2-Feb-08		12:07:10		68.61		38		2-Feb-08		12:06:20		72.8		36		2-Feb-08		12:07:53		71		39.5		14-Mar-08		12:25:59		68.61		45.5

		2-Feb-08		14:07:10		69.2		38		2-Feb-08		14:06:20		71.6		36.5		2-Feb-08		14:07:53		69.8		39.5		14-Mar-08		14:25:59		68.61		45

		2-Feb-08		16:07:10		68.61		38		2-Feb-08		16:06:20		71		36.5		2-Feb-08		16:07:53		69.8		39		14-Mar-08		16:25:59		68.61		45

		2-Feb-08		18:07:10		68		37.5		2-Feb-08		18:06:20		71		35.5		2-Feb-08		18:07:53		71		39		14-Mar-08		18:25:59		68.61		45

		2-Feb-08		20:07:10		67.4		37		2-Feb-08		20:06:20		68.61		35.5		2-Feb-08		20:07:53		69.2		40		14-Mar-08		20:25:59		68.61		45

		2-Feb-08		22:07:10		66.81		36.5		2-Feb-08		22:06:20		68		34		2-Feb-08		22:07:53		67.4		44		14-Mar-08		22:25:59		68.61		45

		3-Feb-08		0:07:10		66.81		35.5		3-Feb-08		0:06:20		68		33		3-Feb-08		0:07:53		66.81		41		15-Mar-08		0:25:59		68.61		45.5

		3-Feb-08		2:07:10		66.2		35		3-Feb-08		2:06:20		68		33		3-Feb-08		2:07:53		65.6		42		15-Mar-08		2:25:59		68.61		46

		3-Feb-08		4:07:10		66.2		34.5		3-Feb-08		4:06:20		68		33		3-Feb-08		4:07:53		65.01		43		15-Mar-08		4:25:59		68.61		45.5

		3-Feb-08		6:07:10		66.2		34.5		3-Feb-08		6:06:20		68		33.5		3-Feb-08		6:07:53		64.4		44		15-Mar-08		6:25:59		68.61		46

		3-Feb-08		8:07:10		66.2		35.5		3-Feb-08		8:06:20		69.8		33		3-Feb-08		8:07:53		67.4		41.5		15-Mar-08		8:25:59		68.61		45.5

		3-Feb-08		10:07:10		66.2		36.5		3-Feb-08		10:06:20		66.81		36.5		3-Feb-08		10:07:53		67.4		42		15-Mar-08		10:25:59		68.61		45

		3-Feb-08		12:07:10		66.81		40		3-Feb-08		12:06:20		65.6		44.5		3-Feb-08		12:07:53		68		47.5		15-Mar-08		12:25:59		68.61		45

		3-Feb-08		14:07:10		66.2		43.5		3-Feb-08		14:06:20		66.2		47.5		3-Feb-08		14:07:53		67.4		49		15-Mar-08		14:25:59		68.61		44.5

		3-Feb-08		16:07:10		66.2		46		3-Feb-08		16:06:20		66.2		49		3-Feb-08		16:07:53		68		49		15-Mar-08		16:25:59		68		44.5

		3-Feb-08		18:07:10		66.2		47.5		3-Feb-08		18:06:20		66.2		50		3-Feb-08		18:07:53		68.61		51		15-Mar-08		18:25:59		68		44.5

		3-Feb-08		20:07:10		66.2		49.5		3-Feb-08		20:06:20		66.81		52		3-Feb-08		20:07:53		67.4		51.5		15-Mar-08		20:25:59		68.61		45

		3-Feb-08		22:07:10		66.2		51.5		3-Feb-08		22:06:20		66.81		53.5		3-Feb-08		22:07:53		68		54		15-Mar-08		22:25:59		68		45

		4-Feb-08		0:07:10		66.2		51.5		4-Feb-08		0:06:20		67.4		52.5		4-Feb-08		0:07:53		68		54		16-Mar-08		0:25:59		68		44.5

		4-Feb-08		2:07:10		66.2		49		4-Feb-08		2:06:20		66.81		48		4-Feb-08		2:07:53		67.4		50.5		16-Mar-08		2:25:59		68.61		44.5

		4-Feb-08		4:07:10		66.2		45		4-Feb-08		4:06:20		65.6		45		4-Feb-08		4:07:53		66.81		47.5		16-Mar-08		4:25:59		68		46

		4-Feb-08		6:07:10		65.6		43		4-Feb-08		6:06:20		65.6		44		4-Feb-08		6:07:53		66.81		47.5		16-Mar-08		6:25:59		68		39

		4-Feb-08		8:07:10		65.6		40.5		4-Feb-08		8:06:20		65.01		41		4-Feb-08		8:07:53		68		45.5		16-Mar-08		8:25:59		68.61		45.5

		4-Feb-08		10:07:10		65.6		41		4-Feb-08		10:06:20		65.6		42.5		4-Feb-08		10:07:53		68.61		45		16-Mar-08		10:25:59		68.61		45.5

		4-Feb-08		12:07:10		65.6		41.5		4-Feb-08		12:06:20		66.2		41		4-Feb-08		12:07:53		68		46		16-Mar-08		12:25:59		68.61		45.5

		4-Feb-08		14:07:10		65.6		40.5		4-Feb-08		14:06:20		66.81		38		4-Feb-08		14:07:53		68		46		16-Mar-08		14:25:59		68.61		35

		4-Feb-08		16:07:10		66.2		39		4-Feb-08		16:06:20		66.81		38		4-Feb-08		16:07:53		68		45		16-Mar-08		16:25:59		68.61		45

		4-Feb-08		18:07:10		66.2		38.5		4-Feb-08		18:06:20		66.81		36.5		4-Feb-08		18:07:53		68		45		16-Mar-08		18:25:59		68.61		45

		4-Feb-08		20:07:10		66.2		37.5		4-Feb-08		20:06:20		65.6		38		4-Feb-08		20:07:53		68		45.5		16-Mar-08		20:25:59		68.61		45

		4-Feb-08		22:07:10		65.6		37.5		4-Feb-08		22:06:20		65.6		38.5		4-Feb-08		22:07:53		67.4		46		16-Mar-08		22:25:59		68		46

		5-Feb-08		0:07:10		65.6		37		5-Feb-08		0:06:20		65.01		38		5-Feb-08		0:07:53		66.81		46.5		17-Mar-08		0:25:59		68.61		44

		5-Feb-08		2:07:10		65.6		36		5-Feb-08		2:06:20		65.6		35.5		5-Feb-08		2:07:53		66.81		46		17-Mar-08		2:25:59		68.61		44

		5-Feb-08		4:07:10		65.6		34.5		5-Feb-08		4:06:20		65.01		35		5-Feb-08		4:07:53		66.2		46		17-Mar-08		4:25:59		68.61		45

		5-Feb-08		6:07:10		65.6		33.5		5-Feb-08		6:06:20		65.01		33		5-Feb-08		6:07:53		66.81		46		17-Mar-08		6:25:59		68		43.5

		5-Feb-08		8:07:10		65.6		33		5-Feb-08		8:06:20		65.01		33.5		5-Feb-08		8:07:53		70.41		39.5		17-Mar-08		8:25:59		68.61		44

		5-Feb-08		10:07:10		65.6		34.5		5-Feb-08		10:06:20		68.61		32.5		5-Feb-08		10:07:53		71		41.5		17-Mar-08		10:25:59		68.61		43

		5-Feb-08		12:07:10		66.2		34.5		5-Feb-08		12:06:20		71		30.5		5-Feb-08		12:07:53		70.41		42.5		17-Mar-08		12:25:59		68		35.5

		5-Feb-08		14:07:10		66.81		32		5-Feb-08		14:06:20		70.41		29.5		5-Feb-08		14:07:53		71		39.5		17-Mar-08		14:25:59		68.61		27.5

		5-Feb-08		16:07:10		67.4		31		5-Feb-08		16:06:20		70.41		28.5		5-Feb-08		16:07:53		71		34.5		17-Mar-08		16:25:59		68.61		26

		5-Feb-08		18:07:10		68		34		5-Feb-08		18:06:20		69.8		29		5-Feb-08		18:07:53		70.41		37.5		17-Mar-08		18:25:59		68		34

		5-Feb-08		20:07:10		67.4		41.5		5-Feb-08		20:06:20		68		32		5-Feb-08		20:07:53		71		36		17-Mar-08		20:25:59		68		44

		5-Feb-08		22:07:10		66.81		35.5		5-Feb-08		22:06:20		67.4		33		5-Feb-08		22:07:53		69.8		39		17-Mar-08		22:25:59		68.61		44

		6-Feb-08		0:07:10		66.81		34.5		6-Feb-08		0:06:20		67.4		33.5		6-Feb-08		0:07:53		68		36.5		18-Mar-08		0:25:59		68.61		37.5

		6-Feb-08		2:07:10		66.81		34		6-Feb-08		2:06:20		67.4		33		6-Feb-08		2:07:53		66.81		36.5		18-Mar-08		2:25:59		68.61		36.5

		6-Feb-08		4:07:10		66.2		34		6-Feb-08		4:06:20		67.4		32.5		6-Feb-08		4:07:53		66.2		37		18-Mar-08		4:25:59		68		44.5

		6-Feb-08		6:07:10		66.2		33		6-Feb-08		6:06:20		68		31.5		6-Feb-08		6:07:53		67.4		36		18-Mar-08		6:25:59		68		42

		6-Feb-08		8:07:10		66.2		32		6-Feb-08		8:06:20		68		30.5		6-Feb-08		8:07:53		68		35		18-Mar-08		8:25:59		68.61		43.5

		6-Feb-08		10:07:10		66.81		34		6-Feb-08		10:06:20		69.8		31.5		6-Feb-08		10:07:53		70.41		36.5		18-Mar-08		10:25:59		68		39.5

		6-Feb-08		12:07:10		67.4		34.5		6-Feb-08		12:06:20		71		31.5		6-Feb-08		12:07:53		69.8		39.5		18-Mar-08		12:25:59		68.61		43.5

		6-Feb-08		14:07:10		67.4		34.5		6-Feb-08		14:06:20		69.2		34.5		6-Feb-08		14:07:53		71		36		18-Mar-08		14:25:59		68		40

		6-Feb-08		16:07:10		68.61		33		6-Feb-08		16:06:20		71		31		6-Feb-08		16:07:53		71		35		18-Mar-08		16:25:59		68.61		46

		6-Feb-08		18:07:10		68		37		6-Feb-08		18:06:20		69.8		33		6-Feb-08		18:07:53		71		38		18-Mar-08		18:25:59		68.61		44.5

		6-Feb-08		20:07:10		66.81		41		6-Feb-08		20:06:20		68		37.5		6-Feb-08		20:07:53		70.41		39		18-Mar-08		20:25:59		68.61		44.5

		6-Feb-08		22:07:10		66.2		44		6-Feb-08		22:06:20		67.4		38		6-Feb-08		22:07:53		69.8		39		18-Mar-08		22:25:59		68.61		44.5

		7-Feb-08		0:07:10		66.2		45		7-Feb-08		0:06:20		68		36		7-Feb-08		0:07:53		68.61		39.5		19-Mar-08		0:25:59		68		41

		7-Feb-08		2:07:10		65.6		46		7-Feb-08		2:06:20		67.4		35.5		7-Feb-08		2:07:53		67.4		40		19-Mar-08		2:25:59		68		45

		7-Feb-08		4:07:10		65.6		46		7-Feb-08		4:06:20		68		34		7-Feb-08		4:07:53		66.81		40		19-Mar-08		4:25:59		68		45

		7-Feb-08		6:07:10		65.6		46.5		7-Feb-08		6:06:20		68		33		7-Feb-08		6:07:53		66.81		39.5		19-Mar-08		6:25:59		68.61		44.5

		7-Feb-08		8:07:10		65.6		47		7-Feb-08		8:06:20		67.4		33		7-Feb-08		8:07:53		69.8		38		19-Mar-08		8:25:59		68.61		44.5

		7-Feb-08		10:07:10		65.6		46.5		7-Feb-08		10:06:20		72.21		33.5		7-Feb-08		10:07:53		71.6		37.5		19-Mar-08		10:25:59		68.61		46.5

		7-Feb-08		12:07:10		66.81		46		7-Feb-08		12:06:20		74.01		36.5		7-Feb-08		12:07:53		69.8		44.5		19-Mar-08		12:25:59		68.61		47.5

		7-Feb-08		14:07:10		67.4		46		7-Feb-08		14:06:20		71.6		34		7-Feb-08		14:07:53		71		47		19-Mar-08		14:25:59		68.61		45

		7-Feb-08		16:07:10		67.4		46		7-Feb-08		16:06:20		69.8		37		7-Feb-08		16:07:53		70.41		43.5		19-Mar-08		16:25:59		68.61		44.5

		7-Feb-08		18:07:10		67.4		46		7-Feb-08		18:06:20		69.2		34		7-Feb-08		18:07:53		70.41		41		19-Mar-08		18:25:59		68.61		47.5

		7-Feb-08		20:07:10		66.2		46.5		7-Feb-08		20:06:20		69.2		34		7-Feb-08		20:07:53		69.8		39		19-Mar-08		20:25:59		68		48

		7-Feb-08		22:07:10		66.2		47		7-Feb-08		22:06:20		66.81		36		7-Feb-08		22:07:53		69.8		38		19-Mar-08		22:25:59		68.61		45

		8-Feb-08		0:07:10		65.6		48		8-Feb-08		0:06:20		65.6		37.5		8-Feb-08		0:07:53		68.61		38.5		20-Mar-08		0:25:59		68.61		45

		8-Feb-08		2:07:10		65.01		48.5		8-Feb-08		2:06:20		65.6		37.5		8-Feb-08		2:07:53		67.4		39		20-Mar-08		2:25:59		68		40

		8-Feb-08		4:07:10		65.01		49		8-Feb-08		4:06:20		65.6		36.5		8-Feb-08		4:07:53		66.81		39.5		20-Mar-08		4:25:59		68		39

		8-Feb-08		6:07:10		65.01		49		8-Feb-08		6:06:20		65.6		36		8-Feb-08		6:07:53		66.81		39		20-Mar-08		6:25:59		68.61		38.5

		8-Feb-08		8:07:10		65.01		48.5		8-Feb-08		8:06:20		68		33.5		8-Feb-08		8:07:53		69.8		37		20-Mar-08		8:25:59		68		44.5

		8-Feb-08		10:07:10		65.01		49		8-Feb-08		10:06:20		70.41		35		8-Feb-08		10:07:53		71.6		38		20-Mar-08		10:25:59		68.61		45

		8-Feb-08		12:07:10		66.2		48		8-Feb-08		12:06:20		70.41		35.5		8-Feb-08		12:07:53		70.41		39		20-Mar-08		12:25:59		68.61		45.5

		8-Feb-08		14:07:10		66.81		48.5		8-Feb-08		14:06:20		71		38.5		8-Feb-08		14:07:53		71.6		46.5		20-Mar-08		14:25:59		68.61		46

		8-Feb-08		16:07:10		68.61		49.5		8-Feb-08		16:06:20		71		39		8-Feb-08		16:07:53		69.8		49		20-Mar-08		16:25:59		68		47

		8-Feb-08		18:07:10		68.61		44.5		8-Feb-08		18:06:20		69.8		41		8-Feb-08		18:07:53		71		47		20-Mar-08		18:25:59		68.61		45

		8-Feb-08		20:07:10		68.61		42.5		8-Feb-08		20:06:20		69.8		40.5		8-Feb-08		20:07:53		69.8		44.5		20-Mar-08		20:25:59		68.61		45

		8-Feb-08		22:07:10		68		45		8-Feb-08		22:06:20		68		44		8-Feb-08		22:07:53		70.41		42.5		20-Mar-08		22:25:59		68.61		44.5

		9-Feb-08		0:07:10		66.81		44		9-Feb-08		0:06:20		66.2		44		9-Feb-08		0:07:53		69.8		41		21-Mar-08		0:25:59		68.61		45

		9-Feb-08		2:07:10		66.2		44		9-Feb-08		2:06:20		66.2		40.5		9-Feb-08		2:07:53		68.61		40		21-Mar-08		2:25:59		68		45.5

		9-Feb-08		4:07:10		66.2		42		9-Feb-08		4:06:20		66.2		37		9-Feb-08		4:07:53		67.4		38.5		21-Mar-08		4:25:59		68		36.5

		9-Feb-08		6:07:10		65.6		40.5		9-Feb-08		6:06:20		66.2		36		9-Feb-08		6:07:53		67.4		37.5		21-Mar-08		6:25:59		68		45.5

		9-Feb-08		8:07:10		65.6		39.5		9-Feb-08		8:06:20		68		32		9-Feb-08		8:07:53		69.2		36		21-Mar-08		8:25:59		68		36

		9-Feb-08		10:07:10		66.2		40		9-Feb-08		10:06:20		71		35		9-Feb-08		10:07:53		71.6		35.5		21-Mar-08		10:25:59		67.4		46.5

		9-Feb-08		12:07:10		67.4		46.5		9-Feb-08		12:06:20		69.2		33.5		9-Feb-08		12:07:53		71		38.5		21-Mar-08		12:25:59		68.61		42

		9-Feb-08		14:07:10		69.8		47.5		9-Feb-08		14:06:20		68.61		33		9-Feb-08		14:07:53		71		34.5		21-Mar-08		14:25:59		68.61		32.5

		9-Feb-08		16:07:10		72.8		42		9-Feb-08		16:06:20		68.61		28.5		9-Feb-08		16:07:53		71		38.5		21-Mar-08		16:25:59		68		32.5

		9-Feb-08		18:07:10		71		48		9-Feb-08		18:06:20		68		29		9-Feb-08		18:07:53		70.41		35.5		21-Mar-08		18:25:59		68		42.5

		9-Feb-08		20:07:10		67.4		48.5		9-Feb-08		20:06:20		68.61		38.5		9-Feb-08		20:07:53		69.8		39.5		21-Mar-08		20:25:59		68.61		37

		9-Feb-08		22:07:10		65.6		51		9-Feb-08		22:06:20		67.4		38.5		9-Feb-08		22:07:53		69.8		38.5		21-Mar-08		22:25:59		68.61		36.5

		10-Feb-08		0:07:10		65.01		49.5		10-Feb-08		0:06:20		66.2		39		10-Feb-08		0:07:53		69.2		37.5		22-Mar-08		0:25:59		68		34.5

		10-Feb-08		2:07:10		65.01		49		10-Feb-08		2:06:20		65.6		38		10-Feb-08		2:07:53		68		37.5		22-Mar-08		2:25:59		68		42.5

		10-Feb-08		4:07:10		65.01		50		10-Feb-08		4:06:20		65.6		36.5		10-Feb-08		4:07:53		66.81		37.5		22-Mar-08		4:25:59		68		38

		10-Feb-08		6:07:10		65.01		51		10-Feb-08		6:06:20		65.6		35.5		10-Feb-08		6:07:53		66.2		38		22-Mar-08		6:25:59		68		35

		10-Feb-08		8:07:10		65.01		50		10-Feb-08		8:06:20		66.2		34		10-Feb-08		8:07:53		66.81		37		22-Mar-08		8:25:59		68		43.5

		10-Feb-08		10:07:10		65.01		49.5		10-Feb-08		10:06:20		67.4		36		10-Feb-08		10:07:53		68		37		22-Mar-08		10:25:59		68		41

		10-Feb-08		12:07:10		66.2		51		10-Feb-08		12:06:20		67.4		40.5		10-Feb-08		12:07:53		69.8		38.5		22-Mar-08		12:25:59		68.61		43.5

		10-Feb-08		14:07:10		68.61		49.5		10-Feb-08		14:06:20		68		41.5		10-Feb-08		14:07:53		70.41		41		22-Mar-08		14:25:59		68		37

		10-Feb-08		16:07:10		69.8		49		10-Feb-08		16:06:20		68		44		10-Feb-08		16:07:53		70.41		45		22-Mar-08		16:25:59		68.61		45

		10-Feb-08		18:07:10		69.8		49.5		10-Feb-08		18:06:20		68		39.5		10-Feb-08		18:07:53		70.41		42		22-Mar-08		18:25:59		68		44.5

		10-Feb-08		20:07:10		67.4		47.5		10-Feb-08		20:06:20		68.61		39.5		10-Feb-08		20:07:53		69.8		46.5		22-Mar-08		20:25:59		68		38.5

		10-Feb-08		22:07:10		66.2		49.5		10-Feb-08		22:06:20		68		39.5		10-Feb-08		22:07:53		70.41		42		22-Mar-08		22:25:59		68		38.5

		11-Feb-08		0:07:10		65.6		49.5		11-Feb-08		0:06:20		66.2		42		11-Feb-08		0:07:53		69.8		41.5		23-Mar-08		0:25:59		68		39

		11-Feb-08		2:07:10		65.01		50		11-Feb-08		2:06:20		66.2		42		11-Feb-08		2:07:53		68.61		42		23-Mar-08		2:25:59		68.61		36.5

		11-Feb-08		4:07:10		65.01		50		11-Feb-08		4:06:20		65.6		40		11-Feb-08		4:07:53		68		41.5		23-Mar-08		4:25:59		68		35.5

		11-Feb-08		6:07:10		65.01		50.5		11-Feb-08		6:06:20		65.6		38		11-Feb-08		6:07:53		67.4		42.5		23-Mar-08		6:25:59		68.61		43.5

		11-Feb-08		8:07:10		65.01		50		11-Feb-08		8:06:20		66.2		36.5		11-Feb-08		8:07:53		68		41.5		23-Mar-08		8:25:59		68		36

		11-Feb-08		10:07:10		65.01		51		11-Feb-08		10:06:20		66.81		39		11-Feb-08		10:07:53		68		42.5		23-Mar-08		10:25:59		68.61		44

		11-Feb-08		12:07:10		66.2		51.5		11-Feb-08		12:06:20		68		41.5		11-Feb-08		12:07:53		69.8		41.5		23-Mar-08		12:25:59		68		40

		11-Feb-08		14:07:10		68		51		11-Feb-08		14:06:20		67.4		43.5		11-Feb-08		14:07:53		69.8		44		23-Mar-08		14:25:59		68.61		44.5

		11-Feb-08		16:07:10		70.41		51		11-Feb-08		16:06:20		68		42		11-Feb-08		16:07:53		70.41		46.5		23-Mar-08		16:25:59		68.61		33

		11-Feb-08		18:07:10		69.8		50.5		11-Feb-08		18:06:20		68		48.5		11-Feb-08		18:07:53		70.41		46		23-Mar-08		18:25:59		68.61		44.5

		11-Feb-08		20:07:10		66.2		52		11-Feb-08		20:06:20		68.61		45.5		11-Feb-08		20:07:53		70.41		46		23-Mar-08		20:25:59		68.61		43.5

		11-Feb-08		22:07:10		65.6		52		11-Feb-08		22:06:20		67.4		44.5		11-Feb-08		22:07:53		70.41		43.5		23-Mar-08		22:25:59		68		45

		12-Feb-08		0:07:10		65.6		51.5		12-Feb-08		0:06:20		66.2		44.5		12-Feb-08		0:07:53		69.2		41.5		24-Mar-08		0:25:59		68		38.5

		12-Feb-08		2:07:10		65.01		50		12-Feb-08		2:06:20		66.2		42		12-Feb-08		2:07:53		68.61		41		24-Mar-08		2:25:59		68.61		39.5

		12-Feb-08		4:07:10		65.01		52		12-Feb-08		4:06:20		65.6		41.5		12-Feb-08		4:07:53		68		41		24-Mar-08		4:25:59		68.61		36

		12-Feb-08		6:07:10		65.01		50		12-Feb-08		6:06:20		65.6		40.5		12-Feb-08		6:07:53		67.4		41		24-Mar-08		6:25:59		68		35.5

		12-Feb-08		8:07:10		65.01		51		12-Feb-08		8:06:20		66.81		37.5		12-Feb-08		8:07:53		69.8		38		24-Mar-08		8:25:59		68.61		33.5

		12-Feb-08		10:07:10		65.6		49.5		12-Feb-08		10:06:20		71		39		12-Feb-08		10:07:53		71		41.5		24-Mar-08		10:25:59		68		37.5

		12-Feb-08		12:07:10		67.4		49.5		12-Feb-08		12:06:20		72.21		42.5		12-Feb-08		12:07:53		70.41		39.5		24-Mar-08		12:25:59		68.61		37.5

		12-Feb-08		14:07:10		70.41		50		12-Feb-08		14:06:20		72.8		41.5		12-Feb-08		14:07:53		71		44		24-Mar-08		14:25:59		68.61		38.5

		12-Feb-08		16:07:10		72.8		49.5		12-Feb-08		16:06:20		71.6		38.5		12-Feb-08		16:07:53		70.41		47.5		24-Mar-08		16:25:59		68		45

		12-Feb-08		18:07:10		71.6		49.5		12-Feb-08		18:06:20		70.41		48.5		12-Feb-08		18:07:53		70.41		50.5		24-Mar-08		18:25:59		68		42.5

		12-Feb-08		20:07:10		67.4		51		12-Feb-08		20:06:20		69.8		43.5		12-Feb-08		20:07:53		69.8		49		24-Mar-08		20:25:59		68		44.5

		12-Feb-08		22:07:10		66.2		52		12-Feb-08		22:06:20		69.2		43.5		12-Feb-08		22:07:53		70.41		45.5		24-Mar-08		22:25:59		68.61		40

		13-Feb-08		0:07:10		66.2		48.5		13-Feb-08		0:06:20		68.61		42.5		13-Feb-08		0:07:53		69.8		42.5		25-Mar-08		0:25:59		68.61		44

		13-Feb-08		2:07:10		65.6		49		13-Feb-08		2:06:20		68.61		40.5		13-Feb-08		2:07:53		69.2		41.5		25-Mar-08		2:25:59		68		38

		13-Feb-08		4:07:10		65.6		48.5		13-Feb-08		4:06:20		68.61		38		13-Feb-08		4:07:53		68.61		40.5		25-Mar-08		4:25:59		68.61		44.5

		13-Feb-08		6:07:10		65.6		50.5		13-Feb-08		6:06:20		68.61		36.5		13-Feb-08		6:07:53		67.4		41		25-Mar-08		6:25:59		68		37.5

		13-Feb-08		8:07:10		65.6		50		13-Feb-08		8:06:20		69.2		36.5		13-Feb-08		8:07:53		69.8		40		25-Mar-08		8:25:59		68		38

		13-Feb-08		10:07:10		66.2		50.5		13-Feb-08		10:06:20		70.41		37.5		13-Feb-08		10:07:53		71.6		42		25-Mar-08		10:25:59		67.4		42.5

		13-Feb-08		12:07:10		67.4		50.5		13-Feb-08		12:06:20		71		43		13-Feb-08		12:07:53		71		47		25-Mar-08		12:25:59		68		44.5

		13-Feb-08		14:07:10		73.4		46		13-Feb-08		14:06:20		71.6		43.5		13-Feb-08		14:07:53		71		52.5		25-Mar-08		14:25:59		68		46

		13-Feb-08		16:07:10		73.4		48.5		13-Feb-08		16:06:20		71.6		40		13-Feb-08		16:07:53		71		50.5		25-Mar-08		16:25:59		68		45.5

		13-Feb-08		18:07:10		71		48		13-Feb-08		18:06:20		70.41		45		13-Feb-08		18:07:53		70.41		47		25-Mar-08		18:25:59		68		44

		13-Feb-08		20:07:10		66.2		53		13-Feb-08		20:06:20		69.8		44		13-Feb-08		20:07:53		70.41		42.5		25-Mar-08		20:25:59		68		42.5

		13-Feb-08		22:07:10		65.6		53		13-Feb-08		22:06:20		69.2		43.5		13-Feb-08		22:07:53		70.41		44		25-Mar-08		22:25:59		68.61		41.5

		14-Feb-08		0:07:10		65.6		50.5		14-Feb-08		0:06:20		68.61		41		14-Feb-08		0:07:53		70.41		42		26-Mar-08		0:25:59		68.61		40.5

		14-Feb-08		2:07:10		65.01		51		14-Feb-08		2:06:20		68.61		39		14-Feb-08		2:07:53		69.2		40		26-Mar-08		2:25:59		68.61		40

		14-Feb-08		4:07:10		65.01		49		14-Feb-08		4:06:20		68.61		39		14-Feb-08		4:07:53		68.61		40.5		26-Mar-08		4:25:59		68.61		39

		14-Feb-08		6:07:10		65.01		51		14-Feb-08		6:06:20		68.61		38.5		14-Feb-08		6:07:53		68		40.5		26-Mar-08		6:25:59		68.61		40

		14-Feb-08		8:07:10		65.6		49.5		14-Feb-08		8:06:20		68.61		37		14-Feb-08		8:07:53		71		40		26-Mar-08		8:25:59		68		41.5

		14-Feb-08		10:07:10		67.4		46.5		14-Feb-08		10:06:20		69.8		30		14-Feb-08		10:07:53		70.41		39		26-Mar-08		10:25:59		68		42.5

		14-Feb-08		12:07:10		68		46.5		14-Feb-08		12:06:20		70.41		30.5		14-Feb-08		12:07:53		71		33		26-Mar-08		12:25:59		68.61		43.5

		14-Feb-08		14:07:10		66.2		46.5		14-Feb-08		14:06:20		72.21		28.5		14-Feb-08		14:07:53		71		38.5		26-Mar-08		14:25:59		68		43

		14-Feb-08		16:07:10		65.6		47		14-Feb-08		16:06:20		72.8		24		14-Feb-08		16:07:53		71		37.5		26-Mar-08		16:25:59		68		42

		14-Feb-08		18:07:10		65.01		49		14-Feb-08		18:06:20		71.6		16.5		14-Feb-08		18:07:53		71		30.5		26-Mar-08		18:25:59		68		40.5

		14-Feb-08		20:07:10		64.4		47		14-Feb-08		20:06:20		71		17		14-Feb-08		20:07:53		70.41		30		26-Mar-08		20:25:59		68.61		38

		14-Feb-08		22:07:10		64.4		49		14-Feb-08		22:06:20		70.41		27.5		14-Feb-08		22:07:53		71		32		26-Mar-08		22:25:59		68		37.5

		15-Feb-08		0:07:10		64.4		49		15-Feb-08		0:06:20		70.41		26		15-Feb-08		0:07:53		70.41		32		27-Mar-08		0:25:59		68		38

		15-Feb-08		2:07:10		64.4		46.5		15-Feb-08		2:06:20		70.41		23.5		15-Feb-08		2:07:53		69.2		31		27-Mar-08		2:25:59		67.4		37.5

		15-Feb-08		4:07:10		64.4		50.5		15-Feb-08		4:06:20		70.41		21		15-Feb-08		4:07:53		68.61		31		27-Mar-08		4:25:59		67.4		36.5

		15-Feb-08		6:07:10		64.4		49		15-Feb-08		6:06:20		70.41		19.5		15-Feb-08		6:07:53		68		30.5		27-Mar-08		6:25:59		67.4		35

		15-Feb-08		8:07:10		64.4		50.5		15-Feb-08		8:06:20		70.41		19.5		15-Feb-08		8:07:53		70.41		31		27-Mar-08		8:25:59		68		35.5

		15-Feb-08		10:07:10		65.01		33.5		15-Feb-08		10:06:20		72.21		19.5		15-Feb-08		10:07:53		71		30.5		27-Mar-08		10:25:59		67.4		37

		15-Feb-08		12:07:10		65.6		48		15-Feb-08		12:06:20		72.8		19		15-Feb-08		12:07:53		71		29.5		27-Mar-08		12:25:59		68		36.5

		15-Feb-08		14:07:10		65.6		49		15-Feb-08		14:06:20		72.8		19.5		15-Feb-08		14:07:53		71		34.5		27-Mar-08		14:25:59		68		39

		15-Feb-08		16:07:10		65.6		48.5		15-Feb-08		16:06:20		73.4		19		15-Feb-08		16:07:53		71		34		27-Mar-08		16:25:59		68		39.5

		15-Feb-08		18:07:10		65.6		49.5		15-Feb-08		18:06:20		71.6		20.5		15-Feb-08		18:07:53		70.41		32		27-Mar-08		18:25:59		68.61		37.5

		15-Feb-08		20:07:10		65.01		43.5		15-Feb-08		20:06:20		71		24.5		15-Feb-08		20:07:53		70.41		31.5		27-Mar-08		20:25:59		68.61		37

		15-Feb-08		22:07:10		65.01		49		15-Feb-08		22:06:20		70.41		26.5		15-Feb-08		22:07:53		69.8		31.5		27-Mar-08		22:25:59		68.61		34.5

		16-Feb-08		0:07:10		65.6		50		16-Feb-08		0:06:20		70.41		26.5		16-Feb-08		0:07:53		69.2		32		28-Mar-08		0:25:59		68		34.5

		16-Feb-08		2:07:10		65.01		50		16-Feb-08		2:06:20		70.41		26.5		16-Feb-08		2:07:53		68.61		33		28-Mar-08		2:25:59		67.4		33

		16-Feb-08		4:07:10		65.01		51		16-Feb-08		4:06:20		70.41		27		16-Feb-08		4:07:53		68		33.5		28-Mar-08		4:25:59		66.81		31.5

		16-Feb-08		6:07:10		65.01		50		16-Feb-08		6:06:20		70.41		26.5		16-Feb-08		6:07:53		66.81		34		28-Mar-08		6:25:59		67.4		31.5

		16-Feb-08		8:07:10		65.01		51		16-Feb-08		8:06:20		70.41		27		16-Feb-08		8:07:53		69.2		33		28-Mar-08		8:25:59		68		30.5

		16-Feb-08		10:07:10		65.6		51		16-Feb-08		10:06:20		71.6		27.5		16-Feb-08		10:07:53		71.6		33.5		28-Mar-08		10:25:59		68		29

		16-Feb-08		12:07:10		65.01		50		16-Feb-08		12:06:20		73.4		28		16-Feb-08		12:07:53		70.41		39		28-Mar-08		12:25:59		68		26

		16-Feb-08		14:07:10		65.6		50		16-Feb-08		14:06:20		73.4		27		16-Feb-08		14:07:53		71		33		28-Mar-08		14:25:59		68.61		25.5

		16-Feb-08		16:07:10		65.6		51.5		16-Feb-08		16:06:20		73.4		37.5		16-Feb-08		16:07:53		71.6		36.5		28-Mar-08		16:25:59		68		23.5

		16-Feb-08		18:07:10		65.01		51		16-Feb-08		18:06:20		67.4		41		16-Feb-08		18:07:53		70.41		40		28-Mar-08		18:25:59		68.61		23.5

		16-Feb-08		20:07:10		65.01		50.5		16-Feb-08		20:06:20		66.2		43		16-Feb-08		20:07:53		71		39.5		28-Mar-08		20:25:59		68		26.5

		16-Feb-08		22:07:10		65.01		52		16-Feb-08		22:06:20		66.81		41		16-Feb-08		22:07:53		70.41		39		28-Mar-08		22:25:59		68		32.5

		17-Feb-08		0:07:10		65.01		52		17-Feb-08		0:06:20		66.2		40		17-Feb-08		0:07:53		69.8		38		29-Mar-08		0:25:59		67.4		33.5

		17-Feb-08		2:07:10		65.01		52.5		17-Feb-08		2:06:20		66.2		40.5		17-Feb-08		2:07:53		69.2		39.5		29-Mar-08		2:25:59		67.4		34

		17-Feb-08		4:07:10		65.01		53		17-Feb-08		4:06:20		66.2		41.5		17-Feb-08		4:07:53		68.61		39.5		29-Mar-08		4:25:59		66.81		34

		17-Feb-08		6:07:10		65.01		53		17-Feb-08		6:06:20		66.2		41		17-Feb-08		6:07:53		68.61		40		29-Mar-08		6:25:59		67.4		33.5

		17-Feb-08		8:07:10		65.01		52		17-Feb-08		8:06:20		65.6		40		17-Feb-08		8:07:53		70.41		39		29-Mar-08		8:25:59		68		34

		17-Feb-08		10:07:10		65.01		52		17-Feb-08		10:06:20		65.6		40.5		17-Feb-08		10:07:53		71		37.5		29-Mar-08		10:25:59		67.4		30.5

		17-Feb-08		12:07:10		65.01		52.5		17-Feb-08		12:06:20		66.81		40.5		17-Feb-08		12:07:53		71		38.5		29-Mar-08		12:25:59		68		37

		17-Feb-08		14:07:10		65.01		52		17-Feb-08		14:06:20		67.4		40.5		17-Feb-08		14:07:53		70.41		41.5		29-Mar-08		14:25:59		68		39.5

		17-Feb-08		16:07:10		65.01		53		17-Feb-08		16:06:20		68		38		17-Feb-08		16:07:53		71		43.5		29-Mar-08		16:25:59		68		42

		17-Feb-08		18:07:10		65.01		52.5		17-Feb-08		18:06:20		66.81		42.5		17-Feb-08		18:07:53		70.41		41.5		29-Mar-08		18:25:59		68		42.5

		17-Feb-08		20:07:10		65.01		52.5		17-Feb-08		20:06:20		66.81		42.5		17-Feb-08		20:07:53		69.8		40.5		29-Mar-08		20:25:59		68		43

		17-Feb-08		22:07:10		65.01		53		17-Feb-08		22:06:20		66.81		40.5		17-Feb-08		22:07:53		69.8		39		29-Mar-08		22:25:59		68		43.5

		18-Feb-08		0:07:10		65.01		52		18-Feb-08		0:06:20		66.2		39.5		18-Feb-08		0:07:53		69.2		38.5		30-Mar-08		0:25:59		68		43.5

		18-Feb-08		2:07:10		65.01		52.5		18-Feb-08		2:06:20		66.2		42.5		18-Feb-08		2:07:53		68.61		40		30-Mar-08		2:25:59		68.61		42.5

		18-Feb-08		4:07:10		65.01		52		18-Feb-08		4:06:20		65.6		41.5		18-Feb-08		4:07:53		68		40.5		30-Mar-08		4:25:59		68.61		41.5

		18-Feb-08		6:07:10		65.01		51.5		18-Feb-08		6:06:20		65.6		41.5		18-Feb-08		6:07:53		68		40.5		30-Mar-08		6:25:59		68.61		40

		18-Feb-08		8:07:10		65.01		52		18-Feb-08		8:06:20		65.6		40		18-Feb-08		8:07:53		67.4		40.5		30-Mar-08		8:25:59		68.61		39

		18-Feb-08		10:07:10		65.01		51.5		18-Feb-08		10:06:20		65.6		41		18-Feb-08		10:07:53		67.4		40.5		30-Mar-08		10:25:59		68.61		39

		18-Feb-08		12:07:10		65.01		52		18-Feb-08		12:06:20		66.2		41.5		18-Feb-08		12:07:53		67.4		41		30-Mar-08		12:25:59		68.61		40

		18-Feb-08		14:07:10		65.01		52.5		18-Feb-08		14:06:20		67.4		42		18-Feb-08		14:07:53		68.61		41.5		30-Mar-08		14:25:59		68.61		40.5

		18-Feb-08		16:07:10		65.01		53.5		18-Feb-08		16:06:20		66.81		45.5		18-Feb-08		16:07:53		69.8		42		30-Mar-08		16:25:59		68.61		40

		18-Feb-08		18:07:10		65.01		54		18-Feb-08		18:06:20		66.2		45		18-Feb-08		18:07:53		69.8		42.5		30-Mar-08		18:25:59		68.61		38.5

		18-Feb-08		20:07:10		65.01		52.5		18-Feb-08		20:06:20		66.81		41.5		18-Feb-08		20:07:53		69.2		41		30-Mar-08		20:25:59		68.61		37

		18-Feb-08		22:07:10		65.01		53		18-Feb-08		22:06:20		66.2		42.5		18-Feb-08		22:07:53		68.61		40.5		30-Mar-08		22:25:59		68.61		32.5

		19-Feb-08		0:07:10		65.01		51		19-Feb-08		0:06:20		66.2		41.5		19-Feb-08		0:07:53		68.61		41		31-Mar-08		0:25:59		68.61		32

		19-Feb-08		2:07:10		65.01		52.5		19-Feb-08		2:06:20		66.2		42.5		19-Feb-08		2:07:53		68		41.5		31-Mar-08		2:25:59		67.4		33

		19-Feb-08		4:07:10		65.01		51		19-Feb-08		4:06:20		66.2		43		19-Feb-08		4:07:53		68		41.5		31-Mar-08		4:25:59		66.81		33.5

		19-Feb-08		6:07:10		65.01		53		19-Feb-08		6:06:20		66.2		43		19-Feb-08		6:07:53		68		42		31-Mar-08		6:25:59		67.4		32.5

		19-Feb-08		8:07:10		65.01		52		19-Feb-08		8:06:20		66.81		42.5		19-Feb-08		8:07:53		68		42.5		31-Mar-08		8:25:59		68		32

		19-Feb-08		10:07:10		65.01		52.5		19-Feb-08		10:06:20		66.2		43.5		19-Feb-08		10:07:53		68.61		42.5		31-Mar-08		10:25:59		68.61		28.5

		19-Feb-08		12:07:10		65.01		52.5		19-Feb-08		12:06:20		66.2		43.5		19-Feb-08		12:07:53		69.2		42.5		31-Mar-08		12:25:59		67.4		25.5

		19-Feb-08		14:07:10		65.01		52		19-Feb-08		14:06:20		66.81		43		19-Feb-08		14:07:53		69.8		42		31-Mar-08		14:25:59		68		24

		19-Feb-08		16:07:10		65.01		52.5		19-Feb-08		16:06:20		66.2		44.5		19-Feb-08		16:07:53		69.8		42.5		31-Mar-08		16:25:59		68.61		24.5

		19-Feb-08		18:07:10		65.01		51.5		19-Feb-08		18:06:20		66.81		43		19-Feb-08		18:07:53		69.8		42		31-Mar-08		18:25:59		68		27.5

		19-Feb-08		20:07:10		65.01		52		19-Feb-08		20:06:20		66.2		43		19-Feb-08		20:07:53		69.8		41.5		31-Mar-08		20:25:59		68		27

		19-Feb-08		22:07:10		65.01		52		19-Feb-08		22:06:20		66.2		42		19-Feb-08		22:07:53		69.8		40.5		31-Mar-08		22:25:59		68		27.5

		20-Feb-08		0:07:10		65.01		52.5		20-Feb-08		0:06:20		66.81		39.5		20-Feb-08		0:07:53		69.8		40		1-Apr-08		0:25:59		67.4		29

		20-Feb-08		2:07:10		65.01		52		20-Feb-08		2:06:20		66.81		40.5		20-Feb-08		2:07:53		69.2		40		1-Apr-08		2:25:59		67.4		29

		20-Feb-08		4:07:10		65.01		52		20-Feb-08		4:06:20		66.81		40.5		20-Feb-08		4:07:53		69.2		40		1-Apr-08		4:25:59		68		28

		20-Feb-08		6:07:10		65.01		52.5		20-Feb-08		6:06:20		66.81		41		20-Feb-08		6:07:53		69.2		40.5		1-Apr-08		6:25:59		68.61		28.5

		20-Feb-08		8:07:10		65.6		51.5		20-Feb-08		8:06:20		67.4		41		20-Feb-08		8:07:53		71		41		1-Apr-08		8:25:59		68		30

		20-Feb-08		10:07:10		65.6		51.5		20-Feb-08		10:06:20		66.81		42		20-Feb-08		10:07:53		71		39.5		1-Apr-08		10:25:59		67.4		31

		20-Feb-08		12:07:10		66.2		51		20-Feb-08		12:06:20		66.81		48.5		20-Feb-08		12:07:53		71		42.5		1-Apr-08		12:25:59		68		25

		20-Feb-08		14:07:10		65.6		52.5		20-Feb-08		14:06:20		66.81		51.5		20-Feb-08		14:07:53		71		39		1-Apr-08		14:25:59		68		29.5

		20-Feb-08		16:07:10		66.81		52.5		20-Feb-08		16:06:20		67.4		48.5		20-Feb-08		16:07:53		70.41		43.5		1-Apr-08		16:25:59		68		31

		20-Feb-08		18:07:10		66.2		52		20-Feb-08		18:06:20		67.4		51.5		20-Feb-08		18:07:53		70.41		48		1-Apr-08		18:25:59		68		29.5

		20-Feb-08		20:07:10		66.2		51		20-Feb-08		20:06:20		66.2		55		20-Feb-08		20:07:53		70.41		47		1-Apr-08		20:25:59		67.4		30.5

		20-Feb-08		22:07:10		66.2		52.5		20-Feb-08		22:06:20		67.4		51.5		20-Feb-08		22:07:53		71		45.5		1-Apr-08		22:25:59		68		29.5

		21-Feb-08		0:07:10		66.2		52.5		21-Feb-08		0:06:20		67.4		50.5		21-Feb-08		0:07:53		70.41		45.5		2-Apr-08		0:25:59		68		32.5

		21-Feb-08		2:07:10		65.6		52.5		21-Feb-08		2:06:20		66.81		47		21-Feb-08		2:07:53		69.8		44		2-Apr-08		2:25:59		68		33.5

		21-Feb-08		4:07:10		65.6		52		21-Feb-08		4:06:20		66.81		47.5		21-Feb-08		4:07:53		69.2		44		2-Apr-08		4:25:59		68		33

		21-Feb-08		6:07:10		65.6		52.5		21-Feb-08		6:06:20		66.81		47		21-Feb-08		6:07:53		68.61		44.5		2-Apr-08		6:25:59		68		31

		21-Feb-08		8:07:10		66.2		52		21-Feb-08		8:06:20		67.4		47		21-Feb-08		8:07:53		71		41.5		2-Apr-08		8:25:59		68		33.5

		21-Feb-08		10:07:10		66.2		52		21-Feb-08		10:06:20		67.4		48.5		21-Feb-08		10:07:53		72.21		44.5		2-Apr-08		10:25:59		68		33

		21-Feb-08		12:07:10		65.6		51.5		21-Feb-08		12:06:20		66.81		49.5		21-Feb-08		12:07:53		70.41		48		2-Apr-08		12:25:59		68.61		33

		21-Feb-08		14:07:10		65.6		51		21-Feb-08		14:06:20		68		41		21-Feb-08		14:07:53		71.6		48.5		2-Apr-08		14:25:59		68		36.5

		21-Feb-08		16:07:10		66.81		50.5		21-Feb-08		16:06:20		68		40.5		21-Feb-08		16:07:53		71		47.5		2-Apr-08		16:25:59		68		34

		21-Feb-08		18:07:10		66.2		52		21-Feb-08		18:06:20		67.4		42.5		21-Feb-08		18:07:53		70.41		45.5		2-Apr-08		18:25:59		68		34

		21-Feb-08		20:07:10		66.2		52.5		21-Feb-08		20:06:20		66.81		44.5		21-Feb-08		20:07:53		70.41		43.5		2-Apr-08		20:25:59		68		37

		21-Feb-08		22:07:10		66.2		51.5		21-Feb-08		22:06:20		67.4		45		21-Feb-08		22:07:53		71		42.5		2-Apr-08		22:25:59		68.61		36.5

		22-Feb-08		0:07:10		66.2		49.5		22-Feb-08		0:06:20		66.81		43		22-Feb-08		0:07:53		70.41		41.5		3-Apr-08		0:25:59		68.61		36.5

		22-Feb-08		2:07:10		65.6		51.5		22-Feb-08		2:06:20		66.81		43.5		22-Feb-08		2:07:53		69.8		41		3-Apr-08		2:25:59		68		36

		22-Feb-08		4:07:10		65.6		52		22-Feb-08		4:06:20		66.81		43.5		22-Feb-08		4:07:53		69.2		41.5		3-Apr-08		4:25:59		67.4		35

		22-Feb-08		6:07:10		66.2		51.5		22-Feb-08		6:06:20		66.81		44		22-Feb-08		6:07:53		69.2		42		3-Apr-08		6:25:59		69.2		34

		22-Feb-08		8:07:10		66.2		51		22-Feb-08		8:06:20		66.2		46		22-Feb-08		8:07:53		71		44		3-Apr-08		8:25:59		67.4		36.5

		22-Feb-08		10:07:10		66.81		48		22-Feb-08		10:06:20		66.2		48		22-Feb-08		10:07:53		71.6		43		3-Apr-08		10:25:59		68		36.5

		22-Feb-08		12:07:10		66.81		48.5		22-Feb-08		12:06:20		67.4		43.5		22-Feb-08		12:07:53		71		39		3-Apr-08		12:25:59		68		37.5

		22-Feb-08		14:07:10		66.81		49		22-Feb-08		14:06:20		68		44.5		22-Feb-08		14:07:53		71		44		3-Apr-08		14:25:59		68		39

		22-Feb-08		16:07:10		66.2		50		22-Feb-08		16:06:20		68		48		22-Feb-08		16:07:53		71		40		3-Apr-08		16:25:59		68		37.5

		22-Feb-08		18:07:10		66.2		51.5		22-Feb-08		18:06:20		66.81		48		22-Feb-08		18:07:53		71		46.5		3-Apr-08		18:25:59		68.61		35

		22-Feb-08		20:07:10		66.2		49		22-Feb-08		20:06:20		67.4		49.5		22-Feb-08		20:07:53		70.41		42		3-Apr-08		20:25:59		68		35.5

		22-Feb-08		22:07:10		66.2		51		22-Feb-08		22:06:20		66.81		51.5		22-Feb-08		22:07:53		70.41		45.5		3-Apr-08		22:25:59		68.61		34

		23-Feb-08		0:07:10		65.6		50.5		23-Feb-08		0:06:20		66.81		49.5		23-Feb-08		0:07:53		70.41		44.5		4-Apr-08		0:25:59		68		34

		23-Feb-08		2:07:10		65.6		49		23-Feb-08		2:06:20		67.4		48		23-Feb-08		2:07:53		69.8		43.5		4-Apr-08		2:25:59		68		33.5

		23-Feb-08		4:07:10		65.6		49		23-Feb-08		4:06:20		67.4		46		23-Feb-08		4:07:53		69.8		43		4-Apr-08		4:25:59		68		35

		23-Feb-08		6:07:10		65.6		46.5		23-Feb-08		6:06:20		66.81		47		23-Feb-08		6:07:53		69.2		43		4-Apr-08		6:25:59		68.61		36.5

		23-Feb-08		8:07:10		66.2		48.5		23-Feb-08		8:06:20		66.2		48		23-Feb-08		8:07:53		71		40.5		4-Apr-08		8:25:59		68		38

		23-Feb-08		10:07:10		66.2		49.5		23-Feb-08		10:06:20		67.4		48		23-Feb-08		10:07:53		71.6		48.5		4-Apr-08		10:25:59		67.4		39

		23-Feb-08		12:07:10		66.81		48.5		23-Feb-08		12:06:20		67.4		47.5		23-Feb-08		12:07:53		71		49.5		4-Apr-08		12:25:59		73.4		36.5

		23-Feb-08		14:07:10		66.81		48.5		23-Feb-08		14:06:20		67.4		47		23-Feb-08		14:07:53		71		45.5		4-Apr-08		14:25:59		74.01		36

		23-Feb-08		16:07:10		66.81		44		23-Feb-08		16:06:20		68		41.5		23-Feb-08		16:07:53		71.6		45.5		4-Apr-08		16:25:59		74.6		37.5

		23-Feb-08		18:07:10		66.2		48		23-Feb-08		18:06:20		67.4		39.5		23-Feb-08		18:07:53		71		42.5		4-Apr-08		18:25:59		74.01		36.5

		23-Feb-08		20:07:10		66.2		48		23-Feb-08		20:06:20		66.81		38		23-Feb-08		20:07:53		70.41		40		4-Apr-08		20:25:59		73.4		36.5

		23-Feb-08		22:07:10		66.2		48.5		23-Feb-08		22:06:20		66.2		38.5		23-Feb-08		22:07:53		69.8		40.5		4-Apr-08		22:25:59		71.6		37

		24-Feb-08		0:07:10		65.6		49.5		24-Feb-08		0:06:20		65.01		38		24-Feb-08		0:07:53		69.2		38		5-Apr-08		0:25:59		70.41		36.5

		24-Feb-08		2:07:10		65.6		41.5		24-Feb-08		2:06:20		64.4		38		24-Feb-08		2:07:53		68		38		5-Apr-08		2:25:59		69.2		36.5

		24-Feb-08		4:07:10		65.6		48		24-Feb-08		4:06:20		63.8		37		24-Feb-08		4:07:53		66.81		37.5		5-Apr-08		4:25:59		68.61		38

		24-Feb-08		6:07:10		65.6		48		24-Feb-08		6:06:20		63.8		38		24-Feb-08		6:07:53		66.2		38.5		5-Apr-08		6:25:59		69.2		37.5

		24-Feb-08		8:07:10		66.2		48		24-Feb-08		8:06:20		64.4		38.5		24-Feb-08		8:07:53		68		38		5-Apr-08		8:25:59		70.41		38.5

		24-Feb-08		10:07:10		66.81		43		24-Feb-08		10:06:20		65.01		42		24-Feb-08		10:07:53		67.4		39.5		5-Apr-08		10:25:59		71.6		38.5

		24-Feb-08		12:07:10		66.81		47		24-Feb-08		12:06:20		66.2		42		24-Feb-08		12:07:53		68		40		5-Apr-08		12:25:59		72.8		38.5

		24-Feb-08		14:07:10		66.2		48		24-Feb-08		14:06:20		66.2		42.5		24-Feb-08		14:07:53		68		41		5-Apr-08		14:25:59		73.4		38.5

		24-Feb-08		16:07:10		66.2		48		24-Feb-08		16:06:20		65.6		44.5		24-Feb-08		16:07:53		68		42		5-Apr-08		16:25:59		74.01		38.5

		24-Feb-08		18:07:10		66.2		49		24-Feb-08		18:06:20		65.01		41.5		24-Feb-08		18:07:53		67.4		41.5		5-Apr-08		18:25:59		73.4		37.5

		24-Feb-08		20:07:10		65.6		45		24-Feb-08		20:06:20		65.6		44		24-Feb-08		20:07:53		66.81		42.5		5-Apr-08		20:25:59		72.8		37

		24-Feb-08		22:07:10		66.2		49		24-Feb-08		22:06:20		65.6		48		24-Feb-08		22:07:53		66.81		44.5		5-Apr-08		22:25:59		71.6		36.5

		25-Feb-08		0:07:10		66.2		49		25-Feb-08		0:06:20		66.2		47.5		25-Feb-08		0:07:53		67.4		45		6-Apr-08		0:25:59		69.8		36

		25-Feb-08		2:07:10		66.2		49		25-Feb-08		2:06:20		66.81		48		25-Feb-08		2:07:53		67.4		45.5		6-Apr-08		2:25:59		68		36.5

		25-Feb-08		4:07:10		66.2		49.5		25-Feb-08		4:06:20		66.81		49		25-Feb-08		4:07:53		67.4		46		6-Apr-08		4:25:59		67.4		37

		25-Feb-08		6:07:10		66.2		48		25-Feb-08		6:06:20		66.81		50		25-Feb-08		6:07:53		67.4		47		6-Apr-08		6:25:59		66.81		36.5

		25-Feb-08		8:07:10		66.2		49.5		25-Feb-08		8:06:20		66.81		51		25-Feb-08		8:07:53		67.4		48		6-Apr-08		8:25:59		66.81		36.5

		25-Feb-08		10:07:10		66.2		51.5		25-Feb-08		10:06:20		67.4		51.5		25-Feb-08		10:07:53		67.4		49.5		6-Apr-08		10:25:59		68.61		38

		25-Feb-08		12:07:10		66.2		52		25-Feb-08		12:06:20		66.81		52.5		25-Feb-08		12:07:53		68		49		6-Apr-08		12:25:59		70.41		38.5

		25-Feb-08		14:07:10		66.2		53		25-Feb-08		14:06:20		67.4		52		25-Feb-08		14:07:53		68		49.5		6-Apr-08		14:25:59		71.6		37.5

		25-Feb-08		16:07:10		66.2		49.5		25-Feb-08		16:06:20		66.2		52.5		25-Feb-08		16:07:53		68		49		6-Apr-08		16:25:59		72.21		37

		25-Feb-08		18:07:10		66.2		50.5		25-Feb-08		18:06:20		67.4		49.5		25-Feb-08		18:07:53		68		48		6-Apr-08		18:25:59		72.8		36.5

		25-Feb-08		20:07:10		66.2		50		25-Feb-08		20:06:20		67.4		47.5		25-Feb-08		20:07:53		68		47.5		6-Apr-08		20:25:59		72.21		36.5

		25-Feb-08		22:07:10		66.2		50		25-Feb-08		22:06:20		66.81		48		25-Feb-08		22:07:53		68		47		6-Apr-08		22:25:59		71		37

		26-Feb-08		0:07:10		66.2		49.5		26-Feb-08		0:06:20		66.81		49.5		26-Feb-08		0:07:53		68		47		7-Apr-08		0:25:59		69.2		37

		26-Feb-08		2:07:10		65.6		50.5		26-Feb-08		2:06:20		66.2		49		26-Feb-08		2:07:53		67.4		47		7-Apr-08		2:25:59		68.61		37.5

		26-Feb-08		4:07:10		65.6		49		26-Feb-08		4:06:20		65.6		47		26-Feb-08		4:07:53		67.4		45.5		7-Apr-08		4:25:59		67.4		37.5

		26-Feb-08		6:07:10		65.6		49		26-Feb-08		6:06:20		65.6		48		26-Feb-08		6:07:53		66.81		45.5		7-Apr-08		6:25:59		66.81		38

		26-Feb-08		8:07:10		66.2		49		26-Feb-08		8:06:20		66.2		46.5		26-Feb-08		8:07:53		69.8		44		7-Apr-08		8:25:59		66.81		38.5

		26-Feb-08		10:07:10		66.81		49		26-Feb-08		10:06:20		66.81		48.5		26-Feb-08		10:07:53		71.6		42		7-Apr-08		10:25:59		68		39.5

		26-Feb-08		12:07:10		66.81		49.5		26-Feb-08		12:06:20		67.4		46.5		26-Feb-08		12:07:53		70.41		49.5		7-Apr-08		12:25:59		68.61		40

		26-Feb-08		14:07:10		66.81		48		26-Feb-08		14:06:20		67.4		45.5		26-Feb-08		14:07:53		71.6		51		7-Apr-08		14:25:59		69.8		39

		26-Feb-08		16:07:10		66.81		47.5		26-Feb-08		16:06:20		67.4		44.5		26-Feb-08		16:07:53		71		50.5		7-Apr-08		16:25:59		70.41		37.5

		26-Feb-08		18:07:10		66.2		49		26-Feb-08		18:06:20		67.4		47		26-Feb-08		18:07:53		71		50.5		7-Apr-08		18:25:59		71		36

		26-Feb-08		20:07:10		66.2		48.5		26-Feb-08		20:06:20		66.2		48.5		26-Feb-08		20:07:53		70.41		46		7-Apr-08		20:25:59		69.8		35

		26-Feb-08		22:07:10		65.6		50		26-Feb-08		22:06:20		66.81		46		26-Feb-08		22:07:53		70.41		44.5		7-Apr-08		22:25:59		68.61		35

		27-Feb-08		0:07:10		65.6		47.5		27-Feb-08		0:06:20		66.2		45		27-Feb-08		0:07:53		69.8		41.5		8-Apr-08		0:25:59		68		35.5

		27-Feb-08		2:07:10		65.6		49		27-Feb-08		2:06:20		65.01		43.5		27-Feb-08		2:07:53		68.61		41		8-Apr-08		2:25:59		66.81		36.5

		27-Feb-08		4:07:10		66.2		49		27-Feb-08		4:06:20		65.01		43.5		27-Feb-08		4:07:53		68		41		8-Apr-08		4:25:59		66.2		37

		27-Feb-08		6:07:10		66.2		48		27-Feb-08		6:06:20		65.01		44		27-Feb-08		6:07:53		67.4		41.5		8-Apr-08		6:25:59		67.4		36

		27-Feb-08		8:07:10		66.2		47.5		27-Feb-08		8:06:20		65.6		41		27-Feb-08		8:07:53		69.8		40		8-Apr-08		8:25:59		68.61		35.5

		27-Feb-08		10:07:10		66.2		47		27-Feb-08		10:06:20		66.81		44.5		27-Feb-08		10:07:53		71.6		38		8-Apr-08		10:25:59		71.6		36

		27-Feb-08		12:07:10		66.81		48.5		27-Feb-08		12:06:20		68		44.5		27-Feb-08		12:07:53		71		40.5		8-Apr-08		12:25:59		72.8		35

		27-Feb-08		14:07:10		66.81		46.5		27-Feb-08		14:06:20		67.4		44		27-Feb-08		14:07:53		70.41		39.5		8-Apr-08		14:25:59		74.01		33.5

		27-Feb-08		16:07:10		66.81		47		27-Feb-08		16:06:20		68.61		42		27-Feb-08		16:07:53		70.41		49.5		8-Apr-08		16:25:59		74.01		35.5

		27-Feb-08		18:07:10		66.2		50		27-Feb-08		18:06:20		68		48.5		27-Feb-08		18:07:53		70.41		42.5		8-Apr-08		18:25:59		73.4		34.5

		27-Feb-08		20:07:10		66.2		49.5		27-Feb-08		20:06:20		66.81		51.5		27-Feb-08		20:07:53		70.41		42.5		8-Apr-08		20:25:59		72.8		34.5

		27-Feb-08		22:07:10		66.2		49.5		27-Feb-08		22:06:20		66.81		50		27-Feb-08		22:07:53		71		46		8-Apr-08		22:25:59		72.21		34

		28-Feb-08		0:07:10		66.2		48.5		28-Feb-08		0:06:20		66.2		49.5		28-Feb-08		0:07:53		71		43		9-Apr-08		0:25:59		70.41		35

		28-Feb-08		2:07:10		66.2		49		28-Feb-08		2:06:20		66.81		47.5		28-Feb-08		2:07:53		70.41		42.5		9-Apr-08		2:25:59		69.2		35

		28-Feb-08		4:07:10		65.6		49		28-Feb-08		4:06:20		66.2		46.5		28-Feb-08		4:07:53		69.8		41.5		9-Apr-08		4:25:59		68.61		35.5

		28-Feb-08		6:07:10		65.6		50		28-Feb-08		6:06:20		65.6		45		28-Feb-08		6:07:53		69.2		41		9-Apr-08		6:25:59		69.2		36

		28-Feb-08		8:07:10		66.2		48		28-Feb-08		8:06:20		65.6		42.5		28-Feb-08		8:07:53		70.41		41.5		9-Apr-08		8:25:59		70.41		36.5

		28-Feb-08		10:07:10		66.2		47.5		28-Feb-08		10:06:20		67.4		46		28-Feb-08		10:07:53		71		39		9-Apr-08		10:25:59		72.8		35.5

		28-Feb-08		12:07:10		66.81		49		28-Feb-08		12:06:20		68		48		28-Feb-08		12:07:53		71		41		9-Apr-08		12:25:59		74.01		35

		28-Feb-08		14:07:10		66.81		49.5		28-Feb-08		14:06:20		68.61		47		28-Feb-08		14:07:53		71		40		9-Apr-08		14:25:59		74.01		34

		28-Feb-08		16:07:10		66.81		51.5		28-Feb-08		16:06:20		67.4		56		28-Feb-08		16:07:53		71		51.5		9-Apr-08		16:25:59		74.01		34.5

		28-Feb-08		18:07:10		66.2		51.5		28-Feb-08		18:06:20		68		49.5		28-Feb-08		18:07:53		71		52		9-Apr-08		18:25:59		74.01		34.5

		28-Feb-08		20:07:10		66.2		48.5		28-Feb-08		20:06:20		66.81		53		28-Feb-08		20:07:53		71.6		47		9-Apr-08		20:25:59		72.8		33.5

		28-Feb-08		22:07:10		66.2		50		28-Feb-08		22:06:20		67.4		49.5		28-Feb-08		22:07:53		72.21		44		9-Apr-08		22:25:59		71		33.5

		29-Feb-08		0:07:10		65.6		49		29-Feb-08		0:06:20		66.81		48		29-Feb-08		0:07:53		71.6		42.5		10-Apr-08		0:25:59		69.2		33.5

		29-Feb-08		2:07:10		65.6		49		29-Feb-08		2:06:20		66.2		46		29-Feb-08		2:07:53		70.41		41.5		10-Apr-08		2:25:59		68		34.5

		29-Feb-08		4:07:10		66.2		49		29-Feb-08		4:06:20		65.01		44.5		29-Feb-08		4:07:53		69.2		40.5		10-Apr-08		4:25:59		66.81		35

		29-Feb-08		6:07:10		65.6		48.5		29-Feb-08		6:06:20		65.01		42		29-Feb-08		6:07:53		68.61		39.5		10-Apr-08		6:25:59		68		34.5

		29-Feb-08		8:07:10		66.2		48		29-Feb-08		8:06:20		65.01		40		29-Feb-08		8:07:53		71		38		10-Apr-08		8:25:59		69.2		35

		29-Feb-08		10:07:10		66.2		48		29-Feb-08		10:06:20		66.81		45.5		29-Feb-08		10:07:53		72.21		42.5		10-Apr-08		10:25:59		72.21		36

		29-Feb-08		12:07:10		66.81		48.5		29-Feb-08		12:06:20		66.81		47.5		29-Feb-08		12:07:53		71.6		47		10-Apr-08		12:25:59		74.01		35.5

		29-Feb-08		14:07:10		66.81		50.5		29-Feb-08		14:06:20		68.61		47.5		29-Feb-08		14:07:53		71		45		10-Apr-08		14:25:59		74.6		36.5

		29-Feb-08		16:07:10		66.81		51.5		29-Feb-08		16:06:20		68		45.5		29-Feb-08		16:07:53		70.41		44		10-Apr-08		16:25:59		74.01		37

		29-Feb-08		18:07:10		66.2		52		29-Feb-08		18:06:20		67.4		54		29-Feb-08		18:07:53		71		52		10-Apr-08		18:25:59		73.4		34.5

		29-Feb-08		20:07:10		66.2		49		29-Feb-08		20:06:20		67.4		48.5		29-Feb-08		20:07:53		69.8		50		10-Apr-08		20:25:59		72.8		35

		29-Feb-08		22:07:10		65.6		50		29-Feb-08		22:06:20		66.81		49.5		29-Feb-08		22:07:53		71.6		44.5		10-Apr-08		22:25:59		71.6		35

		1-Mar-08		0:07:10		65.6		48.5		1-Mar-08		0:06:20		66.81		47		1-Mar-08		0:07:53		71.6		42		11-Apr-08		0:25:59		70.41		35.5

		1-Mar-08		2:07:10		65.6		48.5		1-Mar-08		2:06:20		66.2		49		1-Mar-08		2:07:53		71		42		11-Apr-08		2:25:59		69.2		35

		1-Mar-08		4:07:10		65.6		49.5		1-Mar-08		4:06:20		66.2		48.5		1-Mar-08		4:07:53		70.41		42.5		11-Apr-08		4:25:59		68.61		35.5

		1-Mar-08		6:07:10		65.6		49		1-Mar-08		6:06:20		65.6		48		1-Mar-08		6:07:53		70.41		42.5		11-Apr-08		6:25:59		69.2		35.5

		1-Mar-08		8:07:10		66.2		48.5		1-Mar-08		8:06:20		66.2		46.5		1-Mar-08		8:07:53		71		43.5		11-Apr-08		8:25:59		71		36

		1-Mar-08		10:07:10		66.2		48.5		1-Mar-08		10:06:20		67.4		45		1-Mar-08		10:07:53		71		46		11-Apr-08		10:25:59		72.8		36.5

		1-Mar-08		12:07:10		66.81		49.5		1-Mar-08		12:06:20		66.81		49.5		1-Mar-08		12:07:53		71		48		11-Apr-08		12:25:59		74.6		36.5

		1-Mar-08		14:07:10		66.81		49		1-Mar-08		14:06:20		68		51.5		1-Mar-08		14:07:53		71		40		11-Apr-08		14:25:59		74.6		36

		1-Mar-08		16:07:10		66.81		51.5		1-Mar-08		16:06:20		68		56		1-Mar-08		16:07:53		71		51.5		11-Apr-08		16:25:59		74.6		36.5

		1-Mar-08		18:07:10		66.2		49		1-Mar-08		18:06:20		66.81		50.5		1-Mar-08		18:07:53		70.41		48.5		11-Apr-08		18:25:59		74.01		36

		1-Mar-08		20:07:10		65.6		49.5		1-Mar-08		20:06:20		66.81		49		1-Mar-08		20:07:53		69.8		46.5		11-Apr-08		20:25:59		74.01		36

		1-Mar-08		22:07:10		65.6		49		1-Mar-08		22:06:20		66.81		47		1-Mar-08		22:07:53		69.8		44		11-Apr-08		22:25:59		72.8		36.5

		2-Mar-08		0:07:10		65.6		49		2-Mar-08		0:06:20		66.81		48.5		2-Mar-08		0:07:53		69.8		43.5		12-Apr-08		0:25:59		71.6		37

		2-Mar-08		2:07:10		65.6		49		2-Mar-08		2:06:20		66.81		48.5		2-Mar-08		2:07:53		69.8		43.5		12-Apr-08		2:25:59		69.8		37

		2-Mar-08		4:07:10		65.6		49		2-Mar-08		4:06:20		66.2		48.5		2-Mar-08		4:07:53		69.2		43.5		12-Apr-08		4:25:59		69.2		37.5

		2-Mar-08		6:07:10		65.6		49		2-Mar-08		6:06:20		66.2		48		2-Mar-08		6:07:53		69.2		43.5		12-Apr-08		6:25:59		69.8		37

		2-Mar-08		8:07:10		65.6		49		2-Mar-08		8:06:20		66.81		45		2-Mar-08		8:07:53		71.6		41		12-Apr-08		8:25:59		71		37

		2-Mar-08		10:07:10		66.2		48.5		2-Mar-08		10:06:20		68		42		2-Mar-08		10:07:53		71		36.5		12-Apr-08		10:25:59		73.4		39

		2-Mar-08		12:07:10		66.2		49		2-Mar-08		12:06:20		67.4		35.5		2-Mar-08		12:07:53		70.41		40.5		12-Apr-08		12:25:59		74.6		38.5

		2-Mar-08		14:07:10		65.6		48		2-Mar-08		14:06:20		66.81		34.5		2-Mar-08		14:07:53		71		36.5		12-Apr-08		14:25:59		75.2		36.5

		2-Mar-08		16:07:10		65.6		47		2-Mar-08		16:06:20		67.4		35.5		2-Mar-08		16:07:53		70.41		35		12-Apr-08		16:25:59		74.6		36

		2-Mar-08		18:07:10		65.6		48.5		2-Mar-08		18:06:20		66.2		34.5		2-Mar-08		18:07:53		69.8		34.5		12-Apr-08		18:25:59		74.01		35

		2-Mar-08		20:07:10		65.6		47.5		2-Mar-08		20:06:20		66.2		36.5		2-Mar-08		20:07:53		69.8		35.5		12-Apr-08		20:25:59		73.4		33

		2-Mar-08		22:07:10		65.6		48		2-Mar-08		22:06:20		66.81		37.5		2-Mar-08		22:07:53		69.2		36.5		12-Apr-08		22:25:59		72.8		34.5

		3-Mar-08		0:07:10		65.6		47		3-Mar-08		0:06:20		66.2		37		3-Mar-08		0:07:53		68.61		36.5		13-Apr-08		0:25:59		71.6		35.5

		3-Mar-08		2:07:10		65.6		46.5		3-Mar-08		2:06:20		65.6		35		3-Mar-08		2:07:53		68		36.5		13-Apr-08		2:25:59		70.41		36.5

		3-Mar-08		4:07:10		65.6		49.5		3-Mar-08		4:06:20		65.01		34.5		3-Mar-08		4:07:53		67.4		36		13-Apr-08		4:25:59		69.8		36.5

		3-Mar-08		6:07:10		65.6		48.5		3-Mar-08		6:06:20		65.01		33		3-Mar-08		6:07:53		66.81		36		13-Apr-08		6:25:59		69.8		36.5

		3-Mar-08		8:07:10		66.2		47.5		3-Mar-08		8:06:20		65.01		32.5		3-Mar-08		8:07:53		67.4		34.5		13-Apr-08		8:25:59		69.8		36.5

		3-Mar-08		10:07:10		65.01		47		3-Mar-08		10:06:20		66.2		30.5		3-Mar-08		10:07:53		68		34		13-Apr-08		10:25:59		71.6		38.5

		3-Mar-08		12:07:10		65.6		48		3-Mar-08		12:06:20		67.4		27.5		3-Mar-08		12:07:53		69.2		31.5		13-Apr-08		12:25:59		74.01		37.5

		3-Mar-08		14:07:10		66.2		44.5		3-Mar-08		14:06:20		68		21.5		3-Mar-08		14:07:53		69.8		29		13-Apr-08		14:25:59		74.01		37.5

		3-Mar-08		16:07:10		66.2		44.5		3-Mar-08		16:06:20		68		19		3-Mar-08		16:07:53		69.8		29		13-Apr-08		16:25:59		72.8		38

		3-Mar-08		18:07:10		66.2		45		3-Mar-08		18:06:20		67.4		19		3-Mar-08		18:07:53		69.2		29.5		13-Apr-08		18:25:59		72.8		37.5

		3-Mar-08		20:07:10		65.6		46		3-Mar-08		20:06:20		66.81		19.5		3-Mar-08		20:07:53		70.41		28		13-Apr-08		20:25:59		72.8		37

		3-Mar-08		22:07:10		65.6		47.5		3-Mar-08		22:06:20		67.4		26		3-Mar-08		22:07:53		70.41		29.5		13-Apr-08		22:25:59		72.8		39.5

		4-Mar-08		0:07:10		65.6		48		4-Mar-08		0:06:20		66.2		34		4-Mar-08		0:07:53		69.8		32		14-Apr-08		0:25:59		71.6		39.5

		4-Mar-08		2:07:10		65.6		48.5		4-Mar-08		2:06:20		65.6		35.5		4-Mar-08		2:07:53		69.2		33.5		14-Apr-08		2:25:59		71		39

		4-Mar-08		4:07:10		65.6		46.5		4-Mar-08		4:06:20		65.01		35.5		4-Mar-08		4:07:53		68		34		14-Apr-08		4:25:59		69.8		38.5

		4-Mar-08		6:07:10		66.2		47.5		4-Mar-08		6:06:20		64.4		35		4-Mar-08		6:07:53		67.4		34.5		14-Apr-08		6:25:59		69.2		38.5

		4-Mar-08		8:07:10		66.2		47.5		4-Mar-08		8:06:20		65.01		34		4-Mar-08		8:07:53		69.2		34		14-Apr-08		8:25:59		68.61		39

		4-Mar-08		10:07:10		66.2		46		4-Mar-08		10:06:20		67.4		35.5		4-Mar-08		10:07:53		72.21		36		14-Apr-08		10:25:59		71		40.5

		4-Mar-08		12:07:10		66.81		47		4-Mar-08		12:06:20		68		34.5		4-Mar-08		12:07:53		71		40.5		14-Apr-08		12:25:59		72.8		40

		4-Mar-08		14:07:10		66.81		46		4-Mar-08		14:06:20		68		29		4-Mar-08		14:07:53		71		40		14-Apr-08		14:25:59		74.01		39

		4-Mar-08		16:07:10		66.81		47		4-Mar-08		16:06:20		68.61		31		4-Mar-08		16:07:53		70.41		37		14-Apr-08		16:25:59		74.01		39

		4-Mar-08		18:07:10		66.2		47.5		4-Mar-08		18:06:20		68		30		4-Mar-08		18:07:53		70.41		34.5		14-Apr-08		18:25:59		72.8		39.5

		4-Mar-08		20:07:10		66.2		45.5		4-Mar-08		20:06:20		67.4		30		4-Mar-08		20:07:53		69.8		34		14-Apr-08		20:25:59		72.8		40

		4-Mar-08		22:07:10		65.6		48		4-Mar-08		22:06:20		66.2		32		4-Mar-08		22:07:53		70.41		34		14-Apr-08		22:25:59		71.6		39.5

		5-Mar-08		0:07:10		65.6		47		5-Mar-08		0:06:20		67.4		33		5-Mar-08		0:07:53		71		33.5		15-Apr-08		0:25:59		71		39.5

		5-Mar-08		2:07:10		65.6		47.5		5-Mar-08		2:06:20		65.6		34.5		5-Mar-08		2:07:53		69.8		33.5		15-Apr-08		2:25:59		69.8		39

		5-Mar-08		4:07:10		65.6		48.5		5-Mar-08		4:06:20		65.01		35.5		5-Mar-08		4:07:53		68.61		33.5		15-Apr-08		4:25:59		68.61		39

		5-Mar-08		6:07:10		66.2		49		5-Mar-08		6:06:20		64.4		35		5-Mar-08		6:07:53		67.4		34		15-Apr-08		6:25:59		69.2		39

		5-Mar-08		8:07:10		66.2		47		5-Mar-08		8:06:20		65.01		34.5		5-Mar-08		8:07:53		69.8		33		15-Apr-08		8:25:59		70.41		39.5

		5-Mar-08		10:07:10		66.2		46		5-Mar-08		10:06:20		66.81		37.5		5-Mar-08		10:07:53		72.21		34.5		15-Apr-08		10:25:59		72.8		40.5

		5-Mar-08		12:07:10		66.81		46.5		5-Mar-08		12:06:20		68		38		5-Mar-08		12:07:53		71		42.5		15-Apr-08		12:25:59		74.6		38.5

		5-Mar-08		14:07:10		66.81		47		5-Mar-08		14:06:20		68		38		5-Mar-08		14:07:53		71		36.5		15-Apr-08		14:25:59		74.6		37

		5-Mar-08		16:07:10		66.81		45.5		5-Mar-08		16:06:20		68		35.5		5-Mar-08		16:07:53		70.41		37		15-Apr-08		16:25:59		74.01		36.5

		5-Mar-08		18:07:10		66.81		47.5		5-Mar-08		18:06:20		68		38.5		5-Mar-08		18:07:53		69.8		43		15-Apr-08		18:25:59		73.4		35

		5-Mar-08		20:07:10		66.2		48		5-Mar-08		20:06:20		67.4		42		5-Mar-08		20:07:53		70.41		41.5		15-Apr-08		20:25:59		72.21		34

		5-Mar-08		22:07:10		66.2		48		5-Mar-08		22:06:20		67.4		36.5		5-Mar-08		22:07:53		70.41		39		15-Apr-08		22:25:59		71		33.5

		6-Mar-08		0:07:10		65.6		48.5		6-Mar-08		0:06:20		66.2		38		6-Mar-08		0:07:53		70.41		36.5		16-Apr-08		0:25:59		69.2		33.5

		6-Mar-08		2:07:10		65.6		48.5		6-Mar-08		2:06:20		65.6		38		6-Mar-08		2:07:53		69.8		36		16-Apr-08		2:25:59		68		34

		6-Mar-08		4:07:10		65.6		48.5		6-Mar-08		4:06:20		65.01		37.5		6-Mar-08		4:07:53		68.61		36		16-Apr-08		4:25:59		67.4		35

		6-Mar-08		6:07:10		66.2		48.5		6-Mar-08		6:06:20		65.01		36		6-Mar-08		6:07:53		67.4		36		16-Apr-08		6:25:59		68		34

		6-Mar-08		8:07:10		66.2		47.5		6-Mar-08		8:06:20		65.01		35		6-Mar-08		8:07:53		70.41		34.5		16-Apr-08		8:25:59		70.41		34.5

		6-Mar-08		10:07:10		66.81		46		6-Mar-08		10:06:20		67.4		36.5		6-Mar-08		10:07:53		71.6		35		16-Apr-08		10:25:59		72.8		35

		6-Mar-08		12:07:10		66.81		46.5		6-Mar-08		12:06:20		68		34.5		6-Mar-08		12:07:53		70.41		44.5		16-Apr-08		12:25:59		74.6		34.5

		6-Mar-08		14:07:10		66.81		46.5		6-Mar-08		14:06:20		68.61		28		6-Mar-08		14:07:53		70.41		41		16-Apr-08		14:25:59		74.6		33.5

		6-Mar-08		16:07:10		66.81		43.5		6-Mar-08		16:06:20		68.61		25		6-Mar-08		16:07:53		70.41		39		16-Apr-08		16:25:59		74.01		33.5

		6-Mar-08		18:07:10		66.2		41.5		6-Mar-08		18:06:20		68		29.5		6-Mar-08		18:07:53		69.8		38.5		16-Apr-08		18:25:59		73.4		33

		6-Mar-08		20:07:10		66.2		48.5		6-Mar-08		20:06:20		66.81		37.5		6-Mar-08		20:07:53		71		37.5		16-Apr-08		20:25:59		72.8		32

		6-Mar-08		22:07:10		65.6		47		6-Mar-08		22:06:20		66.81		40		6-Mar-08		22:07:53		71.6		37		16-Apr-08		22:25:59		71.6		32

		7-Mar-08		0:07:10		65.6		48.5		7-Mar-08		0:06:20		66.2		39		7-Mar-08		0:07:53		70.41		36.5		17-Apr-08		0:25:59		69.8		32.5

		7-Mar-08		2:07:10		65.6		48.5		7-Mar-08		2:06:20		65.01		38		7-Mar-08		2:07:53		69.2		36		17-Apr-08		2:25:59		68.61		34

		7-Mar-08		4:07:10		65.6		42.5		7-Mar-08		4:06:20		64.4		37.5		7-Mar-08		4:07:53		68.61		36		17-Apr-08		4:25:59		68		34.5

		7-Mar-08		6:07:10		65.6		47		7-Mar-08		6:06:20		63.8		36.5		7-Mar-08		6:07:53		67.4		36		17-Apr-08		6:25:59		69.2		34

		7-Mar-08		8:07:10		66.2		48		7-Mar-08		8:06:20		65.01		35.5		7-Mar-08		8:07:53		70.41		35		17-Apr-08		8:25:59		71		34.5

		7-Mar-08		10:07:10		65.6		46.5		7-Mar-08		10:06:20		66.81		37.5		7-Mar-08		10:07:53		71.6		33.5		17-Apr-08		10:25:59		74.01		35

		7-Mar-08		12:07:10		66.2		48		7-Mar-08		12:06:20		67.4		39.5		7-Mar-08		12:07:53		71		39.5		17-Apr-08		12:25:59		75.2		34.5

		7-Mar-08		14:07:10		66.2		43.5		7-Mar-08		14:06:20		68		39		7-Mar-08		14:07:53		71.6		38.5		17-Apr-08		14:25:59		75.2		34.5

		7-Mar-08		16:07:10		66.81		47.5		7-Mar-08		16:06:20		68		40		7-Mar-08		16:07:53		70.41		36.5		17-Apr-08		16:25:59		74.6		34.5

		7-Mar-08		18:07:10		66.2		48		7-Mar-08		18:06:20		68		36.5		7-Mar-08		18:07:53		70.41		35		17-Apr-08		18:25:59		74.01		34

		7-Mar-08		20:07:10		66.2		48		7-Mar-08		20:06:20		66.81		40.5		7-Mar-08		20:07:53		69.8		36		17-Apr-08		20:25:59		74.01		35

		7-Mar-08		22:07:10		65.6		48.5		7-Mar-08		22:06:20		66.81		39		7-Mar-08		22:07:53		70.41		38		17-Apr-08		22:25:59		73.4		35

		8-Mar-08		0:07:10		65.6		43		8-Mar-08		0:06:20		66.2		40.5		8-Mar-08		0:07:53		69.8		37		18-Apr-08		0:25:59		71.6		35

		8-Mar-08		2:07:10		65.6		48.5		8-Mar-08		2:06:20		65.01		41.5		8-Mar-08		2:07:53		69.2		37		18-Apr-08		2:25:59		70.41		36

		8-Mar-08		4:07:10		65.6		48		8-Mar-08		4:06:20		64.4		39.5		8-Mar-08		4:07:53		68		37		18-Apr-08		4:25:59		69.2		36

		8-Mar-08		6:07:10		65.6		48.5		8-Mar-08		6:06:20		63.8		38.5		8-Mar-08		6:07:53		67.4		36.5		18-Apr-08		6:25:59		69.8		36

		8-Mar-08		8:07:10		66.2		47.5		8-Mar-08		8:06:20		65.6		37		8-Mar-08		8:07:53		69.2		36		18-Apr-08		8:25:59		71.6		36

		8-Mar-08		10:07:10		66.2		42		8-Mar-08		10:06:20		67.4		39.5		8-Mar-08		10:07:53		71		38.5		18-Apr-08		10:25:59		74.01		37.5

		8-Mar-08		12:07:10		66.2		48		8-Mar-08		12:06:20		68		38.5		8-Mar-08		12:07:53		70.41		43		18-Apr-08		12:25:59		75.2		39

		8-Mar-08		14:07:10		66.2		47		8-Mar-08		14:06:20		67.4		38.5		8-Mar-08		14:07:53		71		36		18-Apr-08		14:25:59		75.2		38

		8-Mar-08		16:07:10		66.2		48		8-Mar-08		16:06:20		67.4		40		8-Mar-08		16:07:53		70.41		42		18-Apr-08		16:25:59		75.2		38

		8-Mar-08		18:07:10		66.2		49		8-Mar-08		18:06:20		67.4		44		8-Mar-08		18:07:53		70.41		42		18-Apr-08		18:25:59		74.6		37

		8-Mar-08		20:07:10		65.6		43.5		8-Mar-08		20:06:20		66.81		41.5		8-Mar-08		20:07:53		69.8		40		18-Apr-08		20:25:59		74.6		38

		8-Mar-08		22:07:10		65.6		48.5		8-Mar-08		22:06:20		66.2		45.5		8-Mar-08		22:07:53		70.41		40.5		18-Apr-08		22:25:59		73.4		37.5

		9-Mar-08		0:07:10		65.6		48.5		9-Mar-08		0:06:20		66.81		44.5		9-Mar-08		0:07:53		70.41		40		19-Apr-08		0:25:59		71.6		37.5

		9-Mar-08		2:07:10		65.6		47		9-Mar-08		2:06:20		66.2		43.5		9-Mar-08		2:07:53		69.8		39		19-Apr-08		2:25:59		71		38.5

		9-Mar-08		4:07:10		65.6		48		9-Mar-08		4:06:20		65.01		42.5		9-Mar-08		4:07:53		69.2		38.5		19-Apr-08		4:25:59		70.41		39.5

		9-Mar-08		6:07:10		65.6		42		9-Mar-08		6:06:20		64.4		42		9-Mar-08		6:07:53		68.61		38.5		19-Apr-08		6:25:59		71.6		39.5

		9-Mar-08		8:07:10		65.6		48		9-Mar-08		8:06:20		65.01		39		9-Mar-08		8:07:53		71		37		19-Apr-08		8:25:59		72.21		39

		9-Mar-08		10:07:10		66.2		48.5		9-Mar-08		10:06:20		66.81		43.5		9-Mar-08		10:07:53		71		34.5		19-Apr-08		10:25:59		73.4		40

		9-Mar-08		12:07:10		66.2		48.5		9-Mar-08		12:06:20		67.4		43		9-Mar-08		12:07:53		71.6		46		19-Apr-08		12:25:59		74.01		40.5

		9-Mar-08		14:07:10		66.2		47.5		9-Mar-08		14:06:20		68		35		9-Mar-08		14:07:53		71		43		19-Apr-08		14:25:59		75.2		41

		9-Mar-08		16:07:10		66.2		44		9-Mar-08		16:06:20		67.4		37.5		9-Mar-08		16:07:53		71		36.5		19-Apr-08		16:25:59		74.6		39.5

		9-Mar-08		18:07:10		66.2		47.5		9-Mar-08		18:06:20		67.4		31.5		9-Mar-08		18:07:53		69.8		36		19-Apr-08		18:25:59		74.01		38.5

		9-Mar-08		20:07:10		66.2		47.5		9-Mar-08		20:06:20		67.4		44.5		9-Mar-08		20:07:53		69.8		42		19-Apr-08		20:25:59		74.01		38.5

		9-Mar-08		22:07:10		65.6		48.5		9-Mar-08		22:06:20		66.2		47.5		9-Mar-08		22:07:53		71.6		40		19-Apr-08		22:25:59		72.8		37.5

		10-Mar-08		0:07:10		65.6		48.5		10-Mar-08		0:06:20		66.81		44.5		10-Mar-08		0:07:53		71		39.5		20-Apr-08		0:25:59		71		38

		10-Mar-08		2:07:10		65.6		48		10-Mar-08		2:06:20		66.2		44.5		10-Mar-08		2:07:53		70.41		39		20-Apr-08		2:25:59		69.8		38

		10-Mar-08		4:07:10		65.6		49		10-Mar-08		4:06:20		65.01		44		10-Mar-08		4:07:53		69.8		38.5		20-Apr-08		4:25:59		68.61		37.5

		10-Mar-08		6:07:10		65.6		49.5		10-Mar-08		6:06:20		64.4		42		10-Mar-08		6:07:53		68.61		38.5		20-Apr-08		6:25:59		68		37.5

		10-Mar-08		8:07:10		65.6		48		10-Mar-08		8:06:20		63.8		40.5		10-Mar-08		8:07:53		68		38		20-Apr-08		8:25:59		67.4		36.5

		10-Mar-08		10:07:10		65.6		48		10-Mar-08		10:06:20		66.2		41.5		10-Mar-08		10:07:53		69.2		39		20-Apr-08		10:25:59		68		37.5

		10-Mar-08		12:07:10		65.6		49		10-Mar-08		12:06:20		66.81		41		10-Mar-08		12:07:53		69.8		40		20-Apr-08		12:25:59		69.2		36.5

		10-Mar-08		14:07:10		66.2		47.5		10-Mar-08		14:06:20		68		37.5		10-Mar-08		14:07:53		70.41		41		20-Apr-08		14:25:59		70.41		33.5

		10-Mar-08		16:07:10		66.2		48		10-Mar-08		16:06:20		68		34.5		10-Mar-08		16:07:53		69.8		41.5		20-Apr-08		16:25:59		70.41		33

		10-Mar-08		18:07:10		66.2		48		10-Mar-08		18:06:20		68		33.5		10-Mar-08		18:07:53		70.41		39.5		20-Apr-08		18:25:59		70.41		32

		10-Mar-08		20:07:10		66.2		48		10-Mar-08		20:06:20		67.4		43		10-Mar-08		20:07:53		71		42		20-Apr-08		20:25:59		69.8		32

		10-Mar-08		22:07:10		65.6		49		10-Mar-08		22:06:20		66.2		45		10-Mar-08		22:07:53		71.6		40.5		20-Apr-08		22:25:59		68.61		33

		11-Mar-08		0:07:10		65.6		49		11-Mar-08		0:06:20		66.81		44.5		11-Mar-08		0:07:53		71		39.5		21-Apr-08		0:25:59		67.4		33.5

		11-Mar-08		2:07:10		65.6		49		11-Mar-08		2:06:20		66.2		45		11-Mar-08		2:07:53		70.41		39.5		21-Apr-08		2:25:59		66.81		34

		11-Mar-08		4:07:10		65.6		48.5		11-Mar-08		4:06:20		65.6		45		11-Mar-08		4:07:53		69.8		39		21-Apr-08		4:25:59		65.6		35

		11-Mar-08		6:07:10		65.6		48		11-Mar-08		6:06:20		65.01		45		11-Mar-08		6:07:53		71		39.5		21-Apr-08		6:25:59		65.01		35.5

		11-Mar-08		8:07:10		66.2		48		11-Mar-08		8:06:20		66.81		43		11-Mar-08		8:07:53		71.6		35.5		21-Apr-08		8:25:59		64.4		36.5

		11-Mar-08		10:07:10		66.81		47.5		11-Mar-08		10:06:20		67.4		43.5		11-Mar-08		10:07:53		71		37		21-Apr-08		10:25:59		65.6		37.5

		11-Mar-08		12:07:10		66.2		48		11-Mar-08		12:06:20		67.4		44		11-Mar-08		12:07:53		71		43		21-Apr-08		12:25:59		66.81		36

		11-Mar-08		14:07:10		66.81		52.5		11-Mar-08		14:06:20		68.61		52		11-Mar-08		14:07:53		70.41		48.5		21-Apr-08		14:25:59		68.61		36

		11-Mar-08		16:07:10		66.2		49.5		11-Mar-08		16:06:20		67.4		49		11-Mar-08		16:07:53		70.41		53		21-Apr-08		16:25:59		69.8		34.5

		11-Mar-08		18:07:10		66.2		49		11-Mar-08		18:06:20		68		45		11-Mar-08		18:07:53		71		42		21-Apr-08		18:25:59		69.8		33

		11-Mar-08		20:07:10		65.6		48.5		11-Mar-08		20:06:20		66.81		46		11-Mar-08		20:07:53		70.41		43		21-Apr-08		20:25:59		69.2		33

		11-Mar-08		22:07:10		65.6		48.5		11-Mar-08		22:06:20		67.4		45.5		11-Mar-08		22:07:53		71		42		21-Apr-08		22:25:59		68.61		34.5

		12-Mar-08		0:07:10		65.6		49		12-Mar-08		0:06:20		66.81		45.5		12-Mar-08		0:07:53		71.6		40.5		22-Apr-08		0:25:59		67.4		34.5

		12-Mar-08		2:07:10		65.6		49		12-Mar-08		2:06:20		66.81		45		12-Mar-08		2:07:53		70.41		40.5		22-Apr-08		2:25:59		66.2		35

		12-Mar-08		4:07:10		65.6		49		12-Mar-08		4:06:20		65.6		44.5		12-Mar-08		4:07:53		69.8		39.5		22-Apr-08		4:25:59		65.6		36

		12-Mar-08		6:07:10		65.6		49		12-Mar-08		6:06:20		65.01		44		12-Mar-08		6:07:53		70.41		39.5		22-Apr-08		6:25:59		66.81		34

		12-Mar-08		8:07:10		66.2		48		12-Mar-08		8:06:20		66.2		42.5		12-Mar-08		8:07:53		71		40.5		22-Apr-08		8:25:59		68		34.5

		12-Mar-08		10:07:10		66.2		49		12-Mar-08		10:06:20		66.81		50		12-Mar-08		10:07:53		70.41		45		22-Apr-08		10:25:59		72.21		36

		12-Mar-08		12:07:10		66.2		50		12-Mar-08		12:06:20		66.81		48		12-Mar-08		12:07:53		71.6		50		22-Apr-08		12:25:59		73.4		35.5

		12-Mar-08		14:07:10		66.2		49.5		12-Mar-08		14:06:20		68		50.5		12-Mar-08		14:07:53		71		41.5		22-Apr-08		14:25:59		73.4		35.5

		12-Mar-08		16:07:10		66.2		51.5		12-Mar-08		16:06:20		66.81		59.5		12-Mar-08		16:07:53		71		50.5		22-Apr-08		16:25:59		73.4		35.5

		12-Mar-08		18:07:10		66.2		51.5		12-Mar-08		18:06:20		67.4		48.5		12-Mar-08		18:07:53		70.41		50		22-Apr-08		18:25:59		72.8		35

		12-Mar-08		20:07:10		65.6		50		12-Mar-08		20:06:20		67.4		51.5		12-Mar-08		20:07:53		70.41		48		22-Apr-08		20:25:59		72.21		34.5

		12-Mar-08		22:07:10		65.6		49		12-Mar-08		22:06:20		67.4		49		12-Mar-08		22:07:53		70.41		44.5		22-Apr-08		22:25:59		71		34

		13-Mar-08		0:07:10		65.6		49		13-Mar-08		0:06:20		66.81		47.5		13-Mar-08		0:07:53		70.41		42		23-Apr-08		0:25:59		69.8		34

		13-Mar-08		2:07:10		65.6		49		13-Mar-08		2:06:20		65.6		46		13-Mar-08		2:07:53		70.41		41		23-Apr-08		2:25:59		68.61		34.5

		13-Mar-08		4:07:10		65.6		49.5		13-Mar-08		4:06:20		65.01		47		13-Mar-08		4:07:53		69.2		41		23-Apr-08		4:25:59		67.4		35

		13-Mar-08		6:07:10		65.6		49		13-Mar-08		6:06:20		65.6		48.5		13-Mar-08		6:07:53		70.41		42.5		23-Apr-08		6:25:59		68.61		34.5

		13-Mar-08		8:07:10		66.2		48		13-Mar-08		8:06:20		67.4		46.5		13-Mar-08		8:07:53		71		44		23-Apr-08		8:25:59		70.41		34.5

		13-Mar-08		10:07:10		66.2		48		13-Mar-08		10:06:20		66.81		46.5		13-Mar-08		10:07:53		71.6		41.5		23-Apr-08		10:25:59		71.6		35.5

		13-Mar-08		12:07:10		66.2		48.5		13-Mar-08		12:06:20		66.81		47.5		13-Mar-08		12:07:53		71		43		23-Apr-08		12:25:59		72.21		37.5

		13-Mar-08		14:07:10		66.81		49		13-Mar-08		14:06:20		67.4		46.5		13-Mar-08		14:07:53		71		46.5		23-Apr-08		14:25:59		72.8		39

		13-Mar-08		16:07:10		66.81		49.5		13-Mar-08		16:06:20		67.4		52		13-Mar-08		16:07:53		70.41		41.5		23-Apr-08		16:25:59		73.4		40.5

		13-Mar-08		18:07:10		66.2		49		13-Mar-08		18:06:20		66.81		49		13-Mar-08		18:07:53		71		44.5		23-Apr-08		18:25:59		73.4		40.5

		13-Mar-08		20:07:10		66.2		48.5		13-Mar-08		20:06:20		66.2		48		13-Mar-08		20:07:53		71		43.5		23-Apr-08		20:25:59		72.8		41.5

		13-Mar-08		22:07:10		66.2		49		13-Mar-08		22:06:20		67.4		46.5		13-Mar-08		22:07:53		72.21		41.5		23-Apr-08		22:25:59		71.6		41.5

		14-Mar-08		0:07:10		66.2		49.5		14-Mar-08		0:06:20		67.4		51		14-Mar-08		0:07:53		71.6		42		24-Apr-08		0:25:59		70.41		42

		14-Mar-08		2:07:10		65.6		50.5		14-Mar-08		2:06:20		67.4		52		14-Mar-08		2:07:53		71.6		43		24-Apr-08		2:25:59		69.2		42

		14-Mar-08		4:07:10		65.6		50.5		14-Mar-08		4:06:20		66.81		53		14-Mar-08		4:07:53		71.6		43.5		24-Apr-08		4:25:59		68.61		42.5

		14-Mar-08		6:07:10		66.2		50.5		14-Mar-08		6:06:20		67.4		53.5		14-Mar-08		6:07:53		71		40.5		24-Apr-08		6:25:59		69.2		42

		14-Mar-08		8:07:10		66.2		49.5		14-Mar-08		8:06:20		66.81		52		14-Mar-08		8:07:53		70.41		50		24-Apr-08		8:25:59		71		42

		14-Mar-08		10:07:10		66.2		51		14-Mar-08		10:06:20		67.4		52.5		14-Mar-08		10:07:53		71		51.5		24-Apr-08		10:25:59		72.8		43

		14-Mar-08		12:07:10		66.2		49.5		14-Mar-08		12:06:20		68		48		14-Mar-08		12:07:53		71		50.5		24-Apr-08		12:25:59		74.01		43

		14-Mar-08		14:07:10		66.81		48.5		14-Mar-08		14:06:20		68.61		47.5		14-Mar-08		14:07:53		71		52.5		24-Apr-08		14:25:59		74.01		40.5

		14-Mar-08		16:07:10		66.2		48		14-Mar-08		16:06:20		68		45.5		14-Mar-08		16:07:53		70.41		44		24-Apr-08		16:25:59		74.01		38.5

		14-Mar-08		18:07:10		65.6		48.5		14-Mar-08		18:06:20		66.81		46		14-Mar-08		18:07:53		70.41		43		24-Apr-08		18:25:59		72.8		36.5

		14-Mar-08		20:07:10		65.6		48.5		14-Mar-08		20:06:20		67.4		45		14-Mar-08		20:07:53		69.8		43		24-Apr-08		20:25:59		72.8		36.5

		14-Mar-08		22:07:10		65.6		48.5		14-Mar-08		22:06:20		67.4		45.5		14-Mar-08		22:07:53		71		41		24-Apr-08		22:25:59		71.6		35

		15-Mar-08		0:07:10		65.6		49		15-Mar-08		0:06:20		66.2		45		15-Mar-08		0:07:53		70.41		40.5		25-Apr-08		0:25:59		69.8		35

		15-Mar-08		2:07:10		65.6		49		15-Mar-08		2:06:20		65.6		44		15-Mar-08		2:07:53		69.8		39.5		25-Apr-08		2:25:59		68		35.5

		15-Mar-08		4:07:10		65.6		49		15-Mar-08		4:06:20		65.01		42.5		15-Mar-08		4:07:53		69.2		39		25-Apr-08		4:25:59		66.81		37

		15-Mar-08		6:07:10		66.2		48.5		15-Mar-08		6:06:20		65.6		44.5		15-Mar-08		6:07:53		69.2		42		25-Apr-08		6:25:59		68		36.5

		15-Mar-08		8:07:10		66.2		47.5		15-Mar-08		8:06:20		66.2		44		15-Mar-08		8:07:53		71		42		25-Apr-08		8:25:59		69.2		36.5

		15-Mar-08		10:07:10		66.81		48		15-Mar-08		10:06:20		67.4		46.5		15-Mar-08		10:07:53		71		47		25-Apr-08		10:25:59		72.8		38.5

		15-Mar-08		12:07:10		66.2		48		15-Mar-08		12:06:20		67.4		46.5		15-Mar-08		12:07:53		71		46.5		25-Apr-08		12:25:59		74.01		37

		15-Mar-08		14:07:10		66.2		48		15-Mar-08		14:06:20		67.4		41		15-Mar-08		14:07:53		71.6		44		25-Apr-08		14:25:59		74.6		36.5

		15-Mar-08		16:07:10		66.2		47.5		15-Mar-08		16:06:20		66.81		38		15-Mar-08		16:07:53		70.41		39.5		25-Apr-08		16:25:59		74.6		37.5

		15-Mar-08		18:07:10		65.6		48		15-Mar-08		18:06:20		66.81		40		15-Mar-08		18:07:53		69.8		38.5		25-Apr-08		18:25:59		74.01		35.5

		15-Mar-08		20:07:10		65.6		42.5		15-Mar-08		20:06:20		65.6		41		15-Mar-08		20:07:53		69.8		37.5		25-Apr-08		20:25:59		74.6		35.5

		15-Mar-08		22:07:10		65.6		49		15-Mar-08		22:06:20		65.01		41.5		15-Mar-08		22:07:53		69.2		37		25-Apr-08		22:25:59		74.01		35.5

		16-Mar-08		0:07:10		65.01		49		16-Mar-08		0:06:20		64.4		42		16-Mar-08		0:07:53		68.61		38		26-Apr-08		0:25:59		72.8		35

		16-Mar-08		2:07:10		65.01		50		16-Mar-08		2:06:20		63.8		43.5		16-Mar-08		2:07:53		68		38.5		26-Apr-08		2:25:59		71		36

		16-Mar-08		4:07:10		65.01		49		16-Mar-08		4:06:20		63.21		44		16-Mar-08		4:07:53		67.4		39		26-Apr-08		4:25:59		69.8		36.5

		16-Mar-08		6:07:10		65.01		49.5		16-Mar-08		6:06:20		63.21		43		16-Mar-08		6:07:53		68		39		26-Apr-08		6:25:59		70.41		37.5

		16-Mar-08		8:07:10		65.6		48		16-Mar-08		8:06:20		62		41.5		16-Mar-08		8:07:53		70.41		36.5		26-Apr-08		8:25:59		72.21		37

		16-Mar-08		10:07:10		65.6		49		16-Mar-08		10:06:20		64.4		44		16-Mar-08		10:07:53		71.6		38.5		26-Apr-08		10:25:59		74.01		38

		16-Mar-08		12:07:10		65.6		44		16-Mar-08		12:06:20		65.6		38		16-Mar-08		12:07:53		71		34		26-Apr-08		12:25:59		75.2		37.5

		16-Mar-08		14:07:10		65.6		38		16-Mar-08		14:06:20		66.2		34.5		16-Mar-08		14:07:53		70.41		33.5		26-Apr-08		14:25:59		73.4		34

		16-Mar-08		16:07:10		65.6		46		16-Mar-08		16:06:20		67.4		33		16-Mar-08		16:07:53		69.8		31.5		26-Apr-08		16:25:59		73.4		35.5

		16-Mar-08		18:07:10		65.6		41		16-Mar-08		18:06:20		66.2		36		16-Mar-08		18:07:53		69.2		34.5		26-Apr-08		18:25:59		73.4		37

		16-Mar-08		20:07:10		65.6		44		16-Mar-08		20:06:20		65.6		40		16-Mar-08		20:07:53		69.2		37		26-Apr-08		20:25:59		73.4		37

		16-Mar-08		22:07:10		65.6		48.5		16-Mar-08		22:06:20		65.6		37.5		16-Mar-08		22:07:53		68.61		36.5		26-Apr-08		22:25:59		72.8		36.5

		17-Mar-08		0:07:10		65.6		47.5		17-Mar-08		0:06:20		65.01		36		17-Mar-08		0:07:53		68		36		27-Apr-08		0:25:59		72.21		36.5

		17-Mar-08		2:07:10		65.6		47		17-Mar-08		2:06:20		64.4		34.5		17-Mar-08		2:07:53		67.4		35		27-Apr-08		2:25:59		71		36

		17-Mar-08		4:07:10		65.6		47.5		17-Mar-08		4:06:20		64.4		34		17-Mar-08		4:07:53		66.81		35		27-Apr-08		4:25:59		70.41		36.5

		17-Mar-08		6:07:10		65.01		38		17-Mar-08		6:06:20		64.4		34.5		17-Mar-08		6:07:53		66.2		35		27-Apr-08		6:25:59		69.8		36

		17-Mar-08		8:07:10		65.01		46.5		17-Mar-08		8:06:20		63.8		34.5		17-Mar-08		8:07:53		67.4		34.5		27-Apr-08		8:25:59		69.8		37.5

		17-Mar-08		10:07:10		65.6		38.5		17-Mar-08		10:06:20		65.01		34		17-Mar-08		10:07:53		68.61		33.5		27-Apr-08		10:25:59		71		40

		17-Mar-08		12:07:10		65.6		33.5		17-Mar-08		12:06:20		67.4		30		17-Mar-08		12:07:53		69.8		31.5		27-Apr-08		12:25:59		72.8		39.5

		17-Mar-08		14:07:10		65.6		42		17-Mar-08		14:06:20		66.81		23		17-Mar-08		14:07:53		69.8		30		27-Apr-08		14:25:59		74.01		38.5

		17-Mar-08		16:07:10		65.6		40		17-Mar-08		16:06:20		66.81		22		17-Mar-08		16:07:53		69.8		29		27-Apr-08		16:25:59		73.4		40.5

		17-Mar-08		18:07:10		65.6		36.5		17-Mar-08		18:06:20		66.2		31.5		17-Mar-08		18:07:53		69.8		31		27-Apr-08		18:25:59		73.4		40.5

		17-Mar-08		20:07:10		65.6		47.5		17-Mar-08		20:06:20		66.2		34.5		17-Mar-08		20:07:53		69.8		33		27-Apr-08		20:25:59		73.4		40.5

		17-Mar-08		22:07:10		65.6		47.5		17-Mar-08		22:06:20		66.81		35		17-Mar-08		22:07:53		70.41		34		27-Apr-08		22:25:59		73.4		38.5

		18-Mar-08		0:07:10		65.6		48		18-Mar-08		0:06:20		66.2		36		18-Mar-08		0:07:53		69.8		33.5		28-Apr-08		0:25:59		72.8		37.5

		18-Mar-08		2:07:10		65.6		39		18-Mar-08		2:06:20		65.01		37		18-Mar-08		2:07:53		68.61		34		28-Apr-08		2:25:59		72.21		39.5

		18-Mar-08		4:07:10		65.6		48		18-Mar-08		4:06:20		65.01		37.5		18-Mar-08		4:07:53		68		35		28-Apr-08		4:25:59		71.6		39.5

		18-Mar-08		6:07:10		66.2		47		18-Mar-08		6:06:20		65.01		37.5		18-Mar-08		6:07:53		69.2		34.5		28-Apr-08		6:25:59		70.41		39.5

		18-Mar-08		8:07:10		66.81		42		18-Mar-08		8:06:20		66.2		36.5		18-Mar-08		8:07:53		71.6		34.5		28-Apr-08		8:25:59		69.8		39.5

		18-Mar-08		10:07:10		66.2		38.5		18-Mar-08		10:06:20		67.4		35.5		18-Mar-08		10:07:53		71.6		39.5		28-Apr-08		10:25:59		71.6		41.5

		18-Mar-08		12:07:10		66.2		42		18-Mar-08		12:06:20		66.81		34.5		18-Mar-08		12:07:53		71.6		37		28-Apr-08		12:25:59		74.01		40

		18-Mar-08		14:07:10		66.81		46		18-Mar-08		14:06:20		66.2		39		18-Mar-08		14:07:53		71.6		34.5		28-Apr-08		14:25:59		74.01		39.5

		18-Mar-08		16:07:10		66.81		47.5		18-Mar-08		16:06:20		65.6		45		18-Mar-08		16:07:53		71.6		40		28-Apr-08		16:25:59		73.4		41.5

		18-Mar-08		18:07:10		66.81		46.5		18-Mar-08		18:06:20		65.6		45.5		18-Mar-08		18:07:53		70.41		37.5		28-Apr-08		18:25:59		73.4		41

		18-Mar-08		20:07:10		66.2		47		18-Mar-08		20:06:20		65.6		47		18-Mar-08		20:07:53		70.41		42.5		28-Apr-08		20:25:59		73.4		40.5

		18-Mar-08		22:07:10		66.2		47.5		18-Mar-08		22:06:20		65.01		47		18-Mar-08		22:07:53		71.6		40.5		28-Apr-08		22:25:59		73.4		39.5

		19-Mar-08		0:07:10		65.6		48		19-Mar-08		0:06:20		65.6		44.5		19-Mar-08		0:07:53		72.21		39		29-Apr-08		0:25:59		72.8		38.5

		19-Mar-08		2:07:10		65.6		48.5		19-Mar-08		2:06:20		64.4		49.5		19-Mar-08		2:07:53		71.6		39		29-Apr-08		2:25:59		71.6		38.5

		19-Mar-08		4:07:10		65.6		48		19-Mar-08		4:06:20		65.6		46.5		19-Mar-08		4:07:53		71		39		29-Apr-08		4:25:59		70.41		38.5

		19-Mar-08		6:07:10		66.2		47		19-Mar-08		6:06:20		65.6		45.5		19-Mar-08		6:07:53		71.6		39.5		29-Apr-08		6:25:59		70.41		38

		19-Mar-08		8:07:10		66.2		47		19-Mar-08		8:06:20		65.01		47		19-Mar-08		8:07:53		70.41		38		29-Apr-08		8:25:59		69.8		39.5

		19-Mar-08		10:07:10		66.2		47		19-Mar-08		10:06:20		66.2		47		19-Mar-08		10:07:53		70.41		37.5		29-Apr-08		10:25:59		72.8		40.5

		19-Mar-08		12:07:10		66.81		48.5		19-Mar-08		12:06:20		66.2		48		19-Mar-08		12:07:53		71.6		50.5		29-Apr-08		12:25:59		73.4		42.5

		19-Mar-08		14:07:10		66.81		49		19-Mar-08		14:06:20		66.2		51		19-Mar-08		14:07:53		71		41		29-Apr-08		14:25:59		73.4		43

		19-Mar-08		16:07:10		66.81		46.5		19-Mar-08		16:06:20		66.2		44		19-Mar-08		16:07:53		71.6		42.5		29-Apr-08		16:25:59		74.01		42.5

		19-Mar-08		18:07:10		66.2		47.5		19-Mar-08		18:06:20		66.2		45		19-Mar-08		18:07:53		70.41		40		29-Apr-08		18:25:59		74.01		41

		19-Mar-08		20:07:10		66.2		49		19-Mar-08		20:06:20		65.01		51.5		19-Mar-08		20:07:53		70.41		45		29-Apr-08		20:25:59		74.6		41

		19-Mar-08		22:07:10		65.6		48		19-Mar-08		22:06:20		65.6		52.5		19-Mar-08		22:07:53		71		44.5		29-Apr-08		22:25:59		74.01		40

		20-Mar-08		0:07:10		65.6		47		20-Mar-08		0:06:20		65.01		50.5		20-Mar-08		0:07:53		71		41.5		30-Apr-08		0:25:59		72.8		36.5

		20-Mar-08		2:07:10		65.6		48.5		20-Mar-08		2:06:20		65.6		47.5		20-Mar-08		2:07:53		71		40		30-Apr-08		2:25:59		71		36

		20-Mar-08		4:07:10		65.6		48.5		20-Mar-08		4:06:20		65.01		44.5		20-Mar-08		4:07:53		70.41		39		30-Apr-08		4:25:59		70.41		36

		20-Mar-08		6:07:10		65.6		41		20-Mar-08		6:06:20		64.4		43.5		20-Mar-08		6:07:53		70.41		38.5		30-Apr-08		6:25:59		70.41		36

		20-Mar-08		8:07:10		66.2		47		20-Mar-08		8:06:20		65.6		45		20-Mar-08		8:07:53		71.6		41		30-Apr-08		8:25:59		71		36

		20-Mar-08		10:07:10		66.2		45		20-Mar-08		10:06:20		65.6		49		20-Mar-08		10:07:53		71		45.5		30-Apr-08		10:25:59		72.8		36

		20-Mar-08		12:07:10		66.2		48		20-Mar-08		12:06:20		65.01		51.5		20-Mar-08		12:07:53		69.8		47		30-Apr-08		12:25:59		72.8		34.5

		20-Mar-08		14:07:10		66.81		47.5		20-Mar-08		14:06:20		65.6		53.5		20-Mar-08		14:07:53		71		51.5		30-Apr-08		14:25:59		73.4		33.5

		20-Mar-08		16:07:10		66.2		50		20-Mar-08		16:06:20		65.6		55.5		20-Mar-08		16:07:53		69.8		50.5		30-Apr-08		16:25:59		73.4		34

		20-Mar-08		18:07:10		66.2		48.5		20-Mar-08		18:06:20		65.6		56		20-Mar-08		18:07:53		69.8		48.5		30-Apr-08		18:25:59		72.8		32

		20-Mar-08		20:07:10		65.6		48.5		20-Mar-08		20:06:20		66.2		46		20-Mar-08		20:07:53		70.41		44		30-Apr-08		20:25:59		73.4		32

		20-Mar-08		22:07:10		65.6		48.5		20-Mar-08		22:06:20		65.6		47.5		20-Mar-08		22:07:53		71		41.5		30-Apr-08		22:25:59		72.21		31

		21-Mar-08		0:07:10		65.6		43		21-Mar-08		0:06:20		65.01		44		21-Mar-08		0:07:53		70.41		40		1-May-08		0:25:59		70.41		31.5

		21-Mar-08		2:07:10		65.6		49		21-Mar-08		2:06:20		65.01		41		21-Mar-08		2:07:53		69.8		38		1-May-08		2:25:59		69.2		31

		21-Mar-08		4:07:10		65.01		39.5		21-Mar-08		4:06:20		64.4		40		21-Mar-08		4:07:53		68.61		37.5		1-May-08		4:25:59		68		31

		21-Mar-08		6:07:10		65.6		48.5		21-Mar-08		6:06:20		64.4		39		21-Mar-08		6:07:53		69.2		37		1-May-08		6:25:59		70.41		30.5

		21-Mar-08		8:07:10		65.6		37.5		21-Mar-08		8:06:20		65.01		37.5		21-Mar-08		8:07:53		71		33		1-May-08		8:25:59		69.2		30

		21-Mar-08		10:07:10		66.2		47		21-Mar-08		10:06:20		66.2		39		21-Mar-08		10:07:53		71		40		1-May-08		10:25:59		71		30

		21-Mar-08		12:07:10		66.2		42.5		21-Mar-08		12:06:20		66.2		32		21-Mar-08		12:07:53		71		37		1-May-08		12:25:59		72.8		29

		21-Mar-08		14:07:10		66.2		46		21-Mar-08		14:06:20		66.81		30.5		21-Mar-08		14:07:53		70.41		31.5		1-May-08		14:25:59		73.4		28

		21-Mar-08		16:07:10		66.2		34.5		21-Mar-08		16:06:20		66.81		33		21-Mar-08		16:07:53		70.41		35.5		1-May-08		16:25:59		72.8		28

		21-Mar-08		18:07:10		66.2		46.5		21-Mar-08		18:06:20		66.2		36		21-Mar-08		18:07:53		70.41		33.5		1-May-08		18:25:59		73.4		29

		21-Mar-08		20:07:10		65.6		40		21-Mar-08		20:06:20		65.6		37		21-Mar-08		20:07:53		70.41		36.5		1-May-08		20:25:59		73.4		29.5

		21-Mar-08		22:07:10		65.6		39		21-Mar-08		22:06:20		65.01		37.5		21-Mar-08		22:07:53		70.41		35		1-May-08		22:25:59		72.8		29.5

		22-Mar-08		0:07:10		65.6		37		22-Mar-08		0:06:20		65.6		35		22-Mar-08		0:07:53		69.8		33.5		2-May-08		0:25:59		71.6		29.5

		22-Mar-08		2:07:10		65.01		36.5		22-Mar-08		2:06:20		65.6		35.5		22-Mar-08		2:07:53		69.2		33.5		2-May-08		2:25:59		70.41		30

		22-Mar-08		4:07:10		65.01		47		22-Mar-08		4:06:20		65.6		35		22-Mar-08		4:07:53		68.61		34		2-May-08		4:25:59		69.2		30

		22-Mar-08		6:07:10		65.6		46		22-Mar-08		6:06:20		65.6		34.5		22-Mar-08		6:07:53		69.2		33.5		2-May-08		6:25:59		71		30.5

		22-Mar-08		8:07:10		65.6		36		22-Mar-08		8:06:20		65.6		34.5		22-Mar-08		8:07:53		71		32.5		2-May-08		8:25:59		69.8		31.5

		22-Mar-08		10:07:10		66.2		41.5		22-Mar-08		10:06:20		65.6		37		22-Mar-08		10:07:53		70.41		34		2-May-08		10:25:59		72.21		32

		22-Mar-08		12:07:10		66.2		42		22-Mar-08		12:06:20		66.81		33.5		22-Mar-08		12:07:53		70.41		32.5		2-May-08		12:25:59		72.8		30.5

		22-Mar-08		14:07:10		66.81		45		22-Mar-08		14:06:20		66.2		33		22-Mar-08		14:07:53		71		33		2-May-08		14:25:59		73.4		28

		22-Mar-08		16:07:10		66.2		41.5		22-Mar-08		16:06:20		65.6		40		22-Mar-08		16:07:53		71		33		2-May-08		16:25:59		74.01		30

		22-Mar-08		18:07:10		66.2		47		22-Mar-08		18:06:20		65.01		40		22-Mar-08		18:07:53		70.41		34.5		2-May-08		18:25:59		72.8		31

		22-Mar-08		20:07:10		65.6		47		22-Mar-08		20:06:20		66.2		43		22-Mar-08		20:07:53		69.8		39.5		2-May-08		20:25:59		74.01		31.5

		22-Mar-08		22:07:10		65.6		47.5		22-Mar-08		22:06:20		65.01		42.5		22-Mar-08		22:07:53		70.41		38.5		2-May-08		22:25:59		74.01		30.5

		23-Mar-08		0:07:10		65.6		47.5		23-Mar-08		0:06:20		65.6		42		23-Mar-08		0:07:53		71		37		3-May-08		0:25:59		73.4		29.5

		23-Mar-08		2:07:10		65.6		40.5		23-Mar-08		2:06:20		65.01		40		23-Mar-08		2:07:53		70.41		36.5		3-May-08		2:25:59		72.21		30.5

		23-Mar-08		4:07:10		65.6		49		23-Mar-08		4:06:20		65.01		38.5		23-Mar-08		4:07:53		69.2		35		3-May-08		4:25:59		70.41		31.5

		23-Mar-08		6:07:10		65.01		38.5		23-Mar-08		6:06:20		65.6		38		23-Mar-08		6:07:53		69.8		35.5		3-May-08		6:25:59		70.41		32

		23-Mar-08		8:07:10		65.6		46		23-Mar-08		8:06:20		65.01		37.5		23-Mar-08		8:07:53		71		34.5		3-May-08		8:25:59		70.41		33.5

		23-Mar-08		10:07:10		65.6		41.5		23-Mar-08		10:06:20		66.2		40.5		23-Mar-08		10:07:53		70.41		34.5		3-May-08		10:25:59		72.8		34.5

		23-Mar-08		12:07:10		66.2		47		23-Mar-08		12:06:20		66.2		42.5		23-Mar-08		12:07:53		69.8		34.5		3-May-08		12:25:59		73.4		34

		23-Mar-08		14:07:10		66.2		42.5		23-Mar-08		14:06:20		65.6		43		23-Mar-08		14:07:53		70.41		43.5		3-May-08		14:25:59		73.4		35.5

		23-Mar-08		16:07:10		66.2		36		23-Mar-08		16:06:20		65.6		36		23-Mar-08		16:07:53		71		38.5		3-May-08		16:25:59		74.01		35

		23-Mar-08		18:07:10		66.2		43.5		23-Mar-08		18:06:20		66.2		42		23-Mar-08		18:07:53		70.41		40		3-May-08		18:25:59		73.4		36.5

		23-Mar-08		20:07:10		65.6		44		23-Mar-08		20:06:20		65.6		45.5		23-Mar-08		20:07:53		69.8		41.5		3-May-08		20:25:59		74.01		36.5

		23-Mar-08		22:07:10		65.6		48		23-Mar-08		22:06:20		65.01		46.5		23-Mar-08		22:07:53		71		39.5		3-May-08		22:25:59		74.01		35

		24-Mar-08		0:07:10		65.6		47.5		24-Mar-08		0:06:20		65.01		44.5		24-Mar-08		0:07:53		71		37.5		4-May-08		0:25:59		72.21		34.5

		24-Mar-08		2:07:10		65.6		43		24-Mar-08		2:06:20		65.6		41		24-Mar-08		2:07:53		69.8		36		4-May-08		2:25:59		70.41		35

		24-Mar-08		4:07:10		65.6		47.5		24-Mar-08		4:06:20		65.01		39.5		24-Mar-08		4:07:53		68.61		36		4-May-08		4:25:59		69.2		34.5

		24-Mar-08		6:07:10		65.01		47.5		24-Mar-08		6:06:20		64.4		38.5		24-Mar-08		6:07:53		68		35.5		4-May-08		6:25:59		69.2		34.5

		24-Mar-08		8:07:10		65.01		36		24-Mar-08		8:06:20		63.8		36.5		24-Mar-08		8:07:53		66.81		35		4-May-08		8:25:59		69.8		35

		24-Mar-08		10:07:10		65.6		47.5		24-Mar-08		10:06:20		65.6		39		24-Mar-08		10:07:53		69.8		35		4-May-08		10:25:59		71.6		37

		24-Mar-08		12:07:10		65.6		39.5		24-Mar-08		12:06:20		66.2		38		24-Mar-08		12:07:53		70.41		36.5		4-May-08		12:25:59		73.4		37

		24-Mar-08		14:07:10		66.2		43.5		24-Mar-08		14:06:20		65.6		39		24-Mar-08		14:07:53		69.8		39		4-May-08		14:25:59		74.6		38

		24-Mar-08		16:07:10		66.2		47.5		24-Mar-08		16:06:20		65.6		45.5		24-Mar-08		16:07:53		70.41		42		4-May-08		16:25:59		74.01		38

		24-Mar-08		18:07:10		66.2		45.5		24-Mar-08		18:06:20		66.2		50		24-Mar-08		18:07:53		69.8		45		4-May-08		18:25:59		73.4		40.5

		24-Mar-08		20:07:10		65.6		47.5		24-Mar-08		20:06:20		66.2		45.5		24-Mar-08		20:07:53		71		42.5		4-May-08		20:25:59		73.4		40

		24-Mar-08		22:07:10		65.6		43		24-Mar-08		22:06:20		65.6		45		24-Mar-08		22:07:53		71.6		39.5		4-May-08		22:25:59		72.8		39

		25-Mar-08		0:07:10		65.6		42.5		25-Mar-08		0:06:20		65.01		46		25-Mar-08		0:07:53		71		38.5		5-May-08		0:25:59		71.6		38.5

		25-Mar-08		2:07:10		65.6		41		25-Mar-08		2:06:20		65.6		42		25-Mar-08		2:07:53		69.8		37.5		5-May-08		2:25:59		71		38

		25-Mar-08		4:07:10		65.6		46		25-Mar-08		4:06:20		65.6		42.5		25-Mar-08		4:07:53		69.2		37		5-May-08		4:25:59		69.8		37.5

		25-Mar-08		6:07:10		65.6		39.5		25-Mar-08		6:06:20		65.6		41		25-Mar-08		6:07:53		69.8		37.5		5-May-08		6:25:59		68.61		37.5

		25-Mar-08		8:07:10		65.6		40		25-Mar-08		8:06:20		65.6		41.5		25-Mar-08		8:07:53		71.6		37		5-May-08		8:25:59		68.61		38

		25-Mar-08		10:07:10		66.2		44.5		25-Mar-08		10:06:20		66.2		49		25-Mar-08		10:07:53		70.41		44.5		5-May-08		10:25:59		69.8		40.5

		25-Mar-08		12:07:10		66.81		46.5		25-Mar-08		12:06:20		66.2		53.5		25-Mar-08		12:07:53		71.6		38.5		5-May-08		12:25:59		71.6		41.5

		25-Mar-08		14:07:10		66.81		47.5		25-Mar-08		14:06:20		66.2		59.5		25-Mar-08		14:07:53		71		46		5-May-08		14:25:59		72.8		41.5

		25-Mar-08		16:07:10		66.81		48.5		25-Mar-08		16:06:20		65.6		53.5		25-Mar-08		16:07:53		71		49		5-May-08		16:25:59		73.4		40.5

		25-Mar-08		18:07:10		66.2		47		25-Mar-08		18:06:20		65.6		57.5		25-Mar-08		18:07:53		70.41		50.5		5-May-08		18:25:59		73.4		39.5

		25-Mar-08		20:07:10		66.2		45.5		25-Mar-08		20:06:20		65.6		55		25-Mar-08		20:07:53		70.41		51		5-May-08		20:25:59		72.8		39

		25-Mar-08		22:07:10		65.6		45		25-Mar-08		22:06:20		65.6		51		25-Mar-08		22:07:53		70.41		46		5-May-08		22:25:59		72.21		38

		26-Mar-08		0:07:10		65.6		44		26-Mar-08		0:06:20		65.6		49		26-Mar-08		0:07:53		69.8		42.5		6-May-08		0:25:59		71.6		37.5

		26-Mar-08		2:07:10		65.6		43		26-Mar-08		2:06:20		65.6		47.5		26-Mar-08		2:07:53		69.8		40.5		6-May-08		2:25:59		70.41		38

		26-Mar-08		4:07:10		65.6		42		26-Mar-08		4:06:20		65.6		45.5		26-Mar-08		4:07:53		69.8		39		6-May-08		4:25:59		69.2		37.5

		26-Mar-08		6:07:10		65.6		43		26-Mar-08		6:06:20		64.4		49.5		26-Mar-08		6:07:53		70.41		40.5		6-May-08		6:25:59		69.8		37.5

		26-Mar-08		8:07:10		66.2		44		26-Mar-08		8:06:20		65.6		50.5		26-Mar-08		8:07:53		71.6		41.5		6-May-08		8:25:59		69.8		40

		26-Mar-08		10:07:10		66.2		45		26-Mar-08		10:06:20		65.01		53		26-Mar-08		10:07:53		71		45.5		6-May-08		10:25:59		72.21		41.5

		26-Mar-08		12:07:10		66.2		46		26-Mar-08		12:06:20		65.6		53.5		26-Mar-08		12:07:53		71		49		6-May-08		12:25:59		73.4		43.5

		26-Mar-08		14:07:10		66.81		45.5		26-Mar-08		14:06:20		65.6		53.5		26-Mar-08		14:07:53		71		48.5		6-May-08		14:25:59		73.4		43

		26-Mar-08		16:07:10		66.2		44		26-Mar-08		16:06:20		66.2		50.5		26-Mar-08		16:07:53		70.41		39.5		6-May-08		16:25:59		74.01		43

		26-Mar-08		18:07:10		65.6		43		26-Mar-08		18:06:20		66.2		45		26-Mar-08		18:07:53		70.41		48		6-May-08		18:25:59		74.01		40

		26-Mar-08		20:07:10		65.6		41		26-Mar-08		20:06:20		65.6		41.5		26-Mar-08		20:07:53		70.41		43.5		6-May-08		20:25:59		73.4		40

		26-Mar-08		22:07:10		65.6		40.5		26-Mar-08		22:06:20		64.4		44		26-Mar-08		22:07:53		72.21		37.5		6-May-08		22:25:59		72.21		39.5

		27-Mar-08		0:07:10		65.6		41		27-Mar-08		0:06:20		65.6		43		27-Mar-08		0:07:53		71.6		36.5		7-May-08		0:25:59		71.6		40

		27-Mar-08		2:07:10		65.01		39.5		27-Mar-08		2:06:20		64.4		42.5		27-Mar-08		2:07:53		70.41		36		7-May-08		2:25:59		71		40

		27-Mar-08		4:07:10		65.01		38		27-Mar-08		4:06:20		63.8		41.5		27-Mar-08		4:07:53		69.8		35		7-May-08		4:25:59		69.8		40

		27-Mar-08		6:07:10		65.01		37		27-Mar-08		6:06:20		63.8		40.5		27-Mar-08		6:07:53		70.41		35		7-May-08		6:25:59		71		40.5

		27-Mar-08		8:07:10		65.6		37		27-Mar-08		8:06:20		63.8		39		27-Mar-08		8:07:53		71.6		34.5		7-May-08		8:25:59		71.6		41.5

		27-Mar-08		10:07:10		65.6		40		27-Mar-08		10:06:20		66.2		41		27-Mar-08		10:07:53		71.6		35		7-May-08		10:25:59		73.4		41

		27-Mar-08		12:07:10		65.6		39		27-Mar-08		12:06:20		69.2		36.5		27-Mar-08		12:07:53		71		42		7-May-08		12:25:59		73.4		43

		27-Mar-08		14:07:10		66.2		40		27-Mar-08		14:06:20		69.2		37		27-Mar-08		14:07:53		71		35.5		7-May-08		14:25:59		73.4		45.5

		27-Mar-08		16:07:10		65.6		43		27-Mar-08		16:06:20		68.61		41.5		27-Mar-08		16:07:53		70.41		37		7-May-08		16:25:59		73.4		44.5

		27-Mar-08		18:07:10		65.6		41		27-Mar-08		18:06:20		68.61		38		27-Mar-08		18:07:53		70.41		42		7-May-08		18:25:59		73.4		43

		27-Mar-08		20:07:10		65.6		40		27-Mar-08		20:06:20		68		38.5		27-Mar-08		20:07:53		72.8		36		7-May-08		20:25:59		74.01		42

		27-Mar-08		22:07:10		65.6		37.5		27-Mar-08		22:06:20		66.81		36		27-Mar-08		22:07:53		74.6		32		7-May-08		22:25:59		74.01		37.5

		28-Mar-08		0:07:10		65.01		36.5		28-Mar-08		0:06:20		65.6		36.5		28-Mar-08		0:07:53		71.6		32.5		8-May-08		0:25:59		73.4		37

		28-Mar-08		2:07:10		65.01		35		28-Mar-08		2:06:20		64.4		35.5		28-Mar-08		2:07:53		69.8		32		8-May-08		2:25:59		71.6		37

		28-Mar-08		4:07:10		65.01		33.5		28-Mar-08		4:06:20		63.8		35		28-Mar-08		4:07:53		68.61		31.5		8-May-08		4:25:59		70.41		37.5

		28-Mar-08		6:07:10		65.01		33		28-Mar-08		6:06:20		63.21		35		28-Mar-08		6:07:53		69.2		32		8-May-08		6:25:59		73.4		35.5

		28-Mar-08		8:07:10		65.6		32		28-Mar-08		8:06:20		64.4		34		28-Mar-08		8:07:53		70.41		32		8-May-08		8:25:59		72.8		35.5

		28-Mar-08		10:07:10		65.6		30.5		28-Mar-08		10:06:20		66.2		31		28-Mar-08		10:07:53		71		33		8-May-08		10:25:59		72.8		37.5

		28-Mar-08		12:07:10		65.6		28		28-Mar-08		12:06:20		68.61		27		28-Mar-08		12:07:53		71		29.5		8-May-08		12:25:59		72.8		38.5

		28-Mar-08		14:07:10		66.2		28		28-Mar-08		14:06:20		69.2		25.5		28-Mar-08		14:07:53		70.41		32.5		8-May-08		14:25:59		73.4		39.5

		28-Mar-08		16:07:10		66.2		23.5		28-Mar-08		16:06:20		69.2		22		28-Mar-08		16:07:53		70.41		28.5		8-May-08		16:25:59		74.01		39.5

		28-Mar-08		18:07:10		65.6		24.5		28-Mar-08		18:06:20		69.2		21		28-Mar-08		18:07:53		71		26.5		8-May-08		18:25:59		73.4		39

		28-Mar-08		20:07:10		65.6		26		28-Mar-08		20:06:20		68.61		23.5		28-Mar-08		20:07:53		71.6		26.5		8-May-08		20:25:59		74.01		39.5

		28-Mar-08		22:07:10		65.01		35		28-Mar-08		22:06:20		67.4		34		28-Mar-08		22:07:53		74.6		28.5		8-May-08		22:25:59		74.01		37.5

		29-Mar-08		0:07:10		65.01		35		29-Mar-08		0:06:20		65.6		35.5		29-Mar-08		0:07:53		72.8		29.5		9-May-08		0:25:59		72.8		37

		29-Mar-08		2:07:10		65.01		36		29-Mar-08		2:06:20		65.01		37.5		29-Mar-08		2:07:53		71		30.5		9-May-08		2:25:59		71		36.5

		29-Mar-08		4:07:10		65.01		35.5		29-Mar-08		4:06:20		64.4		37.5		29-Mar-08		4:07:53		69.8		31		9-May-08		4:25:59		69.2		36.5

		29-Mar-08		6:07:10		65.6		34.5		29-Mar-08		6:06:20		64.4		37		29-Mar-08		6:07:53		70.41		33		9-May-08		6:25:59		72.8		35.5

		29-Mar-08		8:07:10		65.01		36.5		29-Mar-08		8:06:20		65.6		37.5		29-Mar-08		8:07:53		70.41		35		9-May-08		8:25:59		73.4		36.5

		29-Mar-08		10:07:10		65.6		32		29-Mar-08		10:06:20		68		32.5		29-Mar-08		10:07:53		70.41		35.5		9-May-08		10:25:59		73.4		38.5

		29-Mar-08		12:07:10		64.4		39		29-Mar-08		12:06:20		69.2		32		29-Mar-08		12:07:53		71		36.5		9-May-08		12:25:59		72.21		41

		29-Mar-08		14:07:10		66.81		38.5		29-Mar-08		14:06:20		68		38		29-Mar-08		14:07:53		71		44		9-May-08		14:25:59		72.21		41.5

		29-Mar-08		16:07:10		66.81		43		29-Mar-08		16:06:20		65.6		51		29-Mar-08		16:07:53		71		43		9-May-08		16:25:59		73.4		39.5

		29-Mar-08		18:07:10		66.81		44.5		29-Mar-08		18:06:20		64.4		55.5		29-Mar-08		18:07:53		72.21		42.5		9-May-08		18:25:59		72.8		39

		29-Mar-08		20:07:10		66.81		44.5		29-Mar-08		20:06:20		65.01		55		29-Mar-08		20:07:53		71		45.5		9-May-08		20:25:59		73.4		38.5

		29-Mar-08		22:07:10		66.81		45		29-Mar-08		22:06:20		64.4		57		29-Mar-08		22:07:53		70.41		44		9-May-08		22:25:59		72.8		37.5

		30-Mar-08		0:07:10		66.81		45		30-Mar-08		0:06:20		65.01		56		30-Mar-08		0:07:53		70.41		42.5		10-May-08		0:25:59		72.21		36

		30-Mar-08		2:07:10		66.81		44.5		30-Mar-08		2:06:20		65.01		54.5		30-Mar-08		2:07:53		69.8		43		10-May-08		2:25:59		72.21		35

		30-Mar-08		4:07:10		66.81		43.5		30-Mar-08		4:06:20		64.4		53.5		30-Mar-08		4:07:53		69.8		42		10-May-08		4:25:59		72.21		35

		30-Mar-08		6:07:10		66.81		41.5		30-Mar-08		6:06:20		65.01		50		30-Mar-08		6:07:53		69.8		41.5		10-May-08		6:25:59		72.21		34

		30-Mar-08		8:07:10		67.4		40.5		30-Mar-08		8:06:20		65.01		47.5		30-Mar-08		8:07:53		69.8		40		10-May-08		8:25:59		71		36

		30-Mar-08		10:07:10		67.4		39.5		30-Mar-08		10:06:20		64.4		47.5		30-Mar-08		10:07:53		69.8		39.5		10-May-08		10:25:59		73.4		36

		30-Mar-08		12:07:10		68		40.5		30-Mar-08		12:06:20		64.4		48		30-Mar-08		12:07:53		69.8		41		10-May-08		12:25:59		74.6		34.5

		30-Mar-08		14:07:10		67.4		42		30-Mar-08		14:06:20		65.01		51		30-Mar-08		14:07:53		70.41		37.5		10-May-08		14:25:59		75.2		33.5

		30-Mar-08		16:07:10		67.4		40.5		30-Mar-08		16:06:20		65.01		46.5		30-Mar-08		16:07:53		70.41		39		10-May-08		16:25:59		75.2		35.5

		30-Mar-08		18:07:10		67.4		39.5		30-Mar-08		18:06:20		65.01		45.5		30-Mar-08		18:07:53		69.8		43		10-May-08		18:25:59		75.2		35.5

		30-Mar-08		20:07:10		68		37		30-Mar-08		20:06:20		64.4		43		30-Mar-08		20:07:53		70.41		39.5		10-May-08		20:25:59		74.6		36

		30-Mar-08		22:07:10		68		33		30-Mar-08		22:06:20		64.4		37		30-Mar-08		22:07:53		71		35.5		10-May-08		22:25:59		74.6		34.5

		31-Mar-08		0:07:10		68		32		31-Mar-08		0:06:20		65.01		35		31-Mar-08		0:07:53		69.8		33		11-May-08		0:25:59		74.01		34

		31-Mar-08		2:07:10		67.4		32		31-Mar-08		2:06:20		64.4		35.5		31-Mar-08		2:07:53		69.8		32.5		11-May-08		2:25:59		72.21		34

		31-Mar-08		4:07:10		67.4		32.5		31-Mar-08		4:06:20		63.8		37		31-Mar-08		4:07:53		68.61		32.5		11-May-08		4:25:59		71.6		34

		31-Mar-08		6:07:10		68		32.5		31-Mar-08		6:06:20		63.21		38.5		31-Mar-08		6:07:53		68		33		11-May-08		6:25:59		72.21		34

		31-Mar-08		8:07:10		67.4		31		31-Mar-08		8:06:20		63.8		36		31-Mar-08		8:07:53		68		32.5		11-May-08		8:25:59		72.21		34.5

		31-Mar-08		10:07:10		67.4		28.5		31-Mar-08		10:06:20		64.4		32		31-Mar-08		10:07:53		69.2		31		11-May-08		10:25:59		72.8		35

		31-Mar-08		12:07:10		67.4		25.5		31-Mar-08		12:06:20		64.4		29.5		31-Mar-08		12:07:53		69.8		29.5		11-May-08		12:25:59		74.01		35

		31-Mar-08		14:07:10		68		23.5		31-Mar-08		14:06:20		65.01		25.5		31-Mar-08		14:07:53		69.8		27.5		11-May-08		14:25:59		75.81		35.5

		31-Mar-08		16:07:10		67.4		24		31-Mar-08		16:06:20		65.01		26		31-Mar-08		16:07:53		69.2		28		11-May-08		16:25:59		77		34.5

		31-Mar-08		18:07:10		67.4		26.5		31-Mar-08		18:06:20		65.01		29.5		31-Mar-08		18:07:53		69.8		28.5		11-May-08		18:25:59		78.2		35

		31-Mar-08		20:07:10		68		26.5		31-Mar-08		20:06:20		64.4		30		31-Mar-08		20:07:53		71		28.5		11-May-08		20:25:59		77.61		36

		31-Mar-08		22:07:10		67.4		27		31-Mar-08		22:06:20		64.4		30.5		31-Mar-08		22:07:53		70.41		27.5		11-May-08		22:25:59		75.81		37

		1-Apr-08		0:07:10		67.4		27.5		1-Apr-08		0:06:20		64.4		31.5		1-Apr-08		0:07:53		69.2		27.5		12-May-08		0:25:59		74.01		37.5

		1-Apr-08		2:07:10		67.4		28		1-Apr-08		2:06:20		63.8		32.5		1-Apr-08		2:07:53		68.61		28		12-May-08		2:25:59		72.8		38

		1-Apr-08		4:07:10		67.4		28		1-Apr-08		4:06:20		62.6		32.5		1-Apr-08		4:07:53		67.4		28.5		12-May-08		4:25:59		72.21		38

		1-Apr-08		6:07:10		67.4		28.5		1-Apr-08		6:06:20		62		34		1-Apr-08		6:07:53		66.81		29.5		12-May-08		6:25:59		72.21		37.5

		1-Apr-08		8:07:10		68		28.5		1-Apr-08		8:06:20		63.21		34		1-Apr-08		8:07:53		69.8		29.5		12-May-08		8:25:59		72.21		38.5

		1-Apr-08		10:07:10		67.4		30.5		1-Apr-08		10:06:20		65.01		34.5		1-Apr-08		10:07:53		71		31.5		12-May-08		10:25:59		71.6		40

		1-Apr-08		12:07:10		66.81		27		1-Apr-08		12:06:20		65.6		30		1-Apr-08		12:07:53		71		34		12-May-08		12:25:59		72.8		41

		1-Apr-08		14:07:10		66.81		30		1-Apr-08		14:06:20		66.2		31		1-Apr-08		14:07:53		71		35		12-May-08		14:25:59		74.01		36

		1-Apr-08		16:07:10		66.81		31		1-Apr-08		16:06:20		65.6		34		1-Apr-08		16:07:53		71		36.5		12-May-08		16:25:59		74.6		32

		1-Apr-08		18:07:10		66.81		29.5		1-Apr-08		18:06:20		65.01		32.5		1-Apr-08		18:07:53		71		33.5		12-May-08		18:25:59		76.4		31

		1-Apr-08		20:07:10		67.4		30.5		1-Apr-08		20:06:20		65.01		32.5		1-Apr-08		20:07:53		70.41		32		12-May-08		20:25:59		75.81		31.5

		1-Apr-08		22:07:10		67.4		29		1-Apr-08		22:06:20		64.4		32		1-Apr-08		22:07:53		70.41		32		12-May-08		22:25:59		74.01		31

		2-Apr-08		0:07:10		66.81		33		2-Apr-08		0:06:20		65.01		37		2-Apr-08		0:07:53		70.41		31		13-May-08		0:25:59		72.8		31

		2-Apr-08		2:07:10		66.81		34		2-Apr-08		2:06:20		64.4		38.5		2-Apr-08		2:07:53		70.41		31		13-May-08		2:25:59		71.6		31

		2-Apr-08		4:07:10		66.81		33		2-Apr-08		4:06:20		64.4		38		2-Apr-08		4:07:53		70.41		32		13-May-08		4:25:59		71.6		31

		2-Apr-08		6:07:10		66.81		31.5		2-Apr-08		6:06:20		65.01		35		2-Apr-08		6:07:53		71		32		13-May-08		6:25:59		71.6		30

		2-Apr-08		8:07:10		66.81		33.5		2-Apr-08		8:06:20		65.01		37.5		2-Apr-08		8:07:53		71.6		33.5		13-May-08		8:25:59		71.6		30

		2-Apr-08		10:07:10		66.81		33.5		2-Apr-08		10:06:20		66.2		35.5		2-Apr-08		10:07:53		70.41		35		13-May-08		10:25:59		74.01		29.5

		2-Apr-08		12:07:10		66.81		33		2-Apr-08		12:06:20		66.81		33		2-Apr-08		12:07:53		71		36		13-May-08		12:25:59		74.01		29.5

		2-Apr-08		14:07:10		66.81		39		2-Apr-08		14:06:20		67.4		42.5		2-Apr-08		14:07:53		71.6		34.5		13-May-08		14:25:59		75.2		29.5

		2-Apr-08		16:07:10		67.4		34		2-Apr-08		16:06:20		67.4		31.5		2-Apr-08		16:07:53		71.6		36.5		13-May-08		16:25:59		75.2		30

		2-Apr-08		18:07:10		66.81		35		2-Apr-08		18:06:20		66.2		36		2-Apr-08		18:07:53		71		32.5		13-May-08		18:25:59		75.2		30

		2-Apr-08		20:07:10		67.4		36.5		2-Apr-08		20:06:20		66.81		37		2-Apr-08		20:07:53		71		37		13-May-08		20:25:59		74.6		30.5

		2-Apr-08		22:07:10		66.81		37.5		2-Apr-08		22:06:20		65.6		41.5		2-Apr-08		22:07:53		75.2		33		13-May-08		22:25:59		74.01		29.5

		3-Apr-08		0:07:10		66.81		37.5		3-Apr-08		0:06:20		66.2		42		3-Apr-08		0:07:53		71.6		34		14-May-08		0:25:59		73.4		29.5

		3-Apr-08		2:07:10		66.81		36.5		3-Apr-08		2:06:20		65.6		40.5		3-Apr-08		2:07:53		70.41		34.5		14-May-08		2:25:59		72.21		30

		3-Apr-08		4:07:10		67.4		34.5		3-Apr-08		4:06:20		64.4		38.5		3-Apr-08		4:07:53		69.2		33.5		14-May-08		4:25:59		71.6		30.5

		3-Apr-08		6:07:10		67.4		35.5		3-Apr-08		6:06:20		64.4		38		3-Apr-08		6:07:53		69.2		33		14-May-08		6:25:59		72.21		31

		3-Apr-08		8:07:10		67.4		35.5		3-Apr-08		8:06:20		65.01		38.5		3-Apr-08		8:07:53		71		31		14-May-08		8:25:59		71.6		32.5

		3-Apr-08		10:07:10		65.01		39		3-Apr-08		10:06:20		66.2		41		3-Apr-08		10:07:53		71.6		34.5		14-May-08		10:25:59		74.6		33

		3-Apr-08		12:07:10		66.81		38		3-Apr-08		12:06:20		66.81		39		3-Apr-08		12:07:53		71		34.5		14-May-08		12:25:59		74.01		32

		3-Apr-08		14:07:10		66.81		40		3-Apr-08		14:06:20		67.4		41.5		3-Apr-08		14:07:53		71		38		14-May-08		14:25:59		74.01		30.5

		3-Apr-08		16:07:10		66.81		38		3-Apr-08		16:06:20		66.2		40		3-Apr-08		16:07:53		71.6		42.5		14-May-08		16:25:59		74.6		29

		3-Apr-08		18:07:10		66.81		35.5		3-Apr-08		18:06:20		66.81		36		3-Apr-08		18:07:53		71		32		14-May-08		18:25:59		74.01		29

		3-Apr-08		20:07:10		67.4		35.5		3-Apr-08		20:06:20		66.2		37.5		3-Apr-08		20:07:53		71		32.5		14-May-08		20:25:59		74.6		33

		3-Apr-08		22:07:10		67.4		34.5		3-Apr-08		22:06:20		65.6		37		3-Apr-08		22:07:53		72.21		34		14-May-08		22:25:59		75.2		33

		4-Apr-08		0:07:10		67.4		34.5		4-Apr-08		0:06:20		66.2		37.5		4-Apr-08		0:07:53		72.21		33.5		15-May-08		0:25:59		74.6		33.5

		4-Apr-08		2:07:10		66.81		34		4-Apr-08		2:06:20		65.6		36.5		4-Apr-08		2:07:53		70.41		32.5		15-May-08		2:25:59		74.01		34

		4-Apr-08		4:07:10		66.81		35		4-Apr-08		4:06:20		65.01		38		4-Apr-08		4:07:53		69.8		32		15-May-08		4:25:59		73.4		35

		4-Apr-08		6:07:10		66.81		37		4-Apr-08		6:06:20		65.6		40.5		4-Apr-08		6:07:53		69.8		34		15-May-08		6:25:59		73.4		36.5

		4-Apr-08		8:07:10		67.4		37.5		4-Apr-08		8:06:20		66.81		42		4-Apr-08		8:07:53		72.21		33.5		15-May-08		8:25:59		73.4		39

		4-Apr-08		10:07:10		68		38.5		4-Apr-08		10:06:20		66.81		42		4-Apr-08		10:07:53		71.6		36		15-May-08		10:25:59		74.6		40

		4-Apr-08		12:07:10		74.6		35		4-Apr-08		12:06:20		74.6		35.5		4-Apr-08		12:07:53		71.6		42.5		15-May-08		12:25:59		74.01		41.5

		4-Apr-08		14:07:10		66.81		38.5		4-Apr-08		14:06:20		67.4		38.5		4-Apr-08		14:07:53		71.6		45		15-May-08		14:25:59		74.01		38.5

		4-Apr-08		16:07:10		66.81		42		4-Apr-08		16:06:20		66.81		45		4-Apr-08		16:07:53		71		45		15-May-08		16:25:59		74.01		38.5

		4-Apr-08		18:07:10		66.81		40.5		4-Apr-08		18:06:20		66.81		43.5		4-Apr-08		18:07:53		71.6		44		15-May-08		18:25:59		73.4		38.5

		4-Apr-08		20:07:10		66.81		45.5		4-Apr-08		20:06:20		65.6		44		4-Apr-08		20:07:53		71.6		43		15-May-08		20:25:59		75.2		38.5

		4-Apr-08		22:07:10		66.81		45.5		4-Apr-08		22:06:20		66.2		43		4-Apr-08		22:07:53		71.6		35.5		15-May-08		22:25:59		76.4		36

		5-Apr-08		0:07:10		67.4		45		5-Apr-08		0:06:20		65.6		42		5-Apr-08		0:07:53		71		39.5		16-May-08		0:25:59		76.4		35.5

		5-Apr-08		2:07:10		66.81		46.5		5-Apr-08		2:06:20		65.01		43.5		5-Apr-08		2:07:53		70.41		37.5		16-May-08		2:25:59		75.81		35.5

		5-Apr-08		4:07:10		66.81		46.5		5-Apr-08		4:06:20		65.01		44.5		5-Apr-08		4:07:53		69.8		38		16-May-08		4:25:59		75.2		35.5

		5-Apr-08		6:07:10		66.81		46		5-Apr-08		6:06:20		65.01		43		5-Apr-08		6:07:53		70.41		39		16-May-08		6:25:59		75.2		35

		5-Apr-08		8:07:10		68		43.5		5-Apr-08		8:06:20		65.6		43.5		5-Apr-08		8:07:53		71		41		16-May-08		8:25:59		74.6		36.5

		5-Apr-08		10:07:10		67.4		47		5-Apr-08		10:06:20		67.4		40		5-Apr-08		10:07:53		70.41		39		16-May-08		10:25:59		74.01		38.5

		5-Apr-08		12:07:10		67.4		45.5		5-Apr-08		12:06:20		67.4		38.5		5-Apr-08		12:07:53		71		44		16-May-08		12:25:59		73.4		40.5

		5-Apr-08		14:07:10		66.81		47		5-Apr-08		14:06:20		68.61		40.5		5-Apr-08		14:07:53		74.6		35.5		16-May-08		14:25:59		72.8		40.5

		5-Apr-08		16:07:10		66.81		46		5-Apr-08		16:06:20		67.4		43		5-Apr-08		16:07:53		71.6		45.5		16-May-08		16:25:59		73.4		40.5

		5-Apr-08		18:07:10		66.81		46.5		5-Apr-08		18:06:20		66.81		40		5-Apr-08		18:07:53		73.4		40		16-May-08		18:25:59		74.01		40.5

		5-Apr-08		20:07:10		67.4		46.5		5-Apr-08		20:06:20		67.4		40.5		5-Apr-08		20:07:53		75.2		37		16-May-08		20:25:59		75.2		40.5

		5-Apr-08		22:07:10		66.81		46		5-Apr-08		22:06:20		67.4		36.5		5-Apr-08		22:07:53		73.4		36.5		16-May-08		22:25:59		77		40

		6-Apr-08		0:07:10		66.81		46		6-Apr-08		0:06:20		66.81		37		6-Apr-08		0:07:53		71		36		17-May-08		0:25:59		76.4		39

		6-Apr-08		2:07:10		66.81		46.5		6-Apr-08		2:06:20		65.6		37.5		6-Apr-08		2:07:53		69.8		35.5		17-May-08		2:25:59		75.2		39

		6-Apr-08		4:07:10		66.81		47		6-Apr-08		4:06:20		65.01		38		6-Apr-08		4:07:53		68.61		36		17-May-08		4:25:59		74.6		39

		6-Apr-08		6:07:10		67.4		46		6-Apr-08		6:06:20		65.01		37.5		6-Apr-08		6:07:53		67.4		36.5		17-May-08		6:25:59		74.6		40

		6-Apr-08		8:07:10		67.4		47		6-Apr-08		8:06:20		65.01		37.5		6-Apr-08		8:07:53		67.4		36.5		17-May-08		8:25:59		74.6		41.5

		6-Apr-08		10:07:10		67.4		45		6-Apr-08		10:06:20		66.81		37		6-Apr-08		10:07:53		69.2		36.5		17-May-08		10:25:59		74.01		43

		6-Apr-08		12:07:10		67.4		46		6-Apr-08		12:06:20		68		35.5		6-Apr-08		12:07:53		70.41		36.5		17-May-08		12:25:59		73.4		46.5

		6-Apr-08		14:07:10		67.4		46		6-Apr-08		14:06:20		68		37		6-Apr-08		14:07:53		70.41		39		17-May-08		14:25:59		74.01		45.5

		6-Apr-08		16:07:10		68		45.5		6-Apr-08		16:06:20		68		39		6-Apr-08		16:07:53		70.41		40.5		17-May-08		16:25:59		74.01		45

		6-Apr-08		18:07:10		67.4		46.5		6-Apr-08		18:06:20		67.4		38.5		6-Apr-08		18:07:53		71		40		17-May-08		18:25:59		73.4		42.5

		6-Apr-08		20:07:10		68		45.5		6-Apr-08		20:06:20		67.4		39.5		6-Apr-08		20:07:53		72.21		38		17-May-08		20:25:59		75.2		42.5

		6-Apr-08		22:07:10		67.4		43.5		6-Apr-08		22:06:20		67.4		39.5		6-Apr-08		22:07:53		71.6		37		17-May-08		22:25:59		75.81		40

		7-Apr-08		0:07:10		67.4		44		7-Apr-08		0:06:20		66.81		39		7-Apr-08		0:07:53		71		36.5		18-May-08		0:25:59		75.2		39.5

		7-Apr-08		2:07:10		68		46		7-Apr-08		2:06:20		66.2		37.5		7-Apr-08		2:07:53		69.8		36		18-May-08		2:25:59		74.6		40

		7-Apr-08		4:07:10		67.4		45		7-Apr-08		4:06:20		65.6		38		7-Apr-08		4:07:53		69.2		36.5		18-May-08		4:25:59		73.4		40

		7-Apr-08		6:07:10		67.4		45.5		7-Apr-08		6:06:20		65.6		38		7-Apr-08		6:07:53		68.61		37		18-May-08		6:25:59		73.4		39.5

		7-Apr-08		8:07:10		67.4		46.5		7-Apr-08		8:06:20		65.6		39		7-Apr-08		8:07:53		68		37		18-May-08		8:25:59		74.01		40.5

		7-Apr-08		10:07:10		67.4		46		7-Apr-08		10:06:20		66.81		40		7-Apr-08		10:07:53		69.8		37.5		18-May-08		10:25:59		75.81		41.5

		7-Apr-08		12:07:10		68		45		7-Apr-08		12:06:20		66.81		44		7-Apr-08		12:07:53		69.8		39		18-May-08		12:25:59		77.61		42

		7-Apr-08		14:07:10		67.4		45		7-Apr-08		14:06:20		67.4		36		7-Apr-08		14:07:53		71		37		18-May-08		14:25:59		79.41		43

		7-Apr-08		16:07:10		67.4		45.5		7-Apr-08		16:06:20		66.81		35.5		7-Apr-08		16:07:53		71.6		35.5		18-May-08		16:25:59		79.41		41.5

		7-Apr-08		18:07:10		67.4		45.5		7-Apr-08		18:06:20		67.4		33		7-Apr-08		18:07:53		72.21		34.5		18-May-08		18:25:59		78.2		41.5

		7-Apr-08		20:07:10		67.4		44.5		7-Apr-08		20:06:20		66.81		31.5		7-Apr-08		20:07:53		71.6		33		18-May-08		20:25:59		77.61		41

		7-Apr-08		22:07:10		68		46		7-Apr-08		22:06:20		67.4		32.5		7-Apr-08		22:07:53		71		33		18-May-08		22:25:59		76.4		40

		8-Apr-08		0:07:10		67.4		44.5		8-Apr-08		0:06:20		66.81		34		8-Apr-08		0:07:53		69.8		33		19-May-08		0:25:59		74.6		39.5

		8-Apr-08		2:07:10		67.4		46.5		8-Apr-08		2:06:20		66.2		35.5		8-Apr-08		2:07:53		69.2		34		19-May-08		2:25:59		73.4		39

		8-Apr-08		4:07:10		67.4		45.5		8-Apr-08		4:06:20		65.6		35.5		8-Apr-08		4:07:53		68		34.5		19-May-08		4:25:59		72.21		39

		8-Apr-08		6:07:10		67.4		46		8-Apr-08		6:06:20		65.01		35		8-Apr-08		6:07:53		68		35		19-May-08		6:25:59		72.21		39.5

		8-Apr-08		8:07:10		67.4		46.5		8-Apr-08		8:06:20		66.2		35		8-Apr-08		8:07:53		71.6		35		19-May-08		8:25:59		72.21		40

		8-Apr-08		10:07:10		67.4		45		8-Apr-08		10:06:20		68		31.5		8-Apr-08		10:07:53		71.6		33.5		19-May-08		10:25:59		72.8		41.5

		8-Apr-08		12:07:10		66.81		46.5		8-Apr-08		12:06:20		68		29.5		8-Apr-08		12:07:53		71.6		34.5		19-May-08		12:25:59		74.6		41.5

		8-Apr-08		14:07:10		66.81		47		8-Apr-08		14:06:20		67.4		28.5		8-Apr-08		14:07:53		71		34.5		19-May-08		14:25:59		75.81		42

		8-Apr-08		16:07:10		66.81		46.5		8-Apr-08		16:06:20		67.4		35		8-Apr-08		16:07:53		71		37		19-May-08		16:25:59		77		41.5

		8-Apr-08		18:07:10		66.81		46		8-Apr-08		18:06:20		66.81		33		8-Apr-08		18:07:53		71.6		35		19-May-08		18:25:59		77.61		40

		8-Apr-08		20:07:10		66.81		46.5		8-Apr-08		20:06:20		66.81		38.5		8-Apr-08		20:07:53		71		34.5		19-May-08		20:25:59		77		39.5

		8-Apr-08		22:07:10		67.4		47		8-Apr-08		22:06:20		66.2		34		8-Apr-08		22:07:53		71.6		37.5		19-May-08		22:25:59		74.6		39.5

		9-Apr-08		0:07:10		66.81		45.5		9-Apr-08		0:06:20		66.2		38		9-Apr-08		0:07:53		71		35.5		20-May-08		0:25:59		73.4		40

		9-Apr-08		2:07:10		66.81		48		9-Apr-08		2:06:20		66.2		35.5		9-Apr-08		2:07:53		70.41		35		20-May-08		2:25:59		72.21		40

		9-Apr-08		4:07:10		66.81		47.5		9-Apr-08		4:06:20		66.2		36		9-Apr-08		4:07:53		69.8		34.5		20-May-08		4:25:59		72.21		40

		9-Apr-08		6:07:10		66.81		44		9-Apr-08		6:06:20		66.2		37		9-Apr-08		6:07:53		69.8		35.5		20-May-08		6:25:59		72.21		40.5

		9-Apr-08		8:07:10		66.81		47.5		9-Apr-08		8:06:20		66.81		37		9-Apr-08		8:07:53		71		38		20-May-08		8:25:59		71.6		42

		9-Apr-08		10:07:10		66.81		46		9-Apr-08		10:06:20		67.4		34		9-Apr-08		10:07:53		71		34.5		20-May-08		10:25:59		73.4		42.5

		9-Apr-08		12:07:10		66.81		45		9-Apr-08		12:06:20		68		32		9-Apr-08		12:07:53		71		38.5		20-May-08		12:25:59		74.01		43.5

		9-Apr-08		14:07:10		66.81		45		9-Apr-08		14:06:20		68.61		29.5		9-Apr-08		14:07:53		70.41		38.5		20-May-08		14:25:59		74.01		44.5

		9-Apr-08		16:07:10		66.81		47		9-Apr-08		16:06:20		67.4		36		9-Apr-08		16:07:53		71		41.5		20-May-08		16:25:59		74.6		44

		9-Apr-08		18:07:10		66.81		46.5		9-Apr-08		18:06:20		68		34		9-Apr-08		18:07:53		71.6		39.5		20-May-08		18:25:59		74.01		43.5

		9-Apr-08		20:07:10		67.4		47		9-Apr-08		20:06:20		67.4		33.5		9-Apr-08		20:07:53		75.2		35		20-May-08		20:25:59		74.6		43

		9-Apr-08		22:07:10		66.81		47		9-Apr-08		22:06:20		66.81		34.5		9-Apr-08		22:07:53		72.8		34.5		20-May-08		22:25:59		74.01		41

		10-Apr-08		0:07:10		66.81		47.5		10-Apr-08		0:06:20		66.2		33.5		10-Apr-08		0:07:53		70.41		33.5		21-May-08		0:25:59		72.8		41

		10-Apr-08		2:07:10		66.81		47		10-Apr-08		2:06:20		65.6		34.5		10-Apr-08		2:07:53		69.8		33		21-May-08		2:25:59		72.21		41

		10-Apr-08		4:07:10		66.81		47		10-Apr-08		4:06:20		65.01		34.5		10-Apr-08		4:07:53		69.2		33.5		21-May-08		4:25:59		72.21		41

		10-Apr-08		6:07:10		67.4		46		10-Apr-08		6:06:20		65.6		34.5		10-Apr-08		6:07:53		68.61		34.5		21-May-08		6:25:59		72.21		40.5

		10-Apr-08		8:07:10		66.81		47		10-Apr-08		8:06:20		66.2		34.5		10-Apr-08		8:07:53		69.8		35		21-May-08		8:25:59		72.21		42

		10-Apr-08		10:07:10		66.81		47.5		10-Apr-08		10:06:20		68		34		10-Apr-08		10:07:53		70.41		38		21-May-08		10:25:59		73.4		42.5

		10-Apr-08		12:07:10		66.81		47		10-Apr-08		12:06:20		69.2		34		10-Apr-08		12:07:53		70.41		35		21-May-08		12:25:59		73.4		43

		10-Apr-08		14:07:10		66.81		47.5		10-Apr-08		14:06:20		69.8		36		10-Apr-08		14:07:53		71		42.5		21-May-08		14:25:59		74.01		44

		10-Apr-08		16:07:10		66.81		46.5		10-Apr-08		16:06:20		69.2		39.5		10-Apr-08		16:07:53		70.41		47		21-May-08		16:25:59		74.01		41

		10-Apr-08		18:07:10		66.81		47.5		10-Apr-08		18:06:20		68		32		10-Apr-08		18:07:53		69.8		35.5		21-May-08		18:25:59		74.01		35

		10-Apr-08		20:07:10		66.81		46.5		10-Apr-08		20:06:20		67.4		37		10-Apr-08		20:07:53		70.41		41.5		21-May-08		20:25:59		73.4		34.5

		10-Apr-08		22:07:10		66.81		47		10-Apr-08		22:06:20		67.4		37		10-Apr-08		22:07:53		71		37.5		21-May-08		22:25:59		74.01		35

		11-Apr-08		0:07:10		66.81		47.5		11-Apr-08		0:06:20		68		36.5		11-Apr-08		0:07:53		69.2		38		22-May-08		0:25:59		73.4		34.5

		11-Apr-08		2:07:10		66.81		46.5		11-Apr-08		2:06:20		66.81		36.5		11-Apr-08		2:07:53		69.8		36.5		22-May-08		2:25:59		72.21		34.5

		11-Apr-08		4:07:10		66.81		46.5		11-Apr-08		4:06:20		66.2		37.5		11-Apr-08		4:07:53		69.8		35.5		22-May-08		4:25:59		71.6		34

		11-Apr-08		6:07:10		66.81		46.5		11-Apr-08		6:06:20		65.6		37.5		11-Apr-08		6:07:53		69.2		36.5		22-May-08		6:25:59		72.21		32.5

		11-Apr-08		8:07:10		66.81		47.5		11-Apr-08		8:06:20		66.81		38		11-Apr-08		8:07:53		70.41		38.5		22-May-08		8:25:59		71.6		33.5

		11-Apr-08		10:07:10		66.81		48		11-Apr-08		10:06:20		68		36.5		11-Apr-08		10:07:53		70.41		36		22-May-08		10:25:59		73.4		34

		11-Apr-08		12:07:10		66.2		48.5		11-Apr-08		12:06:20		68.61		35		11-Apr-08		12:07:53		71		39.5		22-May-08		12:25:59		73.4		35

		11-Apr-08		14:07:10		66.81		48		11-Apr-08		14:06:20		68.61		34.5		11-Apr-08		14:07:53		70.41		45.5		22-May-08		14:25:59		74.01		35

		11-Apr-08		16:07:10		66.2		45.5		11-Apr-08		16:06:20		68.61		40		11-Apr-08		16:07:53		70.41		47.5		22-May-08		16:25:59		74.01		35

		11-Apr-08		18:07:10		66.81		48		11-Apr-08		18:06:20		68.61		37.5		11-Apr-08		18:07:53		71		45.5		22-May-08		18:25:59		74.01		34.5

		11-Apr-08		20:07:10		66.81		47.5		11-Apr-08		20:06:20		68.61		39.5		11-Apr-08		20:07:53		70.41		42		22-May-08		20:25:59		73.4		34.5

		11-Apr-08		22:07:10		66.81		47		11-Apr-08		22:06:20		67.4		42.5		11-Apr-08		22:07:53		70.41		43		22-May-08		22:25:59		72.8		33.5

		12-Apr-08		0:07:10		66.81		48		12-Apr-08		0:06:20		68		41.5		12-Apr-08		0:07:53		69.8		41.5		23-May-08		0:25:59		72.21		33

		12-Apr-08		2:07:10		66.81		47		12-Apr-08		2:06:20		66.81		42		12-Apr-08		2:07:53		69.8		39		23-May-08		2:25:59		71		32.5

		12-Apr-08		4:07:10		66.81		47.5		12-Apr-08		4:06:20		66.2		41		12-Apr-08		4:07:53		70.41		38.5		23-May-08		4:25:59		71.6		31.5

		12-Apr-08		6:07:10		66.81		47.5		12-Apr-08		6:06:20		66.2		40.5		12-Apr-08		6:07:53		70.41		38		23-May-08		6:25:59		71.6		30.5

		12-Apr-08		8:07:10		66.81		48.5		12-Apr-08		8:06:20		68		39.5		12-Apr-08		8:07:53		69.8		36		23-May-08		8:25:59		71		31.5

		12-Apr-08		10:07:10		66.81		47.5		12-Apr-08		10:06:20		68.61		43		12-Apr-08		10:07:53		70.41		43		23-May-08		10:25:59		73.4		31

		12-Apr-08		12:07:10		66.81		47		12-Apr-08		12:06:20		68		39		12-Apr-08		12:07:53		69.8		47.5		23-May-08		12:25:59		73.4		29.5

		12-Apr-08		14:07:10		67.4		46.5		12-Apr-08		14:06:20		68.61		33.5		12-Apr-08		14:07:53		70.41		40.5		23-May-08		14:25:59		74.01		29

		12-Apr-08		16:07:10		67.4		48		12-Apr-08		16:06:20		67.4		35		12-Apr-08		16:07:53		72.21		40		23-May-08		16:25:59		74.6		30

		12-Apr-08		18:07:10		67.4		45.5		12-Apr-08		18:06:20		67.4		34		12-Apr-08		18:07:53		68		45		23-May-08		18:25:59		74.01		31

		12-Apr-08		20:07:10		67.4		46.5		12-Apr-08		20:06:20		66.81		32.5		12-Apr-08		20:07:53		68		45		23-May-08		20:25:59		74.01		32

		12-Apr-08		22:07:10		67.4		46.5		12-Apr-08		22:06:20		66.2		38.5		12-Apr-08		22:07:53		68		44		23-May-08		22:25:59		74.6		31.5

		13-Apr-08		0:07:10		67.4		46		13-Apr-08		0:06:20		66.81		41		13-Apr-08		0:07:53		66.81		46		24-May-08		0:25:59		73.4		31.5

		13-Apr-08		2:07:10		67.4		46		13-Apr-08		2:06:20		65.6		42		13-Apr-08		2:07:53		66.81		45.5		24-May-08		2:25:59		72.21		32

		13-Apr-08		4:07:10		68		45.5		13-Apr-08		4:06:20		65.6		41		13-Apr-08		4:07:53		66.2		46.5		24-May-08		4:25:59		71.6		32

		13-Apr-08		6:07:10		68		46.5		13-Apr-08		6:06:20		66.81		40		13-Apr-08		6:07:53		66.2		47		24-May-08		6:25:59		72.21		31.5

		13-Apr-08		8:07:10		67.4		46.5		13-Apr-08		8:06:20		66.2		40.5		13-Apr-08		8:07:53		66.2		47.5		24-May-08		8:25:59		71.6		33

		13-Apr-08		10:07:10		68		47		13-Apr-08		10:06:20		66.81		42		13-Apr-08		10:07:53		66.81		47		24-May-08		10:25:59		74.01		33.5

		13-Apr-08		12:07:10		67.4		46		13-Apr-08		12:06:20		67.4		41.5		13-Apr-08		12:07:53		67.4		45.5		24-May-08		12:25:59		73.4		35

		13-Apr-08		14:07:10		67.4		46.5		13-Apr-08		14:06:20		67.4		43		13-Apr-08		14:07:53		67.4		46		24-May-08		14:25:59		74.01		35

		13-Apr-08		16:07:10		67.4		46		13-Apr-08		16:06:20		66.81		40		13-Apr-08		16:07:53		68		45.5		24-May-08		16:25:59		74.01		34.5

		13-Apr-08		18:07:10		67.4		46.5		13-Apr-08		18:06:20		66.81		38.5		13-Apr-08		18:07:53		67.4		45.5		24-May-08		18:25:59		74.01		34.5

		13-Apr-08		20:07:10		68		46		13-Apr-08		20:06:20		66.2		43.5		13-Apr-08		20:07:53		67.4		46		24-May-08		20:25:59		74.01		35.5

		13-Apr-08		22:07:10		67.4		47.5		13-Apr-08		22:06:20		66.2		53.5		13-Apr-08		22:07:53		67.4		46.5		24-May-08		22:25:59		74.01		35

		14-Apr-08		0:07:10		67.4		46		14-Apr-08		0:06:20		66.2		48.5		14-Apr-08		0:07:53		66.81		47		25-May-08		0:25:59		72.8		35.5

		14-Apr-08		2:07:10		67.4		46		14-Apr-08		2:06:20		66.2		46		14-Apr-08		2:07:53		66.81		47		25-May-08		2:25:59		72.21		36

		14-Apr-08		4:07:10		67.4		46		14-Apr-08		4:06:20		65.6		45.5		14-Apr-08		4:07:53		66.2		47.5		25-May-08		4:25:59		71.6		36.5

		14-Apr-08		6:07:10		68.61		46		14-Apr-08		6:06:20		65.6		44		14-Apr-08		6:07:53		66.2		48		25-May-08		6:25:59		71.6		37

		14-Apr-08		8:07:10		67.4		46		14-Apr-08		8:06:20		66.2		41.5		14-Apr-08		8:07:53		66.2		47		25-May-08		8:25:59		71.6		37.5

		14-Apr-08		10:07:10		68		46		14-Apr-08		10:06:20		66.2		43		14-Apr-08		10:07:53		66.2		48		25-May-08		10:25:59		71.6		38.5

		14-Apr-08		12:07:10		67.4		46		14-Apr-08		12:06:20		67.4		43		14-Apr-08		12:07:53		66.81		47		25-May-08		12:25:59		71.6		40

		14-Apr-08		14:07:10		67.4		48		14-Apr-08		14:06:20		67.4		45.5		14-Apr-08		14:07:53		67.4		48.5		25-May-08		14:25:59		71.6		40.5

		14-Apr-08		16:07:10		67.4		46		14-Apr-08		16:06:20		66.81		43		14-Apr-08		16:07:53		66.81		47		25-May-08		16:25:59		71.6		40

		14-Apr-08		18:07:10		67.4		47		14-Apr-08		18:06:20		66.81		46.5		14-Apr-08		18:07:53		66.81		48		25-May-08		18:25:59		71.6		41

		14-Apr-08		20:07:10		67.4		47		14-Apr-08		20:06:20		66.2		50		14-Apr-08		20:07:53		66.2		48		25-May-08		20:25:59		71.6		41

		14-Apr-08		22:07:10		68		45.5		14-Apr-08		22:06:20		66.2		46		14-Apr-08		22:07:53		66.2		48		25-May-08		22:25:59		71.6		41

		15-Apr-08		0:07:10		67.4		46		15-Apr-08		0:06:20		65.6		49		15-Apr-08		0:07:53		66.81		47		26-May-08		0:25:59		71.6		40

		15-Apr-08		2:07:10		67.4		47		15-Apr-08		2:06:20		66.2		46		15-Apr-08		2:07:53		66.81		47.5		26-May-08		2:25:59		71.6		38.5

		15-Apr-08		4:07:10		67.4		44		15-Apr-08		4:06:20		65.6		45		15-Apr-08		4:07:53		66.81		47.5		26-May-08		4:25:59		71.6		37.5

		15-Apr-08		6:07:10		68		46		15-Apr-08		6:06:20		65.01		45		15-Apr-08		6:07:53		66.2		48		26-May-08		6:25:59		71.6		37

		15-Apr-08		8:07:10		67.4		45.5		15-Apr-08		8:06:20		67.4		45		15-Apr-08		8:07:53		65.6		49.5		26-May-08		8:25:59		71.6		37.5

		15-Apr-08		10:07:10		67.4		47		15-Apr-08		10:06:20		69.2		44		15-Apr-08		10:07:53		65.01		49		26-May-08		10:25:59		71.6		39.5

		15-Apr-08		12:07:10		67.4		47		15-Apr-08		12:06:20		69.8		37.5		15-Apr-08		12:07:53		65.6		49		26-May-08		12:25:59		72.21		38.5

		15-Apr-08		14:07:10		67.4		41		15-Apr-08		14:06:20		71		33.5		15-Apr-08		14:07:53		66.2		47.5		26-May-08		14:25:59		72.8		38

		15-Apr-08		16:07:10		67.4		45.5		15-Apr-08		16:06:20		70.41		32.5		15-Apr-08		16:07:53		66.81		47		26-May-08		16:25:59		73.4		36.5

		15-Apr-08		18:07:10		67.4		45.5		15-Apr-08		18:06:20		69.2		31.5		15-Apr-08		18:07:53		68		45.5		26-May-08		18:25:59		74.01		36

		15-Apr-08		20:07:10		67.4		45		15-Apr-08		20:06:20		69.2		29		15-Apr-08		20:07:53		67.4		45		26-May-08		20:25:59		74.01		35.5

		15-Apr-08		22:07:10		68		45.5		15-Apr-08		22:06:20		68		31.5		15-Apr-08		22:07:53		67.4		45		26-May-08		22:25:59		72.21		37

		16-Apr-08		0:07:10		67.4		37		16-Apr-08		0:06:20		66.81		34.5		16-Apr-08		0:07:53		67.4		45.5		27-May-08		0:25:59		72.21		37.5

		16-Apr-08		2:07:10		67.4		46.5		16-Apr-08		2:06:20		65.6		33		16-Apr-08		2:07:53		68		44.5		27-May-08		2:25:59		71.6		37.5

		16-Apr-08		4:07:10		67.4		45		16-Apr-08		4:06:20		65.01		33		16-Apr-08		4:07:53		68		45		27-May-08		4:25:59		71.6		37.5

		16-Apr-08		6:07:10		67.4		45.5		16-Apr-08		6:06:20		65.01		33.5		16-Apr-08		6:07:53		68		44.5		27-May-08		6:25:59		72.21		37.5

		16-Apr-08		8:07:10		67.4		46		16-Apr-08		8:06:20		68		32.5		16-Apr-08		8:07:53		67.4		44		27-May-08		8:25:59		71		39

		16-Apr-08		10:07:10		69.2		34		16-Apr-08		10:06:20		70.41		30		16-Apr-08		10:07:53		66.2		47.5		27-May-08		10:25:59		71		39.5

		16-Apr-08		12:07:10		69.8		44		16-Apr-08		12:06:20		68.61		27.5		16-Apr-08		12:07:53		66.2		48		27-May-08		12:25:59		72.21		40.5

		16-Apr-08		14:07:10		70.41		43		16-Apr-08		14:06:20		69.8		26		16-Apr-08		14:07:53		66.2		49.5		27-May-08		14:25:59		72.8		40

		16-Apr-08		16:07:10		70.41		46		16-Apr-08		16:06:20		69.2		28		16-Apr-08		16:07:53		67.4		47		27-May-08		16:25:59		72.8		39.5

		16-Apr-08		18:07:10		70.41		45.5		16-Apr-08		18:06:20		68.61		31		16-Apr-08		18:07:53		68		48		27-May-08		18:25:59		72.8		41

		16-Apr-08		20:07:10		69.2		44.5		16-Apr-08		20:06:20		68		30		16-Apr-08		20:07:53		67.4		44.5		27-May-08		20:25:59		72.8		40.5

		16-Apr-08		22:07:10		69.2		44.5		16-Apr-08		22:06:20		68		30		16-Apr-08		22:07:53		68		45		27-May-08		22:25:59		72.21		39.5

		17-Apr-08		0:07:10		70.41		46		17-Apr-08		0:06:20		67.4		31.5		17-Apr-08		0:07:53		68		41		28-May-08		0:25:59		72.21		39.5

		17-Apr-08		2:07:10		70.41		43.5		17-Apr-08		2:06:20		66.2		33		17-Apr-08		2:07:53		68		48.5		28-May-08		2:25:59		72.21		40

		17-Apr-08		4:07:10		69.8		46		17-Apr-08		4:06:20		65.6		34		17-Apr-08		4:07:53		68		46.5		28-May-08		4:25:59		71.6		40

		17-Apr-08		6:07:10		69.8		46		17-Apr-08		6:06:20		65.6		34.5		17-Apr-08		6:07:53		68		47		28-May-08		6:25:59		72.21		40.5

		17-Apr-08		8:07:10		71		44.5		17-Apr-08		8:06:20		69.2		33		17-Apr-08		8:07:53		67.4		48		28-May-08		8:25:59		71.6		42.5

		17-Apr-08		10:07:10		70.41		44.5		17-Apr-08		10:06:20		70.41		31.5		17-Apr-08		10:07:53		66.81		45.5		28-May-08		10:25:59		73.4		42

		17-Apr-08		12:07:10		71		45.5		17-Apr-08		12:06:20		71		29		17-Apr-08		12:07:53		68		48.5		28-May-08		12:25:59		74.01		41

		17-Apr-08		14:07:10		71		45.5		17-Apr-08		14:06:20		69.2		29.5		17-Apr-08		14:07:53		67.4		49.5		28-May-08		14:25:59		74.01		41.5

		17-Apr-08		16:07:10		71		45.5		17-Apr-08		16:06:20		68.61		31.5		17-Apr-08		16:07:53		68		48		28-May-08		16:25:59		74.6		39.5

		17-Apr-08		18:07:10		71		46.5		17-Apr-08		18:06:20		70.41		31		17-Apr-08		18:07:53		68.61		48		28-May-08		18:25:59		75.2		38

		17-Apr-08		20:07:10		71		44.5		17-Apr-08		20:06:20		69.8		34.5		17-Apr-08		20:07:53		67.4		46.5		28-May-08		20:25:59		74.6		39.5

		17-Apr-08		22:07:10		69.8		42.5		17-Apr-08		22:06:20		69.8		36.5		17-Apr-08		22:07:53		67.4		46		28-May-08		22:25:59		74.01		38

		18-Apr-08		0:07:10		70.41		45.5		18-Apr-08		0:06:20		68.61		38		18-Apr-08		0:07:53		68		48.5		29-May-08		0:25:59		72.8		38

		18-Apr-08		2:07:10		70.41		42.5		18-Apr-08		2:06:20		67.4		39		18-Apr-08		2:07:53		68		47.5		29-May-08		2:25:59		72.21		38

		18-Apr-08		4:07:10		69.8		46.5		18-Apr-08		4:06:20		66.2		39.5		18-Apr-08		4:07:53		68		47.5		29-May-08		4:25:59		72.21		38.5

		18-Apr-08		6:07:10		69.8		46		18-Apr-08		6:06:20		65.6		40		18-Apr-08		6:07:53		68		42		29-May-08		6:25:59		72.8		38.5

		18-Apr-08		8:07:10		70.41		46.5		18-Apr-08		8:06:20		68.61		39		18-Apr-08		8:07:53		67.4		49		29-May-08		8:25:59		72.8		40

		18-Apr-08		10:07:10		70.41		46		18-Apr-08		10:06:20		71		37.5		18-Apr-08		10:07:53		67.4		47.5		29-May-08		10:25:59		74.01		39

		18-Apr-08		12:07:10		71		44		18-Apr-08		12:06:20		72.21		36.5		18-Apr-08		12:07:53		68		49		29-May-08		12:25:59		74.6		39.5

		18-Apr-08		14:07:10		70.41		44.5		18-Apr-08		14:06:20		71		34.5		18-Apr-08		14:07:53		66.81		49.5		29-May-08		14:25:59		75.2		39

		18-Apr-08		16:07:10		70.41		42.5		18-Apr-08		16:06:20		71		39		18-Apr-08		16:07:53		67.4		49		29-May-08		16:25:59		74.6		39

		18-Apr-08		18:07:10		70.41		45		18-Apr-08		18:06:20		70.41		38		18-Apr-08		18:07:53		68		47.5		29-May-08		18:25:59		74.6		38

		18-Apr-08		20:07:10		70.41		44.5		18-Apr-08		20:06:20		69.8		41		18-Apr-08		20:07:53		67.4		48.5		29-May-08		20:25:59		74.6		39.5

		18-Apr-08		22:07:10		70.41		45.5		18-Apr-08		22:06:20		69.2		41		18-Apr-08		22:07:53		68		48.5		29-May-08		22:25:59		74.6		38.5

		19-Apr-08		0:07:10		69.8		44.5		19-Apr-08		0:06:20		68		42.5		19-Apr-08		0:07:53		67.4		49		30-May-08		0:25:59		74.01		38.5

		19-Apr-08		2:07:10		69.8		45		19-Apr-08		2:06:20		67.4		45		19-Apr-08		2:07:53		67.4		49		30-May-08		2:25:59		72.8		38.5

		19-Apr-08		4:07:10		69.8		40		19-Apr-08		4:06:20		66.81		45		19-Apr-08		4:07:53		68		46.5		30-May-08		4:25:59		72.21		39

		19-Apr-08		6:07:10		69.8		45.5		19-Apr-08		6:06:20		66.81		45		19-Apr-08		6:07:53		68		49		30-May-08		6:25:59		72.21		39.5

		19-Apr-08		8:07:10		69.8		45		19-Apr-08		8:06:20		71		41		19-Apr-08		8:07:53		66.81		50		30-May-08		8:25:59		72.21		41.5

		19-Apr-08		10:07:10		69.8		45		19-Apr-08		10:06:20		71.6		40.5		19-Apr-08		10:07:53		66.81		50		30-May-08		10:25:59		74.6		41.5

		19-Apr-08		12:07:10		70.41		44.5		19-Apr-08		12:06:20		71.6		39		19-Apr-08		12:07:53		66.81		50		30-May-08		12:25:59		74.6		41.5

		19-Apr-08		14:07:10		70.41		42		19-Apr-08		14:06:20		72.8		41		19-Apr-08		14:07:53		66.81		48		30-May-08		14:25:59		74.6		41.5

		19-Apr-08		16:07:10		70.41		45		19-Apr-08		16:06:20		69.8		42.5		19-Apr-08		16:07:53		67.4		48		30-May-08		16:25:59		75.2		40.5

		19-Apr-08		18:07:10		69.8		45		19-Apr-08		18:06:20		69.8		43.5		19-Apr-08		18:07:53		67.4		49.5		30-May-08		18:25:59		74.6		39

		19-Apr-08		20:07:10		69.8		42		19-Apr-08		20:06:20		68.61		41		19-Apr-08		20:07:53		67.4		46		30-May-08		20:25:59		74.6		41

		19-Apr-08		22:07:10		69.8		44.5		19-Apr-08		22:06:20		68.61		39		19-Apr-08		22:07:53		67.4		49.5		30-May-08		22:25:59		74.6		39.5

		20-Apr-08		0:07:10		69.2		44		20-Apr-08		0:06:20		67.4		40		20-Apr-08		0:07:53		67.4		49.5		31-May-08		0:25:59		74.01		39

		20-Apr-08		2:07:10		69.2		44.5		20-Apr-08		2:06:20		66.2		40		20-Apr-08		2:07:53		67.4		48		31-May-08		2:25:59		72.8		39.5

		20-Apr-08		4:07:10		68.61		45.5		20-Apr-08		4:06:20		65.01		38.5		20-Apr-08		4:07:53		66.81		48.5		31-May-08		4:25:59		72.21		40

		20-Apr-08		6:07:10		68.61		46.5		20-Apr-08		6:06:20		65.01		36		20-Apr-08		6:07:53		67.4		48.5		31-May-08		6:25:59		71.6		41

		20-Apr-08		8:07:10		68.61		47		20-Apr-08		8:06:20		65.01		33.5		20-Apr-08		8:07:53		67.4		47.5		31-May-08		8:25:59		71.6		42

		20-Apr-08		10:07:10		68.61		46		20-Apr-08		10:06:20		67.4		30		20-Apr-08		10:07:53		68		47.5		31-May-08		10:25:59		73.4		42.5

		20-Apr-08		12:07:10		69.2		43.5		20-Apr-08		12:06:20		69.2		26		20-Apr-08		12:07:53		67.4		44.5		31-May-08		12:25:59		74.6		42

		20-Apr-08		14:07:10		69.2		43.5		20-Apr-08		14:06:20		69.2		23		20-Apr-08		14:07:53		66.81		36.5		31-May-08		14:25:59		75.2		43.5

		20-Apr-08		16:07:10		69.2		45		20-Apr-08		16:06:20		69.2		23.5		20-Apr-08		16:07:53		67.4		47.5		31-May-08		16:25:59		74.6		43

		20-Apr-08		18:07:10		69.2		44		20-Apr-08		18:06:20		69.8		23		20-Apr-08		18:07:53		67.4		44.5		31-May-08		18:25:59		74.6		44.5

		20-Apr-08		20:07:10		69.2		45.5		20-Apr-08		20:06:20		68		25.5		20-Apr-08		20:07:53		67.4		47		31-May-08		20:25:59		74.6		43

		20-Apr-08		22:07:10		68.61		45		20-Apr-08		22:06:20		66.81		27.5		20-Apr-08		22:07:53		67.4		47.5		31-May-08		22:25:59		74.01		41

		21-Apr-08		0:07:10		68.61		46.5		21-Apr-08		0:06:20		65.6		29		21-Apr-08		0:07:53		67.4		48.5		1-Jun-08		0:25:59		72.8		41

		21-Apr-08		2:07:10		68		44.5		21-Apr-08		2:06:20		65.01		30.5		21-Apr-08		2:07:53		66.81		37.5		1-Jun-08		2:25:59		72.21		40.5

		21-Apr-08		4:07:10		68		46.5		21-Apr-08		4:06:20		63.8		31.5		21-Apr-08		4:07:53		66.81		47.5		1-Jun-08		4:25:59		71.6		40.5

		21-Apr-08		6:07:10		68		47.5		21-Apr-08		6:06:20		63.21		33		21-Apr-08		6:07:53		67.4		47.5		1-Jun-08		6:25:59		72.21		40.5

		21-Apr-08		8:07:10		68		44		21-Apr-08		8:06:20		63.21		33		21-Apr-08		8:07:53		67.4		47.5		1-Jun-08		8:25:59		72.21		40.5

		21-Apr-08		10:07:10		68		47.5		21-Apr-08		10:06:20		65.01		29		21-Apr-08		10:07:53		67.4		47.5		1-Jun-08		10:25:59		72.21		40.5

		21-Apr-08		12:07:10		68		42.5		21-Apr-08		12:06:20		67.4		24.5		21-Apr-08		12:07:53		67.4		42		1-Jun-08		12:25:59		73.4		41

		21-Apr-08		14:07:10		68.61		45.5		21-Apr-08		14:06:20		69.2		27.5		21-Apr-08		14:07:53		67.4		48		1-Jun-08		14:25:59		74.6		41.5

		21-Apr-08		16:07:10		68.61		45		21-Apr-08		16:06:20		69.2		29.5		21-Apr-08		16:07:53		67.4		48		1-Jun-08		16:25:59		75.81		41

		21-Apr-08		18:07:10		68.61		45		21-Apr-08		18:06:20		69.2		27		21-Apr-08		18:07:53		66.81		46.5		1-Jun-08		18:25:59		77		39.5

		21-Apr-08		20:07:10		69.2		45		21-Apr-08		20:06:20		68		30		21-Apr-08		20:07:53		67.4		48		1-Jun-08		20:25:59		76.4		39.5

		21-Apr-08		22:07:10		68.61		46.5		21-Apr-08		22:06:20		66.2		32		21-Apr-08		22:07:53		67.4		48.5		1-Jun-08		22:25:59		74.6		39

		22-Apr-08		0:07:10		68.61		45		22-Apr-08		0:06:20		65.01		30		22-Apr-08		0:07:53		67.4		48		2-Jun-08		0:25:59		72.8		39

		22-Apr-08		2:07:10		68		47		22-Apr-08		2:06:20		64.4		32		22-Apr-08		2:07:53		67.4		48		2-Jun-08		2:25:59		72.21		38.5

		22-Apr-08		4:07:10		67.4		47		22-Apr-08		4:06:20		63.8		32.5		22-Apr-08		4:07:53		66.81		41		2-Jun-08		4:25:59		72.21		38

		22-Apr-08		6:07:10		68		46.5		22-Apr-08		6:06:20		63.21		34		22-Apr-08		6:07:53		67.4		48		2-Jun-08		6:25:59		71.6		37.5

		22-Apr-08		8:07:10		68.61		47		22-Apr-08		8:06:20		66.81		33.5		22-Apr-08		8:07:53		66.81		49		2-Jun-08		8:25:59		71.6		38

		22-Apr-08		10:07:10		69.2		44.5		22-Apr-08		10:06:20		71		29.5		22-Apr-08		10:07:53		66.2		49.5		2-Jun-08		10:25:59		72.21		39

		22-Apr-08		12:07:10		69.8		44		22-Apr-08		12:06:20		71		27.5		22-Apr-08		12:07:53		66.81		48		2-Jun-08		12:25:59		73.4		38.5

		22-Apr-08		14:07:10		69.8		46		22-Apr-08		14:06:20		71		31		22-Apr-08		14:07:53		66.2		49.5		2-Jun-08		14:25:59		75.2		38

		22-Apr-08		16:07:10		69.2		44.5		22-Apr-08		16:06:20		69.8		32.5		22-Apr-08		16:07:53		67.4		47.5		2-Jun-08		16:25:59		75.81		38

		22-Apr-08		18:07:10		69.2		45		22-Apr-08		18:06:20		69.8		32		22-Apr-08		18:07:53		68		46.5		2-Jun-08		18:25:59		76.4		37

		22-Apr-08		20:07:10		69.8		45		22-Apr-08		20:06:20		69.2		31.5		22-Apr-08		20:07:53		68		46.5		2-Jun-08		20:25:59		75.81		37

		22-Apr-08		22:07:10		69.8		43.5		22-Apr-08		22:06:20		68		32		22-Apr-08		22:07:53		68		47		2-Jun-08		22:25:59		74.01		37.5

		23-Apr-08		0:07:10		69.2		45		23-Apr-08		0:06:20		66.81		32		23-Apr-08		0:07:53		67.4		47.5		3-Jun-08		0:25:59		72.21		37

		23-Apr-08		2:07:10		68.61		45		23-Apr-08		2:06:20		65.6		33		23-Apr-08		2:07:53		67.4		47		3-Jun-08		2:25:59		72.21		36.5

		23-Apr-08		4:07:10		68.61		46.5		23-Apr-08		4:06:20		65.01		34.5		23-Apr-08		4:07:53		67.4		47.5		3-Jun-08		4:25:59		71.6		36

		23-Apr-08		6:07:10		68.61		43.5		23-Apr-08		6:06:20		64.4		35.5		23-Apr-08		6:07:53		67.4		47.5		3-Jun-08		6:25:59		72.21		35.5

		23-Apr-08		8:07:10		69.2		42.5		23-Apr-08		8:06:20		66.81		35.5		23-Apr-08		8:07:53		67.4		48		3-Jun-08		8:25:59		71.6		37.5

		23-Apr-08		10:07:10		69.8		46		23-Apr-08		10:06:20		70.41		32.5		23-Apr-08		10:07:53		67.4		48		3-Jun-08		10:25:59		74.01		38

		23-Apr-08		12:07:10		69.2		45.5		23-Apr-08		12:06:20		71		35.5		23-Apr-08		12:07:53		66.81		49.5		3-Jun-08		12:25:59		74.01		39

		23-Apr-08		14:07:10		69.8		45		23-Apr-08		14:06:20		71.6		41		23-Apr-08		14:07:53		66.2		50.5		3-Jun-08		14:25:59		74.6		39.5

		23-Apr-08		16:07:10		70.41		47		23-Apr-08		16:06:20		69.8		49		23-Apr-08		16:07:53		67.4		50.5		3-Jun-08		16:25:59		74.6		39

		23-Apr-08		18:07:10		70.41		44.5		23-Apr-08		18:06:20		69.2		47.5		23-Apr-08		18:07:53		68		50		3-Jun-08		18:25:59		74.6		38.5

		23-Apr-08		20:07:10		70.41		46		23-Apr-08		20:06:20		69.8		49.5		23-Apr-08		20:07:53		68		50		3-Jun-08		20:25:59		74.6		34.5

		23-Apr-08		22:07:10		70.41		46.5		23-Apr-08		22:06:20		69.2		48.5		23-Apr-08		22:07:53		68		50		3-Jun-08		22:25:59		74.6		31.5

		24-Apr-08		0:07:10		70.41		47		24-Apr-08		0:06:20		68		47		24-Apr-08		0:07:53		68		49.5		4-Jun-08		0:25:59		73.4		32.5

		24-Apr-08		2:07:10		69.8		44.5		24-Apr-08		2:06:20		66.81		47.5		24-Apr-08		2:07:53		68		49.5		4-Jun-08		2:25:59		72.8		33.5

		24-Apr-08		4:07:10		69.8		46.5		24-Apr-08		4:06:20		66.2		46		24-Apr-08		4:07:53		68		48.5		4-Jun-08		4:25:59		72.21		34

		24-Apr-08		6:07:10		69.8		46.5		24-Apr-08		6:06:20		65.6		44.5		24-Apr-08		6:07:53		68		49		4-Jun-08		6:25:59		72.21		33.5

		24-Apr-08		8:07:10		70.41		47		24-Apr-08		8:06:20		68		44		24-Apr-08		8:07:53		67.4		50		4-Jun-08		8:25:59		72.21		37

		24-Apr-08		10:07:10		70.41		46		24-Apr-08		10:06:20		70.41		46		24-Apr-08		10:07:53		68		49.5		4-Jun-08		10:25:59		74.01		41.5

		24-Apr-08		12:07:10		70.41		46.5		24-Apr-08		12:06:20		69.8		44.5		24-Apr-08		12:07:53		68		50		4-Jun-08		12:25:59		74.01		44

		24-Apr-08		14:07:10		70.41		46		24-Apr-08		14:06:20		71		36		24-Apr-08		14:07:53		68		49		4-Jun-08		14:25:59		74.01		44.5

		24-Apr-08		16:07:10		70.41		44.5		24-Apr-08		16:06:20		69.8		32		24-Apr-08		16:07:53		68		48		4-Jun-08		16:25:59		73.4		42

		24-Apr-08		18:07:10		69.8		44		24-Apr-08		18:06:20		70.41		31		24-Apr-08		18:07:53		68		45		4-Jun-08		18:25:59		73.4		39

		24-Apr-08		20:07:10		70.41		46		24-Apr-08		20:06:20		69.8		30.5		24-Apr-08		20:07:53		69.2		46.5		4-Jun-08		20:25:59		74.6		39.5

		24-Apr-08		22:07:10		70.41		46		24-Apr-08		22:06:20		68		33		24-Apr-08		22:07:53		68		48.5		4-Jun-08		22:25:59		74.6		38

		25-Apr-08		0:07:10		69.8		45		25-Apr-08		0:06:20		66.2		34		25-Apr-08		0:07:53		68		48.5		5-Jun-08		0:25:59		74.01		37.5

		25-Apr-08		2:07:10		69.2		46		25-Apr-08		2:06:20		65.01		35.5		25-Apr-08		2:07:53		68.61		46		5-Jun-08		2:25:59		72.8		36.5

		25-Apr-08		4:07:10		69.2		45		25-Apr-08		4:06:20		63.8		36		25-Apr-08		4:07:53		68		47.5		5-Jun-08		4:25:59		72.21		36

		25-Apr-08		6:07:10		69.8		45		25-Apr-08		6:06:20		63.21		36		25-Apr-08		6:07:53		68.61		47.5		5-Jun-08		6:25:59		72.21		35.5

		25-Apr-08		8:07:10		69.8		46		25-Apr-08		8:06:20		66.81		35.5		25-Apr-08		8:07:53		68.61		47.5		5-Jun-08		8:25:59		72.21		35.5

		25-Apr-08		10:07:10		69.8		45		25-Apr-08		10:06:20		70.41		32.5		25-Apr-08		10:07:53		67.4		49.5		5-Jun-08		10:25:59		74.01		35.5

		25-Apr-08		12:07:10		70.41		42.5		25-Apr-08		12:06:20		71		28.5		25-Apr-08		12:07:53		68.61		48		5-Jun-08		12:25:59		73.4		35

		25-Apr-08		14:07:10		70.41		45.5		25-Apr-08		14:06:20		71		28		25-Apr-08		14:07:53		68		47.5		5-Jun-08		14:25:59		73.4		34

		25-Apr-08		16:07:10		70.41		46		25-Apr-08		16:06:20		71.6		32.5		25-Apr-08		16:07:53		68.61		48.5		5-Jun-08		16:25:59		74.01		34.5

		25-Apr-08		18:07:10		70.41		45.5		25-Apr-08		18:06:20		70.41		31		25-Apr-08		18:07:53		68		40.5		5-Jun-08		18:25:59		73.4		35

		25-Apr-08		20:07:10		70.41		41.5		25-Apr-08		20:06:20		71		32.5		25-Apr-08		20:07:53		68		48		5-Jun-08		20:25:59		74.01		35.5

		25-Apr-08		22:07:10		69.8		45		25-Apr-08		22:06:20		70.41		35.5		25-Apr-08		22:07:53		68		46		5-Jun-08		22:25:59		74.6		34

		26-Apr-08		0:07:10		70.41		46		26-Apr-08		0:06:20		69.2		36.5		26-Apr-08		0:07:53		68		49		6-Jun-08		0:25:59		74.01		34.5

		26-Apr-08		2:07:10		69.8		45.5		26-Apr-08		2:06:20		67.4		38.5		26-Apr-08		2:07:53		68.61		48		6-Jun-08		2:25:59		72.21		35

		26-Apr-08		4:07:10		69.8		44.5		26-Apr-08		4:06:20		66.2		39		26-Apr-08		4:07:53		68		48		6-Jun-08		4:25:59		71.6		35

		26-Apr-08		6:07:10		69.8		46		26-Apr-08		6:06:20		65.6		38.5		26-Apr-08		6:07:53		68.61		48		6-Jun-08		6:25:59		71.6		35

		26-Apr-08		8:07:10		70.41		46.5		26-Apr-08		8:06:20		68.61		37.5		26-Apr-08		8:07:53		68.61		48.5		6-Jun-08		8:25:59		72.21		37

		26-Apr-08		10:07:10		70.41		45.5		26-Apr-08		10:06:20		71		35.5		26-Apr-08		10:07:53		68		46.5		6-Jun-08		10:25:59		73.4		37.5

		26-Apr-08		12:07:10		71		46.5		26-Apr-08		12:06:20		71		32.5		26-Apr-08		12:07:53		68.61		49		6-Jun-08		12:25:59		73.4		35.5

		26-Apr-08		14:07:10		71		32		26-Apr-08		14:06:20		69.2		31		26-Apr-08		14:07:53		67.4		36		6-Jun-08		14:25:59		74.01		37.5

		26-Apr-08		16:07:10		71		35		26-Apr-08		16:06:20		68.61		36		26-Apr-08		16:07:53		67.4		39.5		6-Jun-08		16:25:59		74.01		38.5

		26-Apr-08		18:07:10		71		39.5		26-Apr-08		18:06:20		69.2		39.5		26-Apr-08		18:07:53		68.61		42.5		6-Jun-08		18:25:59		73.4		38.5

		26-Apr-08		20:07:10		70.41		38		26-Apr-08		20:06:20		69.2		41		26-Apr-08		20:07:53		68.61		41		6-Jun-08		20:25:59		74.01		41

		26-Apr-08		22:07:10		69.8		38		26-Apr-08		22:06:20		68		42		26-Apr-08		22:07:53		68.61		40.5		6-Jun-08		22:25:59		74.6		39

		27-Apr-08		0:07:10		69.8		36.5		27-Apr-08		0:06:20		68		39.5		27-Apr-08		0:07:53		68.61		39.5		7-Jun-08		0:25:59		74.01		38.5

		27-Apr-08		2:07:10		70.41		36.5		27-Apr-08		2:06:20		68		39.5		27-Apr-08		2:07:53		68.61		39.5		7-Jun-08		2:25:59		72.8		39

		27-Apr-08		4:07:10		70.41		37.5		27-Apr-08		4:06:20		66.81		42.5		27-Apr-08		4:07:53		68.61		39.5		7-Jun-08		4:25:59		71.6		38.5

		27-Apr-08		6:07:10		69.8		36		27-Apr-08		6:06:20		67.4		40.5		27-Apr-08		6:07:53		68		39		7-Jun-08		6:25:59		72.21		37.5

		27-Apr-08		8:07:10		69.8		37.5		27-Apr-08		8:06:20		68		42		27-Apr-08		8:07:53		68.61		40.5		7-Jun-08		8:25:59		72.21		38

		27-Apr-08		10:07:10		70.41		40		27-Apr-08		10:06:20		69.2		43		27-Apr-08		10:07:53		68.61		42.5		7-Jun-08		10:25:59		73.4		37.5

		27-Apr-08		12:07:10		71		40		27-Apr-08		12:06:20		69.2		42.5		27-Apr-08		12:07:53		68		44		7-Jun-08		12:25:59		73.4		36

		27-Apr-08		14:07:10		71		40		27-Apr-08		14:06:20		69.2		40.5		27-Apr-08		14:07:53		69.2		42.5		7-Jun-08		14:25:59		73.4		34

		27-Apr-08		16:07:10		71		43		27-Apr-08		16:06:20		69.2		47		27-Apr-08		16:07:53		69.2		46		7-Jun-08		16:25:59		73.4		33.5

		27-Apr-08		18:07:10		71		42.5		27-Apr-08		18:06:20		69.2		43.5		27-Apr-08		18:07:53		69.2		44		7-Jun-08		18:25:59		73.4		34

		27-Apr-08		20:07:10		71.6		38		27-Apr-08		20:06:20		68		43.5		27-Apr-08		20:07:53		68.61		42.5		7-Jun-08		20:25:59		74.01		35

		27-Apr-08		22:07:10		71		37.5		27-Apr-08		22:06:20		68		42.5		27-Apr-08		22:07:53		68.61		41		7-Jun-08		22:25:59		74.01		33.5

		28-Apr-08		0:07:10		70.41		38.5		28-Apr-08		0:06:20		68		40		28-Apr-08		0:07:53		68.61		40		8-Jun-08		0:25:59		73.4		33

		28-Apr-08		2:07:10		69.8		39.5		28-Apr-08		2:06:20		68		45		28-Apr-08		2:07:53		68.61		42		8-Jun-08		2:25:59		72.21		33

		28-Apr-08		4:07:10		69.2		39.5		28-Apr-08		4:06:20		67.4		47.5		28-Apr-08		4:07:53		68		41.5		8-Jun-08		4:25:59		71.6		33

		28-Apr-08		6:07:10		69.2		39.5		28-Apr-08		6:06:20		67.4		45		28-Apr-08		6:07:53		68		41.5		8-Jun-08		6:25:59		71.6		33

		28-Apr-08		8:07:10		70.41		40		28-Apr-08		8:06:20		68		47		28-Apr-08		8:07:53		68.61		42.5		8-Jun-08		8:25:59		71.6		33

		28-Apr-08		10:07:10		70.41		40.5		28-Apr-08		10:06:20		68		47.5		28-Apr-08		10:07:53		68.61		43		8-Jun-08		10:25:59		72.21		34

		28-Apr-08		12:07:10		71		40		28-Apr-08		12:06:20		68.61		44		28-Apr-08		12:07:53		69.2		43		8-Jun-08		12:25:59		74.6		33

		28-Apr-08		14:07:10		71		43		28-Apr-08		14:06:20		69.2		43		28-Apr-08		14:07:53		69.2		45.5		8-Jun-08		14:25:59		75.81		31.5

		28-Apr-08		16:07:10		71		44		28-Apr-08		16:06:20		68.61		52		28-Apr-08		16:07:53		69.2		47		8-Jun-08		16:25:59		77		30.5

		28-Apr-08		18:07:10		71		41.5		28-Apr-08		18:06:20		69.2		46		28-Apr-08		18:07:53		68.61		45		8-Jun-08		18:25:59		77		31.5

		28-Apr-08		20:07:10		71		39		28-Apr-08		20:06:20		68.61		45		28-Apr-08		20:07:53		68.61		43		8-Jun-08		20:25:59		77		33.5

		28-Apr-08		22:07:10		71		38.5		28-Apr-08		22:06:20		68.61		43.5		28-Apr-08		22:07:53		68.61		41.5		8-Jun-08		22:25:59		75.81		34.5

		29-Apr-08		0:07:10		69.2		38.5		29-Apr-08		0:06:20		68		45		29-Apr-08		0:07:53		68		41		9-Jun-08		0:25:59		74.6		34

		29-Apr-08		2:07:10		69.8		38		29-Apr-08		2:06:20		67.4		44.5		29-Apr-08		2:07:53		68.61		40.5		9-Jun-08		2:25:59		74.01		34.5

		29-Apr-08		4:07:10		69.8		37.5		29-Apr-08		4:06:20		66.81		44		29-Apr-08		4:07:53		68.61		40		9-Jun-08		4:25:59		72.8		35

		29-Apr-08		6:07:10		69.2		36.5		29-Apr-08		6:06:20		66.2		44		29-Apr-08		6:07:53		68.61		39		9-Jun-08		6:25:59		72.21		35.5

		29-Apr-08		8:07:10		69.8		38.5		29-Apr-08		8:06:20		68		44.5		29-Apr-08		8:07:53		68		41		9-Jun-08		8:25:59		72.21		36.5

		29-Apr-08		10:07:10		70.41		39.5		29-Apr-08		10:06:20		69.8		45		29-Apr-08		10:07:53		68		43		9-Jun-08		10:25:59		74.01		37

		29-Apr-08		12:07:10		71		42		29-Apr-08		12:06:20		70.41		48.5		29-Apr-08		12:07:53		69.2		44.5		9-Jun-08		12:25:59		76.4		36

		29-Apr-08		14:07:10		71		42.5		29-Apr-08		14:06:20		70.41		48		29-Apr-08		14:07:53		68.61		46.5		9-Jun-08		14:25:59		77.61		35

		29-Apr-08		16:07:10		71		43		29-Apr-08		16:06:20		69.8		49		29-Apr-08		16:07:53		68.61		47		9-Jun-08		16:25:59		78.8		34.5

		29-Apr-08		18:07:10		71.6		41.5		29-Apr-08		18:06:20		69.2		48.5		29-Apr-08		18:07:53		68.61		45.5		9-Jun-08		18:25:59		78.2		35.5

		29-Apr-08		20:07:10		71		40		29-Apr-08		20:06:20		69.2		46.5		29-Apr-08		20:07:53		68.61		43.5		9-Jun-08		20:25:59		78.2		35.5

		29-Apr-08		22:07:10		71		39		29-Apr-08		22:06:20		69.2		47.5		29-Apr-08		22:07:53		68.61		42.5		9-Jun-08		22:25:59		76.4		35.5

		30-Apr-08		0:07:10		69.2		33		30-Apr-08		0:06:20		68		34		30-Apr-08		0:07:53		68		35.5		10-Jun-08		0:25:59		74.6		35.5

		30-Apr-08		2:07:10		69.2		35.5		30-Apr-08		2:06:20		68.61		37.5		30-Apr-08		2:07:53		68.61		37.5		10-Jun-08		2:25:59		73.4		36

		30-Apr-08		4:07:10		69.8		35		30-Apr-08		4:06:20		67.4		38.5		30-Apr-08		4:07:53		68.61		37		10-Jun-08		4:25:59		72.8		36

		30-Apr-08		6:07:10		70.41		35		30-Apr-08		6:06:20		69.2		39		30-Apr-08		6:07:53		68.61		38		10-Jun-08		6:25:59		72.21		37

		30-Apr-08		8:07:10		70.41		34		30-Apr-08		8:06:20		69.8		34		30-Apr-08		8:07:53		68		36.5		10-Jun-08		8:25:59		72.8		39

		30-Apr-08		10:07:10		69.2		34		30-Apr-08		10:06:20		69.8		35		30-Apr-08		10:07:53		67.4		37.5		10-Jun-08		10:25:59		73.4		38.5

		30-Apr-08		12:07:10		69.8		32.5		30-Apr-08		12:06:20		69.8		35		30-Apr-08		12:07:53		68		36		10-Jun-08		12:25:59		72.8		39

		30-Apr-08		14:07:10		69.8		33.5		30-Apr-08		14:06:20		69.2		34		30-Apr-08		14:07:53		68.61		36		10-Jun-08		14:25:59		72.8		39

		30-Apr-08		16:07:10		69.8		34		30-Apr-08		16:06:20		69.2		35		30-Apr-08		16:07:53		68.61		36.5		10-Jun-08		16:25:59		72.21		40

		30-Apr-08		18:07:10		69.8		31		30-Apr-08		18:06:20		69.2		32		30-Apr-08		18:07:53		68		33.5		10-Jun-08		18:25:59		72.8		42.5

		30-Apr-08		20:07:10		68.61		31.5		30-Apr-08		20:06:20		68.61		31.5		30-Apr-08		20:07:53		68		33.5		10-Jun-08		20:25:59		74.6		43

		30-Apr-08		22:07:10		69.2		31		30-Apr-08		22:06:20		68.61		32.5		30-Apr-08		22:07:53		68.61		33.5		10-Jun-08		22:25:59		76.4		40.5

		1-May-08		0:07:10		68.61		31.5		1-May-08		0:06:20		67.4		34		1-May-08		0:07:53		68		34		11-Jun-08		0:25:59		75.81		40.5

		1-May-08		2:07:10		68.61		30.5		1-May-08		2:06:20		66.2		33		1-May-08		2:07:53		68		32.5		11-Jun-08		2:25:59		75.2		39

		1-May-08		4:07:10		68		29.5		1-May-08		4:06:20		65.6		32		1-May-08		4:07:53		68		31		11-Jun-08		4:25:59		74.01		38

		1-May-08		6:07:10		68.61		29		1-May-08		6:06:20		65.6		31.5		1-May-08		6:07:53		68		30.5		11-Jun-08		6:25:59		72.8		37.5

		1-May-08		8:07:10		69.2		28		1-May-08		8:06:20		69.2		30		1-May-08		8:07:53		68.61		30.5		11-Jun-08		8:25:59		72.21		37

		1-May-08		10:07:10		69.8		26		1-May-08		10:06:20		70.41		27.5		1-May-08		10:07:53		68.61		29		11-Jun-08		10:25:59		72.8		33

		1-May-08		12:07:10		69.8		24		1-May-08		12:06:20		70.41		24.5		1-May-08		12:07:53		68.61		27		11-Jun-08		12:25:59		72.8		30.5

		1-May-08		14:07:10		70.41		25		1-May-08		14:06:20		71		26		1-May-08		14:07:53		69.8		27		11-Jun-08		14:25:59		74.01		30.5

		1-May-08		16:07:10		71		25.5		1-May-08		16:06:20		69.8		27.5		1-May-08		16:07:53		69.2		27.5		11-Jun-08		16:25:59		74.01		30.5

		1-May-08		18:07:10		70.41		29		1-May-08		18:06:20		70.41		29.5		1-May-08		18:07:53		69.8		30		11-Jun-08		18:25:59		73.4		32

		1-May-08		20:07:10		69.2		29.5		1-May-08		20:06:20		69.2		30		1-May-08		20:07:53		69.2		31		11-Jun-08		20:25:59		74.6		32.5

		1-May-08		22:07:10		69.2		30.5		1-May-08		22:06:20		69.8		30.5		1-May-08		22:07:53		69.2		32		11-Jun-08		22:25:59		75.2		32

		2-May-08		0:07:10		69.8		30.5		2-May-08		0:06:20		68		33		2-May-08		0:07:53		69.2		32.5		12-Jun-08		0:25:59		74.6		32

		2-May-08		2:07:10		69.8		30.5		2-May-08		2:06:20		67.4		33.5		2-May-08		2:07:53		69.2		32		12-Jun-08		2:25:59		73.4		32.5

		2-May-08		4:07:10		69.2		30.5		2-May-08		4:06:20		66.81		34		2-May-08		4:07:53		69.2		31.5		12-Jun-08		4:25:59		72.21		32.5

		2-May-08		6:07:10		69.2		30		2-May-08		6:06:20		66.81		34		2-May-08		6:07:53		69.2		32		12-Jun-08		6:25:59		71.6		32.5

		2-May-08		8:07:10		69.8		30.5		2-May-08		8:06:20		69.2		33		2-May-08		8:07:53		69.8		32		12-Jun-08		8:25:59		72.21		34.5

		2-May-08		10:07:10		69.8		30		2-May-08		10:06:20		69.8		31.5		2-May-08		10:07:53		69.8		31.5		12-Jun-08		10:25:59		73.4		34.5

		2-May-08		12:07:10		70.41		27		2-May-08		12:06:20		69.8		28		2-May-08		12:07:53		70.41		29.5		12-Jun-08		12:25:59		73.4		32.5

		2-May-08		14:07:10		71		23.5		2-May-08		14:06:20		71		25.5		2-May-08		14:07:53		69.8		26		12-Jun-08		14:25:59		72.8		29

		2-May-08		16:07:10		70.41		29.5		2-May-08		16:06:20		69.8		31		2-May-08		16:07:53		69.2		31		12-Jun-08		16:25:59		73.4		27.5

		2-May-08		18:07:10		70.41		30.5		2-May-08		18:06:20		70.41		31.5		2-May-08		18:07:53		69.8		32		12-Jun-08		18:25:59		73.4		29

		2-May-08		20:07:10		71		34		2-May-08		20:06:20		70.41		34		2-May-08		20:07:53		69.8		34		12-Jun-08		20:25:59		74.6		31.5

		2-May-08		22:07:10		70.41		29		2-May-08		22:06:20		70.41		30		2-May-08		22:07:53		70.41		31		12-Jun-08		22:25:59		75.2		32.5

		3-May-08		0:07:10		69.2		30		3-May-08		0:06:20		69.2		31		3-May-08		0:07:53		69.8		31.5		13-Jun-08		0:25:59		74.6		33

		3-May-08		2:07:10		70.41		33		3-May-08		2:06:20		68.61		36		3-May-08		2:07:53		69.8		34		13-Jun-08		2:25:59		73.4		33.5

		3-May-08		4:07:10		70.41		32.5		3-May-08		4:06:20		67.4		36		3-May-08		4:07:53		69.8		33.5		13-Jun-08		4:25:59		72.8		34

		3-May-08		6:07:10		70.41		32		3-May-08		6:06:20		66.81		36.5		3-May-08		6:07:53		69.8		33.5		13-Jun-08		6:25:59		71.6		35

		3-May-08		8:07:10		70.41		33.5		3-May-08		8:06:20		69.8		35.5		3-May-08		8:07:53		69.2		35		13-Jun-08		8:25:59		72.21		37

		3-May-08		10:07:10		70.41		34		3-May-08		10:06:20		70.41		35.5		3-May-08		10:07:53		69.8		35.5		13-Jun-08		10:25:59		72.21		37

		3-May-08		12:07:10		71		33.5		3-May-08		12:06:20		71		34		3-May-08		12:07:53		69.8		34.5		13-Jun-08		12:25:59		72.21		30.5

		3-May-08		14:07:10		71		36.5		3-May-08		14:06:20		71.6		35		3-May-08		14:07:53		69.8		36.5		13-Jun-08		14:25:59		73.4		27.5

		3-May-08		16:07:10		71		34		3-May-08		16:06:20		70.41		35.5		3-May-08		16:07:53		69.8		36.5		13-Jun-08		16:25:59		73.4		30.5

		3-May-08		18:07:10		71		37.5		3-May-08		18:06:20		71		40		3-May-08		18:07:53		69.8		39		13-Jun-08		18:25:59		73.4		28.5

		3-May-08		20:07:10		71		36.5		3-May-08		20:06:20		70.41		40		3-May-08		20:07:53		69.8		38		13-Jun-08		20:25:59		74.6		29

		3-May-08		22:07:10		71		35.5		3-May-08		22:06:20		69.8		39		3-May-08		22:07:53		69.8		37		13-Jun-08		22:25:59		75.81		29.5

		4-May-08		0:07:10		71		35		4-May-08		0:06:20		68		40		4-May-08		0:07:53		69.2		37		14-Jun-08		0:25:59		75.2		30.5

		4-May-08		2:07:10		70.41		35		4-May-08		2:06:20		66.81		41		4-May-08		2:07:53		69.8		36.5		14-Jun-08		2:25:59		74.01		31.5

		4-May-08		4:07:10		70.41		34.5		4-May-08		4:06:20		66.2		41		4-May-08		4:07:53		69.2		35.5		14-Jun-08		4:25:59		72.8		32

		4-May-08		6:07:10		69.8		33.5		4-May-08		6:06:20		65.6		40		4-May-08		6:07:53		69.8		35		14-Jun-08		6:25:59		72.21		33.5

		4-May-08		8:07:10		70.41		35.5		4-May-08		8:06:20		66.81		41.5		4-May-08		8:07:53		70.41		36		14-Jun-08		8:25:59		72.21		35.5

		4-May-08		10:07:10		70.41		36		4-May-08		10:06:20		69.8		39		4-May-08		10:07:53		70.41		37.5		14-Jun-08		10:25:59		72.8		37

		4-May-08		12:07:10		71		37		4-May-08		12:06:20		71		39.5		4-May-08		12:07:53		70.41		39		14-Jun-08		12:25:59		72.8		39.5

		4-May-08		14:07:10		71		39.5		4-May-08		14:06:20		70.41		45.5		4-May-08		14:07:53		68.61		42.5		14-Jun-08		14:25:59		73.4		38

		4-May-08		16:07:10		71		39.5		4-May-08		16:06:20		70.41		44.5		4-May-08		16:07:53		68.61		43.5		14-Jun-08		16:25:59		72.8		38.5

		4-May-08		18:07:10		71		40		4-May-08		18:06:20		69.8		48		4-May-08		18:07:53		69.2		43		14-Jun-08		18:25:59		73.4		38.5

		4-May-08		20:07:10		71		38.5		4-May-08		20:06:20		69.2		47		4-May-08		20:07:53		68.61		42		14-Jun-08		20:25:59		74.01		37

		4-May-08		22:07:10		71		38		4-May-08		22:06:20		69.8		44		4-May-08		22:07:53		68.61		40.5		14-Jun-08		22:25:59		74.01		37.5

		5-May-08		0:07:10		71		37.5		5-May-08		0:06:20		68.61		44		5-May-08		0:07:53		70.41		39.5		15-Jun-08		0:25:59		72.8		37

		5-May-08		2:07:10		71		37		5-May-08		2:06:20		68		44.5		5-May-08		2:07:53		70.41		38.5		15-Jun-08		2:25:59		72.21		37.5

		5-May-08		4:07:10		70.41		36.5		5-May-08		4:06:20		66.81		44.5		5-May-08		4:07:53		69.8		37.5		15-Jun-08		4:25:59		71.6		37.5

		5-May-08		6:07:10		69.8		35		5-May-08		6:06:20		66.2		43		5-May-08		6:07:53		69.8		37		15-Jun-08		6:25:59		71.6		37.5

		5-May-08		8:07:10		69.8		37		5-May-08		8:06:20		66.2		44.5		5-May-08		8:07:53		69.8		37.5		15-Jun-08		8:25:59		72.21		38

		5-May-08		10:07:10		69.8		38		5-May-08		10:06:20		68.61		44		5-May-08		10:07:53		69.8		39		15-Jun-08		10:25:59		72.21		39

		5-May-08		12:07:10		70.41		40		5-May-08		12:06:20		70.41		45		5-May-08		12:07:53		71		40.5		15-Jun-08		12:25:59		73.4		40

		5-May-08		14:07:10		71		40		5-May-08		14:06:20		71		44.5		5-May-08		14:07:53		71		41.5		15-Jun-08		14:25:59		74.6		41

		5-May-08		16:07:10		71		38		5-May-08		16:06:20		69.8		42		5-May-08		16:07:53		70.41		40		15-Jun-08		16:25:59		75.2		41.5

		5-May-08		18:07:10		71		37.5		5-May-08		18:06:20		70.41		41.5		5-May-08		18:07:53		70.41		39		15-Jun-08		18:25:59		75.81		41

		5-May-08		20:07:10		71		37		5-May-08		20:06:20		70.41		41.5		5-May-08		20:07:53		69.8		38.5		15-Jun-08		20:25:59		75.2		40

		5-May-08		22:07:10		70.41		37		5-May-08		22:06:20		69.8		41		5-May-08		22:07:53		69.8		38.5		15-Jun-08		22:25:59		74.01		39.5

		6-May-08		0:07:10		71		36.5		6-May-08		0:06:20		69.2		42		6-May-08		0:07:53		70.41		38		16-Jun-08		0:25:59		72.8		39

		6-May-08		2:07:10		71		36.5		6-May-08		2:06:20		67.4		43		6-May-08		2:07:53		70.41		37.5		16-Jun-08		2:25:59		72.21		39

		6-May-08		4:07:10		70.41		36		6-May-08		4:06:20		66.81		43		6-May-08		4:07:53		69.8		37		16-Jun-08		4:25:59		71.6		39

		6-May-08		6:07:10		69.8		35.5		6-May-08		6:06:20		65.6		43		6-May-08		6:07:53		69.2		37		16-Jun-08		6:25:59		71		39

		6-May-08		8:07:10		70.41		38		6-May-08		8:06:20		68		43.5		6-May-08		8:07:53		68.61		42		16-Jun-08		8:25:59		70.41		39.5

		6-May-08		10:07:10		70.41		39		6-May-08		10:06:20		71		44		6-May-08		10:07:53		67.4		41.5		16-Jun-08		10:25:59		70.41		40.5

		6-May-08		12:07:10		70.41		40.5		6-May-08		12:06:20		71.6		45		6-May-08		12:07:53		67.4		44		16-Jun-08		12:25:59		72.21		41.5

		6-May-08		14:07:10		71		40.5		6-May-08		14:06:20		71		44.5		6-May-08		14:07:53		67.4		44.5		16-Jun-08		14:25:59		73.4		42.5

		6-May-08		16:07:10		71		40		6-May-08		16:06:20		70.41		46.5		6-May-08		16:07:53		68.61		43.5		16-Jun-08		16:25:59		74.6		41

		6-May-08		18:07:10		70.41		39		6-May-08		18:06:20		69.2		45.5		6-May-08		18:07:53		68.61		41		16-Jun-08		18:25:59		75.2		40

		6-May-08		20:07:10		70.41		39.5		6-May-08		20:06:20		68.61		45		6-May-08		20:07:53		68.61		41.5		16-Jun-08		20:25:59		75.2		39

		6-May-08		22:07:10		70.41		38		6-May-08		22:06:20		69.2		44		6-May-08		22:07:53		68.61		41		16-Jun-08		22:25:59		74.01		38.5

		7-May-08		0:07:10		70.41		38.5		7-May-08		0:06:20		68.61		45		7-May-08		0:07:53		68.61		41		17-Jun-08		0:25:59		72.21		38

		7-May-08		2:07:10		70.41		38.5		7-May-08		2:06:20		68		46.5		7-May-08		2:07:53		68		41.5		17-Jun-08		2:25:59		71		37.5

		7-May-08		4:07:10		69.8		38		7-May-08		4:06:20		67.4		47		7-May-08		4:07:53		68.61		40.5		17-Jun-08		4:25:59		70.41		38.5

		7-May-08		6:07:10		70.41		39		7-May-08		6:06:20		66.81		47.5		7-May-08		6:07:53		68		42		17-Jun-08		6:25:59		70.41		39.5

		7-May-08		8:07:10		70.41		39		7-May-08		8:06:20		69.8		45		7-May-08		8:07:53		68.61		41.5		17-Jun-08		8:25:59		70.41		41.5

		7-May-08		10:07:10		71		38.5		7-May-08		10:06:20		70.41		45		7-May-08		10:07:53		68		42		17-Jun-08		10:25:59		71.6		42.5

		7-May-08		12:07:10		71		40.5		7-May-08		12:06:20		70.41		47		7-May-08		12:07:53		68		43.5		17-Jun-08		12:25:59		73.4		42.5

		7-May-08		14:07:10		71		43.5		7-May-08		14:06:20		69.8		51		7-May-08		14:07:53		68.61		46.5		17-Jun-08		14:25:59		74.01		43.5

		7-May-08		16:07:10		71		43		7-May-08		16:06:20		70.41		56		7-May-08		16:07:53		68.61		46.5		17-Jun-08		16:25:59		74.6		41

		7-May-08		18:07:10		70.41		43.5		7-May-08		18:06:20		71		50		7-May-08		18:07:53		68		46.5		17-Jun-08		18:25:59		74.01		40

		7-May-08		20:07:10		71		36.5		7-May-08		20:06:20		70.41		39		7-May-08		20:07:53		68		41		17-Jun-08		20:25:59		74.01		39.5

		7-May-08		22:07:10		71		34.5		7-May-08		22:06:20		69.8		36		7-May-08		22:07:53		68		38		17-Jun-08		22:25:59		74.01		38.5

		8-May-08		0:07:10		69.8		37		8-May-08		0:06:20		69.8		40.5		8-May-08		0:07:53		68		40		18-Jun-08		0:25:59		72.8		38

		8-May-08		2:07:10		70.41		37		8-May-08		2:06:20		68.61		41		8-May-08		2:07:53		69.2		39		18-Jun-08		2:25:59		71.6		37.5

		8-May-08		4:07:10		70.41		36		8-May-08		4:06:20		68		41.5		8-May-08		4:07:53		69.8		37.5		18-Jun-08		4:25:59		70.41		38.5

		8-May-08		6:07:10		71		34.5		8-May-08		6:06:20		68		39.5		8-May-08		6:07:53		68.61		38		18-Jun-08		6:25:59		70.41		39.5

		8-May-08		8:07:10		71		34.5		8-May-08		8:06:20		69.8		37		8-May-08		8:07:53		68.61		38		18-Jun-08		8:25:59		70.41		41.5

		8-May-08		10:07:10		70.41		36		8-May-08		10:06:20		70.41		38.5		8-May-08		10:07:53		68.61		38		18-Jun-08		10:25:59		72.8		42

		8-May-08		12:07:10		70.41		37		8-May-08		12:06:20		71		38.5		8-May-08		12:07:53		67.4		40.5		18-Jun-08		12:25:59		72.8		41.5

		8-May-08		14:07:10		70.41		39		8-May-08		14:06:20		71		41		8-May-08		14:07:53		67.4		43		18-Jun-08		14:25:59		72.8		42.5

		8-May-08		16:07:10		71		38.5		8-May-08		16:06:20		70.41		43		8-May-08		16:07:53		68		41.5		18-Jun-08		16:25:59		73.4		43

		8-May-08		18:07:10		71		39		8-May-08		18:06:20		71		41.5		8-May-08		18:07:53		68.61		42		18-Jun-08		18:25:59		74.01		34.5

		8-May-08		20:07:10		71		38		8-May-08		20:06:20		70.41		43.5		8-May-08		20:07:53		68		41.5		18-Jun-08		20:25:59		74.6		32

		8-May-08		22:07:10		70.41		37		8-May-08		22:06:20		69.8		41		8-May-08		22:07:53		68		40		18-Jun-08		22:25:59		74.6		30.5

		9-May-08		0:07:10		70.41		37		9-May-08		0:06:20		68.61		41.5		9-May-08		0:07:53		68		40		19-Jun-08		0:25:59		74.01		30.5

		9-May-08		2:07:10		70.41		36.5		9-May-08		2:06:20		67.4		42		9-May-08		2:07:53		68.61		39		19-Jun-08		2:25:59		73.4		31.5

		9-May-08		4:07:10		69.8		35.5		9-May-08		4:06:20		66.81		42.5		9-May-08		4:07:53		69.2		38		19-Jun-08		4:25:59		72.21		33

		9-May-08		6:07:10		71		35.5		9-May-08		6:06:20		66.81		41.5		9-May-08		6:07:53		69.2		37.5		19-Jun-08		6:25:59		71		33.5

		9-May-08		8:07:10		71		37		9-May-08		8:06:20		69.8		42		9-May-08		8:07:53		69.2		39		19-Jun-08		8:25:59		71		35.5

		9-May-08		10:07:10		70.41		38		9-May-08		10:06:20		71		40.5		9-May-08		10:07:53		68.61		40		19-Jun-08		10:25:59		72.8		35.5

		9-May-08		12:07:10		70.41		40		9-May-08		12:06:20		71.6		43		9-May-08		12:07:53		69.2		41.5		19-Jun-08		12:25:59		73.4		33.5

		9-May-08		14:07:10		70.41		39		9-May-08		14:06:20		69.8		45.5		9-May-08		14:07:53		68		42.5		19-Jun-08		14:25:59		72.21		35.5

		9-May-08		16:07:10		70.41		38		9-May-08		16:06:20		69.2		43		9-May-08		16:07:53		67.4		42.5		19-Jun-08		16:25:59		72.21		33.5

		9-May-08		18:07:10		70.41		38.5		9-May-08		18:06:20		68.61		42.5		9-May-08		18:07:53		68.61		41.5		19-Jun-08		18:25:59		74.01		28.5

		9-May-08		20:07:10		70.41		37		9-May-08		20:06:20		68.61		42		9-May-08		20:07:53		68		40		19-Jun-08		20:25:59		74.6		29

		9-May-08		22:07:10		69.8		36.5		9-May-08		22:06:20		68		41.5		9-May-08		22:07:53		68.61		39		19-Jun-08		22:25:59		75.2		27.5

		10-May-08		0:07:10		69.8		35.5		10-May-08		0:06:20		68		40.5		10-May-08		0:07:53		68		39		20-Jun-08		0:25:59		74.6		30

		10-May-08		2:07:10		69.8		34.5		10-May-08		2:06:20		66.81		40.5		10-May-08		2:07:53		68		37.5		20-Jun-08		2:25:59		73.4		31

		10-May-08		4:07:10		69.8		34		10-May-08		4:06:20		66.2		40.5		10-May-08		4:07:53		68.61		37		20-Jun-08		4:25:59		72.8		31.5

		10-May-08		6:07:10		70.41		33.5		10-May-08		6:06:20		65.6		39.5		10-May-08		6:07:53		68.61		35.5		20-Jun-08		6:25:59		71.6		32.5

		10-May-08		8:07:10		70.41		35.5		10-May-08		8:06:20		68		41.5		10-May-08		8:07:53		67.4		38.5		20-Jun-08		8:25:59		72.21		35

		10-May-08		10:07:10		69.8		34		10-May-08		10:06:20		70.41		35		10-May-08		10:07:53		68		37.5		20-Jun-08		10:25:59		73.4		36.5

		10-May-08		12:07:10		71		33.5		10-May-08		12:06:20		71		34.5		10-May-08		12:07:53		68.61		36.5		20-Jun-08		12:25:59		72.8		35

		10-May-08		14:07:10		71.6		32		10-May-08		14:06:20		70.41		34.5		10-May-08		14:07:53		68		35.5		20-Jun-08		14:25:59		72.8		33.5

		10-May-08		16:07:10		71.6		35		10-May-08		16:06:20		69.8		38.5		10-May-08		16:07:53		67.4		40.5		20-Jun-08		16:25:59		72.8		34

		10-May-08		18:07:10		71.6		36		10-May-08		18:06:20		69.2		39.5		10-May-08		18:07:53		67.4		41.5		20-Jun-08		18:25:59		72.8		31

		10-May-08		20:07:10		71		35.5		10-May-08		20:06:20		68.61		40.5		10-May-08		20:07:53		68		39.5		20-Jun-08		20:25:59		74.6		31.5

		10-May-08		22:07:10		70.41		35.5		10-May-08		22:06:20		68.61		39.5		10-May-08		22:07:53		68		38.5		20-Jun-08		22:25:59		75.81		30.5

		11-May-08		0:07:10		70.41		35.5		11-May-08		0:06:20		68.61		39.5		11-May-08		0:07:53		68		38.5		21-Jun-08		0:25:59		75.2		31.5

		11-May-08		2:07:10		70.41		35		11-May-08		2:06:20		67.4		40		11-May-08		2:07:53		68		38		21-Jun-08		2:25:59		74.01		32

		11-May-08		4:07:10		69.8		34		11-May-08		4:06:20		66.81		40.5		11-May-08		4:07:53		68.61		37		21-Jun-08		4:25:59		73.4		32.5

		11-May-08		6:07:10		70.41		34.5		11-May-08		6:06:20		68		39		11-May-08		6:07:53		68.61		36.5		21-Jun-08		6:25:59		72.21		34

		11-May-08		8:07:10		70.41		35.5		11-May-08		8:06:20		69.8		39		11-May-08		8:07:53		68		38.5		21-Jun-08		8:25:59		72.8		35.5

		11-May-08		10:07:10		70.41		35		11-May-08		10:06:20		69.8		36.5		11-May-08		10:07:53		68.61		37.5		21-Jun-08		10:25:59		72.8		35.5

		11-May-08		12:07:10		71		35.5		11-May-08		12:06:20		70.41		38		11-May-08		12:07:53		68.61		39		21-Jun-08		12:25:59		72.8		33.5

		11-May-08		14:07:10		71.6		38		11-May-08		14:06:20		69.2		41		11-May-08		14:07:53		68.61		41.5		21-Jun-08		14:25:59		72.8		32

		11-May-08		16:07:10		71.6		37.5		11-May-08		16:06:20		68.61		40		11-May-08		16:07:53		68.61		40.5		21-Jun-08		16:25:59		73.4		30

		11-May-08		18:07:10		71.6		38.5		11-May-08		18:06:20		69.2		44		11-May-08		18:07:53		68.61		42.5		21-Jun-08		18:25:59		71.6		27

		11-May-08		20:07:10		71.6		39		11-May-08		20:06:20		69.2		50		11-May-08		20:07:53		68.61		43.5		21-Jun-08		20:25:59		74.01		26.5

		11-May-08		22:07:10		71		38.5		11-May-08		22:06:20		68.61		46.5		11-May-08		22:07:53		69.2		41.5		21-Jun-08		22:25:59		75.81		25.5

		12-May-08		0:07:10		69.8		38.5		12-May-08		0:06:20		68.61		47.5		12-May-08		0:07:53		69.2		41		22-Jun-08		0:25:59		75.81		27.5

		12-May-08		2:07:10		70.41		39		12-May-08		2:06:20		68.61		47.5		12-May-08		2:07:53		69.8		41		22-Jun-08		2:25:59		75.2		29

		12-May-08		4:07:10		70.41		38		12-May-08		4:06:20		68		47		12-May-08		4:07:53		69.8		40		22-Jun-08		4:25:59		74.01		29.5

		12-May-08		6:07:10		71		38		12-May-08		6:06:20		67.4		47		12-May-08		6:07:53		69.8		40		22-Jun-08		6:25:59		74.6		30

		12-May-08		8:07:10		71		38.5		12-May-08		8:06:20		67.4		47.5		12-May-08		8:07:53		69.8		40.5		22-Jun-08		8:25:59		75.2		30.5

		12-May-08		10:07:10		70.41		39		12-May-08		10:06:20		68.61		45		12-May-08		10:07:53		69.8		40.5		22-Jun-08		10:25:59		77		31

		12-May-08		12:07:10		70.41		40		12-May-08		12:06:20		69.2		44.5		12-May-08		12:07:53		69.8		41.5		22-Jun-08		12:25:59		78.2		29.5

		12-May-08		14:07:10		71		33		12-May-08		14:06:20		69.2		32		12-May-08		14:07:53		69.8		34.5		22-Jun-08		14:25:59		79.41		28.5

		12-May-08		16:07:10		71		29.5		12-May-08		16:06:20		69.8		29.5		12-May-08		16:07:53		69.8		31		22-Jun-08		16:25:59		79.41		27

		12-May-08		18:07:10		71.6		31.5		12-May-08		18:06:20		69.8		33		12-May-08		18:07:53		69.8		33		22-Jun-08		18:25:59		78.8		25

		12-May-08		20:07:10		71.6		30.5		12-May-08		20:06:20		69.2		33		12-May-08		20:07:53		69.8		33		22-Jun-08		20:25:59		78.8		25

		12-May-08		22:07:10		70.41		30.5		12-May-08		22:06:20		68		33		12-May-08		22:07:53		69.8		32.5		22-Jun-08		22:25:59		77.61		27

		13-May-08		0:07:10		68.61		31		13-May-08		0:06:20		68.61		32.5		13-May-08		0:07:53		68.61		32.5		23-Jun-08		0:25:59		76.4		29

		13-May-08		2:07:10		68		32		13-May-08		2:06:20		68		33		13-May-08		2:07:53		68		33		23-Jun-08		2:25:59		75.2		31

		13-May-08		4:07:10		68		31.5		13-May-08		4:06:20		68.61		32		13-May-08		4:07:53		68		32.5		23-Jun-08		4:25:59		74.01		32

		13-May-08		6:07:10		68		30.5		13-May-08		6:06:20		68.61		31		13-May-08		6:07:53		68		32		23-Jun-08		6:25:59		73.4		32.5

		13-May-08		8:07:10		68.61		29		13-May-08		8:06:20		69.2		31		13-May-08		8:07:53		68.61		31.5		23-Jun-08		8:25:59		72.8		34

		13-May-08		10:07:10		69.8		28		13-May-08		10:06:20		70.41		29.5		13-May-08		10:07:53		68.61		30.5		23-Jun-08		10:25:59		74.01		35.5

		13-May-08		12:07:10		71		27.5		13-May-08		12:06:20		71.6		29		13-May-08		12:07:53		68.61		30.5		23-Jun-08		12:25:59		75.2		35.5

		13-May-08		14:07:10		71.6		28.5		13-May-08		14:06:20		71		30		13-May-08		14:07:53		68.61		31.5		23-Jun-08		14:25:59		76.4		36

		13-May-08		16:07:10		71.6		29.5		13-May-08		16:06:20		69.2		32.5		13-May-08		16:07:53		68.61		33		23-Jun-08		16:25:59		77		36

		13-May-08		18:07:10		71.6		30.5		13-May-08		18:06:20		70.41		33		13-May-08		18:07:53		68.61		34.5		23-Jun-08		18:25:59		77.61		35.5

		13-May-08		20:07:10		71		30		13-May-08		20:06:20		69.8		31.5		13-May-08		20:07:53		68		33.5		23-Jun-08		20:25:59		77.61		34.5

		13-May-08		22:07:10		70.41		30.5		13-May-08		22:06:20		70.41		31.5		13-May-08		22:07:53		68.61		33		23-Jun-08		22:25:59		75.81		34.5

		14-May-08		0:07:10		69.2		31		14-May-08		0:06:20		69.8		32		14-May-08		0:07:53		68		33.5		24-Jun-08		0:25:59		74.6		34.5

		14-May-08		2:07:10		68		32.5		14-May-08		2:06:20		69.2		33.5		14-May-08		2:07:53		68		34.5		24-Jun-08		2:25:59		73.4		34.5

		14-May-08		4:07:10		68		33		14-May-08		4:06:20		69.2		34		14-May-08		4:07:53		68		34.5		24-Jun-08		4:25:59		72.21		34.5

		14-May-08		6:07:10		68.61		33		14-May-08		6:06:20		69.2		34		14-May-08		6:07:53		68		35		24-Jun-08		6:25:59		71		36.5

		14-May-08		8:07:10		69.2		34		14-May-08		8:06:20		70.41		36.5		14-May-08		8:07:53		68		36		24-Jun-08		8:25:59		71		39

		14-May-08		10:07:10		71		34		14-May-08		10:06:20		71		36		14-May-08		10:07:53		67.4		38		24-Jun-08		10:25:59		72.21		40.5

		14-May-08		12:07:10		71.6		28.5		14-May-08		12:06:20		70.41		31.5		14-May-08		12:07:53		68		33		24-Jun-08		12:25:59		72.21		41.5

		14-May-08		14:07:10		71.6		29.5		14-May-08		14:06:20		70.41		32		14-May-08		14:07:53		68		34		24-Jun-08		14:25:59		73.4		39.5

		14-May-08		16:07:10		71.6		26.5		14-May-08		16:06:20		71		28		14-May-08		16:07:53		68		30		24-Jun-08		16:25:59		74.01		39

		14-May-08		18:07:10		71.6		27.5		14-May-08		18:06:20		71		28		14-May-08		18:07:53		68		30.5		24-Jun-08		18:25:59		74.01		38.5

		14-May-08		20:07:10		71.6		35		14-May-08		20:06:20		70.41		39.5		14-May-08		20:07:53		68		39.5		24-Jun-08		20:25:59		74.01		39.5

		14-May-08		22:07:10		71		36		14-May-08		22:06:20		69.8		41		14-May-08		22:07:53		68		40		24-Jun-08		22:25:59		75.2		37

		15-May-08		0:07:10		70.41		36.5		15-May-08		0:06:20		69.8		41		15-May-08		0:07:53		68.61		39.5		25-Jun-08		0:25:59		73.4		37

		15-May-08		2:07:10		69.8		37		15-May-08		2:06:20		69.2		42		15-May-08		2:07:53		68.61		39.5		25-Jun-08		2:25:59		72.21		37

		15-May-08		4:07:10		69.8		38		15-May-08		4:06:20		69.8		42.5		15-May-08		4:07:53		69.2		40.5		25-Jun-08		4:25:59		71		37

		15-May-08		6:07:10		70.41		39		15-May-08		6:06:20		69.8		42.5		15-May-08		6:07:53		68.61		41		25-Jun-08		6:25:59		70.41		38

		15-May-08		8:07:10		71		40		15-May-08		8:06:20		70.41		48.5		15-May-08		8:07:53		68		43.5		25-Jun-08		8:25:59		70.41		40.5

		15-May-08		10:07:10		71.6		40.5		15-May-08		10:06:20		71		46		15-May-08		10:07:53		67.4		46.5		25-Jun-08		10:25:59		72.8		41.5

		15-May-08		12:07:10		71.6		40.5		15-May-08		12:06:20		70.41		46.5		15-May-08		12:07:53		68		46.5		25-Jun-08		12:25:59		73.4		41

		15-May-08		14:07:10		71.6		38		15-May-08		14:06:20		69.8		41		15-May-08		14:07:53		68		43		25-Jun-08		14:25:59		72.8		42

		15-May-08		16:07:10		71.6		37.5		15-May-08		16:06:20		69.8		40.5		15-May-08		16:07:53		68		42.5		25-Jun-08		16:25:59		72.8		41.5

		15-May-08		18:07:10		71.6		39		15-May-08		18:06:20		68.61		42.5		15-May-08		18:07:53		69.2		43		25-Jun-08		18:25:59		74.01		39.5

		15-May-08		20:07:10		71.6		39		15-May-08		20:06:20		68.61		44		15-May-08		20:07:53		68.61		43.5		25-Jun-08		20:25:59		74.01		41

		15-May-08		22:07:10		71.6		37.5		15-May-08		22:06:20		68		44		15-May-08		22:07:53		68.61		42		25-Jun-08		22:25:59		74.6		38.5

		16-May-08		0:07:10		72.21		37		16-May-08		0:06:20		68		42.5		16-May-08		0:07:53		68.61		41.5		26-Jun-08		0:25:59		74.01		37.5

		16-May-08		2:07:10		71.6		37		16-May-08		2:06:20		68		43		16-May-08		2:07:53		69.2		40.5		26-Jun-08		2:25:59		72.8		37.5

		16-May-08		4:07:10		71.6		36.5		16-May-08		4:06:20		68		43		16-May-08		4:07:53		69.2		40.5		26-Jun-08		4:25:59		71.6		38

		16-May-08		6:07:10		71.6		36		16-May-08		6:06:20		68.61		42		16-May-08		6:07:53		69.2		39.5		26-Jun-08		6:25:59		71		38.5

		16-May-08		8:07:10		72.21		36.5		16-May-08		8:06:20		69.8		42		16-May-08		8:07:53		68.61		41		26-Jun-08		8:25:59		71		40.5

		16-May-08		10:07:10		71.6		38		16-May-08		10:06:20		69.2		43		16-May-08		10:07:53		68		43		26-Jun-08		10:25:59		73.4		40.5

		16-May-08		12:07:10		71.6		39.5		16-May-08		12:06:20		70.41		43.5		16-May-08		12:07:53		68		44		26-Jun-08		12:25:59		72.21		43

		16-May-08		14:07:10		71.6		39		16-May-08		14:06:20		70.41		43		16-May-08		14:07:53		68		44		26-Jun-08		14:25:59		72.21		44

		16-May-08		16:07:10		71.6		40		16-May-08		16:06:20		69.2		46		16-May-08		16:07:53		68.61		45		26-Jun-08		16:25:59		72.21		43.5

		16-May-08		18:07:10		71.6		40.5		16-May-08		18:06:20		69.2		45		16-May-08		18:07:53		68.61		45		26-Jun-08		18:25:59		71.6		43

		16-May-08		20:07:10		71.6		42		16-May-08		20:06:20		69.2		48.5		16-May-08		20:07:53		69.2		46.5		26-Jun-08		20:25:59		72.8		40.5

		16-May-08		22:07:10		72.21		41		16-May-08		22:06:20		68.61		54.5		16-May-08		22:07:53		68		46.5		26-Jun-08		22:25:59		73.4		40.5

		17-May-08		0:07:10		72.21		39.5		17-May-08		0:06:20		68.61		50		17-May-08		0:07:53		68.61		44.5		27-Jun-08		0:25:59		72.8		39.5

		17-May-08		2:07:10		72.21		39		17-May-08		2:06:20		68.61		47		17-May-08		2:07:53		68.61		43.5		27-Jun-08		2:25:59		71.6		39

		17-May-08		4:07:10		71.6		39		17-May-08		4:06:20		68		51		17-May-08		4:07:53		68.61		43		27-Jun-08		4:25:59		71		39

		17-May-08		6:07:10		71.6		39		17-May-08		6:06:20		68.61		53		17-May-08		6:07:53		69.2		43		27-Jun-08		6:25:59		70.41		39.5

		17-May-08		8:07:10		72.21		40		17-May-08		8:06:20		69.8		55.5		17-May-08		8:07:53		68		45.5		27-Jun-08		8:25:59		70.41		41

		17-May-08		10:07:10		72.21		40.5		17-May-08		10:06:20		69.8		53.5		17-May-08		10:07:53		68		46		27-Jun-08		10:25:59		72.8		42.5

		17-May-08		12:07:10		71		44.5		17-May-08		12:06:20		69.8		50		17-May-08		12:07:53		68.61		49.5		27-Jun-08		12:25:59		72.21		43

		17-May-08		14:07:10		71.6		45		17-May-08		14:06:20		70.41		52.5		17-May-08		14:07:53		68		51		27-Jun-08		14:25:59		72.21		44.5

		17-May-08		16:07:10		71.6		44.5		17-May-08		16:06:20		69.8		51		17-May-08		16:07:53		68.61		49.5		27-Jun-08		16:25:59		72.8		44

		17-May-08		18:07:10		71.6		41.5		17-May-08		18:06:20		69.2		45.5		17-May-08		18:07:53		68.61		45.5		27-Jun-08		18:25:59		72.8		41

		17-May-08		20:07:10		71.6		41.5		17-May-08		20:06:20		68.61		49		17-May-08		20:07:53		68.61		46		27-Jun-08		20:25:59		73.4		41.5

		17-May-08		22:07:10		72.21		39.5		17-May-08		22:06:20		69.2		48		17-May-08		22:07:53		68		44.5		27-Jun-08		22:25:59		74.01		40

		18-May-08		0:07:10		72.21		39		18-May-08		0:06:20		68		50.5		18-May-08		0:07:53		68.61		43.5		28-Jun-08		0:25:59		73.4		39.5

		18-May-08		2:07:10		71.6		40		18-May-08		2:06:20		68		52		18-May-08		2:07:53		68.61		43.5		28-Jun-08		2:25:59		72.21		39.5

		18-May-08		4:07:10		71		40		18-May-08		4:06:20		68		52.5		18-May-08		4:07:53		69.2		43		28-Jun-08		4:25:59		71.6		39.5

		18-May-08		6:07:10		70.41		39.5		18-May-08		6:06:20		68		50.5		18-May-08		6:07:53		69.2		42		28-Jun-08		6:25:59		71		40

		18-May-08		8:07:10		71		40.5		18-May-08		8:06:20		68.61		53.5		18-May-08		8:07:53		68.61		44		28-Jun-08		8:25:59		71		42

		18-May-08		10:07:10		71.6		42.5		18-May-08		10:06:20		69.2		56.5		18-May-08		10:07:53		68.61		46.5		28-Jun-08		10:25:59		73.4		43

		18-May-08		12:07:10		71.6		44.5		18-May-08		12:06:20		69.2		53.5		18-May-08		12:07:53		68.61		49.5		28-Jun-08		12:25:59		72.8		44

		18-May-08		14:07:10		72.21		48.5		18-May-08		14:06:20		69.2		58.5		18-May-08		14:07:53		68.61		54		28-Jun-08		14:25:59		72.21		45

		18-May-08		16:07:10		72.21		45		18-May-08		16:06:20		68.61		63.5		18-May-08		16:07:53		68.61		51.5		28-Jun-08		16:25:59		72.8		45.5

		18-May-08		18:07:10		72.21		43		18-May-08		18:06:20		68.61		60.5		18-May-08		18:07:53		68.61		49.5		28-Jun-08		18:25:59		72.8		43.5

		18-May-08		20:07:10		72.21		40.5		18-May-08		20:06:20		68.61		52.5		18-May-08		20:07:53		68		46		28-Jun-08		20:25:59		72.8		43.5

		18-May-08		22:07:10		72.21		39		18-May-08		22:06:20		68		51.5		18-May-08		22:07:53		68.61		43.5		28-Jun-08		22:25:59		72.8		42.5

		19-May-08		0:07:10		71		39		19-May-08		0:06:20		68		49.5		19-May-08		0:07:53		69.2		42		29-Jun-08		0:25:59		72.21		42.5

		19-May-08		2:07:10		70.41		39.5		19-May-08		2:06:20		68		49		19-May-08		2:07:53		69.2		42		29-Jun-08		2:25:59		71.6		42.5

		19-May-08		4:07:10		70.41		39		19-May-08		4:06:20		67.4		48		19-May-08		4:07:53		69.2		41.5		29-Jun-08		4:25:59		71		43

		19-May-08		6:07:10		71		39		19-May-08		6:06:20		67.4		49		19-May-08		6:07:53		69.2		41.5		29-Jun-08		6:25:59		71		43.5

		19-May-08		8:07:10		71		39.5		19-May-08		8:06:20		68		49		19-May-08		8:07:53		69.2		42		29-Jun-08		8:25:59		71		44

		19-May-08		10:07:10		70.41		40.5		19-May-08		10:06:20		68		48.5		19-May-08		10:07:53		69.2		43		29-Jun-08		10:25:59		71.6		44.5

		19-May-08		12:07:10		71		41.5		19-May-08		12:06:20		68.61		51		19-May-08		12:07:53		69.2		44.5		29-Jun-08		12:25:59		72.21		45.5

		19-May-08		14:07:10		71.6		41.5		19-May-08		14:06:20		68		54.5		19-May-08		14:07:53		69.8		45		29-Jun-08		14:25:59		74.01		45.5

		19-May-08		16:07:10		72.21		42		19-May-08		16:06:20		68.61		51.5		19-May-08		16:07:53		69.2		46		29-Jun-08		16:25:59		75.2		44.5

		19-May-08		18:07:10		72.21		40		19-May-08		18:06:20		68		55		19-May-08		18:07:53		69.2		44.5		29-Jun-08		18:25:59		75.81		43.5

		19-May-08		20:07:10		72.21		39		19-May-08		20:06:20		68.61		50.5		19-May-08		20:07:53		69.2		43		29-Jun-08		20:25:59		75.2		43

		19-May-08		22:07:10		71		39		19-May-08		22:06:20		67.4		52.5		19-May-08		22:07:53		69.2		42		29-Jun-08		22:25:59		74.01		42.5

		20-May-08		0:07:10		71		39.5		20-May-08		0:06:20		67.4		51		20-May-08		0:07:53		69.2		42		30-Jun-08		0:25:59		72.21		42.5

		20-May-08		2:07:10		71		39.5		20-May-08		2:06:20		68		50		20-May-08		2:07:53		69.2		42		30-Jun-08		2:25:59		71.6		42.5

		20-May-08		4:07:10		70.41		39.5		20-May-08		4:06:20		67.4		49.5		20-May-08		4:07:53		69.2		41.5		30-Jun-08		4:25:59		71		42.5

		20-May-08		6:07:10		71		39.5		20-May-08		6:06:20		68		49.5		20-May-08		6:07:53		69.2		41.5		30-Jun-08		6:25:59		70.41		43

		20-May-08		8:07:10		71		39		20-May-08		8:06:20		68.61		50.5		20-May-08		8:07:53		68.61		44		30-Jun-08		8:25:59		70.41		43.5

		20-May-08		10:07:10		71		39		20-May-08		10:06:20		71		44.5		20-May-08		10:07:53		68.61		43		30-Jun-08		10:25:59		70.41		44

		20-May-08		12:07:10		71		41		20-May-08		12:06:20		71		49.5		20-May-08		12:07:53		68		45		30-Jun-08		12:25:59		72.21		44.5

		20-May-08		14:07:10		71		43		20-May-08		14:06:20		71		55.5		20-May-08		14:07:53		68		48		30-Jun-08		14:25:59		73.4		44.5

		20-May-08		16:07:10		71.6		42		20-May-08		16:06:20		70.41		49.5		20-May-08		16:07:53		68.61		46.5		30-Jun-08		16:25:59		74.6		44.5

		20-May-08		18:07:10		71.6		41		20-May-08		18:06:20		69.8		51		20-May-08		18:07:53		69.2		44.5		30-Jun-08		18:25:59		75.2		43

		20-May-08		20:07:10		71		39		20-May-08		20:06:20		69.8		48.5		20-May-08		20:07:53		69.2		42.5		30-Jun-08		20:25:59		75.2		42.5

		20-May-08		22:07:10		71		39.5		20-May-08		22:06:20		69.8		48		20-May-08		22:07:53		69.8		41.5		30-Jun-08		22:25:59		73.4		42

		21-May-08		0:07:10		70.41		40		21-May-08		0:06:20		69.2		48.5		21-May-08		0:07:53		69.2		42		1-Jul-08		0:25:59		72.21		42

		21-May-08		2:07:10		70.41		40		21-May-08		2:06:20		68.61		48.5		21-May-08		2:07:53		69.8		42		1-Jul-08		2:25:59		71.6		42

		21-May-08		4:07:10		71		39.5		21-May-08		4:06:20		68.61		48		21-May-08		4:07:53		69.2		41.5		1-Jul-08		4:25:59		71		42

		21-May-08		6:07:10		71		39.5		21-May-08		6:06:20		68		48.5		21-May-08		6:07:53		69.8		41		1-Jul-08		6:25:59		71		43

		21-May-08		8:07:10		71		39.5		21-May-08		8:06:20		70.41		48.5		21-May-08		8:07:53		68.61		42		1-Jul-08		8:25:59		70.41		45

		21-May-08		10:07:10		71		40		21-May-08		10:06:20		71		47		21-May-08		10:07:53		68		43		1-Jul-08		10:25:59		72.21		45

		21-May-08		12:07:10		71		41		21-May-08		12:06:20		71		51		21-May-08		12:07:53		68.61		44.5		1-Jul-08		12:25:59		72.21		45

		21-May-08		14:07:10		71		44		21-May-08		14:06:20		71.6		54		21-May-08		14:07:53		68		48.5		1-Jul-08		14:25:59		72.8		46.5

		21-May-08		16:07:10		71		39.5		21-May-08		16:06:20		71		45		21-May-08		16:07:53		69.2		43.5		1-Jul-08		16:25:59		72.8		46.5

		21-May-08		18:07:10		71.6		32		21-May-08		18:06:20		71		34		21-May-08		18:07:53		69.2		36.5		1-Jul-08		18:25:59		72.8		44.5

		21-May-08		20:07:10		71		30		21-May-08		20:06:20		70.41		30		21-May-08		20:07:53		69.8		31.5		1-Jul-08		20:25:59		74.01		42

		21-May-08		22:07:10		70.41		36		21-May-08		22:06:20		70.41		39		21-May-08		22:07:53		69.8		38		1-Jul-08		22:25:59		74.01		43.5

		22-May-08		0:07:10		69.2		35		22-May-08		0:06:20		69.2		37.5		22-May-08		0:07:53		68.61		37		2-Jul-08		0:25:59		73.4		43

		22-May-08		2:07:10		68.61		34.5		22-May-08		2:06:20		69.2		35.5		22-May-08		2:07:53		68.61		36.5		2-Jul-08		2:25:59		72.21		43

		22-May-08		4:07:10		68.61		34		22-May-08		4:06:20		69.2		35		22-May-08		4:07:53		68.61		35		2-Jul-08		4:25:59		72.21		43.5

		22-May-08		6:07:10		69.8		32.5		22-May-08		6:06:20		69.2		34.5		22-May-08		6:07:53		69.2		34.5		2-Jul-08		6:25:59		71.6		44.5

		22-May-08		8:07:10		69.8		32.5		22-May-08		8:06:20		71		34.5		22-May-08		8:07:53		68.61		35		2-Jul-08		8:25:59		71		46.5

		22-May-08		10:07:10		70.41		33.5		22-May-08		10:06:20		71.6		34		22-May-08		10:07:53		68.61		35.5		2-Jul-08		10:25:59		72.21		47.5

		22-May-08		12:07:10		71		33.5		22-May-08		12:06:20		70.41		35.5		22-May-08		12:07:53		69.2		36		2-Jul-08		12:25:59		72.21		46.5

		22-May-08		14:07:10		71		34.5		22-May-08		14:06:20		69.8		37		22-May-08		14:07:53		68.61		38		2-Jul-08		14:25:59		72.21		47.5

		22-May-08		16:07:10		71		35		22-May-08		16:06:20		69.2		38		22-May-08		16:07:53		68.61		38.5		2-Jul-08		16:25:59		72.8		45.5

		22-May-08		18:07:10		71		35		22-May-08		18:06:20		68.61		37.5		22-May-08		18:07:53		68		38		2-Jul-08		18:25:59		72.8		44.5

		22-May-08		20:07:10		70.41		34.5		22-May-08		20:06:20		68.61		37		22-May-08		20:07:53		68		37		2-Jul-08		20:25:59		73.4		42.5

		22-May-08		22:07:10		69.2		33.5		22-May-08		22:06:20		68		36.5		22-May-08		22:07:53		68.61		36		2-Jul-08		22:25:59		74.01		43

		23-May-08		0:07:10		68.61		33.5		23-May-08		0:06:20		68		36		23-May-08		0:07:53		68		35.5		3-Jul-08		0:25:59		72.8		42.5

		23-May-08		2:07:10		68		32.5		23-May-08		2:06:20		68		34.5		23-May-08		2:07:53		68		34.5		3-Jul-08		2:25:59		71.6		42

		23-May-08		4:07:10		68.61		31		23-May-08		4:06:20		68		32.5		23-May-08		4:07:53		68.61		33		3-Jul-08		4:25:59		71		42.5

		23-May-08		6:07:10		69.8		30		23-May-08		6:06:20		68		32		23-May-08		6:07:53		69.2		32		3-Jul-08		6:25:59		70.41		43

		23-May-08		8:07:10		69.8		30		23-May-08		8:06:20		68.61		33		23-May-08		8:07:53		69.2		32		3-Jul-08		8:25:59		71		44.5

		23-May-08		10:07:10		70.41		30		23-May-08		10:06:20		68.61		32.5		23-May-08		10:07:53		68		32		3-Jul-08		10:25:59		72.21		45

		23-May-08		12:07:10		71		25		23-May-08		12:06:20		69.2		27.5		23-May-08		12:07:53		68		28.5		3-Jul-08		12:25:59		71.6		46.5

		23-May-08		14:07:10		71		28.5		23-May-08		14:06:20		68.61		30		23-May-08		14:07:53		67.4		31		3-Jul-08		14:25:59		72.21		46

		23-May-08		16:07:10		71		29.5		23-May-08		16:06:20		68		33		23-May-08		16:07:53		68.61		32.5		3-Jul-08		16:25:59		72.21		45.5

		23-May-08		18:07:10		71		32		23-May-08		18:06:20		68.61		34.5		23-May-08		18:07:53		68.61		35		3-Jul-08		18:25:59		73.4		44

		23-May-08		20:07:10		71		33.5		23-May-08		20:06:20		69.2		36		23-May-08		20:07:53		68.61		36		3-Jul-08		20:25:59		74.01		42

		23-May-08		22:07:10		70.41		33		23-May-08		22:06:20		68.61		37		23-May-08		22:07:53		68.61		36		3-Jul-08		22:25:59		74.6		42

		24-May-08		0:07:10		69.2		33.5		24-May-08		0:06:20		68		37		24-May-08		0:07:53		68.61		36		4-Jul-08		0:25:59		73.4		41.5

		24-May-08		2:07:10		68.61		33.5		24-May-08		2:06:20		68		37		24-May-08		2:07:53		68		36		4-Jul-08		2:25:59		72.21		41.5

		24-May-08		4:07:10		69.2		33		24-May-08		4:06:20		67.4		37		24-May-08		4:07:53		68.61		35		4-Jul-08		4:25:59		71.6		41.5

		24-May-08		6:07:10		70.41		32.5		24-May-08		6:06:20		68		36		24-May-08		6:07:53		69.2		34.5		4-Jul-08		6:25:59		71		42

		24-May-08		8:07:10		70.41		32.5		24-May-08		8:06:20		67.4		38.5		24-May-08		8:07:53		68.61		35.5		4-Jul-08		8:25:59		71		44.5

		24-May-08		10:07:10		70.41		34		24-May-08		10:06:20		70.41		36		24-May-08		10:07:53		68.61		36.5		4-Jul-08		10:25:59		71.6		45

		24-May-08		12:07:10		71		35		24-May-08		12:06:20		71		36		24-May-08		12:07:53		69.2		36.5		4-Jul-08		12:25:59		72.21		48.5

		24-May-08		14:07:10		71		34		24-May-08		14:06:20		71		37		24-May-08		14:07:53		68		37.5		4-Jul-08		14:25:59		73.4		50

		24-May-08		16:07:10		71		34.5		24-May-08		16:06:20		69.8		37		24-May-08		16:07:53		69.2		37		4-Jul-08		16:25:59		72.8		49

		24-May-08		18:07:10		70.41		35.5		24-May-08		18:06:20		70.41		39		24-May-08		18:07:53		69.2		38		4-Jul-08		18:25:59		73.4		48.5

		24-May-08		20:07:10		70.41		36.5		24-May-08		20:06:20		69.8		41		24-May-08		20:07:53		68.61		39		4-Jul-08		20:25:59		74.01		46

		24-May-08		22:07:10		71		36.5		24-May-08		22:06:20		69.2		42.5		24-May-08		22:07:53		68.61		39.5		4-Jul-08		22:25:59		74.01		47

		25-May-08		0:07:10		70.41		37		25-May-08		0:06:20		69.2		42.5		25-May-08		0:07:53		69.2		39.5		5-Jul-08		0:25:59		73.4		46.5

		25-May-08		2:07:10		70.41		37		25-May-08		2:06:20		68.61		42.5		25-May-08		2:07:53		69.2		39		5-Jul-08		2:25:59		72.21		46

		25-May-08		4:07:10		70.41		37.5		25-May-08		4:06:20		68.61		43		25-May-08		4:07:53		69.2		39		5-Jul-08		4:25:59		71.6		45.5

		25-May-08		6:07:10		70.41		37.5		25-May-08		6:06:20		68.61		45		25-May-08		6:07:53		69.2		39.5		5-Jul-08		6:25:59		71		46.5

		25-May-08		8:07:10		70.41		38		25-May-08		8:06:20		68.61		45		25-May-08		8:07:53		69.2		39.5		5-Jul-08		8:25:59		71		48

		25-May-08		10:07:10		70.41		39.5		25-May-08		10:06:20		68.61		48		25-May-08		10:07:53		69.2		41.5		5-Jul-08		10:25:59		72.21		48

		25-May-08		12:07:10		70.41		40		25-May-08		12:06:20		69.2		50		25-May-08		12:07:53		69.8		42		5-Jul-08		12:25:59		72.21		48.5

		25-May-08		14:07:10		69.8		37.5		25-May-08		14:06:20		68.61		46		25-May-08		14:07:53		69.8		40		5-Jul-08		14:25:59		73.4		48

		25-May-08		16:07:10		69.8		38.5		25-May-08		16:06:20		68.61		44.5		25-May-08		16:07:53		69.2		39.5		5-Jul-08		16:25:59		73.4		47.5

		25-May-08		18:07:10		69.8		39.5		25-May-08		18:06:20		69.2		48.5		25-May-08		18:07:53		69.8		41		5-Jul-08		18:25:59		73.4		46.5

		25-May-08		20:07:10		70.41		40		25-May-08		20:06:20		69.2		50		25-May-08		20:07:53		69.2		41.5		5-Jul-08		20:25:59		72.8		45.5

		25-May-08		22:07:10		70.41		40		25-May-08		22:06:20		68.61		48		25-May-08		22:07:53		69.2		41		5-Jul-08		22:25:59		72.8		47

		26-May-08		0:07:10		70.41		39		26-May-08		0:06:20		68		47		26-May-08		0:07:53		69.2		40.5		6-Jul-08		0:25:59		72.21		46

		26-May-08		2:07:10		70.41		37.5		26-May-08		2:06:20		67.4		45		26-May-08		2:07:53		69.2		39		6-Jul-08		2:25:59		72.21		45.5

		26-May-08		4:07:10		70.41		36.5		26-May-08		4:06:20		66.81		44		26-May-08		4:07:53		69.2		38		6-Jul-08		4:25:59		71		45.5

		26-May-08		6:07:10		70.41		36.5		26-May-08		6:06:20		66.81		44.5		26-May-08		6:07:53		69.8		38		6-Jul-08		6:25:59		71		45

		26-May-08		8:07:10		70.41		38.5		26-May-08		8:06:20		67.4		45.5		26-May-08		8:07:53		69.8		39		6-Jul-08		8:25:59		70.41		45.5

		26-May-08		10:07:10		69.8		37		26-May-08		10:06:20		69.2		43		26-May-08		10:07:53		69.2		39.5		6-Jul-08		10:25:59		71.6		47.5

		26-May-08		12:07:10		69.8		37		26-May-08		12:06:20		69.2		40.5		26-May-08		12:07:53		69.2		38.5		6-Jul-08		12:25:59		73.4		48.5

		26-May-08		14:07:10		70.41		37		26-May-08		14:06:20		69.2		40		26-May-08		14:07:53		69.8		38.5		6-Jul-08		14:25:59		75.2		49

		26-May-08		16:07:10		70.41		36		26-May-08		16:06:20		69.2		39		26-May-08		16:07:53		69.2		38		6-Jul-08		16:25:59		77		47.5

		26-May-08		18:07:10		70.41		35.5		26-May-08		18:06:20		68.61		38.5		26-May-08		18:07:53		69.2		37		6-Jul-08		18:25:59		77.61		45.5

		26-May-08		20:07:10		70.41		36		26-May-08		20:06:20		69.2		38.5		26-May-08		20:07:53		69.8		37.5		6-Jul-08		20:25:59		78.2		45

		26-May-08		22:07:10		69.8		37.5		26-May-08		22:06:20		69.2		44		26-May-08		22:07:53		69.2		39.5		6-Jul-08		22:25:59		77		45.5

		27-May-08		0:07:10		70.41		38		27-May-08		0:06:20		68.61		44.5		27-May-08		0:07:53		69.8		39.5		7-Jul-08		0:25:59		75.81		45.5

		27-May-08		2:07:10		70.41		37.5		27-May-08		2:06:20		68		45		27-May-08		2:07:53		69.8		39		7-Jul-08		2:25:59		74.6		44.5

		27-May-08		4:07:10		70.41		37.5		27-May-08		4:06:20		67.4		45.5		27-May-08		4:07:53		69.8		39		7-Jul-08		4:25:59		74.01		44.5

		27-May-08		6:07:10		70.41		37		27-May-08		6:06:20		67.4		45		27-May-08		6:07:53		69.2		38.5		7-Jul-08		6:25:59		72.8		44

		27-May-08		8:07:10		70.41		38		27-May-08		8:06:20		68		45		27-May-08		8:07:53		69.2		39.5		7-Jul-08		8:25:59		72.21		44.5

		27-May-08		10:07:10		69.8		37.5		27-May-08		10:06:20		69.2		42.5		27-May-08		10:07:53		69.2		39		7-Jul-08		10:25:59		73.4		46.5

		27-May-08		12:07:10		70.41		39		27-May-08		12:06:20		69.2		45		27-May-08		12:07:53		69.2		40		7-Jul-08		12:25:59		74.6		48

		27-May-08		14:07:10		70.41		38.5		27-May-08		14:06:20		68.61		45		27-May-08		14:07:53		69.2		40.5		7-Jul-08		14:25:59		76.4		49

		27-May-08		16:07:10		70.41		39		27-May-08		16:06:20		69.2		45.5		27-May-08		16:07:53		69.2		40.5		7-Jul-08		16:25:59		77.61		47.5

		27-May-08		18:07:10		70.41		39		27-May-08		18:06:20		69.2		46		27-May-08		18:07:53		69.2		40.5		7-Jul-08		18:25:59		78.2		46

		27-May-08		20:07:10		70.41		38.5		27-May-08		20:06:20		69.2		46		27-May-08		20:07:53		69.8		40		7-Jul-08		20:25:59		78.2		44.5

		27-May-08		22:07:10		70.41		39		27-May-08		22:06:20		69.2		45		27-May-08		22:07:53		69.8		40		7-Jul-08		22:25:59		76.4		43.5

		28-May-08		0:07:10		70.41		38.5		28-May-08		0:06:20		69.2		46		28-May-08		0:07:53		69.8		40		8-Jul-08		0:25:59		75.2		42.5

		28-May-08		2:07:10		70.41		39		28-May-08		2:06:20		69.2		46.5		28-May-08		2:07:53		69.2		40.5		8-Jul-08		2:25:59		74.01		42.5

		28-May-08		4:07:10		70.41		39		28-May-08		4:06:20		68.61		47		28-May-08		4:07:53		69.8		40.5		8-Jul-08		4:25:59		72.8		42

		28-May-08		6:07:10		70.41		39.5		28-May-08		6:06:20		69.2		47.5		28-May-08		6:07:53		69.2		41		8-Jul-08		6:25:59		72.21		41.5

		28-May-08		8:07:10		70.41		39		28-May-08		8:06:20		69.2		50		28-May-08		8:07:53		69.2		41.5		8-Jul-08		8:25:59		71.6		46

		28-May-08		10:07:10		71		38.5		28-May-08		10:06:20		69.8		45		28-May-08		10:07:53		68.61		41		8-Jul-08		10:25:59		72.8		47

		28-May-08		12:07:10		71		38.5		28-May-08		12:06:20		69.8		44		28-May-08		12:07:53		69.2		41.5		8-Jul-08		12:25:59		72.8		49

		28-May-08		14:07:10		71		39		28-May-08		14:06:20		69.2		43.5		28-May-08		14:07:53		68.61		42.5		8-Jul-08		14:25:59		72.8		49

		28-May-08		16:07:10		71		38		28-May-08		16:06:20		69.8		45.5		28-May-08		16:07:53		68.61		41.5		8-Jul-08		16:25:59		73.4		48.5

		28-May-08		18:07:10		71		37.5		28-May-08		18:06:20		71		41.5		28-May-08		18:07:53		69.2		40.5		8-Jul-08		18:25:59		73.4		47

		28-May-08		20:07:10		71		37.5		28-May-08		20:06:20		70.41		42.5		28-May-08		20:07:53		69.2		40		8-Jul-08		20:25:59		74.6		45.5

		28-May-08		22:07:10		70.41		37.5		28-May-08		22:06:20		71		41.5		28-May-08		22:07:53		69.2		39		8-Jul-08		22:25:59		75.2		45

		29-May-08		0:07:10		70.41		37.5		29-May-08		0:06:20		69.8		43		29-May-08		0:07:53		69.2		39.5		9-Jul-08		0:25:59		75.2		44

		29-May-08		2:07:10		70.41		38		29-May-08		2:06:20		69.2		44		29-May-08		2:07:53		69.8		39.5		9-Jul-08		2:25:59		74.6		44

		29-May-08		4:07:10		70.41		38		29-May-08		4:06:20		68.61		45		29-May-08		4:07:53		69.8		39.5		9-Jul-08		4:25:59		74.01		43.5

		29-May-08		6:07:10		70.41		38.5		29-May-08		6:06:20		68.61		45.5		29-May-08		6:07:53		69.8		40		9-Jul-08		6:25:59		73.4		42

		29-May-08		8:07:10		71		38.5		29-May-08		8:06:20		69.8		46.5		29-May-08		8:07:53		69.2		40.5		9-Jul-08		8:25:59		72.21		45.5

		29-May-08		10:07:10		71		36.5		29-May-08		10:06:20		69.2		41.5		29-May-08		10:07:53		68.61		39.5		9-Jul-08		10:25:59		72.8		50

		29-May-08		12:07:10		71		37.5		29-May-08		12:06:20		69.8		43		29-May-08		12:07:53		69.2		40		9-Jul-08		12:25:59		72.8		50.5

		29-May-08		14:07:10		71		37.5		29-May-08		14:06:20		69.2		41.5		29-May-08		14:07:53		68.61		40.5		9-Jul-08		14:25:59		72.21		49.5

		29-May-08		16:07:10		71		37		29-May-08		16:06:20		69.8		41		29-May-08		16:07:53		68.61		40.5		9-Jul-08		16:25:59		72.8		48.5

		29-May-08		18:07:10		71		38		29-May-08		18:06:20		70.41		42.5		29-May-08		18:07:53		68.61		41		9-Jul-08		18:25:59		73.4		47.5

		29-May-08		20:07:10		71		38		29-May-08		20:06:20		70.41		44.5		29-May-08		20:07:53		69.2		40.5		9-Jul-08		20:25:59		74.01		45

		29-May-08		22:07:10		71		38		29-May-08		22:06:20		70.41		43.5		29-May-08		22:07:53		69.8		40		9-Jul-08		22:25:59		75.81		44

		30-May-08		0:07:10		69.8		38.5		30-May-08		0:06:20		69.2		47		30-May-08		0:07:53		67.4		42.5		10-Jul-08		0:25:59		75.2		44

		30-May-08		2:07:10		70.41		39		30-May-08		2:06:20		68.61		46.5		30-May-08		2:07:53		69.2		41		10-Jul-08		2:25:59		74.6		44

		30-May-08		4:07:10		71		39		30-May-08		4:06:20		68.61		47.5		30-May-08		4:07:53		69.8		40.5		10-Jul-08		4:25:59		74.01		44.5

		30-May-08		6:07:10		71		38.5		30-May-08		6:06:20		68		47.5		30-May-08		6:07:53		69.8		40.5		10-Jul-08		6:25:59		73.4		43

		30-May-08		8:07:10		70.41		39.5		30-May-08		8:06:20		70.41		48.5		30-May-08		8:07:53		68.61		42		10-Jul-08		8:25:59		73.4		46

		30-May-08		10:07:10		71		39		30-May-08		10:06:20		71		44.5		30-May-08		10:07:53		68.61		41.5		10-Jul-08		10:25:59		74.01		47.5

		30-May-08		12:07:10		71.6		39		30-May-08		12:06:20		69.2		49		30-May-08		12:07:53		69.2		41.5		10-Jul-08		12:25:59		72.8		49.5

		30-May-08		14:07:10		71		39.5		30-May-08		14:06:20		69.2		45.5		30-May-08		14:07:53		69.2		42.5		10-Jul-08		14:25:59		72.21		51

		30-May-08		16:07:10		71		39.5		30-May-08		16:06:20		69.2		49		30-May-08		16:07:53		68		44		10-Jul-08		16:25:59		72.8		50.5

		30-May-08		18:07:10		71		39		30-May-08		18:06:20		69.2		47.5		30-May-08		18:07:53		68.61		42		10-Jul-08		18:25:59		73.4		49

		30-May-08		20:07:10		71		38.5		30-May-08		20:06:20		69.2		44		30-May-08		20:07:53		69.2		41		10-Jul-08		20:25:59		74.6		46

		30-May-08		22:07:10		70.41		38.5		30-May-08		22:06:20		68.61		45		30-May-08		22:07:53		69.2		41		10-Jul-08		22:25:59		75.81		47

		31-May-08		0:07:10		71		39.5		31-May-08		0:06:20		68		49.5		31-May-08		0:07:53		69.2		42		11-Jul-08		0:25:59		75.81		46

		31-May-08		2:07:10		70.41		39		31-May-08		2:06:20		68		49.5		31-May-08		2:07:53		69.2		41		11-Jul-08		2:25:59		74.6		46.5

		31-May-08		4:07:10		70.41		39		31-May-08		4:06:20		68		49		31-May-08		4:07:53		69.8		40.5		11-Jul-08		4:25:59		74.01		46.5

		31-May-08		6:07:10		70.41		39		31-May-08		6:06:20		68		51.5		31-May-08		6:07:53		68.61		41.5		11-Jul-08		6:25:59		73.4		44.5

		31-May-08		8:07:10		71		39		31-May-08		8:06:20		68		45.5		31-May-08		8:07:53		68		42.5		11-Jul-08		8:25:59		72.21		47.5

		31-May-08		10:07:10		70.41		39.5		31-May-08		10:06:20		69.2		51		31-May-08		10:07:53		68		42.5		11-Jul-08		10:25:59		73.4		50.5

		31-May-08		12:07:10		71		40		31-May-08		12:06:20		69.2		49		31-May-08		12:07:53		68		44		11-Jul-08		12:25:59		72.8		51

		31-May-08		14:07:10		71		42		31-May-08		14:06:20		69.2		48		31-May-08		14:07:53		68.61		45.5		11-Jul-08		14:25:59		72.8		51.5

		31-May-08		16:07:10		71		40.5		31-May-08		16:06:20		69.2		51		31-May-08		16:07:53		68.61		45		11-Jul-08		16:25:59		72.8		49

		31-May-08		18:07:10		71		40.5		31-May-08		18:06:20		68.61		52.5		31-May-08		18:07:53		68		45		11-Jul-08		18:25:59		73.4		47.5

		31-May-08		20:07:10		71		39.5		31-May-08		20:06:20		68.61		52		31-May-08		20:07:53		68.61		43		11-Jul-08		20:25:59		74.01		46.5

		31-May-08		22:07:10		70.41		39		31-May-08		22:06:20		69.2		48		31-May-08		22:07:53		69.8		41		11-Jul-08		22:25:59		75.2		45

		1-Jun-08		0:07:10		70.41		39.5		1-Jun-08		0:06:20		68.61		47.5		1-Jun-08		0:07:53		68.61		41.5		12-Jul-08		0:25:59		74.6		43.5

		1-Jun-08		2:07:10		70.41		39		1-Jun-08		2:06:20		68.61		47.5		1-Jun-08		2:07:53		69.2		41		12-Jul-08		2:25:59		73.4		44

		1-Jun-08		4:07:10		70.41		39		1-Jun-08		4:06:20		68.61		47.5		1-Jun-08		4:07:53		69.2		41.5		12-Jul-08		4:25:59		72.21		44.5

		1-Jun-08		6:07:10		70.41		39		1-Jun-08		6:06:20		67.4		50.5		1-Jun-08		6:07:53		69.8		41		12-Jul-08		6:25:59		72.21		44

		1-Jun-08		8:07:10		70.41		39.5		1-Jun-08		8:06:20		67.4		51		1-Jun-08		8:07:53		69.2		41.5		12-Jul-08		8:25:59		71.6		46.5

		1-Jun-08		10:07:10		70.41		39.5		1-Jun-08		10:06:20		67.4		50		1-Jun-08		10:07:53		69.8		41		12-Jul-08		10:25:59		72.8		48

		1-Jun-08		12:07:10		70.41		39.5		1-Jun-08		12:06:20		67.4		50.5		1-Jun-08		12:07:53		69.2		42		12-Jul-08		12:25:59		74.6		46.5

		1-Jun-08		14:07:10		71		41		1-Jun-08		14:06:20		68.61		52		1-Jun-08		14:07:53		69.2		43.5		12-Jul-08		14:25:59		74.6		46.5

		1-Jun-08		16:07:10		71		40		1-Jun-08		16:06:20		69.2		50		1-Jun-08		16:07:53		69.2		43.5		12-Jul-08		16:25:59		75.81		45

		1-Jun-08		18:07:10		71.6		39.5		1-Jun-08		18:06:20		69.2		47.5		1-Jun-08		18:07:53		69.2		43		12-Jul-08		18:25:59		75.2		44.5

		1-Jun-08		20:07:10		71.6		38.5		1-Jun-08		20:06:20		68.61		47		1-Jun-08		20:07:53		69.2		42		12-Jul-08		20:25:59		75.81		41.5

		1-Jun-08		22:07:10		70.41		38.5		1-Jun-08		22:06:20		68		47.5		1-Jun-08		22:07:53		68.61		41		12-Jul-08		22:25:59		76.4		43

		2-Jun-08		0:07:10		70.41		38.5		2-Jun-08		0:06:20		68.61		46		2-Jun-08		0:07:53		68.61		41		13-Jul-08		0:25:59		76.4		43

		2-Jun-08		2:07:10		70.41		38		2-Jun-08		2:06:20		68		46		2-Jun-08		2:07:53		68.61		40.5		13-Jul-08		2:25:59		75.81		44

		2-Jun-08		4:07:10		70.41		37		2-Jun-08		4:06:20		67.4		45		2-Jun-08		4:07:53		68.61		39.5		13-Jul-08		4:25:59		75.81		44

		2-Jun-08		6:07:10		69.8		36		2-Jun-08		6:06:20		66.2		44		2-Jun-08		6:07:53		68.61		38.5		13-Jul-08		6:25:59		75.81		44.5

		2-Jun-08		8:07:10		70.41		38		2-Jun-08		8:06:20		66.81		46		2-Jun-08		8:07:53		69.2		40		13-Jul-08		8:25:59		75.81		44.5

		2-Jun-08		10:07:10		69.8		37		2-Jun-08		10:06:20		68.61		40.5		2-Jun-08		10:07:53		68.61		39.5		13-Jul-08		10:25:59		75.81		44.5

		2-Jun-08		12:07:10		70.41		38		2-Jun-08		12:06:20		69.2		41		2-Jun-08		12:07:53		69.2		39.5		13-Jul-08		12:25:59		76.4		44

		2-Jun-08		14:07:10		71		39		2-Jun-08		14:06:20		69.8		42		2-Jun-08		14:07:53		69.2		41.5		13-Jul-08		14:25:59		77.61		44.5

		2-Jun-08		16:07:10		71		38.5		2-Jun-08		16:06:20		69.2		45.5		2-Jun-08		16:07:53		65.01		46		13-Jul-08		16:25:59		78.8		43.5

		2-Jun-08		18:07:10		71		38.5		2-Jun-08		18:06:20		68.61		45		2-Jun-08		18:07:53		67.4		43		13-Jul-08		18:25:59		78.8		43

		2-Jun-08		20:07:10		71		37.5		2-Jun-08		20:06:20		67.4		47		2-Jun-08		20:07:53		66.81		43.5		13-Jul-08		20:25:59		78.8		43.5

		2-Jun-08		22:07:10		69.8		37		2-Jun-08		22:06:20		68		45		2-Jun-08		22:07:53		67.4		42		13-Jul-08		22:25:59		77.61		42.5

		3-Jun-08		0:07:10		69.8		37		3-Jun-08		0:06:20		67.4		44		3-Jun-08		0:07:53		67.4		41		14-Jul-08		0:25:59		77		42.5

		3-Jun-08		2:07:10		70.41		36.5		3-Jun-08		2:06:20		66.81		43.5		3-Jun-08		2:07:53		66.81		40.5		14-Jul-08		2:25:59		76.4		42.5

		3-Jun-08		4:07:10		69.8		35		3-Jun-08		4:06:20		66.2		43		3-Jun-08		4:07:53		67.4		39.5		14-Jul-08		4:25:59		75.81		42.5

		3-Jun-08		6:07:10		70.41		35.5		3-Jun-08		6:06:20		66.2		42.5		3-Jun-08		6:07:53		67.4		38.5		14-Jul-08		6:25:59		75.2		42

		3-Jun-08		8:07:10		70.41		37		3-Jun-08		8:06:20		68		42		3-Jun-08		8:07:53		68.61		39.5		14-Jul-08		8:25:59		74.6		42.5

		3-Jun-08		10:07:10		71		37		3-Jun-08		10:06:20		68		44.5		3-Jun-08		10:07:53		67.4		41.5		14-Jul-08		10:25:59		75.2		42.5

		3-Jun-08		12:07:10		71		37.5		3-Jun-08		12:06:20		71		41		3-Jun-08		12:07:53		68		41.5		14-Jul-08		12:25:59		76.4		43

		3-Jun-08		14:07:10		71		39.5		3-Jun-08		14:06:20		70.41		45.5		3-Jun-08		14:07:53		66.81		45		14-Jul-08		14:25:59		77		43.5

		3-Jun-08		16:07:10		71		39.5		3-Jun-08		16:06:20		69.2		44.5		3-Jun-08		16:07:53		67.4		44.5		14-Jul-08		16:25:59		78.2		43.5

		3-Jun-08		18:07:10		71		39.5		3-Jun-08		18:06:20		69.2		45		3-Jun-08		18:07:53		67.4		44.5		14-Jul-08		18:25:59		78.8		43

		3-Jun-08		20:07:10		71		30.5		3-Jun-08		20:06:20		69.2		31.5		3-Jun-08		20:07:53		67.4		34.5		14-Jul-08		20:25:59		78.8		42.5

		3-Jun-08		22:07:10		70.41		27		3-Jun-08		22:06:20		68.61		29.5		3-Jun-08		22:07:53		68		31		14-Jul-08		22:25:59		77.61		41.5

		4-Jun-08		0:07:10		69.2		34		4-Jun-08		0:06:20		68.61		37		4-Jun-08		0:07:53		68		37		15-Jul-08		0:25:59		77		41

		4-Jun-08		2:07:10		69.2		35.5		4-Jun-08		2:06:20		68		40		4-Jun-08		2:07:53		68		38		15-Jul-08		2:25:59		76.4		41

		4-Jun-08		4:07:10		68.61		35		4-Jun-08		4:06:20		67.4		39.5		4-Jun-08		4:07:53		68		37.5		15-Jul-08		4:25:59		75.81		41.5

		4-Jun-08		6:07:10		69.8		34.5		4-Jun-08		6:06:20		68		39		4-Jun-08		6:07:53		68.61		37		15-Jul-08		6:25:59		75.2		41

		4-Jun-08		8:07:10		69.8		38.5		4-Jun-08		8:06:20		68		46		4-Jun-08		8:07:53		68		40.5		15-Jul-08		8:25:59		74.01		43.5

		4-Jun-08		10:07:10		70.41		41		4-Jun-08		10:06:20		69.8		53		4-Jun-08		10:07:53		68		45		15-Jul-08		10:25:59		74.6		45

		4-Jun-08		12:07:10		71		42.5		4-Jun-08		12:06:20		69.8		50		4-Jun-08		12:07:53		68		46.5		15-Jul-08		12:25:59		75.2		44.5

		4-Jun-08		14:07:10		70.41		41.5		4-Jun-08		14:06:20		69.2		53		4-Jun-08		14:07:53		66.81		47		15-Jul-08		14:25:59		75.81		45

		4-Jun-08		16:07:10		70.41		40		4-Jun-08		16:06:20		70.41		44.5		4-Jun-08		16:07:53		67.4		44.5		15-Jul-08		16:25:59		75.81		44

		4-Jun-08		18:07:10		71		38		4-Jun-08		18:06:20		70.41		38.5		4-Jun-08		18:07:53		67.4		42		15-Jul-08		18:25:59		76.4		42.5

		4-Jun-08		20:07:10		71		38		4-Jun-08		20:06:20		70.41		42		4-Jun-08		20:07:53		67.4		43		15-Jul-08		20:25:59		77		39.5

		4-Jun-08		22:07:10		71		37.5		4-Jun-08		22:06:20		69.8		43		4-Jun-08		22:07:53		67.4		42.5		15-Jul-08		22:25:59		77		41

		5-Jun-08		0:07:10		70.41		38		5-Jun-08		0:06:20		69.2		44		5-Jun-08		0:07:53		68		41.5		16-Jul-08		0:25:59		76.4		41.5

		5-Jun-08		2:07:10		69.8		36		5-Jun-08		2:06:20		69.8		38.5		5-Jun-08		2:07:53		68.61		39		16-Jul-08		2:25:59		75.81		41.5

		5-Jun-08		4:07:10		68.61		36		5-Jun-08		4:06:20		69.2		38.5		5-Jun-08		4:07:53		68		38.5		16-Jul-08		4:25:59		75.81		42

		5-Jun-08		6:07:10		68.61		36		5-Jun-08		6:06:20		68.61		38.5		5-Jun-08		6:07:53		68		38		16-Jul-08		6:25:59		75.2		41

		5-Jun-08		8:07:10		69.2		35		5-Jun-08		8:06:20		69.2		39.5		5-Jun-08		8:07:53		68		38		16-Jul-08		8:25:59		74.6		43.5

		5-Jun-08		10:07:10		70.41		35		5-Jun-08		10:06:20		71		36.5		5-Jun-08		10:07:53		68		38.5		16-Jul-08		10:25:59		75.2		44.5

		5-Jun-08		12:07:10		70.41		34.5		5-Jun-08		12:06:20		69.8		35		5-Jun-08		12:07:53		68.61		37		16-Jul-08		12:25:59		75.2		43.5

		5-Jun-08		14:07:10		70.41		32		5-Jun-08		14:06:20		69.2		34.5		5-Jun-08		14:07:53		68.61		35		16-Jul-08		14:25:59		75.81		45

		5-Jun-08		16:07:10		70.41		34.5		5-Jun-08		16:06:20		70.41		36.5		5-Jun-08		16:07:53		68.61		37.5		16-Jul-08		16:25:59		75.2		43.5

		5-Jun-08		18:07:10		71		35		5-Jun-08		18:06:20		69.8		36		5-Jun-08		18:07:53		68.61		37.5

		5-Jun-08		20:07:10		71		35.5		5-Jun-08		20:06:20		69.2		38.5		5-Jun-08		20:07:53		69.2		38

		5-Jun-08		22:07:10		71		35		5-Jun-08		22:06:20		68.61		39		5-Jun-08		22:07:53		69.2		37.5

		6-Jun-08		0:07:10		69.8		35.5		6-Jun-08		0:06:20		68		41		6-Jun-08		0:07:53		68.61		38.5

		6-Jun-08		2:07:10		69.2		36		6-Jun-08		2:06:20		67.4		41		6-Jun-08		2:07:53		68.61		38

		6-Jun-08		4:07:10		69.2		36		6-Jun-08		4:06:20		67.4		41.5		6-Jun-08		4:07:53		68.61		38.5

		6-Jun-08		6:07:10		69.2		36		6-Jun-08		6:06:20		67.4		41.5		6-Jun-08		6:07:53		68		38.5

		6-Jun-08		8:07:10		69.8		36.5		6-Jun-08		8:06:20		68		42		6-Jun-08		8:07:53		68.61		39.5

		6-Jun-08		10:07:10		70.41		36		6-Jun-08		10:06:20		68		42		6-Jun-08		10:07:53		68		40

		6-Jun-08		12:07:10		70.41		33		6-Jun-08		12:06:20		69.8		36		6-Jun-08		12:07:53		68		37.5

		6-Jun-08		14:07:10		70.41		38.5		6-Jun-08		14:06:20		69.2		40.5		6-Jun-08		14:07:53		67.4		42

		6-Jun-08		16:07:10		70.41		39.5		6-Jun-08		16:06:20		69.8		43		6-Jun-08		16:07:53		68		43

		6-Jun-08		18:07:10		71		38.5		6-Jun-08		18:06:20		69.2		44.5		6-Jun-08		18:07:53		68		42.5

		6-Jun-08		20:07:10		71		39.5		6-Jun-08		20:06:20		69.2		47		6-Jun-08		20:07:53		68.61		43

		6-Jun-08		22:07:10		71		39		6-Jun-08		22:06:20		68.61		51.5		6-Jun-08		22:07:53		68.61		43

		7-Jun-08		0:07:10		70.41		38.5		7-Jun-08		0:06:20		68.61		45		7-Jun-08		0:07:53		69.2		41

		7-Jun-08		2:07:10		69.8		38		7-Jun-08		2:06:20		68		48.5		7-Jun-08		2:07:53		69.2		40.5

		7-Jun-08		4:07:10		69.2		38		7-Jun-08		4:06:20		67.4		45.5		7-Jun-08		4:07:53		68.61		40

		7-Jun-08		6:07:10		69.2		37.5		7-Jun-08		6:06:20		67.4		43.5		7-Jun-08		6:07:53		68.61		39.5

		7-Jun-08		8:07:10		69.8		37.5		7-Jun-08		8:06:20		68.61		44		7-Jun-08		8:07:53		68.61		39.5

		7-Jun-08		10:07:10		70.41		36		7-Jun-08		10:06:20		68.61		40		7-Jun-08		10:07:53		68		39.5

		7-Jun-08		12:07:10		70.41		34.5		7-Jun-08		12:06:20		70.41		36.5		7-Jun-08		12:07:53		69.2		37

		7-Jun-08		14:07:10		70.41		31.5		7-Jun-08		14:06:20		69.8		32.5		7-Jun-08		14:07:53		68.61		33.5

		7-Jun-08		16:07:10		71		32		7-Jun-08		16:06:20		68.61		34.5		7-Jun-08		16:07:53		68		35

		7-Jun-08		18:07:10		70.41		34.5		7-Jun-08		18:06:20		68.61		36.5		7-Jun-08		18:07:53		68.61		36.5

		7-Jun-08		20:07:10		71		34.5		7-Jun-08		20:06:20		69.2		38		7-Jun-08		20:07:53		69.2		37

		7-Jun-08		22:07:10		70.41		34		7-Jun-08		22:06:20		68.61		38		7-Jun-08		22:07:53		68.61		36.5

		8-Jun-08		0:07:10		69.8		34		8-Jun-08		0:06:20		68		38		8-Jun-08		0:07:53		68.61		36.5

		8-Jun-08		2:07:10		69.2		34		8-Jun-08		2:06:20		68		37.5		8-Jun-08		2:07:53		68.61		36

		8-Jun-08		4:07:10		69.2		34		8-Jun-08		4:06:20		68		37		8-Jun-08		4:07:53		68.61		35.5

		8-Jun-08		6:07:10		69.8		33		8-Jun-08		6:06:20		67.4		37		8-Jun-08		6:07:53		68.61		35.5

		8-Jun-08		8:07:10		69.8		33.5		8-Jun-08		8:06:20		68		36.5		8-Jun-08		8:07:53		68.61		35.5

		8-Jun-08		10:07:10		70.41		34.5		8-Jun-08		10:06:20		68		37		8-Jun-08		10:07:53		69.2		35.5

		8-Jun-08		12:07:10		71		33		8-Jun-08		12:06:20		68.61		34.5		8-Jun-08		12:07:53		69.2		35

		8-Jun-08		14:07:10		71		30.5		8-Jun-08		14:06:20		68.61		32		8-Jun-08		14:07:53		69.2		33

		8-Jun-08		16:07:10		71.6		31		8-Jun-08		16:06:20		69.2		33.5		8-Jun-08		16:07:53		68.61		34.5

		8-Jun-08		18:07:10		71.6		34.5		8-Jun-08		18:06:20		68.61		37.5		8-Jun-08		18:07:53		68.61		38

		8-Jun-08		20:07:10		71.6		36.5		8-Jun-08		20:06:20		68.61		45		8-Jun-08		20:07:53		68.61		40.5

		8-Jun-08		22:07:10		71		37		8-Jun-08		22:06:20		68.61		44		8-Jun-08		22:07:53		68.61		40

		9-Jun-08		0:07:10		71		36		9-Jun-08		0:06:20		68.61		40.5		9-Jun-08		0:07:53		69.2		38.5

		9-Jun-08		2:07:10		70.41		36.5		9-Jun-08		2:06:20		68		43		9-Jun-08		2:07:53		69.2		38

		9-Jun-08		4:07:10		69.8		36.5		9-Jun-08		4:06:20		68		43		9-Jun-08		4:07:53		69.2		38.5

		9-Jun-08		6:07:10		69.2		37		9-Jun-08		6:06:20		67.4		43.5		9-Jun-08		6:07:53		69.2		39

		9-Jun-08		8:07:10		69.8		38		9-Jun-08		8:06:20		67.4		45		9-Jun-08		8:07:53		69.2		39

		9-Jun-08		10:07:10		70.41		38.5		9-Jun-08		10:06:20		68.61		43.5		9-Jun-08		10:07:53		69.2		40

		9-Jun-08		12:07:10		71		38		9-Jun-08		12:06:20		68.61		42.5		9-Jun-08		12:07:53		69.8		40.5

		9-Jun-08		14:07:10		71		38		9-Jun-08		14:06:20		68.61		41.5		9-Jun-08		14:07:53		69.2		40.5

		9-Jun-08		16:07:10		72.21		38.5		9-Jun-08		16:06:20		68.61		44.5		9-Jun-08		16:07:53		69.8		42

		9-Jun-08		18:07:10		71.6		39		9-Jun-08		18:06:20		68.61		46.5		9-Jun-08		18:07:53		69.2		43

		9-Jun-08		20:07:10		71.6		38		9-Jun-08		20:06:20		68		48		9-Jun-08		20:07:53		69.2		41.5

		9-Jun-08		22:07:10		71		37.5		9-Jun-08		22:06:20		68		47		9-Jun-08		22:07:53		69.2		40

		10-Jun-08		0:07:10		70.41		37.5		10-Jun-08		0:06:20		68		45.5		10-Jun-08		0:07:53		69.2		39.5

		10-Jun-08		2:07:10		69.8		37		10-Jun-08		2:06:20		67.4		46		10-Jun-08		2:07:53		69.2		39.5

		10-Jun-08		4:07:10		69.8		38		10-Jun-08		4:06:20		68		47		10-Jun-08		4:07:53		69.2		39.5

		10-Jun-08		6:07:10		69.8		38		10-Jun-08		6:06:20		68		44.5		10-Jun-08		6:07:53		69.8		39.5

		10-Jun-08		8:07:10		71		38.5		10-Jun-08		8:06:20		68.61		48		10-Jun-08		8:07:53		69.2		41

		10-Jun-08		10:07:10		71		37.5		10-Jun-08		10:06:20		69.2		43		10-Jun-08		10:07:53		69.2		40.5

		10-Jun-08		12:07:10		71		38		10-Jun-08		12:06:20		70.41		40		10-Jun-08		12:07:53		69.2		40.5

		10-Jun-08		14:07:10		71		37.5		10-Jun-08		14:06:20		71.6		37.5		10-Jun-08		14:07:53		68.61		39.5

		10-Jun-08		16:07:10		70.41		40		10-Jun-08		16:06:20		70.41		41		10-Jun-08		16:07:53		68.61		42

		10-Jun-08		18:07:10		70.41		44		10-Jun-08		18:06:20		71.6		47.5		10-Jun-08		18:07:53		69.2		46.5

		10-Jun-08		20:07:10		71		42		10-Jun-08		20:06:20		71		47		10-Jun-08		20:07:53		68.61		46

		10-Jun-08		22:07:10		71.6		41		10-Jun-08		22:06:20		71		51		10-Jun-08		22:07:53		69.2		44.5

		11-Jun-08		0:07:10		71.6		40.5		11-Jun-08		0:06:20		71		47.5		11-Jun-08		0:07:53		68.61		45

		11-Jun-08		2:07:10		71.6		36.5		11-Jun-08		2:06:20		71		40.5		11-Jun-08		2:07:53		69.2		40

		11-Jun-08		4:07:10		71		37.5		11-Jun-08		4:06:20		69.8		44		11-Jun-08		4:07:53		69.2		40.5

		11-Jun-08		6:07:10		70.41		36.5		11-Jun-08		6:06:20		69.8		41		11-Jun-08		6:07:53		69.2		39

		11-Jun-08		8:07:10		71		35.5		11-Jun-08		8:06:20		70.41		39		11-Jun-08		8:07:53		68		39

		11-Jun-08		10:07:10		71		27.5		11-Jun-08		10:06:20		70.41		29.5		11-Jun-08		10:07:53		67.4		31.5

		11-Jun-08		12:07:10		71		24		11-Jun-08		12:06:20		69.8		24.5		11-Jun-08		12:07:53		68.61		27

		11-Jun-08		14:07:10		71.6		27.5		11-Jun-08		14:06:20		70.41		30.5		11-Jun-08		14:07:53		68		31.5

		11-Jun-08		16:07:10		71		28.5		11-Jun-08		16:06:20		69.8		30		11-Jun-08		16:07:53		68.61		31.5

		11-Jun-08		18:07:10		71		31.5		11-Jun-08		18:06:20		69.8		33		11-Jun-08		18:07:53		68.61		34

		11-Jun-08		20:07:10		71		33.5		11-Jun-08		20:06:20		69.8		35		11-Jun-08		20:07:53		68.61		36

		11-Jun-08		22:07:10		71.6		33.5		11-Jun-08		22:06:20		69.2		37		11-Jun-08		22:07:53		68.61		37

		12-Jun-08		0:07:10		70.41		34		12-Jun-08		0:06:20		69.2		36.5		12-Jun-08		0:07:53		68.61		36.5

		12-Jun-08		2:07:10		69.8		33.5		12-Jun-08		2:06:20		68.61		36.5		12-Jun-08		2:07:53		68.61		36

		12-Jun-08		4:07:10		69.2		34		12-Jun-08		4:06:20		68.61		37		12-Jun-08		4:07:53		68.61		36

		12-Jun-08		6:07:10		68.61		34.5		12-Jun-08		6:06:20		68		37		12-Jun-08		6:07:53		68		36.5

		12-Jun-08		8:07:10		69.8		34.5		12-Jun-08		8:06:20		69.2		37.5		12-Jun-08		8:07:53		68.61		36.5

		12-Jun-08		10:07:10		71		34		12-Jun-08		10:06:20		71		36		12-Jun-08		10:07:53		68.61		37

		12-Jun-08		12:07:10		71		29.5		12-Jun-08		12:06:20		71.6		30		12-Jun-08		12:07:53		69.8		32

		12-Jun-08		14:07:10		71		24.5		12-Jun-08		14:06:20		72.8		26		12-Jun-08		14:07:53		69.8		28.5

		12-Jun-08		16:07:10		71		26.5		12-Jun-08		16:06:20		71.6		20.5		12-Jun-08		16:07:53		69.2		28

		12-Jun-08		18:07:10		70.41		27.5		12-Jun-08		18:06:20		71		27.5		12-Jun-08		18:07:53		69.2		29.5

		12-Jun-08		20:07:10		70.41		35.5		12-Jun-08		20:06:20		71		38.5		12-Jun-08		20:07:53		69.2		38

		12-Jun-08		22:07:10		71		35.5		12-Jun-08		22:06:20		70.41		40		12-Jun-08		22:07:53		69.2		38

		13-Jun-08		0:07:10		70.41		36		13-Jun-08		0:06:20		70.41		39.5		13-Jun-08		0:07:53		69.2		37.5

		13-Jun-08		2:07:10		69.8		36		13-Jun-08		2:06:20		69.8		39.5		13-Jun-08		2:07:53		69.2		37.5

		13-Jun-08		4:07:10		69.8		36.5		13-Jun-08		4:06:20		69.8		40.5		13-Jun-08		4:07:53		69.2		38

		13-Jun-08		6:07:10		69.2		36.5		13-Jun-08		6:06:20		69.8		39.5		13-Jun-08		6:07:53		69.2		37.5

		13-Jun-08		8:07:10		70.41		37		13-Jun-08		8:06:20		70.41		39.5		13-Jun-08		8:07:53		69.2		39

		13-Jun-08		10:07:10		71		36.5		13-Jun-08		10:06:20		70.41		38.5		13-Jun-08		10:07:53		69.2		38.5

		13-Jun-08		12:07:10		71		24		13-Jun-08		12:06:20		71.6		25		13-Jun-08		12:07:53		69.8		28

		13-Jun-08		14:07:10		71		22.5		13-Jun-08		14:06:20		71.6		23.5		13-Jun-08		14:07:53		69.2		25

		13-Jun-08		16:07:10		70.41		29		13-Jun-08		16:06:20		72.21		30		13-Jun-08		16:07:53		69.8		31.5

		13-Jun-08		18:07:10		71		26.5		13-Jun-08		18:06:20		71		27		13-Jun-08		18:07:53		69.8		29

		13-Jun-08		20:07:10		71		29		13-Jun-08		20:06:20		71.6		27.5		13-Jun-08		20:07:53		68.61		29.5

		13-Jun-08		22:07:10		71.6		32.5		13-Jun-08		22:06:20		71		33.5		13-Jun-08		22:07:53		69.2		34.5

		14-Jun-08		0:07:10		71		33		14-Jun-08		0:06:20		70.41		35.5		14-Jun-08		0:07:53		69.2		35.5

		14-Jun-08		2:07:10		70.41		34.5		14-Jun-08		2:06:20		70.41		37		14-Jun-08		2:07:53		69.2		36

		14-Jun-08		4:07:10		69.8		34.5		14-Jun-08		4:06:20		69.8		38.5		14-Jun-08		4:07:53		69.2		36.5

		14-Jun-08		6:07:10		69.8		35.5		14-Jun-08		6:06:20		69.8		38.5		14-Jun-08		6:07:53		68.61		37

		14-Jun-08		8:07:10		70.41		36		14-Jun-08		8:06:20		71		38.5		14-Jun-08		8:07:53		69.2		38

		14-Jun-08		10:07:10		71		36.5		14-Jun-08		10:06:20		71		39.5		14-Jun-08		10:07:53		68.61		39.5

		14-Jun-08		12:07:10		70.41		39		14-Jun-08		12:06:20		71.6		42		14-Jun-08		12:07:53		69.2		41.5

		14-Jun-08		14:07:10		71		37.5		14-Jun-08		14:06:20		72.8		37		14-Jun-08		14:07:53		69.2		39.5

		14-Jun-08		16:07:10		70.41		39		14-Jun-08		16:06:20		71		41		14-Jun-08		16:07:53		69.8		41

		14-Jun-08		18:07:10		70.41		39		14-Jun-08		18:06:20		71		42.5		14-Jun-08		18:07:53		68.61		42

		14-Jun-08		20:07:10		70.41		38		14-Jun-08		20:06:20		70.41		45		14-Jun-08		20:07:53		68.61		41.5

		14-Jun-08		22:07:10		70.41		38		14-Jun-08		22:06:20		71		45		14-Jun-08		22:07:53		68.61		40.5

		15-Jun-08		0:07:10		70.41		38.5		15-Jun-08		0:06:20		69.8		43.5		15-Jun-08		0:07:53		68.61		40.5

		15-Jun-08		2:07:10		70.41		38		15-Jun-08		2:06:20		69.8		44		15-Jun-08		2:07:53		68.61		40.5

		15-Jun-08		4:07:10		69.8		37.5		15-Jun-08		4:06:20		69.2		44		15-Jun-08		4:07:53		68.61		40

		15-Jun-08		6:07:10		69.8		38		15-Jun-08		6:06:20		69.2		45		15-Jun-08		6:07:53		68.61		40.5

		15-Jun-08		8:07:10		70.41		39		15-Jun-08		8:06:20		69.2		45.5		15-Jun-08		8:07:53		68.61		41

		15-Jun-08		10:07:10		70.41		39		15-Jun-08		10:06:20		69.8		45		15-Jun-08		10:07:53		68.61		41

		15-Jun-08		12:07:10		70.41		40		15-Jun-08		12:06:20		70.41		46.5		15-Jun-08		12:07:53		69.2		42

		15-Jun-08		14:07:10		71		41.5		15-Jun-08		14:06:20		71		47.5		15-Jun-08		14:07:53		69.2		44

		15-Jun-08		16:07:10		71		41.5		15-Jun-08		16:06:20		70.41		51.5		15-Jun-08		16:07:53		69.2		44.5

		15-Jun-08		18:07:10		71		40.5		15-Jun-08		18:06:20		70.41		50		15-Jun-08		18:07:53		69.2		43.5

		15-Jun-08		20:07:10		71		38.5		15-Jun-08		20:06:20		69.8		47		15-Jun-08		20:07:53		69.2		41.5

		15-Jun-08		22:07:10		71		38.5		15-Jun-08		22:06:20		70.41		45.5		15-Jun-08		22:07:53		69.2		41

		16-Jun-08		0:07:10		70.41		38.5		16-Jun-08		0:06:20		69.8		44.5		16-Jun-08		0:07:53		69.2		40.5

		16-Jun-08		2:07:10		70.41		38		16-Jun-08		2:06:20		69.2		44.5		16-Jun-08		2:07:53		69.2		40

		16-Jun-08		4:07:10		70.41		38		16-Jun-08		4:06:20		68.61		45		16-Jun-08		4:07:53		69.2		40

		16-Jun-08		6:07:10		69.8		37.5		16-Jun-08		6:06:20		68.61		44.5		16-Jun-08		6:07:53		69.2		39.5

		16-Jun-08		8:07:10		69.8		38		16-Jun-08		8:06:20		68.61		44.5		16-Jun-08		8:07:53		69.2		40

		16-Jun-08		10:07:10		69.8		38.5		16-Jun-08		10:06:20		69.8		44.5		16-Jun-08		10:07:53		69.2		40

		16-Jun-08		12:07:10		70.41		40.5		16-Jun-08		12:06:20		69.8		47		16-Jun-08		12:07:53		69.2		41.5

		16-Jun-08		14:07:10		70.41		42		16-Jun-08		14:06:20		70.41		49.5		16-Jun-08		14:07:53		69.2		43.5

		16-Jun-08		16:07:10		71		40.5		16-Jun-08		16:06:20		71		46		16-Jun-08		16:07:53		69.2		43

		16-Jun-08		18:07:10		71		39.5		16-Jun-08		18:06:20		71		43.5		16-Jun-08		18:07:53		69.2		42.5

		16-Jun-08		20:07:10		71		38		16-Jun-08		20:06:20		70.41		44.5		16-Jun-08		20:07:53		69.2		41

		16-Jun-08		22:07:10		70.41		38		16-Jun-08		22:06:20		70.41		43		16-Jun-08		22:07:53		69.2		40

		17-Jun-08		0:07:10		70.41		37.5		17-Jun-08		0:06:20		69.8		42		17-Jun-08		0:07:53		69.2		39.5

		17-Jun-08		2:07:10		69.8		36.5		17-Jun-08		2:06:20		68.61		43		17-Jun-08		2:07:53		69.2		39

		17-Jun-08		4:07:10		69.8		38		17-Jun-08		4:06:20		68		45.5		17-Jun-08		4:07:53		69.2		40

		17-Jun-08		6:07:10		69.8		38		17-Jun-08		6:06:20		68		45.5		17-Jun-08		6:07:53		69.2		40

		17-Jun-08		8:07:10		70.41		38.5		17-Jun-08		8:06:20		70.41		45		17-Jun-08		8:07:53		68.61		41

		17-Jun-08		10:07:10		70.41		39		17-Jun-08		10:06:20		71		44		17-Jun-08		10:07:53		68.61		41

		17-Jun-08		12:07:10		71		39.5		17-Jun-08		12:06:20		69.8		45.5		17-Jun-08		12:07:53		69.2		42

		17-Jun-08		14:07:10		71		41.5		17-Jun-08		14:06:20		70.41		48.5		17-Jun-08		14:07:53		68		45

		17-Jun-08		16:07:10		71		40		17-Jun-08		16:06:20		70.41		45		17-Jun-08		16:07:53		69.2		43.5

		17-Jun-08		18:07:10		71		39.5		17-Jun-08		18:06:20		70.41		46		17-Jun-08		18:07:53		69.8		41.5

		17-Jun-08		20:07:10		70.41		38.5		17-Jun-08		20:06:20		69.8		44.5		17-Jun-08		20:07:53		69.8		40

		17-Jun-08		22:07:10		70.41		38		17-Jun-08		22:06:20		69.8		43		17-Jun-08		22:07:53		69.8		39.5

		18-Jun-08		0:07:10		70.41		37.5		18-Jun-08		0:06:20		69.2		43		18-Jun-08		0:07:53		69.8		39

		18-Jun-08		2:07:10		70.41		37.5		18-Jun-08		2:06:20		68		43.5		18-Jun-08		2:07:53		69.8		38.5

		18-Jun-08		4:07:10		70.41		38		18-Jun-08		4:06:20		67.4		46		18-Jun-08		4:07:53		69.8		39

		18-Jun-08		6:07:10		70.41		38		18-Jun-08		6:06:20		66.81		46.5		18-Jun-08		6:07:53		69.8		39

		18-Jun-08		8:07:10		70.41		39		18-Jun-08		8:06:20		70.41		43.5		18-Jun-08		8:07:53		69.2		40.5

		18-Jun-08		10:07:10		71		38.5		18-Jun-08		10:06:20		70.41		44.5		18-Jun-08		10:07:53		68.61		41

		18-Jun-08		12:07:10		71		39		18-Jun-08		12:06:20		69.8		44.5		18-Jun-08		12:07:53		69.8		41

		18-Jun-08		14:07:10		71		42		18-Jun-08		14:06:20		69.8		46.5		18-Jun-08		14:07:53		69.2		44.5

		18-Jun-08		16:07:10		71		43.5		18-Jun-08		16:06:20		69.8		51.5		18-Jun-08		16:07:53		69.2		46

		18-Jun-08		18:07:10		71		29		18-Jun-08		18:06:20		69.2		31		18-Jun-08		18:07:53		69.2		32

		18-Jun-08		20:07:10		71		28		18-Jun-08		20:06:20		68.61		29		18-Jun-08		20:07:53		69.2		30

		18-Jun-08		22:07:10		71		29.5		18-Jun-08		22:06:20		68.61		31		18-Jun-08		22:07:53		69.2		31.5

		19-Jun-08		0:07:10		70.41		29		19-Jun-08		0:06:20		68.61		31.5		19-Jun-08		0:07:53		69.2		31

		19-Jun-08		2:07:10		69.8		34		19-Jun-08		2:06:20		68		37		19-Jun-08		2:07:53		69.2		35.5

		19-Jun-08		4:07:10		69.2		35		19-Jun-08		4:06:20		67.4		39.5		19-Jun-08		4:07:53		68.61		36.5

		19-Jun-08		6:07:10		69.8		34		19-Jun-08		6:06:20		67.4		39		19-Jun-08		6:07:53		69.2		35.5

		19-Jun-08		8:07:10		69.8		35.5		19-Jun-08		8:06:20		68		41.5		19-Jun-08		8:07:53		69.2		37.5

		19-Jun-08		10:07:10		71		33.5		19-Jun-08		10:06:20		70.41		36.5		19-Jun-08		10:07:53		69.2		36.5

		19-Jun-08		12:07:10		71		31		19-Jun-08		12:06:20		70.41		33		19-Jun-08		12:07:53		69.8		33

		19-Jun-08		14:07:10		70.41		34.5		19-Jun-08		14:06:20		71		36		19-Jun-08		14:07:53		69.8		36

		19-Jun-08		16:07:10		70.41		31		19-Jun-08		16:06:20		69.2		32.5		19-Jun-08		16:07:53		69.8		32.5

		19-Jun-08		18:07:10		71		25		19-Jun-08		18:06:20		69.2		26		19-Jun-08		18:07:53		69.2		27

		19-Jun-08		20:07:10		71		26		19-Jun-08		20:06:20		69.2		27		19-Jun-08		20:07:53		69.2		27.5

		19-Jun-08		22:07:10		71		30.5		19-Jun-08		22:06:20		68.61		31.5		19-Jun-08		22:07:53		69.2		31.5

		20-Jun-08		0:07:10		71		33		20-Jun-08		0:06:20		68		37		20-Jun-08		0:07:53		68.61		35.5

		20-Jun-08		2:07:10		70.41		33.5		20-Jun-08		2:06:20		68		37.5		20-Jun-08		2:07:53		68.61		35.5

		20-Jun-08		4:07:10		69.8		33.5		20-Jun-08		4:06:20		68		38		20-Jun-08		4:07:53		68.61		36

		20-Jun-08		6:07:10		69.2		34.5		20-Jun-08		6:06:20		67.4		39		20-Jun-08		6:07:53		68		36.5

		20-Jun-08		8:07:10		69.8		35.5		20-Jun-08		8:06:20		68.61		39		20-Jun-08		8:07:53		68.61		37.5

		20-Jun-08		10:07:10		71		35.5		20-Jun-08		10:06:20		70.41		38		20-Jun-08		10:07:53		68.61		38

		20-Jun-08		12:07:10		70.41		34		20-Jun-08		12:06:20		72.21		34.5		20-Jun-08		12:07:53		68.61		36.5

		20-Jun-08		14:07:10		70.41		31		20-Jun-08		14:06:20		69.8		32		20-Jun-08		14:07:53		68		33.5

		20-Jun-08		16:07:10		70.41		32.5		20-Jun-08		16:06:20		71		34.5		20-Jun-08		16:07:53		68.61		35.5

		20-Jun-08		18:07:10		70.41		29		20-Jun-08		18:06:20		69.2		30		20-Jun-08		18:07:53		68.61		31

		20-Jun-08		20:07:10		71		31.5		20-Jun-08		20:06:20		68		34.5		20-Jun-08		20:07:53		68.61		34.5

		20-Jun-08		22:07:10		71		32.5		20-Jun-08		22:06:20		68		36		20-Jun-08		22:07:53		68.61		35

		21-Jun-08		0:07:10		71		34.5		21-Jun-08		0:06:20		68.61		38.5		21-Jun-08		0:07:53		68.61		37

		21-Jun-08		2:07:10		70.41		35		21-Jun-08		2:06:20		67.4		41		21-Jun-08		2:07:53		68.61		37

		21-Jun-08		4:07:10		70.41		36		21-Jun-08		4:06:20		67.4		41		21-Jun-08		4:07:53		69.2		37.5

		21-Jun-08		6:07:10		69.8		36		21-Jun-08		6:06:20		68		43		21-Jun-08		6:07:53		68.61		38.5

		21-Jun-08		8:07:10		71		36		21-Jun-08		8:06:20		68.61		43		21-Jun-08		8:07:53		68.61		39

		21-Jun-08		10:07:10		71		35		21-Jun-08		10:06:20		69.2		37		21-Jun-08		10:07:53		69.2		37

		21-Jun-08		12:07:10		70.41		30.5		21-Jun-08		12:06:20		71		31.5		21-Jun-08		12:07:53		69.2		33

		21-Jun-08		14:07:10		71		30		21-Jun-08		14:06:20		70.41		30.5		21-Jun-08		14:07:53		69.2		31.5

		21-Jun-08		16:07:10		71		26.5		21-Jun-08		16:06:20		71.6		26.5		21-Jun-08		16:07:53		68.61		29

		21-Jun-08		18:07:10		70.41		23		21-Jun-08		18:06:20		70.41		24		21-Jun-08		18:07:53		69.2		26

		21-Jun-08		20:07:10		71		22.5		21-Jun-08		20:06:20		71		22.5		21-Jun-08		20:07:53		69.2		24.5

		21-Jun-08		22:07:10		71		27.5		21-Jun-08		22:06:20		70.41		29		21-Jun-08		22:07:53		69.2		30

		22-Jun-08		0:07:10		71		31		22-Jun-08		0:06:20		70.41		34		22-Jun-08		0:07:53		68.61		34.5

		22-Jun-08		2:07:10		71		31.5		22-Jun-08		2:06:20		69.8		35		22-Jun-08		2:07:53		68.61		35.5

		22-Jun-08		4:07:10		71		32.5		22-Jun-08		4:06:20		69.8		34.5		22-Jun-08		4:07:53		68.61		35.5

		22-Jun-08		6:07:10		70.41		33		22-Jun-08		6:06:20		69.2		35.5		22-Jun-08		6:07:53		68.61		35.5

		22-Jun-08		8:07:10		71		33.5		22-Jun-08		8:06:20		69.2		36.5		22-Jun-08		8:07:53		69.8		35.5

		22-Jun-08		10:07:10		71		34.5		22-Jun-08		10:06:20		70.41		37		22-Jun-08		10:07:53		69.8		37

		22-Jun-08		12:07:10		71.6		32		22-Jun-08		12:06:20		71		34.5		22-Jun-08		12:07:53		69.2		36

		22-Jun-08		14:07:10		71.6		29.5		22-Jun-08		14:06:20		71		32.5		22-Jun-08		14:07:53		69.8		33.5

		22-Jun-08		16:07:10		72.21		26		22-Jun-08		16:06:20		70.41		29		22-Jun-08		16:07:53		69.2		30.5

		22-Jun-08		18:07:10		72.21		22.5		22-Jun-08		18:06:20		70.41		25.5		22-Jun-08		18:07:53		69.2		26.5

		22-Jun-08		20:07:10		72.21		30.5		22-Jun-08		20:06:20		70.41		31.5		22-Jun-08		20:07:53		69.8		31.5

		22-Jun-08		22:07:10		71.6		31		22-Jun-08		22:06:20		70.41		34.5		22-Jun-08		22:07:53		69.2		34

		23-Jun-08		0:07:10		71		34.5		23-Jun-08		0:06:20		69.2		39		23-Jun-08		0:07:53		69.2		36.5

		23-Jun-08		2:07:10		70.41		35.5		23-Jun-08		2:06:20		69.8		41.5		23-Jun-08		2:07:53		69.2		38

		23-Jun-08		4:07:10		70.41		36		23-Jun-08		4:06:20		69.2		42		23-Jun-08		4:07:53		69.8		38

		23-Jun-08		6:07:10		70.41		35.5		23-Jun-08		6:06:20		68.61		42		23-Jun-08		6:07:53		69.8		37.5

		23-Jun-08		8:07:10		70.41		37		23-Jun-08		8:06:20		69.2		44		23-Jun-08		8:07:53		69.8		38.5

		23-Jun-08		10:07:10		71		38		23-Jun-08		10:06:20		69.2		45		23-Jun-08		10:07:53		69.8		39.5

		23-Jun-08		12:07:10		71		38.5		23-Jun-08		12:06:20		69.8		42.5		23-Jun-08		12:07:53		69.8		39.5

		23-Jun-08		14:07:10		71		39		23-Jun-08		14:06:20		70.41		44.5		23-Jun-08		14:07:53		69.8		41

		23-Jun-08		16:07:10		71.6		39.5		23-Jun-08		16:06:20		69.8		46.5		23-Jun-08		16:07:53		69.8		42

		23-Jun-08		18:07:10		71.6		38		23-Jun-08		18:06:20		70.41		42.5		23-Jun-08		18:07:53		69.2		41

		23-Jun-08		20:07:10		71.6		37		23-Jun-08		20:06:20		69.8		43		23-Jun-08		20:07:53		69.8		39.5

		23-Jun-08		22:07:10		71		36		23-Jun-08		22:06:20		69.2		42.5		23-Jun-08		22:07:53		69.8		38.5

		24-Jun-08		0:07:10		69.8		36.5		24-Jun-08		0:06:20		69.2		42		24-Jun-08		0:07:53		69.2		38.5

		24-Jun-08		2:07:10		70.41		36.5		24-Jun-08		2:06:20		68.61		42		24-Jun-08		2:07:53		69.8		38

		24-Jun-08		4:07:10		70.41		36		24-Jun-08		4:06:20		68		42.5		24-Jun-08		4:07:53		69.8		37.5

		24-Jun-08		6:07:10		70.41		37.5		24-Jun-08		6:06:20		67.4		45.5		24-Jun-08		6:07:53		69.8		38.5

		24-Jun-08		8:07:10		70.41		38.5		24-Jun-08		8:06:20		69.8		44.5		24-Jun-08		8:07:53		69.8		40

		24-Jun-08		10:07:10		70.41		38		24-Jun-08		10:06:20		71		44		24-Jun-08		10:07:53		69.2		40.5

		24-Jun-08		12:07:10		70.41		39.5		24-Jun-08		12:06:20		71.6		42.5		24-Jun-08		12:07:53		69.8		41

		24-Jun-08		14:07:10		70.41		38.5		24-Jun-08		14:06:20		71		42.5		24-Jun-08		14:07:53		68		42.5

		24-Jun-08		16:07:10		71		39		24-Jun-08		16:06:20		69.2		47		24-Jun-08		16:07:53		68		42.5

		24-Jun-08		18:07:10		71		38.5		24-Jun-08		18:06:20		69.2		45.5		24-Jun-08		18:07:53		69.2		41.5

		24-Jun-08		20:07:10		70.41		38.5		24-Jun-08		20:06:20		68.61		47		24-Jun-08		20:07:53		69.2		40.5

		24-Jun-08		22:07:10		70.41		38		24-Jun-08		22:06:20		68.61		44		24-Jun-08		22:07:53		69.2		39.5

		25-Jun-08		0:07:10		70.41		38.5		25-Jun-08		0:06:20		68		43.5		25-Jun-08		0:07:53		69.2		40

		25-Jun-08		2:07:10		70.41		37.5		25-Jun-08		2:06:20		67.4		46.5		25-Jun-08		2:07:53		69.8		39

		25-Jun-08		4:07:10		70.41		37.5		25-Jun-08		4:06:20		67.4		45		25-Jun-08		4:07:53		69.8		39

		25-Jun-08		6:07:10		70.41		37		25-Jun-08		6:06:20		66.81		45		25-Jun-08		6:07:53		69.8		38.5

		25-Jun-08		8:07:10		69.8		38.5		25-Jun-08		8:06:20		68		44		25-Jun-08		8:07:53		68.61		40.5

		25-Jun-08		10:07:10		70.41		39		25-Jun-08		10:06:20		69.8		46.5		25-Jun-08		10:07:53		68.61		42

		25-Jun-08		12:07:10		70.41		40.5		25-Jun-08		12:06:20		69.8		44		25-Jun-08		12:07:53		68		43.5

		25-Jun-08		14:07:10		70.41		42		25-Jun-08		14:06:20		69.8		47		25-Jun-08		14:07:53		67.4		46.5

		25-Jun-08		16:07:10		70.41		41.5		25-Jun-08		16:06:20		69.8		50		25-Jun-08		16:07:53		68.61		45

		25-Jun-08		18:07:10		71		39.5		25-Jun-08		18:06:20		69.2		48		25-Jun-08		18:07:53		68.61		43.5

		25-Jun-08		20:07:10		71		38.5		25-Jun-08		20:06:20		69.2		44		25-Jun-08		20:07:53		69.2		42

		25-Jun-08		22:07:10		71		38		25-Jun-08		22:06:20		69.8		43.5		25-Jun-08		22:07:53		69.2		40.5

		26-Jun-08		0:07:10		70.41		38		26-Jun-08		0:06:20		68.61		46		26-Jun-08		0:07:53		69.2		40

		26-Jun-08		2:07:10		69.8		38		26-Jun-08		2:06:20		68.61		44.5		26-Jun-08		2:07:53		68.61		39.5

		26-Jun-08		4:07:10		70.41		38		26-Jun-08		4:06:20		68.61		44		26-Jun-08		4:07:53		69.2		39.5

		26-Jun-08		6:07:10		70.41		37.5		26-Jun-08		6:06:20		68		44.5		26-Jun-08		6:07:53		69.8		39

		26-Jun-08		8:07:10		70.41		39		26-Jun-08		8:06:20		69.2		44		26-Jun-08		8:07:53		68		41.5

		26-Jun-08		10:07:10		70.41		39		26-Jun-08		10:06:20		69.2		45		26-Jun-08		10:07:53		68.61		41.5

		26-Jun-08		12:07:10		70.41		40.5		26-Jun-08		12:06:20		71		43.5		26-Jun-08		12:07:53		68.61		43

		26-Jun-08		14:07:10		70.41		42.5		26-Jun-08		14:06:20		70.41		47.5		26-Jun-08		14:07:53		68		46

		26-Jun-08		16:07:10		70.41		42.5		26-Jun-08		16:06:20		68.61		49.5		26-Jun-08		16:07:53		68.61		45.5

		26-Jun-08		18:07:10		70.41		41.5		26-Jun-08		18:06:20		69.2		47		26-Jun-08		18:07:53		69.2		43.5

		26-Jun-08		20:07:10		70.41		40		26-Jun-08		20:06:20		69.2		47.5		26-Jun-08		20:07:53		69.2		42

		26-Jun-08		22:07:10		70.41		39		26-Jun-08		22:06:20		69.2		46.5		26-Jun-08		22:07:53		69.2		41

		27-Jun-08		0:07:10		69.8		38		27-Jun-08		0:06:20		68		47.5		27-Jun-08		0:07:53		68.61		40.5

		27-Jun-08		2:07:10		69.8		38		27-Jun-08		2:06:20		67.4		46		27-Jun-08		2:07:53		69.2		40

		27-Jun-08		4:07:10		70.41		38		27-Jun-08		4:06:20		68		45		27-Jun-08		4:07:53		69.8		39

		27-Jun-08		6:07:10		69.8		37.5		27-Jun-08		6:06:20		67.4		45		27-Jun-08		6:07:53		69.8		39

		27-Jun-08		8:07:10		70.41		39		27-Jun-08		8:06:20		68.61		49.5		27-Jun-08		8:07:53		69.2		40.5

		27-Jun-08		10:07:10		70.41		39.5		27-Jun-08		10:06:20		69.8		44.5		27-Jun-08		10:07:53		68.61		42

		27-Jun-08		12:07:10		70.41		41		27-Jun-08		12:06:20		70.41		50.5		27-Jun-08		12:07:53		69.2		43

		27-Jun-08		14:07:10		70.41		43		27-Jun-08		14:06:20		71		48.5		27-Jun-08		14:07:53		68		46

		27-Jun-08		16:07:10		70.41		42.5		27-Jun-08		16:06:20		70.41		48.5		27-Jun-08		16:07:53		68		46

		27-Jun-08		18:07:10		70.41		40		27-Jun-08		18:06:20		70.41		44		27-Jun-08		18:07:53		68.61		43

		27-Jun-08		20:07:10		70.41		39		27-Jun-08		20:06:20		70.41		44.5		27-Jun-08		20:07:53		68.61		42

		27-Jun-08		22:07:10		70.41		38.5		27-Jun-08		22:06:20		70.41		45		27-Jun-08		22:07:53		69.2		41

		28-Jun-08		0:07:10		69.8		38.5		28-Jun-08		0:06:20		69.2		46		28-Jun-08		0:07:53		68.61		41

		28-Jun-08		2:07:10		69.8		38.5		28-Jun-08		2:06:20		69.2		45		28-Jun-08		2:07:53		68.61		40.5

		28-Jun-08		4:07:10		69.2		38.5		28-Jun-08		4:06:20		69.2		44.5		28-Jun-08		4:07:53		68.61		40

		28-Jun-08		6:07:10		69.2		39.5		28-Jun-08		6:06:20		69.2		45.5		28-Jun-08		6:07:53		68.61		40.5

		28-Jun-08		8:07:10		69.8		39.5		28-Jun-08		8:06:20		70.41		44		28-Jun-08		8:07:53		68.61		41.5

		28-Jun-08		10:07:10		71		40.5		28-Jun-08		10:06:20		71		50.5		28-Jun-08		10:07:53		68.61		43

		28-Jun-08		12:07:10		70.41		42.5		28-Jun-08		12:06:20		71.6		48		28-Jun-08		12:07:53		69.8		44

		28-Jun-08		14:07:10		70.41		43.5		28-Jun-08		14:06:20		71.6		53.5		28-Jun-08		14:07:53		68.61		46

		28-Jun-08		16:07:10		70.41		44		28-Jun-08		16:06:20		71		50		28-Jun-08		16:07:53		69.2		46.5

		28-Jun-08		18:07:10		71		40.5		28-Jun-08		18:06:20		70.41		51		28-Jun-08		18:07:53		69.2		43.5

		28-Jun-08		20:07:10		71		39.5		28-Jun-08		20:06:20		70.41		49.5		28-Jun-08		20:07:53		69.2		42

		28-Jun-08		22:07:10		70.41		39.5		28-Jun-08		22:06:20		69.8		49		28-Jun-08		22:07:53		69.8		41

		29-Jun-08		0:07:10		69.8		39.5		29-Jun-08		0:06:20		69.8		49.5		29-Jun-08		0:07:53		69.2		41.5

		29-Jun-08		2:07:10		69.8		40		29-Jun-08		2:06:20		69.2		49		29-Jun-08		2:07:53		69.2		41.5

		29-Jun-08		4:07:10		69.8		40		29-Jun-08		4:06:20		69.2		50		29-Jun-08		4:07:53		69.8		41.5

		29-Jun-08		6:07:10		69.8		40		29-Jun-08		6:06:20		69.2		50.5		29-Jun-08		6:07:53		69.8		41

		29-Jun-08		8:07:10		69.8		40		29-Jun-08		8:06:20		69.8		50.5		29-Jun-08		8:07:53		69.8		41.5

		29-Jun-08		10:07:10		70.41		40.5		29-Jun-08		10:06:20		69.2		47		29-Jun-08		10:07:53		69.8		41.5

		29-Jun-08		12:07:10		70.41		41.5		29-Jun-08		12:06:20		69.2		53.5		29-Jun-08		12:07:53		69.8		42.5

		29-Jun-08		14:07:10		70.41		42.5		29-Jun-08		14:06:20		69.8		48		29-Jun-08		14:07:53		70.41		44

		29-Jun-08		16:07:10		71		43		29-Jun-08		16:06:20		69.8		52.5		29-Jun-08		16:07:53		70.41		44.5

		29-Jun-08		18:07:10		71		42		29-Jun-08		18:06:20		70.41		53		29-Jun-08		18:07:53		70.41		44

		29-Jun-08		20:07:10		71		40		29-Jun-08		20:06:20		69.2		52		29-Jun-08		20:07:53		69.8		42

		29-Jun-08		22:07:10		70.41		39.5		29-Jun-08		22:06:20		69.2		50		29-Jun-08		22:07:53		69.8		41

		30-Jun-08		0:07:10		69.2		40		30-Jun-08		0:06:20		69.2		48.5		30-Jun-08		0:07:53		69.2		41

		30-Jun-08		2:07:10		69.2		40		30-Jun-08		2:06:20		69.2		48.5		30-Jun-08		2:07:53		69.8		41

		30-Jun-08		4:07:10		69.2		40		30-Jun-08		4:06:20		69.2		49		30-Jun-08		4:07:53		69.2		41

		30-Jun-08		6:07:10		69.2		40		30-Jun-08		6:06:20		69.2		49		30-Jun-08		6:07:53		69.2		41

		30-Jun-08		8:07:10		69.2		40		30-Jun-08		8:06:20		69.2		49		30-Jun-08		8:07:53		69.8		41

		30-Jun-08		10:07:10		69.2		40		30-Jun-08		10:06:20		69.8		47.5		30-Jun-08		10:07:53		69.8		41

		30-Jun-08		12:07:10		70.41		41.5		30-Jun-08		12:06:20		69.8		49.5		30-Jun-08		12:07:53		70.41		42

		30-Jun-08		14:07:10		70.41		43		30-Jun-08		14:06:20		70.41		48		30-Jun-08		14:07:53		70.41		43.5

		30-Jun-08		16:07:10		71		43		30-Jun-08		16:06:20		70.41		50.5		30-Jun-08		16:07:53		70.41		44.5

		30-Jun-08		18:07:10		71		41.5		30-Jun-08		18:06:20		69.8		50		30-Jun-08		18:07:53		70.41		43.5

		30-Jun-08		20:07:10		71		40		30-Jun-08		20:06:20		69.8		50		30-Jun-08		20:07:53		70.41		42

		30-Jun-08		22:07:10		69.8		39.5		30-Jun-08		22:06:20		69.8		48.5		30-Jun-08		22:07:53		69.8		40.5

		1-Jul-08		0:07:10		69.8		40		1-Jul-08		0:06:20		69.2		48.5		1-Jul-08		0:07:53		69.2		41

		1-Jul-08		2:07:10		69.2		40		1-Jul-08		2:06:20		69.2		48.5		1-Jul-08		2:07:53		69.2		41

		1-Jul-08		4:07:10		69.8		40.5		1-Jul-08		4:06:20		68.61		49		1-Jul-08		4:07:53		69.8		41

		1-Jul-08		6:07:10		69.8		40		1-Jul-08		6:06:20		68.61		49.5		1-Jul-08		6:07:53		69.8		41

		1-Jul-08		8:07:10		70.41		40.5		1-Jul-08		8:06:20		71		48.5		1-Jul-08		8:07:53		69.8		41

		1-Jul-08		10:07:10		70.41		40		1-Jul-08		10:06:20		71		47.5		1-Jul-08		10:07:53		69.8		41.5

		1-Jul-08		12:07:10		70.41		42		1-Jul-08		12:06:20		70.41		46		1-Jul-08		12:07:53		70.41		43.5

		1-Jul-08		14:07:10		71		44		1-Jul-08		14:06:20		70.41		48		1-Jul-08		14:07:53		69.8		45

		1-Jul-08		16:07:10		70.41		44.5		1-Jul-08		16:06:20		70.41		57.5		1-Jul-08		16:07:53		69.2		47

		1-Jul-08		18:07:10		71		43		1-Jul-08		18:06:20		70.41		53		1-Jul-08		18:07:53		69.2		45.5

		1-Jul-08		20:07:10		71		41		1-Jul-08		20:06:20		70.41		53.5		1-Jul-08		20:07:53		69.2		44

		1-Jul-08		22:07:10		71		40		1-Jul-08		22:06:20		69.8		52		1-Jul-08		22:07:53		69.8		42

		2-Jul-08		0:07:10		70.41		40		2-Jul-08		0:06:20		69.2		52		2-Jul-08		0:07:53		69.2		41.5

		2-Jul-08		2:07:10		69.8		40		2-Jul-08		2:06:20		69.2		52		2-Jul-08		2:07:53		69.2		42

		2-Jul-08		4:07:10		69.8		40		2-Jul-08		4:06:20		69.8		51.5		2-Jul-08		4:07:53		69.8		41.5

		2-Jul-08		6:07:10		69.8		40.5		2-Jul-08		6:06:20		69.2		53		2-Jul-08		6:07:53		69.2		42

		2-Jul-08		8:07:10		70.41		41		2-Jul-08		8:06:20		70.41		49		2-Jul-08		8:07:53		69.2		42.5

		2-Jul-08		10:07:10		70.41		40.5		2-Jul-08		10:06:20		69.8		46.5		2-Jul-08		10:07:53		69.8		42

		2-Jul-08		12:07:10		71		42.5		2-Jul-08		12:06:20		70.41		54		2-Jul-08		12:07:53		69.8		43.5

		2-Jul-08		14:07:10		70.41		44.5		2-Jul-08		14:06:20		70.41		50.5		2-Jul-08		14:07:53		69.2		46.5

		2-Jul-08		16:07:10		71		44.5		2-Jul-08		16:06:20		70.41		57.5		2-Jul-08		16:07:53		69.2		47

		2-Jul-08		18:07:10		71		43		2-Jul-08		18:06:20		69.8		49		2-Jul-08		18:07:53		69.8		45

		2-Jul-08		20:07:10		71		41		2-Jul-08		20:06:20		69.8		52		2-Jul-08		20:07:53		69.8		43

		2-Jul-08		22:07:10		70.41		40		2-Jul-08		22:06:20		69.8		49.5		2-Jul-08		22:07:53		69.8		41.5

		3-Jul-08		0:07:10		69.2		40		3-Jul-08		0:06:20		69.8		49		3-Jul-08		0:07:53		69.2		41.5

		3-Jul-08		2:07:10		70.41		40		3-Jul-08		2:06:20		69.2		48		3-Jul-08		2:07:53		69.8		41

		3-Jul-08		4:07:10		70.41		40		3-Jul-08		4:06:20		68.61		49		3-Jul-08		4:07:53		69.8		41

		3-Jul-08		6:07:10		69.8		40		3-Jul-08		6:06:20		68		49.5		3-Jul-08		6:07:53		69.8		41

		3-Jul-08		8:07:10		70.41		40.5		3-Jul-08		8:06:20		69.8		49		3-Jul-08		8:07:53		69.8		41.5

		3-Jul-08		10:07:10		70.41		41		3-Jul-08		10:06:20		70.41		45		3-Jul-08		10:07:53		69.8		41.5

		3-Jul-08		12:07:10		70.41		43		3-Jul-08		12:06:20		71		45.5		3-Jul-08		12:07:53		69.8		43.5

		3-Jul-08		14:07:10		70.41		44.5		3-Jul-08		14:06:20		71		47		3-Jul-08		14:07:53		69.2		46

		3-Jul-08		16:07:10		70.41		44		3-Jul-08		16:06:20		69.8		53		3-Jul-08		16:07:53		69.2		46

		3-Jul-08		18:07:10		70.41		43		3-Jul-08		18:06:20		70.41		49		3-Jul-08		18:07:53		69.8		44.5

		3-Jul-08		20:07:10		70.41		41.5		3-Jul-08		20:06:20		70.41		51.5		3-Jul-08		20:07:53		69.8		43.5

		3-Jul-08		22:07:10		71		40		3-Jul-08		22:06:20		69.2		51		3-Jul-08		22:07:53		69.8		42

		4-Jul-08		0:07:10		69.8		39.5		4-Jul-08		0:06:20		69.2		49.5		4-Jul-08		0:07:53		69.2		41.5

		4-Jul-08		2:07:10		69.2		40.5		4-Jul-08		2:06:20		69.2		47.5		4-Jul-08		2:07:53		69.2		41.5

		4-Jul-08		4:07:10		69.8		40		4-Jul-08		4:06:20		68.61		48		4-Jul-08		4:07:53		69.2		41.5

		4-Jul-08		6:07:10		69.8		39.5		4-Jul-08		6:06:20		69.8		44		4-Jul-08		6:07:53		69.2		41.5

		4-Jul-08		8:07:10		69.8		40		4-Jul-08		8:06:20		69.8		50.5		4-Jul-08		8:07:53		69.2		41.5

		4-Jul-08		10:07:10		71		42		4-Jul-08		10:06:20		69.8		50.5		4-Jul-08		10:07:53		69.2		43

		4-Jul-08		12:07:10		70.41		47		4-Jul-08		12:06:20		71.6		55		4-Jul-08		12:07:53		69.2		48

		4-Jul-08		14:07:10		71		47.5		4-Jul-08		14:06:20		71		55		4-Jul-08		14:07:53		69.2		50

		4-Jul-08		16:07:10		71		48		4-Jul-08		16:06:20		71.6		57		4-Jul-08		16:07:53		69.2		50

		4-Jul-08		18:07:10		71.6		46		4-Jul-08		18:06:20		71.6		54		4-Jul-08		18:07:53		69.2		49.5

		4-Jul-08		20:07:10		71.6		43.5		4-Jul-08		20:06:20		71.6		59		4-Jul-08		20:07:53		69.2		46.5

		4-Jul-08		22:07:10		71		41.5		4-Jul-08		22:06:20		69.8		56.5		4-Jul-08		22:07:53		69.2		45

		5-Jul-08		0:07:10		70.41		42		5-Jul-08		0:06:20		69.8		56.5		5-Jul-08		0:07:53		68.61		44.5

		5-Jul-08		2:07:10		69.8		41		5-Jul-08		2:06:20		69.8		54.5		5-Jul-08		2:07:53		69.2		43.5

		5-Jul-08		4:07:10		69.8		41		5-Jul-08		4:06:20		69.2		53		5-Jul-08		4:07:53		69.2		42.5

		5-Jul-08		6:07:10		69.2		41.5		5-Jul-08		6:06:20		68.61		54.5		5-Jul-08		6:07:53		68.61		43

		5-Jul-08		8:07:10		69.8		42		5-Jul-08		8:06:20		69.2		55		5-Jul-08		8:07:53		69.2		44

		5-Jul-08		10:07:10		71		43		5-Jul-08		10:06:20		69.8		51.5		5-Jul-08		10:07:53		69.2		45

		5-Jul-08		12:07:10		71		45		5-Jul-08		12:06:20		69.8		53.5		5-Jul-08		12:07:53		69.2		47.5

		5-Jul-08		14:07:10		71.6		45.5		5-Jul-08		14:06:20		70.41		55		5-Jul-08		14:07:53		69.2		48.5

		5-Jul-08		16:07:10		71.6		46		5-Jul-08		16:06:20		70.41		55.5		5-Jul-08		16:07:53		69.2		49.5

		5-Jul-08		18:07:10		71.6		45		5-Jul-08		18:06:20		70.41		59.5		5-Jul-08		18:07:53		68.61		48.5

		5-Jul-08		20:07:10		71		42.5		5-Jul-08		20:06:20		69.8		58		5-Jul-08		20:07:53		69.2		46

		5-Jul-08		22:07:10		71		41.5		5-Jul-08		22:06:20		69.2		57.5		5-Jul-08		22:07:53		69.2		45

		6-Jul-08		0:07:10		70.41		41		6-Jul-08		0:06:20		69.2		56		6-Jul-08		0:07:53		69.2		43.5

		6-Jul-08		2:07:10		69.8		40.5		6-Jul-08		2:06:20		68.61		54.5		6-Jul-08		2:07:53		68.61		43

		6-Jul-08		4:07:10		69.8		40.5		6-Jul-08		4:06:20		69.2		52.5		6-Jul-08		4:07:53		68.61		42.5

		6-Jul-08		6:07:10		69.2		41.5		6-Jul-08		6:06:20		69.2		51.5		6-Jul-08		6:07:53		68.61		42.5

		6-Jul-08		8:07:10		69.8		41.5		6-Jul-08		8:06:20		69.2		53		6-Jul-08		8:07:53		68.61		43.5

		6-Jul-08		10:07:10		71		43		6-Jul-08		10:06:20		69.8		55.5		6-Jul-08		10:07:53		69.2		45

		6-Jul-08		12:07:10		71		47		6-Jul-08		12:06:20		70.41		58.5		6-Jul-08		12:07:53		69.2		49

		6-Jul-08		14:07:10		71.6		49		6-Jul-08		14:06:20		70.41		57.5		6-Jul-08		14:07:53		69.2		52

		6-Jul-08		16:07:10		72.21		46		6-Jul-08		16:06:20		70.41		54		6-Jul-08		16:07:53		69.2		51

		6-Jul-08		18:07:10		72.21		47		6-Jul-08		18:06:20		69.8		61		6-Jul-08		18:07:53		69.2		51

		6-Jul-08		20:07:10		72.21		45		6-Jul-08		20:06:20		70.41		54.5		6-Jul-08		20:07:53		69.2		50

		6-Jul-08		22:07:10		72.21		43		6-Jul-08		22:06:20		69.8		62		6-Jul-08		22:07:53		68.61		48

		7-Jul-08		0:07:10		71.6		41.5		7-Jul-08		0:06:20		69.8		57		7-Jul-08		0:07:53		69.2		45

		7-Jul-08		2:07:10		71		41		7-Jul-08		2:06:20		69.8		52		7-Jul-08		2:07:53		69.2		44.5

		7-Jul-08		4:07:10		70.41		41		7-Jul-08		4:06:20		69.2		54		7-Jul-08		4:07:53		69.2		43.5

		7-Jul-08		6:07:10		69.8		40.5		7-Jul-08		6:06:20		69.2		52.5		7-Jul-08		6:07:53		68.61		43

		7-Jul-08		8:07:10		70.41		41.5		7-Jul-08		8:06:20		69.2		53.5		7-Jul-08		8:07:53		69.2		43.5

		7-Jul-08		10:07:10		71		44		7-Jul-08		10:06:20		69.2		58		7-Jul-08		10:07:53		69.2		46

		7-Jul-08		12:07:10		71.6		47.5		7-Jul-08		12:06:20		69.8		62		7-Jul-08		12:07:53		69.2		50

		7-Jul-08		14:07:10		71.6		50.5		7-Jul-08		14:06:20		70.41		59.5		7-Jul-08		14:07:53		69.2		54

		7-Jul-08		16:07:10		72.21		48.5		7-Jul-08		16:06:20		69.8		62		7-Jul-08		16:07:53		69.8		52.5

		7-Jul-08		18:07:10		72.21		46.5		7-Jul-08		18:06:20		70.41		59.5		7-Jul-08		18:07:53		69.2		52

		7-Jul-08		20:07:10		72.21		42.5		7-Jul-08		20:06:20		69.8		55		7-Jul-08		20:07:53		68.61		47.5

		7-Jul-08		22:07:10		72.21		40.5		7-Jul-08		22:06:20		69.8		50		7-Jul-08		22:07:53		69.2		44.5

		8-Jul-08		0:07:10		71		40		8-Jul-08		0:06:20		69.2		52		8-Jul-08		0:07:53		69.2		43.5

		8-Jul-08		2:07:10		70.41		40.5		8-Jul-08		2:06:20		69.2		51		8-Jul-08		2:07:53		69.2		42.5

		8-Jul-08		4:07:10		69.8		40.5		8-Jul-08		4:06:20		68.61		51.5		8-Jul-08		4:07:53		68.61		42.5

		8-Jul-08		6:07:10		69.2		40.5		8-Jul-08		6:06:20		69.2		51.5		8-Jul-08		6:07:53		68.61		42.5

		8-Jul-08		8:07:10		70.41		41.5		8-Jul-08		8:06:20		69.8		53.5		8-Jul-08		8:07:53		68.61		44

		8-Jul-08		10:07:10		71.6		44		8-Jul-08		10:06:20		69.8		50.5		8-Jul-08		10:07:53		68.61		47.5

		8-Jul-08		12:07:10		71		49		8-Jul-08		12:06:20		69.8		54		8-Jul-08		12:07:53		69.2		51

		8-Jul-08		14:07:10		71		49.5		8-Jul-08		14:06:20		70.41		55.5		8-Jul-08		14:07:53		69.2		53.5

		8-Jul-08		16:07:10		71		50		8-Jul-08		16:06:20		70.41		58.5		8-Jul-08		16:07:53		68.61		53.5

		8-Jul-08		18:07:10		71		49		8-Jul-08		18:06:20		70.41		55.5		8-Jul-08		18:07:53		68.61		52.5

		8-Jul-08		20:07:10		71		45		8-Jul-08		20:06:20		71		57.5		8-Jul-08		20:07:53		68		50

		8-Jul-08		22:07:10		71.6		43		8-Jul-08		22:06:20		70.41		53		8-Jul-08		22:07:53		68.61		47.5

		9-Jul-08		0:07:10		71.6		42		9-Jul-08		0:06:20		70.41		52		9-Jul-08		0:07:53		69.2		46

		9-Jul-08		2:07:10		71		41.5		9-Jul-08		2:06:20		69.8		50		9-Jul-08		2:07:53		69.2		44.5

		9-Jul-08		4:07:10		71		41.5		9-Jul-08		4:06:20		69.2		53.5		9-Jul-08		4:07:53		69.2		44

		9-Jul-08		6:07:10		70.41		41		9-Jul-08		6:06:20		69.2		52.5		9-Jul-08		6:07:53		69.2		43.5

		9-Jul-08		8:07:10		71		42.5		9-Jul-08		8:06:20		70.41		56.5		9-Jul-08		8:07:53		68.61		45

		9-Jul-08		10:07:10		71		45.5		9-Jul-08		10:06:20		71		53		9-Jul-08		10:07:53		69.2		48.5

		9-Jul-08		12:07:10		71		49		9-Jul-08		12:06:20		71.6		51		9-Jul-08		12:07:53		69.8		50.5

		9-Jul-08		14:07:10		70.41		47.5		9-Jul-08		14:06:20		71.6		51		9-Jul-08		14:07:53		68.61		51

		9-Jul-08		16:07:10		70.41		49		9-Jul-08		16:06:20		71.6		52.5		9-Jul-08		16:07:53		69.8		50

		9-Jul-08		18:07:10		70.41		48.5		9-Jul-08		18:06:20		70.41		53		9-Jul-08		18:07:53		69.8		50

		9-Jul-08		20:07:10		71		44		9-Jul-08		20:06:20		71		53		9-Jul-08		20:07:53		69.2		47.5

		9-Jul-08		22:07:10		71.6		43		9-Jul-08		22:06:20		70.41		54		9-Jul-08		22:07:53		69.8		46

		10-Jul-08		0:07:10		71.6		42		10-Jul-08		0:06:20		69.8		54.5		10-Jul-08		0:07:53		69.2		45

		10-Jul-08		2:07:10		71.6		41.5		10-Jul-08		2:06:20		69.8		54		10-Jul-08		2:07:53		69.8		44

		10-Jul-08		4:07:10		71		42		10-Jul-08		4:06:20		69.2		58		10-Jul-08		4:07:53		69.8		44

		10-Jul-08		6:07:10		71		41.5		10-Jul-08		6:06:20		69.8		55.5		10-Jul-08		6:07:53		69.8		43.5

		10-Jul-08		8:07:10		71		42.5		10-Jul-08		8:06:20		69.8		58.5		10-Jul-08		8:07:53		69.8		45

		10-Jul-08		10:07:10		71		44.5		10-Jul-08		10:06:20		69.8		58.5		10-Jul-08		10:07:53		68		48.5

		10-Jul-08		12:07:10		70.41		49		10-Jul-08		12:06:20		69.8		56.5		10-Jul-08		12:07:53		69.2		50.5

		10-Jul-08		14:07:10		70.41		52.5		10-Jul-08		14:06:20		71.6		54		10-Jul-08		14:07:53		69.2		54.5

		10-Jul-08		16:07:10		70.41		51		10-Jul-08		16:06:20		71.6		60		10-Jul-08		16:07:53		68.61		54

		10-Jul-08		18:07:10		70.41		49.5		10-Jul-08		18:06:20		70.41		63		10-Jul-08		18:07:53		69.8		51

		10-Jul-08		20:07:10		71		46		10-Jul-08		20:06:20		70.41		58.5		10-Jul-08		20:07:53		69.8		48.5

		10-Jul-08		22:07:10		71.6		43.5		10-Jul-08		22:06:20		70.41		57		10-Jul-08		22:07:53		69.8		47

		11-Jul-08		0:07:10		71.6		42.5		11-Jul-08		0:06:20		69.8		61		11-Jul-08		0:07:53		69.2		46.5

		11-Jul-08		2:07:10		71.6		42.5		11-Jul-08		2:06:20		69.8		53.5		11-Jul-08		2:07:53		69.8		45.5

		11-Jul-08		4:07:10		71		42		11-Jul-08		4:06:20		69.8		53.5		11-Jul-08		4:07:53		69.2		44.5

		11-Jul-08		6:07:10		71		41.5		11-Jul-08		6:06:20		69.8		57		11-Jul-08		6:07:53		69.2		44.5

		11-Jul-08		8:07:10		71		42.5		11-Jul-08		8:06:20		71.6		49		11-Jul-08		8:07:53		69.8		45

		11-Jul-08		10:07:10		71		45.5		11-Jul-08		10:06:20		72.21		56.5		11-Jul-08		10:07:53		68.61		48

		11-Jul-08		12:07:10		71		48.5		11-Jul-08		12:06:20		69.8		63		11-Jul-08		12:07:53		69.2		50.5

		11-Jul-08		14:07:10		71		49.5		11-Jul-08		14:06:20		70.41		55.5		11-Jul-08		14:07:53		69.2		52.5

		11-Jul-08		16:07:10		71		47		11-Jul-08		16:06:20		69.8		63.5		11-Jul-08		16:07:53		69.2		49.5

		11-Jul-08		18:07:10		71		45		11-Jul-08		18:06:20		70.41		54		11-Jul-08		18:07:53		69.2		47.5

		11-Jul-08		20:07:10		71		42.5		11-Jul-08		20:06:20		70.41		53		11-Jul-08		20:07:53		69.2		45.5

		11-Jul-08		22:07:10		71		40.5		11-Jul-08		22:06:20		70.41		52.5		11-Jul-08		22:07:53		69.8		43.5

		12-Jul-08		0:07:10		70.41		41		12-Jul-08		0:06:20		69.2		53		12-Jul-08		0:07:53		69.2		43

		12-Jul-08		2:07:10		70.41		41		12-Jul-08		2:06:20		69.2		52.5		12-Jul-08		2:07:53		69.8		42.5

		12-Jul-08		4:07:10		69.8		40.5		12-Jul-08		4:06:20		69.2		52.5		12-Jul-08		4:07:53		69.2		42.5

		12-Jul-08		6:07:10		69.8		40.5		12-Jul-08		6:06:20		69.2		52.5		12-Jul-08		6:07:53		69.2		42.5

		12-Jul-08		8:07:10		70.41		41.5		12-Jul-08		8:06:20		69.2		55		12-Jul-08		8:07:53		69.2		43

		12-Jul-08		10:07:10		71		42.5		12-Jul-08		10:06:20		69.2		57.5		12-Jul-08		10:07:53		69.2		44.5

		12-Jul-08		12:07:10		71		45.5		12-Jul-08		12:06:20		68.61		53.5		12-Jul-08		12:07:53		69.8		46.5

		12-Jul-08		14:07:10		70.41		45.5		12-Jul-08		14:06:20		69.2		52.5		12-Jul-08		14:07:53		69.8		47.5

		12-Jul-08		16:07:10		70.41		45.5		12-Jul-08		16:06:20		69.2		63.5		12-Jul-08		16:07:53		69.8		47.5

		12-Jul-08		18:07:10		70.41		44.5		12-Jul-08		18:06:20		69.8		54		12-Jul-08		18:07:53		70.41		46.5

		12-Jul-08		20:07:10		71		42.5		12-Jul-08		20:06:20		70.41		54		12-Jul-08		20:07:53		70.41		45

		12-Jul-08		22:07:10		71		42.5		12-Jul-08		22:06:20		69.8		59.5		12-Jul-08		22:07:53		70.41		44.5

		13-Jul-08		0:07:10		71		42.5		13-Jul-08		0:06:20		69.8		60		13-Jul-08		0:07:53		69.8		44

		13-Jul-08		2:07:10		71		42.5		13-Jul-08		2:06:20		69.2		60.5		13-Jul-08		2:07:53		70.41		44.5

		13-Jul-08		4:07:10		71		42.5		13-Jul-08		4:06:20		69.2		60		13-Jul-08		4:07:53		70.41		44.5

		13-Jul-08		6:07:10		71		42.5		13-Jul-08		6:06:20		69.2		61		13-Jul-08		6:07:53		70.41		44.5

		13-Jul-08		8:07:10		71		42.5		13-Jul-08		8:06:20		68.61		59		13-Jul-08		8:07:53		69.8		44

		13-Jul-08		10:07:10		71		43		13-Jul-08		10:06:20		69.2		59.5		13-Jul-08		10:07:53		70.41		44.5

		13-Jul-08		12:07:10		71		45		13-Jul-08		12:06:20		69.2		59		13-Jul-08		12:07:53		69.8		46

		13-Jul-08		14:07:10		71		45		13-Jul-08		14:06:20		70.41		54		13-Jul-08		14:07:53		69.8		47

		13-Jul-08		16:07:10		71.6		44.5		13-Jul-08		16:06:20		69.8		55.5		13-Jul-08		16:07:53		69.8		47

		13-Jul-08		18:07:10		71.6		44		13-Jul-08		18:06:20		69.2		58.5		13-Jul-08		18:07:53		69.2		47

		13-Jul-08		20:07:10		71.6		43		13-Jul-08		20:06:20		69.2		57.5		13-Jul-08		20:07:53		69.8		46.5

		13-Jul-08		22:07:10		71		42.5		13-Jul-08		22:06:20		69.2		60.5		13-Jul-08		22:07:53		70.41		45.5

		14-Jul-08		0:07:10		71		42.5		14-Jul-08		0:06:20		69.2		58		14-Jul-08		0:07:53		70.41		44.5

		14-Jul-08		2:07:10		70.41		42		14-Jul-08		2:06:20		69.2		52		14-Jul-08		2:07:53		70.41		43.5

		14-Jul-08		4:07:10		70.41		42		14-Jul-08		4:06:20		69.2		57.5		14-Jul-08		4:07:53		69.8		43

		14-Jul-08		6:07:10		69.8		41		14-Jul-08		6:06:20		69.2		55.5		14-Jul-08		6:07:53		69.8		42.5

		14-Jul-08		8:07:10		69.8		42		14-Jul-08		8:06:20		69.2		56.5		14-Jul-08		8:07:53		69.8		43

		14-Jul-08		10:07:10		70.41		44		14-Jul-08		10:06:20		69.2		53.5		14-Jul-08		10:07:53		70.41		44.5

		14-Jul-08		12:07:10		70.41		47		14-Jul-08		12:06:20		69.8		62		14-Jul-08		12:07:53		70.41		47

		14-Jul-08		14:07:10		71		47		14-Jul-08		14:06:20		69.8		59.5		14-Jul-08		14:07:53		70.41		48

		14-Jul-08		16:07:10		71		47		14-Jul-08		16:06:20		69.8		60.5		14-Jul-08		16:07:53		70.41		48.5

		14-Jul-08		18:07:10		71		45		14-Jul-08		18:06:20		70.41		57		14-Jul-08		18:07:53		70.41		47

		14-Jul-08		20:07:10		71		43.5		14-Jul-08		20:06:20		69.8		59.5		14-Jul-08		20:07:53		70.41		46

		14-Jul-08		22:07:10		71		42.5		14-Jul-08		22:06:20		69.2		59.5		14-Jul-08		22:07:53		70.41		44.5

		15-Jul-08		0:07:10		70.41		42		15-Jul-08		0:06:20		69.2		57		15-Jul-08		0:07:53		70.41		43.5

		15-Jul-08		2:07:10		70.41		42		15-Jul-08		2:06:20		68.61		56		15-Jul-08		2:07:53		70.41		43.5

		15-Jul-08		4:07:10		69.8		41.5		15-Jul-08		4:06:20		68.61		59		15-Jul-08		4:07:53		69.8		43

		15-Jul-08		6:07:10		69.8		42		15-Jul-08		6:06:20		69.2		56.5		15-Jul-08		6:07:53		69.8		43

		15-Jul-08		8:07:10		70.41		42		15-Jul-08		8:06:20		68		53.5		15-Jul-08		8:07:53		69.8		43.5

		15-Jul-08		10:07:10		71		42		15-Jul-08		10:06:20		69.2		54.5		15-Jul-08		10:07:53		69.8		44

		15-Jul-08		12:07:10		71		44.5		15-Jul-08		12:06:20		69.2		60		15-Jul-08		12:07:53		69.8		45

		15-Jul-08		14:07:10		71		46.5		15-Jul-08		14:06:20		69.2		62		15-Jul-08		14:07:53		69.2		48.5

		15-Jul-08		16:07:10		70.41		45.5		15-Jul-08		16:06:20		69.2		57.5		15-Jul-08		16:07:53		69.8		47.5

		15-Jul-08		18:07:10		70.41		44.5		15-Jul-08		18:06:20		69.8		54.5		15-Jul-08		18:07:53		69.8		46

		15-Jul-08		20:07:10		71		42.5		15-Jul-08		20:06:20		70.41		53.5		15-Jul-08		20:07:53		69.8		44.5

		15-Jul-08		22:07:10		71		41.5		15-Jul-08		22:06:20		69.2		54.5		15-Jul-08		22:07:53		69.8		43.5

		16-Jul-08		0:07:10		70.41		41.5		16-Jul-08		0:06:20		69.2		57		16-Jul-08		0:07:53		69.2		43

		16-Jul-08		2:07:10		69.8		41.5		16-Jul-08		2:06:20		69.8		55.5		16-Jul-08		2:07:53		69.2		43.5

		16-Jul-08		4:07:10		69.8		41.5		16-Jul-08		4:06:20		68.61		56.5		16-Jul-08		4:07:53		69.2		43

		16-Jul-08		6:07:10		69.8		41		16-Jul-08		6:06:20		69.2		56		16-Jul-08		6:07:53		69.2		43

		16-Jul-08		8:07:10		70.41		41.5		16-Jul-08		8:06:20		68.61		58.5		16-Jul-08		8:07:53		69.2		43

		16-Jul-08		10:07:10		70.41		42		16-Jul-08		10:06:20		69.8		55		16-Jul-08		10:07:53		68.61		44.5

		16-Jul-08		12:07:10		71		42.5		16-Jul-08		12:06:20		69.8		51		16-Jul-08		12:07:53		69.2		44.5

		16-Jul-08		14:07:10		71		44.5		16-Jul-08		14:06:20		69.8		51		16-Jul-08		14:07:53		68.61		47.5

		16-Jul-08		16:07:10		71		45		16-Jul-08		16:06:20		70.41		57		16-Jul-08		16:07:53		68.61		48





		



CER 1 Temperature(°F)

CER 2 Temperature(°F)

CER 3 Temperature(°F)

Date

Temperature (Deg. F)

Figure 9.  CER Temperature



		



CER 1 Humidity(%)

CER 3 Humidity(%)

QA Humidity(%)

CER 2 Humidity(%)

Date

Humidity (%)

Figure 10.  CER Relative Humidity



		






_1294743912.xls
Chart4

		38831		38807		38807		38887		38837		38837

		38831		38807		38807		38887		38868		38868

		38832		38811		38811		38896		38898		38898

		38832		38811		38811		38896		38929		38929

		38833		38812		38812		38897		38960		38960

		38833		38812		38812		38897		38990		38990

		38834		38813		38813		38898		39021		39021

		38834		38813		38813		38898		39051		39051

		38835		38814		38814		38903		39082		39082

		38835		38814		38814		38903		39113		39113

		38836		38817		38817		38904		39110		39110

		38836		38817		38817		38904		39148		39148

		38838		38818		38818		38905		39148		39148

		38838		38818		38818		38905		39202		39202

		38839		38819		38819		38908		39218		39218

		38839		38819		38819		38908		39218		39218

		38840		38820		38820		38909		39233		39233

		38841		38820		38820		38909		39263		39263

		38842		38824		38824		38910		39294		39294

		38842		38824		38824		38910		39325		39325

		38843		38825		38825		38911		39330		39330

		38843		38825		38825		38911		39355		39355

		38844		38826		38826		38912		39386		39386

		38845		38826		38826		38912		39416		39416

		38845		38827		38827		38915		39447		39447

		38846		38827		38827		38915		39478		39478

		38846		38831		38828		38916		39507		39507

		38847		38831		38828		38916		39538		39538

		38847		38832		38832		38917		11414		11414

		38848		38832		38832		38917		39599		39599

		38848		38833		38833		38918		39629		39629

		38849		38833		38833		38918		39660		39660

		38849		38834		38834		38919		39690		39690

		38852		38834		38834		38919		39721		39721

		38852		38835		38835		38920

		38853		38835		38835		38920

		38853		38836		38923		38922

		38854		38836		38923		38922

		38854		38838		38924		38923

		38855		38838		38924		38923

		38855		38839		38925		38924

		38856		38839		38925		38924

		38856		38840		38926		38925

		38857		38841		38926		38925

		38857		38842		38927		38930

		38859		38842		38927		38930

		38859		38843		38928		38931

		38860		38843		38928		38931

		38860		38844		38929		38932

		38861		38845		38929		38932

		38861		38845		38930		38933

		38862		38846		38930		38933

		38862		38846		38931		38936

		38867		38847		38931		38936

		38867		38847		38932		38937

		38869		38848		38932		38937

		38869		38848		38933		38938

		38870		38849		38933		38938

		38873		38849		38936		38939

		38873		38852		38936		38939

		38874		38852		38937		38940

		38874		38853		38937		38940

		38875		38853		38939		38943

		38875		38854		38939		38943

		38876		38854		38943		38944

		38876		38855		38944		38944

		38877		38855		38945		38945

		38877		38856		38945		38945

		38880		38856		38946		38946

		38880		38857		38946		38946

		38881		38857		38947		38947

		38881		38859		38947		38947

		38884		38859		38950		38948

		38884		38860		38951		38948

		38904		38860		38951		38950

		38904		38861		38952		38950

		38905		38861		38952		38951

		38906		38862		38953		38951

		38908		38862		38953		38952

		38909		38867		38954		38952

		38910		38867		38954		38953

		38911		38869		38957		38953

		38915		38869		38957		38954

		38916		38870		38959		38954

		38917		38873		38959		38955

		38918		38873		38960		38955

		38919		38874		38960		38957

		38920		38874		38961		38957

		38921		38875		38961		38958

		38922		38875		38965		38958

		38923		38876		38965		38959

		38924		38876		38966		38959

		38924		38877		38966		38960

		38925		38877		38967		38960

		38925		38880		38967		38961

		38926		38880		38968		38966

		38929		38881		38968		38966

		38930		38881		38971		38967

		38931		38882		38971		38967

		38932		38882		38972		38968

		38933		38883		38972		38968

		38936		38883		38973		38971

		38937		38884		38973		38971

		38939		38884		38974		38972

		38939		38885		38974		38972

		38940		38885		38975		38973

		38940		38887		38975		38973

		38943		38887		38978		38974

		38944		38888		38978		38974

		38945		38888		38979		38975

		38945		38889		38979		38975

		38946		38889		38980		38978

		38946		38890		38980		38978

		38947		38890		38981		38979

		38947		38894		38981		38979

		38948		38895		38983		38980

		38948		38896		38983		38980

		38949		38897		38985		38981

		38950		38903		38985		38981

		38950		38904		38992		38982

		38951		38905		38992		38982

		38951		38906		38993		38983

		38952		38908		38993		38983

		38952		38909		38994		38985

		38953		38910		38996		38985

		38953		38911		38999		38986

		38954		38915		38999		38986

		38954		38916		39000		38987

		38955		38917		39000		38987

		38955		38918		39001		38988

		38957		38919		39001		38988

		38957		38920		39002		38989

		38958		38921		39002		38989

		38958		38922		39003		38992

		38959		38923		39003		38992

		38959		38924		39006		38993

		38960		38924		39006		38993

		38960		38925		39007		38994

		38961		38925		39007		38994

		38965		38926		39008		38995

		38965		38929		39008		38995

		38966		38930		39009		38999

		38967		38931		39009		38999

		38968		38932		39010		39000

		38971		38933		39010		39000

		38971		38936		39013		39001

		38972		38937		39013		39001

		38972		38940		39014		39002

		38973		38940		39014		39002

		38973		38943		39016		39003

		38974		38944		39016		39003

		38975		38945		39020		39004

		38978		38946		39020		39004

		38979		38946		39021		39006

		38979		38947		39021		39006

		38980		38947		39022		39007

		38980		38948		39022		39007

		38981		38948		39023		39008

		38981		38949		39023		39008

		38982		38950		39024		39009

		38982		38950		39024		39009

		38983		38951		39027		39010

		38983		38951		39027		39010

		38985		38952		39028		39013

		38985		38952		39028		39013

		38986		38953		39029		39014

		38986		38953		39029		39014

		38987		38954		39030		39015

		38987		38954		39030		39015

		38988		38955		39031		39016

		38988		38955		39031		39016

		38989		38957		39034		39017

		38989		38957		39034		39017

		38992		38958		39035		39018

		38993		38958		39035		39018

		38993		38959		39036		39020

		38994		38959		39036		39020

		38994		38960		39037		39021

		38995		38960		39038		39021

		38995		38961		39038		39022

		38996		38965		39041		39022

		38997		38965		39041		39023

		38997		38966		39042		39023

		38999		38967		39042		39024

		38999		38968		39043		39024

		39000		38971		39043		39027

		39000		38971		39048		39027

		39001		38972		39048		39028

		39001		38972		39049		39028

		39002		38973		39049		39029

		39002		38973		39050		39029

		39003		38974		39050		39030

		39003		38975		39051		39030

		39004		38978		39051		39031

		39004		38979		39052		39031

		39006		38979		39052		39034

		39006		38980		39055		39034

		39007		38980		39055		39035

		39007		38981		39056		39035

		39008		38981		39056		39036

		39008		38982		39057		39036

		39009		38982		39057		39037

		39009		38983		39058		39037

		39010		38983		39058		39038

		39010		38985		39059		39038

		39011		38985		39059		39039

		39011		38986		39062		39039

		39013		38986		39062		39041

		39013		38987		39063		39041

		39014		38987		39063		39042

		39014		38988		39064		39042

		39015		38988		39064		39043

		39015		38989		39065		39043

		39016		38989		39069		39048

		39016		38992		39069		39048

		39017		38993		39070		39049

		39017		38993		39070		39049

		39018		38994		39071		39050

		39018		38994		39071		39050

		39020		38995		39072		39051

		39020		38995		39072		39051

		39021		38996		39073		39052

		39022		38997		39078		39052

		39023		38997		39079		39053

		39023		38999		39079		39053

		39024		38999		39080		39055

		39027		39000		39080		39055

		39028		39000		39084		39056

		39029		39001		39084		39056

		39030		39001		39085		39057

		39031		39002		39085		39057

		39032		39002		39086		39058

		39034		39003		39086		39058

		39034		39003		39087		39059

		39035		39004		39087		39059

		39035		39004		39090		39060

		39036		39006		39090		39060

		39036		39006		39091		39062

		39037		39007		39091		39062

		39038		39007		39092		39063

		39038		39008		39092		39063

		39039		39008		39093		39064

		39039		39009		39093		39064

		39041		39009		39094		39065

		39042		39010		39094		39065

		39043		39010		39097		39066

		39043		39011		39097		39066

		39048		39011		39098		39141

		39048		39013		39098		39141

		39049		39013		39099		39142

		39050		39014		39099		39143

		39051		39014		39100		39144

		39052		39015		39100		39146

		39053		39015		39101		39147

		39055		39016		39101		39148

		39056		39016		39104		39149

		39057		39017		39104		39150

		39057		39017		39105		39153

		39058		39018		39105		39154

		39058		39018		39106		39155

		39059		39020		39106		39156

		39059		39020		39107		39157

		39060		39021		39107		39158

		39062		39022		39108		39160

		39062		39023		39108		39161

		39063		39023		39111		39162

		39063		39024		39111		39163

		39064		39027		39112		39164

		39064		39028		39112		39167

		39065		39029		39113		39168

		39065		39030		39113		39169

		39066		39031		39114		39170

		39066		39032		39114		39171

		39069		39034		39115		39172

		39069		39034		39115		39174

		39070		39035		39118		39175

		39070		39035		39118		39176

		39071		39036		39119		39177

		39072		39036		39119		39178

		39072		39037		39120		39181

		39073		39038		39120		39182

		39073		39038		39121		39183

		39078		39039		39121		39184

		39078		39039		39122		39185

		39079		39041		39122		39188

		39079		39042		39125		39189

		39080		39043		39125		39190

		39080		39043		39126		39191

		39084		39048		39126		39192

		39084		39048		39127		39195

		39085		39049		39127		39196

		39085		39050		39128		39197

		39086		39051		39129		39198

		39087		39052		39133		39199

		39087		39053		39133		39200

		39090		39055		39134		39202

		39090		39056		39134		39203

		39091		39057		39135		39204

		39091		39057		39135		39205

		39092		39058		39136		39206

		39092		39058		39136		39207

		39093		39059		39139		39209

		39093		39059		39139		39210

		39094		39060		39140		39211

		39095		39062		39140		39212

		39095		39062		39141		39213

		39097		39063		39142		39216

		39097		39063		39143		39217

		39098		39064		39146		39218

		39098		39064		39147		39219

		39099		39065		39148		39220

		39100		39065		39149		39221

		39101		39066		39150		39223

		39101		39066		39153		39224

		39102		39069		39154		39225

		39104		39069		39155		39226

		39105		39070		39156		39231

		39106		39070		39157		39232

		39106		39071		39160		39233

		39107		39072		39161		39234

		39107		39072		39162		39235

		39108		39073		39163		39237

		39108		39073		39164		39238

		39111		39078		39167		39239

		39111		39078		39168		39240

		39112		39079		39169		39241

		39112		39079		39170		39242

		39113		39080		39171		39244

		39113		39080		39174		39245

		39114		39084		39175		39246

		39114		39084		39176		39247

		39115		39085		39177		39248

		39115		39085		39178		39249

		39116		39086		39181		39252

		39116		39087		39182		39253

		39118		39087		39183		39254

		39118		39090		39184		39255

		39119		39090		39185		39256

		39119		39091		39188		39258

		39120		39091		39189		39259

		39120		39092		39190		39260

		39121		39092		39191		39261

		39121		39093		39195		39262

		39123		39093		39196		39265

		39123		39094		39197		39266

		39125		39095		39198		39268

		39126		39095		39199		39269

		39126		39097		39202		39272

		39127		39097		39203		39273

		39127		39098		39204		39274

		39128		39098		39205		39275

		39128		39099		39206		39276

		39129		39100		39209		39277

		39129		39101		39210		39279

		39133		39101		39211		39280

		39133		39102		39212		39281

		39134		39104		39213		39282

		39134		39105		39216		39283

		39135		39106		39217		39286

		39135		39106		39218		39287

		39136		39107		39219		39288

		39136		39107		39220		39289

		39139		39108		39223		39290

		39139		39108		39224		39291

		39140		39111		39225		39293

		39140		39111		39226		39294

		39141		39112		39226		39295

		39141		39112		39231		39296

		39142		39113		39232		39297

		39143		39113		39233		39300

		39146		39114		39234		39301

		39147		39114		39237		39302

		39148		39115		39238		39303

		39149		39115		39239		39304

		39150		39116		39240		39305

		39153		39116		39241		39307

		39154		39118		39242		39308

		39155		39118		39244		39309

		39156		39119		39245		39310

		39157		39119		39246		39311

		39160		39120		39247		39314

		39161		39120		39248		39315

		39162		39121		39251		39316

		39163		39121		39252		39317

		39164		39123		39253		39318

		39167		39123		39254		39321

		39168		39125		39258		39322

		39169		39126		39259		39323

		39170		39126		39260		39324

		39171		39127		39261		39325

		39172		39127		39262		39329

		39174		39128		39265		39330

		39175		39128		39266		39331

		39176		39129		39268		39332

		39177		39129		39269		39335

		39178		39133		39272		39336

		39181		39133		39273		39337

		39182		39134		39274		39338

		39183		39134		39275		39339

		39184		39135		39276		39342

		39185		39135		39279		39343

		39186		39136		39280		39344

		39188		39136		39281		39345

		39189		39139		39282		39346

		39190		39139		39283		39347

		39191		39140		39286		39349

		39192		39140		39287		39350

		39193		39141		39288		39351

		39195		39142		39289		39352

		39196		39143		39291		39353

		39197		39146		39293		39356

		39198		39147		39294		39357

		39199		39148		39295		39358

		39202		39149		39296		39359

		39203		39150		39297		39360

		39204		39153		39298		39363

		39205		39154		39300		39364

		39206		39155		39301		39365

		39207		39156		39302		39366

		39209		39157		39303		39367

		39210		39160		39304		39370

		39211		39161		39307		39371

		39212		39162		39308		39372

		39213		39163		39309		39373

		39216		39164		39310		39374

		39217		39167		39311		39377

		39218		39168		39314		39378

		39219		39169		39315		39379

		39220		39170		39316		39380

		39221		39171		39317		39381

		39223		39172		39318		39384

		39224		39174		39321		39385

		39225		39175		39322		39386

		39226		39176		39323		39387

		39227		39177		39324		39388

		39231		39178		39325		39391

		39232		39181		39329		39392

		39233		39182		39330		39393

		39234		39183		39331		39394

		39235		39184		39332		39395

		39237		39185		39333		39398

		39238		39186		39335		39399

		39239		39188		39336		39400

		39240		39189		39337		39401

		39241		39190		39338		39402

		39242		39191		39339		39405

		39244		39192		39340		39406

		39245		39193		39342		39407

		39246		39195		39343		39412

		39247		39196		39344		39413

		39248		39197		39345		39414

		39251		39198		39346		39415

		39252		39199		39349		39416

		39253		39202		39350		39417

		39254		39203		39351		39419

		39255		39204		39352		39420

		39258		39205		39353		39421

		39259		39206		39356		39422

		39260		39207		39357		39423

		39261		39209		39358		39424

		39262		39210		39359		39426

		39265		39211		39360		39427

		39266		39212		39363		39428

		39268		39213		39364		39429

		39269		39216		39365		39430

		39272		39217		39366		39433

		39273		39218		39367		39434

		39274		39219		39368		39435

		39275		39220		39370		39436

		39276		39221		39371		39442

		39279		39223		39372		39443

		39280		39224		39373		39444

		39281		39225		39374		39447

		39282		39226		39377		39449

		39283		39227		39378		39450

		39286		39231		39379		39451

		39287		39232		39380		39454

		39288		39233		39381		39455

		39289		39234		39384		39456

		39290		39235		39385		39457

		39293		39237		39386		39458

		39294		39238		39387		39461

		39295		39239		39388		39462

		39296		39240		39391		39463

		39297		39241		39392		39464

		39298		39242		39393		39465

		39300		39244		39394		39468

		39301		39245		39395		39469

		39302		39246		39398		39470

		39303		39247		39399		39471

		39304		39248		39400		39472

		39307		39251		39401		39475

		39308		39252		39402		39476

		39309		39253		39405		39477

		39311		39254		39406		39478

		39314		39255		39407		39479

		39315		39258		39412		39482

		39316		39259		39413		39483

		39317		39260		39414		39484

		39318		39261		39415		39485

		39319		39262		39416		39486

		39321		39265		39419		39489

		39322		39266		39420		39490

		39323		39268		39421		39491

		39324		39269		39422		39492

		39325		39272		39423		39493

		39329		39273		39426		39494

		39330		39274		39427		39497

		39331		39275		39428		39498

		39332		39276		39429		39499

		39333		39279		39430		39500

		39335		39280		39433		39503

		39336		39281		39434		39504

		39337		39282		39435		39505

		39338		39283		39436		39506

		39339		39286		39437		39507

		39342		39287		39442		39508

		39343		39288		39443		39509

		39344		39289		39444		39510

		39345		39290		39447		39511

		39346		39293				39512

		39349		39294		39492		39513

		39350		39295		39493		39514

		39351		39296		39497		39515

		39352		39297		39498		39517

		39353		39298		39499		39518

		39354		39300		39500		39519

		39356		39301		39503		39520

		39357		39302		39504		39521

		39358		39303		39505		39522

		39359		39304		39506		39524

		39360		39307		39507		39525

		39363		39308		39510		39526

		39364		39309		39511		39527

		39365		39311		39512		39528

		39366		39314		39513		39529

		39367		39315		39514		39531

		39370		39316		39517		39532

		39371		39317		39518		39533

		39372		39318		39519		39534

		39373		39319		39521		39535

		39374		39321		39524		39538

		39377		39322		39525		39539

		39378		39323		39526		39540

		39379		39324		39527		39541

		39380		39325		39528		39542

		39381		39329		39531		39543

		39384		39330		39532		39545

		39385		39331		39533		39546

		39386		39332		39534		39547

		39387		39333		39535		39548

		39388		39335		39538		39549

		39391		39336		39539		39552

		39392		39337		39540		39553

		39393		39338		39541		39554

		39394		39339		39542		39555

		39395		39342		39543		39556

		39398		39343		39545		39557

		39399		39344		39546		39559

		39400		39345		39547		39560

		39401		39346		39548		39561

		39402		39349		39549		39562

		39405		39350		39552		39563

		39406		39351		39553		39568

		39407		39352		39554		39569

		39412		39353		39555		39570

		39413		39354		39556		39571

		39414		39356		39557		39573

		39415		39357		39559		39574

		39416		39358		39560		39575

		39419		39359		39561		39576

		39420		39360		39562		39577

		39421		39363		39563		39578

		39422		39364		39566		39580

		39423		39365		39567		39581

		39426		39366		39568		39582

		39427		39367		39569		39583

		39428		39370		39570		39584

		39429		39371		39571		39587

		39430		39372		39573		39588

		39433		39373		39574		39589

		39434		39374		39575		39590

		39435		39377		39576		39591

		39436		39378		39577		39595

		39437		39379		39578		39596

		39442		39380		39580		39597

		39443		39381		39581		39598

		39444		39384		39582		39599

		39447		39385		39583		39601

		39449		39386		39584		39602

		39450		39387		39587		39603

		39451		39388		39588		39604

		39454		39391		39589		39605

		39455		39392		39590		39608

		39456		39393		39591		39609

		39457		39394		39595		39610

		39458		39395		39596		39611

		39461		39398		39597		39612

		39462		39399		39598		39615

		39463		39400		39601		39616

		39464		39401		39602		39617

		39465		39402		39603		39618

		39468		39405		39604		39619

		39469		39406		39605		39620

		39470		39407		39608		39622

		39471		39412		39609		39623

		39472		39413		39610		39624

		39475		39414		39611		39625

		39476		39415		39612		39626

		39477		39416		39615		39629

		39478		39419		39616		39630

		39479		39420		39617		39631

		39482		39421		39618		39632

		39483		39422		39619		39636

		39484		39423		39620		39637

		39485		39426		39622		39638

		39486		39427		39623		39639

		39487		39428		39624		39640

		39489		39429		39625		39641

		39490		39430		39626		39643

		39491		39433		39629		39644

		39492		39434		39630		39645

		39493		39435		39631		39646

		39497		39436		39632		39647

		39498		39437		39636		39648

		39499		39442		39637		39650

		39500		39443		39638		39651

		39501		39444		39639		39652

		39502		39447		39640		39653

		39503		39449		39641		39654

		39504		39450		39643		39655

		39505		39451		39644		39657

		39506		39454		39645		39658

		39507		39455		39646		39659

		39508		39456		39647		39660

		39510		39457		39648		39661

		39511		39458		39650		39662

		39512		39461		39651		39664

		39513		39462		39652		39665

		39514		39463		39653		39666

		39517		39464		39654		39667

		39518		39465		39655		39668

		39519		39468		39657		39669

		39520		39469		39658		39671

		39521		39470		39659		39672

		39524		39471		39660		39673

		39525		39472		39661		39674

		39526		39475		39662		39675

		39527		39476		39664		39676

		39528		39477		39665		39678

		39529		39478		39666		39679

		39531		39479		39667		39680

		39532		39482		39668		39681

		39533		39483		39669		39682

		39534		39484		39671		39683

		39535		39485		39672		39685

		39538		39486		39673		39686

		39539		39487		39674		39687

		39540		39492		39675		39688

		39541		39493		39676		39689

		39542		39497		39678		39693

		39543		39498		39679		39694

		39545		39499		39680		39695

		39546		39500		39681		39696

		39547		39503		39682		39697

		39548		39504		39683		39699

		39549		39505		39685		39700

		39552		39506		39686		39701

		39553		39507		39687		39702

		39554		39510		39688		39703

		39555		39511		39689		39704

		39556		39512		39693		39706

		39557		39513		39694		39707

		39559		39514		39695		39708

		39560		39517		39696		39709

		39561		39518		39697		39710

		39562		39519		39699		39711

		39563		39521		39700		39713

		39568		39524		39701		39714

		39569		39525		39702		39715

		39570		39526		39703		39716

		39571		39527		39704		39717

		39573		39528		39706		39718

		39574		39531		39707		39720

		39575		39532		39708		39721

		39576		39533		39709

		39577		39534		39710

		39578		39535		39711

		39580		39538		39713

		39581		39539		39714

		39582		39540		39715

		39583		39541		39716

		39584		39542		39717

		39587		39543		39718

		39588		39545		39720

		39589		39546		39721

		39590		39547

		39591		39548

		39595		39549

		39596		39552

		39597		39553

		39598		39554

		39599		39555

		39601		39556

		39602		39557

		39603		39559

		39604		39560

		39605		39561

		39608		39562

		39609		39563

		39610		39568

		39611		39569

		39612		39570

		39615		39571

		39616		39573

		39617		39574

		39618		39575

		39619		39576

		39620		39577

		39622		39578

		39623		39580

		39624		39581

		39625		39582

		39626		39583

		39629		39584

		39630		39587

		39631		39588

		39632		39589

		39636		39590

		39637		39591

		39638		39595

		39639		39596

		39640		39597

		39641		39598

		39643		39601

		39644		39602

		39645		39603

		39646		39604

		39647		39605

		39648		39608

		39650		39609

		39651		39610

		39652		39611

		39653		39612

		39654		39615

		39655		39616

		39657		39617

		39658		39618

		39659		39619

		39660		39620

		39661		39622

		39662		39623

		39664		39624

		39665		39625

		39666		39626

		39667		39629

		39668		39630

		39669		39631

		39671		39632

		39672		39636

		39673		39637

		39674		39638

		39675		39639

		39676		39640

		39678		39641

		39679		39643

		39680		39644

		39681		39645

		39682		39646

		39683		39647

		39685		39648

		39686		39650

		39687		39651

		39688		39652

		39689		39653

		39693		39654

		39694		39655

		39695		39657

		39696		39658

		39697		39659

		39699		39660

		39700		39661

		39701		39662

		39702		39664

		39703		39665

		39704		39666

		39706		39667

		39707		39668

		39708		39669

		39709		39671

		39710		39672

		39711		39673

		39713		39674

		39714		39675

		39715		39676

		39716		39678

		39717		39679

		39718		39680

		39720		39681

		39721		39682

				39683

				39685

				39686

				39687

				39688

				39689

				39693

				39694

				39695

				39696

				39697

				39699

				39700

				39701

				39702

				39703

				39704

				39706

				39707

				39708

				39709

				39710

				39711

				39713

				39714

				39715

				39716

				39717

				39718

				39720

				39721



CER1

CER Change Room

CER2

CER3

CER Alert Level

CER Action Level

Date

Diff. Pressure (Water Column In.)

Figure 5.  CER Differential Pressure Daily Run Chart

0.05

0.05

0.09

0.05

0.05

0.03

0.05

0.06

0.09

0.06

0.05

0.03

0.05

0.05

0.09

0.03

0.05

0.03

0.04

0.05

0.09

0.06

0.05

0.03

0.06

0.05

0.09

0.03

0.05

0.03

0.04

0.06

0.09

0.06

0.05

0.03

0.04

0.05

0.09

0.06

0.05

0.03

0.045

0.06

0.09

0.06

0.05

0.03

0.05

0.055

0.09

0.03

0.05

0.03

0.04

0.05

0.09

0.03

0.05

0.03

0.035

0.055

0.095

0.06

0.05

0.03

0.035

0.055

0.09

0.06

0.05

0.03

0.025

0.055

0.095

0.06

0.03

0.005

0.03

0.055

0.095

0.06

0.03

0.005

0.025

0.055

0.09

0.06

0.03

0.005

0.03

0.055

0.09

0.06

0.015

0.005

0.015

0.055

0.09

0.06

0.015

0.005

0.03

0.055

0.095

0.06

0.015

0.005

0.03

0.06

0.095

0.06

0.015

0.005

0.03

0.055

0.09

0.06

0.015

0.005

0.03

0.055

0.095

0.06

0.015

0.005

0.025

0.06

0.09

0.06

0.015

0.005

0.03

0.045

0.085

0.06

0.015

0.005

0.03

0.05

0.09

0.06

0.015

0.005

0.03

0.055

0.079

0.06

0.015

0.005

0.025

0.05

0.08

0.06

0.015

0.005

0.025

0.06

0.085

0.06

0.015

0.005

0.025

0.06

0.085

0.06

0.015

0.005

0.025

0.06

0.086

0.06

0.015

0.005

0.015

0.06

0.085

0.06

0.015

0.005

0.025

0.05

0.085

0.07

0.015

0.005

0.025

0.02

0.087

0.07

0.015

0.005

0.02

0.06

0.085

0.07

0.015

0.005

0.02

0.055

0.085

0.07

0.015

0.005

0.025

0.04

0.09

0.07

0.01

0.055

0.08

0.07

0.01

0.05

0.085

0.07

0.01

0.05

0.085

0.07

0.025

0.05

0.085

0.06

0.02

0.055

0.075

0.06

0.02

0.05

0.08

0.06

0.03

0.055

0.08

0.06

0.02

0.05

0.075

0.06

0.01

0.045

0.079

0.06

0.02

0.055

0.069

0.06

0.015

0.05

0.07

0.06

0.015

0.065

0.069

0.06

0.015

0.055

0.069

0.06

0.015

0.05

0.075

0.06

0.015

0.05

0.073

0.06

0.015

0.05

0.07

0.06

0.015

0.05

0.075

0.06

0.03

0.055

0.07

0.055

0.015

0.045

0.07

0.06

0.02

0.04

0.07

0.06

0.01

0.045

0.074

0.06

0.01

0.055

0.074

0.06

0.015

0.05

0.074

0.06

0.01

0.06

0.073

0.055

0.013

0.045

0.073

0.055

0.01

0.055

0.073

0.055

0.01

0.05

0.073

0.055

0.01

0.055

0.074

0.055

0.01

0.04

0.071

0.055

0.01

0.045

0.07

0.055

0.01

0.05

0.069

0.055

0.01

0.055

0.069

0.055

0.01

0.04

0.07

0.055

0.03

0.045

0.069

0.055

0.01

0.04

0.069

0.06

0.03

0.043

0.07

0.05

0.01

0.05

0.068

0.065

0.01

0.05

0.065

0.05

0.01

0.05

0.06

0.055

0.05

0.05

0.065

0.055

0.04

0.045

0.065

0.05

0.04

0.05

0.068

0.05

0.04

0.05

0.065

0.056

0.05

0.05

0.055

0.055

0.04

0.045

0.065

0.055

0.05

0.05

0.065

0.05

0.05

0.045

0.065

0.05

0.06

0.05

0.065

0.05

0.04

0.04

0.065

0.055

0.04

0.05

0.063

0.05

0.04

0.055

0.065

0.05

0.033

0.055

0.065

0.05

0.04

0.05

0.06

0.05

0.04

0.055

0.065

0.05

0.04

0.05

0.065

0.05

0.04

0.05

0.065

0.05

0.035

0.05

0.055

0.05

0.04

0.045

0.065

0.05

0.03

0.05

0.055

0.05

0.04

0.01

0.063

0.055

0.04

0.05

0.06

0.05

0.03

0.01

0.063

0.05

0.035

0.05

0.06

0.05

0.03

0.05

0.065

0.05

0.03

0.055

0.06

0.05

0.03

0.055

0.065

0.05

0.03

0.06

0.06

0.05

0.03

0.05

0.065

0.05

0.03

0.04

0.06

0.05

0.05

0.045

0.065

0.06

0.03

0.05

0.06

0.05

0.05

0.05

0.065

0.055

0.03

0.05

0.06

0.05

0.03

0.05

0.063

0.04

0.05

0.05

0.065

0.05

0.03

0.04

0.055

0.05

0.035

0.05

0.065

0.055

0.03

0.04

0.06

0.06

0.03

0.045

0.065

0.05

0.03

0.04

0.062

0.055

0.035

0.04

0.065

0.05

0.03

0.04

0.062

0.05

0.035

0.04

0.059

0.055

0.03

0.04

0.06

0.055

0.03

0.04

0.06

0.05

0.025

0.05

0.05

0.055

0.035

0.05

0.048

0.06

0.035

0.03

0.042

0.06

0.035

0.05

0.048

0.05

0.035

0.04

0.038

0.055

0.035

0.0425

0.055

0.05

0.035

0.04

0.036

0.05

0.035

0.05

0.037

0.05

0.03

0.05

0.032

0.05

0.035

0.05

0.032

0.05

0.03

0.055

0.032

0.05

0.03

0.055

0.033

0.05

0.03

0.055

0.03

0.05

0.03

0.055

0.031

0.055

0.03

0.05

0.03

0.06

0.035

0.055

0.033

0.05

0.03

0.05

0.032

0.05

0.03

0.05

0.032

0.055

0.03

0.05

0.03

0.05

0.03

0.05

0.033

0.05

0.03

0.05

0.03

0.05

0.02

0.05

0.025

0.05

0.02

0.05

0.03

0.05

0.03

0.05

0.03

0.05

0.03

0.05

0.035

0.05

0.03

0.05

0.032

0.05

0.03

0.05

0.026

0.05

0.03

0.03

0.029

0.05

0.025

0.05

0.029

0.05

0.03

0.05

0.03

0.05

0.03

0.035

0.03

0.05

0.03

0.05

0.025

0.05

0.03

0.05

0.023

0.05

0.03

0.05

0.025

0.05

0.03

0.05

0.015

0.05

0.03

0.05

0.026

0.05

0.03

0.05

0.022

0.05

0.02

0.05

0.025

0.05

0.02

0.05

0.015

0.05

0.02

0.05

0.025

0.05

0.02

0.05

0.015

0.05

0.02

0.045

0.025

0.05

0.03

0.05

0.023

0.05

0.02

0.05

0.02

0.05

0.02

0.055

0.018

0.055

0.02

0.05

0.04

0.05

0.02

0.055

0.018

0.05

0.02

0.05

0.02

0.05

0.05

0.055

0.019

0.05

0.03

0.05

0.02

0.05

0.03

0.05

0.015

0.05

0.02

0.05

0.02

0.05

0.03

0.055

0.02

0.05

0.04

0.05

0.02

0.05

0.03

0.05

0.02

0.05

0.03

0.05

0.02

0.05

0.03

0.05

0.02

0.05

0.03

0.05

0.02

0.05

0.04

0.055

0.02

0.05

0.03

0.05

0.018

0.05

0.02

0.045

0.02

0.05

0.05

0.05

0.015

0.05

0.05

0.045

0.02

0.055

0.04

0.05

0.012

0.045

0.04

0.05

0.02

0.05

0.02

0.05

0.02

0.05

0.02

0.05

0.02

0.05

0.03

0.05

0.04

0.05

0.04

0.05

0.02

0.055

0.035

0.05

0.01

0.05

0.035

0.05

0.02

0.06

0.04

0.05

0.015

0.05

0.04

0.05

0.02

0.05

0.04

0.05

0.015

0.05

0.035

0.05

0.01

0.05

0.04

0.05

0.012

0.05

0.035

0.05

0.01

0.06

0.03

0.05

0.015

0.06

0.04

0.05

0.01

0.05

0.03

0.05

0.015

0.055

0.03

0.05

0.01

0.05

0.025

0.05

0.01

0.055

0.02

0.05

0.02

0.055

0.035

0.05

0.01

0.05

0.05

0.05

0.01

0.055

0.04

0.05

0.01

0.05

0.03

0.05

0.01

0.065

0.035

0.05

0.015

0.05

0.04

0.05

0.01

0.06

0.02

0.02

0.015

0.05

0.02

0.03

0.01

0.06

0.035

0.03

0.015

0.05

0.035

0.05

0.02

0.05

0.025

0.05

0.01

0.05

0.045

0.04

0.01

0.05

0.03

0.05

0.01

0.055

0.03

0.05

0.009

0.06

0.03

0.05

0.01

0.05

0.025

0.05

0.01

0.055

0.035

0.04

0.01

0.05

0.035

0.04

0.008

0.05

0.03

0.03

0.01

0.05

0.025

0.03

0.03

0.065

0.035

0.03

0.01

0.05

0.03

0.03

0.01

0.065

0.02

0.03

0.01

0.045

0.015

0.05

0.01

0.05

0.02

0.05

0.01

0.045

0.025

0.03

0.01

0.05

0.03

0.04

0.01

0.05

0.025

0.035

0.01

0.05

0.035

0.035

0.01

0.05

0.035

0.03

0.01

0.05

0.02

0.04

0.01

0.05

0.02

0.03

0.01

0.05

0.02

0.035

0.01

0.05

0.03

0.04

0.01

0.05

0.035

0.04

0.01

0.05

0.035

0.04

0.01

0.05

0.03

0.04

0.01

0.05

0.035

0.04

0.01

0.05

0.03

0.04

0.02

0.055

0.03

0.04

0.01

0.055

0.045

0.04

0.01

0.04

0.035

0.04

0.01

0.05

0.025

0.04

0.02

0.05

0.035

0.03

0.01

0.05

0.03

0.04

0.01

0.04

0.035

0.035

0.015

0.04

0.015

0.04

0.01

0.04

0.015

0.035

0.01

0.04

0.025

0.035

0.01

0.04

0.025

0.03

0.01

0.04

0.025

0.045

0.01

0.04

0.025

0.045

0.01

0.04

0.03

0.04

0.01

0.04

0.03

0.035

0.02

0.04

0.03

0.03

0.01

0.045

0.03

0.03

0.01

0.04

0.035

0.05

0.01

0.04

0.03

0.035

0.005

0.03

0.03

0.035

0.01

0.04

0.03

0.035

0.01

0.04

0.03

0.035

0.01

0.03

0.03

0.035

0.01

0.04

0.03

0.04

0.01

0.04

0.035

0.035

0.01

0.03

0.03

0.05

0.01

0.03

0.03

0.035

0.01

0.04

0.03

0.04

0.01

0.03

0.03

0.035

0.01

0.04

0.03

0.045

0.01

0.03

0.03

0.04

0.005

0.04

0.03

0.04

0.01

0.03

0.03

0.05

0.005

0.03

0.03

0.04

0.01

0.045

0.03

0.04

0.005

0.04

0.03

0.03

0.01

0.04

0.03

0.03

0.005

0.04

0.03

0.03

0.01

0.04

0.02

0.03

0.005

0.03

0.035

0.035

0.01

0.04

0.03

0.03

0.015

0.04

0.03

0.03

0.01

0.035

0.03

0.015

0.018

0.035

0.03

0.03

0.01

0.04

0.03

0.035

0.012

0.035

0.035

0.035

0.01

0.04

0.03

0.035

0.02

0.04

0.03

0.03

0.02

0.03

0.03

0.035

0.015

0.04

0.03

0.035

0.02

0.035

0.03

0.035

0.01

0.035

0.03

0.03

0.015

0.035

0.03

0.03

0.015

0.045

0.03

0.03

0.02

0.04

0.03

0.03

0.015

0.04

0.03

0.03

0.02

0.04

0.03

0.035

0.018

0.04

0.03

0.03

0.02

0.04

0.03

0.03

0.016

0.04

0.03

0.03

0.015

0.035

0.03

0.035

0.014

0.04

0.03

0.03

0.015

0.045

0.03

0.03

0.014

0.04

0.03

0.03

0.01

0.035

0.03

0.03

0.015

0.03

0.03

0.03

0.015

0.035

0.03

0.03

0.01

0.045

0.025

0.03

0.01

0.035

0.02

0.03

0.04

0.04

0.02

0.035

0.04

0.04

0.03

0.03

0.04

0.04

0.03

0.035

0.04

0.04

0.03

0.03

0.04

0.045

0.03

0.03

0.04

0.04

0.03

0.03

0.035

0.03

0.03

0.03

0.04

0.03

0.03

0.03

0.035

0.035

0.03

0.03

0.035

0.035

0.03

0.035

0.035

0.05

0.03

0.03

0.032

0.035

0.035

0.03

0.03

0.04

0.03

0.03

0.03

0.04

0.035

0.03

0.03

0.04

0.035

0.03

0.035

0.045

0.035

0.035

0.035

0.04

0.03

0.03

0.03

0.04

0.035

0.035

0.03

0.04

0.03

0.03

0.025

0.04

0.03

0.03

0.03

0.035

0.03

0.03

0.025

0.045

0.03

0.03

0.03

0.05

0.03

0.03

0.025

0.04

0.035

0.03

0.03

0.04

0.03

0.03

0.03

0.035

0.03

0.03

0.03

0.04

0.03

0.03

0.028

0.04

0.03

0.03

0.032

0.04

0.05

0.03

0.03

0.04

0.04

0.03

0.025

0.04

0.04

0.035

0.025

0.04

0.03

0.03

0.04

0.04

0.03

0.03

0.044

0.04

0.05

0.03

0.049

0.045

0.03

0.03

0.049

0.05

0.035

0.03

0.045

0.05

0.04

0.03

0.045

0.045

0.04

0.03

0.042

0.07

0.04

0.03

0.045

0.045

0.05

0.03

0.042

0.055

0.04

0.03

0.045

0.05

0.04

0.03

0.045

0.05

0.04

0.035

0.045

0.055

0.05

0.03

0.045

0.05

0.05

0.03

0.045

0.075

0.04

0.03

0.045

0.07

0.055

0.03

0.046

0.07

0.04

0.03

0.05

0.07

0.05

0.03

0.055

0.07

0.03

0.03

0.045

0.065

0.05

0.03

0.04

0.055

0.05

0.03

0.044

0.06

0.04

0.035

0.045

0.065

0.03

0.035

0.045

0.05

0.04

0.035

0.04

0.06

0.03

0.03

0.04

0.06

0.03

0.03

0.025

0.06

0.04

0.03

0.045

0.06

0.04

0.035

0.05

0.06

0.04

0.035

0.051

0.06

0.04

0.03

0.044

0.05

0.04

0.03

0.047

0.05

0.04

0.03

0.046

0.05

0.04

0.03

0.05

0.05

0.04

0.03

0.048

0.06

0.03

0.03

0.049

0.05

0.03

0.03

0.049

0.05

0.04

0.03

0.05

0.055

0.04

0.035

0.045

0.055

0.03

0.03

0.048

0.05

0.04

0.03

0.045

0.05

0.035

0.03

0.045

0.05

0.04

0.03

0.045

0.05

0.04

0.03

0.045

0.05

0.035

0.04

0.045

0.05

0.04

0.03

0.042

0.05

0.035

0.035

0.045

0.05

0.035

0.05

0.04

0.05

0.03

0.04

0.063

0.05

0.035

0.04

0.061

0.05

0.04

0.05

0.06

0.05

0.035

0.04

0.062

0.05

0.035

0.04

0.06

0.055

0.035

0.04

0.058

0.045

0.035

0.05

0.06

0.05

0.035

0.05

0.06

0.05

0.03

0.04

0.055

0.045

0.03

0.035

0.056

0.05

0.03

0.04

0.056

0.05

0.03

0.04

0.055

0.045

0.03

0.03

0.05

0.05

0.03

0.04

0.045

0.05

0.03

0.03

0.045

0.05

0.025

0.035

0.04

0.05

0.03

0.03

0.04

0.05

0.035

0.03

0.04

0.05

0.035

0.03

0.04

0.05

0.025

0.03

0.04

0.05

0.02

0.03

0.04

0.05

0.03

0.03

0.044

0.05

0.04

0.03

0.044

0.06

0.025

0.04

0.04

0.05

0.025

0.04

0.04

0.05

0.03

0.04

0.04

0.045

0.02

0.04

0.042

0.05

0.02

0.04

0.04

0.05

0.02

0.03

0.04

0.05

0.02

0.035

0.034

0.05

0.02

0.035

0.032

0.05

0.025

0.035

0.043

0.05

0.03

0.04

0.045

0.045

0.025

0.04

0.045

0.05

0.005

0.04

0.043

0.05

0.035

0.035

0.04

0.045

0.035

0.035

0.04

0.05

0.03

0.04

0.04

0.05

0.03

0.04

0.03

0.045

0.03

0.035

0.04

0.045

0.03

0.03

0.04

0.05

0.025

0.035

0.04

0.05

0.025

0.035

0.045

0.045

0.025

0.035

0.04

0.05

0.02

0.04

0.055

0.045

0.025

0.04

0.055

0.05

0.025

0.04

0.05

0.05

0.048

0.035

0.05

0.045

0.04

0.035

0.04

0.05

0.025

0.04

0.05

0.05

0.03

0.035

0.045

0.05

0.03

0.035

0.04

0.045

0.0175

0.03

0.055

0.05

0.03

0.035

0.05

0.045

0.04

0.035

0.05

0.045

0.025

0.04

0.05

0.045

0.02

0.035

0.05

0.045

0.04

0.04

0.05

0.045

0.02

0.035

0.054

0.045

0.03

0.035

0.054

0.045

0.025

0.02

0.045

0.045

0.02

0.04

0.045

0.045

0.025

0.035

0.04

0.045

0.02

0.04

0.035

0.045

0.03

0.025

0.04

0.045

0.016

0.03

0.04

0.045

0.025

0.03

0.04

0.045

0.02

0.03

0.05

0.045

0.025

0.035

0.04

0.045

0.03

0.035

0.045

0.045

0.045

0.04

0.045

0.045

0.025

0.045

0.05

0.045

0.04

0.03

0.05

0.04

0.04

0.04

0.05

0.04

0.04

0.03

0.04

0.04

0.04

0.03

0.04

0.04

0.04

0.03

0.05

0.04

0.03

0.03

0.045

0.045

0.035

0.03

0.04

0.04

0.035

0.03

0.04

0.04

0.03

0.03

0.04

0.04

0.03

0.03

0.04

0.04

0.035

0.03

0.04

0.04

0.03

0.03

0.04

0.05

0.03

0.03

0.045

0.04

0.03

0.03

0.05

0.04

0.04

0.035

0.045

0.04

0.035

0.02

0.03

0.04

0.035

0.03

0.035

0.04

0.04

0.03

0.03

0.04

0.04

0.03

0.025

0.04

0.035

0.03

0.03

0.04

0.035

0.04

0.035

0.04

0.03

0.025

0.035

0.04

0.035

0.03

0.025

0.04

0.04

0.03

0.04

0.04

0.03

0.025

0.02

0.04

0.03

0.03

0.03

0.04

0.035

0.02

0.02

0.04

0.03

0.03

0.035

0.04

0.03

0.025

0.04

0.04

0.04

0.025

0.04

0.045

0.03

0.03

0.04

0.04

0.03

0.025

0.035

0.04

0.03

0.03

0.045

0.04

0.03

0.03

0.04

0.04

0.03

0.02

0.04

0.04

0.03

0.02

0.04

0.04

0.03

0.02

0.042

0.04

0.03

0.03

0.04

0.04

0.03

0.03

0.03

0.04

0.02

0.04

0.03

0.04

0.04

0.03

0.04

0.04

0.035

0.025

0.03

0.04

0.04

0.03

0.03

0.04

0.03

0.025

0.03

0.04

0.03

0.025

0.03

0.04

0.03

0.03

0.03

0.04

0.03

0.035

0.03

0.04

0.035

0.035

0.03

0.045

0.02

0.03

0.045

0.04

0.04

0.03

0.03

0.04

0.025

0.03

0.03

0.04

0.035

0.025

0.03

0.04

0.035

0.025

0.02

0.04

0.03

0.035

0.03

0.04

0.03

0.03

0.04

0.04

0.03

0.025

0.03

0.04

0.025

0.035

0.025

0.04

0.04

0.03

0.025

0.04

0.04

0.03

0.02

0.04

0.03

0.035

0.04

0.025

0.04

0.04

0.04

0.035

0.03

0.037

0.04

0.025

0.035

0.035

0.04

0.02

0.03

0.03

0.04

0.02

0.03

0.032

0.04

0.02

0.03

0.031

0.04

0.015

0.025

0.069

0.04

0.035

0.03

0.068

0.04

0.03

0.045

0.067

0.04

0.04

0.04

0.063

0.04

0.025

0.04

0.064

0.04

0.03

0.04

0.07

0.04

0.03

0.04

0.07

0.04

0.03

0.04

0.069

0.04

0.03

0.03

0.068

0.04

0.02

0.03

0.067

0.04

0.03

0.035

0.069

0.04

0.02

0.03

0.071

0.045

0.04

0.035

0.056

0.04

0.04

0.02

0.067

0.04

0.025

0.025

0.069

0.04

0.03

0.025

0.062

0.04

0.03

0.03

0.053

0.055

0.04

0.03

0.064

0.04

0.035

0.03

0.063

0.045

0.045

0.03

0.052

0.04

0.02

0.03

0.057

0.05

0.02

0.03

0.056

0.05

0.02

0.03

0.07

0.05

0.03

0.03

0.05

0.05

0.025

0.02

0.06

0.05

0.03

0.02

0.06

0.05

0.025

0.03

0.06

0.05

0.025

0.02

0.06

0.05

0.085

0.035

0.05

0.045

0.08

0.03

0.05

0.04

0.075

0.03

0.055

0.05

0.08

0.04

0.055

0.05

0.075

0.04

0.055

0.045

0.075

0.03

0.05

0.05

0.07

0.025

0.05

0.045

0.075

0.025

0.05

0.04

0.07

0.03

0.05

0.06

0.075

0.03

0.05

0.04

0.08

0.03

0.05

0.04

0.08

0.025

0.05

0.04

0.08

0.03

0.06

0.04

0.075

0.025

0.055

0.045

0.08

0.03

0.05

0.05

0.07

0.03

0.05

0.045

0.08

0.02

0.055

0.04

0.07

0.03

0.05

0.045

0.08

0.02

0.055

0.075

0.025

0.04

0.075

0.03

0.06

0.05

0.075

0.02

0.055

0.04

0.075

0.025

0.045

0.04

0.075

0.025

0.05

0.04

0.075

0.03

0.04

0.04

0.08

0.025

0.04

0.04

0.075

0.025

0.04

0.04

0.08

0.025

0.04

0.04

0.08

0.02

0.04

0.02

0.08

0.035

0.04

0.03

0.08

0.025

0.055

0.03

0.08

0.035

0.04

0.04

0.075

0.025

0.045

0.025

0.08

0.03

0.035

0.025

0.09

0.03

0.035

0.02

0.075

0.04

0.045

0.025

0.09

0.03

0.045

0.025

0.125

0.025

0.045

0.025

0.08

0.03

0.045

0.03

0.08

0.035

0.045

0.03

0.08

0.05

0.035

0.025

0.08

0.05

0.04

0.025

0.09

0.03

0.04

0.025

0.085

0.05

0.04

0.025

0.09

0.05

0.04

0.03

0.08

0.05

0.035

0.025

0.09

0.05

0.035

0.025

0.04

0.05

0.035

0.02

0.11

0.05

0.035

0.025

0.09

0.05

0.04

0.02

0.09

0.05

0.04

0.025

0.095

0.05

0.04

0.03

0.09

0.05

0.04

0.03

0.09

0.045

0.05

0.02

0.1

0.05

0.05

0.02

0.105

0.05

0.05

0.055

0.09

0.05

0.05

0.055

0.03

0.045

0.05

0.065

0.04

0.05

0.05

0.055

0.025

0.045

0.045

0.05

0.02

0.05

0.05

0.06

0.04

0.045

0.05

0.06

0.05

0.045

0.04

0.06

0.02

0.045

0.04

0.06

0.035

0.045

0.04

0.06

0.025

0.045

0.04

0.06

0.025

0.04

0.035

0.065

0.03

0.04

0.07

0.05

0.03

0.03

0.08

0.065

0.05

0.04

0.06

0.06

0.03

0.04

0.06

0.06

0.03

0.04

0.06

0.05

0.035

0.04

0.07

0.07

0.035

0.04

0.065

0.05

0.03

0.04

0.08

0.06

0.035

0.04

0.08

0.07

0.03

0.04

0.09

0.06

0.03

0.025

0.09

0.06

0.03

0.03

0.08

0.06

0.035

0.03

0.09

0.065

0.03

0.03

0.09

0.06

0.035

0.03

0.09

0.06

0.043

0.025

0.08

0.06

0.043

0.03

0.09

0.06

0.043

0.03

0.09

0.06

0.043

0.03

0.09

0.06

0.042

0.025

0.09

0.05

0.039

0.035

0.09

0.055

0.03

0.03

0.06

0.06

0.041

0.035

0.07

0.065

0.047

0.03

0.075

0.055

0.048

0.035

0.07

0.05

0.047

0.035

0.07

0.05

0.042

0.035

0.07

0.06

0.043

0.025

0.06

0.06

0.045

0.03

0.07

0.06

0.043

0.03

0.06

0.06

0.045

0.035

0.06

0.05

0.043

0.025

0.06

0.05

0.04

0.035

0.07

0.05

0.04

0.025

0.07

0.06

0.045

0.02

0.065

0.06

0.045

0.02

0.05

0.05

0.045

0.035

0.06

0.055

0.04

0.033

0.06

0.055

0.045

0.036

0.065

0.055

0.045

0.037

0.06

0.055

0.045

0.037

0.06

0.055

0.04

0.034

0.05

0.06

0.04

0.044

0.06

0.06

0.04

0.043

0.06

0.06

0.045

0.043

0.06

0.06

0.045

0.044

0.06

0.06

0.04

0.046

0.05

0.06

0.04

0.045

0.05

0.06

0.04

0.044

0.065

0.06

0.04

0.039

0.06

0.06

0.05

0.039

0.06

0.06

0.05

0.038

0.06

0.06

0.045

0.037

0.06

0.06

0.04

0.04

0.06

0.06

0.04

0.036

0.06

0.06

0.04

0.039

0.06

0.06

0.04

0.038

0.06

0.065

0.04

0.038

0.06

0.055

0.04

0.037

0.06

0.06

0.045

0.039

0.06

0.06

0.04

0.038

0.06

0.06

0.04

0.038

0.06

0.06

0.045

0.038

0.07

0.06

0.04

0.039

0.06

0.04

0.045

0.06

0.04

0.04

0.05

0.04

0.04

0.06

0.04

0.04

0.065

0.04

0.04

0.055

0.04

0.035

0.06

0.04

0.04

0.055

0.04

0.035

0.06

0.04

0.04

0.06

0.04

0.04

0.05

0.04

0.035

0.04

0.04

0.04

0.04

0.04

0.04

0.05

0.04

0.04

0.04

0.045

0.04

0.04

0.035

0.04

0.05

0.04

0.05

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.035

0.04

0.035

0.04

0.04

0.04

0.035

0.04

0.035

0.04

0.035

0.04

0.035

0.04

0.03

0.04

0.03

0.04

0.035

0.04

0.03

0.04

0.03

0.04

0.035

0.04

0.035

0.04

0.035

0.04

0.03

0.04

0.025

0.04

0.03

0.035

0.03

0.035

0.03

0.035

0.04

0.035

0.03

0.035

0.03

0.035

0.03

0.035

0.02

0.035

0.025

0.04

0.01

0.035

0.01

0.045

0.01

0.045

0.03

0.045

0.01

0.035

0.015

0.035

0.025

0.035

0.03

0.045

0.03

0.035

0.03

0.035

0.04

0.035

0.035

0.035

0.03

0.04

0.03

0.04

0.035

0.04

0.035

0.04

0.035

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.04

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.045

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.05

0.035

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.025

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.03

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.04

0.045

0.045

0.045

0.04

0.04

0.04

0.04



Airstrip Count

		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148

		39206		39206		39206		39148		39148

		39230		39230		39230		39167		39167

		39267		39267		39267		39206		39206

		39297		39297		39297		39230		39230

		39349		39349		39349		39267		39267

		39392		39392		39392		39297		39297

		39427		39427		39427		39349		39349

		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713



CER 1

CER 2

CER3

Alert Level

Action Level

Date

Average CER Count

Figure 1.  Average Airstrip Count

3.625

6

29

10

15

5.375

7.5

28

10

15

13.125

13.25

28.75

10

15

13.25

11

27.75

10

15

4.25

5.25

24.5

10

15

4

1.75

11.75

10

15

4.25

9.25

10

15

19.5

5.5

22.5

10

15

5.75

4.25

13

10

15

3.25

1

4.75

10

15

11.625

8

18.25

10

15

3.875

1.75

10.5

10

15

4.125

2

10

35

45

1.125

0.5

3.5

35

45

3

1.25

6.5

35

45

3.25

0.75

5.25

35

45

2

0.75

2.75

35

45

6.375

1.75

8.25

35

45

13.5

1.25

10.25

35

45

2.6666666667

2.6666666667

11.25

35

45

6.2

4

3.75

35

45

6.2666666667

2

3.75

35

45

7.6666666667

3

7.5

35

45

9.4

2.8888888889

9

35

45

8.4

3.4444444444

6.5

35

45

6.5333333333

2.3333333333

8.5

35

45



Contact Plate Count

		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148

		39206		39206		39206		39148		39148

		39230		39230		39230		39167		39167

		39267		39267		39267		39206		39206

		39297		39297		39297		39230		39230

		39349		39349		39349		39267		39267

		39392		39392		39392		39297		39297

		39427		39427		39427		39392		39392

		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

Alert Level

Action Level

Date

Contact Plate Count

Figure 2. Average Contact Plate Count

1.4285714286

0.25

2.5

10

15

3.7142857143

2.75

4

10

15

1.1428571429

1.75

0.8333333333

10

15

2.4285714286

3

2.5

10

15

2.4285714286

0.75

3.1666666667

10

15

5.5714285714

3.25

5

10

15

5.2857142857

5.2

10

15

2.7142857143

1.5

2

10

15

1.1428571429

0

2

10

15

3.1428571429

1

3.25

10

15

3.4285714286

3.25

2.25

10

15

1.5714285714

0.75

1.5

10

15

1.7142857143

1

2.25

6

7

0.5714285714

0.5

2.25

6

7

1.5714285714

0.5

3

6

7

2

0.75

2.5

6

7

0.7142857143

0.25

1.75

6

7

3.4285714286

1.25

3.25

6

7

4

1

3.75

6

7

1.5333333333

1

3

6

7

2

1

2.25

6

7

1.7333333333

0.6666666667

1.5

6

7

0.9333333333

0.4444444444

1.5

6

7

0.9333333333

0.7777777778

2.5

6

7

1.1333333333

0.6666666667

1.75

6

7

0.9333333333

0.6666666667

1.5

6

7



0.5micron Count

		38776		38776		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126		39126		39126

		39148		39167		39167		39148		39148		39148		39148

		39148		39206		39206		39148		39148		39148		39148

		39167		39230		39230		39167		39167		39167		39167

		39206		39267		39267		39206		39206		39206		39206

		39230		39297		39297		39230		39230		39297		39297

		39267		39349		39349		39267		39267		39349		39349

		39297		39392		39392		39297		39297		39392		39392

		39392		39427		39427		39392		39392		39427		39427

		39545		39545		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

CER 1,3 Alert Level

CER 1,3 Action Level

CER 2 Alert Level

CER 2 Action Level

Date

0.5um/cu ft Count

Figure 3.  Average 0.5mm/cu ft Count

194

383

3263.8

5000

10000

5000

10000

339.5

338.3333333333

1210.4

5000

10000

5000

10000

362.75

719.3333333333

2800.4

5000

10000

5000

10000

688.125

416.3333333333

1999.6

5000

10000

5000

10000

618.75

336.6666666667

2033

5000

10000

5000

10000

692.625

1000

1857.4

5000

10000

5000

10000

401.375

1423.2

5000

10000

5000

10000

523.125

842

2313.2

5000

10000

5000

10000

273

292.3333333333

624.4

5000

10000

5000

10000

588.875

620

1580.4

5000

10000

5000

10000

714

474.6666666667

1255.6

5000

10000

5000

10000

755.625

587.3333333333

1139.8

5000

10000

5000

10000

772.875

643

1484

3800

4500

1250

1500

244

896.6666666667

1571.2

3800

4500

1250

1500

551.75

704.3333333333

2714

3800

4500

1250

1500

678.625

553

1781.8

3800

4500

1250

1500

369.625

300

731.6

3800

4500

1250

1500

664

478

1178.6

3800

4500

1250

1500

835.625

525

1260.6

3800

4500

1250

1500

699

83.7777777778

1354.8

3800

4500

1250

1500

635

204.4444444444

620.8

3800

4500

1250

1500

606

181.3333333333

750.8

3800

4500

1250

1500

606

109.5555555556

474.6

3800

4500

1250

1500

612.0666666667

156.7777777778

659.8

3800

4500

1250

1500

285.1333333333

190.5555555556

945.2

3800

4500

1250

1500

474

216.3333333333

768.6

3800

4500

1250

1500



5.0micron Count

		38776		38776		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148		39148		39148

		39206		39206		39206		39148		39148		39148		39148

		39230		39230		39230		39167		39167		39167		39167

		39267		39267		39267		39206		39206		39267		39267

		39297		39297		39297		39230		39230		39297		39297

		39349		39349		39349		39267		39267		39349		39349

		39392		39392		39392		39297		39297		39392		39392

		39427		39427		39427		39392		39392		39427		39427

		39545		39545		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

CER 1,3 Alert Level

CER 1,3 Action Level

CER 2 Alert Level

CER 2 Action Level

Date

5.0um/cu ft Count

Figure 4.  Average 5.0mm/cu ft Count

14.125

48.6666666667

226.8

30

50

30

50

33.625

49.3333333333

104.4

30

50

30

50

36.25

49

211.4

30

50

30

50

126.75

76.6666666667

305.2

30

50

30

50

67.875

37.3333333333

344.6

30

50

30

50

71.75

72.3333333333

166.4

30

50

30

50

43.5

235

30

50

30

50

65.125

37.3333333333

219.4

30

50

30

50

33.125

31.3333333333

50.6

30

50

30

50

47.75

50.6666666667

99.4

30

50

30

50

43.875

32.3333333333

79.2

30

50

30

50

47.125

44.3333333333

92.8

30

50

30

50

49

43.3333333333

92.2

410

500

90

105

30.75

75.6666666667

129.2

410

500

90

105

78.875

89

258.4

410

500

90

105

60

44

147

410

500

90

105

28.375

22.6666666667

53

410

500

90

105

26.125

20.3333333333

58

410

500

90

105

45.125

24.3333333333

80.8

410

500

90

105

37.3333333333

10

69.2

410

500

90

105

34.6

12.5555555556

33.2

410

500

90

105

29

9.3333333333

34

410

500

90

105

29

7.1111111111

33

410

500

90

105

30.0666666667

8.8888888889

27.6

410

500

78

83

18.7333333333

11.5555555556

43.4

410

500

78

83

24.3333333333

9.8888888889

37.6

410

500

78

83



CER 1

				AIRSTRIPS:																																																																																																		CONTACT PLATES:																																																																																																		PARTICLE COUNTS

				A						B						C						D						E						F						G						H						I						J						K						L						M						N						O						Average								A						B						C						D						E						F						G						H						I						J						K						L						M						N						O						Average								A				B				C				D				E				F				G				H				I				J				K				L				M				N				O				Average

		Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 1		Date		Alert Level		Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 1		Date		Alert Level		Action Level		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		CER 1 0.5um/ cu ft		Date		CER 1,3 Alert Level		CER 1,3 Action Level		CER 1 5.0um/cu ft		Date		CER 1,3 Alert Level		CER 1,3 Action Level

		2/28/06		2		0		2		4		0		4		5		0		5		4		0		4		8		0		8		0		0		0		3		0		3		3		0		3																																												4		2/28/06		10		15		0		0		0		0		0		0		1		0		1		0		0		0		2		0		2		0		0		0		3		0		3		4		0		4						0						0						0						0						0						0						0		1		2/28/06		10		15		207		8		291		16		133		12		278		21		134		13		25		5		262		22		222		16																														194		02/28/06		5000		10000		14		2/28/06		30		50

		3/30/06		4		0		4		4		0		4		7		0		7		6		0		6		10		0		10		2		0		2		6		0		6		4		0		4																																												5		3/30/06		10		15		1		0		1		3		0		3		6		0		6		3		0		3		2		0		2		5		0		5		3		0		3		3		0		3						0						0						0						0						0						0						0		4		3/30/06		10		15		310		48		483		69		134		18		263		24		444		31		679		40		199		8		204		31																														340		03/30/06		5000		10000		34		3/30/06		30		50

		4/28/06		4		0		4		12		0		12		12		0		12		15		0		15		17		0		17		6		4		10		12		0		12		23		0		23																																												13		4/28/06		10		15		0		0		0		2		0		2		2		0		2		0		0		0		0		0		0		0		0		0		4		0		4		0		0		0						0						0						0						0						0						0						0		1		4/28/06		10		15		487		81		221		21		261		19		390		32		480		60		287		23		321		19		455		35																														363		04/28/06		5000		10000		36		4/28/06		30		50

		5/30/06		6		0		6		10		0		10		12		0		12		17		0		17		19		0		19		9		0		9		12		0		12		21		0		21																																												13		5/30/06		10		15		1		0		1		4		0		4		3		0		3		0		0		0		1		0		1		0		0		0		7		0		7		1		0		1						0						0						0						0						0						0						0		2		5/30/06		10		15		678		124		1084		137		214		36		113		21		1478		449		220		32		1009		120		709		95																														688		05/30/06		5000		10000		127		5/30/06		30		50

		7/7/06		4		0		4		2		0		2		6		0		6		4		0		4		8		0		8		1		0		1		4		0		4		5		0		5																																												4		7/7/06		10		15		1		0		1		2		0		2		1		0		1		2		0		2		2		0		2		1		0		1		4		0		4		4		0		4						0						0						0						0						0						0						0		2		7/7/06		10		15		631		86		779		72		1234		81		282		38		464		75		694		93		564		65		302		33																														619		07/07/06		5000		10000		68		7/7/06		30		50

		9/5/06		4		0		4		4		0		4		6		0		6		5		0		5		2		0		2		2		0		2		4		0		4		5		0		5																																												4		9/5/06		10		15		4		0		4		6		0		6		4		0		4		3		0		3		6		0		6		5		0		5		5		0		5		6		0		6						0						0						0						0						0						0						0		6		9/5/06		10		15		1056		113		622		73		227		35		828		84		603		57		875		95		545		56		785		61																														693		09/05/06		5000		10000		72		9/5/06		30		50

		10/5/06		5		0		5		4		0		4		4		0		4		5		0		5		6		0		6		4		0		4		3		0		3		3		0		3																																												4		10/5/06		10		15		5		0		5		6		0		6		4		0		4		4		0		4		5		0		5		3		0		3		6		0		6		4		0		4						0						0						0						0						0						0						0		5		10/5/06		10		15		122		14		263		18		352		48		540		69		361		38		421		63		389		41		763		57																														401		10/05/06		5000		10000		44		10/5/06		30		50

		11/14/06		11		0		11		27		0		27		10		0		10		24		0		24		26		0		26		32		0		32		12		0		12		14		0		14																																												20		11/14/06		10		15		1		0		1		1		0		1		0		0		0		0		0		0		5		0		5		1		0		1		2		0		2		9		0		9						0						0						0						0						0						0						0		3		11/14/06		10		15		596		71		455		67		641		77		585		62		991		81		357		52		62		60		498		51																														523		11/14/06		5000		10000		65		11/14/06		30		50

		12/20/06		2		0		2		1		0		1		5		0		5		1		0		1		13		0		13		7		0		7		13		0		13		4		0		4																																												6		12/20/06		10		15		1		0		1		2		0		2		0		0		0		1		0		1		3		0		3		1		0		1		0		0		0		0		0		0						0						0						0						0						0						0						0		1		12/20/06		10		15		367		35		390		46		168		18		321		30		343		32		191		14		90		25		314		65																														273		12/20/06		5000		10000		33		12/20/06		30		50

		1/16/07		3		0		3		2		0		2		4		0		4		6		0		6		2		0		2		2		0		2		3		0		3		4		0		4																																												3		1/16/07		10		15		2		0		2		2		0		2		1		0		1		3		0		3		4		0		4		2		0		2		4		0		4		4		0		4						0						0						0						0						0						0						0		3		1/16/07		10		15		361		21		449		56		304		35		265		31		761		42		804		62		901		64		866		71																														589		01/16/07		5000		10000		48		1/16/07		30		50

		2/13/07		11		0		11		5		0		5		10		0		10		6		0		6		24		0		24		6		0		6		10		0		10		21		0		21																																												12		2/13/07		10		15		1		0		1		8		0		8		3		0		3		2		0		2		0		0		0		4		0		4		2		0		2		4		0		4						0						0						0						0						0						0						0		3		2/13/07		10		15		611		41		862		50		841		42		942		61		744		40		622		33		402		24		688		60																														714		02/13/07		5000		10000		44		2/13/07		30		50

		3/26/07		3		0		3		4		0		4		4		0		4		6		0		6		2		0		2		4		0		4		6		0		6		2		0		2																																												4		3/7/07		10		15		1		0		1		1		0		1		2		0		2		0		0		0		1		0		1		2		0		2		2		0		2		2		0		2						0						0						0						0						0						0						0		2		3/7/07		10		15		721		51		640		42		871		48		901		52		844		48		408		36		799		49		861		51																														756		03/07/07		5000		10000		47		3/7/07		30		50

		5/4/07		4		0		4		4		0		4		3		0		3		4		0		4		6		0		6		2		0		2		6		0		6		4		0		4																																												4		3/7/07		35		45		2		0		2		1		0		1		2		0		2		1		0		1		0		0		0		1		0		1		2		0		2		3		0		3						0						0						0						0						0						0						0		2		3/7/07		6		7		641		41		722		52		699		47		944		61		872		45		698		41		662		37		945		68																														773		03/07/07		3800		4500		49		3/7/07		410		500

		5/28/07		1		0		1		1		0		1		2		0		2		0		0		0		2		0		2		1		0		1		1		0		1		1		0		1																																												1		3/26/07		35		45		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1						0						0						0						0						0						0						0		1		3/26/07		6		7		161		17		200		21		251		36		275		28		320		53		101		15		460		55		184		21																														244		03/26/07		3800		4500		31		3/26/07		410		500

		7/4/07		2		0		2		3		0		3		3		0		3		3		0		3		2		0		2		4		0		4		4		0		4		3		0		3																																												3		5/4/07		35		45		2		0		2		2		0		2		1		0		1		0		0		0		1		0		1		1		0		1		2		0		2		2		0		2						0						0						0						0						0						0						0		2		5/4/07		6		7		346		64		339		37		537		77		301		55		492		86		292		31		896		120		1211		161																														552		05/04/07		3800		4500		79		5/4/07		410		500

		8/3/07		4		0		4		2		0		2		3		0		3		2		0		2		2		0		2		4		0		4		4		0		4		5		0		5																																												3		5/28/07		35		45		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		3		0		3		3		0		3		2		0		2						0						0						0						0						0						0						0		2		5/28/07		6		7		221		20		107		19		647		49		587		37		744		87		907		78		1241		101		975		89																														679		05/28/07		3800		4500		60		5/28/07		410		500

		9/24/07		2		0		2		1		0		1		1		0		1		2		0		2		3		0		3		3		0		3		2		0		2		2		0		2																																												2		7/4/07		35		45		0		0		0		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		2		0		2		2		0		2						0						0						0						0						0						0						0		1		7/4/07		6		7		310		27		488		31		210		20		401		29		121		18		404		31		601		41		422		30																														370		07/04/07		3800		4500		28		7/4/07		410		500

		11/6/07		6		0		6		4		0		4		4		0		4		4		0		4		8		0		8		7		0		7		8		0		8		10		0		10																																												6		8/3/07		35		45		2		0		2		2		0		2		3		0		3		1		0		1		3		0		3		5		0		5		4		0		4		4		0		4						0						0						0						0						0						0						0		3		8/3/07		6		7		523		33		678		25		498		14		671		22		687		23		721		33		856		34		678		25																														664		08/03/07		3800		4500		26		8/3/07		410		500

		12/11/07		10		0		10		9		0		9		11		0		11		12		0		12		12		0		12		15		0		15		21		0		21		18		0		18																																												14		9/24/07		35		45		2		0		2		1		0		1		3		0		3		4		0		4		4		0		4		4		0		4		3		0		3		7		0		7						0						0						0						0						0						0						0		4		11/6/07		6		7		678		36		761		31		734		34		891		44		851		33		781		33		1011		81		978		69																														836		11/06/07		3800		4500		45		11/6/07		410		500

		4/7/08		6		0		6		5		0		5		7		0		7		6		0		6		0		0		0		0		0		0		2		0		2		4		0		4		4		0		4		3		0		3		2		0		2		0		0		0		0		0		0		0		0		0		1		0		1		3		4/7/08		35		45		2		0		2		1		0		1		3		0		3		3		0		3		2		0		2		1		0		1		1		0		1		0		0		0		2		0		2		0		0		0		2		0		2		1		0		1		1		0		1		2		0		2		2		0		2		2		4/7/08		6		7		989		45		1045		58		1349		61		1305		60		689		46		430		30		1027		60		899		42		621		24		318		19		501		24		313		33		295		13		303		21		401		24		699		04/07/08		3800		4500		37		4/7/08		410		500

		5/7/08		9		0		9		8		0		8		7		0		7		8		0		8		3		0		3		3		0		3		3		0		3		7		0		7		7		0		7		4		0		4		8		0		8		4		0		4		8		0		8		9		0		9		5		0		5		6		5/7/08		35		45		3		0		3		2		0		2		2		0		2		2		0		2		3		0		3		3		0		3		2		0		2		1		0		1		1		0		1		1		0		1		2		0		2		2		0		2		2		0		2		2		0		2		2		0		2		2		5/7/08		6		7		782		44		671		39		724		41		454		22		576		33		430		30		671		32		572		28		781		37		671		32		677		33		476		41		672		31		781		43		587		33		635		05/07/08		3800		4500		35		5/7/08		410		500

		6/3/08		8		0		8		8		0		8		4		0		4		5		0		5		6		0		6		6		0		6		5		0		5		5		0		5		5		0		5		4		0		4		7		0		7		8		0		8		8		0		8		9		0		9		6		0		6		6		6/3/08		35		45		3		0		3		1		0		1		1		0		1		2		0		2		1		0		1		3		0		3		1		0		1		2		0		2		2		0		2		0		0		0		2		0		2		1		0		1		2		0		2		2		0		2		3		0		3		2		6/3/08		6		7		621		33		393		22		891		31		671		25		1192		44		671		19		781		22		245		19		1325		44		601		41		418		31		351		29		301		21		290		23		339		31		606		06/03/08		3800		4500		29		6/3/08		410		500

		7/1/08		9		0		9		9		0		9		7		0		7		9		0		9		8		0		8		5		0		5		8		0		8		8		0		8		8		0		8		6		0		6		11		0		11		6		0		6		9		0		9		9		0		9		3		0		3		8		7/1/08		35		45		1		0		1		2		0		2		0		0		0		1		0		1		1		0		1		1		0		1		0		0		0		0		0		0		2		0		2		1		0		1		1		0		1		2		0		2		0		0		0		1		0		1		1		0		1		1		7/1/08		6		7		621		33		393		22		891		31		671		25		1192		44		671		19		781		22		245		19		1325		44		601		41		418		31		351		29		301		21		290		23		339		31		606		07/01/08		3800		4500		29		7/1/08		410		500

		7/21/08		11		0		11		11		0		11		5		0		5		5		0		5		12		0		12		11		0		11		12		0		12		6		0		6		6		0		6		9		0		9		14		0		14		15		0		15		11		0		11		6		0		6		7		0		7		9		7/21/08		35		45		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		7/21/08		6		7		232		23		452		26		337		27		671		33		476		27		501		28		488		28		782		37		561		27		442		28		891		38		590		29		876		31		991		42		891		27		612		07/21/08		3800		4500		30		7/21/08		410		500

		9/4/08		10		0		10		9		0		9		6		0		6		7		0		7		7		0		7		9		0		9		6		0		6		9		0		9		11		0		11		12		0		12		10		0		10		9		0		9		6		0		6		6		0		6		9		0		9		8		9/4/08		35		45		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		9/4/08		6		7		219		19		140		14		275		16		101		9		244		16		301		21		189		19		181		17		176		17		215		21		414		24		409		21		357		21		454		19		602		27		285		09/04/08		3800		4500		19		9/4/08		410		500

		9/22/08		5		0		5		5		0		5		9		0		9		5		0		5		5		0		5		9		0		9		11		0		11		4		0		4		11		0		11		5		0		5		5		0		5		6		0		6		6		0		6		8		0		8		4		0		4		7		9/22/08		35		45		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		0		0		0		2		0		2		1		0		1		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		9/22/08		6		7		332		21		254		19		354		21		548		31		369		22		584		26		651		22		448		26		296		19		489		29		336		21		754		32		565		26		665		29		465		21		474		09/22/08		3800		4500		24		9/22/08		410		500

		11/6/08		3		0		3		3		0		3		5		0		5		4		0		4		4		0		4		3		0		3		4		0		4		4		0		4		4		0		4		5		0		5		5		0		5		3		0		3		3		0		3		3		0		3		4		0		4		4		11/6/08		35		45		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		1		0		1		0		11/6/08		6		7		721		31		867		39		253		12		458		22		357		20		445		28		432		22		685		31		591		28		241		9		219		8		473		19		501		21		765		33		801		36		521		11/06/08		3800		4500		24		11/6/08		410		500

		12/1/08		2		0		2		0		0		0		0		0		0		2		0		2		2		0		2		3		0		3		0		0		0		1		0		1		4		0		4		3		0		3		2		0		2		1		0		1		0		0		0		2		0		2		3		0		3		2		12/1/08		35		45		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		1		12/1/08		6		7		110		9		89		9		122		13		25		6		59		8		131		18		40		7		274		19		157		12		88		6		150		9		114		8		517		32		180		15		234		21		153		12/01/08		3800		4500		13		12/1/08		410		500

		12/16/08		3		0		3		2		0		2		3		0		3		2		0		2		2		0		2		3		0		3		4		0		4		3		0		3		5		0		5		4		0		4		4		0		4		3		0		3		3		0		3		3		0		3		3		0		3		3		12/16/08		35		45		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		1		0		1		1		12/16/08		6		7		291		18		178		11		271		19		189		14		177		14		276		18		198		11		187		14		278		17		91		7		87		6		287		16		376		21		301		17		227		19		228		12/16/08		3800		4500		15		12/16/08		410		500



&L&"Arial Narrow,Bold"&14CER 1&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER 2

										AIRSTRIPS:																																																												CONTACT PLATES:																																																						PARTICLE COUNTS

				A						B						C						D						E						F						G						H						I						Average						A						B						C						D						E						F						G						H						I						Average						A				B				C				D				E				F				G				H				I				Average

		Sample Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 2		Alert Level		Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 2		Total Alert Level		Total Action Level		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		CER 2 0.5um/cu ft		Date		CER 2 Alert Level		CER 2 Action Level		CER 2 5.0um/cu ft		Date		CER 2 Alert Level		CER 2 Action Level

		2/28/06								6		0		6		0		0		0		9		0		9		9		0		9																										6		10		15								0		0		0		0		0		0		1		0		1		0		0		0																										0		10		15		297		39		288		43		0		0		564		64																						383		2/28/06		5000		10000		49		02/28/06		30		50

		3/30/06								9		0		9		1		0		1		8		0		8		12		0		12																										8		10		15								2		0		2		0		0		0		6		0		6		3		0		3																										3		10		15		460		68		264		39		0		0		291		41																						338		3/30/06		5000		10000		49		03/30/06		30		50

		4/28/06								29		0		29		0		0		0		22		0		22		2		0		2																										13		10		15								2		0		2		2		0		2		0		0		0		3		0		3																										2		10		15		1084		67		543		41		0		0		531		39																						719		4/28/06		5000		10000		49		04/28/06		30		50

		5/30/06								21		0		21		0		0		0		19		0		19		4		0		4																										11		10		15								4		0		4		2		0		2		1		0		1		5		0		5																										3		10		15		435		87		354		66		0		0		460		77																						416		5/30/06		5000		10000		77		05/30/06		30		50

		7/7/06								5		0		5		0		0		0		8		0		8		8		0		8																										5		10		15								0		0		0		0		0		0		2		0		2		1		0		1																										1		10		15		232		33		299		39		0		0		479		40																						337		7/7/06		5000		10000		37		07/07/06		30		50

		9/5/06								3		0		3		0		0		0		2		0		2		2		0		2																										2		10		15								4		0		4		0		0		0		4		0		4		5		0		5																										3		10		15		1289		79		289		30		0		0		1422		108																						1000		9/5/06		5000		10000		72		09/05/06		30		50

		10/5/06																																																																																																																																																																10/5/06		5000		10000				10/05/06		30		50

		11/14/06								16		0		16		0		0		0		4		0		4		2		0		2																										6		10		15								1		0		1		0		0		0		4		0		4		1		0		1																										2		10		15		961		41		877		40		0		0		688		31																						842		11/14/06		5000		10000		37		11/14/06		30		50

		12/20/06								5		0		5		4		0		4		6		0		6		2		0		2																										4		10		15								0		0		0		0		0		0		0		0		0		0		0		0																										0		10		15		463		36		141		17		0		0		273		41																						292		12/20/06		5000		10000		31		12/20/06		30		50

		1/16/07								2		0		2		0		0		0		1		0		1		1		0		1																										1		10		15								1		0		1		0		0		0		1		0		1		2		0		2																										1		10		15		781		62		451		32		0		0		628		58																						620		1/16/07		5000		10000		51		01/16/07		30		50

		2/13/07								12		0		12		0		0		0		10		0		10		10		0		10																										8		10		15								4		0		4		0		0		0		4		0		4		4		1		5																										3		10		15		640		31		285		44		0		0		499		22																						475		2/13/07		5000		10000		32		02/13/07		30		50

		3/26/07								2		0		2		0		0		0		2		0		2		3		0		3																										2		35		45								1		0		1		0		0		0		1		0		1		1		0		1																										1		6		7		490		40		684		51		0		0		588		42																						587		3/7/07		5000		10000		44		03/07/07		30		50

		5/4/07								2		0		2		0		0		0		3		0		3		3		0		3																										2		35		45								1		0		1		0		0		0		1		0		1		2		0		2																										1		6		7		640		41		585		37		0		0		704		52																						643		3/7/07		1250		1500		43		03/07/07		90		105

		5/28/07								0		0		0		0		0		0		1		0		1		1		0		1																										1		35		45								1		0		1		0		0		0		0		0		0		1		0		1																										1		6		7		1104		101		944		81		0		0		642		45																						897		3/26/07		1250		1500		76		03/26/07		90		105

		7/4/07								1		0		1		0		0		0		2		0		2		2		0		2																										1		35		45								0		0		0		0		0		0		1		0		1		1		0		1																										1		6		7		10		0		962		123		0		0		1141		132																						704		5/4/07		1250		1500		89		07/04/07		90		105

		8/3/07								0		0		0		0		0		0		1		0		1		2		0		2																										1		35		45								1		0		1		0		0		0		1		0		1		1		0		1																										1		6		7		0		0		784		61		0		0		875		71																						553		8/3/07		1250		1500		44		08/03/07		90		105

		9/24/07								1		0		1		0		0		0		1		0		1		1		0		1																										1		35		45								0		0		0		0		0		0		0		0		0		1		0		1																										0		6		7		0		0		199		19		0		0		701		49																						300		9/24/07		1250		1500		23		09/24/07		90		105

		11/6/07								1		0		1		0		0		0		3		0		3		3		0		3																										2		35		45								1		0		1		0		0		0		2		0		2		2		0		2																										1		6		7		4		0		563		22		0		0		867		39																						478		11/6/07		1250		1500		20		11/06/07		90		105

		12/11/07								0		0		0		0		0		0		2		0		2		3		0		3																										1		35		45								0		0		0		0		0		0		3		0		3		1		0		1																										1		6		7		2		0		672		36		0		0		901		37																						525		12/11/07		1250		1500		24		12/11/07		90		105

		4/7/08		0		0		0		4		0		4		7		0		7		0		0		0		4		0		4		0		0		0		6		0		6		3		0		3		0		0		0		3		35		45		0		0		0		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		2		0		2		2		0		2		0		0		0		1		6		7		0		0		162		23		208		25		0		0		93		19		0		0		90		6		201		17		0		0		84		4/7/08		1250		1500		10		04/07/08		90		105

		5/7/08		0		0		0		3		0		3		9		0		9		0		0		0		8		0		8		0		0		0		8		0		8		8		0		8		0		0		0		4		35		45		0		0		0		2		0		2		3		0		3		0		0		0		2		0		2		0		0		0		1		0		1		1		0		1		0		0		0		1		6		7		0		0		401		24		489		25		0		0		281		22		0		0		187		18		482		24		0		0		204		5/7/08		1250		1500		13		05/07/08		90		105

		6/3/08		0		0		0		3		0		3		3		0		3		0		0		0		5		0		5		0		0		0		5		0		5		2		0		2		0		0		0		2		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		0		1		0		0		0		1		6		7		0		0		267		10		498		22		0		0		268		22		0		0		301		19		298		11		0		0		181		6/3/08		1250		1500		9		06/03/08		90		105

		7/1/08		0		0		0		8		0		8		0		0		0		8		0		8		6		0		6		0		0		0		3		0		3		2		0		2		0		0		0		3		35		45		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		0		6		7		0		0		403		22		0		0		153		11		287		19		1		0		21		1		121		11		0		0		110		7/1/08		1250		1500		7		07/01/08		90		105

		7/21/08		0		0		0		6		0		6		0		0		0		7		0		7		7		0		7		0		0		0		4		0		4		2		0		2		0		0		0		3		35		45		0		0		0		2		0		2		0		0		0		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		0		0		0		1		6		7		0		0		376		19		0		0		298		17		337		21		0		0		109		8		291		15		0		0		157		7/21/08		1250		1500		9		07/21/08		78		83

		9/4/08		0		0		0		7		0		7		9		0		9		0		0		0		4		0		4		0		0		0		4		0		4		4		0		4		3		0		3		3		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		6		7		0		0		210		19		175		11		0		0		361		18		0		0		101		7		162		9		706		40		191		9/4/08		1250		1500		12		09/04/08		78		83

		9/22/08		0		0		0		5		0		5		4		0		4		0		0		0		4		0		4		0		0		0		2		0		2		4		0		4		2		0		2		2		35		45		0		0		0		2		0		2		0		0		0		0		0		0		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		1		6		7		0		0		332		21		296		15		0		0		194		9		0		0		265		11		295		11		565		22		216		9/22/08		1250		1500		10		09/22/08		78		83

		11/6/08		0		0		0		2		0		2		3		0		3		0		0		0		2		0		2		0		0		0		3		0		3		3		0		3		2		0		2		2		35		45		0		0		0		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		6		7		0		0		776		22		409		19		0		0		292		8		0		0		301		16		228		11		220		9		247		11/6/08		1250		1500		9		11/06/08		78		83

		12/1/08		0		0		0		3		0		3		2		0		2		0		0		0		3		0		3		0		0		0		2		0		2		0		0		0		1		0		1		1		35		45		0		0		0		1		0		1		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		6		7		0		0		290		12		203		11		0		0		221		12		0		0		313		21		19		3		148		10		133		12/1/08		1250		1500		8		12/01/08		78		83

		12/16/08		0		0		0		4		0		4		3		0		3		0		0		0		3		0		3		0		0		0		3		0		3		0		0		0		1		0		1		2		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		6		7		0		0		199		9		289		16		0		0		167		7		0		0		267		17		89		6		177		11		132		12/16/08		1250		1500		7		12/16/08		78		83



&L&"Arial Narrow,Bold"&14CER 2&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER 3

				AIRSTRIPS:																														CONTACT PLATES:																																				PARTICLE COUNTS

				A						B						D						E						Average						A						B						C						D						E						Average						A				B				C				D				E				Average

		Sample Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER3		Total Alert Level		Total Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 3		Total Alert Level		Total Action Level		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		CER 3 0.5um/cu ft		0.5um/cu ft Alert Level		0.5um/cu ft Action Level		CER 3 5.0um/cu ft		5.0um/cu ft Alert Level		5.0um/cu ft Action Level

		2/28/06		29		1		30		21		0		21		28		0		28		37		0		37		29		10		15		3		0		3		3		0		3		3		0		3		2		0		2		4		0		4		3		10		15		4411		344		3943		271		3664		229		3068		212		1233		78		3264		5000		10000		227		30		50

		3/30/06		32		1		33		26		0		26		21		0		21		32		0		32		28		10		15		5		0		5		4		0		4		6		0		6		4		0		4		5		0		5		4		10		15		1261		119		979		81		1461		101		1721		120		630		101		1210		5000		10000		104		30		50

		4/28/06		29		2		31		32		0		32		23		0		23		29		0		29		29		10		15		2		0		2		3		0		3		0		0		0		0		0		0		0		0		0		1		10		15		4536		307		3293		245		2424		222		2637		211		1112		72		2800		5000		10000		211		30		50

		5/30/06		31		0		31		29		0		29		21		1		22		29		0		29		28		10		15		4		0		4		5		0		5		2		0		2		1		0		1		3		0		3		3		10		15		1914		327		2122		327		2561		413		1572		207		1829		252		2000		5000		10000		305		30		50

		7/7/06		26		0		26		19		0		19		22		0		22		31		0		31		25		10		15		4		0		4		5		0		5		3		0		3		2		0		2		5		0		5		3		10		15		2150		382		2668		423		2561		401		2022		399		764		118		2033		5000		10000		345		30		50

		9/5/06		10		0		10		12		0		12		11		0		11		14		0		14		12		10		15		6		0		6		4		0		4		4		0		4		6		0		6		5		0		5		5		10		15		2286		180		2142		171		1829		162		1749		171		1281		148		1857		5000		10000		166		30		50

		10/5/06		9		0		9		10		0		10		10		0		10		8		0		8		9		10		15		7		0		7		5		0		5		6		0		6		4		0		4		4		0		4		5		10		15		1679		346		793		137		1841		241		1429		248		1374		203		1423		5000		10000		235		30		50

		11/14/06		19		2		21		26		0		26		26		0		26		17		0		17		23		10		15		2		0		2		1		0		1		0		0		0		1		0		1		6		0		6		2		10		15		2241		243		2301		231		1974		198		2475		224		2575		201		2313		5000		10000		219		30		50

		12/20/06		10		0		10		13		0		13		13		0		13		16		0		16		13		10		15		5		0		5		1		0		1		0		0		0		3		0		3		1		0		1		2		10		15		406		33		727		46		923		94		604		41		462		39		624		5000		10000		51		30		50

		1/16/07		4		0		4		5		0		5		7		0		7		3		0		3		5		10		15		3		0		3		2		0		2		3		0		3		4		0		4		4		0		4		3		10		15		485		41		1785		101		1986		128		1785		109		1861		118		1580		5000		10000		99		30		50

		2/13/07		12		0		12		22		0		22		18		0		18		21		0		21		18		10		15		2		0		2		4		0		4		2		0		2		1		0		1		2		0		2		2		10		15		1261		87		1641		98		901		62		988		61		1487		88		1256		5000		10000		79		30		50

		3/26/07		11		0		11		12		0		12		10		0		10		9		0		9		11		35		45		2		0		2		1		0		1		2		0		2		1		0		1		2		0		2		2		6		7		1421		109		1221		101		866		71		949		82		1242		101		1140		3800		4500		93		410		500

		5/4/07		10		0		10		10		0		10		9		0		9		11		0		11		10		35		45		2		0		2		3		0		3		1		0		1		2		0		2		2		0		2		2		6		7		1741		110		1444		91		1235		81		1479		87		1521		92		1484		3800		4500		92		410		500

		5/28/07		6		0		6		4		0		4		2		0		2		2		0		2		4		35		45		4		0		4		2		0		2		1		0		1		1		0		1		2		0		2		2		6		7		1421		102		1387		100		1842		169		1785		154		1421		121		1571		3800		4500		129		410		500

		7/4/07		7		0		7		6		0		6		6		0		6		7		0		7		7		35		45		4		0		4		3		0		3		2		0		2		1		0		1		4		0		4		3		6		7		3950		375		2745		292		1658		177		2431		201		2786		247		2714		3800		4500		258		410		500

		8/3/07		6		0		6		6		0		6		4		0		4		5		0		5		5		35		45		3		0		3		3		0		3		2		0		2		2		0		2		2		0		2		3		6		7		1672		145		1897		152		1866		149		1987		151		1487		138		1782		3800		4500		147		410		500

		9/24/07		4		0		4		3		0		3		2		0		2		2		0		2		3		35		45		2		0		2		2		0		2		2		0		2		1		0		1		2		0		2		2		6		7		781		61		1011		72		689		49		768		52		409		31		732		3800		4500		53		410		500

		11/6/07		7		0		7		9		0		9		8		0		8		9		0		9		8		35		45		3		0		3		3		0		3		5		0		5		1		0		1		6		0		6		3		6		7		1276		78		1454		65		1109		55		987		45		1067		47		1179		3800		4500		58		410		500

		12/11/07		9		0		9		12		0		12		9		0		9		11		0		11		10		35		45		2		0		2		4		0		4		4		0		4		5		0		5		4		0		4		4		6		7		1853		101		1321		99		901		45		1241		87		987		72		1261		3800		4500		81		410		500

		4/7/08		8		0		8		15		0		15		12		0		12		10		0		10		11		35		45		2		0		2		3		0		3		2		0		2		3		0		3		4		0		4		3		6		7		1047		69		1642		79		1421		67		1677		71		987		60		1355		3800		4500		69		410		500

		5/7/08		3		0		3		4		0		4		4		0		4		4		0		4		4		35		45		4		0		4		3		0		3		4		0		4		1		0		1		1		0		1		2		6		7		561		31		761		44		660		39		451		21		671		31		621		3800		4500		33		410		500

		6/3/08		3		0		3		4		0		4		4		0		4		4		0		4		4		35		45		2		0		2		2		0		2		2		0		2		1		0		1		1		0		1		2		6		7		409		26		391		33		782		34		891		33		1281		44		751		3800		4500		34		410		500

		7/1/08		7		0		7		7		0		7		8		0		8		8		0		8		8		35		45		2		0		2		2		0		2		1		0		1		1		0		1		1		0		1		2		6		7		1121		81		677		42		339		22		125		11		111		9		475		3800		4500		33		410		500

		7/21/08		9		0		9		8		0		8		8		0		8		11		0		11		9		35		45		3		0		3		3		0		3		2		0		2		2		0		2		2		0		2		3		6		7		891		41		781		33		789		31		499		21		339		12		660		3800		4500		28		410		500

		9/4/08		6		0		6		9		0		9		4		0		4		7		0		7		7		35		45		2		0		2		2		0		2		1		0		1		2		0		2		1		0		1		2		6		7		793		37		1044		44		977		39		1011		57		901		40		945		3800		4500		43		410		500

		9/22/08		9		0		9		9		0		9		9		0		9		7		0		7		9		35		45		1		0		1		2		0		2		2		0		2		2		0		2		1		0		1		2		6		7		984		44		564		31		965		33		698		41		632		39		769		3800		4500		38		410		500

		11/6/08		6		0		6		6		0		6		4		0		4		3		0		3		5		35		45		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		1		6		7		1198		81		901		67		789		43		761		41		904		61		911		3800		4500		59		410		500

		12/1/08		7		0		7		7		0		7		6		0		6		7		0		7		7		35		45		2		0		2		1		0		1		2		0		2		1		0		1		1		0		1		1		6		7		1198		81		901		67		789		43		761		41		904		61		911		3800		4500		59		410		500

		12/16/08		8		0		8		8		0		8		6		0		6		9		0		9		8		35		45		1		0		1		2		0		2		1		0		1		1		0		1		1		0		1		1		6		7		892		41		1098		69		892		34		901		44		1167		72		990		3800		4500		52		410		500



&L&"Arial Narrow,Bold"&14CER 3&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER Pressure

		Daily				Monthly				Daily				Monthly				Daily																		Monthly																		Daily								Monthly								Specs

		Date		CER1		Month		CER1		Date		CER Change Room		Month		CER Change Room		Date		CER2		Temp (F)		Relative Humidity (%)		R&D Bio-Safety Cabinet North (left axis)		R&D Bio-Safety Cabinet South (left axis)		Mfg Bio-Safety Cabinet North (left axis)		Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)		Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)		Month		CER 2		Temp (F)		Relative Humidity (%)		R&D Bio-Safety Cabinet North (left axis)		R&D Bio-Safety Cabinet South (left axis)		Mfg Bio-Safety Cabinet North (left axis)		Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)		Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)		Date		CER3		Temp (ºF)		Humidity (%RH)		Month		CER 3		Temp (ºF)		Humidity (%RH)		Date		CER Alert Level		CER Action Level		Bio-Safety Cabinet Alert Level (left axis)		Bio-Safety Cabinet Action  Level (left axis)		Mfg Bio-Safety Cabinet South Alert Level (right axis)		Mfg Bio-Safety Cabinet South Alarm Level (right axis)

		4/24/06		0.05		April-06		0.045		3/31/06		0.05		March-06		0.055		3/31/06		0.09																March-06		0.090																6/19/06		0.05						June-06		0.051						4/30/06		0.05		0.03

		4/24/06		0.05		May-06		0.022		3/31/06		0.06		April-06		0.053		3/31/06		0.09																April-06		0.089																6/19/06		0.06						July-06		0.061						5/31/06		0.05		0.03

		4/25/06		0.05		June-06		0.013		4/4/06		0.05		May-06		0.050		4/4/06		0.09																July-06		0.076																6/28/06		0.03						August-06		0.055						6/30/06		0.05		0.03

		4/25/06		0.04		July-06		0.041		4/4/06		0.05		June-06		0.046		4/4/06		0.09																August-06		0.068																6/28/06		0.06						September-06		0.052						7/31/06		0.05		0.03

		4/26/06		0.06		August-06		0.033		4/5/06		0.05		July-06		0.048		4/5/06		0.09																September-06		0.062																6/29/06		0.03						October-06		0.051						8/31/06		0.05		0.03

		4/26/06		0.04		September-06		0.027		4/5/06		0.06		August-06		0.050		4/5/06		0.09																October-06		0.034																6/29/06		0.06						November-06		0.053						9/30/06		0.05		0.03

		4/27/06		0.04		October-06		0.033		4/6/06		0.05		September-06		0.048		4/6/06		0.09																November-06		0.020																6/30/06		0.06						December-06		0.051						10/31/06		0.05		0.03

		4/27/06		0.045		November-06		0.028		4/6/06		0.06		October-06		0.053		4/6/06		0.09																December-06		0.012																6/30/06		0.06						February-07		0.040						11/30/06		0.05		0.03

		4/28/06		0.05		December-06		0.030		4/7/06		0.055		November-06		0.035		4/7/06		0.09																January-07		0.011																7/5/06		0.03						March-07		0.037						12/31/06		0.05		0.03

		4/28/06		0.04		January-07		0.030		4/7/06		0.05		December-06		0.031		4/7/06		0.09																February-07		0.013																7/5/06		0.03						April-07		0.038						1/31/07		0.05		0.03

		4/29/06		0.035		February-07		0.038		4/10/06		0.055		January-07		0.031		4/10/06		0.095																March-07		0.031																7/6/06		0.06						May-07		0.038						1/28/07		0.05		0.03

		4/29/06		0.035		March-07		0.037		4/10/06		0.055		February-07		0.035		4/10/06		0.09																April-07		0.033																7/6/06		0.06						June-07		0.040						3/7/07		0.05		0.03

		5/1/06		0.025		April-07		0.031		4/11/06		0.055		March-07		0.036		4/11/06		0.095																May-07		0.044																7/7/06		0.06						July-07		0.057						3/7/07		0.03		0.005

		5/1/06		0.03		May-07		0.027		4/11/06		0.055		April-07		0.035		4/11/06		0.095																June-07		0.048																7/7/06		0.06						August-07		0.053						4/30/07		0.03		0.005

		5/2/06		0.025		June-07		0.027		4/12/06		0.055		May-07		0.032		4/12/06		0.09																July-07		0.050																7/10/06		0.06						September-07		0.050						5/16/07		0.03		0.005

		5/2/06		0.03		July-07		0.035		4/12/06		0.055		June-07		0.028		4/12/06		0.09																August-07		0.042																7/10/06		0.06						October-07		0.049						5/16/07		0.015		0.005

		5/3/06		0.015		August-07		0.032		4/13/06		0.055		July-07		0.030		4/13/06		0.09																September-07		0.046						0.610		0.408								7/11/06		0.06						November-07		0.047						5/31/07		0.015		0.005

		5/4/06		0.03		September-07		0.030		4/13/06		0.055		August-07		0.032		4/13/06		0.095																October-07		0.041						0.620		0.420								7/11/06		0.06						December-07		0.043						6/30/07		0.015		0.005

		5/5/06		0.03		October-07		0.030		4/17/06		0.06		September-07		0.029		4/17/06		0.095																November-07		0.035						0.632		0.424								7/12/06		0.06						January-08		0.040						7/31/07		0.015		0.005

		5/5/06		0.03		November-07		0.065		4/17/06		0.055		October-07		0.027		4/17/06		0.09																December-07		0.030						0.643		0.426								7/12/06		0.06						February-08		0.040						8/31/07		0.015		0.005

		5/6/06		0.03		December-07		0.077		4/18/06		0.055		November-07		0.044		4/18/06		0.095																January-08																		7/13/06		0.06						March-08		0.040						9/5/07		0.015		0.005		0.25		0.1

		5/6/06		0.025		January-08		0.088		4/18/06		0.06		December-07		0.043		4/18/06		0.09																February-08		0.049		69.778		46.100		0.281		0.309		0.428		62.091		1180.364		7/13/06		0.06						April-08		0.048		70.864		42.636		9/30/07		0.015		0.005		0.25		0.1

		5/7/06		0.03		February-08		0.035		4/19/06		0.045		January-08		0.032		4/19/06		0.085																March-08		0.063		70.000		39.750		0.272		0.318		0.441		63.000		1193.000		7/14/06		0.06						May-08		0.040		72.696		37.435		10/31/07		0.015		0.005		0.25		0.1

		5/8/06		0.03		March-08		0.041		4/19/06		0.05		February-08		0.035		4/19/06		0.09																April-08		0.053		71.045		41.000		0.276		0.320		0.454		62.333		1196.333		7/14/06		0.06						June-08		0.025		72.136		33.909		11/30/07		0.015		0.005		0.25		0.1

		5/8/06		0.03		April-08		0.043		4/20/06		0.055		March-08		0.039		4/20/06		0.079																May-08		0.043		72.304		35.913		0.282		0.320		0.449		60.652		1194.957		7/17/06		0.06						July-08		0.059		71.920		39.400		12/31/07		0.015		0.005		0.25		0.1

		5/9/06		0.025		May-08		0.041		4/20/06		0.05		April-08		0.040		4/20/06		0.08																June-08		0.043		71.826		33.522		0.288		0.318		0.447		57.913		790.783		7/17/06		0.06						August-08		0.057		71.600		40.040		1/31/08		0.015		0.005		0.25		0.1

		5/9/06		0.025		June-08		0.039		4/24/06		0.06		May-08		0.040		4/21/06		0.085																July-08		0.077		71.800		38.360		0.285		0.320		0.447		59.789		882.526		7/18/06		0.06						September-08		0.059		71.240		38.000		2/29/08		0.015		0.005		0.25		0.1

		5/10/06		0.025		July-08		0.027		4/24/06		0.06		June-08		0.037		4/21/06		0.085																August-08		0.061		71.440		38.480		0.272		0.318		0.448		0.000		0.000		7/18/06		0.06														3/31/08		0.015		0.005		0.25		0.1

		5/10/06		0.025		August-08		0.031		4/25/06		0.06		July-08		0.040		4/25/06		0.086																September-08		0.059		70.640		38.280		0.259		0.319		0.439		0.000		0.000		7/19/06		0.06														4/1/31		0.015		0.005		0.25		0.1

		5/11/06		0.015		September-08		0.030		4/25/06		0.06		August-08		0.041		4/25/06		0.085																																		7/19/06		0.06														5/31/08		0.015		0.005		0.25		0.1

		5/11/06		0.025						4/26/06		0.05		September-08		0.041		4/26/06		0.085																																		7/20/06		0.07														6/30/08		0.015		0.005		0.25		0.1

		5/12/06		0.025						4/26/06		0.02						4/26/06		0.087																																		7/20/06		0.07														7/31/08		0.015		0.005		0.25		0.1

		5/12/06		0.02						4/27/06		0.06						4/27/06		0.085																																		7/21/06		0.07														8/30/08		0.015		0.005		0.25		0.1

		5/15/06		0.02						4/27/06		0.055						4/27/06		0.085																																		7/21/06		0.07														9/30/08		0.015		0.005		0.25		0.1

		5/15/06		0.025						4/28/06		0.04						4/28/06		0.09																																		7/22/06		0.07

		5/16/06		0.01						4/28/06		0.055						4/28/06		0.08																																		7/22/06		0.07

		5/16/06		0.01						4/29/06		0.05						7/25/06		0.085																																		7/24/06		0.07

		5/17/06		0.01						4/29/06		0.05						7/25/06		0.085																																		7/24/06		0.07

		5/17/06		0.025						5/1/06		0.05						7/26/06		0.085																																		7/25/06		0.06

		5/18/06		0.02						5/1/06		0.055						7/26/06		0.075																																		7/25/06		0.06

		5/18/06		0.02						5/2/06		0.05						7/27/06		0.08																																		7/26/06		0.06

		5/19/06		0.03						5/2/06		0.055						7/27/06		0.08																																		7/26/06		0.06

		5/19/06		0.02						5/3/06		0.05						7/28/06		0.075																																		7/27/06		0.06

		5/20/06		0.01						5/4/06		0.045						7/28/06		0.079																																		7/27/06		0.06

		5/20/06		0.02						5/5/06		0.055						7/29/06		0.069																																		8/1/06		0.06

		5/22/06		0.015						5/5/06		0.05						7/29/06		0.07																																		8/1/06		0.06

		5/22/06		0.015						5/6/06		0.065						7/30/06		0.069																																		8/2/06		0.06

		5/23/06		0.015						5/6/06		0.055						7/30/06		0.069																																		8/2/06		0.06

		5/23/06		0.015						5/7/06		0.05						7/31/06		0.075																																		8/3/06		0.06

		5/24/06		0.015						5/8/06		0.05						7/31/06		0.073																																		8/3/06		0.06

		5/24/06		0.015						5/8/06		0.05						8/1/06		0.07																																		8/4/06		0.06

		5/25/06		0.015						5/9/06		0.05						8/1/06		0.075																																		8/4/06		0.06

		5/25/06		0.03						5/9/06		0.055						8/2/06		0.07																																		8/7/06		0.055

		5/30/06		0.015						5/10/06		0.045						8/2/06		0.07																																		8/7/06		0.06

		5/30/06		0.02						5/10/06		0.04						8/3/06		0.07																																		8/8/06		0.06

		6/1/06		0.01						5/11/06		0.045						8/3/06		0.074																																		8/8/06		0.06

		6/1/06		0.01						5/11/06		0.055						8/4/06		0.074																																		8/9/06		0.06

		6/2/06		0.015						5/12/06		0.05						8/4/06		0.074																																		8/9/06		0.06

		6/5/06		0.01						5/12/06		0.06						8/7/06		0.073																																		8/10/06		0.055

		6/5/06		0.013						5/15/06		0.045						8/7/06		0.073																																		8/10/06		0.055

		6/6/06		0.01						5/15/06		0.055						8/8/06		0.073																																		8/11/06		0.055

		6/6/06		0.01						5/16/06		0.05						8/8/06		0.073																																		8/11/06		0.055

		6/7/06		0.01						5/16/06		0.055						8/10/06		0.074																																		8/14/06		0.055

		6/7/06		0.01						5/17/06		0.04						8/10/06		0.071																																		8/14/06		0.055

		6/8/06		0.01						5/17/06		0.045						8/14/06		0.07																																		8/15/06		0.055

		6/8/06		0.01						5/18/06		0.05						8/15/06		0.069																																		8/15/06		0.055

		6/9/06		0.01						5/18/06		0.055						8/16/06		0.069																																		8/16/06		0.055

		6/9/06		0.01						5/19/06		0.04						8/16/06		0.07																																		8/16/06		0.055

		6/12/06		0.03						5/19/06		0.045						8/17/06		0.069																																		8/17/06		0.055

		6/12/06		0.01						5/20/06		0.04						8/17/06		0.069																																		8/17/06		0.06

		6/13/06		0.03						5/20/06		0.043						8/18/06		0.07																																		8/18/06		0.05

		6/13/06		0.01						5/22/06		0.05						8/18/06		0.068																																		8/18/06		0.065

		6/16/06		0.01						5/22/06		0.05						8/21/06		0.065																																		8/19/06		0.05

		6/16/06		0.01						5/23/06		0.05						8/22/06		0.06																																		8/19/06		0.055

		7/6/06		0.05						5/23/06		0.05						8/22/06		0.065																																		8/21/06		0.055

		7/6/06		0.04						5/24/06		0.045						8/23/06		0.065																																		8/21/06		0.05

		7/7/06		0.04						5/24/06		0.05						8/23/06		0.068																																		8/22/06		0.05

		7/8/06		0.04						5/25/06		0.05						8/24/06		0.065																																		8/22/06		0.056

		7/10/06		0.05						5/25/06		0.05						8/24/06		0.055																																		8/23/06		0.055

		7/11/06		0.04						5/30/06		0.045						8/25/06		0.065																																		8/23/06		0.055

		7/12/06		0.05						5/30/06		0.05						8/25/06		0.065																																		8/24/06		0.05

		7/13/06		0.05						6/1/06		0.045						8/28/06		0.065																																		8/24/06		0.05

		7/17/06		0.06						6/1/06		0.05						8/28/06		0.065																																		8/25/06		0.05

		7/18/06		0.04						6/2/06		0.04						8/30/06		0.065																																		8/25/06		0.055

		7/19/06		0.04						6/5/06		0.05						8/30/06		0.063																																		8/26/06		0.05

		7/20/06		0.04						6/5/06		0.055						8/31/06		0.065																																		8/26/06		0.05

		7/21/06		0.033						6/6/06		0.055						8/31/06		0.065																																		8/28/06		0.05

		7/22/06		0.04						6/6/06		0.05						9/1/06		0.06																																		8/28/06		0.05

		7/23/06		0.04						6/7/06		0.055						9/1/06		0.065																																		8/29/06		0.05

		7/24/06		0.04						6/7/06		0.05						9/5/06		0.065																																		8/29/06		0.05

		7/25/06		0.04						6/8/06		0.05						9/5/06		0.065																																		8/30/06		0.05

		7/26/06		0.035						6/8/06		0.05						9/6/06		0.055																																		8/30/06		0.05

		7/26/06		0.04						6/9/06		0.045						9/6/06		0.065																																		8/31/06		0.05

		7/27/06		0.03						6/9/06		0.05						9/7/06		0.055																																		8/31/06		0.05

		7/27/06		0.04						6/12/06		0.01						9/7/06		0.063																																		9/1/06		0.055

		7/28/06		0.04						6/12/06		0.05						9/8/06		0.06																																		9/6/06		0.05

		7/31/06		0.03						6/13/06		0.01						9/8/06		0.063																																		9/6/06		0.05

		8/1/06		0.035						6/13/06		0.05						9/11/06		0.06																																		9/7/06		0.05

		8/2/06		0.03						6/14/06		0.05						9/11/06		0.065																																		9/7/06		0.05

		8/3/06		0.03						6/14/06		0.055						9/12/06		0.06																																		9/8/06		0.05

		8/4/06		0.03						6/15/06		0.055						9/12/06		0.065																																		9/8/06		0.05

		8/7/06		0.03						6/15/06		0.06						9/13/06		0.06																																		9/11/06		0.05

		8/8/06		0.03						6/16/06		0.05						9/13/06		0.065																																		9/11/06		0.05

		8/10/06		0.03						6/16/06		0.04						9/14/06		0.06																																		9/12/06		0.05

		8/10/06		0.05						6/17/06		0.045						9/14/06		0.065																																		9/12/06		0.06

		8/11/06		0.03						6/17/06		0.05						9/15/06		0.06																																		9/13/06		0.05

		8/11/06		0.05						6/19/06		0.05						9/15/06		0.065																																		9/13/06		0.055

		8/14/06		0.03						6/19/06		0.05						9/18/06		0.06																																		9/14/06		0.05

		8/15/06		0.03						6/20/06		0.05						9/18/06		0.063																																		9/14/06		0.04

		8/16/06		0.05						6/20/06		0.05						9/19/06		0.065																																		9/15/06		0.05

		8/16/06		0.03						6/21/06		0.04						9/19/06		0.055																																		9/15/06		0.05

		8/17/06		0.035						6/21/06		0.05						9/20/06		0.065																																		9/18/06		0.055

		8/17/06		0.03						6/22/06		0.04						9/20/06		0.06																																		9/18/06		0.06

		8/18/06		0.03						6/22/06		0.045						9/21/06		0.065																																		9/19/06		0.05

		8/18/06		0.03						6/26/06		0.04						9/21/06		0.062																																		9/19/06		0.055

		8/19/06		0.035						6/27/06		0.04						9/23/06		0.065																																		9/20/06		0.05

		8/19/06		0.03						6/28/06		0.04						9/23/06		0.062																																		9/20/06		0.05

		8/20/06		0.035						6/29/06		0.04						9/25/06		0.059																																		9/21/06		0.055

		8/21/06		0.03						7/5/06		0.04						9/25/06		0.06																																		9/21/06		0.055

		8/21/06		0.03						7/6/06		0.04						10/2/06		0.06																																		9/22/06		0.05

		8/22/06		0.025						7/7/06		0.05						10/2/06		0.05																																		9/22/06		0.055

		8/22/06		0.035						7/8/06		0.05						10/3/06		0.048																																		9/23/06		0.06

		8/23/06		0.035						7/10/06		0.03						10/3/06		0.042																																		9/23/06		0.06

		8/23/06		0.035						7/11/06		0.05						10/4/06		0.048																																		9/25/06		0.05

		8/24/06		0.035						7/12/06		0.04						10/6/06		0.038																																		9/25/06		0.055

		8/24/06		0.035						7/13/06		0.0425						10/9/06		0.055																																		9/26/06		0.05

		8/25/06		0.035						7/17/06		0.04						10/9/06		0.036																																		9/26/06		0.05

		8/25/06		0.035						7/18/06		0.05						10/10/06		0.037																																		9/27/06		0.05

		8/26/06		0.03						7/19/06		0.05						10/10/06		0.032																																		9/27/06		0.05

		8/26/06		0.035						7/20/06		0.05						10/11/06		0.032																																		9/28/06		0.05

		8/28/06		0.03						7/21/06		0.055						10/11/06		0.032																																		9/28/06		0.05

		8/28/06		0.03						7/22/06		0.055						10/12/06		0.033																																		9/29/06		0.05

		8/29/06		0.03						7/23/06		0.055						10/12/06		0.03																																		9/29/06		0.05

		8/29/06		0.03						7/24/06		0.055						10/13/06		0.031																																		10/2/06		0.055

		8/30/06		0.03						7/25/06		0.05						10/13/06		0.03																																		10/2/06		0.06

		8/30/06		0.035						7/26/06		0.055						10/16/06		0.033																																		10/3/06		0.05

		8/31/06		0.03						7/26/06		0.05						10/16/06		0.032																																		10/3/06		0.05

		8/31/06		0.03						7/27/06		0.05						10/17/06		0.032																																		10/4/06		0.055

		9/1/06		0.03						7/27/06		0.05						10/17/06		0.03																																		10/4/06		0.05

		9/5/06		0.03						7/28/06		0.05						10/18/06		0.033																																		10/5/06		0.05

		9/5/06		0.03						7/31/06		0.05						10/18/06		0.03																																		10/5/06		0.05

		9/6/06		0.02						8/1/06		0.05						10/19/06		0.025																																		10/9/06		0.05

		9/7/06		0.02						8/2/06		0.05						10/19/06		0.03																																		10/9/06		0.05

		9/8/06		0.03						8/3/06		0.05						10/20/06		0.03																																		10/10/06		0.05

		9/11/06		0.03						8/4/06		0.05						10/20/06		0.035																																		10/10/06		0.05

		9/11/06		0.03						8/7/06		0.05						10/23/06		0.032																																		10/11/06		0.05

		9/12/06		0.03						8/8/06		0.05						10/23/06		0.026																																		10/11/06		0.05

		9/12/06		0.03						8/11/06		0.03						10/24/06		0.029																																		10/12/06		0.05

		9/13/06		0.025						8/11/06		0.05						10/24/06		0.029																																		10/12/06		0.05

		9/13/06		0.03						8/14/06		0.05						10/26/06		0.03																																		10/13/06		0.05

		9/14/06		0.03						8/15/06		0.035						10/26/06		0.03																																		10/13/06		0.05

		9/15/06		0.03						8/16/06		0.05						10/30/06		0.025																																		10/14/06		0.05

		9/18/06		0.03						8/17/06		0.05						10/30/06		0.023																																		10/14/06		0.05

		9/19/06		0.03						8/17/06		0.05						10/31/06		0.025																																		10/16/06		0.05

		9/19/06		0.03						8/18/06		0.05						10/31/06		0.015																																		10/16/06		0.05

		9/20/06		0.03						8/18/06		0.05						11/1/06		0.026																																		10/17/06		0.05

		9/20/06		0.03						8/19/06		0.05						11/1/06		0.022																																		10/17/06		0.05

		9/21/06		0.02						8/19/06		0.05						11/2/06		0.025																																		10/18/06		0.05

		9/21/06		0.02						8/20/06		0.05						11/2/06		0.015																																		10/18/06		0.05

		9/22/06		0.02						8/21/06		0.05						11/3/06		0.025																																		10/19/06		0.05

		9/22/06		0.02						8/21/06		0.05						11/3/06		0.015																																		10/19/06		0.05

		9/23/06		0.02						8/22/06		0.045						11/6/06		0.025																																		10/20/06		0.05

		9/23/06		0.03						8/22/06		0.05						11/6/06		0.023																																		10/20/06		0.05

		9/25/06		0.02						8/23/06		0.05						11/7/06		0.02																																		10/23/06		0.05

		9/25/06		0.02						8/23/06		0.055						11/7/06		0.018																																		10/23/06		0.055

		9/26/06		0.02						8/24/06		0.05						11/8/06		0.04																																		10/24/06		0.05

		9/26/06		0.02						8/24/06		0.055						11/8/06		0.018																																		10/24/06		0.05

		9/27/06		0.02						8/25/06		0.05						11/9/06		0.02																																		10/25/06		0.05

		9/27/06		0.05						8/25/06		0.055						11/9/06		0.019																																		10/25/06		0.05

		9/28/06		0.03						8/26/06		0.05						11/10/06		0.02																																		10/26/06		0.05

		9/28/06		0.03						8/26/06		0.05						11/10/06		0.015																																		10/26/06		0.05

		9/29/06		0.02						8/28/06		0.05						11/13/06		0.02																																		10/27/06		0.05

		9/29/06		0.03						8/28/06		0.055						11/13/06		0.02																																		10/27/06		0.05

		10/2/06		0.04						8/29/06		0.05						11/14/06		0.02																																		10/28/06		0.05

		10/3/06		0.03						8/29/06		0.05						11/14/06		0.02																																		10/28/06		0.05

		10/3/06		0.03						8/30/06		0.05						11/15/06		0.02																																		10/30/06		0.05

		10/4/06		0.03						8/30/06		0.05						11/15/06		0.02																																		10/30/06		0.05

		10/4/06		0.03						8/31/06		0.05						11/16/06		0.02																																		10/31/06		0.05

		10/5/06		0.04						8/31/06		0.055						11/17/06		0.02																																		10/31/06		0.05

		10/5/06		0.03						9/1/06		0.05						11/17/06		0.018																																		11/1/06		0.05

		10/6/06		0.02						9/5/06		0.045						11/20/06		0.02																																		11/1/06		0.05

		10/7/06		0.05						9/5/06		0.05						11/20/06		0.015																																		11/2/06		0.05

		10/7/06		0.05						9/6/06		0.045						11/21/06		0.02																																		11/2/06		0.055

		10/9/06		0.04						9/7/06		0.05						11/21/06		0.012																																		11/3/06		0.045

		10/9/06		0.04						9/8/06		0.05						11/22/06		0.02																																		11/3/06		0.05

		10/10/06		0.02						9/11/06		0.05						11/22/06		0.02																																		11/6/06		0.05

		10/10/06		0.02						9/11/06		0.05						11/27/06		0.02																																		11/6/06		0.05

		10/11/06		0.03						9/12/06		0.05						11/27/06		0.04																																		11/7/06		0.05

		10/11/06		0.04						9/12/06		0.05						11/28/06		0.02																																		11/7/06		0.055

		10/12/06		0.035						9/13/06		0.05						11/28/06		0.01																																		11/8/06		0.05

		10/12/06		0.035						9/13/06		0.05						11/29/06		0.02																																		11/8/06		0.06

		10/13/06		0.04						9/14/06		0.05						11/29/06		0.015																																		11/9/06		0.05

		10/13/06		0.04						9/15/06		0.05						11/30/06		0.02																																		11/9/06		0.05

		10/14/06		0.04						9/18/06		0.05						11/30/06		0.015																																		11/10/06		0.05

		10/14/06		0.035						9/19/06		0.05						12/1/06		0.01																																		11/10/06		0.05

		10/16/06		0.04						9/19/06		0.05						12/1/06		0.012																																		11/13/06		0.05

		10/16/06		0.035						9/20/06		0.05						12/4/06		0.01																																		11/13/06		0.06

		10/17/06		0.03						9/20/06		0.05						12/4/06		0.015																																		11/14/06		0.06

		10/17/06		0.04						9/21/06		0.05						12/5/06		0.01																																		11/14/06		0.05

		10/18/06		0.03						9/21/06		0.05						12/5/06		0.015																																		11/15/06		0.055

		10/18/06		0.03						9/22/06		0.05						12/6/06		0.01																																		11/15/06		0.05

		10/19/06		0.025						9/22/06		0.05						12/6/06		0.01																																		11/16/06		0.055

		10/19/06		0.02						9/23/06		0.05						12/7/06		0.02																																		11/16/06		0.055

		10/20/06		0.035						9/23/06		0.05						12/7/06		0.01																																		11/17/06		0.05

		10/20/06		0.05						9/25/06		0.05						12/8/06		0.01																																		11/17/06		0.055

		10/21/06		0.04						9/25/06		0.05						12/8/06		0.01																																		11/18/06		0.05

		10/21/06		0.03						9/26/06		0.05						12/11/06		0.01																																		11/18/06		0.065

		10/23/06		0.035						9/26/06		0.05						12/11/06		0.015																																		11/20/06		0.05

		10/23/06		0.04						9/27/06		0.05						12/12/06		0.01																																		11/20/06		0.06

		10/24/06		0.02						9/27/06		0.02						12/12/06		0.015																																		11/21/06		0.05

		10/24/06		0.02						9/28/06		0.03						12/13/06		0.01																																		11/21/06		0.06

		10/25/06		0.035						9/28/06		0.03						12/13/06		0.015																																		11/22/06		0.05

		10/25/06		0.035						9/29/06		0.05						12/14/06		0.02																																		11/22/06		0.05

		10/26/06		0.025						9/29/06		0.05						12/18/06		0.01																																		11/27/06		0.05

		10/26/06		0.045						10/2/06		0.04						12/18/06		0.01																																		11/27/06		0.05

		10/27/06		0.03						10/3/06		0.05						12/19/06		0.01																																		11/28/06		0.055

		10/27/06		0.03						10/3/06		0.05						12/19/06		0.009																																		11/28/06		0.06

		10/28/06		0.03						10/4/06		0.05						12/20/06		0.01																																		11/29/06		0.05

		10/28/06		0.025						10/4/06		0.05						12/20/06		0.01																																		11/29/06		0.055

		10/30/06		0.035						10/5/06		0.04						12/21/06		0.01																																		11/30/06		0.05

		10/30/06		0.035						10/5/06		0.04						12/21/06		0.008																																		11/30/06		0.05

		10/31/06		0.03						10/6/06		0.03						12/22/06		0.01																																		12/1/06		0.05

		11/1/06		0.025						10/7/06		0.03						12/27/06		0.03																																		12/1/06		0.065

		11/2/06		0.035						10/7/06		0.03						12/28/06		0.01																																		12/2/06		0.05

		11/2/06		0.03						10/9/06		0.03						12/28/06		0.01																																		12/2/06		0.065

		11/3/06		0.02						10/9/06		0.03						12/29/06		0.01																																		12/4/06		0.045

		11/6/06		0.015						10/10/06		0.05						12/29/06		0.01																																		12/4/06		0.05

		11/7/06		0.02						10/10/06		0.05						1/2/07		0.01																																		12/5/06		0.045

		11/8/06		0.025						10/11/06		0.03						1/2/07		0.01																																		12/5/06		0.05

		11/9/06		0.03						10/11/06		0.04						1/3/07		0.01																																		12/6/06		0.05

		11/10/06		0.025						10/12/06		0.035						1/3/07		0.01																																		12/6/06		0.05

		11/11/06		0.035						10/12/06		0.035						1/4/07		0.01																																		12/7/06		0.05

		11/13/06		0.035						10/13/06		0.03						1/4/07		0.01																																		12/7/06		0.05

		11/13/06		0.02						10/13/06		0.04						1/5/07		0.01																																		12/8/06		0.05

		11/14/06		0.02						10/14/06		0.03						1/5/07		0.01																																		12/8/06		0.05

		11/14/06		0.02						10/14/06		0.035						1/8/07		0.01																																		12/9/06		0.05

		11/15/06		0.03						10/16/06		0.04						1/8/07		0.01																																		12/9/06		0.05

		11/15/06		0.035						10/16/06		0.04						1/9/07		0.01																																		12/11/06		0.05

		11/16/06		0.035						10/17/06		0.04						1/9/07		0.01																																		12/11/06		0.05

		11/17/06		0.03						10/17/06		0.04						1/10/07		0.01																																		12/12/06		0.05

		11/17/06		0.035						10/18/06		0.04						1/10/07		0.01																																		12/12/06		0.05

		11/18/06		0.03						10/18/06		0.04						1/11/07		0.02																																		12/13/06		0.055

		11/18/06		0.03						10/19/06		0.04						1/11/07		0.01																																		12/13/06		0.055

		11/20/06		0.045						10/19/06		0.04						1/12/07		0.01																																		12/14/06		0.04

		11/21/06		0.035						10/20/06		0.04						1/12/07		0.01																																		12/14/06		0.05

		11/22/06		0.025						10/20/06		0.04						1/15/07		0.02																																		12/15/06		0.05

		11/22/06		0.035						10/21/06		0.03						1/15/07		0.01																																		12/15/06		0.05

		11/27/06		0.03						10/21/06		0.04						1/16/07		0.01																																		2/28/07		0.04

		11/27/06		0.035						10/23/06		0.035						1/16/07		0.015																																		2/28/07		0.04

		11/28/06		0.015						10/23/06		0.04						1/17/07		0.01																																		3/1/07		0.04

		11/29/06		0.015						10/24/06		0.035						1/17/07		0.01																																		3/2/07		0.04

		11/30/06		0.025						10/24/06		0.035						1/18/07		0.01																																		3/3/07		0.04

		12/1/06		0.025						10/25/06		0.03						1/18/07		0.01																																		3/5/07		0.04

		12/2/06		0.025						10/25/06		0.045						1/19/07		0.01																																		3/6/07		0.04

		12/4/06		0.025						10/26/06		0.045						1/19/07		0.01																																		3/7/07		0.04

		12/5/06		0.03						10/26/06		0.04						1/22/07		0.01																																		3/8/07		0.04

		12/6/06		0.03						10/27/06		0.035						1/22/07		0.02																																		3/9/07		0.04

		12/6/06		0.03						10/27/06		0.03						1/23/07		0.01																																		3/12/07		0.045

		12/7/06		0.03						10/28/06		0.03						1/23/07		0.01																																		3/13/07		0.04

		12/7/06		0.035						10/28/06		0.05						1/24/07		0.01																																		3/14/07		0.04

		12/8/06		0.03						10/30/06		0.035						1/24/07		0.005																																		3/15/07		0.03

		12/8/06		0.03						10/30/06		0.035						1/25/07		0.01																																		3/16/07		0.04

		12/9/06		0.03						10/31/06		0.035						1/25/07		0.01																																		3/17/07		0.04

		12/11/06		0.03						11/1/06		0.035						1/26/07		0.01																																		3/19/07		0.03

		12/11/06		0.03						11/2/06		0.035						1/26/07		0.01																																		3/20/07		0.04

		12/12/06		0.03						11/2/06		0.04						1/29/07		0.01																																		3/21/07		0.04

		12/12/06		0.035						11/3/06		0.035						1/29/07		0.01																																		3/22/07		0.03

		12/13/06		0.03						11/6/06		0.05						1/30/07		0.01																																		3/23/07		0.03

		12/13/06		0.03						11/7/06		0.035						1/30/07		0.01																																		3/26/07		0.04

		12/14/06		0.03						11/8/06		0.04						1/31/07		0.01																																		3/27/07		0.03

		12/14/06		0.03						11/9/06		0.035						1/31/07		0.01																																		3/28/07		0.04

		12/15/06		0.03						11/10/06		0.045						2/1/07		0.01																																		3/29/07		0.03

		12/15/06		0.03						11/11/06		0.04						2/1/07		0.005																																		3/30/07		0.04

		12/18/06		0.03						11/13/06		0.04						2/2/07		0.01																																		3/31/07		0.03

		12/18/06		0.03						11/13/06		0.05						2/2/07		0.005																																		4/2/07		0.03

		12/19/06		0.03						11/14/06		0.04						2/5/07		0.01																																		4/3/07		0.045

		12/19/06		0.03						11/14/06		0.04						2/5/07		0.005																																		4/4/07		0.04

		12/20/06		0.03						11/15/06		0.03						2/6/07		0.01																																		4/5/07		0.04

		12/21/06		0.03						11/15/06		0.03						2/6/07		0.005																																		4/6/07		0.04

		12/21/06		0.03						11/16/06		0.03						2/7/07		0.01																																		4/9/07		0.04

		12/22/06		0.02						11/17/06		0.03						2/7/07		0.005																																		4/10/07		0.03

		12/22/06		0.035						11/17/06		0.035						2/8/07		0.01																																		4/11/07		0.04

		12/27/06		0.03						11/18/06		0.03						2/8/07		0.015																																		4/12/07		0.04

		12/27/06		0.03						11/18/06		0.03						2/9/07		0.01																																		4/13/07		0.035

		12/28/06		0.03						11/20/06		0.015						2/9/07		0.018																																		4/16/07		0.035

		12/28/06		0.03						11/21/06		0.03						2/12/07		0.01																																		4/17/07		0.04

		12/29/06		0.03						11/22/06		0.035						2/12/07		0.012																																		4/18/07		0.035

		12/29/06		0.035						11/22/06		0.035						2/13/07		0.01																																		4/19/07		0.04

		1/2/07		0.03						11/27/06		0.035						2/13/07		0.02																																		4/20/07		0.04

		1/2/07		0.03						11/27/06		0.03						2/14/07		0.02																																		4/23/07		0.03

		1/3/07		0.03						11/28/06		0.035						2/14/07		0.015																																		4/24/07		0.04

		1/3/07		0.03						11/29/06		0.035						2/15/07		0.02																																		4/25/07		0.035

		1/4/07		0.03						11/30/06		0.035						2/16/07		0.01																																		4/26/07		0.035

		1/5/07		0.03						12/1/06		0.03						2/20/07		0.015																																		4/27/07		0.035

		1/5/07		0.03						12/2/06		0.03						2/20/07		0.015																																		4/28/07		0.045

		1/8/07		0.03						12/4/06		0.03						2/21/07		0.02																																		4/30/07		0.04

		1/8/07		0.03						12/5/06		0.03						2/21/07		0.015																																		5/1/07		0.04

		1/9/07		0.03						12/6/06		0.03						2/22/07		0.02																																		5/2/07		0.04

		1/9/07		0.03						12/6/06		0.035						2/22/07		0.018																																		5/3/07		0.04

		1/10/07		0.03						12/7/06		0.03						2/23/07		0.02																																		5/4/07		0.04

		1/10/07		0.03						12/7/06		0.03						2/23/07		0.016																																		5/5/07		0.04

		1/11/07		0.03						12/8/06		0.03						2/26/07		0.015																																		5/7/07		0.035

		1/11/07		0.03						12/8/06		0.035						2/26/07		0.014																																		5/8/07		0.04

		1/12/07		0.03						12/9/06		0.03						2/27/07		0.015																																		5/9/07		0.045

		1/13/07		0.03						12/11/06		0.03						2/27/07		0.014																																		5/10/07		0.04

		1/13/07		0.03						12/11/06		0.03						2/28/07		0.01																																		5/11/07		0.035

		1/15/07		0.03						12/12/06		0.03						3/1/07		0.015																																		5/14/07		0.03

		1/15/07		0.03						12/12/06		0.03						3/2/07		0.015																																		5/15/07		0.035

		1/16/07		0.03						12/13/06		0.03						3/5/07		0.01																																		5/16/07		0.045

		1/16/07		0.025						12/13/06		0.03						3/6/07		0.01																																		5/17/07		0.035

		1/17/07		0.02						12/14/06		0.03						3/7/07		0.04																																		5/18/07		0.04

		1/18/07		0.02						12/14/06		0.035						3/8/07		0.04																																		5/19/07		0.04

		1/19/07		0.03						12/15/06		0.03						3/9/07		0.04																																		5/21/07		0.04

		1/19/07		0.03						12/15/06		0.035						3/12/07		0.04																																		5/22/07		0.04

		1/20/07		0.03						12/18/06		0.03						3/13/07		0.04																																		5/23/07		0.045

		1/22/07		0.03						12/18/06		0.03						3/14/07		0.04																																		5/24/07		0.04

		1/23/07		0.03						12/19/06		0.03						3/15/07		0.035																																		5/29/07		0.03

		1/24/07		0.03						12/19/06		0.03						3/16/07		0.04																																		5/30/07		0.03

		1/24/07		0.03						12/20/06		0.03						3/19/07		0.035																																		5/31/07		0.035

		1/25/07		0.03						12/21/06		0.03						3/20/07		0.035																																		6/1/07		0.035

		1/25/07		0.03						12/21/06		0.035						3/21/07		0.035																																		6/2/07		0.05

		1/26/07		0.03						12/22/06		0.03						3/22/07		0.032																																		6/4/07		0.035

		1/26/07		0.035						12/22/06		0.03						3/23/07		0.03																																		6/5/07		0.04

		1/29/07		0.03						12/27/06		0.03						3/26/07		0.03																																		6/6/07		0.04

		1/29/07		0.035						12/27/06		0.03						3/27/07		0.03																																		6/7/07		0.04

		1/30/07		0.035						12/28/06		0.03						3/28/07		0.035																																		6/8/07		0.045

		1/30/07		0.035						12/28/06		0.035						3/29/07		0.035																																		6/9/07		0.04

		1/31/07		0.03						12/29/06		0.03						3/30/07		0.03																																		6/11/07		0.04

		1/31/07		0.035						12/29/06		0.035						4/2/07		0.03																																		6/12/07		0.04

		2/1/07		0.03						1/2/07		0.03						4/3/07		0.025																																		6/13/07		0.04

		2/1/07		0.03						1/2/07		0.03						4/4/07		0.03																																		6/14/07		0.035

		2/2/07		0.03						1/3/07		0.03						4/5/07		0.025																																		6/15/07		0.045

		2/2/07		0.03						1/3/07		0.03						4/6/07		0.03																																		6/16/07		0.05

		2/3/07		0.03						1/4/07		0.03						4/9/07		0.025																																		6/19/07		0.04

		2/3/07		0.035						1/5/07		0.03						4/10/07		0.03																																		6/20/07		0.04

		2/5/07		0.03						1/5/07		0.03						4/11/07		0.03																																		6/21/07		0.035

		2/5/07		0.03						1/8/07		0.03						4/12/07		0.03																																		6/22/07		0.04

		2/6/07		0.03						1/8/07		0.03						4/13/07		0.028																																		6/23/07		0.04

		2/6/07		0.03						1/9/07		0.03						4/16/07		0.032																																		6/25/07		0.04

		2/7/07		0.05						1/9/07		0.03						4/17/07		0.03																																		6/26/07		0.04

		2/7/07		0.04						1/10/07		0.03						4/18/07		0.025																																		6/27/07		0.04

		2/8/07		0.04						1/10/07		0.035						4/19/07		0.025																																		6/28/07		0.04

		2/8/07		0.03						1/11/07		0.03						4/23/07		0.04																																		6/29/07		0.04

		2/10/07		0.03						1/11/07		0.03						4/24/07		0.044																																		7/2/07		0.04

		2/10/07		0.05						1/12/07		0.03						4/25/07		0.049																																		7/3/07		0.045

		2/12/07		0.03						1/13/07		0.03						4/26/07		0.049																																		7/5/07		0.05

		2/13/07		0.035						1/13/07		0.03						4/27/07		0.045																																		7/6/07		0.05

		2/13/07		0.04						1/15/07		0.03						4/30/07		0.045																																		7/9/07		0.045

		2/14/07		0.04						1/15/07		0.03						5/1/07		0.042																																		7/10/07		0.07

		2/14/07		0.04						1/16/07		0.03						5/2/07		0.045																																		7/11/07		0.045

		2/15/07		0.05						1/16/07		0.03						5/3/07		0.042																																		7/12/07		0.055

		2/15/07		0.04						1/17/07		0.03						5/4/07		0.045																																		7/13/07		0.05

		2/16/07		0.04						1/18/07		0.03						5/7/07		0.045																																		7/14/07		0.05

		2/16/07		0.04						1/19/07		0.035						5/8/07		0.045																																		7/16/07		0.055

		2/20/07		0.05						1/19/07		0.03						5/9/07		0.045																																		7/17/07		0.05

		2/20/07		0.05						1/20/07		0.03						5/10/07		0.045																																		7/18/07		0.075

		2/21/07		0.04						1/22/07		0.03						5/11/07		0.045																																		7/19/07		0.07

		2/21/07		0.055						1/23/07		0.03						5/14/07		0.046																																		7/20/07		0.07

		2/22/07		0.04						1/24/07		0.03						5/15/07		0.05																																		7/23/07		0.07

		2/22/07		0.05						1/24/07		0.03						5/16/07		0.055																																		7/24/07		0.07

		2/23/07		0.03						1/25/07		0.03						5/17/07		0.045																																		7/25/07		0.065

		2/23/07		0.05						1/25/07		0.03						5/18/07		0.04																																		7/26/07		0.055

		2/26/07		0.05						1/26/07		0.03						5/21/07		0.044																																		7/27/07		0.06

		2/26/07		0.04						1/26/07		0.035						5/22/07		0.045																																		7/28/07		0.065

		2/27/07		0.03						1/29/07		0.035						5/23/07		0.045																																		7/30/07		0.05

		2/27/07		0.04						1/29/07		0.035						5/24/07		0.04																																		7/31/07		0.06

		2/28/07		0.03						1/30/07		0.03						5/24/07		0.04																																		8/1/07		0.06

		2/28/07		0.03						1/30/07		0.03						5/29/07		0.025																																		8/2/07		0.06

		3/1/07		0.04						1/31/07		0.03						5/30/07		0.045																																		8/3/07		0.06

		3/2/07		0.04						1/31/07		0.035						5/31/07		0.05																																		8/6/07		0.06

		3/5/07		0.04						2/1/07		0.035						6/1/07		0.051																																		8/7/07		0.06

		3/6/07		0.04						2/1/07		0.03						6/4/07		0.044																																		8/8/07		0.05

		3/7/07		0.04						2/2/07		0.03						6/5/07		0.047																																		8/9/07		0.05

		3/8/07		0.04						2/2/07		0.03						6/6/07		0.046																																		8/10/07		0.05

		3/9/07		0.04						2/3/07		0.03						6/7/07		0.05																																		8/11/07		0.05

		3/12/07		0.04						2/3/07		0.03						6/8/07		0.048																																		8/13/07		0.06

		3/13/07		0.03						2/5/07		0.03						6/9/07		0.049																																		8/14/07		0.05

		3/14/07		0.03						2/5/07		0.03						6/11/07		0.049																																		8/15/07		0.05

		3/15/07		0.04						2/6/07		0.03						6/12/07		0.05																																		8/16/07		0.055

		3/16/07		0.04						2/6/07		0.035						6/13/07		0.045																																		8/17/07		0.055

		3/19/07		0.03						2/7/07		0.03						6/14/07		0.048																																		8/20/07		0.05

		3/20/07		0.04						2/7/07		0.03						6/15/07		0.045																																		8/21/07		0.05

		3/21/07		0.035						2/8/07		0.03						6/18/07		0.045																																		8/22/07		0.05

		3/22/07		0.04						2/8/07		0.03						6/19/07		0.045																																		8/23/07		0.05

		3/23/07		0.04						2/10/07		0.03						6/20/07		0.045																																		8/24/07		0.05

		3/26/07		0.035						2/10/07		0.04						6/21/07		0.045																																		8/27/07		0.05

		3/27/07		0.04						2/12/07		0.03						6/25/07		0.042																																		8/28/07		0.05

		3/28/07		0.035						2/13/07		0.035						6/26/07		0.045																																		8/29/07		0.05

		3/29/07		0.035						2/13/07		0.05						6/27/07		0.04																																		8/30/07		0.05

		3/30/07		0.03						2/14/07		0.04						6/28/07		0.063																																		8/31/07		0.05

		3/31/07		0.035						2/14/07		0.04						6/29/07		0.061																																		9/4/07		0.05

		4/2/07		0.04						2/15/07		0.05						7/2/07		0.06																																		9/5/07		0.05

		4/3/07		0.035						2/15/07		0.04						7/3/07		0.062																																		9/6/07		0.05

		4/4/07		0.035						2/16/07		0.04						7/5/07		0.06																																		9/7/07		0.055

		4/5/07		0.035						2/16/07		0.04						7/6/07		0.058																																		9/10/07		0.045

		4/6/07		0.035						2/20/07		0.05						7/9/07		0.06																																		9/11/07		0.05

		4/9/07		0.035						2/20/07		0.05						7/10/07		0.06																																		9/12/07		0.05

		4/10/07		0.03						2/21/07		0.04						7/11/07		0.055																																		9/13/07		0.045

		4/11/07		0.03						2/21/07		0.035						7/12/07		0.056																																		9/14/07		0.05

		4/12/07		0.03						2/22/07		0.04						7/13/07		0.056																																		9/17/07		0.05

		4/13/07		0.03						2/22/07		0.04						7/16/07		0.055																																		9/18/07		0.045

		4/14/07		0.03						2/23/07		0.03						7/17/07		0.05																																		9/19/07		0.05

		4/16/07		0.03						2/23/07		0.04						7/18/07		0.045																																		9/20/07		0.05

		4/17/07		0.03						2/26/07		0.03						7/19/07		0.045																																		9/21/07		0.05

		4/18/07		0.025						2/26/07		0.035						7/20/07		0.04																																		9/22/07		0.05

		4/19/07		0.03						2/27/07		0.03						7/23/07		0.04																																		9/24/07		0.05

		4/20/07		0.035						2/27/07		0.03						7/24/07		0.04																																		9/25/07		0.05

		4/21/07		0.035						2/28/07		0.03						7/25/07		0.04																																		9/26/07		0.05

		4/23/07		0.025						3/1/07		0.03						7/26/07		0.04																																		9/27/07		0.05

		4/24/07		0.02						3/2/07		0.03						7/28/07		0.04																																		9/28/07		0.05

		4/25/07		0.03						3/5/07		0.03						7/30/07		0.044																																		10/1/07		0.05

		4/26/07		0.04						3/6/07		0.03						7/31/07		0.044																																		10/2/07		0.06

		4/27/07		0.025						3/7/07		0.04						8/1/07		0.04																																		10/3/07		0.05

		4/30/07		0.025						3/8/07		0.04						8/2/07		0.04																																		10/4/07		0.05

		5/1/07		0.03						3/9/07		0.04						8/3/07		0.04																																		10/5/07		0.045

		5/2/07		0.02						3/12/07		0.04						8/4/07		0.042																																		10/8/07		0.05

		5/3/07		0.02						3/13/07		0.04						8/6/07		0.04																																		10/9/07		0.05

		5/4/07		0.02						3/14/07		0.03						8/7/07		0.04																																		10/10/07		0.05

		5/5/07		0.02						3/15/07		0.035						8/8/07		0.034																																		10/11/07		0.05

		5/7/07		0.02						3/16/07		0.035						8/9/07		0.032																																		10/12/07		0.05

		5/8/07		0.025						3/19/07		0.035						8/10/07		0.043																																		10/15/07		0.05

		5/9/07		0.03						3/20/07		0.04						8/13/07		0.045																																		10/16/07		0.045

		5/10/07		0.025						3/21/07		0.04						8/14/07		0.045																																		10/17/07		0.05

		5/11/07		0.005						3/22/07		0.04						8/15/07		0.043																																		10/18/07		0.05

		5/14/07		0.035						3/23/07		0.035						8/16/07		0.04																																		10/19/07		0.045

		5/15/07		0.035						3/26/07		0.035						8/17/07		0.04																																		10/22/07		0.05

		5/16/07		0.03						3/27/07		0.04						8/20/07		0.04																																		10/23/07		0.05

		5/17/07		0.03						3/28/07		0.04						8/21/07		0.03																																		10/24/07		0.045

		5/18/07		0.03						3/29/07		0.035						8/22/07		0.04																																		10/25/07		0.045

		5/19/07		0.03						3/30/07		0.03						8/23/07		0.04																																		10/26/07		0.05

		5/21/07		0.025						3/31/07		0.035						8/24/07		0.04																																		10/29/07		0.05

		5/22/07		0.025						4/2/07		0.035						8/27/07		0.045																																		10/30/07		0.045

		5/23/07		0.025						4/3/07		0.035						8/28/07		0.04																																		10/31/07		0.05

		5/24/07		0.02						4/4/07		0.04						8/29/07		0.055																																		11/1/07		0.045

		5/25/07		0.025						4/5/07		0.04						8/30/07		0.055																																		11/2/07		0.05

		5/29/07		0.025						4/6/07		0.04						8/31/07		0.05																																		11/5/07		0.05

		5/30/07		0.048						4/9/07		0.035						9/4/07		0.05																																		11/6/07		0.045

		5/31/07		0.04						4/10/07		0.035						9/5/07		0.04						0.61		0.4																										11/7/07		0.05

		6/1/07		0.025						4/11/07		0.04						9/6/07		0.05						0.61		0.41																										11/8/07		0.05

		6/2/07		0.03						4/12/07		0.035						9/7/07		0.045						0.6		0.41																										11/9/07		0.05

		6/4/07		0.03						4/13/07		0.035						9/8/07		0.04						0.6		0.41																										11/12/07		0.045

		6/5/07		0.0175						4/14/07		0.03						9/10/07		0.055						0.61		0.41																										11/13/07		0.05

		6/6/07		0.03						4/16/07		0.035						9/11/07		0.05						0.61		0.41																										11/14/07		0.045

		6/7/07		0.04						4/17/07		0.035						9/12/07		0.05						0.61		0.41																										11/15/07		0.045

		6/8/07		0.025						4/18/07		0.04						9/13/07		0.05						0.61		0.41																										11/16/07		0.045

		6/9/07		0.02						4/19/07		0.035						9/14/07		0.05						0.6		0.42																										11/19/07		0.045

		6/11/07		0.04						4/20/07		0.04						9/15/07		0.05						0.6		0.4																										11/20/07		0.045

		6/12/07		0.02						4/21/07		0.035						9/17/07		0.054						0.6		0.41																										11/21/07		0.045

		6/13/07		0.03						4/23/07		0.035						9/18/07		0.054						0.61		0.41																										11/26/07		0.045

		6/14/07		0.025						4/24/07		0.02						9/19/07		0.045						0.65		0.4																										11/27/07		0.045

		6/15/07		0.02						4/25/07		0.04						9/20/07		0.045						0.61		0.41																										11/28/07		0.045

		6/18/07		0.025						4/26/07		0.035						9/21/07		0.04						0.6		0.4																										11/29/07		0.045

		6/19/07		0.02						4/27/07		0.04						9/24/07		0.035						0.6		0.4																										11/30/07		0.045

		6/20/07		0.03						4/30/07		0.025						9/25/07		0.04						0.62		0.4																										12/1/07		0.045

		6/21/07		0.016						5/1/07		0.03						9/26/07		0.04						0.62		0.42																										12/3/07		0.045

		6/22/07		0.025						5/2/07		0.03						9/27/07		0.04						0.62		0.42																										12/4/07		0.045

		6/25/07		0.02						5/3/07		0.03						9/28/07		0.05						0.6		0.4																										12/5/07		0.045

		6/26/07		0.025						5/4/07		0.035						10/1/07		0.04						0.62		0.42																										12/6/07		0.045

		6/27/07		0.03						5/5/07		0.035						10/2/07		0.045						0.62		0.42																										12/7/07		0.045

		6/28/07		0.045						5/7/07		0.04						10/3/07		0.045						0.62		0.42																										12/8/07		0.045

		6/29/07		0.025						5/8/07		0.045						10/4/07		0.05						0.61		0.42																										12/10/07		0.045

		7/2/07		0.04						5/9/07		0.03						10/5/07		0.05						0.62		0.42																										12/11/07		0.04

		7/3/07		0.04						5/10/07		0.04						10/8/07		0.05						0.62		0.42																										12/12/07		0.04

		7/5/07		0.04						5/11/07		0.03						10/9/07		0.04						0.62		0.42																										12/13/07		0.04

		7/6/07		0.04						5/14/07		0.03						10/10/07		0.04						0.62		0.42																										12/14/07		0.04

		7/9/07		0.04						5/15/07		0.03						10/11/07		0.05						0.62		0.42																										12/17/07		0.04

		7/10/07		0.03						5/16/07		0.03						10/12/07		0.045						0.62		0.42																										12/18/07		0.045

		7/11/07		0.035						5/17/07		0.03						10/13/07		0.04						0.62		0.42																										12/19/07		0.04

		7/12/07		0.035						5/18/07		0.03						10/15/07		0.04						0.61		0.41																										12/20/07		0.04

		7/13/07		0.03						5/19/07		0.03						10/16/07		0.04						0.62		0.42																										12/26/07		0.04

		7/16/07		0.03						5/21/07		0.03						10/17/07		0.04						0.61		0.41																										12/27/07		0.04

		7/17/07		0.035						5/22/07		0.03						10/18/07		0.04						0.62		0.42																										12/28/07		0.04

		7/18/07		0.03						5/23/07		0.03						10/19/07		0.04						0.62		0.42																										12/31/07		0.05

		7/19/07		0.03						5/24/07		0.03						10/22/07		0.045						0.62		0.42																										1/2/08		0.04

		7/20/07		0.03						5/25/07		0.03						10/23/07		0.05						0.64		0.44																										1/3/08		0.04

		7/23/07		0.04						5/29/07		0.035						10/24/07		0.045						0.62		0.42																										1/4/08		0.04

		7/24/07		0.035						5/30/07		0.02						10/25/07		0.03						0.62		0.42																										1/7/08		0.04

		7/25/07		0.035						5/31/07		0.03						10/26/07		0.035						0.62		0.42																										1/8/08		0.04

		7/26/07		0.04						6/1/07		0.03						10/29/07		0.03						0.62		0.42																										1/9/08		0.04

		7/27/07		0.04						6/2/07		0.03						10/30/07		0.025						0.62		0.42																										1/10/08		0.04

		7/30/07		0.035						6/4/07		0.03						10/31/07		0.03						0.62		0.42																										1/11/08		0.04

		7/31/07		0.035						6/5/07		0.04						11/1/07		0.035						0.62		0.42																										1/14/08		0.04

		8/1/07		0.03						6/6/07		0.025						11/2/07		0.035						0.62		0.42																										1/15/08		0.04

		8/2/07		0.035						6/7/07		0.03						11/5/07		0.025						0.62		0.4																										1/16/08		0.04

		8/3/07		0.04						6/8/07		0.03						11/6/07		0.04						0.62		0.41																										1/17/08		0.04

		8/4/07		0.03						6/9/07		0.025						11/7/07		0.02						0.62		0.42																										1/18/08		0.04

		8/6/07		0.03						6/11/07		0.03						11/8/07		0.03						0.62		0.42																										1/21/08		0.04

		8/7/07		0.035						6/12/07		0.02						11/9/07		0.02						0.62		0.42																										1/22/08		0.04

		8/8/07		0.03						6/13/07		0.03						11/12/07		0.035						0.62		0.42																										1/23/08		0.04

		8/9/07		0.03						6/14/07		0.025						11/13/07		0.04						0.62		0.4																										1/24/08		0.04

		8/10/07		0.04						6/15/07		0.025						11/14/07		0.04						0.62		0.42																										1/25/08		0.045

		8/13/07		0.03						6/18/07		0.03						11/15/07		0.04						0.62		0.42																										1/28/08		0.04

		8/14/07		0.03						6/19/07		0.025						11/16/07		0.035						0.62		0.42																										1/29/08		0.04

		8/15/07		0.03						6/20/07		0.03						11/19/07		0.045						0.66		0.44																										1/30/08		0.04

		8/17/07		0.03						6/21/07		0.03						11/20/07		0.04						0.64		0.42																										1/31/08		0.04

		8/20/07		0.03						6/22/07		0.02						11/21/07		0.04						0.64		0.42																										2/1/08		0.04

		8/21/07		0.03						6/25/07		0.02						11/26/07		0.04						0.66		0.44																										2/4/08		0.04

		8/22/07		0.03						6/26/07		0.02						11/27/07		0.042						0.66		0.44																										2/5/08		0.04

		8/23/07		0.03						6/27/07		0.03						11/28/07		0.04						0.66		0.44																										2/6/08		0.04

		8/24/07		0.03						6/28/07		0.03						11/29/07		0.03						0.64		0.44																										2/7/08		0.04

		8/25/07		0.02						6/29/07		0.04						11/30/07		0.03						0.64		0.44																										2/8/08		0.04

		8/27/07		0.04						7/2/07		0.03						12/3/07		0.04						0.64		0.44																										2/11/08		0.04

		8/28/07		0.035						7/3/07		0.025						12/4/07		0.03						0.64		0.42																										2/12/08		0.04

		8/29/07		0.04						7/5/07		0.03						12/5/07		0.03						0.64		0.44																										2/13/08		0.04

		8/30/07		0.03						7/6/07		0.025						12/6/07		0.03						0.64		0.42																										2/14/08		0.04

		8/31/07		0.03						7/9/07		0.025						12/7/07		0.03						0.64		0.44																										2/15/08		0.04

		9/4/07		0.03						7/10/07		0.03						12/10/07		0.03						0.64		0.44																										2/16/08		0.04

		9/5/07		0.03						7/11/07		0.035						12/11/07		0.03						0.66		0.42																										2/19/08		0.04

		9/6/07		0.035						7/12/07		0.035						12/12/07		0.03						0.6		0.42																										2/20/08		0.045

		9/7/07		0.02						7/13/07		0.03						12/13/07		0.045						0.66		0.42																										2/21/08		0.04

		9/8/07		0.04						7/16/07		0.03						12/14/07		0.03						0.66		0.42																										2/22/08		0.04

		9/10/07		0.025						7/17/07		0.03						12/17/07		0.03						0.64		0.42																										2/25/08		0.04

		9/11/07		0.035						7/18/07		0.025						12/18/07		0.03						0.66		0.4																										2/26/08		0.04

		9/12/07		0.035						7/19/07		0.025						12/19/07		0.02						0.66		0.42																										2/27/08		0.04

		9/13/07		0.03						7/20/07		0.035						12/20/07		0.03						0.64		0.42																										2/28/08		0.04

		9/14/07		0.03						7/23/07		0.03						12/21/07		0.04						0.66		0.42																										2/29/08		0.04

		9/17/07		0.03						7/24/07		0.025						12/26/07		0.03						0.64		0.42																										3/1/08		0.04

		9/18/07		0.025						7/25/07		0.035						12/27/07		0.025						0.62		0.44																										3/2/08		0.04

		9/19/07		0.04						7/26/07		0.03						12/28/07		0.025						0.64		0.44																										3/3/08		0.04

		9/20/07		0.04						7/27/07		0.03						12/31/07		0.02						0.64		0.44																										3/4/08		0.04

		9/21/07		0.03						7/30/07		0.035																																										3/5/08		0.04

		9/24/07		0.025						7/31/07		0.04						2/14/08		0.04						0.292		0.309		0.485		61		1180																				3/6/08		0.04

		9/25/07		0.035						8/1/07		0.03						2/15/08		0.037		69		50		0.28		0.31		0.414		61		1172																				3/7/08		0.04

		9/26/07		0.025						8/2/07		0.035						2/19/08		0.035		69		48		0.293		0.309		0.426		60		1184																				3/8/08		0.04

		9/27/07		0.02						8/3/07		0.03						2/20/08		0.03		70		46		0.26		0.309		0.41		63		1184																				3/10/08		0.04

		9/28/07		0.02						8/4/07		0.03						2/21/08		0.032		70		46		0.29		0.305		0.441		62		1164																				3/11/08		0.04

		9/29/07		0.02						8/6/07		0.03						2/22/08		0.031		70		45		0.281		0.307		0.419		62		1184																				3/12/08		0.04

		10/1/07		0.015						8/7/07		0.025						2/25/08		0.069		70		46		0.288		0.311		0.421		63		1184																				3/13/08		0.04

		10/2/07		0.035						8/8/07		0.03						2/26/08		0.068		70		44		0.281		0.312		0.413		64		1192																				3/14/08		0.04

		10/3/07		0.03						8/9/07		0.045						2/27/08		0.067		70		45		0.288		0.311		0.413		62		1184																				3/15/08		0.04

		10/4/07		0.04						8/10/07		0.04						2/28/08		0.063		70		46		0.283		0.31		0.457		62		1172																				3/17/08		0.04

		10/5/07		0.025						8/13/07		0.04						2/29/08		0.064		70		45		0.256		0.311		0.409		63		1184																				3/18/08		0.04

		10/8/07		0.03						8/14/07		0.04						3/3/08		0.07		70		33		0.285		0.311		0.435		63		1204																				3/19/08		0.04

		10/9/07		0.03						8/15/07		0.04						3/4/08		0.07		70		44		0.261		0.311		0.438		63		1184																				3/20/08		0.04

		10/10/07		0.03						8/17/07		0.04						3/5/08		0.069		70		44		0.291		0.311		0.445		63		1184																				3/21/08		0.04

		10/11/07		0.03						8/20/07		0.03						3/6/08		0.068		70		44		0.281		0.311		0.458		61		1184																				3/22/08		0.04

		10/12/07		0.02						8/21/07		0.03						3/7/08		0.067		70		44		0.282		0.322		0.455		63		1192																				3/24/08		0.04

		10/15/07		0.03						8/22/07		0.035						3/10/08		0.069		70		46		0.264		0.321		0.428		64		1184																				3/25/08		0.04

		10/16/07		0.02						8/23/07		0.03						3/11/08		0.071		70		43		0.285		0.322		0.438		63		1204																				3/26/08		0.045

		10/17/07		0.04						8/24/07		0.035						3/12/08		0.056		70		44		0.261		0.312		0.422		62		1188																				3/27/08		0.04		70		25

		10/18/07		0.04						8/25/07		0.02						3/14/08		0.067		70		43		0.261		0.321		0.451		63		1184																				3/28/08		0.04		70		41

		10/19/07		0.025						8/27/07		0.025						3/17/08		0.069		70		45		0.26		0.32		0.439		63		1196																				3/31/08		0.04		70		28

		10/22/07		0.03						8/28/07		0.025						3/18/08		0.062		70		47		0.279		0.32		0.422		63		1196																				4/1/08		0.04		70		29

		10/23/07		0.03						8/29/07		0.03						3/19/08		0.053		70		44		0.273		0.321		0.419		64		1192																				4/2/08		0.055		70		36

		10/24/07		0.04						8/30/07		0.03						3/20/08		0.064		70		33		0.262		0.321		0.431		64		1192																				4/3/08		0.04		69		40

		10/25/07		0.035						8/31/07		0.03						3/21/08		0.063		70		35		0.277		0.322		0.439		63		1196																				4/4/08		0.045		70		44

		10/26/07		0.045						9/4/07		0.03						3/24/08		0.052		70		42		0.238		0.321		0.418		63		1184																				4/5/08		0.04		70		41

		10/29/07		0.02						9/5/07		0.03						3/25/08		0.057		70		38		0.264		0.319		0.445		63		1192																				4/7/08		0.05		70		44

		10/30/07		0.02						9/6/07		0.03						3/26/08		0.056		70		35		0.276		0.321		0.447		63		1204																				4/8/08		0.05		70		44

		10/31/07		0.02						9/7/07		0.03						3/27/08		0.07		70		24		0.28		0.32		0.46		63		1204																				4/9/08		0.05		70		44

		11/1/07		0.03						9/8/07		0.03						3/28/08		0.05		70		40		0.26		0.32		0.44		63		1192																				4/10/08		0.05		70		44

		11/2/07		0.025						9/10/07		0.02						3/31/08		0.06		70		27		0.3		0.32		0.48		63		1204																				4/11/08		0.05		70		46

		11/5/07		0.03						9/11/07		0.02						4/1/08		0.06		70		28		0.28		0.32		0.46		61		1192																				4/14/08		0.05		72		41

		11/6/07		0.025						9/12/07		0.03						4/2/08		0.06		70		30		0.28		0.32		0.44		63		1204																				4/15/08		0.05		74		42

		11/7/07		0.025						9/13/07		0.02						4/3/08		0.06		70		38		0.28		0.32		0.44		64		1192																				4/16/08		0.05		70		45

		11/8/07		0.085						9/14/07		0.035						4/4/08		0.05		70		44		0.26		0.32		0.44		63		1196																				4/17/08		0.045		72		46

		11/9/07		0.08						9/17/07		0.03						4/5/08		0.05		70		40		0.26		0.32		0.44		63		1196																				4/18/08		0.04		70		48

		11/12/07		0.075						9/18/07		0.03						4/7/08		0.055		70		44		0.26		0.32		0.46		65		1204																				4/19/08		0.05		69		48

		11/13/07		0.08						9/19/07		0.04						4/8/08		0.055		70		44		0.28		0.32		0.44		61		1192																				4/21/08		0.05		73		47

		11/14/07		0.075						9/20/07		0.04						4/9/08		0.055		70		46		0.28		0.32		0.44		63		1196																				4/22/08		0.045		77		46

		11/15/07		0.075						9/21/07		0.03						4/10/08		0.05		70		45		0.28		0.32		0.44		61		1204																				4/23/08		0.05		71		45

		11/16/07		0.07						9/24/07		0.025						4/11/08		0.05		70		42		0.28		0.32		0.44		61		1192																				4/24/08		0.045		73		46

		11/19/07		0.075						9/25/07		0.025						4/14/08		0.05		70		43		0.28		0.32		0.46		61		1196																				4/25/08		0.04		70		46

		11/20/07		0.07						9/26/07		0.03						4/15/08		0.05		73		41		0.28		0.32		0.44		62		1196																				4/30/08		0.06		69		26

		11/21/07		0.075						9/27/07		0.03						4/16/08		0.05		72		43		0.28		0.32		0.48		62		1196																				5/1/08		0.04		75		42

		11/26/07		0.08						9/28/07		0.03						4/17/08		0.05		72		44		0.28		0.32		0.48		62		1196																				5/2/08		0.04		72		35

		11/27/07		0.08						9/29/07		0.025						4/18/08		0.05		72		45		0.28		0.32		0.48		62		1196																				5/3/08		0.04		78		34

		11/28/07		0.08						10/1/07		0.03						4/19/08		0.06		72		44		0.28		0.32		0.48		62		1196																				5/5/08		0.04		71		40

		11/29/07		0.075						10/2/07		0.025						4/21/08		0.055		71		45		0.28		0.32		0.46		64		1196																				5/6/08		0.045		75		40

		11/30/07		0.08						10/3/07		0.03						4/22/08		0.05		72		43		0.28		0.32		0.46		64		1196																				5/7/08		0.05		72		36

		12/3/07		0.07						10/4/07		0.03						4/23/08		0.05		73		42		0.28		0.32		0.48		63		1196																				5/8/08		0.045		72		38

		12/4/07		0.08						10/5/07		0.02						4/24/08		0.055		73		45		0.28		0.32		0.46		63		1196																				5/9/08		0.04		74		34

		12/5/07		0.07						10/8/07		0.03						4/25/08		0.05		73		41		0.26		0.32		0.44		63		1204																				5/10/08		0.045		72		34

		12/6/07		0.08						10/9/07		0.02						4/28/08								0.26		0.32		0.44		63		1204																				5/12/08		0.055		69		28

		12/7/07		0.075						10/10/07		0.025						4/29/08								0.28		0.32		0.44		60		1184																				5/13/08		0.04		75		31

		12/10/07		0.075						10/11/07		0.03						4/30/08		0.06		70		25		0.28		0.32		0.46		60		1192																				5/14/08		0.05		71		38

		12/11/07		0.075						10/12/07		0.02						5/1/08		0.055		73		39		0.28		0.32		0.46		60		1196																				5/15/08		0.04		72		42

		12/12/07		0.075						10/15/07		0.025						5/2/08		0.045		72		34		0.28		0.32		0.46		60		1210																				5/16/08		0.04		71		48

		12/13/07		0.075						10/16/07		0.025						5/3/08		0.05		73		38		0.28		0.32		0.46		60		1210																				5/19/08		0.04		75		42

		12/14/07		0.075						10/17/07		0.03						5/5/08		0.04		72		38		0.28		0.32		0.44		60		1192																				5/20/08		0.04		73		44

		12/17/07		0.08						10/18/07		0.025						5/6/08		0.04		73		42		0.28		0.32		0.44		60		1184																				5/21/08		0.04		71		36

		12/18/07		0.075						10/19/07		0.025						5/7/08		0.04		73		37		0.28		0.32		0.44		62		1196																				5/22/08		0.04		73		30

		12/19/07		0.08						10/22/07		0.025						5/8/08		0.04		73		35		0.28		0.32		0.44		60		1196																				5/23/08		0.04		71		36

		12/20/07		0.08						10/23/07		0.02						5/9/08		0.04		72		34		0.3		0.32		0.46		62		1204																				5/27/08		0.02		73		37

		12/21/07		0.08						10/24/07		0.035						5/10/08		0.04		72		32		0.3		0.32		0.46		62		1204																				5/28/08		0.03		71		39

		12/26/07		0.08						10/25/07		0.025						5/12/08		0.055		68		28		0.26		0.32		0.42		60		1196																				5/29/08		0.03		74		39

		12/27/07		0.08						10/26/07		0.035						5/13/08		0.04		73		31		0.26		0.32		0.46		61		1192																				5/30/08		0.04		72		38

		12/28/07		0.075						10/29/07		0.025						5/14/08		0.045		73		25		0.3		0.32		0.46		60		1184																				5/31/08		0.025		72		39

		12/31/07		0.08						10/30/07		0.03						5/15/08		0.035		73		39		0.3		0.32		0.46		60		1196																				6/2/08		0.025		74		27

		1/2/08		0.09						10/31/07		0.03						5/16/08		0.035		73		45		0.3		0.32		0.44		60		1184																				6/3/08		0.02		71		34

		1/3/08		0.075						11/1/07		0.04						5/19/08		0.045		72		41		0.28		0.32		0.44		60		1204																				6/4/08		0.025		69		33

		1/4/08		0.09						11/2/07		0.03						5/20/08		0.045		73		42		0.28		0.32		0.44		62		1196																				6/5/08		0.025		71		39

		1/7/08		0.125						11/5/07		0.025						5/21/08		0.045		70		35		0.28		0.32		0.46		60		1196																				6/6/08		0.025		71		32

		1/8/08		0.08						11/6/07		0.03						5/22/08		0.045		72		30		0.28		0.32		0.42		61		1176																				6/9/08		0.03		72		43

		1/9/08		0.08						11/7/07		0.035						5/23/08		0.045		73		34		0.28		0.32		0.46		61		1172																				6/10/08		0.03		73		33

		1/10/08		0.08						11/8/07		0.05						5/27/08		0.035		73		36		0.28		0.32		0.44		61		1196																				6/11/08		0.025		70		33

		1/11/08		0.08						11/9/07		0.05						5/28/08		0.04		72		37		0.28		0.32		0.44		61		1204																				6/12/08		0.025		71		35

		1/14/08		0.09						11/12/07		0.03						5/29/08		0.04		73		37		0.26		0.32		0.44		61		1200																				6/13/08		0.025		75		32

		1/15/08		0.085						11/13/07		0.05						5/30/08		0.04		72		37		0.28		0.32		0.48		61		1196																				6/16/08		0.025		72		37

		1/16/08		0.09						11/14/07		0.05						6/2/08		0.04		71		30		0.28		0.28		0.44		60		1200																				6/17/08		0.03		72		26

		1/17/08		0.08						11/15/07		0.05						6/3/08		0.035		72		35		0.28		0.32		0.42		61		1196																				6/18/08		0.025		73		33

		1/18/08		0.09						11/16/07		0.05						6/4/08		0.035		70		33		0.28		0.32		0.44		61		1188																				6/19/08		0.025		71		29

		1/21/08		0.04						11/19/07		0.05						6/5/08		0.035		71		37		0.3		0.32		0.44		61		1192																				6/20/08		0.02		73		33

		1/22/08		0.11						11/20/07		0.05						6/6/08		0.035		71		31		0.28		0.32		0.44		61		1188																				6/21/08		0.025		74		27

		1/23/08		0.09						11/21/07		0.05						6/9/08		0.04		72		40		0.32		0.32		0.48		61		1188																				6/23/08		0.02		72		37

		1/24/08		0.09						11/26/07		0.05						6/10/08		0.04		72		31		0.3		0.32		0.44		55		1172																				6/24/08		0.025		73		35

		1/25/08		0.095						11/27/07		0.05						6/11/08		0.04		70		34		0.3		0.32		0.48		55		1196																				6/25/08		0.03		72		36

		1/28/08		0.09						11/28/07		0.05						6/12/08		0.04		72		31		0.3		0.32		0.48		55		1196																				6/26/08		0.03		74		35

		1/29/08		0.09						11/29/07		0.045						6/13/08		0.05		71		36		0.26		0.32		0.44		55		1208																				6/27/08		0.02		71		39

		1/30/08		0.1						11/30/07		0.05						6/16/08		0.05		73		34		0.3		0.32		0.46		55		1204																				6/30/08		0.02		73		38

		1/31/08		0.105						12/3/07		0.05						6/17/08		0.05		73		24		0.28		0.32		0.44		55		1216																				7/1/08		0.055		73		39

		2/1/08		0.09						12/4/07		0.05						6/18/08		0.05		73		31		0.3		0.32		0.44		55		1196																				7/2/08		0.055		73		38

		2/4/08		0.03						12/5/07		0.045						6/19/08		0.05		71		30		0.28		0.32		0.46		55		1196																				7/3/08		0.065		71		39

		2/5/08		0.04						12/6/07		0.05						6/20/08		0.05		73		28		0.28		0.32		0.46		55		1196																				7/7/08		0.055		75		38

		2/6/08		0.025						12/7/07		0.045						6/21/08		0.045		72		30		0.26		0.32		0.46		55		32																				7/8/08		0.05		72		40

		2/7/08		0.02						12/10/07		0.05						6/23/08		0.05		73		39		0.28		0.32		0.44		57		32																				7/9/08		0.06		73		39

		2/8/08		0.04						12/11/07		0.045						6/24/08		0.05		72		34		0.28		0.32		0.42		60		32																				7/10/08		0.06		74		39

		2/9/08		0.05						12/12/07		0.045						6/25/08		0.04		73		36		0.28		0.32		0.44		60		32																				7/11/08		0.06		71		40

		2/11/08		0.02						12/13/07		0.045						6/26/08		0.04		72		34		0.28		0.32		0.44		60		32																				7/12/08		0.06		73		42

		2/12/08		0.035						12/14/07		0.045						6/27/08		0.04		71		38		0.32		0.32		0.44		60		32																				7/14/08		0.06		72		41

		2/13/08		0.025						12/17/07		0.045						6/30/08		0.04		73		37		0.3		0.32		0.44		60		32																				7/15/08		0.06		71		41

		2/14/08		0.025						12/18/07		0.04						7/1/08		0.035		71		38		0.28		0.32		0.44		60		32																				7/16/08		0.065		72		40

		2/15/08		0.03						12/19/07		0.04						7/2/08		0.07		72		38		0.3		0.32		0.46		60		32																				7/17/08		0.05		71		41

		2/19/08		0.03						12/20/07		0.03						7/3/08		0.08		72		38		0.32		0.32		0.48		57		32																				7/18/08		0.065		72		40

		2/20/08		0.05						12/21/07		0.04						7/7/08		0.06		73		40		0.28		0.32		0.44		57		32																				7/19/08		0.06		72		39

		2/21/08		0.03						12/26/07		0.04						7/8/08		0.06		72		38		0.28		0.32		0.42		60		32																				7/21/08		0.06		71		40

		2/22/08		0.03						12/27/07		0.04						7/9/08		0.06		73		39		0.28		0.32		0.42																								7/22/08		0.05		74		36

		2/23/08		0.035						12/28/07		0.04						7/10/08		0.07		72		40		0.32		0.32		0.48		55		1104																				7/23/08		0.07		72		39

		2/24/08		0.035						12/31/07		0.04						7/11/08		0.065		71		39		0.3		0.32		0.48		55		1104																				7/24/08		0.05		72		37

		2/25/08		0.03						1/2/08		0.04						7/12/08		0.08		73		40																														7/25/08		0.06		71		38

		2/26/08		0.035						1/3/08		0.04						7/14/08		0.08		72		40		0.3		0.32		0.48		61		1200																				7/26/08		0.07		71		38

		2/27/08		0.03						1/4/08		0.04						7/15/08		0.09		71		40		0.28		0.32		0.42		61		1200																				7/28/08		0.06		70		41

		2/28/08		0.03						1/7/08		0.025						7/16/08		0.09		72		39		0.28		0.32		0.42		61		1200																				7/29/08		0.06		70		41

		2/29/08		0.03						1/8/08		0.03						7/17/08		0.08		72		39		0.28		0.32		0.44		61		1200																				7/30/08		0.06		71		39

		3/1/08		0.035						1/9/08		0.03						7/18/08		0.09		72		38		0.3		0.32		0.48		61		1200																				7/31/08		0.065		71		40

		3/3/08		0.03						1/10/08		0.03						7/19/08		0.09		73		37																														8/1/08		0.06		73		36

		3/4/08		0.035						1/11/08		0.03						7/21/08		0.09		72		38		0.28		0.32		0.4		61		1200																				8/2/08		0.06		71		40

		3/5/08		0.043						1/14/08		0.025						7/22/08		0.08		73		37		0.24		0.32		0.42		61		1200																				8/4/08		0.06		72		40

		3/6/08		0.043						1/15/08		0.03						7/23/08		0.09		71		38		0.28		0.32		0.44		61		1200																				8/5/08		0.06		73		39

		3/7/08		0.043						1/16/08		0.03						7/24/08		0.09		72		36		0.26		0.32		0.46		61		1200																				8/6/08		0.06		71		41

		3/10/08		0.043						1/17/08		0.03						7/25/08		0.09		72		36		0.24		0.32		0.42		61		1200																				8/7/08		0.06		72		39

		3/11/08		0.042						1/18/08		0.025						7/26/08		0.09		71		37		0.28		0.32		0.46		61		1200																				8/8/08		0.05		72		40

		3/12/08		0.039						1/21/08		0.035						7/28/08		0.09		71		38		0.3		0.32		0.46		61		1200																				8/9/08		0.055		71		40

		3/13/08		0.03						1/22/08		0.03						7/29/08		0.06		70		40		0.3		0.32		0.44																								8/11/08		0.06		71		39

		3/14/08		0.041						1/23/08		0.035						7/30/08		0.07		71		38		0.3		0.32		0.48																								8/12/08		0.065		71		41

		3/17/08		0.047						1/24/08		0.03						7/31/08		0.075		71		38																														8/13/08		0.055		71		41

		3/18/08		0.048						1/25/08		0.035						8/1/08		0.07		72		37		0.3		0.32		0.48																								8/14/08		0.05		71		41

		3/19/08		0.047						1/28/08		0.035						8/2/08		0.07		72		38																														8/15/08		0.05		72		39

		3/20/08		0.042						1/29/08		0.035						8/4/08		0.07		73		37		0.28		0.32		0.44																								8/16/08		0.06		72		40

		3/21/08		0.043						1/30/08		0.025						8/5/08		0.06		73		37		0.28		0.34		0.48																								8/18/08		0.06		72		41

		3/22/08		0.045						1/31/08		0.03						8/6/08		0.07		71		38		0.28		0.32		0.48																								8/19/08		0.06		72		41

		3/24/08		0.043						2/1/08		0.03						8/7/08		0.06		71		38		0.32		0.32		0.48																								8/20/08		0.06		71		40

		3/25/08		0.045						2/4/08		0.035						8/8/08		0.06		72		38		0.26		0.32		0.44																								8/21/08		0.05		73		44

		3/26/08		0.043						2/5/08		0.025						8/9/08		0.06		71		40																														8/22/08		0.05		72		40

		3/27/08		0.04						2/6/08		0.035						8/11/08		0.07		71		38		0.28		0.32		0.44																								8/23/08		0.05		72		41

		3/28/08		0.04						2/7/08		0.025						8/12/08		0.07		71		40		0.28		0.32		0.44																								8/25/08		0.06		71		40

		3/31/08		0.045						2/8/08		0.02						8/13/08		0.065		71		40		0.28		0.3		0.46																								8/26/08		0.06		70		39

		4/1/08		0.045						2/9/08		0.02						8/14/08		0.05		71		39		0.26		0.32		0.42																								8/27/08		0.05		71		40

		4/2/08		0.045						2/14/08		0.035						8/15/08		0.06		71		38		0.26		0.32		0.42																								8/28/08		0.055		71		40

		4/3/08		0.04						2/15/08		0.033						8/16/08		0.06		71		40																														8/29/08		0.055		72		39

		4/4/08		0.045						2/19/08		0.036						8/18/08		0.065		71		41		0.26		0.32		0.42																								9/2/08		0.055		69		32

		4/5/08		0.045						2/20/08		0.037						8/19/08		0.06		72		40		0.28		0.32		0.44																								9/3/08		0.055		72		39

		4/7/08		0.045						2/21/08		0.037						8/20/08		0.06		71		31		0.26		0.32		0.42																								9/4/08		0.055		70		38

		4/8/08		0.04						2/22/08		0.034						8/21/08		0.05		73		42		0.28		0.32		0.48																								9/5/08		0.06		71		36

		4/9/08		0.04						2/25/08		0.044						8/22/08		0.06		71		38		0.24		0.32		0.44																								9/6/08		0.06		71		39

		4/10/08		0.04						2/26/08		0.043						8/23/08		0.06		72		40																														9/8/08		0.06		74		38

		4/11/08		0.045						2/27/08		0.043						8/25/08		0.06		71		40		0.26		0.32		0.46																								9/9/08		0.06		72		40

		4/14/08		0.045						2/28/08		0.044						8/26/08		0.06		70		38		0.26		0.32		0.44																								9/10/08		0.06		72		40

		4/15/08		0.04						2/29/08		0.046						8/27/08		0.05		71		38		0.26		0.32		0.44																								9/11/08		0.06		71		41

		4/16/08		0.04						3/3/08		0.045						8/28/08		0.05		71		38		0.26		0.3		0.44																								9/12/08		0.06		70		40

		4/17/08		0.04						3/4/08		0.044						8/29/08		0.065		72		38		0.28		0.3		0.44																								9/13/08		0.06		70		41

		4/18/08		0.04						3/5/08		0.039						9/2/08		0.06		69		31		0.24		0.32		0.42																								9/15/08		0.06		70		40

		4/19/08		0.05						3/6/08		0.039						9/3/08		0.06		72		40		0.28		0.32		0.44																								9/16/08		0.06		71		40

		4/21/08		0.05						3/7/08		0.038						9/4/08		0.06		70		37		0.26		0.32		0.44																								9/17/08		0.06		70		30

		4/22/08		0.045						3/10/08		0.037						9/5/08		0.06		70		36		0.26		0.32		0.44																								9/18/08		0.06		71		37

		4/23/08		0.04						3/11/08		0.04						9/6/08		0.06		70		38																														9/19/08		0.06		72		43

		4/24/08		0.04						3/12/08		0.036						9/8/08		0.06		72		41		0.24		0.32		0.42																								9/20/08		0.06		72		42

		4/25/08		0.04						3/14/08		0.039						9/9/08		0.06		71		40		0.24		0.32		0.44																								9/22/08		0.06		71		39

		4/30/08		0.04						3/17/08		0.038						9/10/08		0.06		70		41		0.28		0.32		0.46																								9/23/08		0.065		72		37

		5/1/08		0.04						3/18/08		0.038						9/11/08		0.06		70		41		0.26		0.32		0.42																								9/24/08		0.055		70		33

		5/2/08		0.04						3/19/08		0.037						9/12/08		0.06		70		40		0.28		0.32		0.48																								9/25/08		0.06		72		32

		5/3/08		0.045						3/20/08		0.039						9/13/08		0.06		70		40																														9/26/08		0.06		72		43

		5/5/08		0.04						3/21/08		0.038						9/15/08		0.06		69		41		0.3		0.32		0.44																								9/27/08		0.06		70		37

		5/6/08		0.04						3/24/08		0.038						9/16/08		0.06		69		41		0.24		0.3		0.42																								9/29/08		0.06		71		40

		5/7/08		0.045						3/25/08		0.038						9/17/08		0.07		69		38		0.26		0.32		0.46																								9/30/08		0.06		75		33

		5/8/08		0.04						3/26/08		0.039						9/18/08		0.06		70		38		0.26		0.32		0.42

		5/9/08		0.04						3/27/08		0.045						9/19/08		0.06		73		42		0.26		0.32		0.42

		5/10/08		0.04						3/28/08		0.04						9/20/08		0.05		73		41

		5/12/08		0.04						3/31/08		0.04						9/22/08		0.06		71		38		0.24		0.32		0.44

		5/13/08		0.04						4/1/08		0.04						9/23/08		0.065		71		37		0.26		0.32		0.44

		5/14/08		0.04						4/2/08		0.04						9/24/08		0.055		71		32		0.26		0.32		0.42

		5/15/08		0.04						4/3/08		0.035						9/25/08		0.06		71		32		0.28		0.32		0.48

		5/16/08		0.04						4/4/08		0.04						9/26/08		0.055		73		41		0.24		0.32		0.44

		5/19/08		0.04						4/5/08		0.035						9/27/08		0.06		71		35

		5/20/08		0.04						4/7/08		0.04						9/29/08		0.06		70		40		0.26		0.32		0.44

		5/21/08		0.04						4/8/08		0.04						9/30/08		0.05		71		36		0.24		0.32		0.44

		5/22/08		0.04						4/9/08		0.035						10/1/08								0.24		0.32		0.44

		5/23/08		0.04						4/10/08		0.04						10/2/08								0.24		0.32		0.44

		5/27/08		0.04						4/11/08		0.04

		5/28/08		0.04						4/14/08		0.04

		5/29/08		0.05						4/15/08		0.04

		5/30/08		0.04						4/16/08		0.04

		5/31/08		0.045						4/17/08		0.04

		6/2/08		0.04						4/18/08		0.035

		6/3/08		0.04						4/19/08		0.05

		6/4/08		0.04						4/21/08		0.05

		6/5/08		0.04						4/22/08		0.04

		6/6/08		0.04						4/23/08		0.04

		6/9/08		0.04						4/24/08		0.04

		6/10/08		0.04						4/25/08		0.04

		6/11/08		0.04						4/30/08		0.04

		6/12/08		0.04						5/1/08		0.04

		6/13/08		0.04						5/2/08		0.04

		6/16/08		0.04						5/3/08		0.04

		6/17/08		0.04						5/5/08		0.04

		6/18/08		0.04						5/6/08		0.04

		6/19/08		0.04						5/7/08		0.04

		6/20/08		0.04						5/8/08		0.04

		6/21/08		0.035						5/9/08		0.04

		6/23/08		0.035						5/10/08		0.04

		6/24/08		0.04						5/12/08		0.04

		6/25/08		0.035						5/13/08		0.04

		6/26/08		0.035						5/14/08		0.04

		6/27/08		0.035						5/15/08		0.04

		6/30/08		0.035						5/16/08		0.04

		7/1/08		0.03						5/19/08		0.04

		7/2/08		0.03						5/20/08		0.04

		7/3/08		0.035						5/21/08		0.04

		7/7/08		0.03						5/22/08		0.04

		7/8/08		0.03						5/23/08		0.04

		7/9/08		0.035						5/27/08		0.04

		7/10/08		0.035						5/28/08		0.04

		7/11/08		0.035						5/29/08		0.04

		7/12/08		0.03						5/30/08		0.04

		7/14/08		0.025						6/2/08		0.04

		7/15/08		0.03						6/3/08		0.035

		7/16/08		0.03						6/4/08		0.035

		7/17/08		0.03						6/5/08		0.035

		7/18/08		0.04						6/6/08		0.035

		7/19/08		0.03						6/9/08		0.035

		7/21/08		0.03						6/10/08		0.035

		7/22/08		0.03						6/11/08		0.035

		7/23/08		0.02						6/12/08		0.035

		7/24/08		0.025						6/13/08		0.04

		7/25/08		0.01						6/16/08		0.035

		7/26/08		0.01						6/17/08		0.045

		7/28/08		0.01						6/18/08		0.045

		7/29/08		0.03						6/19/08		0.045

		7/30/08		0.01						6/20/08		0.035

		7/31/08		0.015						6/21/08		0.035

		8/1/08		0.025						6/23/08		0.035

		8/2/08		0.03						6/24/08		0.045

		8/4/08		0.03						6/25/08		0.035

		8/5/08		0.03						6/26/08		0.035

		8/6/08		0.04						6/27/08		0.035

		8/7/08		0.035						6/30/08		0.035

		8/8/08		0.03						7/1/08		0.04

		8/9/08		0.03						7/2/08		0.04

		8/11/08		0.035						7/3/08		0.04

		8/12/08		0.035						7/7/08		0.04

		8/13/08		0.035						7/8/08		0.04

		8/14/08		0.03						7/9/08		0.04

		8/15/08		0.03						7/10/08		0.04

		8/16/08		0.03						7/11/08		0.04

		8/18/08		0.03						7/12/08		0.04

		8/19/08		0.04						7/14/08		0.04

		8/20/08		0.03						7/15/08		0.04

		8/21/08		0.03						7/16/08		0.04

		8/22/08		0.03						7/17/08		0.04

		8/23/08		0.03						7/18/08		0.04

		8/25/08		0.03						7/19/08		0.04

		8/26/08		0.03						7/21/08		0.04

		8/27/08		0.03						7/22/08		0.04

		8/28/08		0.03						7/23/08		0.04

		8/29/08		0.03						7/24/08		0.04

		9/2/08		0.03						7/25/08		0.04

		9/3/08		0.03						7/26/08		0.04

		9/4/08		0.03						7/28/08		0.04

		9/5/08		0.03						7/29/08		0.04

		9/6/08		0.03						7/30/08		0.04

		9/8/08		0.03						7/31/08		0.04

		9/9/08		0.03						8/1/08		0.045

		9/10/08		0.03						8/2/08		0.04

		9/11/08		0.03						8/4/08		0.04

		9/12/08		0.03						8/5/08		0.04

		9/13/08		0.03						8/6/08		0.05

		9/15/08		0.035						8/7/08		0.04

		9/16/08		0.03						8/8/08		0.04

		9/17/08		0.03						8/9/08		0.04

		9/18/08		0.03						8/11/08		0.04

		9/19/08		0.03						8/12/08		0.04

		9/20/08		0.03						8/13/08		0.04

		9/22/08		0.03						8/14/08		0.04

		9/23/08		0.03						8/15/08		0.04

		9/24/08		0.025						8/16/08		0.04

		9/25/08		0.03						8/18/08		0.04

		9/26/08		0.03						8/19/08		0.04

		9/27/08		0.03						8/20/08		0.04

		9/29/08		0.03						8/21/08		0.04

		9/30/08		0.03						8/22/08		0.04

		10/1/08		0.03						8/23/08		0.04

		10/2/08		0.03						8/25/08		0.04

		10/3/08		0.03						8/26/08		0.04

		10/4/08		0.03						8/27/08		0.04

		10/6/08		0.03						8/28/08		0.04

		10/7/08		0.04						8/29/08		0.04

		10/8/08		0.03						9/2/08		0.04

		10/9/08		0.03						9/3/08		0.04

		10/10/08		0.03						9/4/08		0.04

		10/11/08		0.03						9/5/08		0.04

		10/13/08		0.03						9/6/08		0.04

		10/14/08		0.03						9/8/08		0.04

		10/15/08		0.03						9/9/08		0.04

		10/16/08		0.04						9/10/08		0.04

		10/17/08		0.03						9/11/08		0.04

		10/18/08		0.03						9/12/08		0.04

		10/20/08		0.03						9/13/08		0.04

		10/21/08		0.03						9/15/08		0.04

		10/22/08		0.03						9/16/08		0.04

		10/23/08		0.03						9/17/08		0.04

		10/24/08		0.03						9/18/08		0.04

		10/25/08		0.03						9/19/08		0.04

		10/27/08		0.03						9/20/08		0.04

		10/28/08		0.03						9/22/08		0.04

		10/29/08		0.03						9/23/08		0.045

		10/30/08		0.03						9/24/08		0.045

		10/31/08		0.03						9/25/08		0.045

		11/3/08		0.03						9/26/08		0.04

		11/4/08		0.03						9/27/08		0.04

										9/29/08		0.04

										9/30/08		0.04

										10/1/08		0.04

										10/2/08		0.04

										10/3/08		0.04

										10/4/08		0.04

										10/6/08		0.04

										10/7/08		0.05

										10/8/08		0.045

										10/9/08		0.04

										10/10/08		0.04

										10/11/08		0.04

										10/13/08		0.045

										10/14/08		0.04

										10/15/08		0.045

										10/16/08		0.04

										10/17/08		0.04

										10/18/08		0.04

										10/20/08		0.04

										10/21/08		0.04

										10/22/08		0.04

										10/23/08		0.04

										10/24/08		0.04

										10/25/08		0.04

										10/27/08		0.04

										10/28/08		0.04

										10/29/08		0.04

										10/30/08		0.04

										10/31/08		0.04

										11/3/08		0.04

										11/4/08		0.04

										11/5/08		0.05

										11/6/08		0.04

										11/7/08		0.04

										11/8/08		0.045

										11/10/08		0.04

										11/11/08		0.04

										11/12/08		0.04

										11/13/08		0.04

										11/14/08		0.04

										11/15/08		0.04

										11/17/08		0.04

										11/18/08		0.04

										11/19/08		0.04

										11/20/08		0.045

										11/21/08		0.045

										11/22/08		0.04

										11/24/08		0.04

										11/25/08		0.04

										11/26/08		0.04

										12/1/08		0.04





CER Pressure

		



Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)

R&D Bio-Safety Cabinet South (left axis)

Date

Diff. Pressure (Water Column In.)

Mfg Bio-Safety Cabinet South CFM

Figure 7.  CER2 Bio-Safety Cabinet Differential Pressure Daily Run Chart



Conf-Rel

		



Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

R&D Bio-Safety Cabinet South (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)

Date

Diff. Pressure (Water Column In.)

Mfg Bio-Safety Cabinet (cfm)

Figure 8.  Bio-Safety Cabinet Differential Pressure - Monthly Average



Temp-Humid

		



CER1

CER Change Room

CER2

CER3

CER Alert Level

CER Action Level

Date

Diff. Pressure (Water Column In.)

Figure 5.  CER Differential Pressure Daily Run Chart



Sheet1

		



CER1

CER Change Room

CER 2

CER 3

CER Alert Level

CER Action Level

Date

Diff. Pressure (Water Column In.)

Figure 6.  CER Differential Pressure - Monthly Average



		TO:		DCN 0273 File

		FROM:		Andy Pearson

		DATE:		3/3/07

		RE:		Confidence and Reliability Levels for CER Monitoring

		The table below shows 95/95, and 95/99 confidence/reliability levels for  CER and Change Room

		monitoring carried out from Feb 06 to Feb 07.

		Recommended action and alert levels correspond to worst case 95/95 (alert) and 95/99 (action) values.

						95/95 Limit		Recommended Alert Level		95/99 Limit		95/99 Limit		Recommended Action Level

		Airstrips (utl)		CER1		17		35		21		21		45

				CER2		15				20		20

				CER3		34				43		43

		Contact Plates (utl)		CER1		5		6		6		6		7

				CER2		4				5		5

				CER3		6				7		7

		0.5um Particle Counts (utl)		CER1		1092		3800		1324		1324		4500

				CER3		3797				4549		4549

				CER2		1232		1250		1495		1495		1500

		5.0um Particle Counts (utl)		CER1		159		410		200		200		500

				CER3		410				497		497

				CER2		91		90		107		107		105

		Pressure Differential (ltl)		CER1		0.011		0.030		0.003		0.003		0.005

				CER1/2 Chg Rm		0.021				0.013		0.013

				CER2		-0.021				-0.045		-0.045

				CER3		0.040				0.035		0.035

		Andy Pearson

		Sr.Quality Engineer





		CER2								CER1								CER3								QA

		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 2 Temperature(°F)		CER 2 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 1 Temperature(°F)		CER 1 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 3 Temperature(°F)		CER 3 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		QA Temperature(°F)		QA Humidity(%)

		29-Aug-07		16:07:10		75.81		46.5		29-Aug-07		16:06:20		76.4		48		29-Aug-07		16:07:53		75.81		74		9-Oct-07		16:25:59		78.2		33

		29-Aug-07		18:07:10		74.01		40.5		29-Aug-07		18:06:20		70.41		41.5		29-Aug-07		18:07:53		74.6		41.5		9-Oct-07		18:25:59		75.81		35.5

		29-Aug-07		20:07:10		74.6		40.5		29-Aug-07		20:06:20		71.6		43.5		29-Aug-07		20:07:53		73.4		43		9-Oct-07		20:25:59		75.2		34.5

		29-Aug-07		22:07:10		75.81		40.5		29-Aug-07		22:06:20		71.6		46.5		29-Aug-07		22:07:53		74.6		42		9-Oct-07		22:25:59		74.6		35

		30-Aug-07		0:07:10		75.81		40.5		30-Aug-07		0:06:20		71.6		47.5		30-Aug-07		0:07:53		75.2		41.5		10-Oct-07		0:25:59		73.4		36

		30-Aug-07		2:07:10		75.81		41		30-Aug-07		2:06:20		71		49		30-Aug-07		2:07:53		75.81		41.5		10-Oct-07		2:25:59		72.8		37

		30-Aug-07		4:07:10		75.2		42.5		30-Aug-07		4:06:20		71		51		30-Aug-07		4:07:53		75.2		41.5		10-Oct-07		4:25:59		72.21		38

		30-Aug-07		6:07:10		75.81		41		30-Aug-07		6:06:20		71.6		46.5		30-Aug-07		6:07:53		75.2		42		10-Oct-07		6:25:59		72.21		39

		30-Aug-07		8:07:10		75.81		45.5		30-Aug-07		8:06:20		72.21		55.5		30-Aug-07		8:07:53		75.2		44		10-Oct-07		8:25:59		71.6		41.5

		30-Aug-07		10:07:10		74.6		43.5		30-Aug-07		10:06:20		72.21		41.5		30-Aug-07		10:07:53		74.6		45		10-Oct-07		10:25:59		72.8		42.5

		30-Aug-07		12:07:10		74.6		43.5		30-Aug-07		12:06:20		71.6		46		30-Aug-07		12:07:53		72.8		45.5		10-Oct-07		12:25:59		74.01		42.5

		30-Aug-07		14:07:10		74.6		43		30-Aug-07		14:06:20		72.21		43		30-Aug-07		14:07:53		72.21		44.5		10-Oct-07		14:25:59		75.2		43

		30-Aug-07		16:07:10		75.2		43.5		30-Aug-07		16:06:20		72.21		43.5		30-Aug-07		16:07:53		72.8		44.5		10-Oct-07		16:25:59		75.2		42

		30-Aug-07		18:07:10		75.2		45		30-Aug-07		18:06:20		70.41		49.5		30-Aug-07		18:07:53		71.6		46		10-Oct-07		18:25:59		75.2		41

		30-Aug-07		20:07:10		75.2		45.5		30-Aug-07		20:06:20		71.6		52		30-Aug-07		20:07:53		75.81		45		10-Oct-07		20:25:59		74.01		42.5

		30-Aug-07		22:07:10		76.4		45		30-Aug-07		22:06:20		71		53.5		30-Aug-07		22:07:53		75.2		45		10-Oct-07		22:25:59		73.4		43.5

		31-Aug-07		0:07:10		76.4		44.5		31-Aug-07		0:06:20		71		53.5		31-Aug-07		0:07:53		75.2		44.5		11-Oct-07		0:25:59		72.8		44.5

		31-Aug-07		2:07:10		75.81		44.5		31-Aug-07		2:06:20		71.6		53		31-Aug-07		2:07:53		75.2		45.5		11-Oct-07		2:25:59		72.21		45

		31-Aug-07		4:07:10		75.81		45		31-Aug-07		4:06:20		71.6		53		31-Aug-07		4:07:53		72.8		41.5		11-Oct-07		4:25:59		71.6		45.5

		31-Aug-07		6:07:10		75.81		45.5		31-Aug-07		6:06:20		72.21		54		31-Aug-07		6:07:53		71		54.5		11-Oct-07		6:25:59		72.21		45

		31-Aug-07		8:07:10		75.2		44		31-Aug-07		8:06:20		72.21		43.5		31-Aug-07		8:07:53		71.6		50.5		11-Oct-07		8:25:59		71.6		46.5

		31-Aug-07		10:07:10		74.6		45.5		31-Aug-07		10:06:20		72.21		49.5		31-Aug-07		10:07:53		72.21		44.5		11-Oct-07		10:25:59		72.8		48.5

		31-Aug-07		12:07:10		74.6		49.5		31-Aug-07		12:06:20		71.6		60.5		31-Aug-07		12:07:53		72.21		45		11-Oct-07		12:25:59		74.6		44.5

		31-Aug-07		14:07:10		74.6		45.5		31-Aug-07		14:06:20		71.6		44		31-Aug-07		14:07:53		72.8		47		11-Oct-07		14:25:59		75.81		42.5

		31-Aug-07		16:07:10		74.6		48		31-Aug-07		16:06:20		71.6		56.5		31-Aug-07		16:07:53		72.8		43.5		11-Oct-07		16:25:59		76.4		42.5

		31-Aug-07		18:07:10		75.2		46.5		31-Aug-07		18:06:20		70.41		54.5		31-Aug-07		18:07:53		71		50		11-Oct-07		18:25:59		76.4		41

		31-Aug-07		20:07:10		75.2		46		31-Aug-07		20:06:20		71.6		53		31-Aug-07		20:07:53		74.6		50		11-Oct-07		20:25:59		74.6		41.5

		31-Aug-07		22:07:10		76.4		44		31-Aug-07		22:06:20		71.6		48.5		31-Aug-07		22:07:53		75.2		47		11-Oct-07		22:25:59		74.6		41

		1-Sep-07		0:07:10		76.4		42.5		1-Sep-07		0:06:20		71.6		46.5		1-Sep-07		0:07:53		75.2		45.5		12-Oct-07		0:25:59		73.4		41

		1-Sep-07		2:07:10		76.4		44		1-Sep-07		2:06:20		71.6		53		1-Sep-07		2:07:53		74.6		45.5		12-Oct-07		2:25:59		71.6		41

		1-Sep-07		4:07:10		76.4		44		1-Sep-07		4:06:20		71.6		53		1-Sep-07		4:07:53		72.8		50		12-Oct-07		4:25:59		71		41.5

		1-Sep-07		6:07:10		76.4		45		1-Sep-07		6:06:20		73.4		56.5		1-Sep-07		6:07:53		71.6		45		12-Oct-07		6:25:59		70.41		41.5

		1-Sep-07		8:07:10		75.2		42.5		1-Sep-07		8:06:20		72.21		41		1-Sep-07		8:07:53		71.6		53		12-Oct-07		8:25:59		69.8		41.5

		1-Sep-07		10:07:10		74.6		43.5		1-Sep-07		10:06:20		71.6		42		1-Sep-07		10:07:53		72.21		43.5		12-Oct-07		10:25:59		71.6		44.5

		1-Sep-07		12:07:10		74.6		51.5		1-Sep-07		12:06:20		70.41		64		1-Sep-07		12:07:53		71.6		45.5		12-Oct-07		12:25:59		74.6		43.5

		1-Sep-07		14:07:10		74.6		52		1-Sep-07		14:06:20		70.41		64.5		1-Sep-07		14:07:53		71		50.5		12-Oct-07		14:25:59		75.2		42.5

		1-Sep-07		16:07:10		74.6		46.5		1-Sep-07		16:06:20		70.41		52.5		1-Sep-07		16:07:53		71		57.5		12-Oct-07		16:25:59		75.2		42.5

		1-Sep-07		18:07:10		74.6		45.5		1-Sep-07		18:06:20		70.41		50.5		1-Sep-07		18:07:53		71		58.5		12-Oct-07		18:25:59		74.6		40

		1-Sep-07		20:07:10		74.6		49.5		1-Sep-07		20:06:20		71		56		1-Sep-07		20:07:53		71		55.5		12-Oct-07		20:25:59		74.01		40.5

		1-Sep-07		22:07:10		75.2		47		1-Sep-07		22:06:20		71		56		1-Sep-07		22:07:53		72.21		50.5		12-Oct-07		22:25:59		74.01		40

		2-Sep-07		0:07:10		75.2		45		2-Sep-07		0:06:20		71.6		52.5		2-Sep-07		0:07:53		72.21		50		13-Oct-07		0:25:59		72.8		40.5

		2-Sep-07		2:07:10		75.2		44.5		2-Sep-07		2:06:20		71		51		2-Sep-07		2:07:53		71.6		50		13-Oct-07		2:25:59		71.6		41

		2-Sep-07		4:07:10		74.6		44		2-Sep-07		4:06:20		70.41		51.5		2-Sep-07		4:07:53		70.41		49.5		13-Oct-07		4:25:59		71		42.5

		2-Sep-07		6:07:10		74.01		41.5		2-Sep-07		6:06:20		71		45.5		2-Sep-07		6:07:53		69.2		48.5		13-Oct-07		6:25:59		71.6		43

		2-Sep-07		8:07:10		73.4		44		2-Sep-07		8:06:20		69.8		51		2-Sep-07		8:07:53		69.2		51		13-Oct-07		8:25:59		71		46

		2-Sep-07		10:07:10		74.01		48.5		2-Sep-07		10:06:20		70.41		57.5		2-Sep-07		10:07:53		71		48.5		13-Oct-07		10:25:59		72.21		47.5

		2-Sep-07		12:07:10		74.6		49.5		2-Sep-07		12:06:20		70.41		59.5		2-Sep-07		12:07:53		71		53		13-Oct-07		12:25:59		72.8		47

		2-Sep-07		14:07:10		75.81		49.5		2-Sep-07		14:06:20		70.41		60.5		2-Sep-07		14:07:53		71		60		13-Oct-07		14:25:59		72.21		47.5

		2-Sep-07		16:07:10		76.4		43.5		2-Sep-07		16:06:20		70.41		47.5		2-Sep-07		16:07:53		71		46.5		13-Oct-07		16:25:59		74.01		47

		2-Sep-07		18:07:10		76.4		46.5		2-Sep-07		18:06:20		69.8		55.5		2-Sep-07		18:07:53		71		58		13-Oct-07		18:25:59		74.6		44.5

		2-Sep-07		20:07:10		77		44		2-Sep-07		20:06:20		71		52.5		2-Sep-07		20:07:53		74.01		47		13-Oct-07		20:25:59		72.8		45.5

		2-Sep-07		22:07:10		77		41.5		2-Sep-07		22:06:20		71.6		51		2-Sep-07		22:07:53		74.6		44.5		13-Oct-07		22:25:59		71.6		45

		3-Sep-07		0:07:10		76.4		41		3-Sep-07		0:06:20		71		50.5		3-Sep-07		0:07:53		74.01		44.5		14-Oct-07		0:25:59		71		45

		3-Sep-07		2:07:10		75.81		40		3-Sep-07		2:06:20		71		44		3-Sep-07		2:07:53		72.21		45.5		14-Oct-07		2:25:59		69.8		43.5

		3-Sep-07		4:07:10		75.2		39		3-Sep-07		4:06:20		71		41.5		3-Sep-07		4:07:53		71		46.5		14-Oct-07		4:25:59		69.2		43

		3-Sep-07		6:07:10		75.2		40		3-Sep-07		6:06:20		71.6		46		3-Sep-07		6:07:53		69.2		47.5		14-Oct-07		6:25:59		69.2		42.5

		3-Sep-07		8:07:10		74.01		42		3-Sep-07		8:06:20		69.8		49		3-Sep-07		8:07:53		68.61		49.5		14-Oct-07		8:25:59		69.2		41

		3-Sep-07		10:07:10		74.01		43		3-Sep-07		10:06:20		70.41		48		3-Sep-07		10:07:53		70.41		52		14-Oct-07		10:25:59		71		44

		3-Sep-07		12:07:10		74.6		41.5		3-Sep-07		12:06:20		70.41		43.5		3-Sep-07		12:07:53		71		43.5		14-Oct-07		12:25:59		72.21		45

		3-Sep-07		14:07:10		75.2		43		3-Sep-07		14:06:20		70.41		47		3-Sep-07		14:07:53		71.6		52		14-Oct-07		14:25:59		74.01		44.5

		3-Sep-07		16:07:10		75.81		44.5		3-Sep-07		16:06:20		69.8		49.5		3-Sep-07		16:07:53		71.6		52		14-Oct-07		16:25:59		75.2		44.5

		3-Sep-07		18:07:10		76.4		40.5		3-Sep-07		18:06:20		70.41		47		3-Sep-07		18:07:53		71		45		14-Oct-07		18:25:59		75.81		44

		3-Sep-07		20:07:10		77.61		40		3-Sep-07		20:06:20		71.6		45.5		3-Sep-07		20:07:53		75.81		42		14-Oct-07		20:25:59		74.6		44.5

		3-Sep-07		22:07:10		77		41		3-Sep-07		22:06:20		71.6		50.5		3-Sep-07		22:07:53		74.6		43.5		14-Oct-07		22:25:59		73.4		45

		4-Sep-07		0:07:10		76.4		40.5		4-Sep-07		0:06:20		71		50		4-Sep-07		0:07:53		74.6		43.5		15-Oct-07		0:25:59		72.8		45.5

		4-Sep-07		2:07:10		75.81		40		4-Sep-07		2:06:20		71		49.5		4-Sep-07		2:07:53		72.8		44		15-Oct-07		2:25:59		72.21		46

		4-Sep-07		4:07:10		75.81		39.5		4-Sep-07		4:06:20		71.6		47		4-Sep-07		4:07:53		71.6		45		15-Oct-07		4:25:59		71.6		46

		4-Sep-07		6:07:10		74.6		40		4-Sep-07		6:06:20		71		47.5		4-Sep-07		6:07:53		69.8		46.5		15-Oct-07		6:25:59		71		46.5

		4-Sep-07		8:07:10		74.01		39.5		4-Sep-07		8:06:20		70.41		42		4-Sep-07		8:07:53		69.8		48.5		15-Oct-07		8:25:59		70.41		47

		4-Sep-07		10:07:10		74.01		45.5		4-Sep-07		10:06:20		69.8		53.5		4-Sep-07		10:07:53		71		52		15-Oct-07		10:25:59		69.8		47.5

		4-Sep-07		12:07:10		74.01		48		4-Sep-07		12:06:20		69.8		55		4-Sep-07		12:07:53		71		45.5		15-Oct-07		12:25:59		70.41		48.5

		4-Sep-07		14:07:10		74.01		49		4-Sep-07		14:06:20		70.41		52		4-Sep-07		14:07:53		71		58.5		15-Oct-07		14:25:59		71.6		49

		4-Sep-07		16:07:10		74.6		47.5		4-Sep-07		16:06:20		70.41		50		4-Sep-07		16:07:53		71		49		15-Oct-07		16:25:59		73.4		48

		4-Sep-07		18:07:10		74.6		47.5		4-Sep-07		18:06:20		70.41		50		4-Sep-07		18:07:53		71		49.5		15-Oct-07		18:25:59		74.6		45.5

		4-Sep-07		20:07:10		75.2		50		4-Sep-07		20:06:20		71		58.5		4-Sep-07		20:07:53		71.6		55.5		15-Oct-07		20:25:59		72.8		46

		4-Sep-07		22:07:10		75.81		47.5		4-Sep-07		22:06:20		71.6		56		4-Sep-07		22:07:53		74.01		50		15-Oct-07		22:25:59		71.6		46

		5-Sep-07		0:07:10		75.81		46.5		5-Sep-07		0:06:20		71		56.5		5-Sep-07		0:07:53		74.01		49.5		16-Oct-07		0:25:59		71		46

		5-Sep-07		2:07:10		75.81		44.5		5-Sep-07		2:06:20		71		47.5		5-Sep-07		2:07:53		72.8		50.5		16-Oct-07		2:25:59		70.41		46.5

		5-Sep-07		4:07:10		75.2		45.5		5-Sep-07		4:06:20		71		55		5-Sep-07		4:07:53		71.6		49		16-Oct-07		4:25:59		69.8		46

		5-Sep-07		6:07:10		75.2		47		5-Sep-07		6:06:20		71.6		55		5-Sep-07		6:07:53		70.41		48		16-Oct-07		6:25:59		70.41		46.5

		5-Sep-07		8:07:10		75.2		45		5-Sep-07		8:06:20		72.21		45.5		5-Sep-07		8:07:53		71		53		16-Oct-07		8:25:59		69.8		47.5

		5-Sep-07		10:07:10		74.6		51.5		5-Sep-07		10:06:20		72.21		55		5-Sep-07		10:07:53		72.8		46.5		16-Oct-07		10:25:59		71		49.5

		5-Sep-07		12:07:10		74.01		50.5		5-Sep-07		12:06:20		71		56		5-Sep-07		12:07:53		72.21		57.5		16-Oct-07		12:25:59		72.21		52

		5-Sep-07		14:07:10		74.01		48		5-Sep-07		14:06:20		71.6		54.5		5-Sep-07		14:07:53		72.21		54		16-Oct-07		14:25:59		73.4		52.5

		5-Sep-07		16:07:10		74.01		49		5-Sep-07		16:06:20		71		54		5-Sep-07		16:07:53		72.21		51		16-Oct-07		16:25:59		75.2		47.5

		5-Sep-07		18:07:10		74.6		49		5-Sep-07		18:06:20		70.41		60		5-Sep-07		18:07:53		71.6		48.5		16-Oct-07		18:25:59		75.81		47.5

		5-Sep-07		20:07:10		74.6		48		5-Sep-07		20:06:20		71.6		55		5-Sep-07		20:07:53		71		58		16-Oct-07		20:25:59		74.01		48.5

		5-Sep-07		22:07:10		75.81		46.5		5-Sep-07		22:06:20		71		55.5		5-Sep-07		22:07:53		75.2		47		16-Oct-07		22:25:59		73.4		49

		6-Sep-07		0:07:10		75.81		43.5		6-Sep-07		0:06:20		71.6		50.5		6-Sep-07		0:07:53		74.6		47		17-Oct-07		0:25:59		72.21		49

		6-Sep-07		2:07:10		75.2		44.5		6-Sep-07		2:06:20		71		52.5		6-Sep-07		2:07:53		73.4		47		17-Oct-07		2:25:59		71		48

		6-Sep-07		4:07:10		75.2		43.5		6-Sep-07		4:06:20		71.6		51		6-Sep-07		4:07:53		72.21		48.5		17-Oct-07		4:25:59		70.41		47.5

		6-Sep-07		6:07:10		75.2		42.5		6-Sep-07		6:06:20		71.6		48.5		6-Sep-07		6:07:53		71		50.5		17-Oct-07		6:25:59		69.8		46

		6-Sep-07		8:07:10		75.2		45.5		6-Sep-07		8:06:20		72.21		52		6-Sep-07		8:07:53		71.6		48.5		17-Oct-07		8:25:59		69.2		46.5

		6-Sep-07		10:07:10		75.2		43.5		6-Sep-07		10:06:20		72.21		46		6-Sep-07		10:07:53		72.21		49.5		17-Oct-07		10:25:59		70.41		49

		6-Sep-07		12:07:10		74.6		41.5		6-Sep-07		12:06:20		71.6		42.5		6-Sep-07		12:07:53		72.21		52		17-Oct-07		12:25:59		71.6		51.5

		6-Sep-07		14:07:10		74.01		40		6-Sep-07		14:06:20		71.6		40.5		6-Sep-07		14:07:53		72.21		42		17-Oct-07		14:25:59		72.21		53

		6-Sep-07		16:07:10		74.6		40		6-Sep-07		16:06:20		71.6		43		6-Sep-07		16:07:53		72.21		40		17-Oct-07		16:25:59		72.8		54

		6-Sep-07		18:07:10		74.6		38		6-Sep-07		18:06:20		69.8		42		6-Sep-07		18:07:53		72.21		37.5		17-Oct-07		18:25:59		74.01		50.5

		6-Sep-07		20:07:10		75.2		38		6-Sep-07		20:06:20		71.6		43		6-Sep-07		20:07:53		75.2		39.5		17-Oct-07		20:25:59		72.21		48.5

		6-Sep-07		22:07:10		75.81		38.5		6-Sep-07		22:06:20		71.6		45.5		6-Sep-07		22:07:53		75.2		39.5		17-Oct-07		22:25:59		71		48

		7-Sep-07		0:07:10		75.81		39		7-Sep-07		0:06:20		71.6		46.5		7-Sep-07		0:07:53		75.2		39.5		18-Oct-07		0:25:59		70.41		47

		7-Sep-07		2:07:10		75.81		39		7-Sep-07		2:06:20		71.6		46		7-Sep-07		2:07:53		74.01		41		18-Oct-07		2:25:59		69.2		45.5

		7-Sep-07		4:07:10		75.2		39		7-Sep-07		4:06:20		71		46		7-Sep-07		4:07:53		72.21		37		18-Oct-07		4:25:59		68.61		45

		7-Sep-07		6:07:10		75.81		38		7-Sep-07		6:06:20		71.6		44		7-Sep-07		6:07:53		71		45.5		18-Oct-07		6:25:59		69.2		46

		7-Sep-07		8:07:10		75.81		41		7-Sep-07		8:06:20		71.6		50		7-Sep-07		8:07:53		71.6		39.5		18-Oct-07		8:25:59		69.2		47

		7-Sep-07		10:07:10		75.2		38.5		7-Sep-07		10:06:20		71.6		40.5		7-Sep-07		10:07:53		72.21		40		18-Oct-07		10:25:59		70.41		50

		7-Sep-07		12:07:10		74.6		40		7-Sep-07		12:06:20		71		42.5		7-Sep-07		12:07:53		72.21		51.5		18-Oct-07		12:25:59		72.8		48.5

		7-Sep-07		14:07:10		74.6		43		7-Sep-07		14:06:20		71.6		42		7-Sep-07		14:07:53		71.6		42.5		18-Oct-07		14:25:59		74.6		45

		7-Sep-07		16:07:10		75.81		46		7-Sep-07		16:06:20		71		61		7-Sep-07		16:07:53		71.6		44.5		18-Oct-07		16:25:59		75.81		43

		7-Sep-07		18:07:10		75.2		45.5		7-Sep-07		18:06:20		71		48		7-Sep-07		18:07:53		71		53.5		18-Oct-07		18:25:59		75.81		43

		7-Sep-07		20:07:10		75.81		49		7-Sep-07		20:06:20		71.6		57		7-Sep-07		20:07:53		71.6		55		18-Oct-07		20:25:59		74.6		43.5

		7-Sep-07		22:07:10		75.81		48.5		7-Sep-07		22:06:20		71.6		58		7-Sep-07		22:07:53		72.8		52		18-Oct-07		22:25:59		73.4		44

		8-Sep-07		0:07:10		75.2		47.5		8-Sep-07		0:06:20		71		56.5		8-Sep-07		0:07:53		72.8		51		19-Oct-07		0:25:59		72.21		44.5

		8-Sep-07		2:07:10		75.2		47		8-Sep-07		2:06:20		71.6		55		8-Sep-07		2:07:53		72.21		51.5		19-Oct-07		2:25:59		71		44.5

		8-Sep-07		4:07:10		75.2		47		8-Sep-07		4:06:20		71		55.5		8-Sep-07		4:07:53		71.6		51		19-Oct-07		4:25:59		70.41		45

		8-Sep-07		6:07:10		75.81		47		8-Sep-07		6:06:20		71.6		54.5		8-Sep-07		6:07:53		71		55		19-Oct-07		6:25:59		70.41		45.5

		8-Sep-07		8:07:10		75.2		47.5		8-Sep-07		8:06:20		72.21		56		8-Sep-07		8:07:53		71.6		57		19-Oct-07		8:25:59		70.41		46.5

		8-Sep-07		10:07:10		74.6		44.5		8-Sep-07		10:06:20		72.21		45		8-Sep-07		10:07:53		72.21		46.5		19-Oct-07		10:25:59		71.6		47.5

		8-Sep-07		12:07:10		74.6		50.5		8-Sep-07		12:06:20		71		57		8-Sep-07		12:07:53		72.21		45		19-Oct-07		12:25:59		73.4		46

		8-Sep-07		14:07:10		74.01		46		8-Sep-07		14:06:20		72.21		46		8-Sep-07		14:07:53		71.6		46.5		19-Oct-07		14:25:59		75.2		45.5

		8-Sep-07		16:07:10		74.01		53		8-Sep-07		16:06:20		71		67		8-Sep-07		16:07:53		71.6		50.5		19-Oct-07		16:25:59		74.6		49

		8-Sep-07		18:07:10		74.01		53		8-Sep-07		18:06:20		70.41		63		8-Sep-07		18:07:53		71		53.5		19-Oct-07		18:25:59		74.6		50.5

		8-Sep-07		20:07:10		74.6		51		8-Sep-07		20:06:20		71		58		8-Sep-07		20:07:53		70.41		57		19-Oct-07		20:25:59		74.01		51.5

		8-Sep-07		22:07:10		74.6		48		8-Sep-07		22:06:20		71		55		8-Sep-07		22:07:53		70.41		54		19-Oct-07		22:25:59		74.01		51

		9-Sep-07		0:07:10		74.6		45		9-Sep-07		0:06:20		71		46		9-Sep-07		0:07:53		69.8		53		20-Oct-07		0:25:59		73.4		51.5

		9-Sep-07		2:07:10		74.01		45.5		9-Sep-07		2:06:20		71		52.5		9-Sep-07		2:07:53		69.2		52.5		20-Oct-07		2:25:59		72.8		52.5

		9-Sep-07		4:07:10		74.01		46.5		9-Sep-07		4:06:20		71		53.5		9-Sep-07		4:07:53		69.2		55		20-Oct-07		4:25:59		72.8		53

		9-Sep-07		6:07:10		74.01		48.5		9-Sep-07		6:06:20		71.6		56		9-Sep-07		6:07:53		68.61		56		20-Oct-07		6:25:59		72.8		54

		9-Sep-07		8:07:10		74.01		46		9-Sep-07		8:06:20		71		50		9-Sep-07		8:07:53		68.61		57		20-Oct-07		8:25:59		72.8		56.5

		9-Sep-07		10:07:10		73.4		50.5		9-Sep-07		10:06:20		70.41		57.5		9-Sep-07		10:07:53		68.61		58		20-Oct-07		10:25:59		74.01		57.5

		9-Sep-07		12:07:10		73.4		51.5		9-Sep-07		12:06:20		70.41		56.5		9-Sep-07		12:07:53		69.8		57.5		20-Oct-07		12:25:59		75.2		57.5

		9-Sep-07		14:07:10		73.4		55		9-Sep-07		14:06:20		70.41		63.5		9-Sep-07		14:07:53		70.41		54.5		20-Oct-07		14:25:59		75.81		57

		9-Sep-07		16:07:10		74.6		54		9-Sep-07		16:06:20		70.41		64.5		9-Sep-07		16:07:53		71		51		20-Oct-07		16:25:59		75.81		57

		9-Sep-07		18:07:10		75.2		50		9-Sep-07		18:06:20		70.41		55		9-Sep-07		18:07:53		70.41		60		20-Oct-07		18:25:59		75.81		56

		9-Sep-07		20:07:10		75.2		44.5		9-Sep-07		20:06:20		71.6		47		9-Sep-07		20:07:53		70.41		55		20-Oct-07		20:25:59		74.01		54.5

		9-Sep-07		22:07:10		74.6		47		9-Sep-07		22:06:20		71		54.5		9-Sep-07		22:07:53		69.8		54		20-Oct-07		22:25:59		72.8		53

		10-Sep-07		0:07:10		74.6		46		10-Sep-07		0:06:20		71		52.5		10-Sep-07		0:07:53		69.2		53.5		21-Oct-07		0:25:59		71.6		51

		10-Sep-07		2:07:10		74.6		45.5		10-Sep-07		2:06:20		71.6		51		10-Sep-07		2:07:53		68.61		53.5		21-Oct-07		2:25:59		71		50

		10-Sep-07		4:07:10		74.01		45		10-Sep-07		4:06:20		71.6		50		10-Sep-07		4:07:53		68.61		54		21-Oct-07		4:25:59		70.41		49.5

		10-Sep-07		6:07:10		74.01		45		10-Sep-07		6:06:20		71		51		10-Sep-07		6:07:53		68		54.5		21-Oct-07		6:25:59		69.8		47.5

		10-Sep-07		8:07:10		72.8		44.5		10-Sep-07		8:06:20		69.8		50.5		10-Sep-07		8:07:53		67.4		54.5		21-Oct-07		8:25:59		69.2		45.5

		10-Sep-07		10:07:10		72.8		45.5		10-Sep-07		10:06:20		69.8		46.5		10-Sep-07		10:07:53		67.4		55		21-Oct-07		10:25:59		69.2		48

		10-Sep-07		12:07:10		72.8		46		10-Sep-07		12:06:20		70.41		49.5		10-Sep-07		12:07:53		68.61		56		21-Oct-07		12:25:59		70.41		45.5

		10-Sep-07		14:07:10		73.4		49		10-Sep-07		14:06:20		70.41		56.5		10-Sep-07		14:07:53		69.8		59.5		21-Oct-07		14:25:59		71		42

		10-Sep-07		16:07:10		74.01		53.5		10-Sep-07		16:06:20		70.41		62.5		10-Sep-07		16:07:53		70.41		49		21-Oct-07		16:25:59		72.21		39

		10-Sep-07		18:07:10		74.6		52.5		10-Sep-07		18:06:20		70.41		63		10-Sep-07		18:07:53		71		56		21-Oct-07		18:25:59		73.4		36.5

		10-Sep-07		20:07:10		75.2		49		10-Sep-07		20:06:20		71.6		55.5		10-Sep-07		20:07:53		71.6		54.5		21-Oct-07		20:25:59		72.21		38

		10-Sep-07		22:07:10		74.6		48		10-Sep-07		22:06:20		71		56		10-Sep-07		22:07:53		70.41		54		21-Oct-07		22:25:59		71		40

		11-Sep-07		0:07:10		74.6		47		11-Sep-07		0:06:20		71		54.5		11-Sep-07		0:07:53		69.8		53.5		22-Oct-07		0:25:59		69.8		39.5

		11-Sep-07		2:07:10		74.01		45.5		11-Sep-07		2:06:20		71		52		11-Sep-07		2:07:53		68.61		53.5		22-Oct-07		2:25:59		69.2		39.5

		11-Sep-07		4:07:10		74.01		44.5		11-Sep-07		4:06:20		71.6		48.5		11-Sep-07		4:07:53		68		53.5		22-Oct-07		4:25:59		69.2		39

		11-Sep-07		6:07:10		74.01		43		11-Sep-07		6:06:20		71		48		11-Sep-07		6:07:53		68.61		52		22-Oct-07		6:25:59		68.61		38.5

		11-Sep-07		8:07:10		74.01		43.5		11-Sep-07		8:06:20		70.41		45		11-Sep-07		8:07:53		71.6		51.5		22-Oct-07		8:25:59		68		37.5

		11-Sep-07		10:07:10		74.6		46.5		11-Sep-07		10:06:20		71		45.5		11-Sep-07		10:07:53		71.6		48		22-Oct-07		10:25:59		68		37.5

		11-Sep-07		12:07:10		74.01		52.5		11-Sep-07		12:06:20		71		63		11-Sep-07		12:07:53		72.21		46		22-Oct-07		12:25:59		69.2		36

		11-Sep-07		14:07:10		74.6		46.5		11-Sep-07		14:06:20		71.6		45		11-Sep-07		14:07:53		71.6		45		22-Oct-07		14:25:59		72.21		33

		11-Sep-07		16:07:10		75.2		48.5		11-Sep-07		16:06:20		70.41		52		11-Sep-07		16:07:53		71		63		22-Oct-07		16:25:59		72.8		33

		11-Sep-07		18:07:10		74.6		49.5		11-Sep-07		18:06:20		70.41		54		11-Sep-07		18:07:53		71		60.5		22-Oct-07		18:25:59		72.8		32.5

		11-Sep-07		20:07:10		75.2		50.5		11-Sep-07		20:06:20		71		58.5		11-Sep-07		20:07:53		70.41		57.5		22-Oct-07		20:25:59		72.8		31.5

		11-Sep-07		22:07:10		75.2		45.5		11-Sep-07		22:06:20		71.6		51.5		11-Sep-07		22:07:53		72.21		52		22-Oct-07		22:25:59		72.21		35

		12-Sep-07		0:07:10		74.6		46.5		12-Sep-07		0:06:20		71.6		53		12-Sep-07		0:07:53		71.6		51		23-Oct-07		0:25:59		71.6		36

		12-Sep-07		2:07:10		74.6		45.5		12-Sep-07		2:06:20		71.6		51.5		12-Sep-07		2:07:53		71		51		23-Oct-07		2:25:59		70.41		37

		12-Sep-07		4:07:10		74.01		46.5		12-Sep-07		4:06:20		70.41		53.5		12-Sep-07		4:07:53		70.41		52		23-Oct-07		4:25:59		69.8		36.5

		12-Sep-07		6:07:10		74.6		46.5		12-Sep-07		6:06:20		71		53		12-Sep-07		6:07:53		70.41		50		23-Oct-07		6:25:59		69.8		36.5

		12-Sep-07		8:07:10		74.01		45.5		12-Sep-07		8:06:20		71.6		44.5		12-Sep-07		8:07:53		71		48.5		23-Oct-07		8:25:59		68.61		37.5

		12-Sep-07		10:07:10		74.01		47.5		12-Sep-07		10:06:20		72.21		55		12-Sep-07		10:07:53		71.6		56		23-Oct-07		10:25:59		71.6		39

		12-Sep-07		12:07:10		74.6		47		12-Sep-07		12:06:20		71.6		53		12-Sep-07		12:07:53		72.21		52		23-Oct-07		12:25:59		74.6		37.5

		12-Sep-07		14:07:10		74.01		46		12-Sep-07		14:06:20		71.6		43		12-Sep-07		14:07:53		71.6		54		23-Oct-07		14:25:59		75.2		37

		12-Sep-07		16:07:10		74.6		49		12-Sep-07		16:06:20		71		53		12-Sep-07		16:07:53		71.6		46.5		23-Oct-07		16:25:59		75.81		36.5

		12-Sep-07		18:07:10		74.6		53		12-Sep-07		18:06:20		70.41		65		12-Sep-07		18:07:53		71		62.5		23-Oct-07		18:25:59		75.81		35.5

		12-Sep-07		20:07:10		74.6		52		12-Sep-07		20:06:20		71		60.5		12-Sep-07		20:07:53		71		54.5		23-Oct-07		20:25:59		74.6		36

		12-Sep-07		22:07:10		74.6		49		12-Sep-07		22:06:20		71.6		56.5		12-Sep-07		22:07:53		72.8		52.5		23-Oct-07		22:25:59		74.01		37.5

		13-Sep-07		0:07:10		75.2		49		13-Sep-07		0:06:20		71.6		56.5		13-Sep-07		0:07:53		72.8		53		24-Oct-07		0:25:59		73.4		38.5

		13-Sep-07		2:07:10		75.2		48.5		13-Sep-07		2:06:20		71		57		13-Sep-07		2:07:53		72.21		53		24-Oct-07		2:25:59		72.21		39

		13-Sep-07		4:07:10		74.6		48.5		13-Sep-07		4:06:20		70.41		58.5		13-Sep-07		4:07:53		71.6		56		24-Oct-07		4:25:59		71		39.5

		13-Sep-07		6:07:10		75.2		49		13-Sep-07		6:06:20		71		58		13-Sep-07		6:07:53		70.41		50.5		24-Oct-07		6:25:59		71		39

		13-Sep-07		8:07:10		74.6		50		13-Sep-07		8:06:20		71		52.5		13-Sep-07		8:07:53		71		56		24-Oct-07		8:25:59		69.8		39.5

		13-Sep-07		10:07:10		74.01		45.5		13-Sep-07		10:06:20		71.6		44.5		13-Sep-07		10:07:53		71.6		57		24-Oct-07		10:25:59		72.21		42.5

		13-Sep-07		12:07:10		74.6		48		13-Sep-07		12:06:20		71.6		52.5		13-Sep-07		12:07:53		71.6		48		24-Oct-07		12:25:59		75.2		41

		13-Sep-07		14:07:10		74.6		45.5		13-Sep-07		14:06:20		71.6		44		13-Sep-07		14:07:53		70.41		61.5		24-Oct-07		14:25:59		75.81		40.5

		13-Sep-07		16:07:10		74.6		52.5		13-Sep-07		16:06:20		70.41		58		13-Sep-07		16:07:53		71		61.5		24-Oct-07		16:25:59		76.4		40.5

		13-Sep-07		18:07:10		75.2		47		13-Sep-07		18:06:20		70.41		51		13-Sep-07		18:07:53		70.41		59.5		24-Oct-07		18:25:59		75.81		42.5

		13-Sep-07		20:07:10		75.2		48		13-Sep-07		20:06:20		71.6		55.5		13-Sep-07		20:07:53		71.6		55		24-Oct-07		20:25:59		75.2		45

		13-Sep-07		22:07:10		74.6		47.5		13-Sep-07		22:06:20		71		54.5		13-Sep-07		22:07:53		71.6		52.5		24-Oct-07		22:25:59		75.81		44.5

		14-Sep-07		0:07:10		74.6		46.5		14-Sep-07		0:06:20		71.6		53		14-Sep-07		0:07:53		71.6		51.5		25-Oct-07		0:25:59		74.6		43

		14-Sep-07		2:07:10		74.6		46.5		14-Sep-07		2:06:20		71		51.5		14-Sep-07		2:07:53		71.6		51.5		25-Oct-07		2:25:59		73.4		43

		14-Sep-07		4:07:10		74.6		44.5		14-Sep-07		4:06:20		71.6		50		14-Sep-07		4:07:53		71		45		25-Oct-07		4:25:59		72.21		43

		14-Sep-07		6:07:10		74.6		43.5		14-Sep-07		6:06:20		71		49.5		14-Sep-07		6:07:53		71		51		25-Oct-07		6:25:59		71.6		43

		14-Sep-07		8:07:10		74.01		46		14-Sep-07		8:06:20		71.6		54		14-Sep-07		8:07:53		71		53		25-Oct-07		8:25:59		71		42.5

		14-Sep-07		10:07:10		74.6		46.5		14-Sep-07		10:06:20		71.6		55.5		14-Sep-07		10:07:53		72.21		47.5		25-Oct-07		10:25:59		73.4		44

		14-Sep-07		12:07:10		74.01		47.5		14-Sep-07		12:06:20		70.41		53		14-Sep-07		12:07:53		72.21		43		25-Oct-07		12:25:59		75.2		44

		14-Sep-07		14:07:10		74.6		49		14-Sep-07		14:06:20		71.6		56		14-Sep-07		14:07:53		71.6		48		25-Oct-07		14:25:59		75.81		43

		14-Sep-07		16:07:10		75.2		46.5		14-Sep-07		16:06:20		71		53		14-Sep-07		16:07:53		71.6		58.5		25-Oct-07		16:25:59		75.81		41

		14-Sep-07		18:07:10		75.2		50.5		14-Sep-07		18:06:20		71		64.5		14-Sep-07		18:07:53		71		62		25-Oct-07		18:25:59		75.81		44.5

		14-Sep-07		20:07:10		75.2		50		14-Sep-07		20:06:20		71.6		59		14-Sep-07		20:07:53		72.8		55.5		25-Oct-07		20:25:59		75.2		43.5

		14-Sep-07		22:07:10		75.2		50.5		14-Sep-07		22:06:20		71.6		59.5		14-Sep-07		22:07:53		74.01		52.5		25-Oct-07		22:25:59		74.6		42.5

		15-Sep-07		0:07:10		75.2		48.5		15-Sep-07		0:06:20		71		51.5		15-Sep-07		0:07:53		73.4		52		26-Oct-07		0:25:59		73.4		42.5

		15-Sep-07		2:07:10		74.6		48		15-Sep-07		2:06:20		71.6		56		15-Sep-07		2:07:53		73.4		52		26-Oct-07		2:25:59		72.21		43

		15-Sep-07		4:07:10		74.6		48.5		15-Sep-07		4:06:20		71.6		55.5		15-Sep-07		4:07:53		72.21		54.5		26-Oct-07		4:25:59		71		42.5

		15-Sep-07		6:07:10		75.2		49.5		15-Sep-07		6:06:20		71.6		58.5		15-Sep-07		6:07:53		71		51		26-Oct-07		6:25:59		70.41		41.5

		15-Sep-07		8:07:10		75.2		46		15-Sep-07		8:06:20		72.21		49		15-Sep-07		8:07:53		71.6		56		26-Oct-07		8:25:59		69.2		41

		15-Sep-07		10:07:10		74.6		50		15-Sep-07		10:06:20		71.6		57.5		15-Sep-07		10:07:53		71.6		50		26-Oct-07		10:25:59		71		44.5

		15-Sep-07		12:07:10		74.01		51		15-Sep-07		12:06:20		71		51		15-Sep-07		12:07:53		72.21		49.5		26-Oct-07		12:25:59		74.6		43.5

		15-Sep-07		14:07:10		74.6		46.5		15-Sep-07		14:06:20		71.6		47.5		15-Sep-07		14:07:53		71.6		54		26-Oct-07		14:25:59		75.81		43.5

		15-Sep-07		16:07:10		74.6		45.5		15-Sep-07		16:06:20		69.2		50.5		15-Sep-07		16:07:53		71.6		53		26-Oct-07		16:25:59		76.4		43.5

		15-Sep-07		18:07:10		73.4		46		15-Sep-07		18:06:20		68		50		15-Sep-07		18:07:53		71		48.5		26-Oct-07		18:25:59		75.81		44

		15-Sep-07		20:07:10		74.6		45		15-Sep-07		20:06:20		71		52		15-Sep-07		20:07:53		71		50.5		26-Oct-07		20:25:59		74.6		43

		15-Sep-07		22:07:10		75.2		44.5		15-Sep-07		22:06:20		71.6		52		15-Sep-07		22:07:53		72.8		48		26-Oct-07		22:25:59		73.4		42.5

		16-Sep-07		0:07:10		75.2		44		16-Sep-07		0:06:20		71		51.5		16-Sep-07		0:07:53		72.8		48		27-Oct-07		0:25:59		72.21		43

		16-Sep-07		2:07:10		75.2		43		16-Sep-07		2:06:20		71.6		49.5		16-Sep-07		2:07:53		72.21		47.5		27-Oct-07		2:25:59		71		44

		16-Sep-07		4:07:10		74.6		44		16-Sep-07		4:06:20		71		51		16-Sep-07		4:07:53		71		48.5		27-Oct-07		4:25:59		70.41		44.5

		16-Sep-07		6:07:10		74.01		43		16-Sep-07		6:06:20		69.8		44		16-Sep-07		6:07:53		71		49		27-Oct-07		6:25:59		70.41		45.5

		16-Sep-07		8:07:10		73.4		44		16-Sep-07		8:06:20		68.61		54		16-Sep-07		8:07:53		70.41		48		27-Oct-07		8:25:59		70.41		46

		16-Sep-07		10:07:10		73.4		45.5		16-Sep-07		10:06:20		68.61		57		16-Sep-07		10:07:53		69.8		52.5		27-Oct-07		10:25:59		72.21		45.5

		16-Sep-07		12:07:10		72.8		46		16-Sep-07		12:06:20		68.61		47.5		16-Sep-07		12:07:53		70.41		56		27-Oct-07		12:25:59		74.6		44

		16-Sep-07		14:07:10		73.4		44.5		16-Sep-07		14:06:20		68.61		47		16-Sep-07		14:07:53		71		51		27-Oct-07		14:25:59		75.2		42.5

		16-Sep-07		16:07:10		74.6		45		16-Sep-07		16:06:20		68.61		52		16-Sep-07		16:07:53		71		50.5		27-Oct-07		16:25:59		75.2		43.5

		16-Sep-07		18:07:10		74.6		46		16-Sep-07		18:06:20		68.61		59		16-Sep-07		18:07:53		70.41		53		27-Oct-07		18:25:59		74.6		44

		16-Sep-07		20:07:10		75.81		45		16-Sep-07		20:06:20		71		54		16-Sep-07		20:07:53		71.6		51.5		27-Oct-07		20:25:59		72.21		43.5

		16-Sep-07		22:07:10		75.2		44.5		16-Sep-07		22:06:20		71		52.5		16-Sep-07		22:07:53		72.21		49.5		27-Oct-07		22:25:59		71.6		44

		17-Sep-07		0:07:10		75.2		43		17-Sep-07		0:06:20		71		51.5		17-Sep-07		0:07:53		71.6		49		28-Oct-07		0:25:59		70.41		43.5

		17-Sep-07		2:07:10		74.6		42.5		17-Sep-07		2:06:20		70.41		49.5		17-Sep-07		2:07:53		70.41		48.5		28-Oct-07		2:25:59		69.2		42.5

		17-Sep-07		4:07:10		74.01		41.5		17-Sep-07		4:06:20		70.41		47		17-Sep-07		4:07:53		69.8		48		28-Oct-07		4:25:59		68.61		42

		17-Sep-07		6:07:10		73.4		41.5		17-Sep-07		6:06:20		69.8		42		17-Sep-07		6:07:53		69.2		49		28-Oct-07		6:25:59		68.61		41.5

		17-Sep-07		8:07:10		72.21		44.5		17-Sep-07		8:06:20		68		52.5		17-Sep-07		8:07:53		69.2		50		28-Oct-07		8:25:59		68		42

		17-Sep-07		10:07:10		72.8		47.5		17-Sep-07		10:06:20		68.61		57.5		17-Sep-07		10:07:53		70.41		49.5		28-Oct-07		10:25:59		67.4		44.5

		17-Sep-07		12:07:10		72.8		50.5		17-Sep-07		12:06:20		68.61		61		17-Sep-07		12:07:53		71		49.5		28-Oct-07		12:25:59		68.61		45.5

		17-Sep-07		14:07:10		74.01		45.5		17-Sep-07		14:06:20		69.2		52		17-Sep-07		14:07:53		71		57		28-Oct-07		14:25:59		69.8		46

		17-Sep-07		16:07:10		74.6		49.5		17-Sep-07		16:06:20		68.61		58		17-Sep-07		16:07:53		71		51.5		28-Oct-07		16:25:59		71.6		47

		17-Sep-07		18:07:10		74.6		48.5		17-Sep-07		18:06:20		68.61		61.5		17-Sep-07		18:07:53		71		50		28-Oct-07		18:25:59		71.6		45

		17-Sep-07		20:07:10		75.81		46		17-Sep-07		20:06:20		71		55		17-Sep-07		20:07:53		74.01		48		28-Oct-07		20:25:59		70.41		45

		17-Sep-07		22:07:10		75.81		44		17-Sep-07		22:06:20		71.6		52		17-Sep-07		22:07:53		74.6		46.5		28-Oct-07		22:25:59		69.8		44.5

		18-Sep-07		0:07:10		75.2		42.5		18-Sep-07		0:06:20		71		50		18-Sep-07		0:07:53		73.4		45.5		29-Oct-07		0:25:59		69.2		44

		18-Sep-07		2:07:10		75.2		41.5		18-Sep-07		2:06:20		71.6		48		18-Sep-07		2:07:53		72.21		45.5		29-Oct-07		2:25:59		68.61		44

		18-Sep-07		4:07:10		74.6		40.5		18-Sep-07		4:06:20		71		46.5		18-Sep-07		4:07:53		71		45.5		29-Oct-07		4:25:59		68.61		44

		18-Sep-07		6:07:10		74.6		39.5		18-Sep-07		6:06:20		69.8		45		18-Sep-07		6:07:53		70.41		45.5		29-Oct-07		6:25:59		68		43.5

		18-Sep-07		8:07:10		72.8		40		18-Sep-07		8:06:20		69.2		39.5		18-Sep-07		8:07:53		71		44.5		29-Oct-07		8:25:59		67.4		43

		18-Sep-07		10:07:10		73.4		42.5		18-Sep-07		10:06:20		70.41		46.5		18-Sep-07		10:07:53		71.6		42.5		29-Oct-07		10:25:59		68.61		45.5

		18-Sep-07		12:07:10		73.4		44.5		18-Sep-07		12:06:20		69.8		51		18-Sep-07		12:07:53		72.21		43.5		29-Oct-07		12:25:59		70.41		46.5

		18-Sep-07		14:07:10		73.4		42.5		18-Sep-07		14:06:20		69.8		42		18-Sep-07		14:07:53		71.6		43.5		29-Oct-07		14:25:59		72.21		47.5

		18-Sep-07		16:07:10		74.01		47.5		18-Sep-07		16:06:20		69.2		61		18-Sep-07		16:07:53		71		49.5		29-Oct-07		16:25:59		74.6		47.5

		18-Sep-07		18:07:10		74.01		43.5		18-Sep-07		18:06:20		69.2		49.5		18-Sep-07		18:07:53		71		43		29-Oct-07		18:25:59		75.2		47

		18-Sep-07		20:07:10		74.6		44		18-Sep-07		20:06:20		71.6		50		18-Sep-07		20:07:53		71.6		51.5		29-Oct-07		20:25:59		74.01		46

		18-Sep-07		22:07:10		75.2		42.5		18-Sep-07		22:06:20		71.6		50.5		18-Sep-07		22:07:53		73.4		46		29-Oct-07		22:25:59		72.8		46

		19-Sep-07		0:07:10		75.2		42.5		19-Sep-07		0:06:20		71		49.5		19-Sep-07		0:07:53		73.4		44.5		30-Oct-07		0:25:59		71.6		46

		19-Sep-07		2:07:10		74.6		41		19-Sep-07		2:06:20		71		48		19-Sep-07		2:07:53		72.8		44		30-Oct-07		2:25:59		71		46

		19-Sep-07		4:07:10		74.6		40		19-Sep-07		4:06:20		71		46		19-Sep-07		4:07:53		71		44		30-Oct-07		4:25:59		69.8		45.5

		19-Sep-07		6:07:10		74.01		38.5		19-Sep-07		6:06:20		70.41		41.5		19-Sep-07		6:07:53		70.41		43.5		30-Oct-07		6:25:59		69.8		46

		19-Sep-07		8:07:10		72.8		41		19-Sep-07		8:06:20		69.8		48		19-Sep-07		8:07:53		71		42.5		30-Oct-07		8:25:59		69.2		48

		19-Sep-07		10:07:10		72.8		43.5		19-Sep-07		10:06:20		70.41		51.5		19-Sep-07		10:07:53		71.6		45.5		30-Oct-07		10:25:59		71		48

		19-Sep-07		12:07:10		73.4		45.5		19-Sep-07		12:06:20		70.41		56		19-Sep-07		12:07:53		72.21		53		30-Oct-07		12:25:59		72.8		49

		19-Sep-07		14:07:10		74.6		43.5		19-Sep-07		14:06:20		72.21		49		19-Sep-07		14:07:53		71.6		41		30-Oct-07		14:25:59		74.6		48

		19-Sep-07		16:07:10		73.4		42.5		19-Sep-07		16:06:20		68.61		45		19-Sep-07		16:07:53		72.21		48		30-Oct-07		16:25:59		75.2		47.5

		19-Sep-07		18:07:10		73.4		42		19-Sep-07		18:06:20		68.61		43		19-Sep-07		18:07:53		71		50		30-Oct-07		18:25:59		75.2		45

		19-Sep-07		20:07:10		74.6		42		19-Sep-07		20:06:20		70.41		49		19-Sep-07		20:07:53		71		47.5		30-Oct-07		20:25:59		72.8		45.5

		19-Sep-07		22:07:10		74.6		39.5		19-Sep-07		22:06:20		70.41		46.5		19-Sep-07		22:07:53		72.21		42.5		30-Oct-07		22:25:59		71.6		46.5

		20-Sep-07		0:07:10		74.6		38		20-Sep-07		0:06:20		70.41		44		20-Sep-07		0:07:53		71.6		41		31-Oct-07		0:25:59		71		46.5

		20-Sep-07		2:07:10		74.01		37		20-Sep-07		2:06:20		70.41		42		20-Sep-07		2:07:53		71		40.5		31-Oct-07		2:25:59		70.41		47.5

		20-Sep-07		4:07:10		73.4		36		20-Sep-07		4:06:20		70.41		41		20-Sep-07		4:07:53		69.8		40.5		31-Oct-07		4:25:59		70.41		48

		20-Sep-07		6:07:10		72.8		36		20-Sep-07		6:06:20		69.8		40		20-Sep-07		6:07:53		69.8		40		31-Oct-07		6:25:59		70.41		48.5

		20-Sep-07		8:07:10		72.8		37.5		20-Sep-07		8:06:20		69.8		44		20-Sep-07		8:07:53		71		39.5		31-Oct-07		8:25:59		69.8		48

		20-Sep-07		10:07:10		73.4		37.5		20-Sep-07		10:06:20		70.41		45.5		20-Sep-07		10:07:53		71.6		35.5		31-Oct-07		10:25:59		71.6		48

		20-Sep-07		12:07:10		73.4		36		20-Sep-07		12:06:20		69.2		35.5		20-Sep-07		12:07:53		72.21		34.5		31-Oct-07		12:25:59		72.21		47.5

		20-Sep-07		14:07:10		73.4		34		20-Sep-07		14:06:20		69.8		36		20-Sep-07		14:07:53		71.6		39.5		31-Oct-07		14:25:59		73.4		46.5

		20-Sep-07		16:07:10		73.4		34		20-Sep-07		16:06:20		68.61		37.5		20-Sep-07		16:07:53		71		33		31-Oct-07		16:25:59		74.6		46

		20-Sep-07		18:07:10		74.01		34.5		20-Sep-07		18:06:20		68		41.5		20-Sep-07		18:07:53		70.41		38.5		31-Oct-07		18:25:59		75.2		44.5

		20-Sep-07		20:07:10		74.6		36		20-Sep-07		20:06:20		69.8		41		20-Sep-07		20:07:53		72.8		37.5		31-Oct-07		20:25:59		72.8		44.5

		20-Sep-07		22:07:10		74.6		34		20-Sep-07		22:06:20		70.41		39.5		20-Sep-07		22:07:53		72.21		36.5		31-Oct-07		22:25:59		72.21		45.5

		21-Sep-07		0:07:10		74.01		34.5		21-Sep-07		0:06:20		69.8		40.5		21-Sep-07		0:07:53		71.6		37.5		1-Nov-07		0:25:59		70.41		46

		21-Sep-07		2:07:10		74.01		33.5		21-Sep-07		2:06:20		70.41		36		21-Sep-07		2:07:53		71		37		1-Nov-07		2:25:59		69.8		47

		21-Sep-07		4:07:10		73.4		33		21-Sep-07		4:06:20		70.41		38		21-Sep-07		4:07:53		69.8		37		1-Nov-07		4:25:59		69.8		48

		21-Sep-07		6:07:10		73.4		34.5		21-Sep-07		6:06:20		69.8		39.5		21-Sep-07		6:07:53		69.8		39		1-Nov-07		6:25:59		69.8		48.5

		21-Sep-07		8:07:10		72.8		37.5		21-Sep-07		8:06:20		69.8		44.5		21-Sep-07		8:07:53		71		39		1-Nov-07		8:25:59		69.8		48.5

		21-Sep-07		10:07:10		72.8		38.5		21-Sep-07		10:06:20		69.8		41.5		21-Sep-07		10:07:53		71.6		42		1-Nov-07		10:25:59		72.21		48

		21-Sep-07		12:07:10		74.6		37		21-Sep-07		12:06:20		73.4		36		21-Sep-07		12:07:53		71.6		36.5		1-Nov-07		12:25:59		72.8		48.5

		21-Sep-07		14:07:10		74.6		38.5		21-Sep-07		14:06:20		71.6		45		21-Sep-07		14:07:53		71		41.5		1-Nov-07		14:25:59		73.4		48.5

		21-Sep-07		16:07:10		74.6		38		21-Sep-07		16:06:20		70.41		45.5		21-Sep-07		16:07:53		71		41		1-Nov-07		16:25:59		74.01		49.5

		21-Sep-07		18:07:10		74.6		37.5		21-Sep-07		18:06:20		70.41		44		21-Sep-07		18:07:53		71		40.5		1-Nov-07		18:25:59		74.01		48

		21-Sep-07		20:07:10		75.81		35		21-Sep-07		20:06:20		72.21		39		21-Sep-07		20:07:53		71.6		39		1-Nov-07		20:25:59		72.21		48

		21-Sep-07		22:07:10		75.81		33.5		21-Sep-07		22:06:20		72.8		37.5		21-Sep-07		22:07:53		71		38		1-Nov-07		22:25:59		71.6		49

		22-Sep-07		0:07:10		75.2		33		22-Sep-07		0:06:20		72.21		37		22-Sep-07		0:07:53		70.41		38.5		2-Nov-07		0:25:59		71		49

		22-Sep-07		2:07:10		74.6		32.5		22-Sep-07		2:06:20		71.6		36.5		22-Sep-07		2:07:53		68.61		38.5		2-Nov-07		2:25:59		70.41		49.5

		22-Sep-07		4:07:10		73.4		33		22-Sep-07		4:06:20		70.41		37.5		22-Sep-07		4:07:53		68		39.5		2-Nov-07		4:25:59		69.8		49

		22-Sep-07		6:07:10		72.8		33.5		22-Sep-07		6:06:20		69.8		37.5		22-Sep-07		6:07:53		67.4		40.5		2-Nov-07		6:25:59		69.8		48

		22-Sep-07		8:07:10		72.8		33.5		22-Sep-07		8:06:20		71.6		37.5		22-Sep-07		8:07:53		69.2		40		2-Nov-07		8:25:59		71.6		46.5

		22-Sep-07		10:07:10		73.4		36		22-Sep-07		10:06:20		72.21		39		22-Sep-07		10:07:53		71.6		43.5		2-Nov-07		10:25:59		71.6		48

		22-Sep-07		12:07:10		73.4		36.5		22-Sep-07		12:06:20		71.6		40.5		22-Sep-07		12:07:53		71.6		44.5		2-Nov-07		12:25:59		73.4		48

		22-Sep-07		14:07:10		74.01		38		22-Sep-07		14:06:20		71		40.5		22-Sep-07		14:07:53		72.21		43		2-Nov-07		14:25:59		75.2		48

		22-Sep-07		16:07:10		74.6		40.5		22-Sep-07		16:06:20		70.41		47		22-Sep-07		16:07:53		71.6		47		2-Nov-07		16:25:59		75.2		49.5

		22-Sep-07		18:07:10		74.6		38.5		22-Sep-07		18:06:20		70.41		45		22-Sep-07		18:07:53		71		38.5		2-Nov-07		18:25:59		75.2		50

		22-Sep-07		20:07:10		75.2		37.5		22-Sep-07		20:06:20		72.21		42		22-Sep-07		20:07:53		70.41		44		2-Nov-07		20:25:59		74.6		46

		22-Sep-07		22:07:10		75.81		37.5		22-Sep-07		22:06:20		72.8		42.5		22-Sep-07		22:07:53		71.6		43		2-Nov-07		22:25:59		73.4		45.5

		23-Sep-07		0:07:10		75.81		38.5		23-Sep-07		0:06:20		73.4		43.5		23-Sep-07		0:07:53		71.6		44.5		3-Nov-07		0:25:59		71.6		45

		23-Sep-07		2:07:10		75.2		40		23-Sep-07		2:06:20		72.21		46.5		23-Sep-07		2:07:53		71		46.5		3-Nov-07		2:25:59		69.8		44

		23-Sep-07		4:07:10		75.2		41		23-Sep-07		4:06:20		72.8		46		23-Sep-07		4:07:53		71		47.5		3-Nov-07		4:25:59		69.2		43

		23-Sep-07		6:07:10		74.6		42		23-Sep-07		6:06:20		71.6		44		23-Sep-07		6:07:53		71.6		48		3-Nov-07		6:25:59		69.2		42

		23-Sep-07		8:07:10		74.01		44.5		23-Sep-07		8:06:20		69.8		52		23-Sep-07		8:07:53		71		43.5		3-Nov-07		8:25:59		71.6		39.5

		23-Sep-07		10:07:10		73.4		44.5		23-Sep-07		10:06:20		70.41		50.5		23-Sep-07		10:07:53		71.6		56		3-Nov-07		10:25:59		71.6		42.5

		23-Sep-07		12:07:10		74.01		44.5		23-Sep-07		12:06:20		70.41		48		23-Sep-07		12:07:53		71		49		3-Nov-07		12:25:59		75.2		42.5

		23-Sep-07		14:07:10		73.4		48.5		23-Sep-07		14:06:20		70.41		56.5		23-Sep-07		14:07:53		71		54		3-Nov-07		14:25:59		76.4		42.5

		23-Sep-07		16:07:10		74.01		50.5		23-Sep-07		16:06:20		70.41		60		23-Sep-07		16:07:53		70.41		51		3-Nov-07		16:25:59		75.81		42

		23-Sep-07		18:07:10		73.4		50.5		23-Sep-07		18:06:20		70.41		59		23-Sep-07		18:07:53		69.8		56.5		3-Nov-07		18:25:59		75.81		43.5

		23-Sep-07		20:07:10		74.6		49.5		23-Sep-07		20:06:20		72.21		55		23-Sep-07		20:07:53		69.8		56		3-Nov-07		20:25:59		74.6		43

		23-Sep-07		22:07:10		74.6		48		23-Sep-07		22:06:20		72.21		52.5		23-Sep-07		22:07:53		70.41		55.5		3-Nov-07		22:25:59		73.4		43.5

		24-Sep-07		0:07:10		74.6		47.5		24-Sep-07		0:06:20		72.21		52		24-Sep-07		0:07:53		69.8		54.5		4-Nov-07		0:25:59		71.6		43

		24-Sep-07		2:07:10		74.6		47.5		24-Sep-07		2:06:20		72.21		52		24-Sep-07		2:07:53		69.8		55		4-Nov-07		2:25:59		70.41		42

		24-Sep-07		4:07:10		74.6		47		24-Sep-07		4:06:20		72.21		51.5		24-Sep-07		4:07:53		69.8		54.5		4-Nov-07		4:25:59		69.2		41

		24-Sep-07		6:07:10		74.01		46.5		24-Sep-07		6:06:20		71.6		46		24-Sep-07		6:07:53		69.8		54.5		4-Nov-07		6:25:59		68.61		40

		24-Sep-07		8:07:10		73.4		49		24-Sep-07		8:06:20		70.41		56		24-Sep-07		8:07:53		69.2		55		4-Nov-07		8:25:59		67.4		38.5

		24-Sep-07		10:07:10		72.8		50.5		24-Sep-07		10:06:20		69.8		56.5		24-Sep-07		10:07:53		69.8		55.5		4-Nov-07		10:25:59		68		40.5

		24-Sep-07		12:07:10		72.8		51		24-Sep-07		12:06:20		69.2		55.5		24-Sep-07		12:07:53		69.8		56		4-Nov-07		12:25:59		69.2		42.5

		24-Sep-07		14:07:10		73.4		50		24-Sep-07		14:06:20		69.8		56.5		24-Sep-07		14:07:53		70.41		51.5		4-Nov-07		14:25:59		71		43

		24-Sep-07		16:07:10		74.01		46		24-Sep-07		16:06:20		69.8		44		24-Sep-07		16:07:53		70.41		48		4-Nov-07		16:25:59		72.21		43

		24-Sep-07		18:07:10		74.01		45		24-Sep-07		18:06:20		69.8		51		24-Sep-07		18:07:53		71		46.5		4-Nov-07		18:25:59		72.8		41.5

		24-Sep-07		20:07:10		75.2		40		24-Sep-07		20:06:20		72.8		39.5		24-Sep-07		20:07:53		72.21		45		4-Nov-07		20:25:59		71.6		39

		24-Sep-07		22:07:10		75.81		40		24-Sep-07		22:06:20		73.4		43.5		24-Sep-07		22:07:53		71.6		45.5		4-Nov-07		22:25:59		70.41		39.5

		25-Sep-07		0:07:10		74.6		39		25-Sep-07		0:06:20		72.21		43		25-Sep-07		0:07:53		70.41		45		5-Nov-07		0:25:59		69.8		40

		25-Sep-07		2:07:10		74.01		37.5		25-Sep-07		2:06:20		71.6		41		25-Sep-07		2:07:53		69.2		44		5-Nov-07		2:25:59		68.61		40

		25-Sep-07		4:07:10		73.4		37		25-Sep-07		4:06:20		71		40		25-Sep-07		4:07:53		68		43		5-Nov-07		4:25:59		68		39

		25-Sep-07		6:07:10		72.8		36.5		25-Sep-07		6:06:20		69.8		38.5		25-Sep-07		6:07:53		68.61		42		5-Nov-07		6:25:59		67.4		38.5

		25-Sep-07		8:07:10		72.8		37		25-Sep-07		8:06:20		71		41		25-Sep-07		8:07:53		69.2		41		5-Nov-07		8:25:59		66.2		37.5

		25-Sep-07		10:07:10		74.01		38		25-Sep-07		10:06:20		72.21		40		25-Sep-07		10:07:53		71		48		5-Nov-07		10:25:59		67.4		39.5

		25-Sep-07		12:07:10		74.6		39		25-Sep-07		12:06:20		71.6		43		25-Sep-07		12:07:53		71.6		43		5-Nov-07		12:25:59		69.2		40.5

		25-Sep-07		14:07:10		74.01		34.5		25-Sep-07		14:06:20		71.6		37.5		25-Sep-07		14:07:53		71.6		35		5-Nov-07		14:25:59		71		41.5

		25-Sep-07		16:07:10		74.6		36.5		25-Sep-07		16:06:20		70.41		40.5		25-Sep-07		16:07:53		72.21		39		5-Nov-07		16:25:59		72.21		41.5

		25-Sep-07		18:07:10		74.01		33.5		25-Sep-07		18:06:20		70.41		36		25-Sep-07		18:07:53		71.6		37		5-Nov-07		18:25:59		72.8		41

		25-Sep-07		20:07:10		75.81		36.5		25-Sep-07		20:06:20		72.8		40.5		25-Sep-07		20:07:53		71		42.5		5-Nov-07		20:25:59		71.6		42.5

		25-Sep-07		22:07:10		75.81		36		25-Sep-07		22:06:20		72.8		40		25-Sep-07		22:07:53		72.8		40		5-Nov-07		22:25:59		71		43

		26-Sep-07		0:07:10		75.81		35		26-Sep-07		0:06:20		72.8		39		26-Sep-07		0:07:53		71.6		40		6-Nov-07		0:25:59		69.8		42

		26-Sep-07		2:07:10		75.2		34.5		26-Sep-07		2:06:20		72.21		39		26-Sep-07		2:07:53		69.8		40		6-Nov-07		2:25:59		69.2		41.5

		26-Sep-07		4:07:10		74.01		34		26-Sep-07		4:06:20		71		38		26-Sep-07		4:07:53		68.61		40		6-Nov-07		4:25:59		68		40.5

		26-Sep-07		6:07:10		72.8		33.5		26-Sep-07		6:06:20		70.41		36		26-Sep-07		6:07:53		68.61		39.5		6-Nov-07		6:25:59		68		39.5

		26-Sep-07		8:07:10		73.4		33		26-Sep-07		8:06:20		71.6		36.5		26-Sep-07		8:07:53		70.41		37.5		6-Nov-07		8:25:59		69.8		37

		26-Sep-07		10:07:10		74.01		37		26-Sep-07		10:06:20		71.6		38.5		26-Sep-07		10:07:53		71.6		34.5		6-Nov-07		10:25:59		71		39.5

		26-Sep-07		12:07:10		74.6		34.5		26-Sep-07		12:06:20		71.6		36		26-Sep-07		12:07:53		71.6		35.5		6-Nov-07		12:25:59		73.4		39.5

		26-Sep-07		14:07:10		74.6		33		26-Sep-07		14:06:20		71.6		35.5		26-Sep-07		14:07:53		71.6		34		6-Nov-07		14:25:59		75.2		39.5

		26-Sep-07		16:07:10		75.2		32.5		26-Sep-07		16:06:20		71		35.5		26-Sep-07		16:07:53		71.6		34.5		6-Nov-07		16:25:59		75.81		42.5

		26-Sep-07		18:07:10		74.6		31		26-Sep-07		18:06:20		69.8		34.5		26-Sep-07		18:07:53		71		34.5		6-Nov-07		18:25:59		75.2		41.5

		26-Sep-07		20:07:10		75.81		32		26-Sep-07		20:06:20		72.8		35.5		26-Sep-07		20:07:53		71		33.5		6-Nov-07		20:25:59		72.8		41

		26-Sep-07		22:07:10		76.4		31		26-Sep-07		22:06:20		72.8		35.5		26-Sep-07		22:07:53		73.4		34.5		6-Nov-07		22:25:59		71.6		42

		27-Sep-07		0:07:10		76.4		31		27-Sep-07		0:06:20		72.8		35.5		27-Sep-07		0:07:53		72.8		34.5		7-Nov-07		0:25:59		71		43

		27-Sep-07		2:07:10		75.81		30.5		27-Sep-07		2:06:20		72.21		35		27-Sep-07		2:07:53		71.6		34.5		7-Nov-07		2:25:59		69.8		43

		27-Sep-07		4:07:10		75.2		30		27-Sep-07		4:06:20		72.21		34		27-Sep-07		4:07:53		70.41		35		7-Nov-07		4:25:59		69.2		43.5

		27-Sep-07		6:07:10		75.2		30.5		27-Sep-07		6:06:20		72.21		33		27-Sep-07		6:07:53		70.41		35.5		7-Nov-07		6:25:59		69.2		44

		27-Sep-07		8:07:10		74.6		31.5		27-Sep-07		8:06:20		71.6		35		27-Sep-07		8:07:53		71.6		33		7-Nov-07		8:25:59		71		43

		27-Sep-07		10:07:10		74.6		32		27-Sep-07		10:06:20		72.21		37.5		27-Sep-07		10:07:53		71.6		36.5		7-Nov-07		10:25:59		71.6		42.5

		27-Sep-07		12:07:10		74.6		34		27-Sep-07		12:06:20		71.6		37		27-Sep-07		12:07:53		72.21		39		7-Nov-07		12:25:59		72.8		42

		27-Sep-07		14:07:10		74.6		34		27-Sep-07		14:06:20		71		35.5		27-Sep-07		14:07:53		72.21		34		7-Nov-07		14:25:59		74.01		42.5

		27-Sep-07		16:07:10		75.2		33		27-Sep-07		16:06:20		70.41		37.5		27-Sep-07		16:07:53		71.6		34.5		7-Nov-07		16:25:59		74.6		44

		27-Sep-07		18:07:10		75.2		32.5		27-Sep-07		18:06:20		71		36		27-Sep-07		18:07:53		71.6		35.5		7-Nov-07		18:25:59		74.6		43

		27-Sep-07		20:07:10		76.4		30.5		27-Sep-07		20:06:20		72.8		33.5		27-Sep-07		20:07:53		74.6		31.5		7-Nov-07		20:25:59		72.21		42.5

		27-Sep-07		22:07:10		76.4		30.5		27-Sep-07		22:06:20		72.8		34.5		27-Sep-07		22:07:53		75.2		32		7-Nov-07		22:25:59		71.6		42

		28-Sep-07		0:07:10		76.4		30		28-Sep-07		0:06:20		72.8		34.5		28-Sep-07		0:07:53		74.6		32.5		8-Nov-07		0:25:59		69.8		42.5

		28-Sep-07		2:07:10		75.81		29.5		28-Sep-07		2:06:20		72.8		33		28-Sep-07		2:07:53		72.8		33		8-Nov-07		2:25:59		69.2		43

		28-Sep-07		4:07:10		75.2		30		28-Sep-07		4:06:20		72.8		34		28-Sep-07		4:07:53		71.6		34		8-Nov-07		4:25:59		68.61		42.5

		28-Sep-07		6:07:10		75.2		30.5		28-Sep-07		6:06:20		72.8		32.5		28-Sep-07		6:07:53		70.41		35		8-Nov-07		6:25:59		68.61		43

		28-Sep-07		8:07:10		74.6		31.5		28-Sep-07		8:06:20		71		37		28-Sep-07		8:07:53		71.6		31.5		8-Nov-07		8:25:59		71.6		40.5

		28-Sep-07		10:07:10		74.6		32.5		28-Sep-07		10:06:20		71.6		39		28-Sep-07		10:07:53		71.6		38.5		8-Nov-07		10:25:59		71		41.5

		28-Sep-07		12:07:10		74.6		33		28-Sep-07		12:06:20		71.6		36.5		28-Sep-07		12:07:53		72.21		34.5		8-Nov-07		12:25:59		72.8		43.5

		28-Sep-07		14:07:10		74.01		36		28-Sep-07		14:06:20		71		36		28-Sep-07		14:07:53		71.6		40		8-Nov-07		14:25:59		74.01		42.5

		28-Sep-07		16:07:10		75.2		37.5		28-Sep-07		16:06:20		71		44		28-Sep-07		16:07:53		71.6		41.5		8-Nov-07		16:25:59		75.2		43.5

		28-Sep-07		18:07:10		74.6		39		28-Sep-07		18:06:20		70.41		46.5		28-Sep-07		18:07:53		71		45		8-Nov-07		18:25:59		74.01		43

		28-Sep-07		20:07:10		75.81		37		28-Sep-07		20:06:20		72.8		42		28-Sep-07		20:07:53		71.6		42		8-Nov-07		20:25:59		72.21		43.5

		28-Sep-07		22:07:10		75.81		36.5		28-Sep-07		22:06:20		72.8		42		28-Sep-07		22:07:53		72.21		41		8-Nov-07		22:25:59		72.21		45.5

		29-Sep-07		0:07:10		75.2		36.5		29-Sep-07		0:06:20		72.21		42		29-Sep-07		0:07:53		71.6		42		9-Nov-07		0:25:59		71		44.5

		29-Sep-07		2:07:10		75.2		37		29-Sep-07		2:06:20		72.8		42		29-Sep-07		2:07:53		71		42.5		9-Nov-07		2:25:59		69.8		44.5

		29-Sep-07		4:07:10		75.2		37		29-Sep-07		4:06:20		72.8		41		29-Sep-07		4:07:53		71		42.5		9-Nov-07		4:25:59		69.2		45

		29-Sep-07		6:07:10		75.2		35		29-Sep-07		6:06:20		72.8		35		29-Sep-07		6:07:53		69.8		45.5		9-Nov-07		6:25:59		69.2		46.5

		29-Sep-07		8:07:10		74.6		39		29-Sep-07		8:06:20		71.6		42		29-Sep-07		8:07:53		71		45.5		9-Nov-07		8:25:59		71		45

		29-Sep-07		10:07:10		74.01		40.5		29-Sep-07		10:06:20		71		42		29-Sep-07		10:07:53		71.6		46		9-Nov-07		10:25:59		71		46

		29-Sep-07		12:07:10		74.6		39		29-Sep-07		12:06:20		71.6		38.5		29-Sep-07		12:07:53		71.6		48.5		9-Nov-07		12:25:59		72.21		47

		29-Sep-07		14:07:10		74.01		45		29-Sep-07		14:06:20		71.6		54		29-Sep-07		14:07:53		71.6		47		9-Nov-07		14:25:59		74.01		44.5

		29-Sep-07		16:07:10		74.6		42		29-Sep-07		16:06:20		71.6		48.5		29-Sep-07		16:07:53		71.6		52		9-Nov-07		16:25:59		74.01		44.5

		29-Sep-07		18:07:10		74.6		43.5		29-Sep-07		18:06:20		70.41		53		29-Sep-07		18:07:53		71		52		9-Nov-07		18:25:59		74.01		43.5

		29-Sep-07		20:07:10		75.2		36		29-Sep-07		20:06:20		72.21		38		29-Sep-07		20:07:53		70.41		42		9-Nov-07		20:25:59		73.4		43

		29-Sep-07		22:07:10		75.2		32.5		29-Sep-07		22:06:20		72.8		35		29-Sep-07		22:07:53		71		36.5		9-Nov-07		22:25:59		72.21		45

		30-Sep-07		0:07:10		75.2		31		30-Sep-07		0:06:20		73.4		33.5		30-Sep-07		0:07:53		70.41		35.5		10-Nov-07		0:25:59		71		45

		30-Sep-07		2:07:10		74.6		30.5		30-Sep-07		2:06:20		72.8		32.5		30-Sep-07		2:07:53		69.8		34.5		10-Nov-07		2:25:59		69.8		45.5

		30-Sep-07		4:07:10		74.01		30		30-Sep-07		4:06:20		71.6		32.5		30-Sep-07		4:07:53		68.61		34.5		10-Nov-07		4:25:59		69.2		46

		30-Sep-07		6:07:10		73.4		29.5		30-Sep-07		6:06:20		72.21		32.5		30-Sep-07		6:07:53		68		34.5		10-Nov-07		6:25:59		69.2		45.5

		30-Sep-07		8:07:10		72.21		30.5		30-Sep-07		8:06:20		71		34		30-Sep-07		8:07:53		68		34.5		10-Nov-07		8:25:59		71		42.5

		30-Sep-07		10:07:10		72.8		31		30-Sep-07		10:06:20		71.6		34.5		30-Sep-07		10:07:53		70.41		34.5		10-Nov-07		10:25:59		73.4		43

		30-Sep-07		12:07:10		73.4		31		30-Sep-07		12:06:20		71		33.5		30-Sep-07		12:07:53		70.41		32		10-Nov-07		12:25:59		74.01		43

		30-Sep-07		14:07:10		73.4		29		30-Sep-07		14:06:20		70.41		31.5		30-Sep-07		14:07:53		71		31		10-Nov-07		14:25:59		74.6		42

		30-Sep-07		16:07:10		74.01		30		30-Sep-07		16:06:20		69.8		34.5		30-Sep-07		16:07:53		71		31		10-Nov-07		16:25:59		75.2		43

		30-Sep-07		18:07:10		74.01		29		30-Sep-07		18:06:20		69.8		32.5		30-Sep-07		18:07:53		71		31		10-Nov-07		18:25:59		74.6		44

		30-Sep-07		20:07:10		75.2		28		30-Sep-07		20:06:20		72.21		31		30-Sep-07		20:07:53		71.6		32		10-Nov-07		20:25:59		72.8		44.5

		30-Sep-07		22:07:10		75.81		27.5		30-Sep-07		22:06:20		72.8		31		30-Sep-07		22:07:53		71.6		31.5		10-Nov-07		22:25:59		72.21		45.5

		1-Oct-07		0:07:10		75.2		27		1-Oct-07		0:06:20		72.8		30		1-Oct-07		0:07:53		70.41		32		11-Nov-07		0:25:59		70.41		44

		1-Oct-07		2:07:10		74.01		27.5		1-Oct-07		2:06:20		71.6		30.5		1-Oct-07		2:07:53		68.61		32		11-Nov-07		2:25:59		69.2		43

		1-Oct-07		4:07:10		72.8		27.5		1-Oct-07		4:06:20		70.41		30.5		1-Oct-07		4:07:53		68		32.5		11-Nov-07		4:25:59		68.61		43

		1-Oct-07		6:07:10		72.21		27.5		1-Oct-07		6:06:20		69.8		30		1-Oct-07		6:07:53		66.2		33		11-Nov-07		6:25:59		68		43.5

		1-Oct-07		8:07:10		71		28.5		1-Oct-07		8:06:20		68.61		31.5		1-Oct-07		8:07:53		68		32		11-Nov-07		8:25:59		68		44.5

		1-Oct-07		10:07:10		71.6		30		1-Oct-07		10:06:20		69.8		31.5		1-Oct-07		10:07:53		68.61		33.5		11-Nov-07		10:25:59		69.2		46.5

		1-Oct-07		12:07:10		72.21		30		1-Oct-07		12:06:20		70.41		32		1-Oct-07		12:07:53		70.41		33.5		11-Nov-07		12:25:59		69.2		49

		1-Oct-07		14:07:10		73.4		28.5		1-Oct-07		14:06:20		69.8		30		1-Oct-07		14:07:53		70.41		31.5		11-Nov-07		14:25:59		69.8		50.5

		1-Oct-07		16:07:10		73.4		27		1-Oct-07		16:06:20		69.8		29.5		1-Oct-07		16:07:53		70.41		30.5		11-Nov-07		16:25:59		69.8		52

		1-Oct-07		18:07:10		74.01		30		1-Oct-07		18:06:20		69.8		35.5		1-Oct-07		18:07:53		71		32		11-Nov-07		18:25:59		69.8		53

		1-Oct-07		20:07:10		75.81		33		1-Oct-07		20:06:20		72.8		38		1-Oct-07		20:07:53		72.21		37.5		11-Nov-07		20:25:59		69.2		54

		1-Oct-07		22:07:10		75.2		35.5		1-Oct-07		22:06:20		72.21		41		1-Oct-07		22:07:53		72.21		39.5		11-Nov-07		22:25:59		69.2		55

		2-Oct-07		0:07:10		75.2		35.5		2-Oct-07		0:06:20		72.8		41		2-Oct-07		0:07:53		71.6		41		12-Nov-07		0:25:59		69.2		55.5

		2-Oct-07		2:07:10		75.2		36.5		2-Oct-07		2:06:20		72.8		41		2-Oct-07		2:07:53		71		42.5		12-Nov-07		2:25:59		69.2		55.5

		2-Oct-07		4:07:10		75.2		40		2-Oct-07		4:06:20		72.8		46		2-Oct-07		4:07:53		71		46.5		12-Nov-07		4:25:59		69.2		54

		2-Oct-07		6:07:10		75.2		39		2-Oct-07		6:06:20		72.8		41		2-Oct-07		6:07:53		70.41		53.5		12-Nov-07		6:25:59		68.61		50.5

		2-Oct-07		8:07:10		74.6		44.5		2-Oct-07		8:06:20		71.6		46.5		2-Oct-07		8:07:53		71		51.5		12-Nov-07		8:25:59		68		47.5

		2-Oct-07		10:07:10		74.6		40.5		2-Oct-07		10:06:20		71.6		44.5		2-Oct-07		10:07:53		72.21		41		12-Nov-07		10:25:59		68		47.5

		2-Oct-07		12:07:10		74.6		44.5		2-Oct-07		12:06:20		71		47.5		2-Oct-07		12:07:53		72.21		51.5		12-Nov-07		12:25:59		69.2		46

		2-Oct-07		14:07:10		74.6		42		2-Oct-07		14:06:20		71.6		51		2-Oct-07		14:07:53		71.6		50		12-Nov-07		14:25:59		70.41		44

		2-Oct-07		16:07:10		75.2		38.5		2-Oct-07		16:06:20		71.6		46		2-Oct-07		16:07:53		71		46		12-Nov-07		16:25:59		71		42.5

		2-Oct-07		18:07:10		74.6		34		2-Oct-07		18:06:20		71		39.5		2-Oct-07		18:07:53		71		36		12-Nov-07		18:25:59		71		42.5

		2-Oct-07		20:07:10		75.81		37		2-Oct-07		20:06:20		72.8		41.5		2-Oct-07		20:07:53		70.41		44.5		12-Nov-07		20:25:59		69.8		42.5

		2-Oct-07		22:07:10		76.4		36.5		2-Oct-07		22:06:20		72.8		41.5		2-Oct-07		22:07:53		72.8		41		12-Nov-07		22:25:59		68.61		43

		3-Oct-07		0:07:10		75.81		35.5		3-Oct-07		0:06:20		72.8		40		3-Oct-07		0:07:53		72.21		40		13-Nov-07		0:25:59		68		42.5

		3-Oct-07		2:07:10		75.81		34.5		3-Oct-07		2:06:20		72.8		38		3-Oct-07		2:07:53		71		39.5		13-Nov-07		2:25:59		67.4		42.5

		3-Oct-07		4:07:10		74.6		34.5		3-Oct-07		4:06:20		71.6		38.5		3-Oct-07		4:07:53		69.8		39.5		13-Nov-07		4:25:59		67.4		42

		3-Oct-07		6:07:10		74.01		34.5		3-Oct-07		6:06:20		71.6		37.5		3-Oct-07		6:07:53		69.8		40		13-Nov-07		6:25:59		67.4		42.5

		3-Oct-07		8:07:10		73.4		36.5		3-Oct-07		8:06:20		71.6		42		3-Oct-07		8:07:53		71.6		39.5		13-Nov-07		8:25:59		71		40.5

		3-Oct-07		10:07:10		74.6		39		3-Oct-07		10:06:20		71.6		45		3-Oct-07		10:07:53		71.6		43.5		13-Nov-07		10:25:59		71		41

		3-Oct-07		12:07:10		74.6		38.5		3-Oct-07		12:06:20		71.6		37.5		3-Oct-07		12:07:53		72.21		43		13-Nov-07		12:25:59		74.6		39.5

		3-Oct-07		14:07:10		74.6		39		3-Oct-07		14:06:20		71.6		38		3-Oct-07		14:07:53		72.21		42		13-Nov-07		14:25:59		74.6		38.5

		3-Oct-07		16:07:10		74.6		37		3-Oct-07		16:06:20		71		41.5		3-Oct-07		16:07:53		71		42.5		13-Nov-07		16:25:59		75.2		37.5

		3-Oct-07		18:07:10		74.6		38.5		3-Oct-07		18:06:20		69.8		47.5		3-Oct-07		18:07:53		71		38		13-Nov-07		18:25:59		75.2		35.5

		3-Oct-07		20:07:10		75.81		37.5		3-Oct-07		20:06:20		72.8		43		3-Oct-07		20:07:53		71		44		13-Nov-07		20:25:59		73.4		38.5

		3-Oct-07		22:07:10		76.4		36.5		3-Oct-07		22:06:20		72.8		40		3-Oct-07		22:07:53		71.6		41.5		13-Nov-07		22:25:59		72.21		41

		4-Oct-07		0:07:10		75.81		35		4-Oct-07		0:06:20		72.8		39.5		4-Oct-07		0:07:53		71.6		40.5		14-Nov-07		0:25:59		71.6		43

		4-Oct-07		2:07:10		75.2		34.5		4-Oct-07		2:06:20		72.21		38.5		4-Oct-07		2:07:53		70.41		40.5		14-Nov-07		2:25:59		70.41		44.5

		4-Oct-07		4:07:10		74.01		34		4-Oct-07		4:06:20		71		38.5		4-Oct-07		4:07:53		69.2		40		14-Nov-07		4:25:59		69.8		45

		4-Oct-07		6:07:10		74.01		33.5		4-Oct-07		6:06:20		70.41		37		4-Oct-07		6:07:53		68.61		39.5		14-Nov-07		6:25:59		69.8		47

		4-Oct-07		8:07:10		74.01		34.5		4-Oct-07		8:06:20		71.6		39		4-Oct-07		8:07:53		70.41		38		14-Nov-07		8:25:59		73.4		46

		4-Oct-07		10:07:10		74.6		36		4-Oct-07		10:06:20		72.21		41		4-Oct-07		10:07:53		71.6		35.5		14-Nov-07		10:25:59		74.6		47

		4-Oct-07		12:07:10		76.4		36		4-Oct-07		12:06:20		72.21		41.5		4-Oct-07		12:07:53		71.6		45.5		14-Nov-07		12:25:59		74.6		48.5

		4-Oct-07		14:07:10		75.81		35		4-Oct-07		14:06:20		72.21		36		4-Oct-07		14:07:53		72.21		35.5		14-Nov-07		14:25:59		75.2		49.5

		4-Oct-07		16:07:10		76.4		38.5		4-Oct-07		16:06:20		71		41.5		4-Oct-07		16:07:53		71		49		14-Nov-07		16:25:59		75.2		49.5

		4-Oct-07		18:07:10		76.4		33.5		4-Oct-07		18:06:20		70.41		40		4-Oct-07		18:07:53		70.41		41		14-Nov-07		18:25:59		75.2		49.5

		4-Oct-07		20:07:10		76.4		34		4-Oct-07		20:06:20		72.8		38.5		4-Oct-07		20:07:53		72.8		37.5		14-Nov-07		20:25:59		74.6		49

		4-Oct-07		22:07:10		76.4		31.5		4-Oct-07		22:06:20		72.8		35.5		4-Oct-07		22:07:53		72.8		35		14-Nov-07		22:25:59		74.01		52

		5-Oct-07		0:07:10		75.81		30.5		5-Oct-07		0:06:20		72.8		34.5		5-Oct-07		0:07:53		72.21		34.5		15-Nov-07		0:25:59		72.8		50.5

		5-Oct-07		2:07:10		75.2		29		5-Oct-07		2:06:20		72.8		32.5		5-Oct-07		2:07:53		71		33.5		15-Nov-07		2:25:59		71.6		51

		5-Oct-07		4:07:10		74.6		28.5		5-Oct-07		4:06:20		72.8		31		5-Oct-07		4:07:53		69.8		32.5		15-Nov-07		4:25:59		71		50

		5-Oct-07		6:07:10		74.6		29		5-Oct-07		6:06:20		72.21		31.5		5-Oct-07		6:07:53		69.8		33.5		15-Nov-07		6:25:59		69.8		49

		5-Oct-07		8:07:10		74.01		30.5		5-Oct-07		8:06:20		71.6		33.5		5-Oct-07		8:07:53		71		34		15-Nov-07		8:25:59		72.8		44.5

		5-Oct-07		10:07:10		74.6		31.5		5-Oct-07		10:06:20		72.21		36.5		5-Oct-07		10:07:53		71.6		32.5		15-Nov-07		10:25:59		74.6		47

		5-Oct-07		12:07:10		75.2		32		5-Oct-07		12:06:20		71.6		34		5-Oct-07		12:07:53		71.6		33		15-Nov-07		12:25:59		74.6		48.5

		5-Oct-07		14:07:10		75.2		33		5-Oct-07		14:06:20		72.21		39.5		5-Oct-07		14:07:53		71.6		38.5		15-Nov-07		14:25:59		75.2		48

		5-Oct-07		16:07:10		75.81		32		5-Oct-07		16:06:20		70.41		39.5		5-Oct-07		16:07:53		71		35.5		15-Nov-07		16:25:59		75.2		49

		5-Oct-07		18:07:10		75.2		30		5-Oct-07		18:06:20		69.8		35		5-Oct-07		18:07:53		70.41		34.5		15-Nov-07		18:25:59		74.6		50

		5-Oct-07		20:07:10		75.81		29.5		5-Oct-07		20:06:20		72.21		33.5		5-Oct-07		20:07:53		70.41		34.5		15-Nov-07		20:25:59		74.01		50

		5-Oct-07		22:07:10		75.2		29.5		5-Oct-07		22:06:20		72.21		33.5		5-Oct-07		22:07:53		69.8		34.5		15-Nov-07		22:25:59		74.01		49.5

		6-Oct-07		0:07:10		75.2		29.5		6-Oct-07		0:06:20		72.21		33.5		6-Oct-07		0:07:53		69.2		35		16-Nov-07		0:25:59		72.21		49.5

		6-Oct-07		2:07:10		74.01		30		6-Oct-07		2:06:20		71.6		33.5		6-Oct-07		2:07:53		68		35.5		16-Nov-07		2:25:59		71		48.5

		6-Oct-07		4:07:10		72.8		29.5		6-Oct-07		4:06:20		70.41		33		6-Oct-07		4:07:53		66.81		36		16-Nov-07		4:25:59		69.8		48

		6-Oct-07		6:07:10		72.8		29		6-Oct-07		6:06:20		72.21		30		6-Oct-07		6:07:53		68		34.5		16-Nov-07		6:25:59		69.8		47

		6-Oct-07		8:07:10		72.8		29.5		6-Oct-07		8:06:20		71.6		34.5		6-Oct-07		8:07:53		69.2		33		16-Nov-07		8:25:59		72.8		42.5

		6-Oct-07		10:07:10		73.4		30.5		6-Oct-07		10:06:20		71.6		33.5		6-Oct-07		10:07:53		71.6		31		16-Nov-07		10:25:59		74.01		44

		6-Oct-07		12:07:10		74.01		30.5		6-Oct-07		12:06:20		70.41		36		6-Oct-07		12:07:53		71.6		34.5		16-Nov-07		12:25:59		74.6		47

		6-Oct-07		14:07:10		75.2		28		6-Oct-07		14:06:20		69.2		32.5		6-Oct-07		14:07:53		71		30.5		16-Nov-07		14:25:59		74.6		49.5

		6-Oct-07		16:07:10		75.2		27		6-Oct-07		16:06:20		69.2		31.5		6-Oct-07		16:07:53		70.41		31.5		16-Nov-07		16:25:59		75.81		49.5

		6-Oct-07		18:07:10		75.81		27.5		6-Oct-07		18:06:20		69.2		33		6-Oct-07		18:07:53		71		30		16-Nov-07		18:25:59		75.81		49.5

		6-Oct-07		20:07:10		76.4		27.5		6-Oct-07		20:06:20		72.21		31.5		6-Oct-07		20:07:53		70.41		33.5		16-Nov-07		20:25:59		74.01		50

		6-Oct-07		22:07:10		75.81		27		6-Oct-07		22:06:20		73.4		31.5		6-Oct-07		22:07:53		70.41		33		16-Nov-07		22:25:59		73.4		51.5

		7-Oct-07		0:07:10		75.2		27		7-Oct-07		0:06:20		72.8		30.5		7-Oct-07		0:07:53		69.8		32.5		17-Nov-07		0:25:59		72.21		51

		7-Oct-07		2:07:10		74.6		27		7-Oct-07		2:06:20		72.21		31		7-Oct-07		2:07:53		68.61		33		17-Nov-07		2:25:59		71		51.5

		7-Oct-07		4:07:10		74.01		28		7-Oct-07		4:06:20		71.6		31.5		7-Oct-07		4:07:53		68		34		17-Nov-07		4:25:59		70.41		51.5

		7-Oct-07		6:07:10		72.8		28.5		7-Oct-07		6:06:20		71		32		7-Oct-07		6:07:53		66.81		35		17-Nov-07		6:25:59		70.41		52

		7-Oct-07		8:07:10		72.21		29		7-Oct-07		8:06:20		69.2		32.5		7-Oct-07		8:07:53		67.4		34		17-Nov-07		8:25:59		71		50.5

		7-Oct-07		10:07:10		71.6		31		7-Oct-07		10:06:20		68.61		34.5		7-Oct-07		10:07:53		68.61		35		17-Nov-07		10:25:59		71.6		50.5

		7-Oct-07		12:07:10		72.21		29		7-Oct-07		12:06:20		68.61		31		7-Oct-07		12:07:53		70.41		31.5		17-Nov-07		12:25:59		72.8		50

		7-Oct-07		14:07:10		72.8		26.5		7-Oct-07		14:06:20		69.2		28.5		7-Oct-07		14:07:53		70.41		29		17-Nov-07		14:25:59		75.2		49.5

		7-Oct-07		16:07:10		73.4		27		7-Oct-07		16:06:20		69.2		31		7-Oct-07		16:07:53		70.41		30.5		17-Nov-07		16:25:59		75.2		48

		7-Oct-07		18:07:10		74.01		26		7-Oct-07		18:06:20		69.8		29.5		7-Oct-07		18:07:53		71		29		17-Nov-07		18:25:59		74.6		49

		7-Oct-07		20:07:10		75.2		25		7-Oct-07		20:06:20		72.21		28.5		7-Oct-07		20:07:53		71		29		17-Nov-07		20:25:59		72.8		48.5

		7-Oct-07		22:07:10		75.2		26.5		7-Oct-07		22:06:20		72.8		31		7-Oct-07		22:07:53		70.41		31.5		17-Nov-07		22:25:59		72.21		49

		8-Oct-07		0:07:10		74.6		26.5		8-Oct-07		0:06:20		72.21		30.5		8-Oct-07		0:07:53		69.2		31.5		18-Nov-07		0:25:59		71		52

		8-Oct-07		2:07:10		73.4		25.5		8-Oct-07		2:06:20		71		29		8-Oct-07		2:07:53		68		31		18-Nov-07		2:25:59		70.41		51

		8-Oct-07		4:07:10		72.8		26		8-Oct-07		4:06:20		69.8		29		8-Oct-07		4:07:53		66.81		31.5		18-Nov-07		4:25:59		69.8		50.5

		8-Oct-07		6:07:10		71.6		26		8-Oct-07		6:06:20		69.2		29.5		8-Oct-07		6:07:53		65.6		32		18-Nov-07		6:25:59		69.2		51

		8-Oct-07		8:07:10		71		27		8-Oct-07		8:06:20		68.61		30		8-Oct-07		8:07:53		67.4		31		18-Nov-07		8:25:59		68.61		50.5

		8-Oct-07		10:07:10		71.6		28.5		8-Oct-07		10:06:20		68.61		32		8-Oct-07		10:07:53		68		32.5		18-Nov-07		10:25:59		68.61		51

		8-Oct-07		12:07:10		72.21		29.5		8-Oct-07		12:06:20		69.2		33		8-Oct-07		12:07:53		69.8		33		18-Nov-07		12:25:59		69.2		51.5

		8-Oct-07		14:07:10		72.8		31		8-Oct-07		14:06:20		69.2		34.5		8-Oct-07		14:07:53		70.41		34.5		18-Nov-07		14:25:59		69.8		52

		8-Oct-07		16:07:10		73.4		30.5		8-Oct-07		16:06:20		69.2		35.5		8-Oct-07		16:07:53		70.41		35.5		18-Nov-07		16:25:59		71.6		54

		8-Oct-07		18:07:10		74.01		31.5		8-Oct-07		18:06:20		69.2		35		8-Oct-07		18:07:53		71		34		18-Nov-07		18:25:59		72.21		54

		8-Oct-07		20:07:10		75.2		33.5		8-Oct-07		20:06:20		72.21		36		8-Oct-07		20:07:53		71.6		38.5		18-Nov-07		20:25:59		71		53

		8-Oct-07		22:07:10		75.2		34.5		8-Oct-07		22:06:20		72.21		39.5		8-Oct-07		22:07:53		71		40		18-Nov-07		22:25:59		69.8		53

		9-Oct-07		0:07:10		74.6		34		9-Oct-07		0:06:20		72.21		38.5		9-Oct-07		0:07:53		69.8		40		19-Nov-07		0:25:59		69.2		53

		9-Oct-07		2:07:10		74.01		33.5		9-Oct-07		2:06:20		71.6		37.5		9-Oct-07		2:07:53		68.61		40		19-Nov-07		2:25:59		69.2		53

		9-Oct-07		4:07:10		73.4		33		9-Oct-07		4:06:20		71		36.5		9-Oct-07		4:07:53		67.4		39.5		19-Nov-07		4:25:59		68.61		53

		9-Oct-07		6:07:10		73.4		32.5		9-Oct-07		6:06:20		69.8		36		9-Oct-07		6:07:53		68.61		37.5		19-Nov-07		6:25:59		68.61		53

		9-Oct-07		8:07:10		72.8		33.5		9-Oct-07		8:06:20		69.8		38.5		9-Oct-07		8:07:53		70.41		36		19-Nov-07		8:25:59		68		53

		9-Oct-07		10:07:10		73.4		37.5		9-Oct-07		10:06:20		71		45		9-Oct-07		10:07:53		71.6		37		19-Nov-07		10:25:59		68.61		53

		9-Oct-07		12:07:10		74.6		35.5		9-Oct-07		12:06:20		71		41		9-Oct-07		12:07:53		71.6		42		19-Nov-07		12:25:59		68.61		55

		9-Oct-07		14:07:10		74.6		36		9-Oct-07		14:06:20		71		41		9-Oct-07		14:07:53		71.6		38.5		19-Nov-07		14:25:59		69.8		56

		9-Oct-07		16:07:10		75.2		34		9-Oct-07		16:06:20		69.8		42		9-Oct-07		16:07:53		71.6		37		19-Nov-07		16:25:59		71		57.5

		9-Oct-07		18:07:10		74.01		36.5		9-Oct-07		18:06:20		69.2		44.5		9-Oct-07		18:07:53		71		41.5		19-Nov-07		18:25:59		71.6		56.5

		9-Oct-07		20:07:10		75.81		32		9-Oct-07		20:06:20		72.8		35.5		9-Oct-07		20:07:53		71		37.5		19-Nov-07		20:25:59		71		55

		9-Oct-07		22:07:10		76.4		33.5		9-Oct-07		22:06:20		73.4		38.5		9-Oct-07		22:07:53		71.6		39		19-Nov-07		22:25:59		70.41		54.5

		10-Oct-07		0:07:10		75.81		34.5		10-Oct-07		0:06:20		72.8		39.5		10-Oct-07		0:07:53		70.41		41		20-Nov-07		0:25:59		69.2		53.5

		10-Oct-07		2:07:10		75.2		35.5		10-Oct-07		2:06:20		72.21		40.5		10-Oct-07		2:07:53		69.8		42		20-Nov-07		2:25:59		68.61		52.5

		10-Oct-07		4:07:10		74.6		36		10-Oct-07		4:06:20		72.21		40.5		10-Oct-07		4:07:53		69.2		43		20-Nov-07		4:25:59		68		53

		10-Oct-07		6:07:10		74.6		37.5		10-Oct-07		6:06:20		71		44.5		10-Oct-07		6:07:53		69.2		45		20-Nov-07		6:25:59		68.61		54.5

		10-Oct-07		8:07:10		74.01		39		10-Oct-07		8:06:20		71		38.5		10-Oct-07		8:07:53		71.6		44		20-Nov-07		8:25:59		71.6		54

		10-Oct-07		10:07:10		74.01		43		10-Oct-07		10:06:20		69.8		48.5		10-Oct-07		10:07:53		71		44		20-Nov-07		10:25:59		74.01		55

		10-Oct-07		12:07:10		74.6		42.5		10-Oct-07		12:06:20		70.41		48.5		10-Oct-07		12:07:53		71.6		43		20-Nov-07		12:25:59		74.01		53.5

		10-Oct-07		14:07:10		74.6		44.5		10-Oct-07		14:06:20		71		50.5		10-Oct-07		14:07:53		71		51.5		20-Nov-07		14:25:59		73.4		48.5

		10-Oct-07		16:07:10		74.6		42		10-Oct-07		16:06:20		69.8		57		10-Oct-07		16:07:53		70.41		49		20-Nov-07		16:25:59		74.01		45

		10-Oct-07		18:07:10		74.01		41		10-Oct-07		18:06:20		69.8		51		10-Oct-07		18:07:53		70.41		48		20-Nov-07		18:25:59		74.01		43

		10-Oct-07		20:07:10		75.2		41		10-Oct-07		20:06:20		72.21		47		10-Oct-07		20:07:53		69.8		50		20-Nov-07		20:25:59		72.21		43

		10-Oct-07		22:07:10		75.2		43		10-Oct-07		22:06:20		72.21		50.5		10-Oct-07		22:07:53		69.8		50		20-Nov-07		22:25:59		71		44.5

		11-Oct-07		0:07:10		74.6		44		11-Oct-07		0:06:20		72.21		51		11-Oct-07		0:07:53		69.8		51		21-Nov-07		0:25:59		69.8		44

		11-Oct-07		2:07:10		74.6		44		11-Oct-07		2:06:20		71.6		50.5		11-Oct-07		2:07:53		69.2		51		21-Nov-07		2:25:59		68.61		43

		11-Oct-07		4:07:10		74.01		44		11-Oct-07		4:06:20		71.6		49.5		11-Oct-07		4:07:53		69.2		51.5		21-Nov-07		4:25:59		68		42.5

		11-Oct-07		6:07:10		74.01		44		11-Oct-07		6:06:20		71		50.5		11-Oct-07		6:07:53		69.2		51		21-Nov-07		6:25:59		68		41

		11-Oct-07		8:07:10		73.4		44.5		11-Oct-07		8:06:20		70.41		45		11-Oct-07		8:07:53		71		49		21-Nov-07		8:25:59		71.6		37

		11-Oct-07		10:07:10		73.4		43		11-Oct-07		10:06:20		71.6		45		11-Oct-07		10:07:53		71		48		21-Nov-07		10:25:59		71.6		38

		11-Oct-07		12:07:10		74.01		46		11-Oct-07		12:06:20		70.41		51		11-Oct-07		12:07:53		71.6		49		21-Nov-07		12:25:59		72.21		38.5

		11-Oct-07		14:07:10		74.6		41.5		11-Oct-07		14:06:20		71		41		11-Oct-07		14:07:53		71		49.5		21-Nov-07		14:25:59		72.8		37.5

		11-Oct-07		16:07:10		75.2		46.5		11-Oct-07		16:06:20		69.2		59.5		11-Oct-07		16:07:53		70.41		53		21-Nov-07		16:25:59		73.4		37

		11-Oct-07		18:07:10		74.6		39.5		11-Oct-07		18:06:20		69.8		45		11-Oct-07		18:07:53		70.41		47		21-Nov-07		18:25:59		73.4		38

		11-Oct-07		20:07:10		75.2		40		11-Oct-07		20:06:20		72.21		45		11-Oct-07		20:07:53		70.41		46		21-Nov-07		20:25:59		71.6		38

		11-Oct-07		22:07:10		74.6		39.5		11-Oct-07		22:06:20		72.21		44		11-Oct-07		22:07:53		69.8		45.5		21-Nov-07		22:25:59		69.8		38.5

		12-Oct-07		0:07:10		74.01		38.5		12-Oct-07		0:06:20		72.21		42.5		12-Oct-07		0:07:53		68.61		45		22-Nov-07		0:25:59		68.61		38.5

		12-Oct-07		2:07:10		73.4		38		12-Oct-07		2:06:20		71.6		42		12-Oct-07		2:07:53		67.4		45.5		22-Nov-07		2:25:59		67.4		37.5

		12-Oct-07		4:07:10		72.21		38.5		12-Oct-07		4:06:20		71		42.5		12-Oct-07		4:07:53		66.81		46.5		22-Nov-07		4:25:59		66.81		36.5

		12-Oct-07		6:07:10		72.21		38		12-Oct-07		6:06:20		70.41		41.5		12-Oct-07		6:07:53		68.61		44		22-Nov-07		6:25:59		67.4		35

		12-Oct-07		8:07:10		72.21		38		12-Oct-07		8:06:20		70.41		43.5		12-Oct-07		8:07:53		69.8		42		22-Nov-07		8:25:59		70.41		32.5

		12-Oct-07		10:07:10		72.8		43.5		12-Oct-07		10:06:20		71		51.5		12-Oct-07		10:07:53		71.6		40		22-Nov-07		10:25:59		71.6		33.5

		12-Oct-07		12:07:10		73.4		40.5		12-Oct-07		12:06:20		70.41		45.5		12-Oct-07		12:07:53		71.6		49		22-Nov-07		12:25:59		72.21		35

		12-Oct-07		14:07:10		73.4		43.5		12-Oct-07		14:06:20		69.8		41		12-Oct-07		14:07:53		71		44.5		22-Nov-07		14:25:59		73.4		34

		12-Oct-07		16:07:10		74.01		45		12-Oct-07		16:06:20		69.2		56.5		12-Oct-07		16:07:53		71		46.5		22-Nov-07		16:25:59		72.8		32.5

		12-Oct-07		18:07:10		74.01		39.5		12-Oct-07		18:06:20		69.8		46.5		12-Oct-07		18:07:53		70.41		44.5		22-Nov-07		18:25:59		72.8		34.5

		12-Oct-07		20:07:10		74.6		38.5		12-Oct-07		20:06:20		72.21		42		12-Oct-07		20:07:53		70.41		44		22-Nov-07		20:25:59		71		34

		12-Oct-07		22:07:10		75.2		37		12-Oct-07		22:06:20		72.8		40.5		12-Oct-07		22:07:53		69.8		43.5		22-Nov-07		22:25:59		69.2		35

		13-Oct-07		0:07:10		74.6		36.5		13-Oct-07		0:06:20		72.21		40		13-Oct-07		0:07:53		68.61		44		23-Nov-07		0:25:59		68		35

		13-Oct-07		2:07:10		74.01		38		13-Oct-07		2:06:20		72.21		42		13-Oct-07		2:07:53		68		46		23-Nov-07		2:25:59		66.81		34.5

		13-Oct-07		4:07:10		74.01		39.5		13-Oct-07		4:06:20		72.21		44		13-Oct-07		4:07:53		67.4		48.5		23-Nov-07		4:25:59		66.2		34

		13-Oct-07		6:07:10		73.4		40		13-Oct-07		6:06:20		71		46		13-Oct-07		6:07:53		68.61		48		23-Nov-07		6:25:59		66.81		32.5

		13-Oct-07		8:07:10		72.8		44		13-Oct-07		8:06:20		71		45		13-Oct-07		8:07:53		70.41		48.5		23-Nov-07		8:25:59		69.2		30.5

		13-Oct-07		10:07:10		72.8		44		13-Oct-07		10:06:20		71		43		13-Oct-07		10:07:53		71		50		23-Nov-07		10:25:59		71.6		31

		13-Oct-07		12:07:10		73.4		44		13-Oct-07		12:06:20		70.41		54.5		13-Oct-07		12:07:53		71.6		52		23-Nov-07		12:25:59		70.41		33

		13-Oct-07		14:07:10		73.4		46.5		13-Oct-07		14:06:20		70.41		51		13-Oct-07		14:07:53		71		50		23-Nov-07		14:25:59		71		33.5

		13-Oct-07		16:07:10		72.8		49.5		13-Oct-07		16:06:20		69.2		61		13-Oct-07		16:07:53		71		53		23-Nov-07		16:25:59		71		32.5

		13-Oct-07		18:07:10		72.8		44		13-Oct-07		18:06:20		69.8		50		13-Oct-07		18:07:53		70.41		50.5		23-Nov-07		18:25:59		71		34

		13-Oct-07		20:07:10		73.4		43.5		13-Oct-07		20:06:20		71		48		13-Oct-07		20:07:53		69.8		48.5		23-Nov-07		20:25:59		70.41		34.5

		13-Oct-07		22:07:10		73.4		42.5		13-Oct-07		22:06:20		71.6		46.5		13-Oct-07		22:07:53		68.61		49		23-Nov-07		22:25:59		68.61		34.5

		14-Oct-07		0:07:10		72.21		41.5		14-Oct-07		0:06:20		71		45		14-Oct-07		0:07:53		67.4		49		24-Nov-07		0:25:59		67.4		34.5

		14-Oct-07		2:07:10		71.6		40.5		14-Oct-07		2:06:20		69.8		43.5		14-Oct-07		2:07:53		66.2		48		24-Nov-07		2:25:59		66.81		34

		14-Oct-07		4:07:10		71		40		14-Oct-07		4:06:20		69.2		42.5		14-Oct-07		4:07:53		65.6		47.5		24-Nov-07		4:25:59		66.2		33.5

		14-Oct-07		6:07:10		70.41		39		14-Oct-07		6:06:20		68.61		41		14-Oct-07		6:07:53		65.6		46		24-Nov-07		6:25:59		66.81		32.5

		14-Oct-07		8:07:10		71		37.5		14-Oct-07		8:06:20		68.61		40.5		14-Oct-07		8:07:53		67.4		41.5		24-Nov-07		8:25:59		68.61		29.5

		14-Oct-07		10:07:10		71.6		43.5		14-Oct-07		10:06:20		68.61		49		14-Oct-07		10:07:53		68.61		48.5		24-Nov-07		10:25:59		70.41		25.5

		14-Oct-07		12:07:10		72.21		46		14-Oct-07		12:06:20		68.61		49.5		14-Oct-07		12:07:53		69.8		49.5		24-Nov-07		12:25:59		69.8		24

		14-Oct-07		14:07:10		72.8		47		14-Oct-07		14:06:20		69.2		54		14-Oct-07		14:07:53		70.41		50		24-Nov-07		14:25:59		70.41		23

		14-Oct-07		16:07:10		72.8		45.5		14-Oct-07		16:06:20		69.2		45.5		14-Oct-07		16:07:53		70.41		45.5		24-Nov-07		16:25:59		71.6		22.5

		14-Oct-07		18:07:10		73.4		46		14-Oct-07		18:06:20		69.2		53.5		14-Oct-07		18:07:53		70.41		52.5		24-Nov-07		18:25:59		71		22.5

		14-Oct-07		20:07:10		74.6		44.5		14-Oct-07		20:06:20		71.6		49		14-Oct-07		20:07:53		69.8		50.5		24-Nov-07		20:25:59		69.8		24.5

		14-Oct-07		22:07:10		74.01		43		14-Oct-07		22:06:20		72.21		47		14-Oct-07		22:07:53		69.2		50		24-Nov-07		22:25:59		68.61		27

		15-Oct-07		0:07:10		74.01		43		15-Oct-07		0:06:20		72.21		47		15-Oct-07		0:07:53		68.61		51.5		25-Nov-07		0:25:59		67.4		28

		15-Oct-07		2:07:10		74.01		43.5		15-Oct-07		2:06:20		72.21		47		15-Oct-07		2:07:53		68		52		25-Nov-07		2:25:59		66.81		28.5

		15-Oct-07		4:07:10		73.4		43.5		15-Oct-07		4:06:20		71.6		47		15-Oct-07		4:07:53		67.4		52		25-Nov-07		4:25:59		66.2		28.5

		15-Oct-07		6:07:10		72.8		43.5		15-Oct-07		6:06:20		71		43		15-Oct-07		6:07:53		66.81		52.5		25-Nov-07		6:25:59		65.6		28.5

		15-Oct-07		8:07:10		71.6		45		15-Oct-07		8:06:20		69.2		50		15-Oct-07		8:07:53		68.61		49.5		25-Nov-07		8:25:59		65.6		28

		15-Oct-07		10:07:10		71		46.5		15-Oct-07		10:06:20		68.61		52		15-Oct-07		10:07:53		68		52		25-Nov-07		10:25:59		65.6		29

		15-Oct-07		12:07:10		71		46		15-Oct-07		12:06:20		69.2		52		15-Oct-07		12:07:53		68		53		25-Nov-07		12:25:59		66.2		30.5

		15-Oct-07		14:07:10		71.6		48		15-Oct-07		14:06:20		69.2		45		15-Oct-07		14:07:53		69.2		53		25-Nov-07		14:25:59		68		30

		15-Oct-07		16:07:10		72.21		49.5		15-Oct-07		16:06:20		69.2		49.5		15-Oct-07		16:07:53		69.8		53.5		25-Nov-07		16:25:59		68		30.5

		15-Oct-07		18:07:10		72.8		48		15-Oct-07		18:06:20		69.2		54.5		15-Oct-07		18:07:53		69.8		53.5		25-Nov-07		18:25:59		68		31.5

		15-Oct-07		20:07:10		74.01		44		15-Oct-07		20:06:20		71.6		48		15-Oct-07		20:07:53		69.8		50		25-Nov-07		20:25:59		67.4		32

		15-Oct-07		22:07:10		73.4		42.5		15-Oct-07		22:06:20		71.6		45.5		15-Oct-07		22:07:53		68		50		25-Nov-07		22:25:59		66.81		33

		16-Oct-07		0:07:10		72.8		42		16-Oct-07		0:06:20		71		45.5		16-Oct-07		0:07:53		66.81		50.5		26-Nov-07		0:25:59		66.81		33.5

		16-Oct-07		2:07:10		72.21		42		16-Oct-07		2:06:20		71		45.5		16-Oct-07		2:07:53		66.2		51		26-Nov-07		2:25:59		66.2		33.5

		16-Oct-07		4:07:10		72.21		42.5		16-Oct-07		4:06:20		70.41		46		16-Oct-07		4:07:53		65.6		51.5		26-Nov-07		4:25:59		66.2		34

		16-Oct-07		6:07:10		72.21		43		16-Oct-07		6:06:20		70.41		46.5		16-Oct-07		6:07:53		68.61		48.5		26-Nov-07		6:25:59		66.2		34

		16-Oct-07		8:07:10		72.21		45.5		16-Oct-07		8:06:20		70.41		51.5		16-Oct-07		8:07:53		68.61		49.5		26-Nov-07		8:25:59		65.6		34.5

		16-Oct-07		10:07:10		72.8		45.5		16-Oct-07		10:06:20		71.6		54.5		16-Oct-07		10:07:53		71		49.5		26-Nov-07		10:25:59		65.6		35.5

		16-Oct-07		12:07:10		72.8		48.5		16-Oct-07		12:06:20		69.8		44.5		16-Oct-07		12:07:53		71.6		53		26-Nov-07		12:25:59		66.2		36.5

		16-Oct-07		14:07:10		72.8		53		16-Oct-07		14:06:20		71		54		16-Oct-07		14:07:53		71		57.5		26-Nov-07		14:25:59		66.2		35.5

		16-Oct-07		16:07:10		74.01		48.5		16-Oct-07		16:06:20		69.8		59.5		16-Oct-07		16:07:53		70.41		55.5		26-Nov-07		16:25:59		66.81		35

		16-Oct-07		18:07:10		73.4		47.5		16-Oct-07		18:06:20		70.41		57.5		16-Oct-07		18:07:53		69.8		54.5		26-Nov-07		18:25:59		67.4		35.5

		16-Oct-07		20:07:10		74.6		48		16-Oct-07		20:06:20		72.21		53		16-Oct-07		20:07:53		70.41		54.5		26-Nov-07		20:25:59		66.81		36

		16-Oct-07		22:07:10		74.6		47		16-Oct-07		22:06:20		72.21		51		16-Oct-07		22:07:53		69.8		54		26-Nov-07		22:25:59		66.2		35.5

		17-Oct-07		0:07:10		74.01		45		17-Oct-07		0:06:20		72.8		48.5		17-Oct-07		0:07:53		69.2		52.5		27-Nov-07		0:25:59		65.6		35.5

		17-Oct-07		2:07:10		73.4		43		17-Oct-07		2:06:20		71.6		45.5		17-Oct-07		2:07:53		68		51		27-Nov-07		2:25:59		65.6		34.5

		17-Oct-07		4:07:10		72.8		42.5		17-Oct-07		4:06:20		71		45		17-Oct-07		4:07:53		66.81		50.5		27-Nov-07		4:25:59		65.01		34

		17-Oct-07		6:07:10		72.8		43		17-Oct-07		6:06:20		70.41		44.5		17-Oct-07		6:07:53		68		49		27-Nov-07		6:25:59		66.2		32.5

		17-Oct-07		8:07:10		71.6		43.5		17-Oct-07		8:06:20		69.8		48		17-Oct-07		8:07:53		69.8		46		27-Nov-07		8:25:59		68.61		30.5

		17-Oct-07		10:07:10		72.8		43.5		17-Oct-07		10:06:20		71		52.5		17-Oct-07		10:07:53		71		46		27-Nov-07		10:25:59		70.41		32.5

		17-Oct-07		12:07:10		73.4		46		17-Oct-07		12:06:20		71		55.5		17-Oct-07		12:07:53		71.6		46		27-Nov-07		12:25:59		72.21		33.5

		17-Oct-07		14:07:10		73.4		47		17-Oct-07		14:06:20		71		41		17-Oct-07		14:07:53		71		52.5		27-Nov-07		14:25:59		72.8		34.5

		17-Oct-07		16:07:10		72.8		53		17-Oct-07		16:06:20		69.2		55.5		17-Oct-07		16:07:53		70.41		60.5		27-Nov-07		16:25:59		73.4		35.5

		17-Oct-07		18:07:10		72.8		52		17-Oct-07		18:06:20		69.2		60		17-Oct-07		18:07:53		69.8		55.5		27-Nov-07		18:25:59		72.8		37

		17-Oct-07		20:07:10		72.8		46.5		17-Oct-07		20:06:20		71		49.5		17-Oct-07		20:07:53		69.8		51.5		27-Nov-07		20:25:59		71		37

		17-Oct-07		22:07:10		72.21		44		17-Oct-07		22:06:20		71		46.5		17-Oct-07		22:07:53		68		49.5		27-Nov-07		22:25:59		69.8		36.5

		18-Oct-07		0:07:10		71		42		18-Oct-07		0:06:20		69.8		44		18-Oct-07		0:07:53		66.81		48.5		28-Nov-07		0:25:59		68.61		36.5

		18-Oct-07		2:07:10		70.41		41		18-Oct-07		2:06:20		69.2		43		18-Oct-07		2:07:53		66.2		47.5		28-Nov-07		2:25:59		67.4		36.5

		18-Oct-07		4:07:10		70.41		41.5		18-Oct-07		4:06:20		69.2		44		18-Oct-07		4:07:53		66.2		48.5		28-Nov-07		4:25:59		66.81		36.5

		18-Oct-07		6:07:10		71		43.5		18-Oct-07		6:06:20		69.8		46		18-Oct-07		6:07:53		68		48		28-Nov-07		6:25:59		67.4		36

		18-Oct-07		8:07:10		71.6		44.5		18-Oct-07		8:06:20		71		49.5		18-Oct-07		8:07:53		69.8		46		28-Nov-07		8:25:59		69.8		35

		18-Oct-07		10:07:10		74.01		45.5		18-Oct-07		10:06:20		74.01		41.5		18-Oct-07		10:07:53		71		51.5		28-Nov-07		10:25:59		73.4		36

		18-Oct-07		12:07:10		74.6		44		18-Oct-07		12:06:20		73.4		46.5		18-Oct-07		12:07:53		71.6		50.5		28-Nov-07		12:25:59		72.8		38.5

		18-Oct-07		14:07:10		75.2		41.5		18-Oct-07		14:06:20		74.6		37.5		18-Oct-07		14:07:53		71.6		45		28-Nov-07		14:25:59		73.4		35

		18-Oct-07		16:07:10		75.2		41		18-Oct-07		16:06:20		72.21		41.5		18-Oct-07		16:07:53		70.41		47		28-Nov-07		16:25:59		74.01		34

		18-Oct-07		18:07:10		74.6		41.5		18-Oct-07		18:06:20		71.6		42.5		18-Oct-07		18:07:53		70.41		48.5		28-Nov-07		18:25:59		74.01		35.5

		18-Oct-07		20:07:10		74.6		41		18-Oct-07		20:06:20		72.8		44		18-Oct-07		20:07:53		69.8		47		28-Nov-07		20:25:59		72.21		37

		18-Oct-07		22:07:10		73.4		40.5		18-Oct-07		22:06:20		72.21		43		18-Oct-07		22:07:53		68.61		47.5		28-Nov-07		22:25:59		71		37

		19-Oct-07		0:07:10		72.8		41		19-Oct-07		0:06:20		72.21		43.5		19-Oct-07		0:07:53		67.4		48.5		29-Nov-07		0:25:59		69.8		37

		19-Oct-07		2:07:10		72.21		41.5		19-Oct-07		2:06:20		71		43.5		19-Oct-07		2:07:53		66.81		49.5		29-Nov-07		2:25:59		68.61		37

		19-Oct-07		4:07:10		71.6		42.5		19-Oct-07		4:06:20		71		44.5		19-Oct-07		4:07:53		66.2		52		29-Nov-07		4:25:59		67.4		36.5

		19-Oct-07		6:07:10		71.6		43		19-Oct-07		6:06:20		71		45.5		19-Oct-07		6:07:53		68		49		29-Nov-07		6:25:59		67.4		34.5

		19-Oct-07		8:07:10		72.21		44		19-Oct-07		8:06:20		72.21		47		19-Oct-07		8:07:53		69.2		48		29-Nov-07		8:25:59		69.8		32

		19-Oct-07		10:07:10		72.8		43.5		19-Oct-07		10:06:20		72.21		40		19-Oct-07		10:07:53		71		49.5		29-Nov-07		10:25:59		72.21		33

		19-Oct-07		12:07:10		74.01		44.5		19-Oct-07		12:06:20		72.21		49.5		19-Oct-07		12:07:53		71.6		51		29-Nov-07		12:25:59		72.21		33

		19-Oct-07		14:07:10		75.2		47		19-Oct-07		14:06:20		72.8		47		19-Oct-07		14:07:53		71		54		29-Nov-07		14:25:59		73.4		32.5

		19-Oct-07		16:07:10		74.6		47		19-Oct-07		16:06:20		71.6		45.5		19-Oct-07		16:07:53		71		48		29-Nov-07		16:25:59		73.4		32

		19-Oct-07		18:07:10		74.6		51.5		19-Oct-07		18:06:20		71		56.5		19-Oct-07		18:07:53		70.41		58.5		29-Nov-07		18:25:59		72.8		30.5

		19-Oct-07		20:07:10		74.6		51.5		19-Oct-07		20:06:20		72.8		57		19-Oct-07		20:07:53		70.41		58		29-Nov-07		20:25:59		71		32

		19-Oct-07		22:07:10		74.01		52.5		19-Oct-07		22:06:20		73.4		56		19-Oct-07		22:07:53		70.41		59		29-Nov-07		22:25:59		69.8		32.5

		20-Oct-07		0:07:10		74.01		53		20-Oct-07		0:06:20		72.8		57.5		20-Oct-07		0:07:53		70.41		60.5		30-Nov-07		0:25:59		69.2		33

		20-Oct-07		2:07:10		73.4		55.5		20-Oct-07		2:06:20		72.8		59		20-Oct-07		2:07:53		69.8		61.5		30-Nov-07		2:25:59		68		32.5

		20-Oct-07		4:07:10		73.4		56		20-Oct-07		4:06:20		72.8		59.5		20-Oct-07		4:07:53		69.8		62		30-Nov-07		4:25:59		67.4		32.5

		20-Oct-07		6:07:10		74.01		56		20-Oct-07		6:06:20		72.8		59		20-Oct-07		6:07:53		70.41		65		30-Nov-07		6:25:59		67.4		31.5

		20-Oct-07		8:07:10		73.4		52.5		20-Oct-07		8:06:20		71		55		20-Oct-07		8:07:53		71		63.5		30-Nov-07		8:25:59		69.2		29.5

		20-Oct-07		10:07:10		73.4		54.5		20-Oct-07		10:06:20		71		54		20-Oct-07		10:07:53		71.6		63.5		30-Nov-07		10:25:59		72.21		31.5

		20-Oct-07		12:07:10		74.6		53		20-Oct-07		12:06:20		71		59.5		20-Oct-07		12:07:53		71.6		58		30-Nov-07		12:25:59		71.6		33

		20-Oct-07		14:07:10		75.2		54.5		20-Oct-07		14:06:20		71		48.5		20-Oct-07		14:07:53		71		62		30-Nov-07		14:25:59		74.01		31.5

		20-Oct-07		16:07:10		74.6		56.5		20-Oct-07		16:06:20		69.8		67		20-Oct-07		16:07:53		70.41		70		30-Nov-07		16:25:59		74.6		30.5

		20-Oct-07		18:07:10		73.4		57.5		20-Oct-07		18:06:20		69.2		61		20-Oct-07		18:07:53		70.41		59.5		30-Nov-07		18:25:59		74.01		29

		20-Oct-07		20:07:10		74.6		53.5		20-Oct-07		20:06:20		72.21		58		20-Oct-07		20:07:53		69.8		61.5		30-Nov-07		20:25:59		72.8		27.5

		20-Oct-07		22:07:10		74.01		49		20-Oct-07		22:06:20		72.21		51.5		20-Oct-07		22:07:53		69.2		56.5		30-Nov-07		22:25:59		71		30

		21-Oct-07		0:07:10		73.4		45		21-Oct-07		0:06:20		71.6		46.5		21-Oct-07		0:07:53		68		53		1-Dec-07		0:25:59		69.2		31

		21-Oct-07		2:07:10		72.21		44.5		21-Oct-07		2:06:20		71		47		21-Oct-07		2:07:53		66.81		53.5		1-Dec-07		2:25:59		68		31

		21-Oct-07		4:07:10		71.6		45		21-Oct-07		4:06:20		71		47		21-Oct-07		4:07:53		66.2		54		1-Dec-07		4:25:59		67.4		31

		21-Oct-07		6:07:10		71		43		21-Oct-07		6:06:20		70.41		45		21-Oct-07		6:07:53		65.6		52		1-Dec-07		6:25:59		68		29.5

		21-Oct-07		8:07:10		70.41		42		21-Oct-07		8:06:20		68.61		44		21-Oct-07		8:07:53		68		46		1-Dec-07		8:25:59		71		28

		21-Oct-07		10:07:10		70.41		45		21-Oct-07		10:06:20		69.2		50		21-Oct-07		10:07:53		67.4		52		1-Dec-07		10:25:59		72.8		28

		21-Oct-07		12:07:10		71		41.5		21-Oct-07		12:06:20		68.61		42.5		21-Oct-07		12:07:53		69.2		45		1-Dec-07		12:25:59		74.01		26.5

		21-Oct-07		14:07:10		71		37.5		21-Oct-07		14:06:20		69.2		37		21-Oct-07		14:07:53		69.2		40.5		1-Dec-07		14:25:59		74.01		27

		21-Oct-07		16:07:10		71		36		21-Oct-07		16:06:20		68.61		38		21-Oct-07		16:07:53		69.2		38		1-Dec-07		16:25:59		74.6		26

		21-Oct-07		18:07:10		71.6		35		21-Oct-07		18:06:20		68.61		37		21-Oct-07		18:07:53		69.8		37		1-Dec-07		18:25:59		75.2		26.5

		21-Oct-07		20:07:10		72.21		35.5		21-Oct-07		20:06:20		70.41		38		21-Oct-07		20:07:53		68.61		40		1-Dec-07		20:25:59		74.01		25

		21-Oct-07		22:07:10		72.21		36		21-Oct-07		22:06:20		71		38		21-Oct-07		22:07:53		67.4		42		1-Dec-07		22:25:59		70.41		27

		22-Oct-07		0:07:10		71.6		36		22-Oct-07		0:06:20		70.41		38		22-Oct-07		0:07:53		66.2		42.5		2-Dec-07		0:25:59		68.61		28

		22-Oct-07		2:07:10		71		35.5		22-Oct-07		2:06:20		69.8		37.5		22-Oct-07		2:07:53		65.01		43		2-Dec-07		2:25:59		67.4		27.5

		22-Oct-07		4:07:10		70.41		35.5		22-Oct-07		4:06:20		69.8		37		22-Oct-07		4:07:53		64.4		43		2-Dec-07		4:25:59		66.2		27.5

		22-Oct-07		6:07:10		69.8		34.5		22-Oct-07		6:06:20		69.2		36.5		22-Oct-07		6:07:53		63.8		42.5		2-Dec-07		6:25:59		66.2		27

		22-Oct-07		8:07:10		69.2		34.5		22-Oct-07		8:06:20		68.61		36.5		22-Oct-07		8:07:53		68		37.5		2-Dec-07		8:25:59		66.2		26

		22-Oct-07		10:07:10		69.8		33.5		22-Oct-07		10:06:20		68.61		35		22-Oct-07		10:07:53		67.4		37.5		2-Dec-07		10:25:59		66.2		26.5

		22-Oct-07		12:07:10		69.8		33		22-Oct-07		12:06:20		68.61		34		22-Oct-07		12:07:53		68.61		35.5		2-Dec-07		12:25:59		66.81		29

		22-Oct-07		14:07:10		71		31		22-Oct-07		14:06:20		68.61		32		22-Oct-07		14:07:53		69.8		34		2-Dec-07		14:25:59		67.4		29.5

		22-Oct-07		16:07:10		72.21		30.5		22-Oct-07		16:06:20		68.61		31		22-Oct-07		16:07:53		70.41		33.5		2-Dec-07		16:25:59		68		30

		22-Oct-07		18:07:10		72.21		30.5		22-Oct-07		18:06:20		69.2		32.5		22-Oct-07		18:07:53		70.41		33.5		2-Dec-07		18:25:59		67.4		30

		22-Oct-07		20:07:10		74.01		28		22-Oct-07		20:06:20		72.21		29.5		22-Oct-07		20:07:53		71.6		31		2-Dec-07		20:25:59		66.81		31

		22-Oct-07		22:07:10		74.01		32		22-Oct-07		22:06:20		72.8		35		22-Oct-07		22:07:53		71		36.5		2-Dec-07		22:25:59		66.2		31

		23-Oct-07		0:07:10		73.4		33		23-Oct-07		0:06:20		72.21		36		23-Oct-07		0:07:53		69.2		38		3-Dec-07		0:25:59		66.2		30.5

		23-Oct-07		2:07:10		72.8		33.5		23-Oct-07		2:06:20		71.6		36.5		23-Oct-07		2:07:53		68.61		39		3-Dec-07		2:25:59		66.2		31

		23-Oct-07		4:07:10		72.21		34		23-Oct-07		4:06:20		71		36.5		23-Oct-07		4:07:53		66.81		40		3-Dec-07		4:25:59		66.2		32.5

		23-Oct-07		6:07:10		71.6		34.5		23-Oct-07		6:06:20		69.8		36.5		23-Oct-07		6:07:53		68		39.5		3-Dec-07		6:25:59		66.2		34.5

		23-Oct-07		8:07:10		71.6		35.5		23-Oct-07		8:06:20		69.8		38.5		23-Oct-07		8:07:53		69.2		38		3-Dec-07		8:25:59		66.2		35.5

		23-Oct-07		10:07:10		72.21		37.5		23-Oct-07		10:06:20		70.41		43.5		23-Oct-07		10:07:53		70.41		42		3-Dec-07		10:25:59		66.81		35.5

		23-Oct-07		12:07:10		72.8		35		23-Oct-07		12:06:20		70.41		36.5		23-Oct-07		12:07:53		71.6		34.5		3-Dec-07		12:25:59		67.4		36.5

		23-Oct-07		14:07:10		74.6		38.5		23-Oct-07		14:06:20		69.8		45		23-Oct-07		14:07:53		71.6		41		3-Dec-07		14:25:59		67.4		37.5

		23-Oct-07		16:07:10		75.81		35		23-Oct-07		16:06:20		71		41.5		23-Oct-07		16:07:53		71.6		42.5		3-Dec-07		16:25:59		68		39

		23-Oct-07		18:07:10		75.2		34		23-Oct-07		18:06:20		71.6		36		23-Oct-07		18:07:53		71		36		3-Dec-07		18:25:59		68		39.5

		23-Oct-07		20:07:10		75.81		34.5		23-Oct-07		20:06:20		72.8		38		23-Oct-07		20:07:53		70.41		40.5		3-Dec-07		20:25:59		68		40

		23-Oct-07		22:07:10		75.2		36		23-Oct-07		22:06:20		72.21		40		23-Oct-07		22:07:53		71.6		40.5		3-Dec-07		22:25:59		68		42

		24-Oct-07		0:07:10		74.6		36.5		24-Oct-07		0:06:20		72.21		40.5		24-Oct-07		0:07:53		71		42		4-Dec-07		0:25:59		68		42

		24-Oct-07		2:07:10		74.01		36.5		24-Oct-07		2:06:20		72.21		40		24-Oct-07		2:07:53		69.2		42.5		4-Dec-07		2:25:59		68		41.5

		24-Oct-07		4:07:10		73.4		36.5		24-Oct-07		4:06:20		72.21		39		24-Oct-07		4:07:53		68.61		42.5		4-Dec-07		4:25:59		67.4		41.5

		24-Oct-07		6:07:10		73.4		35.5		24-Oct-07		6:06:20		72.21		38		24-Oct-07		6:07:53		68		42.5		4-Dec-07		6:25:59		68.61		41

		24-Oct-07		8:07:10		73.4		36		24-Oct-07		8:06:20		71.6		40		24-Oct-07		8:07:53		69.8		40		4-Dec-07		8:25:59		72.8		37

		24-Oct-07		10:07:10		75.2		39		24-Oct-07		10:06:20		72.21		40.5		24-Oct-07		10:07:53		71.6		46.5		4-Dec-07		10:25:59		74.6		38

		24-Oct-07		12:07:10		75.81		39.5		24-Oct-07		12:06:20		72.21		38		24-Oct-07		12:07:53		71.6		49		4-Dec-07		12:25:59		75.2		36

		24-Oct-07		14:07:10		75.81		39		24-Oct-07		14:06:20		72.8		46.5		24-Oct-07		14:07:53		71.6		49		4-Dec-07		14:25:59		74.6		37

		24-Oct-07		16:07:10		76.4		40		24-Oct-07		16:06:20		71.6		50		24-Oct-07		16:07:53		71.6		45		4-Dec-07		16:25:59		74.6		38

		24-Oct-07		18:07:10		74.6		41		24-Oct-07		18:06:20		69.8		42		24-Oct-07		18:07:53		71		53.5		4-Dec-07		18:25:59		74.6		39

		24-Oct-07		20:07:10		75.81		43.5		24-Oct-07		20:06:20		73.4		48.5		24-Oct-07		20:07:53		70.41		55.5		4-Dec-07		20:25:59		74.01		39.5

		24-Oct-07		22:07:10		75.81		43.5		24-Oct-07		22:06:20		72.8		48		24-Oct-07		22:07:53		72.8		48		4-Dec-07		22:25:59		72.8		41

		25-Oct-07		0:07:10		75.2		41.5		25-Oct-07		0:06:20		72.8		45.5		25-Oct-07		0:07:53		72.21		46		5-Dec-07		0:25:59		71.6		44.5

		25-Oct-07		2:07:10		74.6		40		25-Oct-07		2:06:20		72.8		43.5		25-Oct-07		2:07:53		71.6		45		5-Dec-07		2:25:59		70.41		45

		25-Oct-07		4:07:10		74.01		39		25-Oct-07		4:06:20		72.8		41.5		25-Oct-07		4:07:53		69.8		44		5-Dec-07		4:25:59		69.8		45.5

		25-Oct-07		6:07:10		73.4		39		25-Oct-07		6:06:20		71.6		42		25-Oct-07		6:07:53		69.2		45		5-Dec-07		6:25:59		70.41		50

		25-Oct-07		8:07:10		72.8		39.5		25-Oct-07		8:06:20		71		45.5		25-Oct-07		8:07:53		71		42.5		5-Dec-07		8:25:59		74.6		47

		25-Oct-07		10:07:10		72.8		43.5		25-Oct-07		10:06:20		70.41		52.5		25-Oct-07		10:07:53		71.6		49.5		5-Dec-07		10:25:59		75.81		48

		25-Oct-07		12:07:10		73.4		43.5		25-Oct-07		12:06:20		70.41		52		25-Oct-07		12:07:53		71.6		44		5-Dec-07		12:25:59		75.2		50

		25-Oct-07		14:07:10		74.01		42		25-Oct-07		14:06:20		71		39.5		25-Oct-07		14:07:53		71.6		47		5-Dec-07		14:25:59		74.6		51.5

		25-Oct-07		16:07:10		74.6		46		25-Oct-07		16:06:20		69.8		54		25-Oct-07		16:07:53		71.6		50.5		5-Dec-07		16:25:59		74.6		50

		25-Oct-07		18:07:10		74.6		47		25-Oct-07		18:06:20		69.2		56.5		25-Oct-07		18:07:53		71		48.5		5-Dec-07		18:25:59		74.6		49.5

		25-Oct-07		20:07:10		75.81		42		25-Oct-07		20:06:20		72.8		46.5		25-Oct-07		20:07:53		72.8		46.5		5-Dec-07		20:25:59		74.6		48.5

		25-Oct-07		22:07:10		75.2		40.5		25-Oct-07		22:06:20		72.8		43.5		25-Oct-07		22:07:53		72.8		44.5		5-Dec-07		22:25:59		72.8		50

		26-Oct-07		0:07:10		74.6		39.5		26-Oct-07		0:06:20		72.8		43.5		26-Oct-07		0:07:53		71.6		44		6-Dec-07		0:25:59		72.21		51.5

		26-Oct-07		2:07:10		74.01		39		26-Oct-07		2:06:20		72.21		42		26-Oct-07		2:07:53		69.8		44		6-Dec-07		2:25:59		71		51.5

		26-Oct-07		4:07:10		72.8		38		26-Oct-07		4:06:20		71		40.5		26-Oct-07		4:07:53		68.61		43.5		6-Dec-07		4:25:59		70.41		52

		26-Oct-07		6:07:10		72.8		37.5		26-Oct-07		6:06:20		70.41		39.5		26-Oct-07		6:07:53		68		43.5		6-Dec-07		6:25:59		70.41		52

		26-Oct-07		8:07:10		72.21		38		26-Oct-07		8:06:20		69.8		42.5		26-Oct-07		8:07:53		69.2		40.5		6-Dec-07		8:25:59		74.6		46.5

		26-Oct-07		10:07:10		72.8		38.5		26-Oct-07		10:06:20		71		40		26-Oct-07		10:07:53		71		47.5		6-Dec-07		10:25:59		75.81		45

		26-Oct-07		12:07:10		73.4		44.5		26-Oct-07		12:06:20		70.41		50.5		26-Oct-07		12:07:53		71.6		44.5		6-Dec-07		12:25:59		75.2		47

		26-Oct-07		14:07:10		74.6		40		26-Oct-07		14:06:20		71		39.5		26-Oct-07		14:07:53		71.6		48.5		6-Dec-07		14:25:59		74.6		49

		26-Oct-07		16:07:10		74.6		47		26-Oct-07		16:06:20		69.8		58.5		26-Oct-07		16:07:53		71		56		6-Dec-07		16:25:59		74.6		47

		26-Oct-07		18:07:10		74.01		47.5		26-Oct-07		18:06:20		69.2		56		26-Oct-07		18:07:53		70.41		52.5		6-Dec-07		18:25:59		74.6		40.5

		26-Oct-07		20:07:10		74.6		41.5		26-Oct-07		20:06:20		71		47.5		26-Oct-07		20:07:53		71		47.5		6-Dec-07		20:25:59		74.01		39.5

		26-Oct-07		22:07:10		74.01		40.5		26-Oct-07		22:06:20		71		40.5		26-Oct-07		22:07:53		70.41		45.5		6-Dec-07		22:25:59		72.21		42

		27-Oct-07		0:07:10		73.4		40.5		27-Oct-07		0:06:20		71.6		44.5		27-Oct-07		0:07:53		69.2		46		7-Dec-07		0:25:59		71		44

		27-Oct-07		2:07:10		72.8		41.5		27-Oct-07		2:06:20		70.41		46.5		27-Oct-07		2:07:53		68		48		7-Dec-07		2:25:59		70.41		43.5

		27-Oct-07		4:07:10		72.21		42		27-Oct-07		4:06:20		70.41		46		27-Oct-07		4:07:53		68		48.5		7-Dec-07		4:25:59		70.41		44

		27-Oct-07		6:07:10		72.8		42		27-Oct-07		6:06:20		71		45.5		27-Oct-07		6:07:53		68		49		7-Dec-07		6:25:59		70.41		44.5

		27-Oct-07		8:07:10		72.21		41		27-Oct-07		8:06:20		71		45.5		27-Oct-07		8:07:53		71		46.5		7-Dec-07		8:25:59		74.6		41

		27-Oct-07		10:07:10		72.8		45		27-Oct-07		10:06:20		71		45.5		27-Oct-07		10:07:53		71		37.5		7-Dec-07		10:25:59		74.6		42

		27-Oct-07		12:07:10		73.4		45		27-Oct-07		12:06:20		70.41		53.5		27-Oct-07		12:07:53		71		52.5		7-Dec-07		12:25:59		72.8		45.5

		27-Oct-07		14:07:10		73.4		42.5		27-Oct-07		14:06:20		71		47.5		27-Oct-07		14:07:53		71		51		7-Dec-07		14:25:59		72.8		46.5

		27-Oct-07		16:07:10		73.4		46		27-Oct-07		16:06:20		68.61		46		27-Oct-07		16:07:53		71		46.5		7-Dec-07		16:25:59		72.8		47.5

		27-Oct-07		18:07:10		73.4		44.5		27-Oct-07		18:06:20		68		46.5		27-Oct-07		18:07:53		69.8		49.5		7-Dec-07		18:25:59		72.8		46

		27-Oct-07		20:07:10		72.8		42		27-Oct-07		20:06:20		69.2		47.5		27-Oct-07		20:07:53		69.8		46.5		7-Dec-07		20:25:59		72.21		46

		27-Oct-07		22:07:10		72.21		41.5		27-Oct-07		22:06:20		69.2		46		27-Oct-07		22:07:53		68.61		46		7-Dec-07		22:25:59		69.8		47.5

		28-Oct-07		0:07:10		71.6		40		28-Oct-07		0:06:20		68.61		44.5		28-Oct-07		0:07:53		67.4		45		8-Dec-07		0:25:59		68.61		48

		28-Oct-07		2:07:10		71		39		28-Oct-07		2:06:20		68.61		43		28-Oct-07		2:07:53		66.2		45		8-Dec-07		2:25:59		68		47

		28-Oct-07		4:07:10		70.41		38.5		28-Oct-07		4:06:20		68.61		41.5		28-Oct-07		4:07:53		65.01		45.5		8-Dec-07		4:25:59		67.4		46.5

		28-Oct-07		6:07:10		69.8		38		28-Oct-07		6:06:20		68		41.5		28-Oct-07		6:07:53		63.8		46		8-Dec-07		6:25:59		68		45.5

		28-Oct-07		8:07:10		69.2		39.5		28-Oct-07		8:06:20		68		43.5		28-Oct-07		8:07:53		66.81		43.5		8-Dec-07		8:25:59		71.6		40

		28-Oct-07		10:07:10		69.2		42		28-Oct-07		10:06:20		68		47		28-Oct-07		10:07:53		66.81		46.5		8-Dec-07		10:25:59		72.21		39.5

		28-Oct-07		12:07:10		69.2		44.5		28-Oct-07		12:06:20		67.4		50		28-Oct-07		12:07:53		67.4		48		8-Dec-07		12:25:59		71.6		40

		28-Oct-07		14:07:10		69.8		47		28-Oct-07		14:06:20		67.4		53		28-Oct-07		14:07:53		68.61		50		8-Dec-07		14:25:59		72.21		39.5

		28-Oct-07		16:07:10		70.41		49.5		28-Oct-07		16:06:20		67.4		49		28-Oct-07		16:07:53		69.2		52		8-Dec-07		16:25:59		72.21		38

		28-Oct-07		18:07:10		71		43		28-Oct-07		18:06:20		68		46.5		28-Oct-07		18:07:53		69.2		47.5		8-Dec-07		18:25:59		71.6		37.5

		28-Oct-07		20:07:10		71		43.5		28-Oct-07		20:06:20		68.61		47		28-Oct-07		20:07:53		68.61		47		8-Dec-07		20:25:59		70.41		36.5

		28-Oct-07		22:07:10		71		41		28-Oct-07		22:06:20		69.2		44.5		28-Oct-07		22:07:53		67.4		46.5		8-Dec-07		22:25:59		69.8		36.5

		29-Oct-07		0:07:10		70.41		41.5		29-Oct-07		0:06:20		68.61		44.5		29-Oct-07		0:07:53		66.2		47		9-Dec-07		0:25:59		68		37

		29-Oct-07		2:07:10		70.41		41.5		29-Oct-07		2:06:20		68.61		44.5		29-Oct-07		2:07:53		65.6		48		9-Dec-07		2:25:59		66.81		37

		29-Oct-07		4:07:10		69.8		40.5		29-Oct-07		4:06:20		68		44		29-Oct-07		4:07:53		65.01		48		9-Dec-07		4:25:59		66.2		36.5

		29-Oct-07		6:07:10		69.8		40.5		29-Oct-07		6:06:20		68		43.5		29-Oct-07		6:07:53		64.4		48		9-Dec-07		6:25:59		66.2		36

		29-Oct-07		8:07:10		69.2		40		29-Oct-07		8:06:20		68		43		29-Oct-07		8:07:53		67.4		43.5		9-Dec-07		8:25:59		66.2		35.5

		29-Oct-07		10:07:10		69.2		43.5		29-Oct-07		10:06:20		68		49.5		29-Oct-07		10:07:53		67.4		48		9-Dec-07		10:25:59		66.2		34

		29-Oct-07		12:07:10		69.8		47.5		29-Oct-07		12:06:20		68		53.5		29-Oct-07		12:07:53		69.2		50		9-Dec-07		12:25:59		66.2		34

		29-Oct-07		14:07:10		71		48.5		29-Oct-07		14:06:20		68		48.5		29-Oct-07		14:07:53		69.8		54.5		9-Dec-07		14:25:59		66.81		33.5

		29-Oct-07		16:07:10		71.6		48.5		29-Oct-07		16:06:20		68.61		55		29-Oct-07		16:07:53		70.41		45.5		9-Dec-07		16:25:59		66.81		33

		29-Oct-07		18:07:10		72.21		50.5		29-Oct-07		18:06:20		68.61		62.5		29-Oct-07		18:07:53		70.41		55.5		9-Dec-07		18:25:59		66.81		31

		29-Oct-07		20:07:10		72.8		48.5		29-Oct-07		20:06:20		69.2		46		29-Oct-07		20:07:53		71.6		50		9-Dec-07		20:25:59		65.6		30.5

		29-Oct-07		22:07:10		72.21		46		29-Oct-07		22:06:20		69.2		51.5		29-Oct-07		22:07:53		70.41		48.5		9-Dec-07		22:25:59		65.01		31.5

		30-Oct-07		0:07:10		71.6		45		30-Oct-07		0:06:20		68.61		50.5		30-Oct-07		0:07:53		69.2		48		10-Dec-07		0:25:59		64.4		31

		30-Oct-07		2:07:10		71.6		44.5		30-Oct-07		2:06:20		68.61		46.5		30-Oct-07		2:07:53		68.61		48.5		10-Dec-07		2:25:59		63.8		31

		30-Oct-07		4:07:10		71		43.5		30-Oct-07		4:06:20		69.2		48		30-Oct-07		4:07:53		67.4		49		10-Dec-07		4:25:59		63.21		31

		30-Oct-07		6:07:10		71.6		43.5		30-Oct-07		6:06:20		69.2		46.5		30-Oct-07		6:07:53		68		49		10-Dec-07		6:25:59		62.6		31

		30-Oct-07		8:07:10		71		46		30-Oct-07		8:06:20		68.61		44.5		30-Oct-07		8:07:53		69.2		47.5		10-Dec-07		8:25:59		63.21		31

		30-Oct-07		10:07:10		72.21		46		30-Oct-07		10:06:20		69.2		55.5		30-Oct-07		10:07:53		71.6		47.5		10-Dec-07		10:25:59		64.4		31

		30-Oct-07		12:07:10		72.21		49		30-Oct-07		12:06:20		69.8		56		30-Oct-07		12:07:53		71		49		10-Dec-07		12:25:59		65.6		31.5

		30-Oct-07		14:07:10		73.4		47		30-Oct-07		14:06:20		70.41		53.5		30-Oct-07		14:07:53		71		55		10-Dec-07		14:25:59		66.2		32

		30-Oct-07		16:07:10		73.4		48.5		30-Oct-07		16:06:20		68.61		61.5		30-Oct-07		16:07:53		70.41		54		10-Dec-07		16:25:59		66.81		32.5

		30-Oct-07		18:07:10		72.8		45		30-Oct-07		18:06:20		69.2		54.5		30-Oct-07		18:07:53		70.41		51.5		10-Dec-07		18:25:59		66.81		33

		30-Oct-07		20:07:10		72.21		46		30-Oct-07		20:06:20		68.61		53		30-Oct-07		20:07:53		69.8		48.5		10-Dec-07		20:25:59		66.2		34

		30-Oct-07		22:07:10		71.6		45.5		30-Oct-07		22:06:20		68.61		51.5		30-Oct-07		22:07:53		69.2		49		10-Dec-07		22:25:59		65.01		35

		31-Oct-07		0:07:10		71.6		45		31-Oct-07		0:06:20		69.2		50		31-Oct-07		0:07:53		68.61		49.5		11-Dec-07		0:25:59		64.4		36.5

		31-Oct-07		2:07:10		71		46.5		31-Oct-07		2:06:20		68.61		52		31-Oct-07		2:07:53		68		51		11-Dec-07		2:25:59		63.21		36.5

		31-Oct-07		4:07:10		71		47		31-Oct-07		4:06:20		68.61		52		31-Oct-07		4:07:53		67.4		52.5		11-Dec-07		4:25:59		63.21		36

		31-Oct-07		6:07:10		71.6		47		31-Oct-07		6:06:20		68.61		52		31-Oct-07		6:07:53		72.21		48		11-Dec-07		6:25:59		64.4		34.5

		31-Oct-07		8:07:10		71.6		47.5		31-Oct-07		8:06:20		69.8		48.5		31-Oct-07		8:07:53		71		43.5		11-Dec-07		8:25:59		66.81		31.5

		31-Oct-07		10:07:10		72.21		48		31-Oct-07		10:06:20		69.8		51.5		31-Oct-07		10:07:53		71.6		49.5		11-Dec-07		10:25:59		69.8		31.5

		31-Oct-07		12:07:10		72.8		46.5		31-Oct-07		12:06:20		69.2		45.5		31-Oct-07		12:07:53		72.21		48		11-Dec-07		12:25:59		74.01		32

		31-Oct-07		14:07:10		72.8		46.5		31-Oct-07		14:06:20		70.41		45.5		31-Oct-07		14:07:53		71		52		11-Dec-07		14:25:59		71.6		33.5

		31-Oct-07		16:07:10		73.4		47		31-Oct-07		16:06:20		68		51		31-Oct-07		16:07:53		71		45.5		11-Dec-07		16:25:59		71.6		34.5

		31-Oct-07		18:07:10		72.8		47		31-Oct-07		18:06:20		68.61		48		31-Oct-07		18:07:53		70.41		51.5		11-Dec-07		18:25:59		71.6		33.5

		31-Oct-07		20:07:10		72.21		45		31-Oct-07		20:06:20		68.61		51.5		31-Oct-07		20:07:53		69.8		48		11-Dec-07		20:25:59		69.8		33.5

		31-Oct-07		22:07:10		72.21		44.5		31-Oct-07		22:06:20		69.2		49.5		31-Oct-07		22:07:53		68.61		49.5		11-Dec-07		22:25:59		67.4		33

		1-Nov-07		0:07:10		71.6		44.5		1-Nov-07		0:06:20		69.2		49.5		1-Nov-07		0:07:53		67.4		50		12-Dec-07		0:25:59		66.2		33.5

		1-Nov-07		2:07:10		71.6		45.5		1-Nov-07		2:06:20		69.2		50		1-Nov-07		2:07:53		66.81		51.5		12-Dec-07		2:25:59		65.01		31

		1-Nov-07		4:07:10		71		46.5		1-Nov-07		4:06:20		68.61		52		1-Nov-07		4:07:53		66.81		53		12-Dec-07		4:25:59		63.8		29

		1-Nov-07		6:07:10		71.6		47.5		1-Nov-07		6:06:20		69.2		53.5		1-Nov-07		6:07:53		68.61		51		12-Dec-07		6:25:59		65.6		24

		1-Nov-07		8:07:10		72.21		44.5		1-Nov-07		8:06:20		69.8		53.5		1-Nov-07		8:07:53		70.41		49		12-Dec-07		8:25:59		69.8		21.5

		1-Nov-07		10:07:10		72.21		47		1-Nov-07		10:06:20		68.61		51.5		1-Nov-07		10:07:53		71		48.5		12-Dec-07		10:25:59		72.21		23

		1-Nov-07		12:07:10		72.8		45.5		1-Nov-07		12:06:20		69.8		44		1-Nov-07		12:07:53		71.6		45.5		12-Dec-07		12:25:59		71.6		22

		1-Nov-07		14:07:10		72.8		46.5		1-Nov-07		14:06:20		68.61		47.5		1-Nov-07		14:07:53		71		51		12-Dec-07		14:25:59		72.21		21

		1-Nov-07		16:07:10		72.8		51.5		1-Nov-07		16:06:20		68.61		60.5		1-Nov-07		16:07:53		70.41		55.5		12-Dec-07		16:25:59		72.21		20.5

		1-Nov-07		18:07:10		72.8		50		1-Nov-07		18:06:20		68.61		59		1-Nov-07		18:07:53		69.8		54.5		12-Dec-07		18:25:59		71.6		23

		1-Nov-07		20:07:10		72.21		47.5		1-Nov-07		20:06:20		68.61		53.5		1-Nov-07		20:07:53		69.8		50.5		12-Dec-07		20:25:59		69.8		24

		1-Nov-07		22:07:10		71.6		47.5		1-Nov-07		22:06:20		69.2		52		1-Nov-07		22:07:53		69.2		51		12-Dec-07		22:25:59		68.61		25.5

		2-Nov-07		0:07:10		71		48		2-Nov-07		0:06:20		68.61		52.5		2-Nov-07		0:07:53		68.61		51.5		13-Dec-07		0:25:59		66.2		26.5

		2-Nov-07		2:07:10		71		48		2-Nov-07		2:06:20		68.61		52.5		2-Nov-07		2:07:53		68		52.5		13-Dec-07		2:25:59		64.4		27

		2-Nov-07		4:07:10		70.41		47.5		2-Nov-07		4:06:20		68.61		52		2-Nov-07		4:07:53		67.4		52.5		13-Dec-07		4:25:59		63.21		27.5

		2-Nov-07		6:07:10		71		46		2-Nov-07		6:06:20		69.2		49		2-Nov-07		6:07:53		68		51.5		13-Dec-07		6:25:59		64.4		28

		2-Nov-07		8:07:10		72.21		46.5		2-Nov-07		8:06:20		68.61		54.5		2-Nov-07		8:07:53		69.8		48		13-Dec-07		8:25:59		68		27.5

		2-Nov-07		10:07:10		73.4		46		2-Nov-07		10:06:20		69.2		53		2-Nov-07		10:07:53		71.6		46.5		13-Dec-07		10:25:59		70.41		28.5

		2-Nov-07		12:07:10		74.01		47		2-Nov-07		12:06:20		69.8		56.5		2-Nov-07		12:07:53		71.6		47.5		13-Dec-07		12:25:59		71.6		29

		2-Nov-07		14:07:10		74.01		44		2-Nov-07		14:06:20		71		48.5		2-Nov-07		14:07:53		71		44		13-Dec-07		14:25:59		71.6		26

		2-Nov-07		16:07:10		74.01		52.5		2-Nov-07		16:06:20		69.2		58		2-Nov-07		16:07:53		71		56.5		13-Dec-07		16:25:59		71.6		25.5

		2-Nov-07		18:07:10		74.01		49.5		2-Nov-07		18:06:20		69.2		49.5		2-Nov-07		18:07:53		70.41		50		13-Dec-07		18:25:59		71.6		26

		2-Nov-07		20:07:10		73.4		46.5		2-Nov-07		20:06:20		69.2		51.5		2-Nov-07		20:07:53		70.41		51		13-Dec-07		20:25:59		71		27.5

		2-Nov-07		22:07:10		72.8		42		2-Nov-07		22:06:20		69.8		47.5		2-Nov-07		22:07:53		69.8		47		13-Dec-07		22:25:59		68		28.5

		3-Nov-07		0:07:10		71.6		42		3-Nov-07		0:06:20		69.2		46		3-Nov-07		0:07:53		68		46.5		14-Dec-07		0:25:59		66.2		29.5

		3-Nov-07		2:07:10		71		40.5		3-Nov-07		2:06:20		69.2		43.5		3-Nov-07		2:07:53		66.81		46.5		14-Dec-07		2:25:59		64.4		29.5

		3-Nov-07		4:07:10		70.41		40		3-Nov-07		4:06:20		68		42.5		3-Nov-07		4:07:53		66.81		45		14-Dec-07		4:25:59		63.8		30

		3-Nov-07		6:07:10		70.41		38		3-Nov-07		6:06:20		67.4		40.5		3-Nov-07		6:07:53		67.4		42.5		14-Dec-07		6:25:59		65.01		29

		3-Nov-07		8:07:10		72.8		36.5		3-Nov-07		8:06:20		69.2		42		3-Nov-07		8:07:53		68.61		39		14-Dec-07		8:25:59		66.81		27

		3-Nov-07		10:07:10		74.01		39.5		3-Nov-07		10:06:20		71.6		46		3-Nov-07		10:07:53		70.41		47		14-Dec-07		10:25:59		70.41		28.5

		3-Nov-07		12:07:10		74.6		40		3-Nov-07		12:06:20		71.6		46.5		3-Nov-07		12:07:53		71.6		45.5		14-Dec-07		12:25:59		72.21		28.5

		3-Nov-07		14:07:10		74.6		42		3-Nov-07		14:06:20		70.41		50		3-Nov-07		14:07:53		71		52		14-Dec-07		14:25:59		72.21		29.5

		3-Nov-07		16:07:10		74.01		42.5		3-Nov-07		16:06:20		69.8		50.5		3-Nov-07		16:07:53		71		49.5		14-Dec-07		16:25:59		72.21		30.5

		3-Nov-07		18:07:10		74.01		47.5		3-Nov-07		18:06:20		69.2		59.5		3-Nov-07		18:07:53		71		47		14-Dec-07		18:25:59		72.8		31.5

		3-Nov-07		20:07:10		74.6		42		3-Nov-07		20:06:20		71		47.5		3-Nov-07		20:07:53		70.41		48.5		14-Dec-07		20:25:59		71		31.5

		3-Nov-07		22:07:10		74.01		40.5		3-Nov-07		22:06:20		71		45		3-Nov-07		22:07:53		69.8		45.5		14-Dec-07		22:25:59		68.61		31

		4-Nov-07		0:07:10		72.8		38.5		4-Nov-07		0:06:20		69.8		42		4-Nov-07		0:07:53		68		44.5		15-Dec-07		0:25:59		66.2		31.5

		4-Nov-07		2:07:10		71.6		37.5		4-Nov-07		2:06:20		69.8		40		4-Nov-07		2:07:53		66.81		44		15-Dec-07		2:25:59		64.4		31.5

		4-Nov-07		4:07:10		71		36.5		4-Nov-07		4:06:20		69.2		39		4-Nov-07		4:07:53		65.01		43.5		15-Dec-07		4:25:59		63.21		31

		4-Nov-07		6:07:10		69.8		35.5		4-Nov-07		6:06:20		68.61		38		4-Nov-07		6:07:53		63.8		43.5		15-Dec-07		6:25:59		64.4		30

		4-Nov-07		8:07:10		69.2		35		4-Nov-07		8:06:20		67.4		38		4-Nov-07		8:07:53		66.81		39		15-Dec-07		8:25:59		66.81		28.5

		4-Nov-07		10:07:10		69.8		37.5		4-Nov-07		10:06:20		68.61		40.5		4-Nov-07		10:07:53		67.4		41		15-Dec-07		10:25:59		69.2		30

		4-Nov-07		12:07:10		70.41		40.5		4-Nov-07		12:06:20		68.61		43		4-Nov-07		12:07:53		68.61		43.5		15-Dec-07		12:25:59		72.21		31

		4-Nov-07		14:07:10		71		41		4-Nov-07		14:06:20		69.2		39.5		4-Nov-07		14:07:53		70.41		41		15-Dec-07		14:25:59		71.6		32

		4-Nov-07		16:07:10		72.21		42.5		4-Nov-07		16:06:20		69.2		41.5		4-Nov-07		16:07:53		70.41		46.5		15-Dec-07		16:25:59		72.21		31.5

		4-Nov-07		18:07:10		72.8		38.5		4-Nov-07		18:06:20		69.2		41		4-Nov-07		18:07:53		69.8		44		15-Dec-07		18:25:59		71.6		34

		4-Nov-07		20:07:10		72.8		36		4-Nov-07		20:06:20		70.41		39		4-Nov-07		20:07:53		70.41		40		15-Dec-07		20:25:59		71		34.5

		4-Nov-07		22:07:10		72.8		35.5		4-Nov-07		22:06:20		70.41		39		4-Nov-07		22:07:53		69.2		40		15-Dec-07		22:25:59		68.61		34

		5-Nov-07		0:07:10		72.21		36.5		5-Nov-07		0:06:20		70.41		40		5-Nov-07		0:07:53		67.4		42		16-Dec-07		0:25:59		67.4		35

		5-Nov-07		2:07:10		71.6		36		5-Nov-07		2:06:20		70.41		38.5		5-Nov-07		2:07:53		65.6		42		16-Dec-07		2:25:59		66.81		35

		5-Nov-07		4:07:10		70.41		35.5		5-Nov-07		4:06:20		69.2		37.5		5-Nov-07		4:07:53		64.4		42.5		16-Dec-07		4:25:59		66.2		35.5

		5-Nov-07		6:07:10		69.8		34.5		5-Nov-07		6:06:20		68.61		37		5-Nov-07		6:07:53		64.4		41.5		16-Dec-07		6:25:59		66.2		35.5

		5-Nov-07		8:07:10		69.2		34		5-Nov-07		8:06:20		67.4		37		5-Nov-07		8:07:53		66.81		37.5		16-Dec-07		8:25:59		65.6		35.5

		5-Nov-07		10:07:10		69.2		37		5-Nov-07		10:06:20		68		40		5-Nov-07		10:07:53		67.4		40.5		16-Dec-07		10:25:59		65.6		36

		5-Nov-07		12:07:10		69.8		39		5-Nov-07		12:06:20		68.61		39		5-Nov-07		12:07:53		68		42		16-Dec-07		12:25:59		66.2		37.5

		5-Nov-07		14:07:10		71		40.5		5-Nov-07		14:06:20		68.61		43		5-Nov-07		14:07:53		69.8		42.5		16-Dec-07		14:25:59		66.2		38.5

		5-Nov-07		16:07:10		71.6		41.5		5-Nov-07		16:06:20		69.2		40.5		5-Nov-07		16:07:53		69.8		45		16-Dec-07		16:25:59		66.2		40

		5-Nov-07		18:07:10		72.21		40.5		5-Nov-07		18:06:20		68.61		45		5-Nov-07		18:07:53		70.41		43.5		16-Dec-07		18:25:59		65.6		41.5

		5-Nov-07		20:07:10		72.8		40		5-Nov-07		20:06:20		71		43		5-Nov-07		20:07:53		70.41		44.5		16-Dec-07		20:25:59		65.01		42

		5-Nov-07		22:07:10		72.21		40.5		5-Nov-07		22:06:20		70.41		44.5		5-Nov-07		22:07:53		69.2		44.5		16-Dec-07		22:25:59		65.01		42

		6-Nov-07		0:07:10		71.6		39		6-Nov-07		0:06:20		70.41		41.5		6-Nov-07		0:07:53		67.4		44		17-Dec-07		0:25:59		64.4		42.5

		6-Nov-07		2:07:10		71		38		6-Nov-07		2:06:20		69.8		40		6-Nov-07		2:07:53		66.2		44		17-Dec-07		2:25:59		63.8		43.5

		6-Nov-07		4:07:10		69.8		36		6-Nov-07		4:06:20		68.61		38		6-Nov-07		4:07:53		65.01		42.5		17-Dec-07		4:25:59		63.8		43.5

		6-Nov-07		6:07:10		69.2		35		6-Nov-07		6:06:20		67.4		37		6-Nov-07		6:07:53		67.4		38		17-Dec-07		6:25:59		63.21		43

		6-Nov-07		8:07:10		71.6		33.5		6-Nov-07		8:06:20		68		36		6-Nov-07		8:07:53		68		37		17-Dec-07		8:25:59		64.4		44

		6-Nov-07		10:07:10		72.8		35.5		6-Nov-07		10:06:20		70.41		42.5		6-Nov-07		10:07:53		70.41		35.5		17-Dec-07		10:25:59		65.6		43.5

		6-Nov-07		12:07:10		74.01		38.5		6-Nov-07		12:06:20		70.41		47.5		6-Nov-07		12:07:53		70.41		46.5		17-Dec-07		12:25:59		66.2		43.5

		6-Nov-07		14:07:10		74.01		37		6-Nov-07		14:06:20		71		39		6-Nov-07		14:07:53		70.41		49.5		17-Dec-07		14:25:59		66.2		42

		6-Nov-07		16:07:10		74.6		44		6-Nov-07		16:06:20		70.41		48.5		6-Nov-07		16:07:53		71		49		17-Dec-07		16:25:59		66.81		41.5

		6-Nov-07		18:07:10		74.6		41.5		6-Nov-07		18:06:20		69.2		43		6-Nov-07		18:07:53		70.41		46.5		17-Dec-07		18:25:59		66.81		41.5

		6-Nov-07		20:07:10		73.4		39.5		6-Nov-07		20:06:20		70.41		44.5		6-Nov-07		20:07:53		69.8		44.5		17-Dec-07		20:25:59		65.6		41.5

		6-Nov-07		22:07:10		72.8		40		6-Nov-07		22:06:20		70.41		44		6-Nov-07		22:07:53		68		46		17-Dec-07		22:25:59		65.01		43.5

		7-Nov-07		0:07:10		72.21		40.5		7-Nov-07		0:06:20		70.41		44.5		7-Nov-07		0:07:53		67.4		47		18-Dec-07		0:25:59		64.4		44.5

		7-Nov-07		2:07:10		71.6		41		7-Nov-07		2:06:20		70.41		44		7-Nov-07		2:07:53		66.2		48		18-Dec-07		2:25:59		63.8		45

		7-Nov-07		4:07:10		71		41		7-Nov-07		4:06:20		69.8		43.5		7-Nov-07		4:07:53		65.6		48.5		18-Dec-07		4:25:59		63.8		44

		7-Nov-07		6:07:10		70.41		41.5		7-Nov-07		6:06:20		69.8		43.5		7-Nov-07		6:07:53		67.4		45		18-Dec-07		6:25:59		65.6		46

		7-Nov-07		8:07:10		71.6		41.5		7-Nov-07		8:06:20		68.61		45		7-Nov-07		8:07:53		70.41		43.5		18-Dec-07		8:25:59		68		45

		7-Nov-07		10:07:10		72.8		41		7-Nov-07		10:06:20		70.41		47.5		7-Nov-07		10:07:53		71		44		18-Dec-07		10:25:59		71		45

		7-Nov-07		12:07:10		72.8		40		7-Nov-07		12:06:20		71		38.5		7-Nov-07		12:07:53		70.41		45.5		18-Dec-07		12:25:59		71.6		44

		7-Nov-07		14:07:10		73.4		42.5		7-Nov-07		14:06:20		71		50.5		7-Nov-07		14:07:53		70.41		45.5		18-Dec-07		14:25:59		71.6		45.5

		7-Nov-07		16:07:10		74.01		46		7-Nov-07		16:06:20		70.41		46		7-Nov-07		16:07:53		71		53		18-Dec-07		16:25:59		71.6		45

		7-Nov-07		18:07:10		74.01		43.5		7-Nov-07		18:06:20		69.2		51.5		7-Nov-07		18:07:53		69.8		50		18-Dec-07		18:25:59		72.21		44

		7-Nov-07		20:07:10		72.8		40.5		7-Nov-07		20:06:20		70.41		44		7-Nov-07		20:07:53		69.2		45.5		18-Dec-07		20:25:59		70.41		43

		7-Nov-07		22:07:10		72.21		39		7-Nov-07		22:06:20		70.41		41		7-Nov-07		22:07:53		68		44		18-Dec-07		22:25:59		68.61		44

		8-Nov-07		0:07:10		71.6		40		8-Nov-07		0:06:20		70.41		42.5		8-Nov-07		0:07:53		66.81		46.5		19-Dec-07		0:25:59		67.4		45

		8-Nov-07		2:07:10		71		40.5		8-Nov-07		2:06:20		70.41		42		8-Nov-07		2:07:53		65.6		47.5		19-Dec-07		2:25:59		66.2		46

		8-Nov-07		4:07:10		70.41		39.5		8-Nov-07		4:06:20		69.8		40.5		8-Nov-07		4:07:53		65.01		47		19-Dec-07		4:25:59		65.01		46.5

		8-Nov-07		6:07:10		69.8		39.5		8-Nov-07		6:06:20		69.8		40		8-Nov-07		6:07:53		67.4		43		19-Dec-07		6:25:59		65.6		49

		8-Nov-07		8:07:10		71.6		38.5		8-Nov-07		8:06:20		68.61		42.5		8-Nov-07		8:07:53		69.2		41.5		19-Dec-07		8:25:59		69.2		46.5

		8-Nov-07		10:07:10		71		40		8-Nov-07		10:06:20		67.4		47		8-Nov-07		10:07:53		71		41		19-Dec-07		10:25:59		71.6		47

		8-Nov-07		12:07:10		72.21		43		8-Nov-07		12:06:20		70.41		46.5		8-Nov-07		12:07:53		70.41		47		19-Dec-07		12:25:59		72.21		46.5

		8-Nov-07		14:07:10		71.6		41		8-Nov-07		14:06:20		68		43		8-Nov-07		14:07:53		71.6		45.5		19-Dec-07		14:25:59		72.21		49.5

		8-Nov-07		16:07:10		74.01		43.5		8-Nov-07		16:06:20		71.6		43		8-Nov-07		16:07:53		70.41		53		19-Dec-07		16:25:59		72.8		46.5

		8-Nov-07		18:07:10		73.4		43		8-Nov-07		18:06:20		71		47.5		8-Nov-07		18:07:53		69.8		48		19-Dec-07		18:25:59		72.21		44.5

		8-Nov-07		20:07:10		71.6		43		8-Nov-07		20:06:20		69.2		46.5		8-Nov-07		20:07:53		69.8		47		19-Dec-07		20:25:59		71.6		42

		8-Nov-07		22:07:10		71.6		44		8-Nov-07		22:06:20		68.61		48		8-Nov-07		22:07:53		68.61		48		19-Dec-07		22:25:59		69.2		43

		9-Nov-07		0:07:10		71		43		9-Nov-07		0:06:20		68.61		46.5		9-Nov-07		0:07:53		68		47		20-Dec-07		0:25:59		68		42.5

		9-Nov-07		2:07:10		70.41		44		9-Nov-07		2:06:20		68.61		47.5		9-Nov-07		2:07:53		67.4		48.5		20-Dec-07		2:25:59		67.4		42.5

		9-Nov-07		4:07:10		70.41		44.5		9-Nov-07		4:06:20		68.61		47.5		9-Nov-07		4:07:53		66.81		49.5		20-Dec-07		4:25:59		66.81		42.5

		9-Nov-07		6:07:10		69.8		44		9-Nov-07		6:06:20		68.61		46.5		9-Nov-07		6:07:53		68		47		20-Dec-07		6:25:59		67.4		42.5

		9-Nov-07		8:07:10		71.6		43		9-Nov-07		8:06:20		69.8		46		9-Nov-07		8:07:53		70.41		47		20-Dec-07		8:25:59		69.8		41.5

		9-Nov-07		10:07:10		71.6		44.5		9-Nov-07		10:06:20		71		48		9-Nov-07		10:07:53		71.6		47.5		20-Dec-07		10:25:59		71.6		41.5

		9-Nov-07		12:07:10		72.21		45		9-Nov-07		12:06:20		71		49		9-Nov-07		12:07:53		70.41		48		20-Dec-07		12:25:59		72.8		41

		9-Nov-07		14:07:10		74.01		42.5		9-Nov-07		14:06:20		71.6		44.5		9-Nov-07		14:07:53		71		49.5		20-Dec-07		14:25:59		72.8		42.5

		9-Nov-07		16:07:10		74.01		44		9-Nov-07		16:06:20		71.6		49		9-Nov-07		16:07:53		69.8		49.5		20-Dec-07		16:25:59		72.8		43.5

		9-Nov-07		18:07:10		72.8		42.5		9-Nov-07		18:06:20		70.41		46.5		9-Nov-07		18:07:53		69.8		50		20-Dec-07		18:25:59		72.8		43

		9-Nov-07		20:07:10		72.8		42.5		9-Nov-07		20:06:20		69.8		46		9-Nov-07		20:07:53		69.2		47		20-Dec-07		20:25:59		71.6		43

		9-Nov-07		22:07:10		71.6		43.5		9-Nov-07		22:06:20		69.2		47		9-Nov-07		22:07:53		69.2		47.5		20-Dec-07		22:25:59		70.41		45

		10-Nov-07		0:07:10		71		44.5		10-Nov-07		0:06:20		69.2		48.5		10-Nov-07		0:07:53		68.61		48.5		21-Dec-07		0:25:59		69.2		45.5

		10-Nov-07		2:07:10		71		45		10-Nov-07		2:06:20		68.61		49.5		10-Nov-07		2:07:53		68		49.5		21-Dec-07		2:25:59		68.61		46.5

		10-Nov-07		4:07:10		70.41		45		10-Nov-07		4:06:20		68.61		48		10-Nov-07		4:07:53		67.4		49.5		21-Dec-07		4:25:59		68.61		46.5

		10-Nov-07		6:07:10		69.8		42		10-Nov-07		6:06:20		68.61		45		10-Nov-07		6:07:53		66.81		47		21-Dec-07		6:25:59		68.61		46

		10-Nov-07		8:07:10		72.21		40		10-Nov-07		8:06:20		68.61		44		10-Nov-07		8:07:53		69.8		44		21-Dec-07		8:25:59		70.41		41

		10-Nov-07		10:07:10		74.01		39.5		10-Nov-07		10:06:20		71		42		10-Nov-07		10:07:53		70.41		47		21-Dec-07		10:25:59		72.8		40.5

		10-Nov-07		12:07:10		73.4		41		10-Nov-07		12:06:20		71		48.5		10-Nov-07		12:07:53		70.41		47		21-Dec-07		12:25:59		72.21		38.5

		10-Nov-07		14:07:10		73.4		40		10-Nov-07		14:06:20		71.6		41		10-Nov-07		14:07:53		71		51		21-Dec-07		14:25:59		72.8		37

		10-Nov-07		16:07:10		74.01		44		10-Nov-07		16:06:20		71		50		10-Nov-07		16:07:53		70.41		41.5		21-Dec-07		16:25:59		72.21		35.5

		10-Nov-07		18:07:10		73.4		44.5		10-Nov-07		18:06:20		69.8		51		10-Nov-07		18:07:53		70.41		52.5		21-Dec-07		18:25:59		71.6		34.5

		10-Nov-07		20:07:10		72.8		44		10-Nov-07		20:06:20		69.2		48.5		10-Nov-07		20:07:53		69.8		48.5		21-Dec-07		20:25:59		69.8		34.5

		10-Nov-07		22:07:10		71.6		42.5		10-Nov-07		22:06:20		68.61		46.5		10-Nov-07		22:07:53		69.2		46.5		21-Dec-07		22:25:59		68.61		35

		11-Nov-07		0:07:10		71		41		11-Nov-07		0:06:20		68.61		44.5		11-Nov-07		0:07:53		68		45		22-Dec-07		0:25:59		68		35

		11-Nov-07		2:07:10		70.41		40		11-Nov-07		2:06:20		68		43		11-Nov-07		2:07:53		66.2		45		22-Dec-07		2:25:59		67.4		34.5

		11-Nov-07		4:07:10		69.8		40		11-Nov-07		4:06:20		68		44		11-Nov-07		4:07:53		65.6		46.5		22-Dec-07		4:25:59		66.2		34

		11-Nov-07		6:07:10		69.8		41		11-Nov-07		6:06:20		68		45.5		11-Nov-07		6:07:53		65.01		48		22-Dec-07		6:25:59		66.81		33

		11-Nov-07		8:07:10		69.8		43		11-Nov-07		8:06:20		68		47.5		11-Nov-07		8:07:53		67.4		47		22-Dec-07		8:25:59		69.2		30.5

		11-Nov-07		10:07:10		69.8		46		11-Nov-07		10:06:20		68		51		11-Nov-07		10:07:53		68		48.5		22-Dec-07		10:25:59		70.41		31

		11-Nov-07		12:07:10		69.8		50		11-Nov-07		12:06:20		68		55		11-Nov-07		12:07:53		67.4		53.5		22-Dec-07		12:25:59		71		30

		11-Nov-07		14:07:10		70.41		52.5		11-Nov-07		14:06:20		68.61		57.5		11-Nov-07		14:07:53		68		54.5		22-Dec-07		14:25:59		70.41		30

		11-Nov-07		16:07:10		70.41		53.5		11-Nov-07		16:06:20		68.61		58.5		11-Nov-07		16:07:53		68		55.5		22-Dec-07		16:25:59		71.6		29.5

		11-Nov-07		18:07:10		70.41		54.5		11-Nov-07		18:06:20		68.61		59		11-Nov-07		18:07:53		68.61		56.5		22-Dec-07		18:25:59		70.41		30

		11-Nov-07		20:07:10		70.41		54.5		11-Nov-07		20:06:20		68.61		59		11-Nov-07		20:07:53		68.61		56		22-Dec-07		20:25:59		69.2		30.5

		11-Nov-07		22:07:10		70.41		55		11-Nov-07		22:06:20		68.61		59.5		11-Nov-07		22:07:53		68		56.5		22-Dec-07		22:25:59		66.81		31.5

		12-Nov-07		0:07:10		70.41		55		12-Nov-07		0:06:20		68.61		59		12-Nov-07		0:07:53		68		57		23-Dec-07		0:25:59		64.4		32

		12-Nov-07		2:07:10		70.41		55		12-Nov-07		2:06:20		68.61		59		12-Nov-07		2:07:53		68		57.5		23-Dec-07		2:25:59		63.21		32.5

		12-Nov-07		4:07:10		69.8		50.5		12-Nov-07		4:06:20		68.61		52		12-Nov-07		4:07:53		67.4		55.5		23-Dec-07		4:25:59		62.6		31.5

		12-Nov-07		6:07:10		69.8		45.5		12-Nov-07		6:06:20		68.61		46		12-Nov-07		6:07:53		66.2		51.5		23-Dec-07		6:25:59		62		31

		12-Nov-07		8:07:10		69.2		43.5		12-Nov-07		8:06:20		68		45.5		12-Nov-07		8:07:53		67.4		47		23-Dec-07		8:25:59		62.6		31

		12-Nov-07		10:07:10		69.2		44		12-Nov-07		10:06:20		68.61		46		12-Nov-07		10:07:53		68		47		23-Dec-07		10:25:59		62.6		32

		12-Nov-07		12:07:10		70.41		43		12-Nov-07		12:06:20		69.2		43.5		12-Nov-07		12:07:53		68		46.5		23-Dec-07		12:25:59		62.6		33.5

		12-Nov-07		14:07:10		71		39.5		12-Nov-07		14:06:20		69.2		39		12-Nov-07		14:07:53		69.2		43		23-Dec-07		14:25:59		65.01		35

		12-Nov-07		16:07:10		71		38.5		12-Nov-07		16:06:20		69.2		38.5		12-Nov-07		16:07:53		69.8		42.5		23-Dec-07		16:25:59		65.01		34

		12-Nov-07		18:07:10		71.6		39		12-Nov-07		18:06:20		69.8		38.5		12-Nov-07		18:07:53		69.8		42.5		23-Dec-07		18:25:59		64.4		34

		12-Nov-07		20:07:10		71		39.5		12-Nov-07		20:06:20		68.61		42		12-Nov-07		20:07:53		69.2		43		23-Dec-07		20:25:59		63.21		35.5

		12-Nov-07		22:07:10		70.41		39		12-Nov-07		22:06:20		68.61		41.5		12-Nov-07		22:07:53		67.4		43		23-Dec-07		22:25:59		62.6		35.5

		13-Nov-07		0:07:10		69.8		38.5		13-Nov-07		0:06:20		68		41		13-Nov-07		0:07:53		65.6		43.5		24-Dec-07		0:25:59		62.6		36

		13-Nov-07		2:07:10		69.2		38		13-Nov-07		2:06:20		68		40.5		13-Nov-07		2:07:53		64.4		44.5		24-Dec-07		2:25:59		62		36

		13-Nov-07		4:07:10		69.2		38		13-Nov-07		4:06:20		68		40.5		13-Nov-07		4:07:53		63.8		45		24-Dec-07		4:25:59		62		36

		13-Nov-07		6:07:10		68.61		39		13-Nov-07		6:06:20		68		41.5		13-Nov-07		6:07:53		66.81		43		24-Dec-07		6:25:59		62		36

		13-Nov-07		8:07:10		71.6		38		13-Nov-07		8:06:20		69.2		41		13-Nov-07		8:07:53		69.2		41.5		24-Dec-07		8:25:59		62		36

		13-Nov-07		10:07:10		72.8		38		13-Nov-07		10:06:20		70.41		42.5		13-Nov-07		10:07:53		71		41		24-Dec-07		10:25:59		62		36.5

		13-Nov-07		12:07:10		75.2		37.5		13-Nov-07		12:06:20		71		40		13-Nov-07		12:07:53		70.41		42.5		24-Dec-07		12:25:59		62		38

		13-Nov-07		14:07:10		74.6		35		13-Nov-07		14:06:20		71.6		38.5		13-Nov-07		14:07:53		71.6		42		24-Dec-07		14:25:59		63.21		41.5

		13-Nov-07		16:07:10		74.01		34.5		13-Nov-07		16:06:20		71.6		37.5		13-Nov-07		16:07:53		70.41		41		24-Dec-07		16:25:59		64.4		42.5

		13-Nov-07		18:07:10		74.01		32		13-Nov-07		18:06:20		69.8		31.5		13-Nov-07		18:07:53		70.41		38		24-Dec-07		18:25:59		65.6		43

		13-Nov-07		20:07:10		73.4		37		13-Nov-07		20:06:20		69.8		42		13-Nov-07		20:07:53		70.41		42		24-Dec-07		20:25:59		65.01		45.5

		13-Nov-07		22:07:10		72.8		40		13-Nov-07		22:06:20		69.8		45		13-Nov-07		22:07:53		69.8		44		24-Dec-07		22:25:59		64.4		44.5

		14-Nov-07		0:07:10		72.21		42		14-Nov-07		0:06:20		69.2		47.5		14-Nov-07		0:07:53		69.8		45		25-Dec-07		0:25:59		63.8		45

		14-Nov-07		2:07:10		72.21		43		14-Nov-07		2:06:20		69.8		48		14-Nov-07		2:07:53		69.2		47.5		25-Dec-07		2:25:59		63.8		45

		14-Nov-07		4:07:10		71.6		44.5		14-Nov-07		4:06:20		69.2		50		14-Nov-07		4:07:53		68.61		48.5		25-Dec-07		4:25:59		63.21		44.5

		14-Nov-07		6:07:10		71		46		14-Nov-07		6:06:20		69.2		51.5		14-Nov-07		6:07:53		68.61		50		25-Dec-07		6:25:59		64.4		44

		14-Nov-07		8:07:10		73.4		45		14-Nov-07		8:06:20		69.8		51.5		14-Nov-07		8:07:53		70.41		44		25-Dec-07		8:25:59		66.81		40.5

		14-Nov-07		10:07:10		74.01		46		14-Nov-07		10:06:20		71.6		54.5		14-Nov-07		10:07:53		70.41		53		25-Dec-07		10:25:59		69.2		36.5

		14-Nov-07		12:07:10		74.01		47.5		14-Nov-07		12:06:20		72.21		54		14-Nov-07		12:07:53		70.41		47		25-Dec-07		12:25:59		70.41		34.5

		14-Nov-07		14:07:10		74.01		48		14-Nov-07		14:06:20		72.21		45		14-Nov-07		14:07:53		70.41		47		25-Dec-07		14:25:59		71		33

		14-Nov-07		16:07:10		74.6		49.5		14-Nov-07		16:06:20		71.6		44.5		14-Nov-07		16:07:53		71		59.5		25-Dec-07		16:25:59		70.41		33.5

		14-Nov-07		18:07:10		74.6		49.5		14-Nov-07		18:06:20		71		49		14-Nov-07		18:07:53		71		53.5		25-Dec-07		18:25:59		68.61		33.5

		14-Nov-07		20:07:10		74.01		49		14-Nov-07		20:06:20		70.41		52.5		14-Nov-07		20:07:53		70.41		57.5		25-Dec-07		20:25:59		66.81		35

		14-Nov-07		22:07:10		73.4		52		14-Nov-07		22:06:20		69.8		61		14-Nov-07		22:07:53		71		55.5		25-Dec-07		22:25:59		64.4		35.5

		15-Nov-07		0:07:10		72.8		52		15-Nov-07		0:06:20		69.8		57		15-Nov-07		0:07:53		71		54		26-Dec-07		0:25:59		63.21		35

		15-Nov-07		2:07:10		72.21		50.5		15-Nov-07		2:06:20		69.8		56		15-Nov-07		2:07:53		70.41		53.5		26-Dec-07		2:25:59		62.6		34

		15-Nov-07		4:07:10		71.6		47		15-Nov-07		4:06:20		68.61		50.5		15-Nov-07		4:07:53		69.8		50.5		26-Dec-07		4:25:59		62		33.5

		15-Nov-07		6:07:10		71		45.5		15-Nov-07		6:06:20		68.61		49		15-Nov-07		6:07:53		68.61		49.5		26-Dec-07		6:25:59		62		33

		15-Nov-07		8:07:10		72.21		43.5		15-Nov-07		8:06:20		69.2		47		15-Nov-07		8:07:53		70.41		47.5		26-Dec-07		8:25:59		62.6		32.5

		15-Nov-07		10:07:10		74.01		44.5		15-Nov-07		10:06:20		71.6		56		15-Nov-07		10:07:53		71		46.5		26-Dec-07		10:25:59		62		32.5

		15-Nov-07		12:07:10		74.01		46.5		15-Nov-07		12:06:20		71.6		54		15-Nov-07		12:07:53		71.6		50.5		26-Dec-07		12:25:59		62		33.5

		15-Nov-07		14:07:10		74.01		47.5		15-Nov-07		14:06:20		71.6		56		15-Nov-07		14:07:53		71		52		26-Dec-07		14:25:59		62.6		34.5

		15-Nov-07		16:07:10		74.6		50		15-Nov-07		16:06:20		71.6		45.5		15-Nov-07		16:07:53		70.41		56		26-Dec-07		16:25:59		63.8		35.5

		15-Nov-07		18:07:10		74.01		51		15-Nov-07		18:06:20		70.41		51		15-Nov-07		18:07:53		70.41		56		26-Dec-07		18:25:59		63.8		37

		15-Nov-07		20:07:10		73.4		50		15-Nov-07		20:06:20		69.8		56.5		15-Nov-07		20:07:53		71		55.5		26-Dec-07		20:25:59		63.21		38

		15-Nov-07		22:07:10		73.4		48.5		15-Nov-07		22:06:20		69.8		54.5		15-Nov-07		22:07:53		71.6		51.5		26-Dec-07		22:25:59		62.6		37.5

		16-Nov-07		0:07:10		72.8		46.5		16-Nov-07		0:06:20		69.8		51		16-Nov-07		0:07:53		71		50		27-Dec-07		0:25:59		62		38.5

		16-Nov-07		2:07:10		71.6		45.5		16-Nov-07		2:06:20		68.61		49.5		16-Nov-07		2:07:53		69.2		49		27-Dec-07		2:25:59		62		39

		16-Nov-07		4:07:10		71		45.5		16-Nov-07		4:06:20		68.61		49.5		16-Nov-07		4:07:53		68.61		49.5		27-Dec-07		4:25:59		62		38

		16-Nov-07		6:07:10		70.41		44		16-Nov-07		6:06:20		68.61		47.5		16-Nov-07		6:07:53		67.4		49		27-Dec-07		6:25:59		62		37.5

		16-Nov-07		8:07:10		71.6		42.5		16-Nov-07		8:06:20		68.61		46		16-Nov-07		8:07:53		70.41		46		27-Dec-07		8:25:59		63.21		36.5

		16-Nov-07		10:07:10		72.8		44.5		16-Nov-07		10:06:20		71		49.5		16-Nov-07		10:07:53		72.21		47		27-Dec-07		10:25:59		67.4		35

		16-Nov-07		12:07:10		73.4		45		16-Nov-07		12:06:20		71.6		50.5		16-Nov-07		12:07:53		71		47		27-Dec-07		12:25:59		72.21		30.5

		16-Nov-07		14:07:10		74.01		46.5		16-Nov-07		14:06:20		71.6		53.5		16-Nov-07		14:07:53		71.6		51.5		27-Dec-07		14:25:59		71		28

		16-Nov-07		16:07:10		74.01		50		16-Nov-07		16:06:20		71.6		52		16-Nov-07		16:07:53		71		60.5		27-Dec-07		16:25:59		71		26

		16-Nov-07		18:07:10		74.01		49.5		16-Nov-07		18:06:20		70.41		62		16-Nov-07		18:07:53		70.41		53.5		27-Dec-07		18:25:59		70.41		26

		16-Nov-07		20:07:10		73.4		51		16-Nov-07		20:06:20		69.8		57.5		16-Nov-07		20:07:53		70.41		57		27-Dec-07		20:25:59		69.2		26.5

		16-Nov-07		22:07:10		72.8		51		16-Nov-07		22:06:20		69.8		56.5		16-Nov-07		22:07:53		70.41		55.5		27-Dec-07		22:25:59		66.2		31.5

		17-Nov-07		0:07:10		72.21		50.5		17-Nov-07		0:06:20		69.8		56		17-Nov-07		0:07:53		70.41		54		28-Dec-07		0:25:59		63.8		29.5

		17-Nov-07		2:07:10		71.6		50.5		17-Nov-07		2:06:20		69.2		56		17-Nov-07		2:07:53		69.8		53.5		28-Dec-07		2:25:59		62.6		29.5

		17-Nov-07		4:07:10		71.6		50.5		17-Nov-07		4:06:20		69.2		55.5		17-Nov-07		4:07:53		69.2		54		28-Dec-07		4:25:59		62.6		29.5

		17-Nov-07		6:07:10		71		49.5		17-Nov-07		6:06:20		68		54		17-Nov-07		6:07:53		68.61		53.5		28-Dec-07		6:25:59		62.6		29

		17-Nov-07		8:07:10		71.6		49.5		17-Nov-07		8:06:20		68		55		17-Nov-07		8:07:53		71		53		28-Dec-07		8:25:59		65.01		28.5

		17-Nov-07		10:07:10		72.21		47.5		17-Nov-07		10:06:20		71		51.5		17-Nov-07		10:07:53		71		49.5		28-Dec-07		10:25:59		68.61		28

		17-Nov-07		12:07:10		73.4		47.5		17-Nov-07		12:06:20		72.21		55		17-Nov-07		12:07:53		71.6		55.5		28-Dec-07		12:25:59		71.6		27

		17-Nov-07		14:07:10		74.01		49.5		17-Nov-07		14:06:20		71		46		17-Nov-07		14:07:53		71		57.5		28-Dec-07		14:25:59		71		28.5

		17-Nov-07		16:07:10		74.6		50		17-Nov-07		16:06:20		71.6		48		17-Nov-07		16:07:53		70.41		58		28-Dec-07		16:25:59		71		28.5

		17-Nov-07		18:07:10		74.6		48.5		17-Nov-07		18:06:20		69.8		55		17-Nov-07		18:07:53		70.41		50		28-Dec-07		18:25:59		72.21		29.5

		17-Nov-07		20:07:10		72.8		47.5		17-Nov-07		20:06:20		69.8		52		17-Nov-07		20:07:53		69.8		52		28-Dec-07		20:25:59		71		32

		17-Nov-07		22:07:10		71.6		48		17-Nov-07		22:06:20		69.2		53.5		17-Nov-07		22:07:53		69.2		51.5		28-Dec-07		22:25:59		68		34.5

		18-Nov-07		0:07:10		71.6		49.5		18-Nov-07		0:06:20		68.61		54		18-Nov-07		0:07:53		69.2		53		29-Dec-07		0:25:59		65.6		35

		18-Nov-07		2:07:10		71		49		18-Nov-07		2:06:20		68		54.5		18-Nov-07		2:07:53		68		53		29-Dec-07		2:25:59		64.4		36

		18-Nov-07		4:07:10		70.41		50		18-Nov-07		4:06:20		68		55		18-Nov-07		4:07:53		67.4		53.5		29-Dec-07		4:25:59		63.21		37

		18-Nov-07		6:07:10		69.8		49.5		18-Nov-07		6:06:20		67.4		54.5		18-Nov-07		6:07:53		66.81		54		29-Dec-07		6:25:59		64.4		37.5

		18-Nov-07		8:07:10		69.8		49.5		18-Nov-07		8:06:20		67.4		54.5		18-Nov-07		8:07:53		67.4		53		29-Dec-07		8:25:59		66.81		36.5

		18-Nov-07		10:07:10		69.2		49.5		18-Nov-07		10:06:20		67.4		54.5		18-Nov-07		10:07:53		67.4		53		29-Dec-07		10:25:59		69.8		36

		18-Nov-07		12:07:10		69.8		51.5		18-Nov-07		12:06:20		67.4		56.5		18-Nov-07		12:07:53		67.4		55.5		29-Dec-07		12:25:59		72.8		34

		18-Nov-07		14:07:10		70.41		52		18-Nov-07		14:06:20		68.61		55.5		18-Nov-07		14:07:53		68		55.5		29-Dec-07		14:25:59		72.8		34

		18-Nov-07		16:07:10		71		53.5		18-Nov-07		16:06:20		69.2		53.5		18-Nov-07		16:07:53		69.8		58		29-Dec-07		16:25:59		73.4		33

		18-Nov-07		18:07:10		71.6		55		18-Nov-07		18:06:20		69.2		56		18-Nov-07		18:07:53		69.8		58.5		29-Dec-07		18:25:59		72.21		33.5

		18-Nov-07		20:07:10		71		52		18-Nov-07		20:06:20		69.2		55.5		18-Nov-07		20:07:53		69.8		54.5		29-Dec-07		20:25:59		71		34

		18-Nov-07		22:07:10		70.41		52		18-Nov-07		22:06:20		68.61		56		18-Nov-07		22:07:53		68.61		55		29-Dec-07		22:25:59		67.4		36

		19-Nov-07		0:07:10		70.41		52		19-Nov-07		0:06:20		68		56		19-Nov-07		0:07:53		68.61		54.5		30-Dec-07		0:25:59		65.01		37.5

		19-Nov-07		2:07:10		69.8		51		19-Nov-07		2:06:20		67.4		56		19-Nov-07		2:07:53		68		55		30-Dec-07		2:25:59		63.8		38

		19-Nov-07		4:07:10		69.8		51		19-Nov-07		4:06:20		67.4		56.5		19-Nov-07		4:07:53		67.4		55.5		30-Dec-07		4:25:59		63.21		39

		19-Nov-07		6:07:10		69.8		51		19-Nov-07		6:06:20		67.4		55.5		19-Nov-07		6:07:53		66.81		56		30-Dec-07		6:25:59		62.6		39.5

		19-Nov-07		8:07:10		69.2		51		19-Nov-07		8:06:20		67.4		55.5		19-Nov-07		8:07:53		67.4		54		30-Dec-07		8:25:59		62.6		40.5

		19-Nov-07		10:07:10		69.2		52		19-Nov-07		10:06:20		67.4		56.5		19-Nov-07		10:07:53		67.4		55.5		30-Dec-07		10:25:59		63.21		42.5

		19-Nov-07		12:07:10		69.8		54.5		19-Nov-07		12:06:20		68		60		19-Nov-07		12:07:53		67.4		58		30-Dec-07		12:25:59		63.21		43.5

		19-Nov-07		14:07:10		70.41		56.5		19-Nov-07		14:06:20		68.61		60		19-Nov-07		14:07:53		68.61		59.5		30-Dec-07		14:25:59		63.8		44.5

		19-Nov-07		16:07:10		71		59		19-Nov-07		16:06:20		69.2		65		19-Nov-07		16:07:53		69.2		61.5		30-Dec-07		16:25:59		63.21		45

		19-Nov-07		18:07:10		71		55		19-Nov-07		18:06:20		69.8		54		19-Nov-07		18:07:53		69.8		59		30-Dec-07		18:25:59		63.21		46

		19-Nov-07		20:07:10		71.6		53		19-Nov-07		20:06:20		69.8		55		19-Nov-07		20:07:53		69.8		56		30-Dec-07		20:25:59		62.6		46.5

		19-Nov-07		22:07:10		71		52		19-Nov-07		22:06:20		69.2		54.5		19-Nov-07		22:07:53		69.2		54.5		30-Dec-07		22:25:59		62.6		47

		20-Nov-07		0:07:10		70.41		50		20-Nov-07		0:06:20		68		53.5		20-Nov-07		0:07:53		68.61		53		31-Dec-07		0:25:59		62.6		47.5

		20-Nov-07		2:07:10		69.8		48.5		20-Nov-07		2:06:20		68		52.5		20-Nov-07		2:07:53		67.4		52.5		31-Dec-07		2:25:59		62.6		48

		20-Nov-07		4:07:10		69.2		50		20-Nov-07		4:06:20		67.4		54.5		20-Nov-07		4:07:53		66.81		54		31-Dec-07		4:25:59		62.6		48.5

		20-Nov-07		6:07:10		69.2		52.5		20-Nov-07		6:06:20		67.4		58		20-Nov-07		6:07:53		67.4		54.5		31-Dec-07		6:25:59		62		48

		20-Nov-07		8:07:10		71		54.5		20-Nov-07		8:06:20		68.61		60		20-Nov-07		8:07:53		69.8		56.5		31-Dec-07		8:25:59		63.21		46

		20-Nov-07		10:07:10		72.8		56		20-Nov-07		10:06:20		70.41		58		20-Nov-07		10:07:53		71		50		31-Dec-07		10:25:59		63.8		44

		20-Nov-07		12:07:10		74.6		50.5		20-Nov-07		12:06:20		71		58.5		20-Nov-07		12:07:53		71.6		58		31-Dec-07		12:25:59		65.01		42.5

		20-Nov-07		14:07:10		74.6		45.5		20-Nov-07		14:06:20		71.6		52		20-Nov-07		14:07:53		71		52		31-Dec-07		14:25:59		65.6		41.5

		20-Nov-07		16:07:10		74.01		41		20-Nov-07		16:06:20		72.21		44		20-Nov-07		16:07:53		70.41		51.5		31-Dec-07		16:25:59		65.6		40.5

		20-Nov-07		18:07:10		73.4		40.5		20-Nov-07		18:06:20		69.8		42.5		20-Nov-07		18:07:53		70.41		48		31-Dec-07		18:25:59		65.6		39

		20-Nov-07		20:07:10		72.8		40		20-Nov-07		20:06:20		69.8		42		20-Nov-07		20:07:53		69.2		45.5		31-Dec-07		20:25:59		64.4		38.5

		20-Nov-07		22:07:10		71.6		39.5		20-Nov-07		22:06:20		68.61		42.5		20-Nov-07		22:07:53		68.61		44		31-Dec-07		22:25:59		62.6		38.5

		21-Nov-07		0:07:10		71		39		21-Nov-07		0:06:20		68.61		40.5		21-Nov-07		0:07:53		68		43		1-Jan-08		0:25:59		62.6		37

		21-Nov-07		2:07:10		70.41		38.5		21-Nov-07		2:06:20		68		40.5		21-Nov-07		2:07:53		66.2		43.5		1-Jan-08		2:25:59		62		36

		21-Nov-07		4:07:10		69.8		37		21-Nov-07		4:06:20		68		39.5		21-Nov-07		4:07:53		65.01		43.5		1-Jan-08		4:25:59		62		35

		21-Nov-07		6:07:10		69.2		36.5		21-Nov-07		6:06:20		68		38.5		21-Nov-07		6:07:53		67.4		39.5		1-Jan-08		6:25:59		62.6		33.5

		21-Nov-07		8:07:10		71		35.5		21-Nov-07		8:06:20		68		37		21-Nov-07		8:07:53		68.61		38		1-Jan-08		8:25:59		65.01		32.5

		21-Nov-07		10:07:10		71.6		35.5		21-Nov-07		10:06:20		69.8		34.5		21-Nov-07		10:07:53		71.6		37		1-Jan-08		10:25:59		68		31

		21-Nov-07		12:07:10		72.8		33.5		21-Nov-07		12:06:20		70.41		34.5		21-Nov-07		12:07:53		70.41		38.5		1-Jan-08		12:25:59		72.21		30.5

		21-Nov-07		14:07:10		73.4		33.5		21-Nov-07		14:06:20		71		35		21-Nov-07		14:07:53		71.6		34.5		1-Jan-08		14:25:59		71.6		31.5

		21-Nov-07		16:07:10		74.6		33.5		21-Nov-07		16:06:20		71		36		21-Nov-07		16:07:53		71		37.5		1-Jan-08		16:25:59		72.21		30.5

		21-Nov-07		18:07:10		74.01		35		21-Nov-07		18:06:20		69.8		37.5		21-Nov-07		18:07:53		70.41		38.5		1-Jan-08		18:25:59		71		31.5

		21-Nov-07		20:07:10		72.8		34		21-Nov-07		20:06:20		69.2		36		21-Nov-07		20:07:53		70.41		38		1-Jan-08		20:25:59		70.41		31.5

		21-Nov-07		22:07:10		71		34		21-Nov-07		22:06:20		68.61		36.5		21-Nov-07		22:07:53		68		37.5		1-Jan-08		22:25:59		66.2		32.5

		22-Nov-07		0:07:10		70.41		33.5		22-Nov-07		0:06:20		68		35.5		22-Nov-07		0:07:53		65.6		38		2-Jan-08		0:25:59		63.8		33

		22-Nov-07		2:07:10		69.8		32		22-Nov-07		2:06:20		68		34		22-Nov-07		2:07:53		64.4		38		2-Jan-08		2:25:59		62.6		33

		22-Nov-07		4:07:10		69.2		31		22-Nov-07		4:06:20		67.4		33		22-Nov-07		4:07:53		63.21		37.5		2-Jan-08		4:25:59		62		32.5

		22-Nov-07		6:07:10		68.61		31		22-Nov-07		6:06:20		68		32.5		22-Nov-07		6:07:53		66.81		33.5		2-Jan-08		6:25:59		62.6		31.5

		22-Nov-07		8:07:10		70.41		30.5		22-Nov-07		8:06:20		69.8		31.5		22-Nov-07		8:07:53		69.2		32		2-Jan-08		8:25:59		63.8		31

		22-Nov-07		10:07:10		71.6		31.5		22-Nov-07		10:06:20		70.41		33.5		22-Nov-07		10:07:53		71.6		33		2-Jan-08		10:25:59		64.4		31

		22-Nov-07		12:07:10		72.21		32.5		22-Nov-07		12:06:20		71		34		22-Nov-07		12:07:53		70.41		35.5		2-Jan-08		12:25:59		66.81		32.5

		22-Nov-07		14:07:10		73.4		31.5		22-Nov-07		14:06:20		71		32.5		22-Nov-07		14:07:53		71.6		33.5		2-Jan-08		14:25:59		68.61		34

		22-Nov-07		16:07:10		73.4		29		22-Nov-07		16:06:20		69.8		29		22-Nov-07		16:07:53		71.6		33		2-Jan-08		16:25:59		70.41		34.5

		22-Nov-07		18:07:10		74.01		31.5		22-Nov-07		18:06:20		69.8		34		22-Nov-07		18:07:53		70.41		36		2-Jan-08		18:25:59		71		33.5

		22-Nov-07		20:07:10		71.6		31		22-Nov-07		20:06:20		68.61		33		22-Nov-07		20:07:53		69.8		34.5		2-Jan-08		20:25:59		70.41		33

		22-Nov-07		22:07:10		70.41		31.5		22-Nov-07		22:06:20		66.81		34.5		22-Nov-07		22:07:53		66.81		35.5		2-Jan-08		22:25:59		66.2		34.5

		23-Nov-07		0:07:10		69.2		31.5		23-Nov-07		0:06:20		66.2		35		23-Nov-07		0:07:53		64.4		37		3-Jan-08		0:25:59		64.4		35.5

		23-Nov-07		2:07:10		68.61		31		23-Nov-07		2:06:20		66.2		34		23-Nov-07		2:07:53		63.21		37		3-Jan-08		2:25:59		62.6		35.5

		23-Nov-07		4:07:10		68		31		23-Nov-07		4:06:20		66.2		33.5		23-Nov-07		4:07:53		62		36.5		3-Jan-08		4:25:59		62		36

		23-Nov-07		6:07:10		67.4		30		23-Nov-07		6:06:20		66.2		31.5		23-Nov-07		6:07:53		66.2		32.5		3-Jan-08		6:25:59		63.8		36

		23-Nov-07		8:07:10		69.2		28.5		23-Nov-07		8:06:20		67.4		30		23-Nov-07		8:07:53		67.4		31		3-Jan-08		8:25:59		65.01		34.5

		23-Nov-07		10:07:10		69.8		30		23-Nov-07		10:06:20		68		33		23-Nov-07		10:07:53		68		32.5		3-Jan-08		10:25:59		67.4		35

		23-Nov-07		12:07:10		70.41		31.5		23-Nov-07		12:06:20		68.61		33		23-Nov-07		12:07:53		68.61		33.5		3-Jan-08		12:25:59		72.8		33.5

		23-Nov-07		14:07:10		71		31		23-Nov-07		14:06:20		69.2		32		23-Nov-07		14:07:53		69.2		34		3-Jan-08		14:25:59		73.4		33

		23-Nov-07		16:07:10		71.6		29.5		23-Nov-07		16:06:20		69.2		29		23-Nov-07		16:07:53		69.8		32.5		3-Jan-08		16:25:59		72.8		34

		23-Nov-07		18:07:10		71.6		31.5		23-Nov-07		18:06:20		69.8		31.5		23-Nov-07		18:07:53		69.8		34		3-Jan-08		18:25:59		72.8		34.5

		23-Nov-07		20:07:10		71.6		32		23-Nov-07		20:06:20		68.61		35		23-Nov-07		20:07:53		68.61		36		3-Jan-08		20:25:59		71.6		35

		23-Nov-07		22:07:10		69.8		32		23-Nov-07		22:06:20		67.4		35.5		23-Nov-07		22:07:53		66.81		36		3-Jan-08		22:25:59		68		36

		24-Nov-07		0:07:10		68.61		32		24-Nov-07		0:06:20		66.2		35.5		24-Nov-07		0:07:53		65.01		36.5		4-Jan-08		0:25:59		65.6		36.5

		24-Nov-07		2:07:10		68		31.5		24-Nov-07		2:06:20		66.2		33.5		24-Nov-07		2:07:53		63.8		36.5		4-Jan-08		2:25:59		64.4		38

		24-Nov-07		4:07:10		67.4		30.5		24-Nov-07		4:06:20		66.2		31.5		24-Nov-07		4:07:53		62.6		35.5		4-Jan-08		4:25:59		63.8		39

		24-Nov-07		6:07:10		67.4		30.5		24-Nov-07		6:06:20		66.2		32.5		24-Nov-07		6:07:53		66.81		32		4-Jan-08		6:25:59		65.01		41

		24-Nov-07		8:07:10		69.2		27		24-Nov-07		8:06:20		68		28		24-Nov-07		8:07:53		68		30		4-Jan-08		8:25:59		68.61		40

		24-Nov-07		10:07:10		70.41		23.5		24-Nov-07		10:06:20		69.2		22		24-Nov-07		10:07:53		68		26		4-Jan-08		10:25:59		71.6		41

		24-Nov-07		12:07:10		71		20.5		24-Nov-07		12:06:20		69.2		18.5		24-Nov-07		12:07:53		68.61		24		4-Jan-08		12:25:59		74.01		40.5

		24-Nov-07		14:07:10		71		19		24-Nov-07		14:06:20		69.2		16		24-Nov-07		14:07:53		69.2		23		4-Jan-08		14:25:59		73.4		42.5

		24-Nov-07		16:07:10		71.6		18.5		24-Nov-07		16:06:20		69.2		16.5		24-Nov-07		16:07:53		69.8		22		4-Jan-08		16:25:59		74.01		41.5

		24-Nov-07		18:07:10		71.6		18.5		24-Nov-07		18:06:20		69.2		17		24-Nov-07		18:07:53		70.41		22		4-Jan-08		18:25:59		73.4		42

		24-Nov-07		20:07:10		71.6		21		24-Nov-07		20:06:20		69.2		22		24-Nov-07		20:07:53		69.2		24.5		4-Jan-08		20:25:59		72.8		43

		24-Nov-07		22:07:10		69.8		24.5		24-Nov-07		22:06:20		67.4		28		24-Nov-07		22:07:53		67.4		28		4-Jan-08		22:25:59		69.8		44

		25-Nov-07		0:07:10		69.2		25.5		25-Nov-07		0:06:20		66.81		29		25-Nov-07		0:07:53		65.6		29.5		5-Jan-08		0:25:59		68		45

		25-Nov-07		2:07:10		68		25.5		25-Nov-07		2:06:20		66.2		28.5		25-Nov-07		2:07:53		63.8		30.5		5-Jan-08		2:25:59		67.4		45.5

		25-Nov-07		4:07:10		67.4		26		25-Nov-07		4:06:20		66.2		28.5		25-Nov-07		4:07:53		62.6		30.5		5-Jan-08		4:25:59		66.81		46

		25-Nov-07		6:07:10		66.81		25.5		25-Nov-07		6:06:20		66.2		28		25-Nov-07		6:07:53		62		31		5-Jan-08		6:25:59		67.4		49

		25-Nov-07		8:07:10		67.4		24.5		25-Nov-07		8:06:20		67.4		26		25-Nov-07		8:07:53		66.81		26.5		5-Jan-08		8:25:59		71.6		48.5

		25-Nov-07		10:07:10		68		26.5		25-Nov-07		10:06:20		68		29		25-Nov-07		10:07:53		67.4		28		5-Jan-08		10:25:59		73.4		48.5

		25-Nov-07		12:07:10		68.61		27.5		25-Nov-07		12:06:20		68		29		25-Nov-07		12:07:53		67.4		30		5-Jan-08		12:25:59		72.8		48.5

		25-Nov-07		14:07:10		69.2		26		25-Nov-07		14:06:20		69.2		26		25-Nov-07		14:07:53		68		29		5-Jan-08		14:25:59		72.21		46

		25-Nov-07		16:07:10		69.8		27.5		25-Nov-07		16:06:20		69.2		28.5		25-Nov-07		16:07:53		68.61		30.5		5-Jan-08		16:25:59		72.8		44.5

		25-Nov-07		18:07:10		70.41		29.5		25-Nov-07		18:06:20		69.2		30.5		25-Nov-07		18:07:53		68.61		31.5		5-Jan-08		18:25:59		73.4		42

		25-Nov-07		20:07:10		69.2		29.5		25-Nov-07		20:06:20		68		32		25-Nov-07		20:07:53		67.4		32.5		5-Jan-08		20:25:59		72.21		41.5

		25-Nov-07		22:07:10		68.61		32		25-Nov-07		22:06:20		66.81		35.5		25-Nov-07		22:07:53		66.2		35		5-Jan-08		22:25:59		68.61		43.5

		26-Nov-07		0:07:10		68		32		26-Nov-07		0:06:20		66.2		35.5		26-Nov-07		0:07:53		65.01		36		6-Jan-08		0:25:59		67.4		44

		26-Nov-07		2:07:10		68		32.5		26-Nov-07		2:06:20		66.2		35.5		26-Nov-07		2:07:53		63.8		37		6-Jan-08		2:25:59		66.2		43.5

		26-Nov-07		4:07:10		67.4		32.5		26-Nov-07		4:06:20		66.2		35.5		26-Nov-07		4:07:53		63.21		37.5		6-Jan-08		4:25:59		65.6		43.5

		26-Nov-07		6:07:10		67.4		33		26-Nov-07		6:06:20		66.2		35.5		26-Nov-07		6:07:53		62.6		38		6-Jan-08		6:25:59		65.01		43.5

		26-Nov-07		8:07:10		68		32.5		26-Nov-07		8:06:20		67.4		34.5		26-Nov-07		8:07:53		67.4		34		6-Jan-08		8:25:59		64.4		43.5

		26-Nov-07		10:07:10		68		34		26-Nov-07		10:06:20		67.4		36.5		26-Nov-07		10:07:53		67.4		36		6-Jan-08		10:25:59		64.4		44.5

		26-Nov-07		12:07:10		68.61		34.5		26-Nov-07		12:06:20		67.4		37		26-Nov-07		12:07:53		68		35.5		6-Jan-08		12:25:59		64.4		45.5

		26-Nov-07		14:07:10		68.61		32		26-Nov-07		14:06:20		68		32		26-Nov-07		14:07:53		68		34		6-Jan-08		14:25:59		64.4		47

		26-Nov-07		16:07:10		69.2		32		26-Nov-07		16:06:20		68.61		33		26-Nov-07		16:07:53		67.4		34.5		6-Jan-08		16:25:59		65.01		47.5

		26-Nov-07		18:07:10		69.2		33		26-Nov-07		18:06:20		68		35		26-Nov-07		18:07:53		68		35.5		6-Jan-08		18:25:59		64.4		47.5

		26-Nov-07		20:07:10		68.61		34		26-Nov-07		20:06:20		67.4		36.5		26-Nov-07		20:07:53		66.81		36.5		6-Jan-08		20:25:59		64.4		47.5

		26-Nov-07		22:07:10		68		33.5		26-Nov-07		22:06:20		66.2		36		26-Nov-07		22:07:53		64.4		37.5		6-Jan-08		22:25:59		64.4		46.5

		27-Nov-07		0:07:10		67.4		33		27-Nov-07		0:06:20		66.2		36		27-Nov-07		0:07:53		63.8		38		7-Jan-08		0:25:59		64.4		46

		27-Nov-07		2:07:10		66.81		32		27-Nov-07		2:06:20		66.2		34		27-Nov-07		2:07:53		62.6		36.5		7-Jan-08		2:25:59		63.8		45

		27-Nov-07		4:07:10		66.81		31.5		27-Nov-07		4:06:20		65.6		32.5		27-Nov-07		4:07:53		62		36.5		7-Jan-08		4:25:59		63.8		44.5

		27-Nov-07		6:07:10		66.81		30.5		27-Nov-07		6:06:20		65.6		32		27-Nov-07		6:07:53		66.81		32		7-Jan-08		6:25:59		63.21		43.5

		27-Nov-07		8:07:10		69.2		28.5		27-Nov-07		8:06:20		67.4		30.5		27-Nov-07		8:07:53		68.61		30.5		7-Jan-08		8:25:59		63.21		43

		27-Nov-07		10:07:10		69.8		31		27-Nov-07		10:06:20		69.8		32.5		27-Nov-07		10:07:53		69.2		32		7-Jan-08		10:25:59		63.8		42

		27-Nov-07		12:07:10		71		32.5		27-Nov-07		12:06:20		71.6		34		27-Nov-07		12:07:53		71		33.5		7-Jan-08		12:25:59		63.8		43

		27-Nov-07		14:07:10		71.6		34		27-Nov-07		14:06:20		71		35.5		27-Nov-07		14:07:53		71		34.5		7-Jan-08		14:25:59		65.01		44.5

		27-Nov-07		16:07:10		72.21		34		27-Nov-07		16:06:20		71.6		37.5		27-Nov-07		16:07:53		70.41		38		7-Jan-08		16:25:59		65.01		44.5

		27-Nov-07		18:07:10		72.21		36.5		27-Nov-07		18:06:20		69.8		39.5		27-Nov-07		18:07:53		69.8		39		7-Jan-08		18:25:59		65.6		44

		27-Nov-07		20:07:10		71.6		36.5		27-Nov-07		20:06:20		68.61		40		27-Nov-07		20:07:53		69.2		39.5		7-Jan-08		20:25:59		64.4		44.5

		27-Nov-07		22:07:10		69.8		35		27-Nov-07		22:06:20		67.4		38.5		27-Nov-07		22:07:53		67.4		38.5		7-Jan-08		22:25:59		63.8		45

		28-Nov-07		0:07:10		69.2		35		28-Nov-07		0:06:20		66.81		38.5		28-Nov-07		0:07:53		66.2		38.5		8-Jan-08		0:25:59		63.8		45.5

		28-Nov-07		2:07:10		68		34.5		28-Nov-07		2:06:20		66.2		38		28-Nov-07		2:07:53		65.01		39		8-Jan-08		2:25:59		63.8		45.5

		28-Nov-07		4:07:10		68		34		28-Nov-07		4:06:20		66.2		37		28-Nov-07		4:07:53		63.8		39		8-Jan-08		4:25:59		63.8		46

		28-Nov-07		6:07:10		67.4		34.5		28-Nov-07		6:06:20		66.2		37.5		28-Nov-07		6:07:53		67.4		35.5		8-Jan-08		6:25:59		65.01		45

		28-Nov-07		8:07:10		69.8		34		28-Nov-07		8:06:20		68		36.5		28-Nov-07		8:07:53		69.2		36.5		8-Jan-08		8:25:59		67.4		40.5

		28-Nov-07		10:07:10		71		34.5		28-Nov-07		10:06:20		70.41		36.5		28-Nov-07		10:07:53		71.6		36		8-Jan-08		10:25:59		69.8		39

		28-Nov-07		12:07:10		72.21		39		28-Nov-07		12:06:20		71		43.5		28-Nov-07		12:07:53		71		41		8-Jan-08		12:25:59		73.4		39

		28-Nov-07		14:07:10		72.8		34		28-Nov-07		14:06:20		71		34		28-Nov-07		14:07:53		71		39		8-Jan-08		14:25:59		72.8		37

		28-Nov-07		16:07:10		72.8		33.5		28-Nov-07		16:06:20		71.6		34.5		28-Nov-07		16:07:53		71		37.5		8-Jan-08		16:25:59		72.21		36

		28-Nov-07		18:07:10		72.8		35		28-Nov-07		18:06:20		70.41		37.5		28-Nov-07		18:07:53		71		37.5		8-Jan-08		18:25:59		72.21		35.5

		28-Nov-07		20:07:10		72.8		35		28-Nov-07		20:06:20		69.8		37.5		28-Nov-07		20:07:53		70.41		38.5		8-Jan-08		20:25:59		71.6		34.5

		28-Nov-07		22:07:10		71.6		35		28-Nov-07		22:06:20		68.61		38		28-Nov-07		22:07:53		69.2		38		8-Jan-08		22:25:59		68		37.5

		29-Nov-07		0:07:10		70.41		35.5		29-Nov-07		0:06:20		67.4		38.5		29-Nov-07		0:07:53		68		38		9-Jan-08		0:25:59		66.81		38

		29-Nov-07		2:07:10		69.2		34		29-Nov-07		2:06:20		66.81		37		29-Nov-07		2:07:53		66.2		38		9-Jan-08		2:25:59		65.6		39

		29-Nov-07		4:07:10		68.61		33		29-Nov-07		4:06:20		66.81		35.5		29-Nov-07		4:07:53		65.01		37.5		9-Jan-08		4:25:59		65.01		39.5

		29-Nov-07		6:07:10		68.61		32		29-Nov-07		6:06:20		66.2		33.5		29-Nov-07		6:07:53		66.81		34.5		9-Jan-08		6:25:59		65.6		39.5

		29-Nov-07		8:07:10		70.41		30.5		29-Nov-07		8:06:20		68		32		29-Nov-07		8:07:53		68		33.5		9-Jan-08		8:25:59		68.61		38

		29-Nov-07		10:07:10		71.6		32.5		29-Nov-07		10:06:20		71		34.5		29-Nov-07		10:07:53		70.41		34		9-Jan-08		10:25:59		71		40

		29-Nov-07		12:07:10		72.8		31		29-Nov-07		12:06:20		71.6		32.5		29-Nov-07		12:07:53		71		33		9-Jan-08		12:25:59		73.4		39

		29-Nov-07		14:07:10		72.8		31		29-Nov-07		14:06:20		71.6		32.5		29-Nov-07		14:07:53		71.6		31		9-Jan-08		14:25:59		74.01		40

		29-Nov-07		16:07:10		72.8		30.5		29-Nov-07		16:06:20		71.6		31.5		29-Nov-07		16:07:53		71		35		9-Jan-08		16:25:59		74.6		41

		29-Nov-07		18:07:10		72.8		28		29-Nov-07		18:06:20		69.2		29		29-Nov-07		18:07:53		71		32		9-Jan-08		18:25:59		75.2		41.5

		29-Nov-07		20:07:10		72.21		30		29-Nov-07		20:06:20		69.2		31		29-Nov-07		20:07:53		69.8		32.5		9-Jan-08		20:25:59		73.4		41.5

		29-Nov-07		22:07:10		70.41		31		29-Nov-07		22:06:20		67.4		34		29-Nov-07		22:07:53		68		34		9-Jan-08		22:25:59		69.8		42.5

		30-Nov-07		0:07:10		69.2		31		30-Nov-07		0:06:20		66.81		34		30-Nov-07		0:07:53		66.2		34.5		10-Jan-08		0:25:59		68		44

		30-Nov-07		2:07:10		68.61		30.5		30-Nov-07		2:06:20		66.2		33.5		30-Nov-07		2:07:53		65.01		35		10-Jan-08		2:25:59		66.81		44.5

		30-Nov-07		4:07:10		68		30		30-Nov-07		4:06:20		65.6		33		30-Nov-07		4:07:53		63.21		35		10-Jan-08		4:25:59		66.2		45

		30-Nov-07		6:07:10		67.4		30		30-Nov-07		6:06:20		66.2		32		30-Nov-07		6:07:53		67.4		31		10-Jan-08		6:25:59		68		45

		30-Nov-07		8:07:10		69.8		28		30-Nov-07		8:06:20		68.61		30.5		30-Nov-07		8:07:53		68		31		10-Jan-08		8:25:59		71.6		41.5

		30-Nov-07		10:07:10		71		30		30-Nov-07		10:06:20		70.41		33		30-Nov-07		10:07:53		70.41		32		10-Jan-08		10:25:59		73.4		40.5

		30-Nov-07		12:07:10		71.6		31.5		30-Nov-07		12:06:20		71		31		30-Nov-07		12:07:53		71.6		31.5		10-Jan-08		12:25:59		74.6		39.5

		30-Nov-07		14:07:10		72.8		30		30-Nov-07		14:06:20		71		31		30-Nov-07		14:07:53		71		35		10-Jan-08		14:25:59		74.6		39

		30-Nov-07		16:07:10		73.4		28		30-Nov-07		16:06:20		71		29		30-Nov-07		16:07:53		71		32.5		10-Jan-08		16:25:59		74.6		39

		30-Nov-07		18:07:10		73.4		26.5		30-Nov-07		18:06:20		69.8		26.5		30-Nov-07		18:07:53		69.8		31		10-Jan-08		18:25:59		73.4		39.5

		30-Nov-07		20:07:10		72.21		26		30-Nov-07		20:06:20		69.2		27.5		30-Nov-07		20:07:53		69.2		29		10-Jan-08		20:25:59		74.01		38.5

		30-Nov-07		22:07:10		71		27.5		30-Nov-07		22:06:20		68		30.5		30-Nov-07		22:07:53		68		31		10-Jan-08		22:25:59		70.41		43

		1-Dec-07		0:07:10		69.8		28.5		1-Dec-07		0:06:20		67.4		32		1-Dec-07		0:07:53		66.81		32.5		11-Jan-08		0:25:59		68.61		42.5

		1-Dec-07		2:07:10		69.2		28.5		1-Dec-07		2:06:20		66.81		31.5		1-Dec-07		2:07:53		65.01		33		11-Jan-08		2:25:59		67.4		43.5

		1-Dec-07		4:07:10		68.61		28		1-Dec-07		4:06:20		66.2		30.5		1-Dec-07		4:07:53		64.4		33		11-Jan-08		4:25:59		66.2		44

		1-Dec-07		6:07:10		68.61		28		1-Dec-07		6:06:20		66.2		30.5		1-Dec-07		6:07:53		66.81		30.5		11-Jan-08		6:25:59		68		44.5

		1-Dec-07		8:07:10		70.41		27		1-Dec-07		8:06:20		68		29		1-Dec-07		8:07:53		69.2		29.5		11-Jan-08		8:25:59		71.6		42

		1-Dec-07		10:07:10		71		27.5		1-Dec-07		10:06:20		70.41		29.5		1-Dec-07		10:07:53		71		29		11-Jan-08		10:25:59		74.01		41.5

		1-Dec-07		12:07:10		72.21		26.5		1-Dec-07		12:06:20		71.6		27		1-Dec-07		12:07:53		71		29.5		11-Jan-08		12:25:59		74.6		41

		1-Dec-07		14:07:10		72.8		24.5		1-Dec-07		14:06:20		71		26		1-Dec-07		14:07:53		70.41		29		11-Jan-08		14:25:59		74.01		43

		1-Dec-07		16:07:10		72.8		24.5		1-Dec-07		16:06:20		71		25.5		1-Dec-07		16:07:53		70.41		28		11-Jan-08		16:25:59		73.4		44.5

		1-Dec-07		18:07:10		72.8		26.5		1-Dec-07		18:06:20		69.8		28.5		1-Dec-07		18:07:53		70.41		30.5		11-Jan-08		18:25:59		71.6		45.5

		1-Dec-07		20:07:10		71.6		24.5		1-Dec-07		20:06:20		68		26		1-Dec-07		20:07:53		68.61		28		11-Jan-08		20:25:59		69.2		46.5

		1-Dec-07		22:07:10		69.8		24.5		1-Dec-07		22:06:20		66.81		27.5		1-Dec-07		22:07:53		66.2		28.5		11-Jan-08		22:25:59		68.61		47

		2-Dec-07		0:07:10		68.61		26		2-Dec-07		0:06:20		66.2		28		2-Dec-07		0:07:53		64.4		31.5		12-Jan-08		0:25:59		67.4		47.5

		2-Dec-07		2:07:10		68		25		2-Dec-07		2:06:20		65.6		28		2-Dec-07		2:07:53		63.21		30.5		12-Jan-08		2:25:59		66.81		48

		2-Dec-07		4:07:10		67.4		24.5		2-Dec-07		4:06:20		65.6		26.5		2-Dec-07		4:07:53		62		29.5		12-Jan-08		4:25:59		66.2		48

		2-Dec-07		6:07:10		66.81		24		2-Dec-07		6:06:20		65.6		26		2-Dec-07		6:07:53		61.41		29		12-Jan-08		6:25:59		66.2		49

		2-Dec-07		8:07:10		67.4		23		2-Dec-07		8:06:20		67.4		24.5		2-Dec-07		8:07:53		66.81		25.5		12-Jan-08		8:25:59		69.8		44.5

		2-Dec-07		10:07:10		67.4		24.5		2-Dec-07		10:06:20		67.4		26		2-Dec-07		10:07:53		68.61		25		12-Jan-08		10:25:59		71.6		43.5

		2-Dec-07		12:07:10		68		27		2-Dec-07		12:06:20		68		28.5		2-Dec-07		12:07:53		68.61		28		12-Jan-08		12:25:59		70.41		45

		2-Dec-07		14:07:10		68.61		27.5		2-Dec-07		14:06:20		68		28.5		2-Dec-07		14:07:53		69.2		29		12-Jan-08		14:25:59		71		44.5

		2-Dec-07		16:07:10		69.2		28		2-Dec-07		16:06:20		68		29.5		2-Dec-07		16:07:53		68		30		12-Jan-08		16:25:59		70.41		44

		2-Dec-07		18:07:10		69.2		28.5		2-Dec-07		18:06:20		68		30		2-Dec-07		18:07:53		67.4		31		12-Jan-08		18:25:59		69.8		44

		2-Dec-07		20:07:10		68		30		2-Dec-07		20:06:20		66.81		33		2-Dec-07		20:07:53		67.4		31		12-Jan-08		20:25:59		68.61		44.5

		2-Dec-07		22:07:10		67.4		29.5		2-Dec-07		22:06:20		66.2		32.5		2-Dec-07		22:07:53		63.8		33.5		12-Jan-08		22:25:59		67.4		46

		3-Dec-07		0:07:10		66.81		29.5		3-Dec-07		0:06:20		65.6		32		3-Dec-07		0:07:53		62.6		33.5		13-Jan-08		0:25:59		66.2		46.5

		3-Dec-07		2:07:10		66.81		30		3-Dec-07		2:06:20		66.2		33		3-Dec-07		2:07:53		62		34.5		13-Jan-08		2:25:59		66.2		47

		3-Dec-07		4:07:10		66.81		32.5		3-Dec-07		4:06:20		66.2		36		3-Dec-07		4:07:53		62.6		37.5		13-Jan-08		4:25:59		65.6		47

		3-Dec-07		6:07:10		66.81		35		3-Dec-07		6:06:20		66.2		39		3-Dec-07		6:07:53		62.6		40		13-Jan-08		6:25:59		65.01		47

		3-Dec-07		8:07:10		68		35.5		3-Dec-07		8:06:20		67.4		38		3-Dec-07		8:07:53		68.61		36		13-Jan-08		8:25:59		65.01		47.5

		3-Dec-07		10:07:10		68		35		3-Dec-07		10:06:20		67.4		37		3-Dec-07		10:07:53		68		36.5		13-Jan-08		10:25:59		65.01		48.5

		3-Dec-07		12:07:10		68		36		3-Dec-07		12:06:20		67.4		38		3-Dec-07		12:07:53		67.4		37.5		13-Jan-08		12:25:59		65.01		50

		3-Dec-07		14:07:10		68.61		36.5		3-Dec-07		14:06:20		68		39		3-Dec-07		14:07:53		68		38		13-Jan-08		14:25:59		65.6		51

		3-Dec-07		16:07:10		69.2		39		3-Dec-07		16:06:20		68		42.5		3-Dec-07		16:07:53		67.4		41		13-Jan-08		16:25:59		66.81		50

		3-Dec-07		18:07:10		69.2		39.5		3-Dec-07		18:06:20		68		42.5		3-Dec-07		18:07:53		67.4		42		13-Jan-08		18:25:59		67.4		49.5

		3-Dec-07		20:07:10		68.61		41		3-Dec-07		20:06:20		67.4		44.5		3-Dec-07		20:07:53		67.4		43		13-Jan-08		20:25:59		66.2		49.5

		3-Dec-07		22:07:10		68.61		44.5		3-Dec-07		22:06:20		66.81		50		3-Dec-07		22:07:53		66.2		47.5		13-Jan-08		22:25:59		65.6		49

		4-Dec-07		0:07:10		68.61		43		4-Dec-07		0:06:20		66.81		47		4-Dec-07		0:07:53		66.2		46.5		14-Jan-08		0:25:59		65.01		48

		4-Dec-07		2:07:10		68.61		42		4-Dec-07		2:06:20		66.81		45.5		4-Dec-07		2:07:53		66.2		45.5		14-Jan-08		2:25:59		64.4		48.5

		4-Dec-07		4:07:10		68.61		40.5		4-Dec-07		4:06:20		67.4		43		4-Dec-07		4:07:53		66.2		44.5		14-Jan-08		4:25:59		64.4		49

		4-Dec-07		6:07:10		68.61		40		4-Dec-07		6:06:20		67.4		42		4-Dec-07		6:07:53		66.2		44		14-Jan-08		6:25:59		64.4		49.5

		4-Dec-07		8:07:10		71.6		37		4-Dec-07		8:06:20		69.2		39		4-Dec-07		8:07:53		69.2		41		14-Jan-08		8:25:59		65.01		50.5

		4-Dec-07		10:07:10		72.8		39		4-Dec-07		10:06:20		71		42		4-Dec-07		10:07:53		70.41		43.5		14-Jan-08		10:25:59		65.6		49.5

		4-Dec-07		12:07:10		74.6		37.5		4-Dec-07		12:06:20		71.6		39		4-Dec-07		12:07:53		71		38.5		14-Jan-08		12:25:59		66.2		49

		4-Dec-07		14:07:10		73.4		38		4-Dec-07		14:06:20		71		42.5		4-Dec-07		14:07:53		71		39.5		14-Jan-08		14:25:59		66.81		48.5

		4-Dec-07		16:07:10		74.01		39.5		4-Dec-07		16:06:20		71.6		41.5		4-Dec-07		16:07:53		70.41		40		14-Jan-08		16:25:59		66.81		49

		4-Dec-07		18:07:10		74.01		40		4-Dec-07		18:06:20		70.41		42		4-Dec-07		18:07:53		71		45		14-Jan-08		18:25:59		66.81		49.5

		4-Dec-07		20:07:10		72.8		40.5		4-Dec-07		20:06:20		69.8		44		4-Dec-07		20:07:53		70.41		44		14-Jan-08		20:25:59		66.2		49

		4-Dec-07		22:07:10		72.21		44		4-Dec-07		22:06:20		69.8		50.5		4-Dec-07		22:07:53		69.8		46.5		14-Jan-08		22:25:59		65.01		49

		5-Dec-07		0:07:10		72.21		47		5-Dec-07		0:06:20		69.2		53.5		5-Dec-07		0:07:53		69.8		49.5		15-Jan-08		0:25:59		64.4		47.5

		5-Dec-07		2:07:10		71.6		48.5		5-Dec-07		2:06:20		69.2		54.5		5-Dec-07		2:07:53		69.2		51		15-Jan-08		2:25:59		63.8		47

		5-Dec-07		4:07:10		71		49.5		5-Dec-07		4:06:20		69.2		55		5-Dec-07		4:07:53		68.61		52.5		15-Jan-08		4:25:59		63.8		46.5

		5-Dec-07		6:07:10		71		50.5		5-Dec-07		6:06:20		68.61		56		5-Dec-07		6:07:53		68		53.5		15-Jan-08		6:25:59		64.4		46.5

		5-Dec-07		8:07:10		73.4		50		5-Dec-07		8:06:20		69.8		57.5		5-Dec-07		8:07:53		71		53		15-Jan-08		8:25:59		67.4		44

		5-Dec-07		10:07:10		74.01		49		5-Dec-07		10:06:20		71		44		5-Dec-07		10:07:53		71		57.5		15-Jan-08		10:25:59		71		43.5

		5-Dec-07		12:07:10		74.01		48		5-Dec-07		12:06:20		71.6		54		5-Dec-07		12:07:53		71		51		15-Jan-08		12:25:59		70.41		43

		5-Dec-07		14:07:10		74.01		49		5-Dec-07		14:06:20		71.6		54		5-Dec-07		14:07:53		71		48.5		15-Jan-08		14:25:59		69.8		44

		5-Dec-07		16:07:10		74.01		51		5-Dec-07		16:06:20		71.6		54		5-Dec-07		16:07:53		71		59.5		15-Jan-08		16:25:59		70.41		45

		5-Dec-07		18:07:10		73.4		50.5		5-Dec-07		18:06:20		69.8		57		5-Dec-07		18:07:53		71		47.5		15-Jan-08		18:25:59		71.6		43.5

		5-Dec-07		20:07:10		73.4		50		5-Dec-07		20:06:20		69.8		56		5-Dec-07		20:07:53		71		54.5		15-Jan-08		20:25:59		69.2		43

		5-Dec-07		22:07:10		72.8		50.5		5-Dec-07		22:06:20		69.8		56.5		5-Dec-07		22:07:53		70.41		55		15-Jan-08		22:25:59		66.81		43.5

		6-Dec-07		0:07:10		72.21		51.5		6-Dec-07		0:06:20		69.2		57		6-Dec-07		0:07:53		70.41		54.5		16-Jan-08		0:25:59		65.01		43.5

		6-Dec-07		2:07:10		71.6		51.5		6-Dec-07		2:06:20		69.2		57		6-Dec-07		2:07:53		69.8		54		16-Jan-08		2:25:59		64.4		43.5

		6-Dec-07		4:07:10		71.6		52		6-Dec-07		4:06:20		68.61		57.5		6-Dec-07		4:07:53		69.8		54		16-Jan-08		4:25:59		63.8		43.5

		6-Dec-07		6:07:10		71		50		6-Dec-07		6:06:20		68		54		6-Dec-07		6:07:53		69.2		53		16-Jan-08		6:25:59		64.4		42.5

		6-Dec-07		8:07:10		72.8		47.5		6-Dec-07		8:06:20		69.8		52		6-Dec-07		8:07:53		71		52		16-Jan-08		8:25:59		66.81		39.5

		6-Dec-07		10:07:10		74.01		45.5		6-Dec-07		10:06:20		71		45		6-Dec-07		10:07:53		71		50		16-Jan-08		10:25:59		70.41		38

		6-Dec-07		12:07:10		74.01		46		6-Dec-07		12:06:20		71		55		6-Dec-07		12:07:53		71		48		16-Jan-08		12:25:59		71		39.5

		6-Dec-07		14:07:10		74.01		46		6-Dec-07		14:06:20		71		57		6-Dec-07		14:07:53		71		54.5		16-Jan-08		14:25:59		72.21		40.5

		6-Dec-07		16:07:10		74.6		47.5		6-Dec-07		16:06:20		71		47.5		6-Dec-07		16:07:53		70.41		51.5		16-Jan-08		16:25:59		72.21		43

		6-Dec-07		18:07:10		74.01		39		6-Dec-07		18:06:20		69.8		41		6-Dec-07		18:07:53		69.8		45		16-Jan-08		18:25:59		72.8		41.5

		6-Dec-07		20:07:10		73.4		38		6-Dec-07		20:06:20		69.8		40		6-Dec-07		20:07:53		69.8		43.5		16-Jan-08		20:25:59		71		41.5

		6-Dec-07		22:07:10		72.21		40		6-Dec-07		22:06:20		69.2		44		6-Dec-07		22:07:53		70.41		44		16-Jan-08		22:25:59		68.61		41.5

		7-Dec-07		0:07:10		71.6		42		7-Dec-07		0:06:20		68		47		7-Dec-07		0:07:53		69.8		44.5		17-Jan-08		0:25:59		66.2		41.5

		7-Dec-07		2:07:10		70.41		42.5		7-Dec-07		2:06:20		67.4		48		7-Dec-07		2:07:53		69.2		45		17-Jan-08		2:25:59		65.01		41.5

		7-Dec-07		4:07:10		69.8		43		7-Dec-07		4:06:20		66.81		48.5		7-Dec-07		4:07:53		68.61		45.5		17-Jan-08		4:25:59		64.4		41.5

		7-Dec-07		6:07:10		69.8		43.5		7-Dec-07		6:06:20		66.81		49		7-Dec-07		6:07:53		68		46.5		17-Jan-08		6:25:59		65.01		39.5

		7-Dec-07		8:07:10		72.21		42		7-Dec-07		8:06:20		68.61		47.5		7-Dec-07		8:07:53		70.41		45		17-Jan-08		8:25:59		66.81		36.5

		7-Dec-07		10:07:10		73.4		42.5		7-Dec-07		10:06:20		71		49.5		7-Dec-07		10:07:53		71		48		17-Jan-08		10:25:59		71		33

		7-Dec-07		12:07:10		72.8		45		7-Dec-07		12:06:20		71		44.5		7-Dec-07		12:07:53		70.41		50.5		17-Jan-08		12:25:59		71.6		27

		7-Dec-07		14:07:10		72.21		47		7-Dec-07		14:06:20		71		47		7-Dec-07		14:07:53		71.6		52.5		17-Jan-08		14:25:59		72.8		25.5

		7-Dec-07		16:07:10		72.21		46		7-Dec-07		16:06:20		71		50		7-Dec-07		16:07:53		70.41		50		17-Jan-08		16:25:59		72.21		23.5

		7-Dec-07		18:07:10		72.21		45.5		7-Dec-07		18:06:20		69.2		50.5		7-Dec-07		18:07:53		70.41		51.5		17-Jan-08		18:25:59		72.21		23

		7-Dec-07		20:07:10		71		47		7-Dec-07		20:06:20		68.61		51		7-Dec-07		20:07:53		69.8		49		17-Jan-08		20:25:59		71.6		23

		7-Dec-07		22:07:10		69.8		47.5		7-Dec-07		22:06:20		67.4		52.5		7-Dec-07		22:07:53		69.8		48.5		17-Jan-08		22:25:59		69.2		24.5

		8-Dec-07		0:07:10		69.2		48		8-Dec-07		0:06:20		66.81		52.5		8-Dec-07		0:07:53		69.2		49		18-Jan-08		0:25:59		67.4		25.5

		8-Dec-07		2:07:10		68.61		44.5		8-Dec-07		2:06:20		66.81		47		8-Dec-07		2:07:53		68		46.5		18-Jan-08		2:25:59		66.2		26

		8-Dec-07		4:07:10		68.61		44		8-Dec-07		4:06:20		66.2		47		8-Dec-07		4:07:53		66.81		47		18-Jan-08		4:25:59		65.01		26

		8-Dec-07		6:07:10		68		43		8-Dec-07		6:06:20		66.2		45.5		8-Dec-07		6:07:53		67.4		45		18-Jan-08		6:25:59		66.2		26.5

		8-Dec-07		8:07:10		71		39		8-Dec-07		8:06:20		68		41		8-Dec-07		8:07:53		69.8		42		18-Jan-08		8:25:59		68.61		26

		8-Dec-07		10:07:10		72.21		37		8-Dec-07		10:06:20		69.8		40.5		8-Dec-07		10:07:53		71.6		40.5		18-Jan-08		10:25:59		72.21		27.5

		8-Dec-07		12:07:10		71.6		37.5		8-Dec-07		12:06:20		71		40.5		8-Dec-07		12:07:53		71		41		18-Jan-08		12:25:59		71.6		28

		8-Dec-07		14:07:10		71.6		36.5		8-Dec-07		14:06:20		71		40		8-Dec-07		14:07:53		71		35		18-Jan-08		14:25:59		72.21		29.5

		8-Dec-07		16:07:10		71.6		35.5		8-Dec-07		16:06:20		71		38		8-Dec-07		16:07:53		70.41		38.5		18-Jan-08		16:25:59		72.8		29

		8-Dec-07		18:07:10		71.6		35.5		8-Dec-07		18:06:20		69.8		35.5		8-Dec-07		18:07:53		69.8		37.5		18-Jan-08		18:25:59		72.21		30

		8-Dec-07		20:07:10		70.41		35		8-Dec-07		20:06:20		67.4		36.5		8-Dec-07		20:07:53		69.2		37		18-Jan-08		20:25:59		71.6		31.5

		8-Dec-07		22:07:10		69.2		33.5		8-Dec-07		22:06:20		66.81		36		8-Dec-07		22:07:53		67.4		37		18-Jan-08		22:25:59		68.61		32

		9-Dec-07		0:07:10		68.61		33.5		9-Dec-07		0:06:20		66.81		35.5		9-Dec-07		0:07:53		66.2		37		19-Jan-08		0:25:59		66.81		32.5

		9-Dec-07		2:07:10		68		33		9-Dec-07		2:06:20		66.2		35		9-Dec-07		2:07:53		65.6		37		19-Jan-08		2:25:59		65.01		33

		9-Dec-07		4:07:10		68		32.5		9-Dec-07		4:06:20		66.2		34		9-Dec-07		4:07:53		64.4		37		19-Jan-08		4:25:59		64.4		33

		9-Dec-07		6:07:10		67.4		32		9-Dec-07		6:06:20		66.2		33.5		9-Dec-07		6:07:53		63.8		36.5		19-Jan-08		6:25:59		66.2		32

		9-Dec-07		8:07:10		68		30.5		9-Dec-07		8:06:20		67.4		31.5		9-Dec-07		8:07:53		67.4		33		19-Jan-08		8:25:59		68.61		30

		9-Dec-07		10:07:10		68.61		30.5		9-Dec-07		10:06:20		68		31		9-Dec-07		10:07:53		68.61		31.5		19-Jan-08		10:25:59		70.41		31

		9-Dec-07		12:07:10		68.61		29.5		9-Dec-07		12:06:20		68.61		29		9-Dec-07		12:07:53		69.8		30		19-Jan-08		12:25:59		71		32.5

		9-Dec-07		14:07:10		68.61		28.5		9-Dec-07		14:06:20		68		28		9-Dec-07		14:07:53		70.41		30		19-Jan-08		14:25:59		71.6		33

		9-Dec-07		16:07:10		69.2		25		9-Dec-07		16:06:20		68		22.5		9-Dec-07		16:07:53		69.2		28.5		19-Jan-08		16:25:59		72.8		32.5

		9-Dec-07		18:07:10		69.2		24		9-Dec-07		18:06:20		68		23		9-Dec-07		18:07:53		68.61		27.5		19-Jan-08		18:25:59		72.8		33

		9-Dec-07		20:07:10		68.61		24		9-Dec-07		20:06:20		67.4		23.5		9-Dec-07		20:07:53		67.4		27		19-Jan-08		20:25:59		72.21		32

		9-Dec-07		22:07:10		68		24		9-Dec-07		22:06:20		66.81		24		9-Dec-07		22:07:53		66.2		27		19-Jan-08		22:25:59		68		34.5

		10-Dec-07		0:07:10		67.4		24		10-Dec-07		0:06:20		66.2		24.5		10-Dec-07		0:07:53		65.6		27.5		20-Jan-08		0:25:59		66.2		34.5

		10-Dec-07		2:07:10		67.4		24.5		10-Dec-07		2:06:20		66.2		25		10-Dec-07		2:07:53		64.4		28		20-Jan-08		2:25:59		65.01		34.5

		10-Dec-07		4:07:10		66.81		25		10-Dec-07		4:06:20		65.6		26.5		10-Dec-07		4:07:53		63.8		28.5		20-Jan-08		4:25:59		63.8		34

		10-Dec-07		6:07:10		66.2		26		10-Dec-07		6:06:20		65.6		28		10-Dec-07		6:07:53		63.21		29.5		20-Jan-08		6:25:59		63.21		33.5

		10-Dec-07		8:07:10		66.81		26		10-Dec-07		8:06:20		67.4		27		10-Dec-07		8:07:53		68.61		26.5		20-Jan-08		8:25:59		63.21		32.5

		10-Dec-07		10:07:10		67.4		26.5		10-Dec-07		10:06:20		67.4		27.5		10-Dec-07		10:07:53		67.4		27.5		20-Jan-08		10:25:59		63.21		33

		10-Dec-07		12:07:10		68		27.5		10-Dec-07		12:06:20		68		28		10-Dec-07		12:07:53		68		29		20-Jan-08		12:25:59		63.8		37

		10-Dec-07		14:07:10		68.61		28.5		10-Dec-07		14:06:20		68		29.5		10-Dec-07		14:07:53		68		30		20-Jan-08		14:25:59		65.01		39

		10-Dec-07		16:07:10		69.2		28.5		10-Dec-07		16:06:20		68.61		29		10-Dec-07		16:07:53		68		31.5		20-Jan-08		16:25:59		66.2		37.5

		10-Dec-07		18:07:10		69.2		30		10-Dec-07		18:06:20		68		31.5		10-Dec-07		18:07:53		67.4		32.5		20-Jan-08		18:25:59		66.81		37

		10-Dec-07		20:07:10		68.61		31		10-Dec-07		20:06:20		66.81		33.5		10-Dec-07		20:07:53		66.81		33.5		20-Jan-08		20:25:59		65.6		37

		10-Dec-07		22:07:10		68		32.5		10-Dec-07		22:06:20		66.2		35.5		10-Dec-07		22:07:53		65.6		35		20-Jan-08		22:25:59		65.01		37

		11-Dec-07		0:07:10		67.4		33.5		11-Dec-07		0:06:20		66.2		36.5		11-Dec-07		0:07:53		65.01		36.5		21-Jan-08		0:25:59		64.4		37

		11-Dec-07		2:07:10		66.81		32		11-Dec-07		2:06:20		66.2		34.5		11-Dec-07		2:07:53		64.4		36		21-Jan-08		2:25:59		63.8		38

		11-Dec-07		4:07:10		66.81		31.5		11-Dec-07		4:06:20		66.2		33		11-Dec-07		4:07:53		63.21		35.5		21-Jan-08		4:25:59		63.8		38.5

		11-Dec-07		6:07:10		66.81		30.5		11-Dec-07		6:06:20		66.2		32		11-Dec-07		6:07:53		67.4		31.5		21-Jan-08		6:25:59		63.21		38

		11-Dec-07		8:07:10		68.61		28.5		11-Dec-07		8:06:20		67.4		30		11-Dec-07		8:07:53		68		30.5		21-Jan-08		8:25:59		63.21		38

		11-Dec-07		10:07:10		69.2		30		11-Dec-07		10:06:20		69.8		31.5		11-Dec-07		10:07:53		69.2		31		21-Jan-08		10:25:59		63.8		38

		11-Dec-07		12:07:10		71.6		31.5		11-Dec-07		12:06:20		70.41		34		11-Dec-07		12:07:53		71.6		32.5		21-Jan-08		12:25:59		65.01		39

		11-Dec-07		14:07:10		71.6		32.5		11-Dec-07		14:06:20		70.41		34		11-Dec-07		14:07:53		71		35.5		21-Jan-08		14:25:59		65.6		36

		11-Dec-07		16:07:10		72.21		32.5		11-Dec-07		16:06:20		69.8		34.5		11-Dec-07		16:07:53		71		35		21-Jan-08		16:25:59		65.6		36

		11-Dec-07		18:07:10		72.21		31		11-Dec-07		18:06:20		69.8		31		11-Dec-07		18:07:53		71		34.5		21-Jan-08		18:25:59		65.6		35.5

		11-Dec-07		20:07:10		70.41		32.5		11-Dec-07		20:06:20		67.4		36		11-Dec-07		20:07:53		70.41		33.5		21-Jan-08		20:25:59		65.01		36

		11-Dec-07		22:07:10		69.2		27		11-Dec-07		22:06:20		66.81		26.5		11-Dec-07		22:07:53		68		31		21-Jan-08		22:25:59		63.8		36.5

		12-Dec-07		0:07:10		68.61		25		12-Dec-07		0:06:20		66.81		24		12-Dec-07		0:07:53		66.81		29		22-Jan-08		0:25:59		63.21		36

		12-Dec-07		2:07:10		68		22		12-Dec-07		2:06:20		66.81		20		12-Dec-07		2:07:53		66.2		26		22-Jan-08		2:25:59		63.21		35

		12-Dec-07		4:07:10		67.4		19.5		12-Dec-07		4:06:20		66.2		17		12-Dec-07		4:07:53		65.6		23.5		22-Jan-08		4:25:59		62.6		33.5

		12-Dec-07		6:07:10		67.4		18.5		12-Dec-07		6:06:20		66.2		16.5		12-Dec-07		6:07:53		65.01		22.5		22-Jan-08		6:25:59		64.4		32.5

		12-Dec-07		8:07:10		69.8		17.5		12-Dec-07		8:06:20		68		16		12-Dec-07		8:07:53		68		20.5		22-Jan-08		8:25:59		66.81		31

		12-Dec-07		10:07:10		71.6		19.5		12-Dec-07		10:06:20		70.41		20		12-Dec-07		10:07:53		71		22		22-Jan-08		10:25:59		69.8		31.5

		12-Dec-07		12:07:10		72.21		18.5		12-Dec-07		12:06:20		71		18		12-Dec-07		12:07:53		71		22.5		22-Jan-08		12:25:59		74.6		30.5

		12-Dec-07		14:07:10		72.21		17.5		12-Dec-07		14:06:20		71		18.5		12-Dec-07		14:07:53		71.6		23		22-Jan-08		14:25:59		72.8		34

		12-Dec-07		16:07:10		72.21		17		12-Dec-07		16:06:20		71		19		12-Dec-07		16:07:53		70.41		22		22-Jan-08		16:25:59		73.4		34.5

		12-Dec-07		18:07:10		72.21		19		12-Dec-07		18:06:20		69.2		19		12-Dec-07		18:07:53		70.41		23.5		22-Jan-08		18:25:59		73.4		33.5

		12-Dec-07		20:07:10		70.41		22		12-Dec-07		20:06:20		67.4		24		12-Dec-07		20:07:53		69.8		24		22-Jan-08		20:25:59		72.21		34

		12-Dec-07		22:07:10		69.2		22.5		12-Dec-07		22:06:20		66.81		26		12-Dec-07		22:07:53		68.61		25		22-Jan-08		22:25:59		67.4		36

		13-Dec-07		0:07:10		68.61		23		13-Dec-07		0:06:20		66.2		26		13-Dec-07		0:07:53		66.81		25.5		23-Jan-08		0:25:59		65.6		37.5

		13-Dec-07		2:07:10		67.4		23		13-Dec-07		2:06:20		66.2		26		13-Dec-07		2:07:53		65.01		26.5		23-Jan-08		2:25:59		64.4		38

		13-Dec-07		4:07:10		66.81		23.5		13-Dec-07		4:06:20		66.2		25.5		13-Dec-07		4:07:53		63.8		27.5		23-Jan-08		4:25:59		63.8		38

		13-Dec-07		6:07:10		67.4		24.5		13-Dec-07		6:06:20		66.2		27		13-Dec-07		6:07:53		67.4		25.5		23-Jan-08		6:25:59		66.2		37.5

		13-Dec-07		8:07:10		70.41		24.5		13-Dec-07		8:06:20		68		27		13-Dec-07		8:07:53		68.61		26.5		23-Jan-08		8:25:59		68.61		34.5

		13-Dec-07		10:07:10		71.6		25		13-Dec-07		10:06:20		70.41		27.5		13-Dec-07		10:07:53		70.41		27.5		23-Jan-08		10:25:59		72.21		33

		13-Dec-07		12:07:10		72.21		26.5		13-Dec-07		12:06:20		71		28.5		13-Dec-07		12:07:53		70.41		30		23-Jan-08		12:25:59		74.01		31.5

		13-Dec-07		14:07:10		72.21		25.5		13-Dec-07		14:06:20		71		27		13-Dec-07		14:07:53		70.41		30.5		23-Jan-08		14:25:59		72.8		31.5

		13-Dec-07		16:07:10		72.21		22.5		13-Dec-07		16:06:20		71		23.5		13-Dec-07		16:07:53		70.41		28		23-Jan-08		16:25:59		72.21		31.5

		13-Dec-07		18:07:10		72.8		23.5		13-Dec-07		18:06:20		69.8		24		13-Dec-07		18:07:53		69.8		27.5		23-Jan-08		18:25:59		72.8		30.5

		13-Dec-07		20:07:10		70.41		25.5		13-Dec-07		20:06:20		67.4		28.5		13-Dec-07		20:07:53		69.2		28		23-Jan-08		20:25:59		72.8		30

		13-Dec-07		22:07:10		69.2		25.5		13-Dec-07		22:06:20		66.81		29		13-Dec-07		22:07:53		68		28.5		23-Jan-08		22:25:59		68		32

		14-Dec-07		0:07:10		68		26		14-Dec-07		0:06:20		66.2		29		14-Dec-07		0:07:53		66.2		29		24-Jan-08		0:25:59		65.6		33

		14-Dec-07		2:07:10		67.4		26.5		14-Dec-07		2:06:20		66.2		29		14-Dec-07		2:07:53		64.4		30		24-Jan-08		2:25:59		64.4		34

		14-Dec-07		4:07:10		66.81		26		14-Dec-07		4:06:20		66.2		28.5		14-Dec-07		4:07:53		63.21		30.5		24-Jan-08		4:25:59		63.8		35

		14-Dec-07		6:07:10		66.81		25.5		14-Dec-07		6:06:20		66.2		27		14-Dec-07		6:07:53		66.2		27		24-Jan-08		6:25:59		65.6		36

		14-Dec-07		8:07:10		69.2		24		14-Dec-07		8:06:20		67.4		26		14-Dec-07		8:07:53		68.61		26.5		24-Jan-08		8:25:59		68		34.5

		14-Dec-07		10:07:10		69.8		26		14-Dec-07		10:06:20		69.8		28		14-Dec-07		10:07:53		69.8		27.5		24-Jan-08		10:25:59		71.6		34.5

		14-Dec-07		12:07:10		71		28		14-Dec-07		12:06:20		70.41		30.5		14-Dec-07		12:07:53		71.6		28.5		24-Jan-08		12:25:59		74.01		33.5

		14-Dec-07		14:07:10		71.6		28		14-Dec-07		14:06:20		71		29.5		14-Dec-07		14:07:53		71		28.5		24-Jan-08		14:25:59		71.6		35

		14-Dec-07		16:07:10		72.21		29		14-Dec-07		16:06:20		71.6		30		14-Dec-07		16:07:53		69.8		32		24-Jan-08		16:25:59		72.21		34.5

		14-Dec-07		18:07:10		73.4		30		14-Dec-07		18:06:20		69.8		33		14-Dec-07		18:07:53		70.41		33.5		24-Jan-08		18:25:59		72.21		33.5

		14-Dec-07		20:07:10		71		30.5		14-Dec-07		20:06:20		69.2		33		14-Dec-07		20:07:53		69.2		32		24-Jan-08		20:25:59		72.21		33.5

		14-Dec-07		22:07:10		69.2		29.5		14-Dec-07		22:06:20		66.81		32.5		14-Dec-07		22:07:53		68		31.5		24-Jan-08		22:25:59		68		36

		15-Dec-07		0:07:10		68		29		15-Dec-07		0:06:20		66.2		32		15-Dec-07		0:07:53		65.6		32		25-Jan-08		0:25:59		65.6		36.5

		15-Dec-07		2:07:10		67.4		28		15-Dec-07		2:06:20		66.2		30.5		15-Dec-07		2:07:53		63.8		32		25-Jan-08		2:25:59		65.01		37.5

		15-Dec-07		4:07:10		66.81		27		15-Dec-07		4:06:20		65.6		29		15-Dec-07		4:07:53		63.21		31.5		25-Jan-08		4:25:59		64.4		38.5

		15-Dec-07		6:07:10		66.81		27		15-Dec-07		6:06:20		66.2		28.5		15-Dec-07		6:07:53		67.4		27.5		25-Jan-08		6:25:59		66.2		38

		15-Dec-07		8:07:10		68.61		25		15-Dec-07		8:06:20		67.4		26		15-Dec-07		8:07:53		68.61		27		25-Jan-08		8:25:59		69.2		36

		15-Dec-07		10:07:10		70.41		27		15-Dec-07		10:06:20		69.8		28.5		15-Dec-07		10:07:53		70.41		28.5		25-Jan-08		10:25:59		72.8		36

		15-Dec-07		12:07:10		71.6		29.5		15-Dec-07		12:06:20		71		29.5		15-Dec-07		12:07:53		71.6		30		25-Jan-08		12:25:59		74.01		34.5

		15-Dec-07		14:07:10		71.6		30.5		15-Dec-07		14:06:20		71		31.5		15-Dec-07		14:07:53		70.41		30		25-Jan-08		14:25:59		73.4		35

		15-Dec-07		16:07:10		71.6		30.5		15-Dec-07		16:06:20		71		31.5		15-Dec-07		16:07:53		71		32.5		25-Jan-08		16:25:59		74.01		35.5

		15-Dec-07		18:07:10		72.8		33		15-Dec-07		18:06:20		69.8		37		15-Dec-07		18:07:53		70.41		35.5		25-Jan-08		18:25:59		72.8		35

		15-Dec-07		20:07:10		71		34.5		15-Dec-07		20:06:20		67.4		39		15-Dec-07		20:07:53		69.2		35.5		25-Jan-08		20:25:59		72.21		34

		15-Dec-07		22:07:10		69.2		33.5		15-Dec-07		22:06:20		66.81		37.5		15-Dec-07		22:07:53		67.4		35.5		25-Jan-08		22:25:59		69.2		36

		16-Dec-07		0:07:10		68.61		34		16-Dec-07		0:06:20		66.2		38		16-Dec-07		0:07:53		66.2		36.5		26-Jan-08		0:25:59		67.4		36.5

		16-Dec-07		2:07:10		68		34		16-Dec-07		2:06:20		66.2		38		16-Dec-07		2:07:53		65.6		37.5		26-Jan-08		2:25:59		66.2		37

		16-Dec-07		4:07:10		68		35		16-Dec-07		4:06:20		66.2		39		16-Dec-07		4:07:53		65.01		38.5		26-Jan-08		4:25:59		65.6		37

		16-Dec-07		6:07:10		67.4		35		16-Dec-07		6:06:20		66.2		38		16-Dec-07		6:07:53		64.4		39		26-Jan-08		6:25:59		66.81		37

		16-Dec-07		8:07:10		68		34		16-Dec-07		8:06:20		67.4		36.5		16-Dec-07		8:07:53		66.81		37		26-Jan-08		8:25:59		70.41		37

		16-Dec-07		10:07:10		68		34.5		16-Dec-07		10:06:20		67.4		36.5		16-Dec-07		10:07:53		66.81		36		26-Jan-08		10:25:59		73.4		38

		16-Dec-07		12:07:10		68		35		16-Dec-07		12:06:20		68		37		16-Dec-07		12:07:53		67.4		36.5		26-Jan-08		12:25:59		72.8		39

		16-Dec-07		14:07:10		68.61		37		16-Dec-07		14:06:20		68		39.5		16-Dec-07		14:07:53		66.81		39		26-Jan-08		14:25:59		73.4		39.5

		16-Dec-07		16:07:10		69.2		39		16-Dec-07		16:06:20		68		42.5		16-Dec-07		16:07:53		67.4		41.5		26-Jan-08		16:25:59		73.4		39.5

		16-Dec-07		18:07:10		69.2		40.5		16-Dec-07		18:06:20		68		44		16-Dec-07		18:07:53		68		42.5		26-Jan-08		18:25:59		73.4		40

		16-Dec-07		20:07:10		68.61		40.5		16-Dec-07		20:06:20		66.81		44		16-Dec-07		20:07:53		67.4		42		26-Jan-08		20:25:59		72.8		41

		16-Dec-07		22:07:10		68		40.5		16-Dec-07		22:06:20		66.81		44		16-Dec-07		22:07:53		66.2		43		26-Jan-08		22:25:59		69.8		43

		17-Dec-07		0:07:10		68		41		17-Dec-07		0:06:20		66.2		44.5		17-Dec-07		0:07:53		66.2		43.5		27-Jan-08		0:25:59		68		44

		17-Dec-07		2:07:10		67.4		41		17-Dec-07		2:06:20		66.2		44.5		17-Dec-07		2:07:53		65.6		44		27-Jan-08		2:25:59		67.4		45.5

		17-Dec-07		4:07:10		67.4		40.5		17-Dec-07		4:06:20		66.2		44.5		17-Dec-07		4:07:53		65.01		44		27-Jan-08		4:25:59		66.81		46.5

		17-Dec-07		6:07:10		66.81		40.5		17-Dec-07		6:06:20		66.2		43.5		17-Dec-07		6:07:53		65.01		43.5		27-Jan-08		6:25:59		66.2		47

		17-Dec-07		8:07:10		68		40		17-Dec-07		8:06:20		67.4		42.5		17-Dec-07		8:07:53		66.81		41.5		27-Jan-08		8:25:59		66.2		46.5

		17-Dec-07		10:07:10		68		40.5		17-Dec-07		10:06:20		67.4		43		17-Dec-07		10:07:53		67.4		42		27-Jan-08		10:25:59		66.2		45.5

		17-Dec-07		12:07:10		68		40.5		17-Dec-07		12:06:20		67.4		42.5		17-Dec-07		12:07:53		67.4		42.5		27-Jan-08		12:25:59		66.81		45

		17-Dec-07		14:07:10		68.61		37		17-Dec-07		14:06:20		68		37		17-Dec-07		14:07:53		67.4		40		27-Jan-08		14:25:59		67.4		46

		17-Dec-07		16:07:10		68.61		37.5		17-Dec-07		16:06:20		67.4		39.5		17-Dec-07		16:07:53		67.4		40.5		27-Jan-08		16:25:59		68		45.5

		17-Dec-07		18:07:10		68.61		38		17-Dec-07		18:06:20		68		39.5		17-Dec-07		18:07:53		67.4		40		27-Jan-08		18:25:59		67.4		44.5

		17-Dec-07		20:07:10		68		40		17-Dec-07		20:06:20		66.81		43.5		17-Dec-07		20:07:53		66.81		42		27-Jan-08		20:25:59		66.81		44

		17-Dec-07		22:07:10		68		42.5		17-Dec-07		22:06:20		66.2		47		17-Dec-07		22:07:53		65.6		45		27-Jan-08		22:25:59		66.2		44

		18-Dec-07		0:07:10		67.4		43.5		18-Dec-07		0:06:20		66.2		48.5		18-Dec-07		0:07:53		65.6		46.5		28-Jan-08		0:25:59		66.2		44.5

		18-Dec-07		2:07:10		67.4		43.5		18-Dec-07		2:06:20		66.81		46.5		18-Dec-07		2:07:53		65.6		46.5		28-Jan-08		2:25:59		66.2		46

		18-Dec-07		4:07:10		67.4		42		18-Dec-07		4:06:20		66.2		44.5		18-Dec-07		4:07:53		65.01		45.5		28-Jan-08		4:25:59		65.6		46.5

		18-Dec-07		6:07:10		67.4		43		18-Dec-07		6:06:20		66.2		46		18-Dec-07		6:07:53		66.81		43.5		28-Jan-08		6:25:59		65.6		47

		18-Dec-07		8:07:10		69.8		41		18-Dec-07		8:06:20		68		44.5		18-Dec-07		8:07:53		69.2		43		28-Jan-08		8:25:59		65.6		47.5

		18-Dec-07		10:07:10		71		42		18-Dec-07		10:06:20		71		39		18-Dec-07		10:07:53		71.6		41.5		28-Jan-08		10:25:59		66.81		47.5

		18-Dec-07		12:07:10		71.6		41		18-Dec-07		12:06:20		71.6		43.5		18-Dec-07		12:07:53		71.6		43.5		28-Jan-08		12:25:59		68		47

		18-Dec-07		14:07:10		71.6		41		18-Dec-07		14:06:20		71		45		18-Dec-07		14:07:53		71		45.5		28-Jan-08		14:25:59		68.61		46.5

		18-Dec-07		16:07:10		72.21		44		18-Dec-07		16:06:20		71		39.5		18-Dec-07		16:07:53		71		46		28-Jan-08		16:25:59		68.61		46.5

		18-Dec-07		18:07:10		72.21		42		18-Dec-07		18:06:20		69.2		45		18-Dec-07		18:07:53		71.6		40.5		28-Jan-08		18:25:59		69.2		46.5

		18-Dec-07		20:07:10		71		41.5		18-Dec-07		20:06:20		68		45		18-Dec-07		20:07:53		70.41		42.5		28-Jan-08		20:25:59		67.4		47.5

		18-Dec-07		22:07:10		69.8		43		18-Dec-07		22:06:20		66.81		48.5		18-Dec-07		22:07:53		68.61		44.5		28-Jan-08		22:25:59		66.2		46

		19-Dec-07		0:07:10		69.2		44		19-Dec-07		0:06:20		66.81		48.5		19-Dec-07		0:07:53		68		45.5		29-Jan-08		0:25:59		65.01		42.5

		19-Dec-07		2:07:10		68.61		44.5		19-Dec-07		2:06:20		66.81		49		19-Dec-07		2:07:53		67.4		46.5		29-Jan-08		2:25:59		64.4		41

		19-Dec-07		4:07:10		68.61		44.5		19-Dec-07		4:06:20		66.81		48.5		19-Dec-07		4:07:53		66.81		47.5		29-Jan-08		4:25:59		64.4		40.5

		19-Dec-07		6:07:10		68		45		19-Dec-07		6:06:20		66.81		48.5		19-Dec-07		6:07:53		68		46		29-Jan-08		6:25:59		66.2		39

		19-Dec-07		8:07:10		70.41		43		19-Dec-07		8:06:20		68.61		46		19-Dec-07		8:07:53		69.8		44.5		29-Jan-08		8:25:59		68.61		37

		19-Dec-07		10:07:10		71.6		42		19-Dec-07		10:06:20		71		48.5		19-Dec-07		10:07:53		71		43.5		29-Jan-08		10:25:59		73.4		35.5

		19-Dec-07		12:07:10		72.21		44		19-Dec-07		12:06:20		71.6		49.5		19-Dec-07		12:07:53		70.41		50		29-Jan-08		12:25:59		71		37

		19-Dec-07		14:07:10		72.21		45.5		19-Dec-07		14:06:20		71		53.5		19-Dec-07		14:07:53		69.8		49.5		29-Jan-08		14:25:59		71.6		36

		19-Dec-07		16:07:10		72.8		45.5		19-Dec-07		16:06:20		71		47		19-Dec-07		16:07:53		70.41		47		29-Jan-08		16:25:59		72.8		35.5

		19-Dec-07		18:07:10		72.21		41.5		19-Dec-07		18:06:20		69.2		44		19-Dec-07		18:07:53		69.8		44.5		29-Jan-08		18:25:59		72.21		35.5

		19-Dec-07		20:07:10		71		41		19-Dec-07		20:06:20		67.4		44.5		19-Dec-07		20:07:53		69.2		43		29-Jan-08		20:25:59		72.21		33.5

		19-Dec-07		22:07:10		69.8		39		19-Dec-07		22:06:20		66.81		42		19-Dec-07		22:07:53		68		42		29-Jan-08		22:25:59		68		36

		20-Dec-07		0:07:10		68.61		38.5		20-Dec-07		0:06:20		66.2		42		20-Dec-07		0:07:53		66.2		42		30-Jan-08		0:25:59		66.2		36

		20-Dec-07		2:07:10		68.61		39		20-Dec-07		2:06:20		66.2		43		20-Dec-07		2:07:53		65.6		43		30-Jan-08		2:25:59		65.01		36

		20-Dec-07		4:07:10		68		40		20-Dec-07		4:06:20		66.2		43.5		20-Dec-07		4:07:53		65.01		44		30-Jan-08		4:25:59		63.8		35

		20-Dec-07		6:07:10		68		40		20-Dec-07		6:06:20		66.2		43.5		20-Dec-07		6:07:53		67.4		41.5		30-Jan-08		6:25:59		66.2		34

		20-Dec-07		8:07:10		70.41		39		20-Dec-07		8:06:20		68		42.5		20-Dec-07		8:07:53		69.8		41		30-Jan-08		8:25:59		69.2		33

		20-Dec-07		10:07:10		72.21		39		20-Dec-07		10:06:20		70.41		42		20-Dec-07		10:07:53		71.6		39.5		30-Jan-08		10:25:59		72.8		33.5

		20-Dec-07		12:07:10		72.21		41		20-Dec-07		12:06:20		71		45.5		20-Dec-07		12:07:53		71.6		43		30-Jan-08		12:25:59		73.4		34

		20-Dec-07		14:07:10		72.8		39.5		20-Dec-07		14:06:20		70.41		47.5		20-Dec-07		14:07:53		71.6		42		30-Jan-08		14:25:59		72.8		37.5

		20-Dec-07		16:07:10		72.21		43		20-Dec-07		16:06:20		70.41		43		20-Dec-07		16:07:53		70.41		46		30-Jan-08		16:25:59		72.8		39.5

		20-Dec-07		18:07:10		72.8		41.5		20-Dec-07		18:06:20		69.2		45.5		20-Dec-07		18:07:53		70.41		44.5		30-Jan-08		18:25:59		72.21		37.5

		20-Dec-07		20:07:10		71.6		42.5		20-Dec-07		20:06:20		68.61		47.5		20-Dec-07		20:07:53		69.8		45		30-Jan-08		20:25:59		72.21		34.5

		20-Dec-07		22:07:10		70.41		44.5		20-Dec-07		22:06:20		68		49.5		20-Dec-07		22:07:53		69.2		46.5		30-Jan-08		22:25:59		69.2		36

		21-Dec-07		0:07:10		69.8		46		21-Dec-07		0:06:20		67.4		51.5		21-Dec-07		0:07:53		68		47.5		31-Jan-08		0:25:59		67.4		36.5

		21-Dec-07		2:07:10		69.2		46		21-Dec-07		2:06:20		67.4		51		21-Dec-07		2:07:53		68		49		31-Jan-08		2:25:59		66.2		36.5

		21-Dec-07		4:07:10		69.2		46.5		21-Dec-07		4:06:20		66.81		51.5		21-Dec-07		4:07:53		67.4		49		31-Jan-08		4:25:59		65.6		37

		21-Dec-07		6:07:10		68.61		44.5		21-Dec-07		6:06:20		66.81		47		21-Dec-07		6:07:53		67.4		47		31-Jan-08		6:25:59		66.81		36

		21-Dec-07		8:07:10		71		38.5		21-Dec-07		8:06:20		68		39		21-Dec-07		8:07:53		69.8		42		31-Jan-08		8:25:59		70.41		34.5

		21-Dec-07		10:07:10		71.6		38.5		21-Dec-07		10:06:20		69.8		38		21-Dec-07		10:07:53		71.6		39.5		31-Jan-08		10:25:59		74.01		34

		21-Dec-07		12:07:10		72.21		37		21-Dec-07		12:06:20		69.8		38.5		21-Dec-07		12:07:53		71		40		31-Jan-08		12:25:59		71		36

		21-Dec-07		14:07:10		72.21		35.5		21-Dec-07		14:06:20		70.41		35		21-Dec-07		14:07:53		71		40.5		31-Jan-08		14:25:59		72.21		35.5

		21-Dec-07		16:07:10		72.21		33		21-Dec-07		16:06:20		70.41		32.5		21-Dec-07		16:07:53		71		35.5		31-Jan-08		16:25:59		72.21		35

		21-Dec-07		18:07:10		71.6		31.5		21-Dec-07		18:06:20		69.2		30.5		21-Dec-07		18:07:53		70.41		34		31-Jan-08		18:25:59		72.21		35.5

		21-Dec-07		20:07:10		69.8		32		21-Dec-07		20:06:20		67.4		34		21-Dec-07		20:07:53		69.2		33.5		31-Jan-08		20:25:59		72.21		35.5

		21-Dec-07		22:07:10		69.2		32		21-Dec-07		22:06:20		66.81		34		21-Dec-07		22:07:53		67.4		34.5		31-Jan-08		22:25:59		69.2		38

		22-Dec-07		0:07:10		68.61		31.5		22-Dec-07		0:06:20		66.2		33.5		22-Dec-07		0:07:53		65.6		35		1-Feb-08		0:25:59		67.4		38.5

		22-Dec-07		2:07:10		68		31		22-Dec-07		2:06:20		66.2		33		22-Dec-07		2:07:53		64.4		35		1-Feb-08		2:25:59		66.2		39

		22-Dec-07		4:07:10		67.4		30		22-Dec-07		4:06:20		66.2		31.5		22-Dec-07		4:07:53		63.21		35		1-Feb-08		4:25:59		65.6		40

		22-Dec-07		6:07:10		67.4		29.5		22-Dec-07		6:06:20		66.2		30.5		22-Dec-07		6:07:53		66.2		31.5		1-Feb-08		6:25:59		66.81		40

		22-Dec-07		8:07:10		69.2		28		22-Dec-07		8:06:20		69.2		29		22-Dec-07		8:07:53		68.61		31.5		1-Feb-08		8:25:59		70.41		39

		22-Dec-07		10:07:10		71		28		22-Dec-07		10:06:20		70.41		30		22-Dec-07		10:07:53		70.41		31		1-Feb-08		10:25:59		73.4		40

		22-Dec-07		12:07:10		71		28.5		22-Dec-07		12:06:20		70.41		29.5		22-Dec-07		12:07:53		71.6		28.5		1-Feb-08		12:25:59		72.21		41

		22-Dec-07		14:07:10		71		26.5		22-Dec-07		14:06:20		69.2		26		22-Dec-07		14:07:53		69.8		30		1-Feb-08		14:25:59		72.8		42.5

		22-Dec-07		16:07:10		71		26.5		22-Dec-07		16:06:20		69.2		26		22-Dec-07		16:07:53		69.2		29.5		1-Feb-08		16:25:59		72.8		44

		22-Dec-07		18:07:10		70.41		26.5		22-Dec-07		18:06:20		69.2		26		22-Dec-07		18:07:53		69.2		29.5		1-Feb-08		18:25:59		72.21		45.5

		22-Dec-07		20:07:10		69.8		28		22-Dec-07		20:06:20		66.81		31		22-Dec-07		20:07:53		68		31.5		1-Feb-08		20:25:59		72.8		41

		22-Dec-07		22:07:10		68.61		28.5		22-Dec-07		22:06:20		66.2		31		22-Dec-07		22:07:53		66.2		31.5		1-Feb-08		22:25:59		69.8		42

		23-Dec-07		0:07:10		68		28		23-Dec-07		0:06:20		65.6		31		23-Dec-07		0:07:53		64.4		31.5		2-Feb-08		0:25:59		67.4		41.5

		23-Dec-07		2:07:10		66.81		27.5		23-Dec-07		2:06:20		65.6		30		23-Dec-07		2:07:53		63.21		32		2-Feb-08		2:25:59		65.6		40.5

		23-Dec-07		4:07:10		66.81		27		23-Dec-07		4:06:20		65.6		29.5		23-Dec-07		4:07:53		62		31.5		2-Feb-08		4:25:59		64.4		39.5

		23-Dec-07		6:07:10		66.2		26.5		23-Dec-07		6:06:20		65.6		28		23-Dec-07		6:07:53		61.41		31.5		2-Feb-08		6:25:59		65.6		37

		23-Dec-07		8:07:10		66.81		26.5		23-Dec-07		8:06:20		66.81		28		23-Dec-07		8:07:53		67.4		28		2-Feb-08		8:25:59		68		34.5

		23-Dec-07		10:07:10		67.4		28		23-Dec-07		10:06:20		67.4		29.5		23-Dec-07		10:07:53		68		28		2-Feb-08		10:25:59		71		38.5

		23-Dec-07		12:07:10		67.4		30		23-Dec-07		12:06:20		67.4		31.5		23-Dec-07		12:07:53		68		30.5		2-Feb-08		12:25:59		71.6		37

		23-Dec-07		14:07:10		68		29.5		23-Dec-07		14:06:20		67.4		30.5		23-Dec-07		14:07:53		68		31		2-Feb-08		14:25:59		71.6		39

		23-Dec-07		16:07:10		68		29.5		23-Dec-07		16:06:20		68		30.5		23-Dec-07		16:07:53		68		31.5		2-Feb-08		16:25:59		71.6		39

		23-Dec-07		18:07:10		68.61		29.5		23-Dec-07		18:06:20		67.4		30		23-Dec-07		18:07:53		68		31.5		2-Feb-08		18:25:59		71.6		39

		23-Dec-07		20:07:10		68		31.5		23-Dec-07		20:06:20		66.2		34		23-Dec-07		20:07:53		68.61		31.5		2-Feb-08		20:25:59		71.6		38.5

		23-Dec-07		22:07:10		67.4		32		23-Dec-07		22:06:20		66.2		34.5		23-Dec-07		22:07:53		68.61		32		2-Feb-08		22:25:59		68.61		39.5

		24-Dec-07		0:07:10		66.81		32		24-Dec-07		0:06:20		65.6		34.5		24-Dec-07		0:07:53		68.61		31.5		3-Feb-08		0:25:59		66.81		40.5

		24-Dec-07		2:07:10		66.81		31.5		24-Dec-07		2:06:20		66.2		33.5		24-Dec-07		2:07:53		68.61		31.5		3-Feb-08		2:25:59		66.2		41

		24-Dec-07		4:07:10		66.81		31.5		24-Dec-07		4:06:20		65.6		34		24-Dec-07		4:07:53		68.61		31.5		3-Feb-08		4:25:59		65.6		42

		24-Dec-07		6:07:10		66.81		31.5		24-Dec-07		6:06:20		65.6		33		24-Dec-07		6:07:53		68		31		3-Feb-08		6:25:59		65.01		42.5

		24-Dec-07		8:07:10		67.4		31		24-Dec-07		8:06:20		67.4		32		24-Dec-07		8:07:53		69.2		30.5		3-Feb-08		8:25:59		65.01		43

		24-Dec-07		10:07:10		67.4		32		24-Dec-07		10:06:20		67.4		33.5		24-Dec-07		10:07:53		69.2		31		3-Feb-08		10:25:59		66.2		43

		24-Dec-07		12:07:10		68		32.5		24-Dec-07		12:06:20		67.4		33.5		24-Dec-07		12:07:53		68.61		32		3-Feb-08		12:25:59		66.81		45

		24-Dec-07		14:07:10		68.61		36		24-Dec-07		14:06:20		68		38.5		24-Dec-07		14:07:53		69.2		35.5		3-Feb-08		14:25:59		67.4		46

		24-Dec-07		16:07:10		69.2		40		24-Dec-07		16:06:20		68.61		44		24-Dec-07		16:07:53		69.8		39.5		3-Feb-08		16:25:59		67.4		48.5

		24-Dec-07		18:07:10		69.8		43		24-Dec-07		18:06:20		68.61		48		24-Dec-07		18:07:53		69.8		43		3-Feb-08		18:25:59		66.81		50.5

		24-Dec-07		20:07:10		68.61		43		24-Dec-07		20:06:20		66.81		47.5		24-Dec-07		20:07:53		69.2		42.5		3-Feb-08		20:25:59		66.81		50

		24-Dec-07		22:07:10		68		41.5		24-Dec-07		22:06:20		66.2		46		24-Dec-07		22:07:53		69.8		40.5		3-Feb-08		22:25:59		66.2		51.5

		25-Dec-07		0:07:10		68		41.5		25-Dec-07		0:06:20		66.2		45		25-Dec-07		0:07:53		69.8		40		4-Feb-08		0:25:59		66.2		52.5

		25-Dec-07		2:07:10		67.4		40.5		25-Dec-07		2:06:20		66.2		44.5		25-Dec-07		2:07:53		69.8		39		4-Feb-08		2:25:59		66.2		51.5

		25-Dec-07		4:07:10		67.4		40.5		25-Dec-07		4:06:20		66.2		43.5		25-Dec-07		4:07:53		69.8		38		4-Feb-08		4:25:59		65.6		49.5

		25-Dec-07		6:07:10		67.4		39.5		25-Dec-07		6:06:20		66.2		42		25-Dec-07		6:07:53		69.8		37		4-Feb-08		6:25:59		65.6		48.5

		25-Dec-07		8:07:10		69.2		37.5		25-Dec-07		8:06:20		67.4		40		25-Dec-07		8:07:53		69.2		38		4-Feb-08		8:25:59		65.6		47

		25-Dec-07		10:07:10		69.8		33.5		25-Dec-07		10:06:20		68		34.5		25-Dec-07		10:07:53		68.61		35		4-Feb-08		10:25:59		66.2		46

		25-Dec-07		12:07:10		71		31.5		25-Dec-07		12:06:20		69.2		31		25-Dec-07		12:07:53		69.2		33.5		4-Feb-08		12:25:59		66.81		46.5

		25-Dec-07		14:07:10		70.41		30		25-Dec-07		14:06:20		69.2		28		25-Dec-07		14:07:53		69.8		31.5		4-Feb-08		14:25:59		67.4		46

		25-Dec-07		16:07:10		70.41		27.5		25-Dec-07		16:06:20		68.61		26		25-Dec-07		16:07:53		70.41		30.5		4-Feb-08		16:25:59		67.4		45.5

		25-Dec-07		18:07:10		70.41		29.5		25-Dec-07		18:06:20		68.61		29		25-Dec-07		18:07:53		70.41		30.5		4-Feb-08		18:25:59		67.4		45

		25-Dec-07		20:07:10		69.2		32		25-Dec-07		20:06:20		66.81		34.5		25-Dec-07		20:07:53		69.2		33		4-Feb-08		20:25:59		66.2		45

		25-Dec-07		22:07:10		68		30		25-Dec-07		22:06:20		66.2		31.5		25-Dec-07		22:07:53		67.4		32		4-Feb-08		22:25:59		65.6		45

		26-Dec-07		0:07:10		67.4		29.5		26-Dec-07		0:06:20		65.6		31		26-Dec-07		0:07:53		65.6		31.5		5-Feb-08		0:25:59		65.6		44.5

		26-Dec-07		2:07:10		66.81		28.5		26-Dec-07		2:06:20		65.6		30		26-Dec-07		2:07:53		64.4		31.5		5-Feb-08		2:25:59		65.01		44.5

		26-Dec-07		4:07:10		66.2		28		26-Dec-07		4:06:20		65.6		29.5		26-Dec-07		4:07:53		62.6		31		5-Feb-08		4:25:59		65.01		44

		26-Dec-07		6:07:10		66.2		27.5		26-Dec-07		6:06:20		65.6		29		26-Dec-07		6:07:53		66.81		28.5		5-Feb-08		6:25:59		66.2		42.5

		26-Dec-07		8:07:10		66.81		26.5		26-Dec-07		8:06:20		66.81		27		26-Dec-07		8:07:53		68		27.5		5-Feb-08		8:25:59		69.8		39.5

		26-Dec-07		10:07:10		67.4		26.5		26-Dec-07		10:06:20		67.4		27.5		26-Dec-07		10:07:53		68.61		27.5		5-Feb-08		10:25:59		72.8		37.5

		26-Dec-07		12:07:10		67.4		27.5		26-Dec-07		12:06:20		67.4		28		26-Dec-07		12:07:53		68.61		28.5		5-Feb-08		12:25:59		71.6		37.5

		26-Dec-07		14:07:10		68		28		26-Dec-07		14:06:20		68		28		26-Dec-07		14:07:53		68.61		29.5		5-Feb-08		14:25:59		71.6		36

		26-Dec-07		16:07:10		68.61		29.5		26-Dec-07		16:06:20		68		30.5		26-Dec-07		16:07:53		68.61		31		5-Feb-08		16:25:59		72.8		34.5

		26-Dec-07		18:07:10		68.61		32.5		26-Dec-07		18:06:20		68		35		26-Dec-07		18:07:53		68.61		34		5-Feb-08		18:25:59		72.8		34.5

		26-Dec-07		20:07:10		68		33.5		26-Dec-07		20:06:20		66.81		36		26-Dec-07		20:07:53		69.2		34		5-Feb-08		20:25:59		72.21		34

		26-Dec-07		22:07:10		67.4		34		26-Dec-07		22:06:20		66.2		36.5		26-Dec-07		22:07:53		67.4		34.5		5-Feb-08		22:25:59		69.2		36

		27-Dec-07		0:07:10		66.81		34.5		27-Dec-07		0:06:20		66.2		38		27-Dec-07		0:07:53		66.2		36		6-Feb-08		0:25:59		67.4		37

		27-Dec-07		2:07:10		66.81		34		27-Dec-07		2:06:20		66.2		36		27-Dec-07		2:07:53		65.01		36		6-Feb-08		2:25:59		66.2		38

		27-Dec-07		4:07:10		66.2		32.5		27-Dec-07		4:06:20		65.6		34		27-Dec-07		4:07:53		63.8		35		6-Feb-08		4:25:59		65.6		38

		27-Dec-07		6:07:10		66.2		31.5		27-Dec-07		6:06:20		65.6		32.5		27-Dec-07		6:07:53		68		31.5		6-Feb-08		6:25:59		66.81		39.5

		27-Dec-07		8:07:10		68		30		27-Dec-07		8:06:20		67.4		31		27-Dec-07		8:07:53		70.41		30.5		6-Feb-08		8:25:59		70.41		36.5

		27-Dec-07		10:07:10		69.2		30.5		27-Dec-07		10:06:20		69.8		31.5		27-Dec-07		10:07:53		71		30.5		6-Feb-08		10:25:59		72.8		35.5

		27-Dec-07		12:07:10		71		28.5		27-Dec-07		12:06:20		70.41		28.5		27-Dec-07		12:07:53		71		29		6-Feb-08		12:25:59		71		37

		27-Dec-07		14:07:10		70.41		25.5		27-Dec-07		14:06:20		70.41		24.5		27-Dec-07		14:07:53		71		25.5		6-Feb-08		14:25:59		72.21		37

		27-Dec-07		16:07:10		71		22.5		27-Dec-07		16:06:20		71		22		27-Dec-07		16:07:53		69.8		24		6-Feb-08		16:25:59		72.8		34.5

		27-Dec-07		18:07:10		70.41		23		27-Dec-07		18:06:20		68.61		23.5		27-Dec-07		18:07:53		69.2		24.5		6-Feb-08		18:25:59		72.8		35

		27-Dec-07		20:07:10		69.8		24		27-Dec-07		20:06:20		66.81		26		27-Dec-07		20:07:53		68		26		6-Feb-08		20:25:59		72.8		37

		27-Dec-07		22:07:10		68		24		27-Dec-07		22:06:20		66.2		26		27-Dec-07		22:07:53		66.2		27		6-Feb-08		22:25:59		69.8		38

		28-Dec-07		0:07:10		67.4		24.5		28-Dec-07		0:06:20		65.6		26		28-Dec-07		0:07:53		65.01		27.5		7-Feb-08		0:25:59		68		38.5

		28-Dec-07		2:07:10		66.81		24		28-Dec-07		2:06:20		65.6		26		28-Dec-07		2:07:53		63.21		28		7-Feb-08		2:25:59		66.81		38.5

		28-Dec-07		4:07:10		66.2		24		28-Dec-07		4:06:20		65.6		25.5		28-Dec-07		4:07:53		62.6		28		7-Feb-08		4:25:59		66.2		38.5

		28-Dec-07		6:07:10		66.2		24.5		28-Dec-07		6:06:20		65.6		25.5		28-Dec-07		6:07:53		66.2		26		7-Feb-08		6:25:59		67.4		38.5

		28-Dec-07		8:07:10		68		23.5		28-Dec-07		8:06:20		67.4		24.5		28-Dec-07		8:07:53		68		25.5		7-Feb-08		8:25:59		71.6		38

		28-Dec-07		10:07:10		69.2		24		28-Dec-07		10:06:20		69.2		25.5		28-Dec-07		10:07:53		69.8		25		7-Feb-08		10:25:59		72.21		37.5

		28-Dec-07		12:07:10		70.41		25		28-Dec-07		12:06:20		70.41		26		28-Dec-07		12:07:53		71		26		7-Feb-08		12:25:59		71.6		40.5

		28-Dec-07		14:07:10		70.41		25.5		28-Dec-07		14:06:20		70.41		26		28-Dec-07		14:07:53		71		27		7-Feb-08		14:25:59		71.6		40

		28-Dec-07		16:07:10		71		26.5		28-Dec-07		16:06:20		70.41		27.5		28-Dec-07		16:07:53		71		25		7-Feb-08		16:25:59		72.8		38

		28-Dec-07		18:07:10		71		28.5		28-Dec-07		18:06:20		68.61		31.5		28-Dec-07		18:07:53		71		29.5		7-Feb-08		18:25:59		72.8		37.5

		28-Dec-07		20:07:10		71		31.5		28-Dec-07		20:06:20		66.81		37		28-Dec-07		20:07:53		69.8		32.5		7-Feb-08		20:25:59		72.21		36

		28-Dec-07		22:07:10		69.8		33		28-Dec-07		22:06:20		66.2		38.5		28-Dec-07		22:07:53		68		34.5		7-Feb-08		22:25:59		69.2		37.5

		29-Dec-07		0:07:10		68.61		34		29-Dec-07		0:06:20		66.2		39		29-Dec-07		0:07:53		66.81		36		8-Feb-08		0:25:59		67.4		38.5

		29-Dec-07		2:07:10		68		34		29-Dec-07		2:06:20		66.2		37.5		29-Dec-07		2:07:53		66.2		36.5		8-Feb-08		2:25:59		66.81		39

		29-Dec-07		4:07:10		67.4		34		29-Dec-07		4:06:20		66.2		38		29-Dec-07		4:07:53		65.01		37		8-Feb-08		4:25:59		65.6		39.5

		29-Dec-07		6:07:10		68		33.5		29-Dec-07		6:06:20		65.6		36.5		29-Dec-07		6:07:53		66.81		35.5		8-Feb-08		6:25:59		67.4		39.5

		29-Dec-07		8:07:10		69.8		32		29-Dec-07		8:06:20		68		34.5		29-Dec-07		8:07:53		68.61		35.5		8-Feb-08		8:25:59		71		37.5

		29-Dec-07		10:07:10		70.41		32		29-Dec-07		10:06:20		69.8		33		29-Dec-07		10:07:53		70.41		33.5		8-Feb-08		10:25:59		71.6		38

		29-Dec-07		12:07:10		72.21		33		29-Dec-07		12:06:20		70.41		35		29-Dec-07		12:07:53		71.6		34		8-Feb-08		12:25:59		71		39

		29-Dec-07		14:07:10		72.8		32.5		29-Dec-07		14:06:20		71		34		29-Dec-07		14:07:53		71.6		34		8-Feb-08		14:25:59		72.21		40

		29-Dec-07		16:07:10		72.8		32		29-Dec-07		16:06:20		71		35		29-Dec-07		16:07:53		70.41		34.5		8-Feb-08		16:25:59		73.4		41

		29-Dec-07		18:07:10		72.21		32		29-Dec-07		18:06:20		69.2		35		29-Dec-07		18:07:53		69.2		35.5		8-Feb-08		18:25:59		74.01		40

		29-Dec-07		20:07:10		71		33		29-Dec-07		20:06:20		67.4		37.5		29-Dec-07		20:07:53		68		36.5		8-Feb-08		20:25:59		72.21		40.5

		29-Dec-07		22:07:10		69.2		34		29-Dec-07		22:06:20		66.81		38.5		29-Dec-07		22:07:53		66.2		37.5		8-Feb-08		22:25:59		70.41		41.5

		30-Dec-07		0:07:10		68		34.5		30-Dec-07		0:06:20		66.2		38.5		30-Dec-07		0:07:53		65.01		38.5		9-Feb-08		0:25:59		69.2		41.5

		30-Dec-07		2:07:10		67.4		35.5		30-Dec-07		2:06:20		65.6		39		30-Dec-07		2:07:53		63.8		40		9-Feb-08		2:25:59		68		41

		30-Dec-07		4:07:10		67.4		36		30-Dec-07		4:06:20		66.2		39.5		30-Dec-07		4:07:53		63.8		41		9-Feb-08		4:25:59		66.2		40.5

		30-Dec-07		6:07:10		66.81		37		30-Dec-07		6:06:20		65.6		40.5		30-Dec-07		6:07:53		63.21		42		9-Feb-08		6:25:59		67.4		39.5

		30-Dec-07		8:07:10		67.4		37		30-Dec-07		8:06:20		67.4		39		30-Dec-07		8:07:53		69.2		37		9-Feb-08		8:25:59		71		36.5

		30-Dec-07		10:07:10		68		37.5		30-Dec-07		10:06:20		67.4		40		30-Dec-07		10:07:53		67.4		39.5		9-Feb-08		10:25:59		71		37.5

		30-Dec-07		12:07:10		68		39		30-Dec-07		12:06:20		67.4		41.5		30-Dec-07		12:07:53		67.4		39.5		9-Feb-08		12:25:59		70.41		39

		30-Dec-07		14:07:10		68		40		30-Dec-07		14:06:20		67.4		42.5		30-Dec-07		14:07:53		67.4		40.5		9-Feb-08		14:25:59		71.6		37.5

		30-Dec-07		16:07:10		68		41		30-Dec-07		16:06:20		67.4		43.5		30-Dec-07		16:07:53		66.81		42.5		9-Feb-08		16:25:59		72.8		34

		30-Dec-07		18:07:10		68		41.5		30-Dec-07		18:06:20		67.4		44		30-Dec-07		18:07:53		66.81		43.5		9-Feb-08		18:25:59		73.4		33.5

		30-Dec-07		20:07:10		67.4		42.5		30-Dec-07		20:06:20		66.2		46		30-Dec-07		20:07:53		67.4		43		9-Feb-08		20:25:59		71.6		37.5

		30-Dec-07		22:07:10		66.81		43		30-Dec-07		22:06:20		66.2		46.5		30-Dec-07		22:07:53		65.01		45.5		9-Feb-08		22:25:59		69.8		38.5

		31-Dec-07		0:07:10		66.81		43.5		31-Dec-07		0:06:20		66.2		46.5		31-Dec-07		0:07:53		64.4		47		10-Feb-08		0:25:59		68		39

		31-Dec-07		2:07:10		66.81		44		31-Dec-07		2:06:20		66.2		47		31-Dec-07		2:07:53		63.8		48		10-Feb-08		2:25:59		66.2		39

		31-Dec-07		4:07:10		66.81		44		31-Dec-07		4:06:20		66.2		47		31-Dec-07		4:07:53		63.21		49		10-Feb-08		4:25:59		65.6		39.5

		31-Dec-07		6:07:10		66.81		42.5		31-Dec-07		6:06:20		65.6		44		31-Dec-07		6:07:53		63.21		48		10-Feb-08		6:25:59		64.4		40

		31-Dec-07		8:07:10		66.81		39.5		31-Dec-07		8:06:20		67.4		40		31-Dec-07		8:07:53		66.2		42		10-Feb-08		8:25:59		64.4		39.5

		31-Dec-07		10:07:10		67.4		38		31-Dec-07		10:06:20		67.4		38.5		31-Dec-07		10:07:53		68		38.5		10-Feb-08		10:25:59		65.01		40.5

		31-Dec-07		12:07:10		67.4		36.5		31-Dec-07		12:06:20		67.4		37		31-Dec-07		12:07:53		66.81		38		10-Feb-08		12:25:59		66.81		43

		31-Dec-07		14:07:10		68		34.5		31-Dec-07		14:06:20		68		34		31-Dec-07		14:07:53		67.4		36.5		10-Feb-08		14:25:59		68.61		44

		31-Dec-07		16:07:10		68		32		31-Dec-07		16:06:20		67.4		31.5		31-Dec-07		16:07:53		67.4		35		10-Feb-08		16:25:59		69.8		42

		31-Dec-07		18:07:10		68		30.5		31-Dec-07		18:06:20		68		30		31-Dec-07		18:07:53		67.4		33.5		10-Feb-08		18:25:59		71		42.5

		31-Dec-07		20:07:10		67.4		31		31-Dec-07		20:06:20		66.2		31.5		31-Dec-07		20:07:53		65.6		33.5		10-Feb-08		20:25:59		69.8		42.5

		31-Dec-07		22:07:10		66.81		31.5		31-Dec-07		22:06:20		65.6		33		31-Dec-07		22:07:53		63.8		35		10-Feb-08		22:25:59		68		43

		1-Jan-08		0:07:10		66.2		30.5		1-Jan-08		0:06:20		65.6		31.5		1-Jan-08		0:07:53		63.21		34.5		11-Feb-08		0:25:59		66.81		43

		1-Jan-08		2:07:10		66.2		29.5		1-Jan-08		2:06:20		65.6		30		1-Jan-08		2:07:53		62		33.5		11-Feb-08		2:25:59		65.6		43

		1-Jan-08		4:07:10		66.2		29		1-Jan-08		4:06:20		65.6		29.5		1-Jan-08		4:07:53		61.41		33.5		11-Feb-08		4:25:59		65.01		43

		1-Jan-08		6:07:10		66.2		28.5		1-Jan-08		6:06:20		65.6		29.5		1-Jan-08		6:07:53		67.4		29		11-Feb-08		6:25:59		64.4		42.5

		1-Jan-08		8:07:10		67.4		27		1-Jan-08		8:06:20		68.61		27.5		1-Jan-08		8:07:53		69.2		28.5		11-Feb-08		8:25:59		64.4		41.5

		1-Jan-08		10:07:10		68.61		27.5		1-Jan-08		10:06:20		69.2		28.5		1-Jan-08		10:07:53		69.8		29		11-Feb-08		10:25:59		65.6		41.5

		1-Jan-08		12:07:10		69.8		29		1-Jan-08		12:06:20		69.2		28.5		1-Jan-08		12:07:53		71.6		29		11-Feb-08		12:25:59		68		45

		1-Jan-08		14:07:10		71		29.5		1-Jan-08		14:06:20		70.41		30.5		1-Jan-08		14:07:53		71		31.5		11-Feb-08		14:25:59		69.2		45

		1-Jan-08		16:07:10		71.6		28.5		1-Jan-08		16:06:20		69.2		29		1-Jan-08		16:07:53		69.8		30.5		11-Feb-08		16:25:59		70.41		44.5

		1-Jan-08		18:07:10		71.6		29		1-Jan-08		18:06:20		69.2		30		1-Jan-08		18:07:53		69.8		31.5		11-Feb-08		18:25:59		71		45

		1-Jan-08		20:07:10		70.41		28.5		1-Jan-08		20:06:20		67.4		31		1-Jan-08		20:07:53		68.61		31.5		11-Feb-08		20:25:59		69.8		45

		1-Jan-08		22:07:10		68.61		28.5		1-Jan-08		22:06:20		66.81		31		1-Jan-08		22:07:53		66.2		31.5		11-Feb-08		22:25:59		68		45.5

		2-Jan-08		0:07:10		67.4		28.5		2-Jan-08		0:06:20		66.2		30.5		2-Jan-08		0:07:53		63.8		32		12-Feb-08		0:25:59		66.81		45.5

		2-Jan-08		2:07:10		66.81		29		2-Jan-08		2:06:20		65.6		31		2-Jan-08		2:07:53		62		33		12-Feb-08		2:25:59		65.6		45

		2-Jan-08		4:07:10		66.2		27.5		2-Jan-08		4:06:20		65.6		29.5		2-Jan-08		4:07:53		60.8		33		12-Feb-08		4:25:59		65.01		45

		2-Jan-08		6:07:10		66.81		27		2-Jan-08		6:06:20		65.6		29		2-Jan-08		6:07:53		66.81		28.5		12-Feb-08		6:25:59		66.2		44

		2-Jan-08		8:07:10		67.4		26		2-Jan-08		8:06:20		66.81		27.5		2-Jan-08		8:07:53		67.4		27.5		12-Feb-08		8:25:59		69.2		40.5

		2-Jan-08		10:07:10		68		26.5		2-Jan-08		10:06:20		67.4		28		2-Jan-08		10:07:53		67.4		28		12-Feb-08		10:25:59		72.8		40

		2-Jan-08		12:07:10		69.2		29.5		2-Jan-08		12:06:20		68		31.5		2-Jan-08		12:07:53		67.4		31		12-Feb-08		12:25:59		71.6		43

		2-Jan-08		14:07:10		70.41		31.5		2-Jan-08		14:06:20		68.61		33.5		2-Jan-08		14:07:53		68		33.5		12-Feb-08		14:25:59		72.8		43.5

		2-Jan-08		16:07:10		71.6		32		2-Jan-08		16:06:20		69.2		34		2-Jan-08		16:07:53		69.2		34.5		12-Feb-08		16:25:59		74.01		43.5

		2-Jan-08		18:07:10		72.21		31		2-Jan-08		18:06:20		69.2		33		2-Jan-08		18:07:53		68.61		34.5		12-Feb-08		18:25:59		74.01		44.5

		2-Jan-08		20:07:10		71.6		31		2-Jan-08		20:06:20		68		34		2-Jan-08		20:07:53		68		34.5		12-Feb-08		20:25:59		71.6		43.5

		2-Jan-08		22:07:10		69.2		31		2-Jan-08		22:06:20		66.81		35.5		2-Jan-08		22:07:53		66.81		34.5		12-Feb-08		22:25:59		70.41		44.5

		3-Jan-08		0:07:10		68		32		3-Jan-08		0:06:20		66.2		35.5		3-Jan-08		0:07:53		64.4		36		13-Feb-08		0:25:59		68.61		44.5

		3-Jan-08		2:07:10		66.81		31.5		3-Jan-08		2:06:20		66.2		34		3-Jan-08		2:07:53		63.21		36.5		13-Feb-08		2:25:59		67.4		44

		3-Jan-08		4:07:10		66.2		31.5		3-Jan-08		4:06:20		66.2		34		3-Jan-08		4:07:53		62		36.5		13-Feb-08		4:25:59		66.2		44

		3-Jan-08		6:07:10		66.81		31.5		3-Jan-08		6:06:20		65.6		34		3-Jan-08		6:07:53		66.81		33.5		13-Feb-08		6:25:59		66.81		43.5

		3-Jan-08		8:07:10		68.61		29.5		3-Jan-08		8:06:20		67.4		31.5		3-Jan-08		8:07:53		68		32.5		13-Feb-08		8:25:59		72.21		39.5

		3-Jan-08		10:07:10		69.2		30.5		3-Jan-08		10:06:20		69.8		32.5		3-Jan-08		10:07:53		69.8		32		13-Feb-08		10:25:59		71.6		40.5

		3-Jan-08		12:07:10		71.6		32		3-Jan-08		12:06:20		71		32.5		3-Jan-08		12:07:53		72.21		32.5		13-Feb-08		12:25:59		72.21		43

		3-Jan-08		14:07:10		72.8		31		3-Jan-08		14:06:20		71		30.5		3-Jan-08		14:07:53		71		35		13-Feb-08		14:25:59		74.01		43.5

		3-Jan-08		16:07:10		72.21		32.5		3-Jan-08		16:06:20		71		34.5		3-Jan-08		16:07:53		70.41		33.5		13-Feb-08		16:25:59		74.6		44.5

		3-Jan-08		18:07:10		72.21		32.5		3-Jan-08		18:06:20		69.2		35		3-Jan-08		18:07:53		70.41		35.5		13-Feb-08		18:25:59		74.01		44

		3-Jan-08		20:07:10		71.6		34		3-Jan-08		20:06:20		68		39		3-Jan-08		20:07:53		69.8		36.5		13-Feb-08		20:25:59		72.21		43.5

		3-Jan-08		22:07:10		70.41		33.5		3-Jan-08		22:06:20		66.81		37.5		3-Jan-08		22:07:53		68		36.5		13-Feb-08		22:25:59		71		43.5

		4-Jan-08		0:07:10		69.2		33		4-Jan-08		0:06:20		66.2		37		4-Jan-08		0:07:53		66.2		36.5		14-Feb-08		0:25:59		68.61		43.5

		4-Jan-08		2:07:10		68.61		34.5		4-Jan-08		2:06:20		66.2		39		4-Jan-08		2:07:53		65.01		38.5		14-Feb-08		2:25:59		67.4		43.5

		4-Jan-08		4:07:10		68		35		4-Jan-08		4:06:20		66.2		39.5		4-Jan-08		4:07:53		65.01		39.5		14-Feb-08		4:25:59		66.2		43.5

		4-Jan-08		6:07:10		68.61		36.5		4-Jan-08		6:06:20		66.2		41		4-Jan-08		6:07:53		66.81		40		14-Feb-08		6:25:59		66.81		44

		4-Jan-08		8:07:10		71		37.5		4-Jan-08		8:06:20		68.61		42		4-Jan-08		8:07:53		70.41		39.5		14-Feb-08		8:25:59		70.41		41

		4-Jan-08		10:07:10		72.21		39		4-Jan-08		10:06:20		70.41		40		4-Jan-08		10:07:53		71.6		40.5		14-Feb-08		10:25:59		71.6		37

		4-Jan-08		12:07:10		73.4		40		4-Jan-08		12:06:20		71		46.5		4-Jan-08		12:07:53		71		45.5		14-Feb-08		12:25:59		71.6		36.5

		4-Jan-08		14:07:10		72.8		42.5		4-Jan-08		14:06:20		71		47.5		4-Jan-08		14:07:53		71		45.5		14-Feb-08		14:25:59		72.8		36

		4-Jan-08		16:07:10		73.4		43.5		4-Jan-08		16:06:20		70.41		49		4-Jan-08		16:07:53		71.6		41.5		14-Feb-08		16:25:59		73.4		32

		4-Jan-08		18:07:10		72.8		42.5		4-Jan-08		18:06:20		69.8		47.5		4-Jan-08		18:07:53		71		42		14-Feb-08		18:25:59		73.4		29

		4-Jan-08		20:07:10		71.6		42.5		4-Jan-08		20:06:20		69.2		48		4-Jan-08		20:07:53		69.8		45.5		14-Feb-08		20:25:59		71.6		28

		4-Jan-08		22:07:10		71		43		4-Jan-08		22:06:20		68		49.5		4-Jan-08		22:07:53		69.2		46.5		14-Feb-08		22:25:59		70.41		31.5

		5-Jan-08		0:07:10		69.8		43.5		5-Jan-08		0:06:20		67.4		50.5		5-Jan-08		0:07:53		69.2		46.5		15-Feb-08		0:25:59		68.61		32.5

		5-Jan-08		2:07:10		69.2		44		5-Jan-08		2:06:20		67.4		51		5-Jan-08		2:07:53		68.61		47		15-Feb-08		2:25:59		67.4		33

		5-Jan-08		4:07:10		69.2		45		5-Jan-08		4:06:20		67.4		52.5		5-Jan-08		4:07:53		68.61		48		15-Feb-08		4:25:59		66.2		33.5

		5-Jan-08		6:07:10		68.61		46		5-Jan-08		6:06:20		67.4		53.5		5-Jan-08		6:07:53		68		49		15-Feb-08		6:25:59		66.81		33.5

		5-Jan-08		8:07:10		69.8		47		5-Jan-08		8:06:20		69.2		53.5		5-Jan-08		8:07:53		70.41		53		15-Feb-08		8:25:59		70.41		32

		5-Jan-08		10:07:10		71		49.5		5-Jan-08		10:06:20		70.41		56.5		5-Jan-08		10:07:53		71		49		15-Feb-08		10:25:59		71.6		30.5

		5-Jan-08		12:07:10		71		49.5		5-Jan-08		12:06:20		71		51		5-Jan-08		12:07:53		71		54.5		15-Feb-08		12:25:59		72.21		30

		5-Jan-08		14:07:10		70.41		46		5-Jan-08		14:06:20		70.41		47		5-Jan-08		14:07:53		72.21		45.5		15-Feb-08		14:25:59		72.8		30.5

		5-Jan-08		16:07:10		69.8		45.5		5-Jan-08		16:06:20		71		46		5-Jan-08		16:07:53		71		46		15-Feb-08		16:25:59		73.4		29.5

		5-Jan-08		18:07:10		73.4		41.5		5-Jan-08		18:06:20		74.01		42		5-Jan-08		18:07:53		74.01		42.5		15-Feb-08		18:25:59		74.01		30

		5-Jan-08		20:07:10		69.2		42.5		5-Jan-08		20:06:20		68		44.5		5-Jan-08		20:07:53		69.2		43.5		15-Feb-08		20:25:59		71		30

		5-Jan-08		22:07:10		68		41.5		5-Jan-08		22:06:20		66.81		43.5		5-Jan-08		22:07:53		68		44		15-Feb-08		22:25:59		69.2		31.5

		6-Jan-08		0:07:10		67.4		41		6-Jan-08		0:06:20		66.81		42.5		6-Jan-08		0:07:53		67.4		43.5		16-Feb-08		0:25:59		68		33

		6-Jan-08		2:07:10		66.81		39.5		6-Jan-08		2:06:20		66.81		39.5		6-Jan-08		2:07:53		66.2		42.5		16-Feb-08		2:25:59		66.2		34

		6-Jan-08		4:07:10		66.2		41		6-Jan-08		4:06:20		66.2		42		6-Jan-08		4:07:53		65.6		43		16-Feb-08		4:25:59		65.6		35

		6-Jan-08		6:07:10		65.6		41		6-Jan-08		6:06:20		66.2		41		6-Jan-08		6:07:53		65.01		43.5		16-Feb-08		6:25:59		66.2		36

		6-Jan-08		8:07:10		65.6		42		6-Jan-08		8:06:20		68		40		6-Jan-08		8:07:53		66.81		41		16-Feb-08		8:25:59		69.2		34

		6-Jan-08		10:07:10		65.6		43.5		6-Jan-08		10:06:20		68		42.5		6-Jan-08		10:07:53		66.81		42.5		16-Feb-08		10:25:59		71.6		34.5

		6-Jan-08		12:07:10		65.6		44.5		6-Jan-08		12:06:20		68		42.5		6-Jan-08		12:07:53		67.4		43		16-Feb-08		12:25:59		72.21		34

		6-Jan-08		14:07:10		65.6		45.5		6-Jan-08		14:06:20		68		44		6-Jan-08		14:07:53		67.4		45		16-Feb-08		14:25:59		72.8		34

		6-Jan-08		16:07:10		66.2		45		6-Jan-08		16:06:20		68		43.5		6-Jan-08		16:07:53		68		44.5		16-Feb-08		16:25:59		74.6		37

		6-Jan-08		18:07:10		66.2		45		6-Jan-08		18:06:20		68		44		6-Jan-08		18:07:53		67.4		45		16-Feb-08		18:25:59		74.01		37

		6-Jan-08		20:07:10		66.2		45		6-Jan-08		20:06:20		66.81		44.5		6-Jan-08		20:07:53		67.4		44		16-Feb-08		20:25:59		71.6		37.5

		6-Jan-08		22:07:10		65.6		43		6-Jan-08		22:06:20		66.81		42.5		6-Jan-08		22:07:53		66.2		43.5		16-Feb-08		22:25:59		69.2		38

		7-Jan-08		0:07:10		65.01		42.5		7-Jan-08		0:06:20		66.2		41.5		7-Jan-08		0:07:53		65.6		43		17-Feb-08		0:25:59		68		39

		7-Jan-08		2:07:10		65.01		42.5		7-Jan-08		2:06:20		66.2		41		7-Jan-08		2:07:53		65.6		43		17-Feb-08		2:25:59		67.4		39.5

		7-Jan-08		4:07:10		64.4		41.5		7-Jan-08		4:06:20		66.2		40		7-Jan-08		4:07:53		65.01		42		17-Feb-08		4:25:59		66.81		40.5

		7-Jan-08		6:07:10		64.4		40		7-Jan-08		6:06:20		66.2		38		7-Jan-08		6:07:53		64.4		41		17-Feb-08		6:25:59		66.81		41

		7-Jan-08		8:07:10		64.4		40.5		7-Jan-08		8:06:20		67.4		37		7-Jan-08		8:07:53		66.81		38.5		17-Feb-08		8:25:59		66.2		41

		7-Jan-08		10:07:10		64.4		39		7-Jan-08		10:06:20		67.4		35.5		7-Jan-08		10:07:53		67.4		36.5		17-Feb-08		10:25:59		66.2		41

		7-Jan-08		12:07:10		64.4		41		7-Jan-08		12:06:20		68		38.5		7-Jan-08		12:07:53		67.4		38.5		17-Feb-08		12:25:59		66.81		42

		7-Jan-08		14:07:10		65.01		43		7-Jan-08		14:06:20		68		41		7-Jan-08		14:07:53		67.4		41		17-Feb-08		14:25:59		67.4		43

		7-Jan-08		16:07:10		65.6		42.5		7-Jan-08		16:06:20		68		39.5		7-Jan-08		16:07:53		68		40.5		17-Feb-08		16:25:59		68.61		42

		7-Jan-08		18:07:10		65.6		41.5		7-Jan-08		18:06:20		68		39.5		7-Jan-08		18:07:53		68		40		17-Feb-08		18:25:59		69.2		41

		7-Jan-08		20:07:10		65.6		42		7-Jan-08		20:06:20		66.81		41.5		7-Jan-08		20:07:53		66.81		41		17-Feb-08		20:25:59		68		41.5

		7-Jan-08		22:07:10		65.01		43.5		7-Jan-08		22:06:20		66.81		42.5		7-Jan-08		22:07:53		65.6		43		17-Feb-08		22:25:59		67.4		42

		8-Jan-08		0:07:10		65.01		44.5		8-Jan-08		0:06:20		66.81		43		8-Jan-08		0:07:53		65.6		44		18-Feb-08		0:25:59		66.2		42

		8-Jan-08		2:07:10		64.4		44		8-Jan-08		2:06:20		66.81		42.5		8-Jan-08		2:07:53		65.01		44		18-Feb-08		2:25:59		65.6		42.5

		8-Jan-08		4:07:10		64.4		44.5		8-Jan-08		4:06:20		66.2		42.5		8-Jan-08		4:07:53		65.01		44		18-Feb-08		4:25:59		65.01		43.5

		8-Jan-08		6:07:10		64.4		44		8-Jan-08		6:06:20		66.2		41.5		8-Jan-08		6:07:53		66.81		41.5		18-Feb-08		6:25:59		65.01		44

		8-Jan-08		8:07:10		65.6		41		8-Jan-08		8:06:20		68		37.5		8-Jan-08		8:07:53		69.2		38.5		18-Feb-08		8:25:59		65.6		43

		8-Jan-08		10:07:10		66.2		39.5		8-Jan-08		10:06:20		69.8		35.5		8-Jan-08		10:07:53		71		36.5		18-Feb-08		10:25:59		66.2		42.5

		8-Jan-08		12:07:10		67.4		42		8-Jan-08		12:06:20		71.6		40.5		8-Jan-08		12:07:53		72.21		39		18-Feb-08		12:25:59		67.4		42

		8-Jan-08		14:07:10		68		38.5		8-Jan-08		14:06:20		71.6		35.5		8-Jan-08		14:07:53		70.41		40.5		18-Feb-08		14:25:59		68		42.5

		8-Jan-08		16:07:10		68.61		35.5		8-Jan-08		16:06:20		71		33.5		8-Jan-08		16:07:53		71		35.5		18-Feb-08		16:25:59		68		43.5

		8-Jan-08		18:07:10		68.61		34		8-Jan-08		18:06:20		69.2		34		8-Jan-08		18:07:53		70.41		36		18-Feb-08		18:25:59		68		43.5

		8-Jan-08		20:07:10		68		34.5		8-Jan-08		20:06:20		67.4		36		8-Jan-08		20:07:53		69.2		36		18-Feb-08		20:25:59		67.4		43.5

		8-Jan-08		22:07:10		67.4		35.5		8-Jan-08		22:06:20		66.81		36.5		8-Jan-08		22:07:53		67.4		38		18-Feb-08		22:25:59		66.2		43.5

		9-Jan-08		0:07:10		66.81		36.5		9-Jan-08		0:06:20		66.81		37		9-Jan-08		0:07:53		65.6		38.5		19-Feb-08		0:25:59		65.6		44.5

		9-Jan-08		2:07:10		65.6		37.5		9-Jan-08		2:06:20		66.81		37.5		9-Jan-08		2:07:53		64.4		39.5		19-Feb-08		2:25:59		65.6		45

		9-Jan-08		4:07:10		65.01		38		9-Jan-08		4:06:20		66.2		38		9-Jan-08		4:07:53		63.21		41		19-Feb-08		4:25:59		65.01		45.5

		9-Jan-08		6:07:10		65.01		39		9-Jan-08		6:06:20		66.2		38.5		9-Jan-08		6:07:53		67.4		38		19-Feb-08		6:25:59		66.2		45

		9-Jan-08		8:07:10		65.6		39		9-Jan-08		8:06:20		68		37.5		9-Jan-08		8:07:53		68.61		39		19-Feb-08		8:25:59		69.8		42.5

		9-Jan-08		10:07:10		66.81		41		9-Jan-08		10:06:20		71		37.5		9-Jan-08		10:07:53		70.41		39.5		19-Feb-08		10:25:59		72.21		40.5

		9-Jan-08		12:07:10		67.4		42.5		9-Jan-08		12:06:20		71		42		9-Jan-08		12:07:53		71		41.5		19-Feb-08		12:25:59		71.6		40.5

		9-Jan-08		14:07:10		68.61		44.5		9-Jan-08		14:06:20		72.8		43.5		9-Jan-08		14:07:53		71.6		42.5		19-Feb-08		14:25:59		71.6		40.5

		9-Jan-08		16:07:10		69.2		46		9-Jan-08		16:06:20		74.01		42.5		9-Jan-08		16:07:53		71		44		19-Feb-08		16:25:59		72.21		40.5

		9-Jan-08		18:07:10		69.8		46		9-Jan-08		18:06:20		71		46		9-Jan-08		18:07:53		71.6		38.5		19-Feb-08		18:25:59		71.6		41

		9-Jan-08		20:07:10		70.41		45		9-Jan-08		20:06:20		69.8		45		9-Jan-08		20:07:53		70.41		44.5		19-Feb-08		20:25:59		71.6		41

		9-Jan-08		22:07:10		69.2		42.5		9-Jan-08		22:06:20		68		44.5		9-Jan-08		22:07:53		68.61		43.5		19-Feb-08		22:25:59		69.2		41.5

		10-Jan-08		0:07:10		68		44		10-Jan-08		0:06:20		66.81		46.5		10-Jan-08		0:07:53		67.4		45		20-Feb-08		0:25:59		67.4		42

		10-Jan-08		2:07:10		67.4		45		10-Jan-08		2:06:20		66.81		47		10-Jan-08		2:07:53		66.2		46.5		20-Feb-08		2:25:59		66.81		42.5

		10-Jan-08		4:07:10		66.81		45.5		10-Jan-08		4:06:20		66.81		46		10-Jan-08		4:07:53		65.6		47		20-Feb-08		4:25:59		66.2		43.5

		10-Jan-08		6:07:10		66.2		46		10-Jan-08		6:06:20		67.4		45.5		10-Jan-08		6:07:53		66.81		45.5		20-Feb-08		6:25:59		66.81		43.5

		10-Jan-08		8:07:10		66.81		45		10-Jan-08		8:06:20		69.8		41.5		10-Jan-08		8:07:53		70.41		43		20-Feb-08		8:25:59		71.6		42

		10-Jan-08		10:07:10		68		44.5		10-Jan-08		10:06:20		70.41		41		10-Jan-08		10:07:53		72.21		41.5		20-Feb-08		10:25:59		72.8		41

		10-Jan-08		12:07:10		68.61		43.5		10-Jan-08		12:06:20		70.41		39		10-Jan-08		12:07:53		71.6		42		20-Feb-08		12:25:59		72.8		41.5

		10-Jan-08		14:07:10		69.2		43.5		10-Jan-08		14:06:20		70.41		45		10-Jan-08		14:07:53		71.6		44		20-Feb-08		14:25:59		72.21		43.5

		10-Jan-08		16:07:10		69.2		43		10-Jan-08		16:06:20		70.41		39.5		10-Jan-08		16:07:53		71		43		20-Feb-08		16:25:59		72.21		45.5

		10-Jan-08		18:07:10		69.2		43		10-Jan-08		18:06:20		68.61		44		10-Jan-08		18:07:53		70.41		43.5		20-Feb-08		18:25:59		71.6		45.5

		10-Jan-08		20:07:10		69.2		42.5		10-Jan-08		20:06:20		68		44.5		10-Jan-08		20:07:53		69.2		42.5		20-Feb-08		20:25:59		71.6		45.5

		10-Jan-08		22:07:10		68.61		43		10-Jan-08		22:06:20		67.4		45		10-Jan-08		22:07:53		68		44		20-Feb-08		22:25:59		70.41		45.5

		11-Jan-08		0:07:10		68		43.5		11-Jan-08		0:06:20		67.4		44.5		11-Jan-08		0:07:53		67.4		44.5		21-Feb-08		0:25:59		68.61		46

		11-Jan-08		2:07:10		67.4		44		11-Jan-08		2:06:20		67.4		45.5		11-Jan-08		2:07:53		66.81		45.5		21-Feb-08		2:25:59		68		46

		11-Jan-08		4:07:10		67.4		44		11-Jan-08		4:06:20		67.4		45		11-Jan-08		4:07:53		65.6		46.5		21-Feb-08		4:25:59		66.81		46.5

		11-Jan-08		6:07:10		66.81		44.5		11-Jan-08		6:06:20		67.4		45		11-Jan-08		6:07:53		68		45		21-Feb-08		6:25:59		66.81		47

		11-Jan-08		8:07:10		67.4		45		11-Jan-08		8:06:20		67.4		45		11-Jan-08		8:07:53		69.8		44		21-Feb-08		8:25:59		71		44.5

		11-Jan-08		10:07:10		68		46		11-Jan-08		10:06:20		72.21		42.5		11-Jan-08		10:07:53		71.6		43		21-Feb-08		10:25:59		72.21		44

		11-Jan-08		12:07:10		69.2		46.5		11-Jan-08		12:06:20		72.8		44		11-Jan-08		12:07:53		71.6		47		21-Feb-08		12:25:59		72.8		43.5

		11-Jan-08		14:07:10		70.41		47.5		11-Jan-08		14:06:20		72.8		46		11-Jan-08		14:07:53		71		41.5		21-Feb-08		14:25:59		73.4		42

		11-Jan-08		16:07:10		70.41		47		11-Jan-08		16:06:20		73.4		40		11-Jan-08		16:07:53		71		48.5		21-Feb-08		16:25:59		74.01		40.5

		11-Jan-08		18:07:10		70.41		47		11-Jan-08		18:06:20		71		46.5		11-Jan-08		18:07:53		70.41		44.5		21-Feb-08		18:25:59		73.4		41

		11-Jan-08		20:07:10		69.8		46		11-Jan-08		20:06:20		69.2		48		11-Jan-08		20:07:53		70.41		44.5		21-Feb-08		20:25:59		72.21		40.5

		11-Jan-08		22:07:10		68.61		47		11-Jan-08		22:06:20		68		49.5		11-Jan-08		22:07:53		69.2		47		21-Feb-08		22:25:59		71		41

		12-Jan-08		0:07:10		68		48		12-Jan-08		0:06:20		68		49.5		12-Jan-08		0:07:53		68		48		22-Feb-08		0:25:59		69.8		41

		12-Jan-08		2:07:10		67.4		49		12-Jan-08		2:06:20		68		50		12-Jan-08		2:07:53		67.4		49		22-Feb-08		2:25:59		68.61		42

		12-Jan-08		4:07:10		66.81		48.5		12-Jan-08		4:06:20		67.4		48.5		12-Jan-08		4:07:53		66.81		49		22-Feb-08		4:25:59		67.4		43

		12-Jan-08		6:07:10		66.81		47.5		12-Jan-08		6:06:20		67.4		46.5		12-Jan-08		6:07:53		67.4		47.5		22-Feb-08		6:25:59		67.4		43.5

		12-Jan-08		8:07:10		66.81		46		12-Jan-08		8:06:20		69.2		43		12-Jan-08		8:07:53		69.8		45		22-Feb-08		8:25:59		71.6		42

		12-Jan-08		10:07:10		68		45.5		12-Jan-08		10:06:20		72.8		38		12-Jan-08		10:07:53		71.6		43		22-Feb-08		10:25:59		72.8		41

		12-Jan-08		12:07:10		68		45.5		12-Jan-08		12:06:20		71		45		12-Jan-08		12:07:53		71		41		22-Feb-08		12:25:59		72.8		42.5

		12-Jan-08		14:07:10		68		44.5		12-Jan-08		14:06:20		70.41		42		12-Jan-08		14:07:53		69.8		44		22-Feb-08		14:25:59		72.21		42

		12-Jan-08		16:07:10		68		45		12-Jan-08		16:06:20		68.61		44		12-Jan-08		16:07:53		70.41		43.5		22-Feb-08		16:25:59		72.21		43.5

		12-Jan-08		18:07:10		67.4		45		12-Jan-08		18:06:20		68.61		44.5		12-Jan-08		18:07:53		69.8		43.5		22-Feb-08		18:25:59		72.21		44

		12-Jan-08		20:07:10		67.4		45.5		12-Jan-08		20:06:20		68		45.5		12-Jan-08		20:07:53		69.2		44		22-Feb-08		20:25:59		72.21		43.5

		12-Jan-08		22:07:10		66.81		45.5		12-Jan-08		22:06:20		66.81		46.5		12-Jan-08		22:07:53		69.2		44.5		22-Feb-08		22:25:59		70.41		44.5

		13-Jan-08		0:07:10		65.6		47		13-Jan-08		0:06:20		66.2		48		13-Jan-08		0:07:53		69.2		43.5		23-Feb-08		0:25:59		68.61		45

		13-Jan-08		2:07:10		65.01		47.5		13-Jan-08		2:06:20		66.2		47.5		13-Jan-08		2:07:53		69.2		43		23-Feb-08		2:25:59		68		45.5

		13-Jan-08		4:07:10		65.01		48		13-Jan-08		4:06:20		66.2		47		13-Jan-08		4:07:53		69.8		42.5		23-Feb-08		4:25:59		67.4		45.5

		13-Jan-08		6:07:10		64.4		49		13-Jan-08		6:06:20		66.2		48		13-Jan-08		6:07:53		69.8		43		23-Feb-08		6:25:59		67.4		45

		13-Jan-08		8:07:10		64.4		49		13-Jan-08		8:06:20		67.4		45.5		13-Jan-08		8:07:53		69.8		42.5		23-Feb-08		8:25:59		72.8		42.5

		13-Jan-08		10:07:10		64.4		49.5		13-Jan-08		10:06:20		68		45.5		13-Jan-08		10:07:53		69.8		42.5		23-Feb-08		10:25:59		72.8		42.5

		13-Jan-08		12:07:10		65.01		50		13-Jan-08		12:06:20		68		47		13-Jan-08		12:07:53		69.8		45		23-Feb-08		12:25:59		71.6		42.5

		13-Jan-08		14:07:10		65.6		49.5		13-Jan-08		14:06:20		68.61		46		13-Jan-08		14:07:53		69.8		44		23-Feb-08		14:25:59		71.6		43

		13-Jan-08		16:07:10		66.2		49.5		13-Jan-08		16:06:20		69.2		46		13-Jan-08		16:07:53		69.8		45.5		23-Feb-08		16:25:59		72.8		41

		13-Jan-08		18:07:10		66.81		49.5		13-Jan-08		18:06:20		69.2		45		13-Jan-08		18:07:53		69.8		46.5		23-Feb-08		18:25:59		72.8		38.5

		13-Jan-08		20:07:10		66.81		48.5		13-Jan-08		20:06:20		68		47.5		13-Jan-08		20:07:53		69.2		45.5		23-Feb-08		20:25:59		71.6		38

		13-Jan-08		22:07:10		66.2		47		13-Jan-08		22:06:20		66.2		46		13-Jan-08		22:07:53		69.2		43		23-Feb-08		22:25:59		69.2		38.5

		14-Jan-08		0:07:10		65.01		46.5		14-Jan-08		0:06:20		65.6		45.5		14-Jan-08		0:07:53		69.2		41		24-Feb-08		0:25:59		66.81		39.5

		14-Jan-08		2:07:10		64.4		48		14-Jan-08		2:06:20		65.6		47		14-Jan-08		2:07:53		69.8		41.5		24-Feb-08		2:25:59		65.6		40

		14-Jan-08		4:07:10		64.4		49.5		14-Jan-08		4:06:20		65.6		48		14-Jan-08		4:07:53		69.8		42		24-Feb-08		4:25:59		64.4		40

		14-Jan-08		6:07:10		64.4		50.5		14-Jan-08		6:06:20		66.2		49		14-Jan-08		6:07:53		69.8		42.5		24-Feb-08		6:25:59		64.4		40.5

		14-Jan-08		8:07:10		64.4		51.5		14-Jan-08		8:06:20		68		47		14-Jan-08		8:07:53		69.8		43		24-Feb-08		8:25:59		65.01		40.5

		14-Jan-08		10:07:10		64.4		50		14-Jan-08		10:06:20		68		45.5		14-Jan-08		10:07:53		69.8		42		24-Feb-08		10:25:59		65.01		41.5

		14-Jan-08		12:07:10		65.01		49		14-Jan-08		12:06:20		68		44.5		14-Jan-08		12:07:53		70.41		39.5		24-Feb-08		12:25:59		65.6		42.5

		14-Jan-08		14:07:10		65.01		49		14-Jan-08		14:06:20		68		45		14-Jan-08		14:07:53		69.8		38.5		24-Feb-08		14:25:59		66.2		43.5

		14-Jan-08		16:07:10		65.6		49.5		14-Jan-08		16:06:20		68.61		46.5		14-Jan-08		16:07:53		69.8		42.5		24-Feb-08		16:25:59		65.6		43.5

		14-Jan-08		18:07:10		66.2		49.5		14-Jan-08		18:06:20		68.61		47		14-Jan-08		18:07:53		69.8		45		24-Feb-08		18:25:59		65.01		44

		14-Jan-08		20:07:10		66.2		48.5		14-Jan-08		20:06:20		67.4		47		14-Jan-08		20:07:53		69.8		44		24-Feb-08		20:25:59		64.4		45

		14-Jan-08		22:07:10		65.6		47		14-Jan-08		22:06:20		66.2		46		14-Jan-08		22:07:53		69.8		41.5		24-Feb-08		22:25:59		64.4		46

		15-Jan-08		0:07:10		64.4		44		15-Jan-08		0:06:20		65.6		42		15-Jan-08		0:07:53		69.2		39		25-Feb-08		0:25:59		64.4		47.5

		15-Jan-08		2:07:10		63.8		45		15-Jan-08		2:06:20		65.6		43		15-Jan-08		2:07:53		69.8		38.5		25-Feb-08		2:25:59		64.4		48

		15-Jan-08		4:07:10		63.8		45		15-Jan-08		4:06:20		65.6		42.5		15-Jan-08		4:07:53		69.8		38		25-Feb-08		4:25:59		64.4		49

		15-Jan-08		6:07:10		63.21		46		15-Jan-08		6:06:20		65.6		44		15-Jan-08		6:07:53		69.8		38.5		25-Feb-08		6:25:59		64.4		49.5

		15-Jan-08		8:07:10		63.8		47		15-Jan-08		8:06:20		67.4		42.5		15-Jan-08		8:07:53		71		39.5		25-Feb-08		8:25:59		65.01		49.5

		15-Jan-08		10:07:10		65.01		47.5		15-Jan-08		10:06:20		70.41		41.5		15-Jan-08		10:07:53		71		37		25-Feb-08		10:25:59		66.2		49.5

		15-Jan-08		12:07:10		65.6		47.5		15-Jan-08		12:06:20		70.41		43		15-Jan-08		12:07:53		71		43.5		25-Feb-08		12:25:59		66.81		49.5

		15-Jan-08		14:07:10		66.2		48		15-Jan-08		14:06:20		70.41		46.5		15-Jan-08		14:07:53		71		43.5		25-Feb-08		14:25:59		67.4		50

		15-Jan-08		16:07:10		66.81		49.5		15-Jan-08		16:06:20		71		44		15-Jan-08		16:07:53		70.41		45		25-Feb-08		16:25:59		67.4		50

		15-Jan-08		18:07:10		66.81		48		15-Jan-08		18:06:20		69.2		44		15-Jan-08		18:07:53		70.41		43.5		25-Feb-08		18:25:59		67.4		49.5

		15-Jan-08		20:07:10		66.81		45.5		15-Jan-08		20:06:20		67.4		44		15-Jan-08		20:07:53		69.8		41.5		25-Feb-08		20:25:59		66.81		49

		15-Jan-08		22:07:10		65.6		43.5		15-Jan-08		22:06:20		65.6		42.5		15-Jan-08		22:07:53		68.61		41		25-Feb-08		22:25:59		66.2		49

		16-Jan-08		0:07:10		65.01		43		16-Jan-08		0:06:20		65.6		41		16-Jan-08		0:07:53		66.81		40		26-Feb-08		0:25:59		65.6		49.5

		16-Jan-08		2:07:10		64.4		42.5		16-Jan-08		2:06:20		65.01		41.5		16-Jan-08		2:07:53		65.6		41		26-Feb-08		2:25:59		65.01		50

		16-Jan-08		4:07:10		63.8		42.5		16-Jan-08		4:06:20		65.6		40		16-Jan-08		4:07:53		64.4		41		26-Feb-08		4:25:59		64.4		49.5

		16-Jan-08		6:07:10		63.21		42		16-Jan-08		6:06:20		65.01		40		16-Jan-08		6:07:53		67.4		38		26-Feb-08		6:25:59		66.2		48

		16-Jan-08		8:07:10		63.8		41		16-Jan-08		8:06:20		67.4		37		16-Jan-08		8:07:53		69.2		36.5		26-Feb-08		8:25:59		69.8		45

		16-Jan-08		10:07:10		65.01		41		16-Jan-08		10:06:20		70.41		36		16-Jan-08		10:07:53		71		36		26-Feb-08		10:25:59		72.21		44

		16-Jan-08		12:07:10		65.6		42.5		16-Jan-08		12:06:20		71		35		16-Jan-08		12:07:53		71.6		36		26-Feb-08		12:25:59		72.21		43.5

		16-Jan-08		14:07:10		66.81		44.5		16-Jan-08		14:06:20		71		39		16-Jan-08		14:07:53		70.41		43.5		26-Feb-08		14:25:59		72.8		43

		16-Jan-08		16:07:10		68		46		16-Jan-08		16:06:20		71.6		40.5		16-Jan-08		16:07:53		69.8		44.5		26-Feb-08		16:25:59		73.4		42

		16-Jan-08		18:07:10		68		44.5		16-Jan-08		18:06:20		69.8		42		16-Jan-08		18:07:53		69.8		43.5		26-Feb-08		18:25:59		73.4		42.5

		16-Jan-08		20:07:10		68		44		16-Jan-08		20:06:20		68.61		43.5		16-Jan-08		20:07:53		69.2		43		26-Feb-08		20:25:59		72.21		42.5

		16-Jan-08		22:07:10		67.4		42		16-Jan-08		22:06:20		66.81		43		16-Jan-08		22:07:53		68.61		40.5		26-Feb-08		22:25:59		70.41		43.5

		17-Jan-08		0:07:10		66.2		40.5		17-Jan-08		0:06:20		65.6		41		17-Jan-08		0:07:53		66.81		39.5		27-Feb-08		0:25:59		68		43.5

		17-Jan-08		2:07:10		65.01		40.5		17-Jan-08		2:06:20		65.6		39		17-Jan-08		2:07:53		65.6		39.5		27-Feb-08		2:25:59		66.81		43.5

		17-Jan-08		4:07:10		63.8		40		17-Jan-08		4:06:20		65.6		38.5		17-Jan-08		4:07:53		64.4		39.5		27-Feb-08		4:25:59		65.6		43.5

		17-Jan-08		6:07:10		63.8		39.5		17-Jan-08		6:06:20		65.6		37		17-Jan-08		6:07:53		66.2		37		27-Feb-08		6:25:59		66.81		43.5

		17-Jan-08		8:07:10		64.4		38.5		17-Jan-08		8:06:20		68		34.5		17-Jan-08		8:07:53		69.2		35.5		27-Feb-08		8:25:59		71.6		41

		17-Jan-08		10:07:10		65.01		35		17-Jan-08		10:06:20		70.41		29.5		17-Jan-08		10:07:53		71.6		31		27-Feb-08		10:25:59		72.21		41

		17-Jan-08		12:07:10		66.2		29		17-Jan-08		12:06:20		71		21.5		17-Jan-08		12:07:53		69.8		23.5		27-Feb-08		12:25:59		72.21		42.5

		17-Jan-08		14:07:10		67.4		27		17-Jan-08		14:06:20		71		22.5		17-Jan-08		14:07:53		71		23.5		27-Feb-08		14:25:59		74.01		40

		17-Jan-08		16:07:10		68		25		17-Jan-08		16:06:20		70.41		21.5		17-Jan-08		16:07:53		70.41		24.5		27-Feb-08		16:25:59		74.01		40

		17-Jan-08		18:07:10		68.61		24		17-Jan-08		18:06:20		69.8		19		17-Jan-08		18:07:53		69.8		22.5		27-Feb-08		18:25:59		74.01		41.5

		17-Jan-08		20:07:10		68.61		22		17-Jan-08		20:06:20		69.8		18		17-Jan-08		20:07:53		70.41		23		27-Feb-08		20:25:59		72.8		42.5

		17-Jan-08		22:07:10		68.61		20.5		17-Jan-08		22:06:20		69.2		17.5		17-Jan-08		22:07:53		70.41		24		27-Feb-08		22:25:59		71.6		43

		18-Jan-08		0:07:10		68		20		18-Jan-08		0:06:20		68		18		18-Jan-08		0:07:53		69.2		23		28-Feb-08		0:25:59		69.8		43

		18-Jan-08		2:07:10		67.4		21.5		18-Jan-08		2:06:20		66.2		22		18-Jan-08		2:07:53		68		24		28-Feb-08		2:25:59		68.61		44

		18-Jan-08		4:07:10		66.2		21		18-Jan-08		4:06:20		66.2		20		18-Jan-08		4:07:53		66.81		23.5		28-Feb-08		4:25:59		67.4		44

		18-Jan-08		6:07:10		65.6		24.5		18-Jan-08		6:06:20		65.6		26		18-Jan-08		6:07:53		65.6		26		28-Feb-08		6:25:59		67.4		43.5

		18-Jan-08		8:07:10		65.6		26.5		18-Jan-08		8:06:20		67.4		26		18-Jan-08		8:07:53		69.8		26		28-Feb-08		8:25:59		71		41

		18-Jan-08		10:07:10		66.81		29		18-Jan-08		10:06:20		70.41		27.5		18-Jan-08		10:07:53		71.6		27		28-Feb-08		10:25:59		72.21		41

		18-Jan-08		12:07:10		67.4		28.5		18-Jan-08		12:06:20		71		26.5		18-Jan-08		12:07:53		71		28		28-Feb-08		12:25:59		72.8		42.5

		18-Jan-08		14:07:10		68		29		18-Jan-08		14:06:20		71		28		18-Jan-08		14:07:53		71		29		28-Feb-08		14:25:59		74.01		42.5

		18-Jan-08		16:07:10		68.61		29		18-Jan-08		16:06:20		70.41		29.5		18-Jan-08		16:07:53		71		31.5		28-Feb-08		16:25:59		75.2		43.5

		18-Jan-08		18:07:10		69.2		30		18-Jan-08		18:06:20		69.8		29.5		18-Jan-08		18:07:53		70.41		31.5		28-Feb-08		18:25:59		74.6		43.5

		18-Jan-08		20:07:10		69.2		32		18-Jan-08		20:06:20		68.61		34		18-Jan-08		20:07:53		71		32.5		28-Feb-08		20:25:59		72.21		44

		18-Jan-08		22:07:10		68		32		18-Jan-08		22:06:20		66.81		34.5		18-Jan-08		22:07:53		69.8		32		28-Feb-08		22:25:59		71.6		44.5

		19-Jan-08		0:07:10		66.81		32.5		19-Jan-08		0:06:20		66.2		34		19-Jan-08		0:07:53		68		32.5		29-Feb-08		0:25:59		69.2		44

		19-Jan-08		2:07:10		66.2		32.5		19-Jan-08		2:06:20		65.6		33		19-Jan-08		2:07:53		66.2		32.5		29-Feb-08		2:25:59		68		43.5

		19-Jan-08		4:07:10		65.01		32.5		19-Jan-08		4:06:20		65.6		32.5		19-Jan-08		4:07:53		65.01		32.5		29-Feb-08		4:25:59		66.81		43

		19-Jan-08		6:07:10		64.4		32.5		19-Jan-08		6:06:20		65.6		32		19-Jan-08		6:07:53		67.4		30		29-Feb-08		6:25:59		67.4		42.5

		19-Jan-08		8:07:10		65.01		32		19-Jan-08		8:06:20		68		29.5		19-Jan-08		8:07:53		69.2		31		29-Feb-08		8:25:59		70.41		40

		19-Jan-08		10:07:10		65.6		33		19-Jan-08		10:06:20		68.61		31		19-Jan-08		10:07:53		71.6		30		29-Feb-08		10:25:59		72.21		40.5

		19-Jan-08		12:07:10		65.6		35.5		19-Jan-08		12:06:20		70.41		33.5		19-Jan-08		12:07:53		71		30.5		29-Feb-08		12:25:59		73.4		42

		19-Jan-08		14:07:10		66.2		35.5		19-Jan-08		14:06:20		70.41		33.5		19-Jan-08		14:07:53		71		34.5		29-Feb-08		14:25:59		74.6		41.5

		19-Jan-08		16:07:10		67.4		35		19-Jan-08		16:06:20		71		32		19-Jan-08		16:07:53		71		34.5		29-Feb-08		16:25:59		74.6		41.5

		19-Jan-08		18:07:10		68		35.5		19-Jan-08		18:06:20		69.8		34		19-Jan-08		18:07:53		70.41		35		29-Feb-08		18:25:59		74.01		43.5

		19-Jan-08		20:07:10		68		34		19-Jan-08		20:06:20		68		34.5		19-Jan-08		20:07:53		69.8		34		29-Feb-08		20:25:59		72.21		42.5

		19-Jan-08		22:07:10		67.4		34.5		19-Jan-08		22:06:20		66.2		36.5		19-Jan-08		22:07:53		68.61		35		29-Feb-08		22:25:59		71		43.5

		20-Jan-08		0:07:10		66.2		34		20-Jan-08		0:06:20		65.6		35		20-Jan-08		0:07:53		67.4		34		1-Mar-08		0:25:59		69.8		43

		20-Jan-08		2:07:10		65.6		34		20-Jan-08		2:06:20		65.6		34		20-Jan-08		2:07:53		65.6		34		1-Mar-08		2:25:59		68.61		43.5

		20-Jan-08		4:07:10		64.4		33		20-Jan-08		4:06:20		65.6		33		20-Jan-08		4:07:53		64.4		33.5		1-Mar-08		4:25:59		68		44

		20-Jan-08		6:07:10		63.8		32.5		20-Jan-08		6:06:20		65.6		31		20-Jan-08		6:07:53		63.21		33.5		1-Mar-08		6:25:59		68		44.5

		20-Jan-08		8:07:10		63.8		31.5		20-Jan-08		8:06:20		67.4		28		20-Jan-08		8:07:53		67.4		29		1-Mar-08		8:25:59		71.6		42

		20-Jan-08		10:07:10		63.8		32		20-Jan-08		10:06:20		68		30		20-Jan-08		10:07:53		66.81		29.5		1-Mar-08		10:25:59		72.8		41.5

		20-Jan-08		12:07:10		64.4		36.5		20-Jan-08		12:06:20		68.61		35		20-Jan-08		12:07:53		67.4		33		1-Mar-08		12:25:59		72.21		43

		20-Jan-08		14:07:10		65.01		37		20-Jan-08		14:06:20		68.61		35		20-Jan-08		14:07:53		67.4		35.5		1-Mar-08		14:25:59		72.8		44

		20-Jan-08		16:07:10		66.2		36.5		20-Jan-08		16:06:20		69.8		33.5		20-Jan-08		16:07:53		68.61		35.5		1-Mar-08		16:25:59		74.01		45

		20-Jan-08		18:07:10		66.81		36.5		20-Jan-08		18:06:20		69.2		34.5		20-Jan-08		18:07:53		69.8		35.5		1-Mar-08		18:25:59		73.4		43.5

		20-Jan-08		20:07:10		66.81		34.5		20-Jan-08		20:06:20		68		33.5		20-Jan-08		20:07:53		69.2		34		1-Mar-08		20:25:59		72.21		43

		20-Jan-08		22:07:10		66.2		35		20-Jan-08		22:06:20		66.2		35.5		20-Jan-08		22:07:53		67.4		34.5		1-Mar-08		22:25:59		71		43

		21-Jan-08		0:07:10		65.01		35		21-Jan-08		0:06:20		65.6		35		21-Jan-08		0:07:53		65.6		34.5		2-Mar-08		0:25:59		69.2		43

		21-Jan-08		2:07:10		64.4		38.5		21-Jan-08		2:06:20		65.6		39		21-Jan-08		2:07:53		65.01		37		2-Mar-08		2:25:59		68.61		44

		21-Jan-08		4:07:10		64.4		38.5		21-Jan-08		4:06:20		65.6		38		21-Jan-08		4:07:53		64.4		38		2-Mar-08		4:25:59		67.4		44.5

		21-Jan-08		6:07:10		63.8		37		21-Jan-08		6:06:20		65.6		36		21-Jan-08		6:07:53		63.8		37.5		2-Mar-08		6:25:59		67.4		44.5

		21-Jan-08		8:07:10		63.8		38		21-Jan-08		8:06:20		67.4		35		21-Jan-08		8:07:53		66.81		34.5		2-Mar-08		8:25:59		67.4		44

		21-Jan-08		10:07:10		63.8		38.5		21-Jan-08		10:06:20		68		35		21-Jan-08		10:07:53		66.81		35.5		2-Mar-08		10:25:59		68		43.5

		21-Jan-08		12:07:10		64.4		40		21-Jan-08		12:06:20		68		36.5		21-Jan-08		12:07:53		67.4		36		2-Mar-08		12:25:59		69.2		42

		21-Jan-08		14:07:10		64.4		35		21-Jan-08		14:06:20		68		31		21-Jan-08		14:07:53		67.4		33.5		2-Mar-08		14:25:59		70.41		40.5

		21-Jan-08		16:07:10		65.01		34.5		21-Jan-08		16:06:20		68		32		21-Jan-08		16:07:53		67.4		34		2-Mar-08		16:25:59		69.8		39

		21-Jan-08		18:07:10		65.6		33.5		21-Jan-08		18:06:20		68		31		21-Jan-08		18:07:53		67.4		33.5		2-Mar-08		18:25:59		69.8		38

		21-Jan-08		20:07:10		65.6		34.5		21-Jan-08		20:06:20		66.2		34		21-Jan-08		20:07:53		66.81		34		2-Mar-08		20:25:59		68.61		39

		21-Jan-08		22:07:10		65.01		34.5		21-Jan-08		22:06:20		65.6		34		21-Jan-08		22:07:53		65.01		34.5		2-Mar-08		22:25:59		67.4		39.5

		22-Jan-08		0:07:10		64.4		34.5		22-Jan-08		0:06:20		65.6		33.5		22-Jan-08		0:07:53		63.8		35		3-Mar-08		0:25:59		66.81		40

		22-Jan-08		2:07:10		63.8		34		22-Jan-08		2:06:20		65.01		32		22-Jan-08		2:07:53		62.6		34		3-Mar-08		2:25:59		65.6		40

		22-Jan-08		4:07:10		63.21		32.5		22-Jan-08		4:06:20		65.01		30.5		22-Jan-08		4:07:53		61.41		33.5		3-Mar-08		4:25:59		65.01		39.5

		22-Jan-08		6:07:10		62.6		31.5		22-Jan-08		6:06:20		65.01		30		22-Jan-08		6:07:53		66.81		29.5		3-Mar-08		6:25:59		64.4		39.5

		22-Jan-08		8:07:10		63.21		32		22-Jan-08		8:06:20		67.4		28.5		22-Jan-08		8:07:53		68		30		3-Mar-08		8:25:59		65.01		38.5

		22-Jan-08		10:07:10		64.4		33.5		22-Jan-08		10:06:20		69.2		30		22-Jan-08		10:07:53		70.41		30.5		3-Mar-08		10:25:59		66.2		38

		22-Jan-08		12:07:10		65.01		36		22-Jan-08		12:06:20		70.41		32.5		22-Jan-08		12:07:53		71.6		31		3-Mar-08		12:25:59		66.81		38

		22-Jan-08		14:07:10		66.2		37.5		22-Jan-08		14:06:20		71		35.5		22-Jan-08		14:07:53		71		36		3-Mar-08		14:25:59		67.4		35.5

		22-Jan-08		16:07:10		66.81		39		22-Jan-08		16:06:20		71		34.5		22-Jan-08		16:07:53		70.41		37		3-Mar-08		16:25:59		68.61		33.5

		22-Jan-08		18:07:10		67.4		37		22-Jan-08		18:06:20		68.61		36		22-Jan-08		18:07:53		69.8		36		3-Mar-08		18:25:59		68.61		31.5

		22-Jan-08		20:07:10		67.4		36.5		22-Jan-08		20:06:20		68		36.5		22-Jan-08		20:07:53		69.8		35		3-Mar-08		20:25:59		68.61		31

		22-Jan-08		22:07:10		66.81		37		22-Jan-08		22:06:20		67.4		36.5		22-Jan-08		22:07:53		67.4		36		3-Mar-08		22:25:59		68		33

		23-Jan-08		0:07:10		65.6		37.5		23-Jan-08		0:06:20		67.4		36.5		23-Jan-08		0:07:53		65.6		37.5		4-Mar-08		0:25:59		66.81		35

		23-Jan-08		2:07:10		65.01		37		23-Jan-08		2:06:20		67.4		35.5		23-Jan-08		2:07:53		65.01		38		4-Mar-08		2:25:59		66.2		37

		23-Jan-08		4:07:10		64.4		37.5		23-Jan-08		4:06:20		66.81		35.5		23-Jan-08		4:07:53		63.8		38.5		4-Mar-08		4:25:59		65.6		37.5

		23-Jan-08		6:07:10		64.4		37		23-Jan-08		6:06:20		66.81		35		23-Jan-08		6:07:53		67.4		35.5		4-Mar-08		6:25:59		66.2		37.5

		23-Jan-08		8:07:10		65.01		36		23-Jan-08		8:06:20		68		33		23-Jan-08		8:07:53		69.2		34		4-Mar-08		8:25:59		69.2		35.5

		23-Jan-08		10:07:10		65.6		36.5		23-Jan-08		10:06:20		69.2		34		23-Jan-08		10:07:53		71		35		4-Mar-08		10:25:59		71.6		36.5

		23-Jan-08		12:07:10		66.2		36		23-Jan-08		12:06:20		69.8		33		23-Jan-08		12:07:53		71		34		4-Mar-08		12:25:59		72.21		36.5

		23-Jan-08		14:07:10		66.81		34.5		23-Jan-08		14:06:20		70.41		32		23-Jan-08		14:07:53		70.41		35		4-Mar-08		14:25:59		73.4		33.5

		23-Jan-08		16:07:10		66.81		33.5		23-Jan-08		16:06:20		69.8		31.5		23-Jan-08		16:07:53		70.41		32		4-Mar-08		16:25:59		74.01		33.5

		23-Jan-08		18:07:10		66.81		33		23-Jan-08		18:06:20		69.2		31		23-Jan-08		18:07:53		69.2		32		4-Mar-08		18:25:59		74.01		33

		23-Jan-08		20:07:10		66.81		32.5		23-Jan-08		20:06:20		68		31		23-Jan-08		20:07:53		68		32.5		4-Mar-08		20:25:59		72.21		32

		23-Jan-08		22:07:10		66.2		32.5		23-Jan-08		22:06:20		67.4		32		23-Jan-08		22:07:53		68		32.5		4-Mar-08		22:25:59		71		33.5

		24-Jan-08		0:07:10		65.6		33.5		24-Jan-08		0:06:20		66.81		32.5		24-Jan-08		0:07:53		66.2		33		5-Mar-08		0:25:59		69.2		34.5

		24-Jan-08		2:07:10		65.01		34		24-Jan-08		2:06:20		67.4		32.5		24-Jan-08		2:07:53		64.4		34.5		5-Mar-08		2:25:59		68		35.5

		24-Jan-08		4:07:10		64.4		35.5		24-Jan-08		4:06:20		67.4		34		24-Jan-08		4:07:53		63.8		36		5-Mar-08		4:25:59		66.81		36

		24-Jan-08		6:07:10		64.4		37		24-Jan-08		6:06:20		66.81		35		24-Jan-08		6:07:53		68		34		5-Mar-08		6:25:59		66.81		36.5

		24-Jan-08		8:07:10		65.01		37		24-Jan-08		8:06:20		68		35		24-Jan-08		8:07:53		69.2		35.5		5-Mar-08		8:25:59		69.8		34

		24-Jan-08		10:07:10		65.6		38		24-Jan-08		10:06:20		71		33.5		24-Jan-08		10:07:53		71		35		5-Mar-08		10:25:59		72.21		36

		24-Jan-08		12:07:10		66.81		39		24-Jan-08		12:06:20		71		36		24-Jan-08		12:07:53		71		37		5-Mar-08		12:25:59		72.8		36.5

		24-Jan-08		14:07:10		68		38		24-Jan-08		14:06:20		71		37		24-Jan-08		14:07:53		71		38.5		5-Mar-08		14:25:59		74.01		36.5

		24-Jan-08		16:07:10		68		36		24-Jan-08		16:06:20		71		34		24-Jan-08		16:07:53		71.6		35		5-Mar-08		16:25:59		74.6		35.5

		24-Jan-08		18:07:10		68.61		34.5		24-Jan-08		18:06:20		68.61		33.5		24-Jan-08		18:07:53		71		34		5-Mar-08		18:25:59		74.6		36.5

		24-Jan-08		20:07:10		68		35.5		24-Jan-08		20:06:20		68		36.5		24-Jan-08		20:07:53		69.8		35		5-Mar-08		20:25:59		72.8		37

		24-Jan-08		22:07:10		67.4		36.5		24-Jan-08		22:06:20		67.4		37		24-Jan-08		22:07:53		68		36		5-Mar-08		22:25:59		71		37

		25-Jan-08		0:07:10		66.2		36.5		25-Jan-08		0:06:20		67.4		36		25-Jan-08		0:07:53		66.2		37		6-Mar-08		0:25:59		69.2		37

		25-Jan-08		2:07:10		65.6		37.5		25-Jan-08		2:06:20		66.81		37		25-Jan-08		2:07:53		65.01		38		6-Mar-08		2:25:59		68		37.5

		25-Jan-08		4:07:10		65.01		39		25-Jan-08		4:06:20		67.4		37.5		25-Jan-08		4:07:53		64.4		39.5		6-Mar-08		4:25:59		66.81		38

		25-Jan-08		6:07:10		64.4		39.5		25-Jan-08		6:06:20		67.4		38		25-Jan-08		6:07:53		66.81		38		6-Mar-08		6:25:59		66.81		37.5

		25-Jan-08		8:07:10		65.01		39		25-Jan-08		8:06:20		68		36.5		25-Jan-08		8:07:53		69.2		36		6-Mar-08		8:25:59		70.41		35.5

		25-Jan-08		10:07:10		65.6		40.5		25-Jan-08		10:06:20		69.8		37		25-Jan-08		10:07:53		71.6		36		6-Mar-08		10:25:59		71.6		36.5

		25-Jan-08		12:07:10		66.81		39.5		25-Jan-08		12:06:20		69.8		37.5		25-Jan-08		12:07:53		72.21		36		6-Mar-08		12:25:59		72.8		35.5

		25-Jan-08		14:07:10		67.4		38		25-Jan-08		14:06:20		69.8		37.5		25-Jan-08		14:07:53		71		37.5		6-Mar-08		14:25:59		74.01		32.5

		25-Jan-08		16:07:10		68.61		37.5		25-Jan-08		16:06:20		70.41		37		25-Jan-08		16:07:53		70.41		38		6-Mar-08		16:25:59		74.6		31

		25-Jan-08		18:07:10		68.61		36		25-Jan-08		18:06:20		68		36.5		25-Jan-08		18:07:53		69.8		36		6-Mar-08		18:25:59		68.61		44.5

		25-Jan-08		20:07:10		68.61		35		25-Jan-08		20:06:20		67.4		37		25-Jan-08		20:07:53		68.61		36		6-Mar-08		20:25:59		68.61		44

		25-Jan-08		22:07:10		68		35.5		25-Jan-08		22:06:20		66.81		37		25-Jan-08		22:07:53		67.4		37.5		6-Mar-08		22:25:59		68.61		42.5

		26-Jan-08		0:07:10		67.4		35.5		26-Jan-08		0:06:20		66.81		36		26-Jan-08		0:07:53		66.81		37.5		7-Mar-08		0:25:59		68.61		44

		26-Jan-08		2:07:10		66.81		36		26-Jan-08		2:06:20		66.81		36.5		26-Jan-08		2:07:53		65.6		37.5		7-Mar-08		2:25:59		68		43

		26-Jan-08		4:07:10		66.2		35		26-Jan-08		4:06:20		66.81		35		26-Jan-08		4:07:53		65.6		37.5		7-Mar-08		4:25:59		69.2		44

		26-Jan-08		6:07:10		65.6		37.5		26-Jan-08		6:06:20		66.81		38		26-Jan-08		6:07:53		68.61		36.5		7-Mar-08		6:25:59		68.61		43.5

		26-Jan-08		8:07:10		66.2		39.5		26-Jan-08		8:06:20		67.4		40		26-Jan-08		8:07:53		69.2		38.5		7-Mar-08		8:25:59		68.61		44.5

		26-Jan-08		10:07:10		67.4		42		26-Jan-08		10:06:20		69.8		42		26-Jan-08		10:07:53		71.6		40.5		7-Mar-08		10:25:59		68.61		44.5

		26-Jan-08		12:07:10		68.61		41		26-Jan-08		12:06:20		69.2		42.5		26-Jan-08		12:07:53		71		43		7-Mar-08		12:25:59		68.61		45

		26-Jan-08		14:07:10		69.8		42		26-Jan-08		14:06:20		71		44		26-Jan-08		14:07:53		71		38.5		7-Mar-08		14:25:59		68.61		45

		26-Jan-08		16:07:10		70.41		43.5		26-Jan-08		16:06:20		70.41		46.5		26-Jan-08		16:07:53		70.41		44.5		7-Mar-08		16:25:59		68.61		44

		26-Jan-08		18:07:10		69.8		42.5		26-Jan-08		18:06:20		68.61		45.5		26-Jan-08		18:07:53		69.2		44		7-Mar-08		18:25:59		68.61		44.5

		26-Jan-08		20:07:10		69.2		44.5		26-Jan-08		20:06:20		68		48		26-Jan-08		20:07:53		68.61		45.5		7-Mar-08		20:25:59		68.61		46.5

		26-Jan-08		22:07:10		68.61		46.5		26-Jan-08		22:06:20		68		49.5		26-Jan-08		22:07:53		68		47.5		7-Mar-08		22:25:59		68.61		45.5

		27-Jan-08		0:07:10		68.61		47.5		27-Jan-08		0:06:20		67.4		51		27-Jan-08		0:07:53		67.4		48		8-Mar-08		0:25:59		68.61		44.5

		27-Jan-08		2:07:10		68		48.5		27-Jan-08		2:06:20		67.4		51.5		27-Jan-08		2:07:53		67.4		48.5		8-Mar-08		2:25:59		68		45

		27-Jan-08		4:07:10		68		49		27-Jan-08		4:06:20		67.4		51		27-Jan-08		4:07:53		67.4		49		8-Mar-08		4:25:59		68		44

		27-Jan-08		6:07:10		67.4		48		27-Jan-08		6:06:20		67.4		49		27-Jan-08		6:07:53		66.81		49		8-Mar-08		6:25:59		68		45

		27-Jan-08		8:07:10		67.4		44.5		27-Jan-08		8:06:20		68		43.5		27-Jan-08		8:07:53		68		45.5		8-Mar-08		8:25:59		68.61		45

		27-Jan-08		10:07:10		67.4		40.5		27-Jan-08		10:06:20		67.4		39.5		27-Jan-08		10:07:53		68		43		8-Mar-08		10:25:59		68.61		45

		27-Jan-08		12:07:10		67.4		39.5		27-Jan-08		12:06:20		67.4		39		27-Jan-08		12:07:53		67.4		42		8-Mar-08		12:25:59		68.61		45

		27-Jan-08		14:07:10		67.4		39		27-Jan-08		14:06:20		68		38.5		27-Jan-08		14:07:53		68		42		8-Mar-08		14:25:59		68.61		45

		27-Jan-08		16:07:10		67.4		39.5		27-Jan-08		16:06:20		68		39		27-Jan-08		16:07:53		68		41		8-Mar-08		16:25:59		68.61		45

		27-Jan-08		18:07:10		68		40		27-Jan-08		18:06:20		68.61		40.5		27-Jan-08		18:07:53		68.61		41.5		8-Mar-08		18:25:59		68.61		44.5

		27-Jan-08		20:07:10		68		39.5		27-Jan-08		20:06:20		67.4		40.5		27-Jan-08		20:07:53		68		42		8-Mar-08		20:25:59		68.61		45.5

		27-Jan-08		22:07:10		67.4		41		27-Jan-08		22:06:20		67.4		42		27-Jan-08		22:07:53		67.4		42.5		8-Mar-08		22:25:59		68.61		45

		28-Jan-08		0:07:10		67.4		43.5		28-Jan-08		0:06:20		67.4		46.5		28-Jan-08		0:07:53		67.4		44		9-Mar-08		0:25:59		68		45

		28-Jan-08		2:07:10		66.81		47.5		28-Jan-08		2:06:20		67.4		49		28-Jan-08		2:07:53		66.81		46.5		9-Mar-08		2:25:59		68		45

		28-Jan-08		4:07:10		66.81		46.5		28-Jan-08		4:06:20		67.4		47		28-Jan-08		4:07:53		66.81		46.5		9-Mar-08		4:25:59		68.61		45

		28-Jan-08		6:07:10		66.81		47.5		28-Jan-08		6:06:20		67.4		48.5		28-Jan-08		6:07:53		66.81		47.5		9-Mar-08		6:25:59		68.61		44.5

		28-Jan-08		8:07:10		66.81		48.5		28-Jan-08		8:06:20		68		48.5		28-Jan-08		8:07:53		67.4		47		9-Mar-08		8:25:59		68.61		45.5

		28-Jan-08		10:07:10		66.81		49.5		28-Jan-08		10:06:20		68		49		28-Jan-08		10:07:53		67.4		47.5		9-Mar-08		10:25:59		68.61		45

		28-Jan-08		12:07:10		66.81		48		28-Jan-08		12:06:20		68		47.5		28-Jan-08		12:07:53		68		47.5		9-Mar-08		12:25:59		68.61		45.5

		28-Jan-08		14:07:10		66.81		45.5		28-Jan-08		14:06:20		68		45		28-Jan-08		14:07:53		68		46		9-Mar-08		14:25:59		68.61		45

		28-Jan-08		16:07:10		67.4		47.5		28-Jan-08		16:06:20		68		49		28-Jan-08		16:07:53		68		47.5		9-Mar-08		16:25:59		68.61		45

		28-Jan-08		18:07:10		68		48.5		28-Jan-08		18:06:20		68		49		28-Jan-08		18:07:53		67.4		48.5		9-Mar-08		18:25:59		68.61		45

		28-Jan-08		20:07:10		68		49		28-Jan-08		20:06:20		67.4		50.5		28-Jan-08		20:07:53		67.4		49		9-Mar-08		20:25:59		68.61		46

		28-Jan-08		22:07:10		67.4		40.5		28-Jan-08		22:06:20		66.81		37.5		28-Jan-08		22:07:53		66.2		41.5		9-Mar-08		22:25:59		68.61		45

		29-Jan-08		0:07:10		66.2		36.5		29-Jan-08		0:06:20		66.2		35		29-Jan-08		0:07:53		63.8		38		10-Mar-08		0:25:59		68		45

		29-Jan-08		2:07:10		65.6		36.5		29-Jan-08		2:06:20		66.81		35.5		29-Jan-08		2:07:53		63.21		39		10-Mar-08		2:25:59		68.61		45

		29-Jan-08		4:07:10		65.6		36.5		29-Jan-08		4:06:20		66.81		35		29-Jan-08		4:07:53		62.6		39.5		10-Mar-08		4:25:59		68.61		45.5

		29-Jan-08		6:07:10		65.6		36		29-Jan-08		6:06:20		66.81		35		29-Jan-08		6:07:53		66.81		36.5		10-Mar-08		6:25:59		68.61		45.5

		29-Jan-08		8:07:10		65.6		36		29-Jan-08		8:06:20		67.4		34.5		29-Jan-08		8:07:53		69.2		35		10-Mar-08		8:25:59		68		45.5

		29-Jan-08		10:07:10		66.2		37.5		29-Jan-08		10:06:20		69.8		34.5		29-Jan-08		10:07:53		70.41		36.5		10-Mar-08		10:25:59		68		45.5

		29-Jan-08		12:07:10		67.4		37.5		29-Jan-08		12:06:20		70.41		35.5		29-Jan-08		12:07:53		71		37		10-Mar-08		12:25:59		68.61		45.5

		29-Jan-08		14:07:10		68.61		35		29-Jan-08		14:06:20		71		31		29-Jan-08		14:07:53		70.41		38		10-Mar-08		14:25:59		68.61		45

		29-Jan-08		16:07:10		69.2		34.5		29-Jan-08		16:06:20		69.8		34		29-Jan-08		16:07:53		70.41		35.5		10-Mar-08		16:25:59		68.61		45.5

		29-Jan-08		18:07:10		69.8		33.5		29-Jan-08		18:06:20		69.2		34		29-Jan-08		18:07:53		69.8		35		10-Mar-08		18:25:59		68.61		45

		29-Jan-08		20:07:10		69.2		32.5		29-Jan-08		20:06:20		67.4		33.5		29-Jan-08		20:07:53		68		35		10-Mar-08		20:25:59		68.61		45

		29-Jan-08		22:07:10		68.61		32.5		29-Jan-08		22:06:20		67.4		33.5		29-Jan-08		22:07:53		66.2		35.5		10-Mar-08		22:25:59		68		45

		30-Jan-08		0:07:10		68		31.5		30-Jan-08		0:06:20		66.81		32.5		30-Jan-08		0:07:53		65.01		35.5		11-Mar-08		0:25:59		68.61		45

		30-Jan-08		2:07:10		67.4		30.5		30-Jan-08		2:06:20		66.81		30.5		30-Jan-08		2:07:53		63.21		34.5		11-Mar-08		2:25:59		68.61		45

		30-Jan-08		4:07:10		66.81		30		30-Jan-08		4:06:20		66.81		30		30-Jan-08		4:07:53		62		34		11-Mar-08		4:25:59		68.61		46

		30-Jan-08		6:07:10		66.81		31		30-Jan-08		6:06:20		66.81		31		30-Jan-08		6:07:53		67.4		31.5		11-Mar-08		6:25:59		68.61		45.5

		30-Jan-08		8:07:10		66.81		31.5		30-Jan-08		8:06:20		67.4		31.5		30-Jan-08		8:07:53		69.2		33		11-Mar-08		8:25:59		68.61		44.5

		30-Jan-08		10:07:10		67.4		33.5		30-Jan-08		10:06:20		69.8		32.5		30-Jan-08		10:07:53		70.41		35		11-Mar-08		10:25:59		68		45

		30-Jan-08		12:07:10		68.61		36		30-Jan-08		12:06:20		71		36		30-Jan-08		12:07:53		71		37.5		11-Mar-08		12:25:59		68.61		46

		30-Jan-08		14:07:10		69.8		39		30-Jan-08		14:06:20		71.6		40.5		30-Jan-08		14:07:53		71		42		11-Mar-08		14:25:59		68		49.5

		30-Jan-08		16:07:10		71.6		40.5		30-Jan-08		16:06:20		71.6		43		30-Jan-08		16:07:53		71		42		11-Mar-08		16:25:59		68.61		46

		30-Jan-08		18:07:10		71		36		30-Jan-08		18:06:20		68.61		36.5		30-Jan-08		18:07:53		69.8		38		11-Mar-08		18:25:59		68		45

		30-Jan-08		20:07:10		70.41		33		30-Jan-08		20:06:20		68		34		30-Jan-08		20:07:53		68.61		36.5		11-Mar-08		20:25:59		68.61		45

		30-Jan-08		22:07:10		69.8		31.5		30-Jan-08		22:06:20		68		32.5		30-Jan-08		22:07:53		67.4		36		11-Mar-08		22:25:59		68.61		45.5

		31-Jan-08		0:07:10		69.2		32		31-Jan-08		0:06:20		68		33.5		31-Jan-08		0:07:53		65.6		36.5		12-Mar-08		0:25:59		68.61		45

		31-Jan-08		2:07:10		68.61		33		31-Jan-08		2:06:20		68		34		31-Jan-08		2:07:53		65.01		37		12-Mar-08		2:25:59		68		45

		31-Jan-08		4:07:10		68.61		33.5		31-Jan-08		4:06:20		68		34.5		31-Jan-08		4:07:53		64.4		38		12-Mar-08		4:25:59		68		46

		31-Jan-08		6:07:10		68		33.5		31-Jan-08		6:06:20		68		34.5		31-Jan-08		6:07:53		66.81		36		12-Mar-08		6:25:59		68		45

		31-Jan-08		8:07:10		69.8		32.5		31-Jan-08		8:06:20		68		34		31-Jan-08		8:07:53		68.61		35.5		12-Mar-08		8:25:59		68.61		46

		31-Jan-08		10:07:10		71.6		33		31-Jan-08		10:06:20		71		34.5		31-Jan-08		10:07:53		71.6		36.5		12-Mar-08		10:25:59		68.61		45.5

		31-Jan-08		12:07:10		71.6		33.5		31-Jan-08		12:06:20		71		33.5		31-Jan-08		12:07:53		70.41		38		12-Mar-08		12:25:59		68		46

		31-Jan-08		14:07:10		71.6		33.5		31-Jan-08		14:06:20		71		36		31-Jan-08		14:07:53		71.6		36		12-Mar-08		14:25:59		68		46.5

		31-Jan-08		16:07:10		71.6		33.5		31-Jan-08		16:06:20		71		35.5		31-Jan-08		16:07:53		69.8		37		12-Mar-08		16:25:59		68.61		48.5

		31-Jan-08		18:07:10		71		34		31-Jan-08		18:06:20		68.61		37		31-Jan-08		18:07:53		71		36.5		12-Mar-08		18:25:59		68.61		47.5

		31-Jan-08		20:07:10		69.2		36		31-Jan-08		20:06:20		68.61		38		31-Jan-08		20:07:53		70.41		37.5		12-Mar-08		20:25:59		68.61		45.5

		31-Jan-08		22:07:10		67.4		37.5		31-Jan-08		22:06:20		68		38		31-Jan-08		22:07:53		69.2		38.5		12-Mar-08		22:25:59		68.61		45.5

		1-Feb-08		0:07:10		66.2		39		1-Feb-08		0:06:20		68		38		1-Feb-08		0:07:53		67.4		39		13-Mar-08		0:25:59		68		46

		1-Feb-08		2:07:10		65.01		40.5		1-Feb-08		2:06:20		68		38		1-Feb-08		2:07:53		66.2		40		13-Mar-08		2:25:59		68		45

		1-Feb-08		4:07:10		64.4		42		1-Feb-08		4:06:20		68		39		1-Feb-08		4:07:53		65.6		41		13-Mar-08		4:25:59		68.61		45

		1-Feb-08		6:07:10		63.8		43		1-Feb-08		6:06:20		68		39		1-Feb-08		6:07:53		66.81		40.5		13-Mar-08		6:25:59		68.61		45

		1-Feb-08		8:07:10		66.2		42		1-Feb-08		8:06:20		68		40.5		1-Feb-08		8:07:53		69.8		40		13-Mar-08		8:25:59		68.61		45.5

		1-Feb-08		10:07:10		68.61		42		1-Feb-08		10:06:20		71		41.5		1-Feb-08		10:07:53		71.6		42		13-Mar-08		10:25:59		68		45.5

		1-Feb-08		12:07:10		69.2		43		1-Feb-08		12:06:20		71		43		1-Feb-08		12:07:53		71		46		13-Mar-08		12:25:59		68.61		45

		1-Feb-08		14:07:10		69.8		45		1-Feb-08		14:06:20		71		44		1-Feb-08		14:07:53		71		40		13-Mar-08		14:25:59		68.61		47

		1-Feb-08		16:07:10		70.41		46.5		1-Feb-08		16:06:20		71		45		1-Feb-08		16:07:53		70.41		48		13-Mar-08		16:25:59		68.61		47

		1-Feb-08		18:07:10		69.2		48.5		1-Feb-08		18:06:20		69.2		50		1-Feb-08		18:07:53		70.41		48		13-Mar-08		18:25:59		68		45.5

		1-Feb-08		20:07:10		68		44.5		1-Feb-08		20:06:20		68.61		43.5		1-Feb-08		20:07:53		70.41		43.5		13-Mar-08		20:25:59		68.61		45

		1-Feb-08		22:07:10		66.81		41.5		1-Feb-08		22:06:20		68		39.5		1-Feb-08		22:07:53		69.2		41		13-Mar-08		22:25:59		68.61		45.5

		2-Feb-08		0:07:10		65.6		40		2-Feb-08		0:06:20		68		37.5		2-Feb-08		0:07:53		66.81		40		14-Mar-08		0:25:59		68.61		47.5

		2-Feb-08		2:07:10		64.4		38		2-Feb-08		2:06:20		68		34		2-Feb-08		2:07:53		64.4		39		14-Mar-08		2:25:59		68		46

		2-Feb-08		4:07:10		63.21		37.5		2-Feb-08		4:06:20		68		33		2-Feb-08		4:07:53		62.6		38		14-Mar-08		4:25:59		68		47

		2-Feb-08		6:07:10		62.6		36.5		2-Feb-08		6:06:20		68		32		2-Feb-08		6:07:53		67.4		33.5		14-Mar-08		6:25:59		68		46.5

		2-Feb-08		8:07:10		63.8		35		2-Feb-08		8:06:20		67.4		31.5		2-Feb-08		8:07:53		68		33.5		14-Mar-08		8:25:59		68.61		47.5

		2-Feb-08		10:07:10		66.2		36		2-Feb-08		10:06:20		71		33		2-Feb-08		10:07:53		70.41		35.5		14-Mar-08		10:25:59		68		48

		2-Feb-08		12:07:10		68.61		38		2-Feb-08		12:06:20		72.8		36		2-Feb-08		12:07:53		71		39.5		14-Mar-08		12:25:59		68.61		45.5

		2-Feb-08		14:07:10		69.2		38		2-Feb-08		14:06:20		71.6		36.5		2-Feb-08		14:07:53		69.8		39.5		14-Mar-08		14:25:59		68.61		45

		2-Feb-08		16:07:10		68.61		38		2-Feb-08		16:06:20		71		36.5		2-Feb-08		16:07:53		69.8		39		14-Mar-08		16:25:59		68.61		45

		2-Feb-08		18:07:10		68		37.5		2-Feb-08		18:06:20		71		35.5		2-Feb-08		18:07:53		71		39		14-Mar-08		18:25:59		68.61		45

		2-Feb-08		20:07:10		67.4		37		2-Feb-08		20:06:20		68.61		35.5		2-Feb-08		20:07:53		69.2		40		14-Mar-08		20:25:59		68.61		45

		2-Feb-08		22:07:10		66.81		36.5		2-Feb-08		22:06:20		68		34		2-Feb-08		22:07:53		67.4		44		14-Mar-08		22:25:59		68.61		45

		3-Feb-08		0:07:10		66.81		35.5		3-Feb-08		0:06:20		68		33		3-Feb-08		0:07:53		66.81		41		15-Mar-08		0:25:59		68.61		45.5

		3-Feb-08		2:07:10		66.2		35		3-Feb-08		2:06:20		68		33		3-Feb-08		2:07:53		65.6		42		15-Mar-08		2:25:59		68.61		46

		3-Feb-08		4:07:10		66.2		34.5		3-Feb-08		4:06:20		68		33		3-Feb-08		4:07:53		65.01		43		15-Mar-08		4:25:59		68.61		45.5

		3-Feb-08		6:07:10		66.2		34.5		3-Feb-08		6:06:20		68		33.5		3-Feb-08		6:07:53		64.4		44		15-Mar-08		6:25:59		68.61		46

		3-Feb-08		8:07:10		66.2		35.5		3-Feb-08		8:06:20		69.8		33		3-Feb-08		8:07:53		67.4		41.5		15-Mar-08		8:25:59		68.61		45.5

		3-Feb-08		10:07:10		66.2		36.5		3-Feb-08		10:06:20		66.81		36.5		3-Feb-08		10:07:53		67.4		42		15-Mar-08		10:25:59		68.61		45

		3-Feb-08		12:07:10		66.81		40		3-Feb-08		12:06:20		65.6		44.5		3-Feb-08		12:07:53		68		47.5		15-Mar-08		12:25:59		68.61		45

		3-Feb-08		14:07:10		66.2		43.5		3-Feb-08		14:06:20		66.2		47.5		3-Feb-08		14:07:53		67.4		49		15-Mar-08		14:25:59		68.61		44.5

		3-Feb-08		16:07:10		66.2		46		3-Feb-08		16:06:20		66.2		49		3-Feb-08		16:07:53		68		49		15-Mar-08		16:25:59		68		44.5

		3-Feb-08		18:07:10		66.2		47.5		3-Feb-08		18:06:20		66.2		50		3-Feb-08		18:07:53		68.61		51		15-Mar-08		18:25:59		68		44.5

		3-Feb-08		20:07:10		66.2		49.5		3-Feb-08		20:06:20		66.81		52		3-Feb-08		20:07:53		67.4		51.5		15-Mar-08		20:25:59		68.61		45

		3-Feb-08		22:07:10		66.2		51.5		3-Feb-08		22:06:20		66.81		53.5		3-Feb-08		22:07:53		68		54		15-Mar-08		22:25:59		68		45

		4-Feb-08		0:07:10		66.2		51.5		4-Feb-08		0:06:20		67.4		52.5		4-Feb-08		0:07:53		68		54		16-Mar-08		0:25:59		68		44.5

		4-Feb-08		2:07:10		66.2		49		4-Feb-08		2:06:20		66.81		48		4-Feb-08		2:07:53		67.4		50.5		16-Mar-08		2:25:59		68.61		44.5

		4-Feb-08		4:07:10		66.2		45		4-Feb-08		4:06:20		65.6		45		4-Feb-08		4:07:53		66.81		47.5		16-Mar-08		4:25:59		68		46

		4-Feb-08		6:07:10		65.6		43		4-Feb-08		6:06:20		65.6		44		4-Feb-08		6:07:53		66.81		47.5		16-Mar-08		6:25:59		68		39

		4-Feb-08		8:07:10		65.6		40.5		4-Feb-08		8:06:20		65.01		41		4-Feb-08		8:07:53		68		45.5		16-Mar-08		8:25:59		68.61		45.5

		4-Feb-08		10:07:10		65.6		41		4-Feb-08		10:06:20		65.6		42.5		4-Feb-08		10:07:53		68.61		45		16-Mar-08		10:25:59		68.61		45.5

		4-Feb-08		12:07:10		65.6		41.5		4-Feb-08		12:06:20		66.2		41		4-Feb-08		12:07:53		68		46		16-Mar-08		12:25:59		68.61		45.5

		4-Feb-08		14:07:10		65.6		40.5		4-Feb-08		14:06:20		66.81		38		4-Feb-08		14:07:53		68		46		16-Mar-08		14:25:59		68.61		35

		4-Feb-08		16:07:10		66.2		39		4-Feb-08		16:06:20		66.81		38		4-Feb-08		16:07:53		68		45		16-Mar-08		16:25:59		68.61		45

		4-Feb-08		18:07:10		66.2		38.5		4-Feb-08		18:06:20		66.81		36.5		4-Feb-08		18:07:53		68		45		16-Mar-08		18:25:59		68.61		45

		4-Feb-08		20:07:10		66.2		37.5		4-Feb-08		20:06:20		65.6		38		4-Feb-08		20:07:53		68		45.5		16-Mar-08		20:25:59		68.61		45

		4-Feb-08		22:07:10		65.6		37.5		4-Feb-08		22:06:20		65.6		38.5		4-Feb-08		22:07:53		67.4		46		16-Mar-08		22:25:59		68		46

		5-Feb-08		0:07:10		65.6		37		5-Feb-08		0:06:20		65.01		38		5-Feb-08		0:07:53		66.81		46.5		17-Mar-08		0:25:59		68.61		44

		5-Feb-08		2:07:10		65.6		36		5-Feb-08		2:06:20		65.6		35.5		5-Feb-08		2:07:53		66.81		46		17-Mar-08		2:25:59		68.61		44

		5-Feb-08		4:07:10		65.6		34.5		5-Feb-08		4:06:20		65.01		35		5-Feb-08		4:07:53		66.2		46		17-Mar-08		4:25:59		68.61		45

		5-Feb-08		6:07:10		65.6		33.5		5-Feb-08		6:06:20		65.01		33		5-Feb-08		6:07:53		66.81		46		17-Mar-08		6:25:59		68		43.5

		5-Feb-08		8:07:10		65.6		33		5-Feb-08		8:06:20		65.01		33.5		5-Feb-08		8:07:53		70.41		39.5		17-Mar-08		8:25:59		68.61		44

		5-Feb-08		10:07:10		65.6		34.5		5-Feb-08		10:06:20		68.61		32.5		5-Feb-08		10:07:53		71		41.5		17-Mar-08		10:25:59		68.61		43

		5-Feb-08		12:07:10		66.2		34.5		5-Feb-08		12:06:20		71		30.5		5-Feb-08		12:07:53		70.41		42.5		17-Mar-08		12:25:59		68		35.5

		5-Feb-08		14:07:10		66.81		32		5-Feb-08		14:06:20		70.41		29.5		5-Feb-08		14:07:53		71		39.5		17-Mar-08		14:25:59		68.61		27.5

		5-Feb-08		16:07:10		67.4		31		5-Feb-08		16:06:20		70.41		28.5		5-Feb-08		16:07:53		71		34.5		17-Mar-08		16:25:59		68.61		26

		5-Feb-08		18:07:10		68		34		5-Feb-08		18:06:20		69.8		29		5-Feb-08		18:07:53		70.41		37.5		17-Mar-08		18:25:59		68		34

		5-Feb-08		20:07:10		67.4		41.5		5-Feb-08		20:06:20		68		32		5-Feb-08		20:07:53		71		36		17-Mar-08		20:25:59		68		44

		5-Feb-08		22:07:10		66.81		35.5		5-Feb-08		22:06:20		67.4		33		5-Feb-08		22:07:53		69.8		39		17-Mar-08		22:25:59		68.61		44

		6-Feb-08		0:07:10		66.81		34.5		6-Feb-08		0:06:20		67.4		33.5		6-Feb-08		0:07:53		68		36.5		18-Mar-08		0:25:59		68.61		37.5

		6-Feb-08		2:07:10		66.81		34		6-Feb-08		2:06:20		67.4		33		6-Feb-08		2:07:53		66.81		36.5		18-Mar-08		2:25:59		68.61		36.5

		6-Feb-08		4:07:10		66.2		34		6-Feb-08		4:06:20		67.4		32.5		6-Feb-08		4:07:53		66.2		37		18-Mar-08		4:25:59		68		44.5

		6-Feb-08		6:07:10		66.2		33		6-Feb-08		6:06:20		68		31.5		6-Feb-08		6:07:53		67.4		36		18-Mar-08		6:25:59		68		42

		6-Feb-08		8:07:10		66.2		32		6-Feb-08		8:06:20		68		30.5		6-Feb-08		8:07:53		68		35		18-Mar-08		8:25:59		68.61		43.5

		6-Feb-08		10:07:10		66.81		34		6-Feb-08		10:06:20		69.8		31.5		6-Feb-08		10:07:53		70.41		36.5		18-Mar-08		10:25:59		68		39.5

		6-Feb-08		12:07:10		67.4		34.5		6-Feb-08		12:06:20		71		31.5		6-Feb-08		12:07:53		69.8		39.5		18-Mar-08		12:25:59		68.61		43.5

		6-Feb-08		14:07:10		67.4		34.5		6-Feb-08		14:06:20		69.2		34.5		6-Feb-08		14:07:53		71		36		18-Mar-08		14:25:59		68		40

		6-Feb-08		16:07:10		68.61		33		6-Feb-08		16:06:20		71		31		6-Feb-08		16:07:53		71		35		18-Mar-08		16:25:59		68.61		46

		6-Feb-08		18:07:10		68		37		6-Feb-08		18:06:20		69.8		33		6-Feb-08		18:07:53		71		38		18-Mar-08		18:25:59		68.61		44.5

		6-Feb-08		20:07:10		66.81		41		6-Feb-08		20:06:20		68		37.5		6-Feb-08		20:07:53		70.41		39		18-Mar-08		20:25:59		68.61		44.5

		6-Feb-08		22:07:10		66.2		44		6-Feb-08		22:06:20		67.4		38		6-Feb-08		22:07:53		69.8		39		18-Mar-08		22:25:59		68.61		44.5

		7-Feb-08		0:07:10		66.2		45		7-Feb-08		0:06:20		68		36		7-Feb-08		0:07:53		68.61		39.5		19-Mar-08		0:25:59		68		41

		7-Feb-08		2:07:10		65.6		46		7-Feb-08		2:06:20		67.4		35.5		7-Feb-08		2:07:53		67.4		40		19-Mar-08		2:25:59		68		45

		7-Feb-08		4:07:10		65.6		46		7-Feb-08		4:06:20		68		34		7-Feb-08		4:07:53		66.81		40		19-Mar-08		4:25:59		68		45

		7-Feb-08		6:07:10		65.6		46.5		7-Feb-08		6:06:20		68		33		7-Feb-08		6:07:53		66.81		39.5		19-Mar-08		6:25:59		68.61		44.5

		7-Feb-08		8:07:10		65.6		47		7-Feb-08		8:06:20		67.4		33		7-Feb-08		8:07:53		69.8		38		19-Mar-08		8:25:59		68.61		44.5

		7-Feb-08		10:07:10		65.6		46.5		7-Feb-08		10:06:20		72.21		33.5		7-Feb-08		10:07:53		71.6		37.5		19-Mar-08		10:25:59		68.61		46.5

		7-Feb-08		12:07:10		66.81		46		7-Feb-08		12:06:20		74.01		36.5		7-Feb-08		12:07:53		69.8		44.5		19-Mar-08		12:25:59		68.61		47.5

		7-Feb-08		14:07:10		67.4		46		7-Feb-08		14:06:20		71.6		34		7-Feb-08		14:07:53		71		47		19-Mar-08		14:25:59		68.61		45

		7-Feb-08		16:07:10		67.4		46		7-Feb-08		16:06:20		69.8		37		7-Feb-08		16:07:53		70.41		43.5		19-Mar-08		16:25:59		68.61		44.5

		7-Feb-08		18:07:10		67.4		46		7-Feb-08		18:06:20		69.2		34		7-Feb-08		18:07:53		70.41		41		19-Mar-08		18:25:59		68.61		47.5

		7-Feb-08		20:07:10		66.2		46.5		7-Feb-08		20:06:20		69.2		34		7-Feb-08		20:07:53		69.8		39		19-Mar-08		20:25:59		68		48

		7-Feb-08		22:07:10		66.2		47		7-Feb-08		22:06:20		66.81		36		7-Feb-08		22:07:53		69.8		38		19-Mar-08		22:25:59		68.61		45

		8-Feb-08		0:07:10		65.6		48		8-Feb-08		0:06:20		65.6		37.5		8-Feb-08		0:07:53		68.61		38.5		20-Mar-08		0:25:59		68.61		45

		8-Feb-08		2:07:10		65.01		48.5		8-Feb-08		2:06:20		65.6		37.5		8-Feb-08		2:07:53		67.4		39		20-Mar-08		2:25:59		68		40

		8-Feb-08		4:07:10		65.01		49		8-Feb-08		4:06:20		65.6		36.5		8-Feb-08		4:07:53		66.81		39.5		20-Mar-08		4:25:59		68		39

		8-Feb-08		6:07:10		65.01		49		8-Feb-08		6:06:20		65.6		36		8-Feb-08		6:07:53		66.81		39		20-Mar-08		6:25:59		68.61		38.5

		8-Feb-08		8:07:10		65.01		48.5		8-Feb-08		8:06:20		68		33.5		8-Feb-08		8:07:53		69.8		37		20-Mar-08		8:25:59		68		44.5

		8-Feb-08		10:07:10		65.01		49		8-Feb-08		10:06:20		70.41		35		8-Feb-08		10:07:53		71.6		38		20-Mar-08		10:25:59		68.61		45

		8-Feb-08		12:07:10		66.2		48		8-Feb-08		12:06:20		70.41		35.5		8-Feb-08		12:07:53		70.41		39		20-Mar-08		12:25:59		68.61		45.5

		8-Feb-08		14:07:10		66.81		48.5		8-Feb-08		14:06:20		71		38.5		8-Feb-08		14:07:53		71.6		46.5		20-Mar-08		14:25:59		68.61		46

		8-Feb-08		16:07:10		68.61		49.5		8-Feb-08		16:06:20		71		39		8-Feb-08		16:07:53		69.8		49		20-Mar-08		16:25:59		68		47

		8-Feb-08		18:07:10		68.61		44.5		8-Feb-08		18:06:20		69.8		41		8-Feb-08		18:07:53		71		47		20-Mar-08		18:25:59		68.61		45

		8-Feb-08		20:07:10		68.61		42.5		8-Feb-08		20:06:20		69.8		40.5		8-Feb-08		20:07:53		69.8		44.5		20-Mar-08		20:25:59		68.61		45

		8-Feb-08		22:07:10		68		45		8-Feb-08		22:06:20		68		44		8-Feb-08		22:07:53		70.41		42.5		20-Mar-08		22:25:59		68.61		44.5

		9-Feb-08		0:07:10		66.81		44		9-Feb-08		0:06:20		66.2		44		9-Feb-08		0:07:53		69.8		41		21-Mar-08		0:25:59		68.61		45

		9-Feb-08		2:07:10		66.2		44		9-Feb-08		2:06:20		66.2		40.5		9-Feb-08		2:07:53		68.61		40		21-Mar-08		2:25:59		68		45.5

		9-Feb-08		4:07:10		66.2		42		9-Feb-08		4:06:20		66.2		37		9-Feb-08		4:07:53		67.4		38.5		21-Mar-08		4:25:59		68		36.5

		9-Feb-08		6:07:10		65.6		40.5		9-Feb-08		6:06:20		66.2		36		9-Feb-08		6:07:53		67.4		37.5		21-Mar-08		6:25:59		68		45.5

		9-Feb-08		8:07:10		65.6		39.5		9-Feb-08		8:06:20		68		32		9-Feb-08		8:07:53		69.2		36		21-Mar-08		8:25:59		68		36

		9-Feb-08		10:07:10		66.2		40		9-Feb-08		10:06:20		71		35		9-Feb-08		10:07:53		71.6		35.5		21-Mar-08		10:25:59		67.4		46.5

		9-Feb-08		12:07:10		67.4		46.5		9-Feb-08		12:06:20		69.2		33.5		9-Feb-08		12:07:53		71		38.5		21-Mar-08		12:25:59		68.61		42

		9-Feb-08		14:07:10		69.8		47.5		9-Feb-08		14:06:20		68.61		33		9-Feb-08		14:07:53		71		34.5		21-Mar-08		14:25:59		68.61		32.5

		9-Feb-08		16:07:10		72.8		42		9-Feb-08		16:06:20		68.61		28.5		9-Feb-08		16:07:53		71		38.5		21-Mar-08		16:25:59		68		32.5

		9-Feb-08		18:07:10		71		48		9-Feb-08		18:06:20		68		29		9-Feb-08		18:07:53		70.41		35.5		21-Mar-08		18:25:59		68		42.5

		9-Feb-08		20:07:10		67.4		48.5		9-Feb-08		20:06:20		68.61		38.5		9-Feb-08		20:07:53		69.8		39.5		21-Mar-08		20:25:59		68.61		37

		9-Feb-08		22:07:10		65.6		51		9-Feb-08		22:06:20		67.4		38.5		9-Feb-08		22:07:53		69.8		38.5		21-Mar-08		22:25:59		68.61		36.5

		10-Feb-08		0:07:10		65.01		49.5		10-Feb-08		0:06:20		66.2		39		10-Feb-08		0:07:53		69.2		37.5		22-Mar-08		0:25:59		68		34.5

		10-Feb-08		2:07:10		65.01		49		10-Feb-08		2:06:20		65.6		38		10-Feb-08		2:07:53		68		37.5		22-Mar-08		2:25:59		68		42.5

		10-Feb-08		4:07:10		65.01		50		10-Feb-08		4:06:20		65.6		36.5		10-Feb-08		4:07:53		66.81		37.5		22-Mar-08		4:25:59		68		38

		10-Feb-08		6:07:10		65.01		51		10-Feb-08		6:06:20		65.6		35.5		10-Feb-08		6:07:53		66.2		38		22-Mar-08		6:25:59		68		35

		10-Feb-08		8:07:10		65.01		50		10-Feb-08		8:06:20		66.2		34		10-Feb-08		8:07:53		66.81		37		22-Mar-08		8:25:59		68		43.5

		10-Feb-08		10:07:10		65.01		49.5		10-Feb-08		10:06:20		67.4		36		10-Feb-08		10:07:53		68		37		22-Mar-08		10:25:59		68		41

		10-Feb-08		12:07:10		66.2		51		10-Feb-08		12:06:20		67.4		40.5		10-Feb-08		12:07:53		69.8		38.5		22-Mar-08		12:25:59		68.61		43.5

		10-Feb-08		14:07:10		68.61		49.5		10-Feb-08		14:06:20		68		41.5		10-Feb-08		14:07:53		70.41		41		22-Mar-08		14:25:59		68		37

		10-Feb-08		16:07:10		69.8		49		10-Feb-08		16:06:20		68		44		10-Feb-08		16:07:53		70.41		45		22-Mar-08		16:25:59		68.61		45

		10-Feb-08		18:07:10		69.8		49.5		10-Feb-08		18:06:20		68		39.5		10-Feb-08		18:07:53		70.41		42		22-Mar-08		18:25:59		68		44.5

		10-Feb-08		20:07:10		67.4		47.5		10-Feb-08		20:06:20		68.61		39.5		10-Feb-08		20:07:53		69.8		46.5		22-Mar-08		20:25:59		68		38.5

		10-Feb-08		22:07:10		66.2		49.5		10-Feb-08		22:06:20		68		39.5		10-Feb-08		22:07:53		70.41		42		22-Mar-08		22:25:59		68		38.5

		11-Feb-08		0:07:10		65.6		49.5		11-Feb-08		0:06:20		66.2		42		11-Feb-08		0:07:53		69.8		41.5		23-Mar-08		0:25:59		68		39

		11-Feb-08		2:07:10		65.01		50		11-Feb-08		2:06:20		66.2		42		11-Feb-08		2:07:53		68.61		42		23-Mar-08		2:25:59		68.61		36.5

		11-Feb-08		4:07:10		65.01		50		11-Feb-08		4:06:20		65.6		40		11-Feb-08		4:07:53		68		41.5		23-Mar-08		4:25:59		68		35.5

		11-Feb-08		6:07:10		65.01		50.5		11-Feb-08		6:06:20		65.6		38		11-Feb-08		6:07:53		67.4		42.5		23-Mar-08		6:25:59		68.61		43.5

		11-Feb-08		8:07:10		65.01		50		11-Feb-08		8:06:20		66.2		36.5		11-Feb-08		8:07:53		68		41.5		23-Mar-08		8:25:59		68		36

		11-Feb-08		10:07:10		65.01		51		11-Feb-08		10:06:20		66.81		39		11-Feb-08		10:07:53		68		42.5		23-Mar-08		10:25:59		68.61		44

		11-Feb-08		12:07:10		66.2		51.5		11-Feb-08		12:06:20		68		41.5		11-Feb-08		12:07:53		69.8		41.5		23-Mar-08		12:25:59		68		40

		11-Feb-08		14:07:10		68		51		11-Feb-08		14:06:20		67.4		43.5		11-Feb-08		14:07:53		69.8		44		23-Mar-08		14:25:59		68.61		44.5

		11-Feb-08		16:07:10		70.41		51		11-Feb-08		16:06:20		68		42		11-Feb-08		16:07:53		70.41		46.5		23-Mar-08		16:25:59		68.61		33

		11-Feb-08		18:07:10		69.8		50.5		11-Feb-08		18:06:20		68		48.5		11-Feb-08		18:07:53		70.41		46		23-Mar-08		18:25:59		68.61		44.5

		11-Feb-08		20:07:10		66.2		52		11-Feb-08		20:06:20		68.61		45.5		11-Feb-08		20:07:53		70.41		46		23-Mar-08		20:25:59		68.61		43.5

		11-Feb-08		22:07:10		65.6		52		11-Feb-08		22:06:20		67.4		44.5		11-Feb-08		22:07:53		70.41		43.5		23-Mar-08		22:25:59		68		45

		12-Feb-08		0:07:10		65.6		51.5		12-Feb-08		0:06:20		66.2		44.5		12-Feb-08		0:07:53		69.2		41.5		24-Mar-08		0:25:59		68		38.5

		12-Feb-08		2:07:10		65.01		50		12-Feb-08		2:06:20		66.2		42		12-Feb-08		2:07:53		68.61		41		24-Mar-08		2:25:59		68.61		39.5

		12-Feb-08		4:07:10		65.01		52		12-Feb-08		4:06:20		65.6		41.5		12-Feb-08		4:07:53		68		41		24-Mar-08		4:25:59		68.61		36

		12-Feb-08		6:07:10		65.01		50		12-Feb-08		6:06:20		65.6		40.5		12-Feb-08		6:07:53		67.4		41		24-Mar-08		6:25:59		68		35.5

		12-Feb-08		8:07:10		65.01		51		12-Feb-08		8:06:20		66.81		37.5		12-Feb-08		8:07:53		69.8		38		24-Mar-08		8:25:59		68.61		33.5

		12-Feb-08		10:07:10		65.6		49.5		12-Feb-08		10:06:20		71		39		12-Feb-08		10:07:53		71		41.5		24-Mar-08		10:25:59		68		37.5

		12-Feb-08		12:07:10		67.4		49.5		12-Feb-08		12:06:20		72.21		42.5		12-Feb-08		12:07:53		70.41		39.5		24-Mar-08		12:25:59		68.61		37.5

		12-Feb-08		14:07:10		70.41		50		12-Feb-08		14:06:20		72.8		41.5		12-Feb-08		14:07:53		71		44		24-Mar-08		14:25:59		68.61		38.5

		12-Feb-08		16:07:10		72.8		49.5		12-Feb-08		16:06:20		71.6		38.5		12-Feb-08		16:07:53		70.41		47.5		24-Mar-08		16:25:59		68		45

		12-Feb-08		18:07:10		71.6		49.5		12-Feb-08		18:06:20		70.41		48.5		12-Feb-08		18:07:53		70.41		50.5		24-Mar-08		18:25:59		68		42.5

		12-Feb-08		20:07:10		67.4		51		12-Feb-08		20:06:20		69.8		43.5		12-Feb-08		20:07:53		69.8		49		24-Mar-08		20:25:59		68		44.5

		12-Feb-08		22:07:10		66.2		52		12-Feb-08		22:06:20		69.2		43.5		12-Feb-08		22:07:53		70.41		45.5		24-Mar-08		22:25:59		68.61		40

		13-Feb-08		0:07:10		66.2		48.5		13-Feb-08		0:06:20		68.61		42.5		13-Feb-08		0:07:53		69.8		42.5		25-Mar-08		0:25:59		68.61		44

		13-Feb-08		2:07:10		65.6		49		13-Feb-08		2:06:20		68.61		40.5		13-Feb-08		2:07:53		69.2		41.5		25-Mar-08		2:25:59		68		38

		13-Feb-08		4:07:10		65.6		48.5		13-Feb-08		4:06:20		68.61		38		13-Feb-08		4:07:53		68.61		40.5		25-Mar-08		4:25:59		68.61		44.5

		13-Feb-08		6:07:10		65.6		50.5		13-Feb-08		6:06:20		68.61		36.5		13-Feb-08		6:07:53		67.4		41		25-Mar-08		6:25:59		68		37.5

		13-Feb-08		8:07:10		65.6		50		13-Feb-08		8:06:20		69.2		36.5		13-Feb-08		8:07:53		69.8		40		25-Mar-08		8:25:59		68		38

		13-Feb-08		10:07:10		66.2		50.5		13-Feb-08		10:06:20		70.41		37.5		13-Feb-08		10:07:53		71.6		42		25-Mar-08		10:25:59		67.4		42.5

		13-Feb-08		12:07:10		67.4		50.5		13-Feb-08		12:06:20		71		43		13-Feb-08		12:07:53		71		47		25-Mar-08		12:25:59		68		44.5

		13-Feb-08		14:07:10		73.4		46		13-Feb-08		14:06:20		71.6		43.5		13-Feb-08		14:07:53		71		52.5		25-Mar-08		14:25:59		68		46

		13-Feb-08		16:07:10		73.4		48.5		13-Feb-08		16:06:20		71.6		40		13-Feb-08		16:07:53		71		50.5		25-Mar-08		16:25:59		68		45.5

		13-Feb-08		18:07:10		71		48		13-Feb-08		18:06:20		70.41		45		13-Feb-08		18:07:53		70.41		47		25-Mar-08		18:25:59		68		44

		13-Feb-08		20:07:10		66.2		53		13-Feb-08		20:06:20		69.8		44		13-Feb-08		20:07:53		70.41		42.5		25-Mar-08		20:25:59		68		42.5

		13-Feb-08		22:07:10		65.6		53		13-Feb-08		22:06:20		69.2		43.5		13-Feb-08		22:07:53		70.41		44		25-Mar-08		22:25:59		68.61		41.5

		14-Feb-08		0:07:10		65.6		50.5		14-Feb-08		0:06:20		68.61		41		14-Feb-08		0:07:53		70.41		42		26-Mar-08		0:25:59		68.61		40.5

		14-Feb-08		2:07:10		65.01		51		14-Feb-08		2:06:20		68.61		39		14-Feb-08		2:07:53		69.2		40		26-Mar-08		2:25:59		68.61		40

		14-Feb-08		4:07:10		65.01		49		14-Feb-08		4:06:20		68.61		39		14-Feb-08		4:07:53		68.61		40.5		26-Mar-08		4:25:59		68.61		39

		14-Feb-08		6:07:10		65.01		51		14-Feb-08		6:06:20		68.61		38.5		14-Feb-08		6:07:53		68		40.5		26-Mar-08		6:25:59		68.61		40

		14-Feb-08		8:07:10		65.6		49.5		14-Feb-08		8:06:20		68.61		37		14-Feb-08		8:07:53		71		40		26-Mar-08		8:25:59		68		41.5

		14-Feb-08		10:07:10		67.4		46.5		14-Feb-08		10:06:20		69.8		30		14-Feb-08		10:07:53		70.41		39		26-Mar-08		10:25:59		68		42.5

		14-Feb-08		12:07:10		68		46.5		14-Feb-08		12:06:20		70.41		30.5		14-Feb-08		12:07:53		71		33		26-Mar-08		12:25:59		68.61		43.5

		14-Feb-08		14:07:10		66.2		46.5		14-Feb-08		14:06:20		72.21		28.5		14-Feb-08		14:07:53		71		38.5		26-Mar-08		14:25:59		68		43

		14-Feb-08		16:07:10		65.6		47		14-Feb-08		16:06:20		72.8		24		14-Feb-08		16:07:53		71		37.5		26-Mar-08		16:25:59		68		42

		14-Feb-08		18:07:10		65.01		49		14-Feb-08		18:06:20		71.6		16.5		14-Feb-08		18:07:53		71		30.5		26-Mar-08		18:25:59		68		40.5

		14-Feb-08		20:07:10		64.4		47		14-Feb-08		20:06:20		71		17		14-Feb-08		20:07:53		70.41		30		26-Mar-08		20:25:59		68.61		38

		14-Feb-08		22:07:10		64.4		49		14-Feb-08		22:06:20		70.41		27.5		14-Feb-08		22:07:53		71		32		26-Mar-08		22:25:59		68		37.5

		15-Feb-08		0:07:10		64.4		49		15-Feb-08		0:06:20		70.41		26		15-Feb-08		0:07:53		70.41		32		27-Mar-08		0:25:59		68		38

		15-Feb-08		2:07:10		64.4		46.5		15-Feb-08		2:06:20		70.41		23.5		15-Feb-08		2:07:53		69.2		31		27-Mar-08		2:25:59		67.4		37.5

		15-Feb-08		4:07:10		64.4		50.5		15-Feb-08		4:06:20		70.41		21		15-Feb-08		4:07:53		68.61		31		27-Mar-08		4:25:59		67.4		36.5

		15-Feb-08		6:07:10		64.4		49		15-Feb-08		6:06:20		70.41		19.5		15-Feb-08		6:07:53		68		30.5		27-Mar-08		6:25:59		67.4		35

		15-Feb-08		8:07:10		64.4		50.5		15-Feb-08		8:06:20		70.41		19.5		15-Feb-08		8:07:53		70.41		31		27-Mar-08		8:25:59		68		35.5

		15-Feb-08		10:07:10		65.01		33.5		15-Feb-08		10:06:20		72.21		19.5		15-Feb-08		10:07:53		71		30.5		27-Mar-08		10:25:59		67.4		37

		15-Feb-08		12:07:10		65.6		48		15-Feb-08		12:06:20		72.8		19		15-Feb-08		12:07:53		71		29.5		27-Mar-08		12:25:59		68		36.5

		15-Feb-08		14:07:10		65.6		49		15-Feb-08		14:06:20		72.8		19.5		15-Feb-08		14:07:53		71		34.5		27-Mar-08		14:25:59		68		39

		15-Feb-08		16:07:10		65.6		48.5		15-Feb-08		16:06:20		73.4		19		15-Feb-08		16:07:53		71		34		27-Mar-08		16:25:59		68		39.5

		15-Feb-08		18:07:10		65.6		49.5		15-Feb-08		18:06:20		71.6		20.5		15-Feb-08		18:07:53		70.41		32		27-Mar-08		18:25:59		68.61		37.5

		15-Feb-08		20:07:10		65.01		43.5		15-Feb-08		20:06:20		71		24.5		15-Feb-08		20:07:53		70.41		31.5		27-Mar-08		20:25:59		68.61		37

		15-Feb-08		22:07:10		65.01		49		15-Feb-08		22:06:20		70.41		26.5		15-Feb-08		22:07:53		69.8		31.5		27-Mar-08		22:25:59		68.61		34.5

		16-Feb-08		0:07:10		65.6		50		16-Feb-08		0:06:20		70.41		26.5		16-Feb-08		0:07:53		69.2		32		28-Mar-08		0:25:59		68		34.5

		16-Feb-08		2:07:10		65.01		50		16-Feb-08		2:06:20		70.41		26.5		16-Feb-08		2:07:53		68.61		33		28-Mar-08		2:25:59		67.4		33

		16-Feb-08		4:07:10		65.01		51		16-Feb-08		4:06:20		70.41		27		16-Feb-08		4:07:53		68		33.5		28-Mar-08		4:25:59		66.81		31.5

		16-Feb-08		6:07:10		65.01		50		16-Feb-08		6:06:20		70.41		26.5		16-Feb-08		6:07:53		66.81		34		28-Mar-08		6:25:59		67.4		31.5

		16-Feb-08		8:07:10		65.01		51		16-Feb-08		8:06:20		70.41		27		16-Feb-08		8:07:53		69.2		33		28-Mar-08		8:25:59		68		30.5

		16-Feb-08		10:07:10		65.6		51		16-Feb-08		10:06:20		71.6		27.5		16-Feb-08		10:07:53		71.6		33.5		28-Mar-08		10:25:59		68		29

		16-Feb-08		12:07:10		65.01		50		16-Feb-08		12:06:20		73.4		28		16-Feb-08		12:07:53		70.41		39		28-Mar-08		12:25:59		68		26

		16-Feb-08		14:07:10		65.6		50		16-Feb-08		14:06:20		73.4		27		16-Feb-08		14:07:53		71		33		28-Mar-08		14:25:59		68.61		25.5

		16-Feb-08		16:07:10		65.6		51.5		16-Feb-08		16:06:20		73.4		37.5		16-Feb-08		16:07:53		71.6		36.5		28-Mar-08		16:25:59		68		23.5

		16-Feb-08		18:07:10		65.01		51		16-Feb-08		18:06:20		67.4		41		16-Feb-08		18:07:53		70.41		40		28-Mar-08		18:25:59		68.61		23.5

		16-Feb-08		20:07:10		65.01		50.5		16-Feb-08		20:06:20		66.2		43		16-Feb-08		20:07:53		71		39.5		28-Mar-08		20:25:59		68		26.5

		16-Feb-08		22:07:10		65.01		52		16-Feb-08		22:06:20		66.81		41		16-Feb-08		22:07:53		70.41		39		28-Mar-08		22:25:59		68		32.5

		17-Feb-08		0:07:10		65.01		52		17-Feb-08		0:06:20		66.2		40		17-Feb-08		0:07:53		69.8		38		29-Mar-08		0:25:59		67.4		33.5

		17-Feb-08		2:07:10		65.01		52.5		17-Feb-08		2:06:20		66.2		40.5		17-Feb-08		2:07:53		69.2		39.5		29-Mar-08		2:25:59		67.4		34

		17-Feb-08		4:07:10		65.01		53		17-Feb-08		4:06:20		66.2		41.5		17-Feb-08		4:07:53		68.61		39.5		29-Mar-08		4:25:59		66.81		34

		17-Feb-08		6:07:10		65.01		53		17-Feb-08		6:06:20		66.2		41		17-Feb-08		6:07:53		68.61		40		29-Mar-08		6:25:59		67.4		33.5

		17-Feb-08		8:07:10		65.01		52		17-Feb-08		8:06:20		65.6		40		17-Feb-08		8:07:53		70.41		39		29-Mar-08		8:25:59		68		34

		17-Feb-08		10:07:10		65.01		52		17-Feb-08		10:06:20		65.6		40.5		17-Feb-08		10:07:53		71		37.5		29-Mar-08		10:25:59		67.4		30.5

		17-Feb-08		12:07:10		65.01		52.5		17-Feb-08		12:06:20		66.81		40.5		17-Feb-08		12:07:53		71		38.5		29-Mar-08		12:25:59		68		37

		17-Feb-08		14:07:10		65.01		52		17-Feb-08		14:06:20		67.4		40.5		17-Feb-08		14:07:53		70.41		41.5		29-Mar-08		14:25:59		68		39.5

		17-Feb-08		16:07:10		65.01		53		17-Feb-08		16:06:20		68		38		17-Feb-08		16:07:53		71		43.5		29-Mar-08		16:25:59		68		42

		17-Feb-08		18:07:10		65.01		52.5		17-Feb-08		18:06:20		66.81		42.5		17-Feb-08		18:07:53		70.41		41.5		29-Mar-08		18:25:59		68		42.5

		17-Feb-08		20:07:10		65.01		52.5		17-Feb-08		20:06:20		66.81		42.5		17-Feb-08		20:07:53		69.8		40.5		29-Mar-08		20:25:59		68		43

		17-Feb-08		22:07:10		65.01		53		17-Feb-08		22:06:20		66.81		40.5		17-Feb-08		22:07:53		69.8		39		29-Mar-08		22:25:59		68		43.5

		18-Feb-08		0:07:10		65.01		52		18-Feb-08		0:06:20		66.2		39.5		18-Feb-08		0:07:53		69.2		38.5		30-Mar-08		0:25:59		68		43.5

		18-Feb-08		2:07:10		65.01		52.5		18-Feb-08		2:06:20		66.2		42.5		18-Feb-08		2:07:53		68.61		40		30-Mar-08		2:25:59		68.61		42.5

		18-Feb-08		4:07:10		65.01		52		18-Feb-08		4:06:20		65.6		41.5		18-Feb-08		4:07:53		68		40.5		30-Mar-08		4:25:59		68.61		41.5

		18-Feb-08		6:07:10		65.01		51.5		18-Feb-08		6:06:20		65.6		41.5		18-Feb-08		6:07:53		68		40.5		30-Mar-08		6:25:59		68.61		40

		18-Feb-08		8:07:10		65.01		52		18-Feb-08		8:06:20		65.6		40		18-Feb-08		8:07:53		67.4		40.5		30-Mar-08		8:25:59		68.61		39

		18-Feb-08		10:07:10		65.01		51.5		18-Feb-08		10:06:20		65.6		41		18-Feb-08		10:07:53		67.4		40.5		30-Mar-08		10:25:59		68.61		39

		18-Feb-08		12:07:10		65.01		52		18-Feb-08		12:06:20		66.2		41.5		18-Feb-08		12:07:53		67.4		41		30-Mar-08		12:25:59		68.61		40

		18-Feb-08		14:07:10		65.01		52.5		18-Feb-08		14:06:20		67.4		42		18-Feb-08		14:07:53		68.61		41.5		30-Mar-08		14:25:59		68.61		40.5

		18-Feb-08		16:07:10		65.01		53.5		18-Feb-08		16:06:20		66.81		45.5		18-Feb-08		16:07:53		69.8		42		30-Mar-08		16:25:59		68.61		40

		18-Feb-08		18:07:10		65.01		54		18-Feb-08		18:06:20		66.2		45		18-Feb-08		18:07:53		69.8		42.5		30-Mar-08		18:25:59		68.61		38.5

		18-Feb-08		20:07:10		65.01		52.5		18-Feb-08		20:06:20		66.81		41.5		18-Feb-08		20:07:53		69.2		41		30-Mar-08		20:25:59		68.61		37

		18-Feb-08		22:07:10		65.01		53		18-Feb-08		22:06:20		66.2		42.5		18-Feb-08		22:07:53		68.61		40.5		30-Mar-08		22:25:59		68.61		32.5

		19-Feb-08		0:07:10		65.01		51		19-Feb-08		0:06:20		66.2		41.5		19-Feb-08		0:07:53		68.61		41		31-Mar-08		0:25:59		68.61		32

		19-Feb-08		2:07:10		65.01		52.5		19-Feb-08		2:06:20		66.2		42.5		19-Feb-08		2:07:53		68		41.5		31-Mar-08		2:25:59		67.4		33

		19-Feb-08		4:07:10		65.01		51		19-Feb-08		4:06:20		66.2		43		19-Feb-08		4:07:53		68		41.5		31-Mar-08		4:25:59		66.81		33.5

		19-Feb-08		6:07:10		65.01		53		19-Feb-08		6:06:20		66.2		43		19-Feb-08		6:07:53		68		42		31-Mar-08		6:25:59		67.4		32.5

		19-Feb-08		8:07:10		65.01		52		19-Feb-08		8:06:20		66.81		42.5		19-Feb-08		8:07:53		68		42.5		31-Mar-08		8:25:59		68		32

		19-Feb-08		10:07:10		65.01		52.5		19-Feb-08		10:06:20		66.2		43.5		19-Feb-08		10:07:53		68.61		42.5		31-Mar-08		10:25:59		68.61		28.5

		19-Feb-08		12:07:10		65.01		52.5		19-Feb-08		12:06:20		66.2		43.5		19-Feb-08		12:07:53		69.2		42.5		31-Mar-08		12:25:59		67.4		25.5

		19-Feb-08		14:07:10		65.01		52		19-Feb-08		14:06:20		66.81		43		19-Feb-08		14:07:53		69.8		42		31-Mar-08		14:25:59		68		24

		19-Feb-08		16:07:10		65.01		52.5		19-Feb-08		16:06:20		66.2		44.5		19-Feb-08		16:07:53		69.8		42.5		31-Mar-08		16:25:59		68.61		24.5

		19-Feb-08		18:07:10		65.01		51.5		19-Feb-08		18:06:20		66.81		43		19-Feb-08		18:07:53		69.8		42		31-Mar-08		18:25:59		68		27.5

		19-Feb-08		20:07:10		65.01		52		19-Feb-08		20:06:20		66.2		43		19-Feb-08		20:07:53		69.8		41.5		31-Mar-08		20:25:59		68		27

		19-Feb-08		22:07:10		65.01		52		19-Feb-08		22:06:20		66.2		42		19-Feb-08		22:07:53		69.8		40.5		31-Mar-08		22:25:59		68		27.5

		20-Feb-08		0:07:10		65.01		52.5		20-Feb-08		0:06:20		66.81		39.5		20-Feb-08		0:07:53		69.8		40		1-Apr-08		0:25:59		67.4		29

		20-Feb-08		2:07:10		65.01		52		20-Feb-08		2:06:20		66.81		40.5		20-Feb-08		2:07:53		69.2		40		1-Apr-08		2:25:59		67.4		29

		20-Feb-08		4:07:10		65.01		52		20-Feb-08		4:06:20		66.81		40.5		20-Feb-08		4:07:53		69.2		40		1-Apr-08		4:25:59		68		28

		20-Feb-08		6:07:10		65.01		52.5		20-Feb-08		6:06:20		66.81		41		20-Feb-08		6:07:53		69.2		40.5		1-Apr-08		6:25:59		68.61		28.5

		20-Feb-08		8:07:10		65.6		51.5		20-Feb-08		8:06:20		67.4		41		20-Feb-08		8:07:53		71		41		1-Apr-08		8:25:59		68		30

		20-Feb-08		10:07:10		65.6		51.5		20-Feb-08		10:06:20		66.81		42		20-Feb-08		10:07:53		71		39.5		1-Apr-08		10:25:59		67.4		31

		20-Feb-08		12:07:10		66.2		51		20-Feb-08		12:06:20		66.81		48.5		20-Feb-08		12:07:53		71		42.5		1-Apr-08		12:25:59		68		25

		20-Feb-08		14:07:10		65.6		52.5		20-Feb-08		14:06:20		66.81		51.5		20-Feb-08		14:07:53		71		39		1-Apr-08		14:25:59		68		29.5

		20-Feb-08		16:07:10		66.81		52.5		20-Feb-08		16:06:20		67.4		48.5		20-Feb-08		16:07:53		70.41		43.5		1-Apr-08		16:25:59		68		31

		20-Feb-08		18:07:10		66.2		52		20-Feb-08		18:06:20		67.4		51.5		20-Feb-08		18:07:53		70.41		48		1-Apr-08		18:25:59		68		29.5

		20-Feb-08		20:07:10		66.2		51		20-Feb-08		20:06:20		66.2		55		20-Feb-08		20:07:53		70.41		47		1-Apr-08		20:25:59		67.4		30.5

		20-Feb-08		22:07:10		66.2		52.5		20-Feb-08		22:06:20		67.4		51.5		20-Feb-08		22:07:53		71		45.5		1-Apr-08		22:25:59		68		29.5

		21-Feb-08		0:07:10		66.2		52.5		21-Feb-08		0:06:20		67.4		50.5		21-Feb-08		0:07:53		70.41		45.5		2-Apr-08		0:25:59		68		32.5

		21-Feb-08		2:07:10		65.6		52.5		21-Feb-08		2:06:20		66.81		47		21-Feb-08		2:07:53		69.8		44		2-Apr-08		2:25:59		68		33.5

		21-Feb-08		4:07:10		65.6		52		21-Feb-08		4:06:20		66.81		47.5		21-Feb-08		4:07:53		69.2		44		2-Apr-08		4:25:59		68		33

		21-Feb-08		6:07:10		65.6		52.5		21-Feb-08		6:06:20		66.81		47		21-Feb-08		6:07:53		68.61		44.5		2-Apr-08		6:25:59		68		31

		21-Feb-08		8:07:10		66.2		52		21-Feb-08		8:06:20		67.4		47		21-Feb-08		8:07:53		71		41.5		2-Apr-08		8:25:59		68		33.5

		21-Feb-08		10:07:10		66.2		52		21-Feb-08		10:06:20		67.4		48.5		21-Feb-08		10:07:53		72.21		44.5		2-Apr-08		10:25:59		68		33

		21-Feb-08		12:07:10		65.6		51.5		21-Feb-08		12:06:20		66.81		49.5		21-Feb-08		12:07:53		70.41		48		2-Apr-08		12:25:59		68.61		33

		21-Feb-08		14:07:10		65.6		51		21-Feb-08		14:06:20		68		41		21-Feb-08		14:07:53		71.6		48.5		2-Apr-08		14:25:59		68		36.5

		21-Feb-08		16:07:10		66.81		50.5		21-Feb-08		16:06:20		68		40.5		21-Feb-08		16:07:53		71		47.5		2-Apr-08		16:25:59		68		34

		21-Feb-08		18:07:10		66.2		52		21-Feb-08		18:06:20		67.4		42.5		21-Feb-08		18:07:53		70.41		45.5		2-Apr-08		18:25:59		68		34

		21-Feb-08		20:07:10		66.2		52.5		21-Feb-08		20:06:20		66.81		44.5		21-Feb-08		20:07:53		70.41		43.5		2-Apr-08		20:25:59		68		37

		21-Feb-08		22:07:10		66.2		51.5		21-Feb-08		22:06:20		67.4		45		21-Feb-08		22:07:53		71		42.5		2-Apr-08		22:25:59		68.61		36.5

		22-Feb-08		0:07:10		66.2		49.5		22-Feb-08		0:06:20		66.81		43		22-Feb-08		0:07:53		70.41		41.5		3-Apr-08		0:25:59		68.61		36.5

		22-Feb-08		2:07:10		65.6		51.5		22-Feb-08		2:06:20		66.81		43.5		22-Feb-08		2:07:53		69.8		41		3-Apr-08		2:25:59		68		36

		22-Feb-08		4:07:10		65.6		52		22-Feb-08		4:06:20		66.81		43.5		22-Feb-08		4:07:53		69.2		41.5		3-Apr-08		4:25:59		67.4		35

		22-Feb-08		6:07:10		66.2		51.5		22-Feb-08		6:06:20		66.81		44		22-Feb-08		6:07:53		69.2		42		3-Apr-08		6:25:59		69.2		34

		22-Feb-08		8:07:10		66.2		51		22-Feb-08		8:06:20		66.2		46		22-Feb-08		8:07:53		71		44		3-Apr-08		8:25:59		67.4		36.5

		22-Feb-08		10:07:10		66.81		48		22-Feb-08		10:06:20		66.2		48		22-Feb-08		10:07:53		71.6		43		3-Apr-08		10:25:59		68		36.5

		22-Feb-08		12:07:10		66.81		48.5		22-Feb-08		12:06:20		67.4		43.5		22-Feb-08		12:07:53		71		39		3-Apr-08		12:25:59		68		37.5

		22-Feb-08		14:07:10		66.81		49		22-Feb-08		14:06:20		68		44.5		22-Feb-08		14:07:53		71		44		3-Apr-08		14:25:59		68		39

		22-Feb-08		16:07:10		66.2		50		22-Feb-08		16:06:20		68		48		22-Feb-08		16:07:53		71		40		3-Apr-08		16:25:59		68		37.5

		22-Feb-08		18:07:10		66.2		51.5		22-Feb-08		18:06:20		66.81		48		22-Feb-08		18:07:53		71		46.5		3-Apr-08		18:25:59		68.61		35

		22-Feb-08		20:07:10		66.2		49		22-Feb-08		20:06:20		67.4		49.5		22-Feb-08		20:07:53		70.41		42		3-Apr-08		20:25:59		68		35.5

		22-Feb-08		22:07:10		66.2		51		22-Feb-08		22:06:20		66.81		51.5		22-Feb-08		22:07:53		70.41		45.5		3-Apr-08		22:25:59		68.61		34

		23-Feb-08		0:07:10		65.6		50.5		23-Feb-08		0:06:20		66.81		49.5		23-Feb-08		0:07:53		70.41		44.5		4-Apr-08		0:25:59		68		34

		23-Feb-08		2:07:10		65.6		49		23-Feb-08		2:06:20		67.4		48		23-Feb-08		2:07:53		69.8		43.5		4-Apr-08		2:25:59		68		33.5

		23-Feb-08		4:07:10		65.6		49		23-Feb-08		4:06:20		67.4		46		23-Feb-08		4:07:53		69.8		43		4-Apr-08		4:25:59		68		35

		23-Feb-08		6:07:10		65.6		46.5		23-Feb-08		6:06:20		66.81		47		23-Feb-08		6:07:53		69.2		43		4-Apr-08		6:25:59		68.61		36.5

		23-Feb-08		8:07:10		66.2		48.5		23-Feb-08		8:06:20		66.2		48		23-Feb-08		8:07:53		71		40.5		4-Apr-08		8:25:59		68		38

		23-Feb-08		10:07:10		66.2		49.5		23-Feb-08		10:06:20		67.4		48		23-Feb-08		10:07:53		71.6		48.5		4-Apr-08		10:25:59		67.4		39

		23-Feb-08		12:07:10		66.81		48.5		23-Feb-08		12:06:20		67.4		47.5		23-Feb-08		12:07:53		71		49.5		4-Apr-08		12:25:59		73.4		36.5

		23-Feb-08		14:07:10		66.81		48.5		23-Feb-08		14:06:20		67.4		47		23-Feb-08		14:07:53		71		45.5		4-Apr-08		14:25:59		74.01		36

		23-Feb-08		16:07:10		66.81		44		23-Feb-08		16:06:20		68		41.5		23-Feb-08		16:07:53		71.6		45.5		4-Apr-08		16:25:59		74.6		37.5

		23-Feb-08		18:07:10		66.2		48		23-Feb-08		18:06:20		67.4		39.5		23-Feb-08		18:07:53		71		42.5		4-Apr-08		18:25:59		74.01		36.5

		23-Feb-08		20:07:10		66.2		48		23-Feb-08		20:06:20		66.81		38		23-Feb-08		20:07:53		70.41		40		4-Apr-08		20:25:59		73.4		36.5

		23-Feb-08		22:07:10		66.2		48.5		23-Feb-08		22:06:20		66.2		38.5		23-Feb-08		22:07:53		69.8		40.5		4-Apr-08		22:25:59		71.6		37

		24-Feb-08		0:07:10		65.6		49.5		24-Feb-08		0:06:20		65.01		38		24-Feb-08		0:07:53		69.2		38		5-Apr-08		0:25:59		70.41		36.5

		24-Feb-08		2:07:10		65.6		41.5		24-Feb-08		2:06:20		64.4		38		24-Feb-08		2:07:53		68		38		5-Apr-08		2:25:59		69.2		36.5

		24-Feb-08		4:07:10		65.6		48		24-Feb-08		4:06:20		63.8		37		24-Feb-08		4:07:53		66.81		37.5		5-Apr-08		4:25:59		68.61		38

		24-Feb-08		6:07:10		65.6		48		24-Feb-08		6:06:20		63.8		38		24-Feb-08		6:07:53		66.2		38.5		5-Apr-08		6:25:59		69.2		37.5

		24-Feb-08		8:07:10		66.2		48		24-Feb-08		8:06:20		64.4		38.5		24-Feb-08		8:07:53		68		38		5-Apr-08		8:25:59		70.41		38.5

		24-Feb-08		10:07:10		66.81		43		24-Feb-08		10:06:20		65.01		42		24-Feb-08		10:07:53		67.4		39.5		5-Apr-08		10:25:59		71.6		38.5

		24-Feb-08		12:07:10		66.81		47		24-Feb-08		12:06:20		66.2		42		24-Feb-08		12:07:53		68		40		5-Apr-08		12:25:59		72.8		38.5

		24-Feb-08		14:07:10		66.2		48		24-Feb-08		14:06:20		66.2		42.5		24-Feb-08		14:07:53		68		41		5-Apr-08		14:25:59		73.4		38.5

		24-Feb-08		16:07:10		66.2		48		24-Feb-08		16:06:20		65.6		44.5		24-Feb-08		16:07:53		68		42		5-Apr-08		16:25:59		74.01		38.5

		24-Feb-08		18:07:10		66.2		49		24-Feb-08		18:06:20		65.01		41.5		24-Feb-08		18:07:53		67.4		41.5		5-Apr-08		18:25:59		73.4		37.5

		24-Feb-08		20:07:10		65.6		45		24-Feb-08		20:06:20		65.6		44		24-Feb-08		20:07:53		66.81		42.5		5-Apr-08		20:25:59		72.8		37

		24-Feb-08		22:07:10		66.2		49		24-Feb-08		22:06:20		65.6		48		24-Feb-08		22:07:53		66.81		44.5		5-Apr-08		22:25:59		71.6		36.5

		25-Feb-08		0:07:10		66.2		49		25-Feb-08		0:06:20		66.2		47.5		25-Feb-08		0:07:53		67.4		45		6-Apr-08		0:25:59		69.8		36

		25-Feb-08		2:07:10		66.2		49		25-Feb-08		2:06:20		66.81		48		25-Feb-08		2:07:53		67.4		45.5		6-Apr-08		2:25:59		68		36.5

		25-Feb-08		4:07:10		66.2		49.5		25-Feb-08		4:06:20		66.81		49		25-Feb-08		4:07:53		67.4		46		6-Apr-08		4:25:59		67.4		37

		25-Feb-08		6:07:10		66.2		48		25-Feb-08		6:06:20		66.81		50		25-Feb-08		6:07:53		67.4		47		6-Apr-08		6:25:59		66.81		36.5

		25-Feb-08		8:07:10		66.2		49.5		25-Feb-08		8:06:20		66.81		51		25-Feb-08		8:07:53		67.4		48		6-Apr-08		8:25:59		66.81		36.5

		25-Feb-08		10:07:10		66.2		51.5		25-Feb-08		10:06:20		67.4		51.5		25-Feb-08		10:07:53		67.4		49.5		6-Apr-08		10:25:59		68.61		38

		25-Feb-08		12:07:10		66.2		52		25-Feb-08		12:06:20		66.81		52.5		25-Feb-08		12:07:53		68		49		6-Apr-08		12:25:59		70.41		38.5

		25-Feb-08		14:07:10		66.2		53		25-Feb-08		14:06:20		67.4		52		25-Feb-08		14:07:53		68		49.5		6-Apr-08		14:25:59		71.6		37.5

		25-Feb-08		16:07:10		66.2		49.5		25-Feb-08		16:06:20		66.2		52.5		25-Feb-08		16:07:53		68		49		6-Apr-08		16:25:59		72.21		37

		25-Feb-08		18:07:10		66.2		50.5		25-Feb-08		18:06:20		67.4		49.5		25-Feb-08		18:07:53		68		48		6-Apr-08		18:25:59		72.8		36.5

		25-Feb-08		20:07:10		66.2		50		25-Feb-08		20:06:20		67.4		47.5		25-Feb-08		20:07:53		68		47.5		6-Apr-08		20:25:59		72.21		36.5

		25-Feb-08		22:07:10		66.2		50		25-Feb-08		22:06:20		66.81		48		25-Feb-08		22:07:53		68		47		6-Apr-08		22:25:59		71		37

		26-Feb-08		0:07:10		66.2		49.5		26-Feb-08		0:06:20		66.81		49.5		26-Feb-08		0:07:53		68		47		7-Apr-08		0:25:59		69.2		37

		26-Feb-08		2:07:10		65.6		50.5		26-Feb-08		2:06:20		66.2		49		26-Feb-08		2:07:53		67.4		47		7-Apr-08		2:25:59		68.61		37.5

		26-Feb-08		4:07:10		65.6		49		26-Feb-08		4:06:20		65.6		47		26-Feb-08		4:07:53		67.4		45.5		7-Apr-08		4:25:59		67.4		37.5

		26-Feb-08		6:07:10		65.6		49		26-Feb-08		6:06:20		65.6		48		26-Feb-08		6:07:53		66.81		45.5		7-Apr-08		6:25:59		66.81		38

		26-Feb-08		8:07:10		66.2		49		26-Feb-08		8:06:20		66.2		46.5		26-Feb-08		8:07:53		69.8		44		7-Apr-08		8:25:59		66.81		38.5

		26-Feb-08		10:07:10		66.81		49		26-Feb-08		10:06:20		66.81		48.5		26-Feb-08		10:07:53		71.6		42		7-Apr-08		10:25:59		68		39.5

		26-Feb-08		12:07:10		66.81		49.5		26-Feb-08		12:06:20		67.4		46.5		26-Feb-08		12:07:53		70.41		49.5		7-Apr-08		12:25:59		68.61		40

		26-Feb-08		14:07:10		66.81		48		26-Feb-08		14:06:20		67.4		45.5		26-Feb-08		14:07:53		71.6		51		7-Apr-08		14:25:59		69.8		39

		26-Feb-08		16:07:10		66.81		47.5		26-Feb-08		16:06:20		67.4		44.5		26-Feb-08		16:07:53		71		50.5		7-Apr-08		16:25:59		70.41		37.5

		26-Feb-08		18:07:10		66.2		49		26-Feb-08		18:06:20		67.4		47		26-Feb-08		18:07:53		71		50.5		7-Apr-08		18:25:59		71		36

		26-Feb-08		20:07:10		66.2		48.5		26-Feb-08		20:06:20		66.2		48.5		26-Feb-08		20:07:53		70.41		46		7-Apr-08		20:25:59		69.8		35

		26-Feb-08		22:07:10		65.6		50		26-Feb-08		22:06:20		66.81		46		26-Feb-08		22:07:53		70.41		44.5		7-Apr-08		22:25:59		68.61		35

		27-Feb-08		0:07:10		65.6		47.5		27-Feb-08		0:06:20		66.2		45		27-Feb-08		0:07:53		69.8		41.5		8-Apr-08		0:25:59		68		35.5

		27-Feb-08		2:07:10		65.6		49		27-Feb-08		2:06:20		65.01		43.5		27-Feb-08		2:07:53		68.61		41		8-Apr-08		2:25:59		66.81		36.5

		27-Feb-08		4:07:10		66.2		49		27-Feb-08		4:06:20		65.01		43.5		27-Feb-08		4:07:53		68		41		8-Apr-08		4:25:59		66.2		37

		27-Feb-08		6:07:10		66.2		48		27-Feb-08		6:06:20		65.01		44		27-Feb-08		6:07:53		67.4		41.5		8-Apr-08		6:25:59		67.4		36

		27-Feb-08		8:07:10		66.2		47.5		27-Feb-08		8:06:20		65.6		41		27-Feb-08		8:07:53		69.8		40		8-Apr-08		8:25:59		68.61		35.5

		27-Feb-08		10:07:10		66.2		47		27-Feb-08		10:06:20		66.81		44.5		27-Feb-08		10:07:53		71.6		38		8-Apr-08		10:25:59		71.6		36

		27-Feb-08		12:07:10		66.81		48.5		27-Feb-08		12:06:20		68		44.5		27-Feb-08		12:07:53		71		40.5		8-Apr-08		12:25:59		72.8		35

		27-Feb-08		14:07:10		66.81		46.5		27-Feb-08		14:06:20		67.4		44		27-Feb-08		14:07:53		70.41		39.5		8-Apr-08		14:25:59		74.01		33.5

		27-Feb-08		16:07:10		66.81		47		27-Feb-08		16:06:20		68.61		42		27-Feb-08		16:07:53		70.41		49.5		8-Apr-08		16:25:59		74.01		35.5

		27-Feb-08		18:07:10		66.2		50		27-Feb-08		18:06:20		68		48.5		27-Feb-08		18:07:53		70.41		42.5		8-Apr-08		18:25:59		73.4		34.5

		27-Feb-08		20:07:10		66.2		49.5		27-Feb-08		20:06:20		66.81		51.5		27-Feb-08		20:07:53		70.41		42.5		8-Apr-08		20:25:59		72.8		34.5

		27-Feb-08		22:07:10		66.2		49.5		27-Feb-08		22:06:20		66.81		50		27-Feb-08		22:07:53		71		46		8-Apr-08		22:25:59		72.21		34

		28-Feb-08		0:07:10		66.2		48.5		28-Feb-08		0:06:20		66.2		49.5		28-Feb-08		0:07:53		71		43		9-Apr-08		0:25:59		70.41		35

		28-Feb-08		2:07:10		66.2		49		28-Feb-08		2:06:20		66.81		47.5		28-Feb-08		2:07:53		70.41		42.5		9-Apr-08		2:25:59		69.2		35

		28-Feb-08		4:07:10		65.6		49		28-Feb-08		4:06:20		66.2		46.5		28-Feb-08		4:07:53		69.8		41.5		9-Apr-08		4:25:59		68.61		35.5

		28-Feb-08		6:07:10		65.6		50		28-Feb-08		6:06:20		65.6		45		28-Feb-08		6:07:53		69.2		41		9-Apr-08		6:25:59		69.2		36

		28-Feb-08		8:07:10		66.2		48		28-Feb-08		8:06:20		65.6		42.5		28-Feb-08		8:07:53		70.41		41.5		9-Apr-08		8:25:59		70.41		36.5

		28-Feb-08		10:07:10		66.2		47.5		28-Feb-08		10:06:20		67.4		46		28-Feb-08		10:07:53		71		39		9-Apr-08		10:25:59		72.8		35.5

		28-Feb-08		12:07:10		66.81		49		28-Feb-08		12:06:20		68		48		28-Feb-08		12:07:53		71		41		9-Apr-08		12:25:59		74.01		35

		28-Feb-08		14:07:10		66.81		49.5		28-Feb-08		14:06:20		68.61		47		28-Feb-08		14:07:53		71		40		9-Apr-08		14:25:59		74.01		34

		28-Feb-08		16:07:10		66.81		51.5		28-Feb-08		16:06:20		67.4		56		28-Feb-08		16:07:53		71		51.5		9-Apr-08		16:25:59		74.01		34.5

		28-Feb-08		18:07:10		66.2		51.5		28-Feb-08		18:06:20		68		49.5		28-Feb-08		18:07:53		71		52		9-Apr-08		18:25:59		74.01		34.5

		28-Feb-08		20:07:10		66.2		48.5		28-Feb-08		20:06:20		66.81		53		28-Feb-08		20:07:53		71.6		47		9-Apr-08		20:25:59		72.8		33.5

		28-Feb-08		22:07:10		66.2		50		28-Feb-08		22:06:20		67.4		49.5		28-Feb-08		22:07:53		72.21		44		9-Apr-08		22:25:59		71		33.5

		29-Feb-08		0:07:10		65.6		49		29-Feb-08		0:06:20		66.81		48		29-Feb-08		0:07:53		71.6		42.5		10-Apr-08		0:25:59		69.2		33.5

		29-Feb-08		2:07:10		65.6		49		29-Feb-08		2:06:20		66.2		46		29-Feb-08		2:07:53		70.41		41.5		10-Apr-08		2:25:59		68		34.5

		29-Feb-08		4:07:10		66.2		49		29-Feb-08		4:06:20		65.01		44.5		29-Feb-08		4:07:53		69.2		40.5		10-Apr-08		4:25:59		66.81		35

		29-Feb-08		6:07:10		65.6		48.5		29-Feb-08		6:06:20		65.01		42		29-Feb-08		6:07:53		68.61		39.5		10-Apr-08		6:25:59		68		34.5

		29-Feb-08		8:07:10		66.2		48		29-Feb-08		8:06:20		65.01		40		29-Feb-08		8:07:53		71		38		10-Apr-08		8:25:59		69.2		35

		29-Feb-08		10:07:10		66.2		48		29-Feb-08		10:06:20		66.81		45.5		29-Feb-08		10:07:53		72.21		42.5		10-Apr-08		10:25:59		72.21		36

		29-Feb-08		12:07:10		66.81		48.5		29-Feb-08		12:06:20		66.81		47.5		29-Feb-08		12:07:53		71.6		47		10-Apr-08		12:25:59		74.01		35.5

		29-Feb-08		14:07:10		66.81		50.5		29-Feb-08		14:06:20		68.61		47.5		29-Feb-08		14:07:53		71		45		10-Apr-08		14:25:59		74.6		36.5

		29-Feb-08		16:07:10		66.81		51.5		29-Feb-08		16:06:20		68		45.5		29-Feb-08		16:07:53		70.41		44		10-Apr-08		16:25:59		74.01		37

		29-Feb-08		18:07:10		66.2		52		29-Feb-08		18:06:20		67.4		54		29-Feb-08		18:07:53		71		52		10-Apr-08		18:25:59		73.4		34.5

		29-Feb-08		20:07:10		66.2		49		29-Feb-08		20:06:20		67.4		48.5		29-Feb-08		20:07:53		69.8		50		10-Apr-08		20:25:59		72.8		35

		29-Feb-08		22:07:10		65.6		50		29-Feb-08		22:06:20		66.81		49.5		29-Feb-08		22:07:53		71.6		44.5		10-Apr-08		22:25:59		71.6		35

		1-Mar-08		0:07:10		65.6		48.5		1-Mar-08		0:06:20		66.81		47		1-Mar-08		0:07:53		71.6		42		11-Apr-08		0:25:59		70.41		35.5

		1-Mar-08		2:07:10		65.6		48.5		1-Mar-08		2:06:20		66.2		49		1-Mar-08		2:07:53		71		42		11-Apr-08		2:25:59		69.2		35

		1-Mar-08		4:07:10		65.6		49.5		1-Mar-08		4:06:20		66.2		48.5		1-Mar-08		4:07:53		70.41		42.5		11-Apr-08		4:25:59		68.61		35.5

		1-Mar-08		6:07:10		65.6		49		1-Mar-08		6:06:20		65.6		48		1-Mar-08		6:07:53		70.41		42.5		11-Apr-08		6:25:59		69.2		35.5

		1-Mar-08		8:07:10		66.2		48.5		1-Mar-08		8:06:20		66.2		46.5		1-Mar-08		8:07:53		71		43.5		11-Apr-08		8:25:59		71		36

		1-Mar-08		10:07:10		66.2		48.5		1-Mar-08		10:06:20		67.4		45		1-Mar-08		10:07:53		71		46		11-Apr-08		10:25:59		72.8		36.5

		1-Mar-08		12:07:10		66.81		49.5		1-Mar-08		12:06:20		66.81		49.5		1-Mar-08		12:07:53		71		48		11-Apr-08		12:25:59		74.6		36.5

		1-Mar-08		14:07:10		66.81		49		1-Mar-08		14:06:20		68		51.5		1-Mar-08		14:07:53		71		40		11-Apr-08		14:25:59		74.6		36

		1-Mar-08		16:07:10		66.81		51.5		1-Mar-08		16:06:20		68		56		1-Mar-08		16:07:53		71		51.5		11-Apr-08		16:25:59		74.6		36.5

		1-Mar-08		18:07:10		66.2		49		1-Mar-08		18:06:20		66.81		50.5		1-Mar-08		18:07:53		70.41		48.5		11-Apr-08		18:25:59		74.01		36

		1-Mar-08		20:07:10		65.6		49.5		1-Mar-08		20:06:20		66.81		49		1-Mar-08		20:07:53		69.8		46.5		11-Apr-08		20:25:59		74.01		36

		1-Mar-08		22:07:10		65.6		49		1-Mar-08		22:06:20		66.81		47		1-Mar-08		22:07:53		69.8		44		11-Apr-08		22:25:59		72.8		36.5

		2-Mar-08		0:07:10		65.6		49		2-Mar-08		0:06:20		66.81		48.5		2-Mar-08		0:07:53		69.8		43.5		12-Apr-08		0:25:59		71.6		37

		2-Mar-08		2:07:10		65.6		49		2-Mar-08		2:06:20		66.81		48.5		2-Mar-08		2:07:53		69.8		43.5		12-Apr-08		2:25:59		69.8		37

		2-Mar-08		4:07:10		65.6		49		2-Mar-08		4:06:20		66.2		48.5		2-Mar-08		4:07:53		69.2		43.5		12-Apr-08		4:25:59		69.2		37.5

		2-Mar-08		6:07:10		65.6		49		2-Mar-08		6:06:20		66.2		48		2-Mar-08		6:07:53		69.2		43.5		12-Apr-08		6:25:59		69.8		37

		2-Mar-08		8:07:10		65.6		49		2-Mar-08		8:06:20		66.81		45		2-Mar-08		8:07:53		71.6		41		12-Apr-08		8:25:59		71		37

		2-Mar-08		10:07:10		66.2		48.5		2-Mar-08		10:06:20		68		42		2-Mar-08		10:07:53		71		36.5		12-Apr-08		10:25:59		73.4		39

		2-Mar-08		12:07:10		66.2		49		2-Mar-08		12:06:20		67.4		35.5		2-Mar-08		12:07:53		70.41		40.5		12-Apr-08		12:25:59		74.6		38.5

		2-Mar-08		14:07:10		65.6		48		2-Mar-08		14:06:20		66.81		34.5		2-Mar-08		14:07:53		71		36.5		12-Apr-08		14:25:59		75.2		36.5

		2-Mar-08		16:07:10		65.6		47		2-Mar-08		16:06:20		67.4		35.5		2-Mar-08		16:07:53		70.41		35		12-Apr-08		16:25:59		74.6		36

		2-Mar-08		18:07:10		65.6		48.5		2-Mar-08		18:06:20		66.2		34.5		2-Mar-08		18:07:53		69.8		34.5		12-Apr-08		18:25:59		74.01		35

		2-Mar-08		20:07:10		65.6		47.5		2-Mar-08		20:06:20		66.2		36.5		2-Mar-08		20:07:53		69.8		35.5		12-Apr-08		20:25:59		73.4		33

		2-Mar-08		22:07:10		65.6		48		2-Mar-08		22:06:20		66.81		37.5		2-Mar-08		22:07:53		69.2		36.5		12-Apr-08		22:25:59		72.8		34.5

		3-Mar-08		0:07:10		65.6		47		3-Mar-08		0:06:20		66.2		37		3-Mar-08		0:07:53		68.61		36.5		13-Apr-08		0:25:59		71.6		35.5

		3-Mar-08		2:07:10		65.6		46.5		3-Mar-08		2:06:20		65.6		35		3-Mar-08		2:07:53		68		36.5		13-Apr-08		2:25:59		70.41		36.5

		3-Mar-08		4:07:10		65.6		49.5		3-Mar-08		4:06:20		65.01		34.5		3-Mar-08		4:07:53		67.4		36		13-Apr-08		4:25:59		69.8		36.5

		3-Mar-08		6:07:10		65.6		48.5		3-Mar-08		6:06:20		65.01		33		3-Mar-08		6:07:53		66.81		36		13-Apr-08		6:25:59		69.8		36.5

		3-Mar-08		8:07:10		66.2		47.5		3-Mar-08		8:06:20		65.01		32.5		3-Mar-08		8:07:53		67.4		34.5		13-Apr-08		8:25:59		69.8		36.5

		3-Mar-08		10:07:10		65.01		47		3-Mar-08		10:06:20		66.2		30.5		3-Mar-08		10:07:53		68		34		13-Apr-08		10:25:59		71.6		38.5

		3-Mar-08		12:07:10		65.6		48		3-Mar-08		12:06:20		67.4		27.5		3-Mar-08		12:07:53		69.2		31.5		13-Apr-08		12:25:59		74.01		37.5

		3-Mar-08		14:07:10		66.2		44.5		3-Mar-08		14:06:20		68		21.5		3-Mar-08		14:07:53		69.8		29		13-Apr-08		14:25:59		74.01		37.5

		3-Mar-08		16:07:10		66.2		44.5		3-Mar-08		16:06:20		68		19		3-Mar-08		16:07:53		69.8		29		13-Apr-08		16:25:59		72.8		38

		3-Mar-08		18:07:10		66.2		45		3-Mar-08		18:06:20		67.4		19		3-Mar-08		18:07:53		69.2		29.5		13-Apr-08		18:25:59		72.8		37.5

		3-Mar-08		20:07:10		65.6		46		3-Mar-08		20:06:20		66.81		19.5		3-Mar-08		20:07:53		70.41		28		13-Apr-08		20:25:59		72.8		37

		3-Mar-08		22:07:10		65.6		47.5		3-Mar-08		22:06:20		67.4		26		3-Mar-08		22:07:53		70.41		29.5		13-Apr-08		22:25:59		72.8		39.5

		4-Mar-08		0:07:10		65.6		48		4-Mar-08		0:06:20		66.2		34		4-Mar-08		0:07:53		69.8		32		14-Apr-08		0:25:59		71.6		39.5

		4-Mar-08		2:07:10		65.6		48.5		4-Mar-08		2:06:20		65.6		35.5		4-Mar-08		2:07:53		69.2		33.5		14-Apr-08		2:25:59		71		39

		4-Mar-08		4:07:10		65.6		46.5		4-Mar-08		4:06:20		65.01		35.5		4-Mar-08		4:07:53		68		34		14-Apr-08		4:25:59		69.8		38.5

		4-Mar-08		6:07:10		66.2		47.5		4-Mar-08		6:06:20		64.4		35		4-Mar-08		6:07:53		67.4		34.5		14-Apr-08		6:25:59		69.2		38.5

		4-Mar-08		8:07:10		66.2		47.5		4-Mar-08		8:06:20		65.01		34		4-Mar-08		8:07:53		69.2		34		14-Apr-08		8:25:59		68.61		39

		4-Mar-08		10:07:10		66.2		46		4-Mar-08		10:06:20		67.4		35.5		4-Mar-08		10:07:53		72.21		36		14-Apr-08		10:25:59		71		40.5

		4-Mar-08		12:07:10		66.81		47		4-Mar-08		12:06:20		68		34.5		4-Mar-08		12:07:53		71		40.5		14-Apr-08		12:25:59		72.8		40

		4-Mar-08		14:07:10		66.81		46		4-Mar-08		14:06:20		68		29		4-Mar-08		14:07:53		71		40		14-Apr-08		14:25:59		74.01		39

		4-Mar-08		16:07:10		66.81		47		4-Mar-08		16:06:20		68.61		31		4-Mar-08		16:07:53		70.41		37		14-Apr-08		16:25:59		74.01		39

		4-Mar-08		18:07:10		66.2		47.5		4-Mar-08		18:06:20		68		30		4-Mar-08		18:07:53		70.41		34.5		14-Apr-08		18:25:59		72.8		39.5

		4-Mar-08		20:07:10		66.2		45.5		4-Mar-08		20:06:20		67.4		30		4-Mar-08		20:07:53		69.8		34		14-Apr-08		20:25:59		72.8		40

		4-Mar-08		22:07:10		65.6		48		4-Mar-08		22:06:20		66.2		32		4-Mar-08		22:07:53		70.41		34		14-Apr-08		22:25:59		71.6		39.5

		5-Mar-08		0:07:10		65.6		47		5-Mar-08		0:06:20		67.4		33		5-Mar-08		0:07:53		71		33.5		15-Apr-08		0:25:59		71		39.5

		5-Mar-08		2:07:10		65.6		47.5		5-Mar-08		2:06:20		65.6		34.5		5-Mar-08		2:07:53		69.8		33.5		15-Apr-08		2:25:59		69.8		39

		5-Mar-08		4:07:10		65.6		48.5		5-Mar-08		4:06:20		65.01		35.5		5-Mar-08		4:07:53		68.61		33.5		15-Apr-08		4:25:59		68.61		39

		5-Mar-08		6:07:10		66.2		49		5-Mar-08		6:06:20		64.4		35		5-Mar-08		6:07:53		67.4		34		15-Apr-08		6:25:59		69.2		39

		5-Mar-08		8:07:10		66.2		47		5-Mar-08		8:06:20		65.01		34.5		5-Mar-08		8:07:53		69.8		33		15-Apr-08		8:25:59		70.41		39.5

		5-Mar-08		10:07:10		66.2		46		5-Mar-08		10:06:20		66.81		37.5		5-Mar-08		10:07:53		72.21		34.5		15-Apr-08		10:25:59		72.8		40.5

		5-Mar-08		12:07:10		66.81		46.5		5-Mar-08		12:06:20		68		38		5-Mar-08		12:07:53		71		42.5		15-Apr-08		12:25:59		74.6		38.5

		5-Mar-08		14:07:10		66.81		47		5-Mar-08		14:06:20		68		38		5-Mar-08		14:07:53		71		36.5		15-Apr-08		14:25:59		74.6		37

		5-Mar-08		16:07:10		66.81		45.5		5-Mar-08		16:06:20		68		35.5		5-Mar-08		16:07:53		70.41		37		15-Apr-08		16:25:59		74.01		36.5

		5-Mar-08		18:07:10		66.81		47.5		5-Mar-08		18:06:20		68		38.5		5-Mar-08		18:07:53		69.8		43		15-Apr-08		18:25:59		73.4		35

		5-Mar-08		20:07:10		66.2		48		5-Mar-08		20:06:20		67.4		42		5-Mar-08		20:07:53		70.41		41.5		15-Apr-08		20:25:59		72.21		34

		5-Mar-08		22:07:10		66.2		48		5-Mar-08		22:06:20		67.4		36.5		5-Mar-08		22:07:53		70.41		39		15-Apr-08		22:25:59		71		33.5

		6-Mar-08		0:07:10		65.6		48.5		6-Mar-08		0:06:20		66.2		38		6-Mar-08		0:07:53		70.41		36.5		16-Apr-08		0:25:59		69.2		33.5

		6-Mar-08		2:07:10		65.6		48.5		6-Mar-08		2:06:20		65.6		38		6-Mar-08		2:07:53		69.8		36		16-Apr-08		2:25:59		68		34

		6-Mar-08		4:07:10		65.6		48.5		6-Mar-08		4:06:20		65.01		37.5		6-Mar-08		4:07:53		68.61		36		16-Apr-08		4:25:59		67.4		35

		6-Mar-08		6:07:10		66.2		48.5		6-Mar-08		6:06:20		65.01		36		6-Mar-08		6:07:53		67.4		36		16-Apr-08		6:25:59		68		34

		6-Mar-08		8:07:10		66.2		47.5		6-Mar-08		8:06:20		65.01		35		6-Mar-08		8:07:53		70.41		34.5		16-Apr-08		8:25:59		70.41		34.5

		6-Mar-08		10:07:10		66.81		46		6-Mar-08		10:06:20		67.4		36.5		6-Mar-08		10:07:53		71.6		35		16-Apr-08		10:25:59		72.8		35

		6-Mar-08		12:07:10		66.81		46.5		6-Mar-08		12:06:20		68		34.5		6-Mar-08		12:07:53		70.41		44.5		16-Apr-08		12:25:59		74.6		34.5

		6-Mar-08		14:07:10		66.81		46.5		6-Mar-08		14:06:20		68.61		28		6-Mar-08		14:07:53		70.41		41		16-Apr-08		14:25:59		74.6		33.5

		6-Mar-08		16:07:10		66.81		43.5		6-Mar-08		16:06:20		68.61		25		6-Mar-08		16:07:53		70.41		39		16-Apr-08		16:25:59		74.01		33.5

		6-Mar-08		18:07:10		66.2		41.5		6-Mar-08		18:06:20		68		29.5		6-Mar-08		18:07:53		69.8		38.5		16-Apr-08		18:25:59		73.4		33

		6-Mar-08		20:07:10		66.2		48.5		6-Mar-08		20:06:20		66.81		37.5		6-Mar-08		20:07:53		71		37.5		16-Apr-08		20:25:59		72.8		32

		6-Mar-08		22:07:10		65.6		47		6-Mar-08		22:06:20		66.81		40		6-Mar-08		22:07:53		71.6		37		16-Apr-08		22:25:59		71.6		32

		7-Mar-08		0:07:10		65.6		48.5		7-Mar-08		0:06:20		66.2		39		7-Mar-08		0:07:53		70.41		36.5		17-Apr-08		0:25:59		69.8		32.5

		7-Mar-08		2:07:10		65.6		48.5		7-Mar-08		2:06:20		65.01		38		7-Mar-08		2:07:53		69.2		36		17-Apr-08		2:25:59		68.61		34

		7-Mar-08		4:07:10		65.6		42.5		7-Mar-08		4:06:20		64.4		37.5		7-Mar-08		4:07:53		68.61		36		17-Apr-08		4:25:59		68		34.5

		7-Mar-08		6:07:10		65.6		47		7-Mar-08		6:06:20		63.8		36.5		7-Mar-08		6:07:53		67.4		36		17-Apr-08		6:25:59		69.2		34

		7-Mar-08		8:07:10		66.2		48		7-Mar-08		8:06:20		65.01		35.5		7-Mar-08		8:07:53		70.41		35		17-Apr-08		8:25:59		71		34.5

		7-Mar-08		10:07:10		65.6		46.5		7-Mar-08		10:06:20		66.81		37.5		7-Mar-08		10:07:53		71.6		33.5		17-Apr-08		10:25:59		74.01		35

		7-Mar-08		12:07:10		66.2		48		7-Mar-08		12:06:20		67.4		39.5		7-Mar-08		12:07:53		71		39.5		17-Apr-08		12:25:59		75.2		34.5

		7-Mar-08		14:07:10		66.2		43.5		7-Mar-08		14:06:20		68		39		7-Mar-08		14:07:53		71.6		38.5		17-Apr-08		14:25:59		75.2		34.5

		7-Mar-08		16:07:10		66.81		47.5		7-Mar-08		16:06:20		68		40		7-Mar-08		16:07:53		70.41		36.5		17-Apr-08		16:25:59		74.6		34.5

		7-Mar-08		18:07:10		66.2		48		7-Mar-08		18:06:20		68		36.5		7-Mar-08		18:07:53		70.41		35		17-Apr-08		18:25:59		74.01		34

		7-Mar-08		20:07:10		66.2		48		7-Mar-08		20:06:20		66.81		40.5		7-Mar-08		20:07:53		69.8		36		17-Apr-08		20:25:59		74.01		35

		7-Mar-08		22:07:10		65.6		48.5		7-Mar-08		22:06:20		66.81		39		7-Mar-08		22:07:53		70.41		38		17-Apr-08		22:25:59		73.4		35

		8-Mar-08		0:07:10		65.6		43		8-Mar-08		0:06:20		66.2		40.5		8-Mar-08		0:07:53		69.8		37		18-Apr-08		0:25:59		71.6		35

		8-Mar-08		2:07:10		65.6		48.5		8-Mar-08		2:06:20		65.01		41.5		8-Mar-08		2:07:53		69.2		37		18-Apr-08		2:25:59		70.41		36

		8-Mar-08		4:07:10		65.6		48		8-Mar-08		4:06:20		64.4		39.5		8-Mar-08		4:07:53		68		37		18-Apr-08		4:25:59		69.2		36

		8-Mar-08		6:07:10		65.6		48.5		8-Mar-08		6:06:20		63.8		38.5		8-Mar-08		6:07:53		67.4		36.5		18-Apr-08		6:25:59		69.8		36

		8-Mar-08		8:07:10		66.2		47.5		8-Mar-08		8:06:20		65.6		37		8-Mar-08		8:07:53		69.2		36		18-Apr-08		8:25:59		71.6		36

		8-Mar-08		10:07:10		66.2		42		8-Mar-08		10:06:20		67.4		39.5		8-Mar-08		10:07:53		71		38.5		18-Apr-08		10:25:59		74.01		37.5

		8-Mar-08		12:07:10		66.2		48		8-Mar-08		12:06:20		68		38.5		8-Mar-08		12:07:53		70.41		43		18-Apr-08		12:25:59		75.2		39

		8-Mar-08		14:07:10		66.2		47		8-Mar-08		14:06:20		67.4		38.5		8-Mar-08		14:07:53		71		36		18-Apr-08		14:25:59		75.2		38

		8-Mar-08		16:07:10		66.2		48		8-Mar-08		16:06:20		67.4		40		8-Mar-08		16:07:53		70.41		42		18-Apr-08		16:25:59		75.2		38

		8-Mar-08		18:07:10		66.2		49		8-Mar-08		18:06:20		67.4		44		8-Mar-08		18:07:53		70.41		42		18-Apr-08		18:25:59		74.6		37

		8-Mar-08		20:07:10		65.6		43.5		8-Mar-08		20:06:20		66.81		41.5		8-Mar-08		20:07:53		69.8		40		18-Apr-08		20:25:59		74.6		38

		8-Mar-08		22:07:10		65.6		48.5		8-Mar-08		22:06:20		66.2		45.5		8-Mar-08		22:07:53		70.41		40.5		18-Apr-08		22:25:59		73.4		37.5

		9-Mar-08		0:07:10		65.6		48.5		9-Mar-08		0:06:20		66.81		44.5		9-Mar-08		0:07:53		70.41		40		19-Apr-08		0:25:59		71.6		37.5

		9-Mar-08		2:07:10		65.6		47		9-Mar-08		2:06:20		66.2		43.5		9-Mar-08		2:07:53		69.8		39		19-Apr-08		2:25:59		71		38.5

		9-Mar-08		4:07:10		65.6		48		9-Mar-08		4:06:20		65.01		42.5		9-Mar-08		4:07:53		69.2		38.5		19-Apr-08		4:25:59		70.41		39.5

		9-Mar-08		6:07:10		65.6		42		9-Mar-08		6:06:20		64.4		42		9-Mar-08		6:07:53		68.61		38.5		19-Apr-08		6:25:59		71.6		39.5

		9-Mar-08		8:07:10		65.6		48		9-Mar-08		8:06:20		65.01		39		9-Mar-08		8:07:53		71		37		19-Apr-08		8:25:59		72.21		39

		9-Mar-08		10:07:10		66.2		48.5		9-Mar-08		10:06:20		66.81		43.5		9-Mar-08		10:07:53		71		34.5		19-Apr-08		10:25:59		73.4		40

		9-Mar-08		12:07:10		66.2		48.5		9-Mar-08		12:06:20		67.4		43		9-Mar-08		12:07:53		71.6		46		19-Apr-08		12:25:59		74.01		40.5

		9-Mar-08		14:07:10		66.2		47.5		9-Mar-08		14:06:20		68		35		9-Mar-08		14:07:53		71		43		19-Apr-08		14:25:59		75.2		41

		9-Mar-08		16:07:10		66.2		44		9-Mar-08		16:06:20		67.4		37.5		9-Mar-08		16:07:53		71		36.5		19-Apr-08		16:25:59		74.6		39.5

		9-Mar-08		18:07:10		66.2		47.5		9-Mar-08		18:06:20		67.4		31.5		9-Mar-08		18:07:53		69.8		36		19-Apr-08		18:25:59		74.01		38.5

		9-Mar-08		20:07:10		66.2		47.5		9-Mar-08		20:06:20		67.4		44.5		9-Mar-08		20:07:53		69.8		42		19-Apr-08		20:25:59		74.01		38.5

		9-Mar-08		22:07:10		65.6		48.5		9-Mar-08		22:06:20		66.2		47.5		9-Mar-08		22:07:53		71.6		40		19-Apr-08		22:25:59		72.8		37.5

		10-Mar-08		0:07:10		65.6		48.5		10-Mar-08		0:06:20		66.81		44.5		10-Mar-08		0:07:53		71		39.5		20-Apr-08		0:25:59		71		38

		10-Mar-08		2:07:10		65.6		48		10-Mar-08		2:06:20		66.2		44.5		10-Mar-08		2:07:53		70.41		39		20-Apr-08		2:25:59		69.8		38

		10-Mar-08		4:07:10		65.6		49		10-Mar-08		4:06:20		65.01		44		10-Mar-08		4:07:53		69.8		38.5		20-Apr-08		4:25:59		68.61		37.5

		10-Mar-08		6:07:10		65.6		49.5		10-Mar-08		6:06:20		64.4		42		10-Mar-08		6:07:53		68.61		38.5		20-Apr-08		6:25:59		68		37.5

		10-Mar-08		8:07:10		65.6		48		10-Mar-08		8:06:20		63.8		40.5		10-Mar-08		8:07:53		68		38		20-Apr-08		8:25:59		67.4		36.5

		10-Mar-08		10:07:10		65.6		48		10-Mar-08		10:06:20		66.2		41.5		10-Mar-08		10:07:53		69.2		39		20-Apr-08		10:25:59		68		37.5

		10-Mar-08		12:07:10		65.6		49		10-Mar-08		12:06:20		66.81		41		10-Mar-08		12:07:53		69.8		40		20-Apr-08		12:25:59		69.2		36.5

		10-Mar-08		14:07:10		66.2		47.5		10-Mar-08		14:06:20		68		37.5		10-Mar-08		14:07:53		70.41		41		20-Apr-08		14:25:59		70.41		33.5

		10-Mar-08		16:07:10		66.2		48		10-Mar-08		16:06:20		68		34.5		10-Mar-08		16:07:53		69.8		41.5		20-Apr-08		16:25:59		70.41		33

		10-Mar-08		18:07:10		66.2		48		10-Mar-08		18:06:20		68		33.5		10-Mar-08		18:07:53		70.41		39.5		20-Apr-08		18:25:59		70.41		32

		10-Mar-08		20:07:10		66.2		48		10-Mar-08		20:06:20		67.4		43		10-Mar-08		20:07:53		71		42		20-Apr-08		20:25:59		69.8		32

		10-Mar-08		22:07:10		65.6		49		10-Mar-08		22:06:20		66.2		45		10-Mar-08		22:07:53		71.6		40.5		20-Apr-08		22:25:59		68.61		33

		11-Mar-08		0:07:10		65.6		49		11-Mar-08		0:06:20		66.81		44.5		11-Mar-08		0:07:53		71		39.5		21-Apr-08		0:25:59		67.4		33.5

		11-Mar-08		2:07:10		65.6		49		11-Mar-08		2:06:20		66.2		45		11-Mar-08		2:07:53		70.41		39.5		21-Apr-08		2:25:59		66.81		34

		11-Mar-08		4:07:10		65.6		48.5		11-Mar-08		4:06:20		65.6		45		11-Mar-08		4:07:53		69.8		39		21-Apr-08		4:25:59		65.6		35

		11-Mar-08		6:07:10		65.6		48		11-Mar-08		6:06:20		65.01		45		11-Mar-08		6:07:53		71		39.5		21-Apr-08		6:25:59		65.01		35.5

		11-Mar-08		8:07:10		66.2		48		11-Mar-08		8:06:20		66.81		43		11-Mar-08		8:07:53		71.6		35.5		21-Apr-08		8:25:59		64.4		36.5

		11-Mar-08		10:07:10		66.81		47.5		11-Mar-08		10:06:20		67.4		43.5		11-Mar-08		10:07:53		71		37		21-Apr-08		10:25:59		65.6		37.5

		11-Mar-08		12:07:10		66.2		48		11-Mar-08		12:06:20		67.4		44		11-Mar-08		12:07:53		71		43		21-Apr-08		12:25:59		66.81		36

		11-Mar-08		14:07:10		66.81		52.5		11-Mar-08		14:06:20		68.61		52		11-Mar-08		14:07:53		70.41		48.5		21-Apr-08		14:25:59		68.61		36

		11-Mar-08		16:07:10		66.2		49.5		11-Mar-08		16:06:20		67.4		49		11-Mar-08		16:07:53		70.41		53		21-Apr-08		16:25:59		69.8		34.5

		11-Mar-08		18:07:10		66.2		49		11-Mar-08		18:06:20		68		45		11-Mar-08		18:07:53		71		42		21-Apr-08		18:25:59		69.8		33

		11-Mar-08		20:07:10		65.6		48.5		11-Mar-08		20:06:20		66.81		46		11-Mar-08		20:07:53		70.41		43		21-Apr-08		20:25:59		69.2		33

		11-Mar-08		22:07:10		65.6		48.5		11-Mar-08		22:06:20		67.4		45.5		11-Mar-08		22:07:53		71		42		21-Apr-08		22:25:59		68.61		34.5

		12-Mar-08		0:07:10		65.6		49		12-Mar-08		0:06:20		66.81		45.5		12-Mar-08		0:07:53		71.6		40.5		22-Apr-08		0:25:59		67.4		34.5

		12-Mar-08		2:07:10		65.6		49		12-Mar-08		2:06:20		66.81		45		12-Mar-08		2:07:53		70.41		40.5		22-Apr-08		2:25:59		66.2		35

		12-Mar-08		4:07:10		65.6		49		12-Mar-08		4:06:20		65.6		44.5		12-Mar-08		4:07:53		69.8		39.5		22-Apr-08		4:25:59		65.6		36

		12-Mar-08		6:07:10		65.6		49		12-Mar-08		6:06:20		65.01		44		12-Mar-08		6:07:53		70.41		39.5		22-Apr-08		6:25:59		66.81		34

		12-Mar-08		8:07:10		66.2		48		12-Mar-08		8:06:20		66.2		42.5		12-Mar-08		8:07:53		71		40.5		22-Apr-08		8:25:59		68		34.5

		12-Mar-08		10:07:10		66.2		49		12-Mar-08		10:06:20		66.81		50		12-Mar-08		10:07:53		70.41		45		22-Apr-08		10:25:59		72.21		36

		12-Mar-08		12:07:10		66.2		50		12-Mar-08		12:06:20		66.81		48		12-Mar-08		12:07:53		71.6		50		22-Apr-08		12:25:59		73.4		35.5

		12-Mar-08		14:07:10		66.2		49.5		12-Mar-08		14:06:20		68		50.5		12-Mar-08		14:07:53		71		41.5		22-Apr-08		14:25:59		73.4		35.5

		12-Mar-08		16:07:10		66.2		51.5		12-Mar-08		16:06:20		66.81		59.5		12-Mar-08		16:07:53		71		50.5		22-Apr-08		16:25:59		73.4		35.5

		12-Mar-08		18:07:10		66.2		51.5		12-Mar-08		18:06:20		67.4		48.5		12-Mar-08		18:07:53		70.41		50		22-Apr-08		18:25:59		72.8		35

		12-Mar-08		20:07:10		65.6		50		12-Mar-08		20:06:20		67.4		51.5		12-Mar-08		20:07:53		70.41		48		22-Apr-08		20:25:59		72.21		34.5

		12-Mar-08		22:07:10		65.6		49		12-Mar-08		22:06:20		67.4		49		12-Mar-08		22:07:53		70.41		44.5		22-Apr-08		22:25:59		71		34

		13-Mar-08		0:07:10		65.6		49		13-Mar-08		0:06:20		66.81		47.5		13-Mar-08		0:07:53		70.41		42		23-Apr-08		0:25:59		69.8		34

		13-Mar-08		2:07:10		65.6		49		13-Mar-08		2:06:20		65.6		46		13-Mar-08		2:07:53		70.41		41		23-Apr-08		2:25:59		68.61		34.5

		13-Mar-08		4:07:10		65.6		49.5		13-Mar-08		4:06:20		65.01		47		13-Mar-08		4:07:53		69.2		41		23-Apr-08		4:25:59		67.4		35

		13-Mar-08		6:07:10		65.6		49		13-Mar-08		6:06:20		65.6		48.5		13-Mar-08		6:07:53		70.41		42.5		23-Apr-08		6:25:59		68.61		34.5

		13-Mar-08		8:07:10		66.2		48		13-Mar-08		8:06:20		67.4		46.5		13-Mar-08		8:07:53		71		44		23-Apr-08		8:25:59		70.41		34.5

		13-Mar-08		10:07:10		66.2		48		13-Mar-08		10:06:20		66.81		46.5		13-Mar-08		10:07:53		71.6		41.5		23-Apr-08		10:25:59		71.6		35.5

		13-Mar-08		12:07:10		66.2		48.5		13-Mar-08		12:06:20		66.81		47.5		13-Mar-08		12:07:53		71		43		23-Apr-08		12:25:59		72.21		37.5

		13-Mar-08		14:07:10		66.81		49		13-Mar-08		14:06:20		67.4		46.5		13-Mar-08		14:07:53		71		46.5		23-Apr-08		14:25:59		72.8		39

		13-Mar-08		16:07:10		66.81		49.5		13-Mar-08		16:06:20		67.4		52		13-Mar-08		16:07:53		70.41		41.5		23-Apr-08		16:25:59		73.4		40.5

		13-Mar-08		18:07:10		66.2		49		13-Mar-08		18:06:20		66.81		49		13-Mar-08		18:07:53		71		44.5		23-Apr-08		18:25:59		73.4		40.5

		13-Mar-08		20:07:10		66.2		48.5		13-Mar-08		20:06:20		66.2		48		13-Mar-08		20:07:53		71		43.5		23-Apr-08		20:25:59		72.8		41.5

		13-Mar-08		22:07:10		66.2		49		13-Mar-08		22:06:20		67.4		46.5		13-Mar-08		22:07:53		72.21		41.5		23-Apr-08		22:25:59		71.6		41.5

		14-Mar-08		0:07:10		66.2		49.5		14-Mar-08		0:06:20		67.4		51		14-Mar-08		0:07:53		71.6		42		24-Apr-08		0:25:59		70.41		42

		14-Mar-08		2:07:10		65.6		50.5		14-Mar-08		2:06:20		67.4		52		14-Mar-08		2:07:53		71.6		43		24-Apr-08		2:25:59		69.2		42

		14-Mar-08		4:07:10		65.6		50.5		14-Mar-08		4:06:20		66.81		53		14-Mar-08		4:07:53		71.6		43.5		24-Apr-08		4:25:59		68.61		42.5

		14-Mar-08		6:07:10		66.2		50.5		14-Mar-08		6:06:20		67.4		53.5		14-Mar-08		6:07:53		71		40.5		24-Apr-08		6:25:59		69.2		42

		14-Mar-08		8:07:10		66.2		49.5		14-Mar-08		8:06:20		66.81		52		14-Mar-08		8:07:53		70.41		50		24-Apr-08		8:25:59		71		42

		14-Mar-08		10:07:10		66.2		51		14-Mar-08		10:06:20		67.4		52.5		14-Mar-08		10:07:53		71		51.5		24-Apr-08		10:25:59		72.8		43

		14-Mar-08		12:07:10		66.2		49.5		14-Mar-08		12:06:20		68		48		14-Mar-08		12:07:53		71		50.5		24-Apr-08		12:25:59		74.01		43

		14-Mar-08		14:07:10		66.81		48.5		14-Mar-08		14:06:20		68.61		47.5		14-Mar-08		14:07:53		71		52.5		24-Apr-08		14:25:59		74.01		40.5

		14-Mar-08		16:07:10		66.2		48		14-Mar-08		16:06:20		68		45.5		14-Mar-08		16:07:53		70.41		44		24-Apr-08		16:25:59		74.01		38.5

		14-Mar-08		18:07:10		65.6		48.5		14-Mar-08		18:06:20		66.81		46		14-Mar-08		18:07:53		70.41		43		24-Apr-08		18:25:59		72.8		36.5

		14-Mar-08		20:07:10		65.6		48.5		14-Mar-08		20:06:20		67.4		45		14-Mar-08		20:07:53		69.8		43		24-Apr-08		20:25:59		72.8		36.5

		14-Mar-08		22:07:10		65.6		48.5		14-Mar-08		22:06:20		67.4		45.5		14-Mar-08		22:07:53		71		41		24-Apr-08		22:25:59		71.6		35

		15-Mar-08		0:07:10		65.6		49		15-Mar-08		0:06:20		66.2		45		15-Mar-08		0:07:53		70.41		40.5		25-Apr-08		0:25:59		69.8		35

		15-Mar-08		2:07:10		65.6		49		15-Mar-08		2:06:20		65.6		44		15-Mar-08		2:07:53		69.8		39.5		25-Apr-08		2:25:59		68		35.5

		15-Mar-08		4:07:10		65.6		49		15-Mar-08		4:06:20		65.01		42.5		15-Mar-08		4:07:53		69.2		39		25-Apr-08		4:25:59		66.81		37

		15-Mar-08		6:07:10		66.2		48.5		15-Mar-08		6:06:20		65.6		44.5		15-Mar-08		6:07:53		69.2		42		25-Apr-08		6:25:59		68		36.5

		15-Mar-08		8:07:10		66.2		47.5		15-Mar-08		8:06:20		66.2		44		15-Mar-08		8:07:53		71		42		25-Apr-08		8:25:59		69.2		36.5

		15-Mar-08		10:07:10		66.81		48		15-Mar-08		10:06:20		67.4		46.5		15-Mar-08		10:07:53		71		47		25-Apr-08		10:25:59		72.8		38.5

		15-Mar-08		12:07:10		66.2		48		15-Mar-08		12:06:20		67.4		46.5		15-Mar-08		12:07:53		71		46.5		25-Apr-08		12:25:59		74.01		37

		15-Mar-08		14:07:10		66.2		48		15-Mar-08		14:06:20		67.4		41		15-Mar-08		14:07:53		71.6		44		25-Apr-08		14:25:59		74.6		36.5

		15-Mar-08		16:07:10		66.2		47.5		15-Mar-08		16:06:20		66.81		38		15-Mar-08		16:07:53		70.41		39.5		25-Apr-08		16:25:59		74.6		37.5

		15-Mar-08		18:07:10		65.6		48		15-Mar-08		18:06:20		66.81		40		15-Mar-08		18:07:53		69.8		38.5		25-Apr-08		18:25:59		74.01		35.5

		15-Mar-08		20:07:10		65.6		42.5		15-Mar-08		20:06:20		65.6		41		15-Mar-08		20:07:53		69.8		37.5		25-Apr-08		20:25:59		74.6		35.5

		15-Mar-08		22:07:10		65.6		49		15-Mar-08		22:06:20		65.01		41.5		15-Mar-08		22:07:53		69.2		37		25-Apr-08		22:25:59		74.01		35.5

		16-Mar-08		0:07:10		65.01		49		16-Mar-08		0:06:20		64.4		42		16-Mar-08		0:07:53		68.61		38		26-Apr-08		0:25:59		72.8		35

		16-Mar-08		2:07:10		65.01		50		16-Mar-08		2:06:20		63.8		43.5		16-Mar-08		2:07:53		68		38.5		26-Apr-08		2:25:59		71		36

		16-Mar-08		4:07:10		65.01		49		16-Mar-08		4:06:20		63.21		44		16-Mar-08		4:07:53		67.4		39		26-Apr-08		4:25:59		69.8		36.5

		16-Mar-08		6:07:10		65.01		49.5		16-Mar-08		6:06:20		63.21		43		16-Mar-08		6:07:53		68		39		26-Apr-08		6:25:59		70.41		37.5

		16-Mar-08		8:07:10		65.6		48		16-Mar-08		8:06:20		62		41.5		16-Mar-08		8:07:53		70.41		36.5		26-Apr-08		8:25:59		72.21		37

		16-Mar-08		10:07:10		65.6		49		16-Mar-08		10:06:20		64.4		44		16-Mar-08		10:07:53		71.6		38.5		26-Apr-08		10:25:59		74.01		38

		16-Mar-08		12:07:10		65.6		44		16-Mar-08		12:06:20		65.6		38		16-Mar-08		12:07:53		71		34		26-Apr-08		12:25:59		75.2		37.5

		16-Mar-08		14:07:10		65.6		38		16-Mar-08		14:06:20		66.2		34.5		16-Mar-08		14:07:53		70.41		33.5		26-Apr-08		14:25:59		73.4		34

		16-Mar-08		16:07:10		65.6		46		16-Mar-08		16:06:20		67.4		33		16-Mar-08		16:07:53		69.8		31.5		26-Apr-08		16:25:59		73.4		35.5

		16-Mar-08		18:07:10		65.6		41		16-Mar-08		18:06:20		66.2		36		16-Mar-08		18:07:53		69.2		34.5		26-Apr-08		18:25:59		73.4		37

		16-Mar-08		20:07:10		65.6		44		16-Mar-08		20:06:20		65.6		40		16-Mar-08		20:07:53		69.2		37		26-Apr-08		20:25:59		73.4		37

		16-Mar-08		22:07:10		65.6		48.5		16-Mar-08		22:06:20		65.6		37.5		16-Mar-08		22:07:53		68.61		36.5		26-Apr-08		22:25:59		72.8		36.5

		17-Mar-08		0:07:10		65.6		47.5		17-Mar-08		0:06:20		65.01		36		17-Mar-08		0:07:53		68		36		27-Apr-08		0:25:59		72.21		36.5

		17-Mar-08		2:07:10		65.6		47		17-Mar-08		2:06:20		64.4		34.5		17-Mar-08		2:07:53		67.4		35		27-Apr-08		2:25:59		71		36

		17-Mar-08		4:07:10		65.6		47.5		17-Mar-08		4:06:20		64.4		34		17-Mar-08		4:07:53		66.81		35		27-Apr-08		4:25:59		70.41		36.5

		17-Mar-08		6:07:10		65.01		38		17-Mar-08		6:06:20		64.4		34.5		17-Mar-08		6:07:53		66.2		35		27-Apr-08		6:25:59		69.8		36

		17-Mar-08		8:07:10		65.01		46.5		17-Mar-08		8:06:20		63.8		34.5		17-Mar-08		8:07:53		67.4		34.5		27-Apr-08		8:25:59		69.8		37.5

		17-Mar-08		10:07:10		65.6		38.5		17-Mar-08		10:06:20		65.01		34		17-Mar-08		10:07:53		68.61		33.5		27-Apr-08		10:25:59		71		40

		17-Mar-08		12:07:10		65.6		33.5		17-Mar-08		12:06:20		67.4		30		17-Mar-08		12:07:53		69.8		31.5		27-Apr-08		12:25:59		72.8		39.5

		17-Mar-08		14:07:10		65.6		42		17-Mar-08		14:06:20		66.81		23		17-Mar-08		14:07:53		69.8		30		27-Apr-08		14:25:59		74.01		38.5

		17-Mar-08		16:07:10		65.6		40		17-Mar-08		16:06:20		66.81		22		17-Mar-08		16:07:53		69.8		29		27-Apr-08		16:25:59		73.4		40.5

		17-Mar-08		18:07:10		65.6		36.5		17-Mar-08		18:06:20		66.2		31.5		17-Mar-08		18:07:53		69.8		31		27-Apr-08		18:25:59		73.4		40.5

		17-Mar-08		20:07:10		65.6		47.5		17-Mar-08		20:06:20		66.2		34.5		17-Mar-08		20:07:53		69.8		33		27-Apr-08		20:25:59		73.4		40.5

		17-Mar-08		22:07:10		65.6		47.5		17-Mar-08		22:06:20		66.81		35		17-Mar-08		22:07:53		70.41		34		27-Apr-08		22:25:59		73.4		38.5

		18-Mar-08		0:07:10		65.6		48		18-Mar-08		0:06:20		66.2		36		18-Mar-08		0:07:53		69.8		33.5		28-Apr-08		0:25:59		72.8		37.5

		18-Mar-08		2:07:10		65.6		39		18-Mar-08		2:06:20		65.01		37		18-Mar-08		2:07:53		68.61		34		28-Apr-08		2:25:59		72.21		39.5

		18-Mar-08		4:07:10		65.6		48		18-Mar-08		4:06:20		65.01		37.5		18-Mar-08		4:07:53		68		35		28-Apr-08		4:25:59		71.6		39.5

		18-Mar-08		6:07:10		66.2		47		18-Mar-08		6:06:20		65.01		37.5		18-Mar-08		6:07:53		69.2		34.5		28-Apr-08		6:25:59		70.41		39.5

		18-Mar-08		8:07:10		66.81		42		18-Mar-08		8:06:20		66.2		36.5		18-Mar-08		8:07:53		71.6		34.5		28-Apr-08		8:25:59		69.8		39.5

		18-Mar-08		10:07:10		66.2		38.5		18-Mar-08		10:06:20		67.4		35.5		18-Mar-08		10:07:53		71.6		39.5		28-Apr-08		10:25:59		71.6		41.5

		18-Mar-08		12:07:10		66.2		42		18-Mar-08		12:06:20		66.81		34.5		18-Mar-08		12:07:53		71.6		37		28-Apr-08		12:25:59		74.01		40

		18-Mar-08		14:07:10		66.81		46		18-Mar-08		14:06:20		66.2		39		18-Mar-08		14:07:53		71.6		34.5		28-Apr-08		14:25:59		74.01		39.5

		18-Mar-08		16:07:10		66.81		47.5		18-Mar-08		16:06:20		65.6		45		18-Mar-08		16:07:53		71.6		40		28-Apr-08		16:25:59		73.4		41.5

		18-Mar-08		18:07:10		66.81		46.5		18-Mar-08		18:06:20		65.6		45.5		18-Mar-08		18:07:53		70.41		37.5		28-Apr-08		18:25:59		73.4		41

		18-Mar-08		20:07:10		66.2		47		18-Mar-08		20:06:20		65.6		47		18-Mar-08		20:07:53		70.41		42.5		28-Apr-08		20:25:59		73.4		40.5

		18-Mar-08		22:07:10		66.2		47.5		18-Mar-08		22:06:20		65.01		47		18-Mar-08		22:07:53		71.6		40.5		28-Apr-08		22:25:59		73.4		39.5

		19-Mar-08		0:07:10		65.6		48		19-Mar-08		0:06:20		65.6		44.5		19-Mar-08		0:07:53		72.21		39		29-Apr-08		0:25:59		72.8		38.5

		19-Mar-08		2:07:10		65.6		48.5		19-Mar-08		2:06:20		64.4		49.5		19-Mar-08		2:07:53		71.6		39		29-Apr-08		2:25:59		71.6		38.5

		19-Mar-08		4:07:10		65.6		48		19-Mar-08		4:06:20		65.6		46.5		19-Mar-08		4:07:53		71		39		29-Apr-08		4:25:59		70.41		38.5

		19-Mar-08		6:07:10		66.2		47		19-Mar-08		6:06:20		65.6		45.5		19-Mar-08		6:07:53		71.6		39.5		29-Apr-08		6:25:59		70.41		38

		19-Mar-08		8:07:10		66.2		47		19-Mar-08		8:06:20		65.01		47		19-Mar-08		8:07:53		70.41		38		29-Apr-08		8:25:59		69.8		39.5

		19-Mar-08		10:07:10		66.2		47		19-Mar-08		10:06:20		66.2		47		19-Mar-08		10:07:53		70.41		37.5		29-Apr-08		10:25:59		72.8		40.5

		19-Mar-08		12:07:10		66.81		48.5		19-Mar-08		12:06:20		66.2		48		19-Mar-08		12:07:53		71.6		50.5		29-Apr-08		12:25:59		73.4		42.5

		19-Mar-08		14:07:10		66.81		49		19-Mar-08		14:06:20		66.2		51		19-Mar-08		14:07:53		71		41		29-Apr-08		14:25:59		73.4		43

		19-Mar-08		16:07:10		66.81		46.5		19-Mar-08		16:06:20		66.2		44		19-Mar-08		16:07:53		71.6		42.5		29-Apr-08		16:25:59		74.01		42.5

		19-Mar-08		18:07:10		66.2		47.5		19-Mar-08		18:06:20		66.2		45		19-Mar-08		18:07:53		70.41		40		29-Apr-08		18:25:59		74.01		41

		19-Mar-08		20:07:10		66.2		49		19-Mar-08		20:06:20		65.01		51.5		19-Mar-08		20:07:53		70.41		45		29-Apr-08		20:25:59		74.6		41

		19-Mar-08		22:07:10		65.6		48		19-Mar-08		22:06:20		65.6		52.5		19-Mar-08		22:07:53		71		44.5		29-Apr-08		22:25:59		74.01		40

		20-Mar-08		0:07:10		65.6		47		20-Mar-08		0:06:20		65.01		50.5		20-Mar-08		0:07:53		71		41.5		30-Apr-08		0:25:59		72.8		36.5

		20-Mar-08		2:07:10		65.6		48.5		20-Mar-08		2:06:20		65.6		47.5		20-Mar-08		2:07:53		71		40		30-Apr-08		2:25:59		71		36

		20-Mar-08		4:07:10		65.6		48.5		20-Mar-08		4:06:20		65.01		44.5		20-Mar-08		4:07:53		70.41		39		30-Apr-08		4:25:59		70.41		36

		20-Mar-08		6:07:10		65.6		41		20-Mar-08		6:06:20		64.4		43.5		20-Mar-08		6:07:53		70.41		38.5		30-Apr-08		6:25:59		70.41		36

		20-Mar-08		8:07:10		66.2		47		20-Mar-08		8:06:20		65.6		45		20-Mar-08		8:07:53		71.6		41		30-Apr-08		8:25:59		71		36

		20-Mar-08		10:07:10		66.2		45		20-Mar-08		10:06:20		65.6		49		20-Mar-08		10:07:53		71		45.5		30-Apr-08		10:25:59		72.8		36

		20-Mar-08		12:07:10		66.2		48		20-Mar-08		12:06:20		65.01		51.5		20-Mar-08		12:07:53		69.8		47		30-Apr-08		12:25:59		72.8		34.5

		20-Mar-08		14:07:10		66.81		47.5		20-Mar-08		14:06:20		65.6		53.5		20-Mar-08		14:07:53		71		51.5		30-Apr-08		14:25:59		73.4		33.5

		20-Mar-08		16:07:10		66.2		50		20-Mar-08		16:06:20		65.6		55.5		20-Mar-08		16:07:53		69.8		50.5		30-Apr-08		16:25:59		73.4		34

		20-Mar-08		18:07:10		66.2		48.5		20-Mar-08		18:06:20		65.6		56		20-Mar-08		18:07:53		69.8		48.5		30-Apr-08		18:25:59		72.8		32

		20-Mar-08		20:07:10		65.6		48.5		20-Mar-08		20:06:20		66.2		46		20-Mar-08		20:07:53		70.41		44		30-Apr-08		20:25:59		73.4		32

		20-Mar-08		22:07:10		65.6		48.5		20-Mar-08		22:06:20		65.6		47.5		20-Mar-08		22:07:53		71		41.5		30-Apr-08		22:25:59		72.21		31

		21-Mar-08		0:07:10		65.6		43		21-Mar-08		0:06:20		65.01		44		21-Mar-08		0:07:53		70.41		40		1-May-08		0:25:59		70.41		31.5

		21-Mar-08		2:07:10		65.6		49		21-Mar-08		2:06:20		65.01		41		21-Mar-08		2:07:53		69.8		38		1-May-08		2:25:59		69.2		31

		21-Mar-08		4:07:10		65.01		39.5		21-Mar-08		4:06:20		64.4		40		21-Mar-08		4:07:53		68.61		37.5		1-May-08		4:25:59		68		31

		21-Mar-08		6:07:10		65.6		48.5		21-Mar-08		6:06:20		64.4		39		21-Mar-08		6:07:53		69.2		37		1-May-08		6:25:59		70.41		30.5

		21-Mar-08		8:07:10		65.6		37.5		21-Mar-08		8:06:20		65.01		37.5		21-Mar-08		8:07:53		71		33		1-May-08		8:25:59		69.2		30

		21-Mar-08		10:07:10		66.2		47		21-Mar-08		10:06:20		66.2		39		21-Mar-08		10:07:53		71		40		1-May-08		10:25:59		71		30

		21-Mar-08		12:07:10		66.2		42.5		21-Mar-08		12:06:20		66.2		32		21-Mar-08		12:07:53		71		37		1-May-08		12:25:59		72.8		29

		21-Mar-08		14:07:10		66.2		46		21-Mar-08		14:06:20		66.81		30.5		21-Mar-08		14:07:53		70.41		31.5		1-May-08		14:25:59		73.4		28

		21-Mar-08		16:07:10		66.2		34.5		21-Mar-08		16:06:20		66.81		33		21-Mar-08		16:07:53		70.41		35.5		1-May-08		16:25:59		72.8		28

		21-Mar-08		18:07:10		66.2		46.5		21-Mar-08		18:06:20		66.2		36		21-Mar-08		18:07:53		70.41		33.5		1-May-08		18:25:59		73.4		29

		21-Mar-08		20:07:10		65.6		40		21-Mar-08		20:06:20		65.6		37		21-Mar-08		20:07:53		70.41		36.5		1-May-08		20:25:59		73.4		29.5

		21-Mar-08		22:07:10		65.6		39		21-Mar-08		22:06:20		65.01		37.5		21-Mar-08		22:07:53		70.41		35		1-May-08		22:25:59		72.8		29.5

		22-Mar-08		0:07:10		65.6		37		22-Mar-08		0:06:20		65.6		35		22-Mar-08		0:07:53		69.8		33.5		2-May-08		0:25:59		71.6		29.5

		22-Mar-08		2:07:10		65.01		36.5		22-Mar-08		2:06:20		65.6		35.5		22-Mar-08		2:07:53		69.2		33.5		2-May-08		2:25:59		70.41		30

		22-Mar-08		4:07:10		65.01		47		22-Mar-08		4:06:20		65.6		35		22-Mar-08		4:07:53		68.61		34		2-May-08		4:25:59		69.2		30

		22-Mar-08		6:07:10		65.6		46		22-Mar-08		6:06:20		65.6		34.5		22-Mar-08		6:07:53		69.2		33.5		2-May-08		6:25:59		71		30.5

		22-Mar-08		8:07:10		65.6		36		22-Mar-08		8:06:20		65.6		34.5		22-Mar-08		8:07:53		71		32.5		2-May-08		8:25:59		69.8		31.5

		22-Mar-08		10:07:10		66.2		41.5		22-Mar-08		10:06:20		65.6		37		22-Mar-08		10:07:53		70.41		34		2-May-08		10:25:59		72.21		32

		22-Mar-08		12:07:10		66.2		42		22-Mar-08		12:06:20		66.81		33.5		22-Mar-08		12:07:53		70.41		32.5		2-May-08		12:25:59		72.8		30.5

		22-Mar-08		14:07:10		66.81		45		22-Mar-08		14:06:20		66.2		33		22-Mar-08		14:07:53		71		33		2-May-08		14:25:59		73.4		28

		22-Mar-08		16:07:10		66.2		41.5		22-Mar-08		16:06:20		65.6		40		22-Mar-08		16:07:53		71		33		2-May-08		16:25:59		74.01		30

		22-Mar-08		18:07:10		66.2		47		22-Mar-08		18:06:20		65.01		40		22-Mar-08		18:07:53		70.41		34.5		2-May-08		18:25:59		72.8		31

		22-Mar-08		20:07:10		65.6		47		22-Mar-08		20:06:20		66.2		43		22-Mar-08		20:07:53		69.8		39.5		2-May-08		20:25:59		74.01		31.5

		22-Mar-08		22:07:10		65.6		47.5		22-Mar-08		22:06:20		65.01		42.5		22-Mar-08		22:07:53		70.41		38.5		2-May-08		22:25:59		74.01		30.5

		23-Mar-08		0:07:10		65.6		47.5		23-Mar-08		0:06:20		65.6		42		23-Mar-08		0:07:53		71		37		3-May-08		0:25:59		73.4		29.5

		23-Mar-08		2:07:10		65.6		40.5		23-Mar-08		2:06:20		65.01		40		23-Mar-08		2:07:53		70.41		36.5		3-May-08		2:25:59		72.21		30.5

		23-Mar-08		4:07:10		65.6		49		23-Mar-08		4:06:20		65.01		38.5		23-Mar-08		4:07:53		69.2		35		3-May-08		4:25:59		70.41		31.5

		23-Mar-08		6:07:10		65.01		38.5		23-Mar-08		6:06:20		65.6		38		23-Mar-08		6:07:53		69.8		35.5		3-May-08		6:25:59		70.41		32

		23-Mar-08		8:07:10		65.6		46		23-Mar-08		8:06:20		65.01		37.5		23-Mar-08		8:07:53		71		34.5		3-May-08		8:25:59		70.41		33.5

		23-Mar-08		10:07:10		65.6		41.5		23-Mar-08		10:06:20		66.2		40.5		23-Mar-08		10:07:53		70.41		34.5		3-May-08		10:25:59		72.8		34.5

		23-Mar-08		12:07:10		66.2		47		23-Mar-08		12:06:20		66.2		42.5		23-Mar-08		12:07:53		69.8		34.5		3-May-08		12:25:59		73.4		34

		23-Mar-08		14:07:10		66.2		42.5		23-Mar-08		14:06:20		65.6		43		23-Mar-08		14:07:53		70.41		43.5		3-May-08		14:25:59		73.4		35.5

		23-Mar-08		16:07:10		66.2		36		23-Mar-08		16:06:20		65.6		36		23-Mar-08		16:07:53		71		38.5		3-May-08		16:25:59		74.01		35

		23-Mar-08		18:07:10		66.2		43.5		23-Mar-08		18:06:20		66.2		42		23-Mar-08		18:07:53		70.41		40		3-May-08		18:25:59		73.4		36.5

		23-Mar-08		20:07:10		65.6		44		23-Mar-08		20:06:20		65.6		45.5		23-Mar-08		20:07:53		69.8		41.5		3-May-08		20:25:59		74.01		36.5

		23-Mar-08		22:07:10		65.6		48		23-Mar-08		22:06:20		65.01		46.5		23-Mar-08		22:07:53		71		39.5		3-May-08		22:25:59		74.01		35

		24-Mar-08		0:07:10		65.6		47.5		24-Mar-08		0:06:20		65.01		44.5		24-Mar-08		0:07:53		71		37.5		4-May-08		0:25:59		72.21		34.5

		24-Mar-08		2:07:10		65.6		43		24-Mar-08		2:06:20		65.6		41		24-Mar-08		2:07:53		69.8		36		4-May-08		2:25:59		70.41		35

		24-Mar-08		4:07:10		65.6		47.5		24-Mar-08		4:06:20		65.01		39.5		24-Mar-08		4:07:53		68.61		36		4-May-08		4:25:59		69.2		34.5

		24-Mar-08		6:07:10		65.01		47.5		24-Mar-08		6:06:20		64.4		38.5		24-Mar-08		6:07:53		68		35.5		4-May-08		6:25:59		69.2		34.5

		24-Mar-08		8:07:10		65.01		36		24-Mar-08		8:06:20		63.8		36.5		24-Mar-08		8:07:53		66.81		35		4-May-08		8:25:59		69.8		35

		24-Mar-08		10:07:10		65.6		47.5		24-Mar-08		10:06:20		65.6		39		24-Mar-08		10:07:53		69.8		35		4-May-08		10:25:59		71.6		37

		24-Mar-08		12:07:10		65.6		39.5		24-Mar-08		12:06:20		66.2		38		24-Mar-08		12:07:53		70.41		36.5		4-May-08		12:25:59		73.4		37

		24-Mar-08		14:07:10		66.2		43.5		24-Mar-08		14:06:20		65.6		39		24-Mar-08		14:07:53		69.8		39		4-May-08		14:25:59		74.6		38

		24-Mar-08		16:07:10		66.2		47.5		24-Mar-08		16:06:20		65.6		45.5		24-Mar-08		16:07:53		70.41		42		4-May-08		16:25:59		74.01		38

		24-Mar-08		18:07:10		66.2		45.5		24-Mar-08		18:06:20		66.2		50		24-Mar-08		18:07:53		69.8		45		4-May-08		18:25:59		73.4		40.5

		24-Mar-08		20:07:10		65.6		47.5		24-Mar-08		20:06:20		66.2		45.5		24-Mar-08		20:07:53		71		42.5		4-May-08		20:25:59		73.4		40

		24-Mar-08		22:07:10		65.6		43		24-Mar-08		22:06:20		65.6		45		24-Mar-08		22:07:53		71.6		39.5		4-May-08		22:25:59		72.8		39

		25-Mar-08		0:07:10		65.6		42.5		25-Mar-08		0:06:20		65.01		46		25-Mar-08		0:07:53		71		38.5		5-May-08		0:25:59		71.6		38.5

		25-Mar-08		2:07:10		65.6		41		25-Mar-08		2:06:20		65.6		42		25-Mar-08		2:07:53		69.8		37.5		5-May-08		2:25:59		71		38

		25-Mar-08		4:07:10		65.6		46		25-Mar-08		4:06:20		65.6		42.5		25-Mar-08		4:07:53		69.2		37		5-May-08		4:25:59		69.8		37.5

		25-Mar-08		6:07:10		65.6		39.5		25-Mar-08		6:06:20		65.6		41		25-Mar-08		6:07:53		69.8		37.5		5-May-08		6:25:59		68.61		37.5

		25-Mar-08		8:07:10		65.6		40		25-Mar-08		8:06:20		65.6		41.5		25-Mar-08		8:07:53		71.6		37		5-May-08		8:25:59		68.61		38

		25-Mar-08		10:07:10		66.2		44.5		25-Mar-08		10:06:20		66.2		49		25-Mar-08		10:07:53		70.41		44.5		5-May-08		10:25:59		69.8		40.5

		25-Mar-08		12:07:10		66.81		46.5		25-Mar-08		12:06:20		66.2		53.5		25-Mar-08		12:07:53		71.6		38.5		5-May-08		12:25:59		71.6		41.5

		25-Mar-08		14:07:10		66.81		47.5		25-Mar-08		14:06:20		66.2		59.5		25-Mar-08		14:07:53		71		46		5-May-08		14:25:59		72.8		41.5

		25-Mar-08		16:07:10		66.81		48.5		25-Mar-08		16:06:20		65.6		53.5		25-Mar-08		16:07:53		71		49		5-May-08		16:25:59		73.4		40.5

		25-Mar-08		18:07:10		66.2		47		25-Mar-08		18:06:20		65.6		57.5		25-Mar-08		18:07:53		70.41		50.5		5-May-08		18:25:59		73.4		39.5

		25-Mar-08		20:07:10		66.2		45.5		25-Mar-08		20:06:20		65.6		55		25-Mar-08		20:07:53		70.41		51		5-May-08		20:25:59		72.8		39

		25-Mar-08		22:07:10		65.6		45		25-Mar-08		22:06:20		65.6		51		25-Mar-08		22:07:53		70.41		46		5-May-08		22:25:59		72.21		38

		26-Mar-08		0:07:10		65.6		44		26-Mar-08		0:06:20		65.6		49		26-Mar-08		0:07:53		69.8		42.5		6-May-08		0:25:59		71.6		37.5

		26-Mar-08		2:07:10		65.6		43		26-Mar-08		2:06:20		65.6		47.5		26-Mar-08		2:07:53		69.8		40.5		6-May-08		2:25:59		70.41		38

		26-Mar-08		4:07:10		65.6		42		26-Mar-08		4:06:20		65.6		45.5		26-Mar-08		4:07:53		69.8		39		6-May-08		4:25:59		69.2		37.5

		26-Mar-08		6:07:10		65.6		43		26-Mar-08		6:06:20		64.4		49.5		26-Mar-08		6:07:53		70.41		40.5		6-May-08		6:25:59		69.8		37.5

		26-Mar-08		8:07:10		66.2		44		26-Mar-08		8:06:20		65.6		50.5		26-Mar-08		8:07:53		71.6		41.5		6-May-08		8:25:59		69.8		40

		26-Mar-08		10:07:10		66.2		45		26-Mar-08		10:06:20		65.01		53		26-Mar-08		10:07:53		71		45.5		6-May-08		10:25:59		72.21		41.5

		26-Mar-08		12:07:10		66.2		46		26-Mar-08		12:06:20		65.6		53.5		26-Mar-08		12:07:53		71		49		6-May-08		12:25:59		73.4		43.5

		26-Mar-08		14:07:10		66.81		45.5		26-Mar-08		14:06:20		65.6		53.5		26-Mar-08		14:07:53		71		48.5		6-May-08		14:25:59		73.4		43

		26-Mar-08		16:07:10		66.2		44		26-Mar-08		16:06:20		66.2		50.5		26-Mar-08		16:07:53		70.41		39.5		6-May-08		16:25:59		74.01		43

		26-Mar-08		18:07:10		65.6		43		26-Mar-08		18:06:20		66.2		45		26-Mar-08		18:07:53		70.41		48		6-May-08		18:25:59		74.01		40

		26-Mar-08		20:07:10		65.6		41		26-Mar-08		20:06:20		65.6		41.5		26-Mar-08		20:07:53		70.41		43.5		6-May-08		20:25:59		73.4		40

		26-Mar-08		22:07:10		65.6		40.5		26-Mar-08		22:06:20		64.4		44		26-Mar-08		22:07:53		72.21		37.5		6-May-08		22:25:59		72.21		39.5

		27-Mar-08		0:07:10		65.6		41		27-Mar-08		0:06:20		65.6		43		27-Mar-08		0:07:53		71.6		36.5		7-May-08		0:25:59		71.6		40

		27-Mar-08		2:07:10		65.01		39.5		27-Mar-08		2:06:20		64.4		42.5		27-Mar-08		2:07:53		70.41		36		7-May-08		2:25:59		71		40

		27-Mar-08		4:07:10		65.01		38		27-Mar-08		4:06:20		63.8		41.5		27-Mar-08		4:07:53		69.8		35		7-May-08		4:25:59		69.8		40

		27-Mar-08		6:07:10		65.01		37		27-Mar-08		6:06:20		63.8		40.5		27-Mar-08		6:07:53		70.41		35		7-May-08		6:25:59		71		40.5

		27-Mar-08		8:07:10		65.6		37		27-Mar-08		8:06:20		63.8		39		27-Mar-08		8:07:53		71.6		34.5		7-May-08		8:25:59		71.6		41.5

		27-Mar-08		10:07:10		65.6		40		27-Mar-08		10:06:20		66.2		41		27-Mar-08		10:07:53		71.6		35		7-May-08		10:25:59		73.4		41

		27-Mar-08		12:07:10		65.6		39		27-Mar-08		12:06:20		69.2		36.5		27-Mar-08		12:07:53		71		42		7-May-08		12:25:59		73.4		43

		27-Mar-08		14:07:10		66.2		40		27-Mar-08		14:06:20		69.2		37		27-Mar-08		14:07:53		71		35.5		7-May-08		14:25:59		73.4		45.5

		27-Mar-08		16:07:10		65.6		43		27-Mar-08		16:06:20		68.61		41.5		27-Mar-08		16:07:53		70.41		37		7-May-08		16:25:59		73.4		44.5

		27-Mar-08		18:07:10		65.6		41		27-Mar-08		18:06:20		68.61		38		27-Mar-08		18:07:53		70.41		42		7-May-08		18:25:59		73.4		43

		27-Mar-08		20:07:10		65.6		40		27-Mar-08		20:06:20		68		38.5		27-Mar-08		20:07:53		72.8		36		7-May-08		20:25:59		74.01		42

		27-Mar-08		22:07:10		65.6		37.5		27-Mar-08		22:06:20		66.81		36		27-Mar-08		22:07:53		74.6		32		7-May-08		22:25:59		74.01		37.5

		28-Mar-08		0:07:10		65.01		36.5		28-Mar-08		0:06:20		65.6		36.5		28-Mar-08		0:07:53		71.6		32.5		8-May-08		0:25:59		73.4		37

		28-Mar-08		2:07:10		65.01		35		28-Mar-08		2:06:20		64.4		35.5		28-Mar-08		2:07:53		69.8		32		8-May-08		2:25:59		71.6		37

		28-Mar-08		4:07:10		65.01		33.5		28-Mar-08		4:06:20		63.8		35		28-Mar-08		4:07:53		68.61		31.5		8-May-08		4:25:59		70.41		37.5

		28-Mar-08		6:07:10		65.01		33		28-Mar-08		6:06:20		63.21		35		28-Mar-08		6:07:53		69.2		32		8-May-08		6:25:59		73.4		35.5

		28-Mar-08		8:07:10		65.6		32		28-Mar-08		8:06:20		64.4		34		28-Mar-08		8:07:53		70.41		32		8-May-08		8:25:59		72.8		35.5

		28-Mar-08		10:07:10		65.6		30.5		28-Mar-08		10:06:20		66.2		31		28-Mar-08		10:07:53		71		33		8-May-08		10:25:59		72.8		37.5

		28-Mar-08		12:07:10		65.6		28		28-Mar-08		12:06:20		68.61		27		28-Mar-08		12:07:53		71		29.5		8-May-08		12:25:59		72.8		38.5

		28-Mar-08		14:07:10		66.2		28		28-Mar-08		14:06:20		69.2		25.5		28-Mar-08		14:07:53		70.41		32.5		8-May-08		14:25:59		73.4		39.5

		28-Mar-08		16:07:10		66.2		23.5		28-Mar-08		16:06:20		69.2		22		28-Mar-08		16:07:53		70.41		28.5		8-May-08		16:25:59		74.01		39.5

		28-Mar-08		18:07:10		65.6		24.5		28-Mar-08		18:06:20		69.2		21		28-Mar-08		18:07:53		71		26.5		8-May-08		18:25:59		73.4		39

		28-Mar-08		20:07:10		65.6		26		28-Mar-08		20:06:20		68.61		23.5		28-Mar-08		20:07:53		71.6		26.5		8-May-08		20:25:59		74.01		39.5

		28-Mar-08		22:07:10		65.01		35		28-Mar-08		22:06:20		67.4		34		28-Mar-08		22:07:53		74.6		28.5		8-May-08		22:25:59		74.01		37.5

		29-Mar-08		0:07:10		65.01		35		29-Mar-08		0:06:20		65.6		35.5		29-Mar-08		0:07:53		72.8		29.5		9-May-08		0:25:59		72.8		37

		29-Mar-08		2:07:10		65.01		36		29-Mar-08		2:06:20		65.01		37.5		29-Mar-08		2:07:53		71		30.5		9-May-08		2:25:59		71		36.5

		29-Mar-08		4:07:10		65.01		35.5		29-Mar-08		4:06:20		64.4		37.5		29-Mar-08		4:07:53		69.8		31		9-May-08		4:25:59		69.2		36.5

		29-Mar-08		6:07:10		65.6		34.5		29-Mar-08		6:06:20		64.4		37		29-Mar-08		6:07:53		70.41		33		9-May-08		6:25:59		72.8		35.5

		29-Mar-08		8:07:10		65.01		36.5		29-Mar-08		8:06:20		65.6		37.5		29-Mar-08		8:07:53		70.41		35		9-May-08		8:25:59		73.4		36.5

		29-Mar-08		10:07:10		65.6		32		29-Mar-08		10:06:20		68		32.5		29-Mar-08		10:07:53		70.41		35.5		9-May-08		10:25:59		73.4		38.5

		29-Mar-08		12:07:10		64.4		39		29-Mar-08		12:06:20		69.2		32		29-Mar-08		12:07:53		71		36.5		9-May-08		12:25:59		72.21		41

		29-Mar-08		14:07:10		66.81		38.5		29-Mar-08		14:06:20		68		38		29-Mar-08		14:07:53		71		44		9-May-08		14:25:59		72.21		41.5

		29-Mar-08		16:07:10		66.81		43		29-Mar-08		16:06:20		65.6		51		29-Mar-08		16:07:53		71		43		9-May-08		16:25:59		73.4		39.5

		29-Mar-08		18:07:10		66.81		44.5		29-Mar-08		18:06:20		64.4		55.5		29-Mar-08		18:07:53		72.21		42.5		9-May-08		18:25:59		72.8		39

		29-Mar-08		20:07:10		66.81		44.5		29-Mar-08		20:06:20		65.01		55		29-Mar-08		20:07:53		71		45.5		9-May-08		20:25:59		73.4		38.5

		29-Mar-08		22:07:10		66.81		45		29-Mar-08		22:06:20		64.4		57		29-Mar-08		22:07:53		70.41		44		9-May-08		22:25:59		72.8		37.5

		30-Mar-08		0:07:10		66.81		45		30-Mar-08		0:06:20		65.01		56		30-Mar-08		0:07:53		70.41		42.5		10-May-08		0:25:59		72.21		36

		30-Mar-08		2:07:10		66.81		44.5		30-Mar-08		2:06:20		65.01		54.5		30-Mar-08		2:07:53		69.8		43		10-May-08		2:25:59		72.21		35

		30-Mar-08		4:07:10		66.81		43.5		30-Mar-08		4:06:20		64.4		53.5		30-Mar-08		4:07:53		69.8		42		10-May-08		4:25:59		72.21		35

		30-Mar-08		6:07:10		66.81		41.5		30-Mar-08		6:06:20		65.01		50		30-Mar-08		6:07:53		69.8		41.5		10-May-08		6:25:59		72.21		34

		30-Mar-08		8:07:10		67.4		40.5		30-Mar-08		8:06:20		65.01		47.5		30-Mar-08		8:07:53		69.8		40		10-May-08		8:25:59		71		36

		30-Mar-08		10:07:10		67.4		39.5		30-Mar-08		10:06:20		64.4		47.5		30-Mar-08		10:07:53		69.8		39.5		10-May-08		10:25:59		73.4		36

		30-Mar-08		12:07:10		68		40.5		30-Mar-08		12:06:20		64.4		48		30-Mar-08		12:07:53		69.8		41		10-May-08		12:25:59		74.6		34.5

		30-Mar-08		14:07:10		67.4		42		30-Mar-08		14:06:20		65.01		51		30-Mar-08		14:07:53		70.41		37.5		10-May-08		14:25:59		75.2		33.5

		30-Mar-08		16:07:10		67.4		40.5		30-Mar-08		16:06:20		65.01		46.5		30-Mar-08		16:07:53		70.41		39		10-May-08		16:25:59		75.2		35.5

		30-Mar-08		18:07:10		67.4		39.5		30-Mar-08		18:06:20		65.01		45.5		30-Mar-08		18:07:53		69.8		43		10-May-08		18:25:59		75.2		35.5

		30-Mar-08		20:07:10		68		37		30-Mar-08		20:06:20		64.4		43		30-Mar-08		20:07:53		70.41		39.5		10-May-08		20:25:59		74.6		36

		30-Mar-08		22:07:10		68		33		30-Mar-08		22:06:20		64.4		37		30-Mar-08		22:07:53		71		35.5		10-May-08		22:25:59		74.6		34.5

		31-Mar-08		0:07:10		68		32		31-Mar-08		0:06:20		65.01		35		31-Mar-08		0:07:53		69.8		33		11-May-08		0:25:59		74.01		34

		31-Mar-08		2:07:10		67.4		32		31-Mar-08		2:06:20		64.4		35.5		31-Mar-08		2:07:53		69.8		32.5		11-May-08		2:25:59		72.21		34

		31-Mar-08		4:07:10		67.4		32.5		31-Mar-08		4:06:20		63.8		37		31-Mar-08		4:07:53		68.61		32.5		11-May-08		4:25:59		71.6		34

		31-Mar-08		6:07:10		68		32.5		31-Mar-08		6:06:20		63.21		38.5		31-Mar-08		6:07:53		68		33		11-May-08		6:25:59		72.21		34

		31-Mar-08		8:07:10		67.4		31		31-Mar-08		8:06:20		63.8		36		31-Mar-08		8:07:53		68		32.5		11-May-08		8:25:59		72.21		34.5

		31-Mar-08		10:07:10		67.4		28.5		31-Mar-08		10:06:20		64.4		32		31-Mar-08		10:07:53		69.2		31		11-May-08		10:25:59		72.8		35

		31-Mar-08		12:07:10		67.4		25.5		31-Mar-08		12:06:20		64.4		29.5		31-Mar-08		12:07:53		69.8		29.5		11-May-08		12:25:59		74.01		35

		31-Mar-08		14:07:10		68		23.5		31-Mar-08		14:06:20		65.01		25.5		31-Mar-08		14:07:53		69.8		27.5		11-May-08		14:25:59		75.81		35.5

		31-Mar-08		16:07:10		67.4		24		31-Mar-08		16:06:20		65.01		26		31-Mar-08		16:07:53		69.2		28		11-May-08		16:25:59		77		34.5

		31-Mar-08		18:07:10		67.4		26.5		31-Mar-08		18:06:20		65.01		29.5		31-Mar-08		18:07:53		69.8		28.5		11-May-08		18:25:59		78.2		35

		31-Mar-08		20:07:10		68		26.5		31-Mar-08		20:06:20		64.4		30		31-Mar-08		20:07:53		71		28.5		11-May-08		20:25:59		77.61		36

		31-Mar-08		22:07:10		67.4		27		31-Mar-08		22:06:20		64.4		30.5		31-Mar-08		22:07:53		70.41		27.5		11-May-08		22:25:59		75.81		37

		1-Apr-08		0:07:10		67.4		27.5		1-Apr-08		0:06:20		64.4		31.5		1-Apr-08		0:07:53		69.2		27.5		12-May-08		0:25:59		74.01		37.5

		1-Apr-08		2:07:10		67.4		28		1-Apr-08		2:06:20		63.8		32.5		1-Apr-08		2:07:53		68.61		28		12-May-08		2:25:59		72.8		38

		1-Apr-08		4:07:10		67.4		28		1-Apr-08		4:06:20		62.6		32.5		1-Apr-08		4:07:53		67.4		28.5		12-May-08		4:25:59		72.21		38

		1-Apr-08		6:07:10		67.4		28.5		1-Apr-08		6:06:20		62		34		1-Apr-08		6:07:53		66.81		29.5		12-May-08		6:25:59		72.21		37.5

		1-Apr-08		8:07:10		68		28.5		1-Apr-08		8:06:20		63.21		34		1-Apr-08		8:07:53		69.8		29.5		12-May-08		8:25:59		72.21		38.5

		1-Apr-08		10:07:10		67.4		30.5		1-Apr-08		10:06:20		65.01		34.5		1-Apr-08		10:07:53		71		31.5		12-May-08		10:25:59		71.6		40

		1-Apr-08		12:07:10		66.81		27		1-Apr-08		12:06:20		65.6		30		1-Apr-08		12:07:53		71		34		12-May-08		12:25:59		72.8		41

		1-Apr-08		14:07:10		66.81		30		1-Apr-08		14:06:20		66.2		31		1-Apr-08		14:07:53		71		35		12-May-08		14:25:59		74.01		36

		1-Apr-08		16:07:10		66.81		31		1-Apr-08		16:06:20		65.6		34		1-Apr-08		16:07:53		71		36.5		12-May-08		16:25:59		74.6		32

		1-Apr-08		18:07:10		66.81		29.5		1-Apr-08		18:06:20		65.01		32.5		1-Apr-08		18:07:53		71		33.5		12-May-08		18:25:59		76.4		31

		1-Apr-08		20:07:10		67.4		30.5		1-Apr-08		20:06:20		65.01		32.5		1-Apr-08		20:07:53		70.41		32		12-May-08		20:25:59		75.81		31.5

		1-Apr-08		22:07:10		67.4		29		1-Apr-08		22:06:20		64.4		32		1-Apr-08		22:07:53		70.41		32		12-May-08		22:25:59		74.01		31

		2-Apr-08		0:07:10		66.81		33		2-Apr-08		0:06:20		65.01		37		2-Apr-08		0:07:53		70.41		31		13-May-08		0:25:59		72.8		31

		2-Apr-08		2:07:10		66.81		34		2-Apr-08		2:06:20		64.4		38.5		2-Apr-08		2:07:53		70.41		31		13-May-08		2:25:59		71.6		31

		2-Apr-08		4:07:10		66.81		33		2-Apr-08		4:06:20		64.4		38		2-Apr-08		4:07:53		70.41		32		13-May-08		4:25:59		71.6		31

		2-Apr-08		6:07:10		66.81		31.5		2-Apr-08		6:06:20		65.01		35		2-Apr-08		6:07:53		71		32		13-May-08		6:25:59		71.6		30

		2-Apr-08		8:07:10		66.81		33.5		2-Apr-08		8:06:20		65.01		37.5		2-Apr-08		8:07:53		71.6		33.5		13-May-08		8:25:59		71.6		30

		2-Apr-08		10:07:10		66.81		33.5		2-Apr-08		10:06:20		66.2		35.5		2-Apr-08		10:07:53		70.41		35		13-May-08		10:25:59		74.01		29.5

		2-Apr-08		12:07:10		66.81		33		2-Apr-08		12:06:20		66.81		33		2-Apr-08		12:07:53		71		36		13-May-08		12:25:59		74.01		29.5

		2-Apr-08		14:07:10		66.81		39		2-Apr-08		14:06:20		67.4		42.5		2-Apr-08		14:07:53		71.6		34.5		13-May-08		14:25:59		75.2		29.5

		2-Apr-08		16:07:10		67.4		34		2-Apr-08		16:06:20		67.4		31.5		2-Apr-08		16:07:53		71.6		36.5		13-May-08		16:25:59		75.2		30

		2-Apr-08		18:07:10		66.81		35		2-Apr-08		18:06:20		66.2		36		2-Apr-08		18:07:53		71		32.5		13-May-08		18:25:59		75.2		30

		2-Apr-08		20:07:10		67.4		36.5		2-Apr-08		20:06:20		66.81		37		2-Apr-08		20:07:53		71		37		13-May-08		20:25:59		74.6		30.5

		2-Apr-08		22:07:10		66.81		37.5		2-Apr-08		22:06:20		65.6		41.5		2-Apr-08		22:07:53		75.2		33		13-May-08		22:25:59		74.01		29.5

		3-Apr-08		0:07:10		66.81		37.5		3-Apr-08		0:06:20		66.2		42		3-Apr-08		0:07:53		71.6		34		14-May-08		0:25:59		73.4		29.5

		3-Apr-08		2:07:10		66.81		36.5		3-Apr-08		2:06:20		65.6		40.5		3-Apr-08		2:07:53		70.41		34.5		14-May-08		2:25:59		72.21		30

		3-Apr-08		4:07:10		67.4		34.5		3-Apr-08		4:06:20		64.4		38.5		3-Apr-08		4:07:53		69.2		33.5		14-May-08		4:25:59		71.6		30.5

		3-Apr-08		6:07:10		67.4		35.5		3-Apr-08		6:06:20		64.4		38		3-Apr-08		6:07:53		69.2		33		14-May-08		6:25:59		72.21		31

		3-Apr-08		8:07:10		67.4		35.5		3-Apr-08		8:06:20		65.01		38.5		3-Apr-08		8:07:53		71		31		14-May-08		8:25:59		71.6		32.5

		3-Apr-08		10:07:10		65.01		39		3-Apr-08		10:06:20		66.2		41		3-Apr-08		10:07:53		71.6		34.5		14-May-08		10:25:59		74.6		33

		3-Apr-08		12:07:10		66.81		38		3-Apr-08		12:06:20		66.81		39		3-Apr-08		12:07:53		71		34.5		14-May-08		12:25:59		74.01		32

		3-Apr-08		14:07:10		66.81		40		3-Apr-08		14:06:20		67.4		41.5		3-Apr-08		14:07:53		71		38		14-May-08		14:25:59		74.01		30.5

		3-Apr-08		16:07:10		66.81		38		3-Apr-08		16:06:20		66.2		40		3-Apr-08		16:07:53		71.6		42.5		14-May-08		16:25:59		74.6		29

		3-Apr-08		18:07:10		66.81		35.5		3-Apr-08		18:06:20		66.81		36		3-Apr-08		18:07:53		71		32		14-May-08		18:25:59		74.01		29

		3-Apr-08		20:07:10		67.4		35.5		3-Apr-08		20:06:20		66.2		37.5		3-Apr-08		20:07:53		71		32.5		14-May-08		20:25:59		74.6		33

		3-Apr-08		22:07:10		67.4		34.5		3-Apr-08		22:06:20		65.6		37		3-Apr-08		22:07:53		72.21		34		14-May-08		22:25:59		75.2		33

		4-Apr-08		0:07:10		67.4		34.5		4-Apr-08		0:06:20		66.2		37.5		4-Apr-08		0:07:53		72.21		33.5		15-May-08		0:25:59		74.6		33.5

		4-Apr-08		2:07:10		66.81		34		4-Apr-08		2:06:20		65.6		36.5		4-Apr-08		2:07:53		70.41		32.5		15-May-08		2:25:59		74.01		34

		4-Apr-08		4:07:10		66.81		35		4-Apr-08		4:06:20		65.01		38		4-Apr-08		4:07:53		69.8		32		15-May-08		4:25:59		73.4		35

		4-Apr-08		6:07:10		66.81		37		4-Apr-08		6:06:20		65.6		40.5		4-Apr-08		6:07:53		69.8		34		15-May-08		6:25:59		73.4		36.5

		4-Apr-08		8:07:10		67.4		37.5		4-Apr-08		8:06:20		66.81		42		4-Apr-08		8:07:53		72.21		33.5		15-May-08		8:25:59		73.4		39

		4-Apr-08		10:07:10		68		38.5		4-Apr-08		10:06:20		66.81		42		4-Apr-08		10:07:53		71.6		36		15-May-08		10:25:59		74.6		40

		4-Apr-08		12:07:10		74.6		35		4-Apr-08		12:06:20		74.6		35.5		4-Apr-08		12:07:53		71.6		42.5		15-May-08		12:25:59		74.01		41.5

		4-Apr-08		14:07:10		66.81		38.5		4-Apr-08		14:06:20		67.4		38.5		4-Apr-08		14:07:53		71.6		45		15-May-08		14:25:59		74.01		38.5

		4-Apr-08		16:07:10		66.81		42		4-Apr-08		16:06:20		66.81		45		4-Apr-08		16:07:53		71		45		15-May-08		16:25:59		74.01		38.5

		4-Apr-08		18:07:10		66.81		40.5		4-Apr-08		18:06:20		66.81		43.5		4-Apr-08		18:07:53		71.6		44		15-May-08		18:25:59		73.4		38.5

		4-Apr-08		20:07:10		66.81		45.5		4-Apr-08		20:06:20		65.6		44		4-Apr-08		20:07:53		71.6		43		15-May-08		20:25:59		75.2		38.5

		4-Apr-08		22:07:10		66.81		45.5		4-Apr-08		22:06:20		66.2		43		4-Apr-08		22:07:53		71.6		35.5		15-May-08		22:25:59		76.4		36

		5-Apr-08		0:07:10		67.4		45		5-Apr-08		0:06:20		65.6		42		5-Apr-08		0:07:53		71		39.5		16-May-08		0:25:59		76.4		35.5

		5-Apr-08		2:07:10		66.81		46.5		5-Apr-08		2:06:20		65.01		43.5		5-Apr-08		2:07:53		70.41		37.5		16-May-08		2:25:59		75.81		35.5

		5-Apr-08		4:07:10		66.81		46.5		5-Apr-08		4:06:20		65.01		44.5		5-Apr-08		4:07:53		69.8		38		16-May-08		4:25:59		75.2		35.5

		5-Apr-08		6:07:10		66.81		46		5-Apr-08		6:06:20		65.01		43		5-Apr-08		6:07:53		70.41		39		16-May-08		6:25:59		75.2		35

		5-Apr-08		8:07:10		68		43.5		5-Apr-08		8:06:20		65.6		43.5		5-Apr-08		8:07:53		71		41		16-May-08		8:25:59		74.6		36.5

		5-Apr-08		10:07:10		67.4		47		5-Apr-08		10:06:20		67.4		40		5-Apr-08		10:07:53		70.41		39		16-May-08		10:25:59		74.01		38.5

		5-Apr-08		12:07:10		67.4		45.5		5-Apr-08		12:06:20		67.4		38.5		5-Apr-08		12:07:53		71		44		16-May-08		12:25:59		73.4		40.5

		5-Apr-08		14:07:10		66.81		47		5-Apr-08		14:06:20		68.61		40.5		5-Apr-08		14:07:53		74.6		35.5		16-May-08		14:25:59		72.8		40.5

		5-Apr-08		16:07:10		66.81		46		5-Apr-08		16:06:20		67.4		43		5-Apr-08		16:07:53		71.6		45.5		16-May-08		16:25:59		73.4		40.5

		5-Apr-08		18:07:10		66.81		46.5		5-Apr-08		18:06:20		66.81		40		5-Apr-08		18:07:53		73.4		40		16-May-08		18:25:59		74.01		40.5

		5-Apr-08		20:07:10		67.4		46.5		5-Apr-08		20:06:20		67.4		40.5		5-Apr-08		20:07:53		75.2		37		16-May-08		20:25:59		75.2		40.5

		5-Apr-08		22:07:10		66.81		46		5-Apr-08		22:06:20		67.4		36.5		5-Apr-08		22:07:53		73.4		36.5		16-May-08		22:25:59		77		40

		6-Apr-08		0:07:10		66.81		46		6-Apr-08		0:06:20		66.81		37		6-Apr-08		0:07:53		71		36		17-May-08		0:25:59		76.4		39

		6-Apr-08		2:07:10		66.81		46.5		6-Apr-08		2:06:20		65.6		37.5		6-Apr-08		2:07:53		69.8		35.5		17-May-08		2:25:59		75.2		39

		6-Apr-08		4:07:10		66.81		47		6-Apr-08		4:06:20		65.01		38		6-Apr-08		4:07:53		68.61		36		17-May-08		4:25:59		74.6		39

		6-Apr-08		6:07:10		67.4		46		6-Apr-08		6:06:20		65.01		37.5		6-Apr-08		6:07:53		67.4		36.5		17-May-08		6:25:59		74.6		40

		6-Apr-08		8:07:10		67.4		47		6-Apr-08		8:06:20		65.01		37.5		6-Apr-08		8:07:53		67.4		36.5		17-May-08		8:25:59		74.6		41.5

		6-Apr-08		10:07:10		67.4		45		6-Apr-08		10:06:20		66.81		37		6-Apr-08		10:07:53		69.2		36.5		17-May-08		10:25:59		74.01		43

		6-Apr-08		12:07:10		67.4		46		6-Apr-08		12:06:20		68		35.5		6-Apr-08		12:07:53		70.41		36.5		17-May-08		12:25:59		73.4		46.5

		6-Apr-08		14:07:10		67.4		46		6-Apr-08		14:06:20		68		37		6-Apr-08		14:07:53		70.41		39		17-May-08		14:25:59		74.01		45.5

		6-Apr-08		16:07:10		68		45.5		6-Apr-08		16:06:20		68		39		6-Apr-08		16:07:53		70.41		40.5		17-May-08		16:25:59		74.01		45

		6-Apr-08		18:07:10		67.4		46.5		6-Apr-08		18:06:20		67.4		38.5		6-Apr-08		18:07:53		71		40		17-May-08		18:25:59		73.4		42.5

		6-Apr-08		20:07:10		68		45.5		6-Apr-08		20:06:20		67.4		39.5		6-Apr-08		20:07:53		72.21		38		17-May-08		20:25:59		75.2		42.5

		6-Apr-08		22:07:10		67.4		43.5		6-Apr-08		22:06:20		67.4		39.5		6-Apr-08		22:07:53		71.6		37		17-May-08		22:25:59		75.81		40

		7-Apr-08		0:07:10		67.4		44		7-Apr-08		0:06:20		66.81		39		7-Apr-08		0:07:53		71		36.5		18-May-08		0:25:59		75.2		39.5

		7-Apr-08		2:07:10		68		46		7-Apr-08		2:06:20		66.2		37.5		7-Apr-08		2:07:53		69.8		36		18-May-08		2:25:59		74.6		40

		7-Apr-08		4:07:10		67.4		45		7-Apr-08		4:06:20		65.6		38		7-Apr-08		4:07:53		69.2		36.5		18-May-08		4:25:59		73.4		40

		7-Apr-08		6:07:10		67.4		45.5		7-Apr-08		6:06:20		65.6		38		7-Apr-08		6:07:53		68.61		37		18-May-08		6:25:59		73.4		39.5

		7-Apr-08		8:07:10		67.4		46.5		7-Apr-08		8:06:20		65.6		39		7-Apr-08		8:07:53		68		37		18-May-08		8:25:59		74.01		40.5

		7-Apr-08		10:07:10		67.4		46		7-Apr-08		10:06:20		66.81		40		7-Apr-08		10:07:53		69.8		37.5		18-May-08		10:25:59		75.81		41.5

		7-Apr-08		12:07:10		68		45		7-Apr-08		12:06:20		66.81		44		7-Apr-08		12:07:53		69.8		39		18-May-08		12:25:59		77.61		42

		7-Apr-08		14:07:10		67.4		45		7-Apr-08		14:06:20		67.4		36		7-Apr-08		14:07:53		71		37		18-May-08		14:25:59		79.41		43

		7-Apr-08		16:07:10		67.4		45.5		7-Apr-08		16:06:20		66.81		35.5		7-Apr-08		16:07:53		71.6		35.5		18-May-08		16:25:59		79.41		41.5

		7-Apr-08		18:07:10		67.4		45.5		7-Apr-08		18:06:20		67.4		33		7-Apr-08		18:07:53		72.21		34.5		18-May-08		18:25:59		78.2		41.5

		7-Apr-08		20:07:10		67.4		44.5		7-Apr-08		20:06:20		66.81		31.5		7-Apr-08		20:07:53		71.6		33		18-May-08		20:25:59		77.61		41

		7-Apr-08		22:07:10		68		46		7-Apr-08		22:06:20		67.4		32.5		7-Apr-08		22:07:53		71		33		18-May-08		22:25:59		76.4		40

		8-Apr-08		0:07:10		67.4		44.5		8-Apr-08		0:06:20		66.81		34		8-Apr-08		0:07:53		69.8		33		19-May-08		0:25:59		74.6		39.5

		8-Apr-08		2:07:10		67.4		46.5		8-Apr-08		2:06:20		66.2		35.5		8-Apr-08		2:07:53		69.2		34		19-May-08		2:25:59		73.4		39

		8-Apr-08		4:07:10		67.4		45.5		8-Apr-08		4:06:20		65.6		35.5		8-Apr-08		4:07:53		68		34.5		19-May-08		4:25:59		72.21		39

		8-Apr-08		6:07:10		67.4		46		8-Apr-08		6:06:20		65.01		35		8-Apr-08		6:07:53		68		35		19-May-08		6:25:59		72.21		39.5

		8-Apr-08		8:07:10		67.4		46.5		8-Apr-08		8:06:20		66.2		35		8-Apr-08		8:07:53		71.6		35		19-May-08		8:25:59		72.21		40

		8-Apr-08		10:07:10		67.4		45		8-Apr-08		10:06:20		68		31.5		8-Apr-08		10:07:53		71.6		33.5		19-May-08		10:25:59		72.8		41.5

		8-Apr-08		12:07:10		66.81		46.5		8-Apr-08		12:06:20		68		29.5		8-Apr-08		12:07:53		71.6		34.5		19-May-08		12:25:59		74.6		41.5

		8-Apr-08		14:07:10		66.81		47		8-Apr-08		14:06:20		67.4		28.5		8-Apr-08		14:07:53		71		34.5		19-May-08		14:25:59		75.81		42

		8-Apr-08		16:07:10		66.81		46.5		8-Apr-08		16:06:20		67.4		35		8-Apr-08		16:07:53		71		37		19-May-08		16:25:59		77		41.5

		8-Apr-08		18:07:10		66.81		46		8-Apr-08		18:06:20		66.81		33		8-Apr-08		18:07:53		71.6		35		19-May-08		18:25:59		77.61		40

		8-Apr-08		20:07:10		66.81		46.5		8-Apr-08		20:06:20		66.81		38.5		8-Apr-08		20:07:53		71		34.5		19-May-08		20:25:59		77		39.5

		8-Apr-08		22:07:10		67.4		47		8-Apr-08		22:06:20		66.2		34		8-Apr-08		22:07:53		71.6		37.5		19-May-08		22:25:59		74.6		39.5

		9-Apr-08		0:07:10		66.81		45.5		9-Apr-08		0:06:20		66.2		38		9-Apr-08		0:07:53		71		35.5		20-May-08		0:25:59		73.4		40

		9-Apr-08		2:07:10		66.81		48		9-Apr-08		2:06:20		66.2		35.5		9-Apr-08		2:07:53		70.41		35		20-May-08		2:25:59		72.21		40

		9-Apr-08		4:07:10		66.81		47.5		9-Apr-08		4:06:20		66.2		36		9-Apr-08		4:07:53		69.8		34.5		20-May-08		4:25:59		72.21		40

		9-Apr-08		6:07:10		66.81		44		9-Apr-08		6:06:20		66.2		37		9-Apr-08		6:07:53		69.8		35.5		20-May-08		6:25:59		72.21		40.5

		9-Apr-08		8:07:10		66.81		47.5		9-Apr-08		8:06:20		66.81		37		9-Apr-08		8:07:53		71		38		20-May-08		8:25:59		71.6		42

		9-Apr-08		10:07:10		66.81		46		9-Apr-08		10:06:20		67.4		34		9-Apr-08		10:07:53		71		34.5		20-May-08		10:25:59		73.4		42.5

		9-Apr-08		12:07:10		66.81		45		9-Apr-08		12:06:20		68		32		9-Apr-08		12:07:53		71		38.5		20-May-08		12:25:59		74.01		43.5

		9-Apr-08		14:07:10		66.81		45		9-Apr-08		14:06:20		68.61		29.5		9-Apr-08		14:07:53		70.41		38.5		20-May-08		14:25:59		74.01		44.5

		9-Apr-08		16:07:10		66.81		47		9-Apr-08		16:06:20		67.4		36		9-Apr-08		16:07:53		71		41.5		20-May-08		16:25:59		74.6		44

		9-Apr-08		18:07:10		66.81		46.5		9-Apr-08		18:06:20		68		34		9-Apr-08		18:07:53		71.6		39.5		20-May-08		18:25:59		74.01		43.5

		9-Apr-08		20:07:10		67.4		47		9-Apr-08		20:06:20		67.4		33.5		9-Apr-08		20:07:53		75.2		35		20-May-08		20:25:59		74.6		43

		9-Apr-08		22:07:10		66.81		47		9-Apr-08		22:06:20		66.81		34.5		9-Apr-08		22:07:53		72.8		34.5		20-May-08		22:25:59		74.01		41

		10-Apr-08		0:07:10		66.81		47.5		10-Apr-08		0:06:20		66.2		33.5		10-Apr-08		0:07:53		70.41		33.5		21-May-08		0:25:59		72.8		41

		10-Apr-08		2:07:10		66.81		47		10-Apr-08		2:06:20		65.6		34.5		10-Apr-08		2:07:53		69.8		33		21-May-08		2:25:59		72.21		41

		10-Apr-08		4:07:10		66.81		47		10-Apr-08		4:06:20		65.01		34.5		10-Apr-08		4:07:53		69.2		33.5		21-May-08		4:25:59		72.21		41

		10-Apr-08		6:07:10		67.4		46		10-Apr-08		6:06:20		65.6		34.5		10-Apr-08		6:07:53		68.61		34.5		21-May-08		6:25:59		72.21		40.5

		10-Apr-08		8:07:10		66.81		47		10-Apr-08		8:06:20		66.2		34.5		10-Apr-08		8:07:53		69.8		35		21-May-08		8:25:59		72.21		42

		10-Apr-08		10:07:10		66.81		47.5		10-Apr-08		10:06:20		68		34		10-Apr-08		10:07:53		70.41		38		21-May-08		10:25:59		73.4		42.5

		10-Apr-08		12:07:10		66.81		47		10-Apr-08		12:06:20		69.2		34		10-Apr-08		12:07:53		70.41		35		21-May-08		12:25:59		73.4		43

		10-Apr-08		14:07:10		66.81		47.5		10-Apr-08		14:06:20		69.8		36		10-Apr-08		14:07:53		71		42.5		21-May-08		14:25:59		74.01		44

		10-Apr-08		16:07:10		66.81		46.5		10-Apr-08		16:06:20		69.2		39.5		10-Apr-08		16:07:53		70.41		47		21-May-08		16:25:59		74.01		41

		10-Apr-08		18:07:10		66.81		47.5		10-Apr-08		18:06:20		68		32		10-Apr-08		18:07:53		69.8		35.5		21-May-08		18:25:59		74.01		35

		10-Apr-08		20:07:10		66.81		46.5		10-Apr-08		20:06:20		67.4		37		10-Apr-08		20:07:53		70.41		41.5		21-May-08		20:25:59		73.4		34.5

		10-Apr-08		22:07:10		66.81		47		10-Apr-08		22:06:20		67.4		37		10-Apr-08		22:07:53		71		37.5		21-May-08		22:25:59		74.01		35

		11-Apr-08		0:07:10		66.81		47.5		11-Apr-08		0:06:20		68		36.5		11-Apr-08		0:07:53		69.2		38		22-May-08		0:25:59		73.4		34.5

		11-Apr-08		2:07:10		66.81		46.5		11-Apr-08		2:06:20		66.81		36.5		11-Apr-08		2:07:53		69.8		36.5		22-May-08		2:25:59		72.21		34.5

		11-Apr-08		4:07:10		66.81		46.5		11-Apr-08		4:06:20		66.2		37.5		11-Apr-08		4:07:53		69.8		35.5		22-May-08		4:25:59		71.6		34

		11-Apr-08		6:07:10		66.81		46.5		11-Apr-08		6:06:20		65.6		37.5		11-Apr-08		6:07:53		69.2		36.5		22-May-08		6:25:59		72.21		32.5

		11-Apr-08		8:07:10		66.81		47.5		11-Apr-08		8:06:20		66.81		38		11-Apr-08		8:07:53		70.41		38.5		22-May-08		8:25:59		71.6		33.5

		11-Apr-08		10:07:10		66.81		48		11-Apr-08		10:06:20		68		36.5		11-Apr-08		10:07:53		70.41		36		22-May-08		10:25:59		73.4		34

		11-Apr-08		12:07:10		66.2		48.5		11-Apr-08		12:06:20		68.61		35		11-Apr-08		12:07:53		71		39.5		22-May-08		12:25:59		73.4		35

		11-Apr-08		14:07:10		66.81		48		11-Apr-08		14:06:20		68.61		34.5		11-Apr-08		14:07:53		70.41		45.5		22-May-08		14:25:59		74.01		35

		11-Apr-08		16:07:10		66.2		45.5		11-Apr-08		16:06:20		68.61		40		11-Apr-08		16:07:53		70.41		47.5		22-May-08		16:25:59		74.01		35

		11-Apr-08		18:07:10		66.81		48		11-Apr-08		18:06:20		68.61		37.5		11-Apr-08		18:07:53		71		45.5		22-May-08		18:25:59		74.01		34.5

		11-Apr-08		20:07:10		66.81		47.5		11-Apr-08		20:06:20		68.61		39.5		11-Apr-08		20:07:53		70.41		42		22-May-08		20:25:59		73.4		34.5

		11-Apr-08		22:07:10		66.81		47		11-Apr-08		22:06:20		67.4		42.5		11-Apr-08		22:07:53		70.41		43		22-May-08		22:25:59		72.8		33.5

		12-Apr-08		0:07:10		66.81		48		12-Apr-08		0:06:20		68		41.5		12-Apr-08		0:07:53		69.8		41.5		23-May-08		0:25:59		72.21		33

		12-Apr-08		2:07:10		66.81		47		12-Apr-08		2:06:20		66.81		42		12-Apr-08		2:07:53		69.8		39		23-May-08		2:25:59		71		32.5

		12-Apr-08		4:07:10		66.81		47.5		12-Apr-08		4:06:20		66.2		41		12-Apr-08		4:07:53		70.41		38.5		23-May-08		4:25:59		71.6		31.5

		12-Apr-08		6:07:10		66.81		47.5		12-Apr-08		6:06:20		66.2		40.5		12-Apr-08		6:07:53		70.41		38		23-May-08		6:25:59		71.6		30.5

		12-Apr-08		8:07:10		66.81		48.5		12-Apr-08		8:06:20		68		39.5		12-Apr-08		8:07:53		69.8		36		23-May-08		8:25:59		71		31.5

		12-Apr-08		10:07:10		66.81		47.5		12-Apr-08		10:06:20		68.61		43		12-Apr-08		10:07:53		70.41		43		23-May-08		10:25:59		73.4		31

		12-Apr-08		12:07:10		66.81		47		12-Apr-08		12:06:20		68		39		12-Apr-08		12:07:53		69.8		47.5		23-May-08		12:25:59		73.4		29.5

		12-Apr-08		14:07:10		67.4		46.5		12-Apr-08		14:06:20		68.61		33.5		12-Apr-08		14:07:53		70.41		40.5		23-May-08		14:25:59		74.01		29

		12-Apr-08		16:07:10		67.4		48		12-Apr-08		16:06:20		67.4		35		12-Apr-08		16:07:53		72.21		40		23-May-08		16:25:59		74.6		30

		12-Apr-08		18:07:10		67.4		45.5		12-Apr-08		18:06:20		67.4		34		12-Apr-08		18:07:53		68		45		23-May-08		18:25:59		74.01		31

		12-Apr-08		20:07:10		67.4		46.5		12-Apr-08		20:06:20		66.81		32.5		12-Apr-08		20:07:53		68		45		23-May-08		20:25:59		74.01		32

		12-Apr-08		22:07:10		67.4		46.5		12-Apr-08		22:06:20		66.2		38.5		12-Apr-08		22:07:53		68		44		23-May-08		22:25:59		74.6		31.5

		13-Apr-08		0:07:10		67.4		46		13-Apr-08		0:06:20		66.81		41		13-Apr-08		0:07:53		66.81		46		24-May-08		0:25:59		73.4		31.5

		13-Apr-08		2:07:10		67.4		46		13-Apr-08		2:06:20		65.6		42		13-Apr-08		2:07:53		66.81		45.5		24-May-08		2:25:59		72.21		32

		13-Apr-08		4:07:10		68		45.5		13-Apr-08		4:06:20		65.6		41		13-Apr-08		4:07:53		66.2		46.5		24-May-08		4:25:59		71.6		32

		13-Apr-08		6:07:10		68		46.5		13-Apr-08		6:06:20		66.81		40		13-Apr-08		6:07:53		66.2		47		24-May-08		6:25:59		72.21		31.5

		13-Apr-08		8:07:10		67.4		46.5		13-Apr-08		8:06:20		66.2		40.5		13-Apr-08		8:07:53		66.2		47.5		24-May-08		8:25:59		71.6		33

		13-Apr-08		10:07:10		68		47		13-Apr-08		10:06:20		66.81		42		13-Apr-08		10:07:53		66.81		47		24-May-08		10:25:59		74.01		33.5

		13-Apr-08		12:07:10		67.4		46		13-Apr-08		12:06:20		67.4		41.5		13-Apr-08		12:07:53		67.4		45.5		24-May-08		12:25:59		73.4		35

		13-Apr-08		14:07:10		67.4		46.5		13-Apr-08		14:06:20		67.4		43		13-Apr-08		14:07:53		67.4		46		24-May-08		14:25:59		74.01		35

		13-Apr-08		16:07:10		67.4		46		13-Apr-08		16:06:20		66.81		40		13-Apr-08		16:07:53		68		45.5		24-May-08		16:25:59		74.01		34.5

		13-Apr-08		18:07:10		67.4		46.5		13-Apr-08		18:06:20		66.81		38.5		13-Apr-08		18:07:53		67.4		45.5		24-May-08		18:25:59		74.01		34.5

		13-Apr-08		20:07:10		68		46		13-Apr-08		20:06:20		66.2		43.5		13-Apr-08		20:07:53		67.4		46		24-May-08		20:25:59		74.01		35.5

		13-Apr-08		22:07:10		67.4		47.5		13-Apr-08		22:06:20		66.2		53.5		13-Apr-08		22:07:53		67.4		46.5		24-May-08		22:25:59		74.01		35

		14-Apr-08		0:07:10		67.4		46		14-Apr-08		0:06:20		66.2		48.5		14-Apr-08		0:07:53		66.81		47		25-May-08		0:25:59		72.8		35.5

		14-Apr-08		2:07:10		67.4		46		14-Apr-08		2:06:20		66.2		46		14-Apr-08		2:07:53		66.81		47		25-May-08		2:25:59		72.21		36

		14-Apr-08		4:07:10		67.4		46		14-Apr-08		4:06:20		65.6		45.5		14-Apr-08		4:07:53		66.2		47.5		25-May-08		4:25:59		71.6		36.5

		14-Apr-08		6:07:10		68.61		46		14-Apr-08		6:06:20		65.6		44		14-Apr-08		6:07:53		66.2		48		25-May-08		6:25:59		71.6		37

		14-Apr-08		8:07:10		67.4		46		14-Apr-08		8:06:20		66.2		41.5		14-Apr-08		8:07:53		66.2		47		25-May-08		8:25:59		71.6		37.5

		14-Apr-08		10:07:10		68		46		14-Apr-08		10:06:20		66.2		43		14-Apr-08		10:07:53		66.2		48		25-May-08		10:25:59		71.6		38.5

		14-Apr-08		12:07:10		67.4		46		14-Apr-08		12:06:20		67.4		43		14-Apr-08		12:07:53		66.81		47		25-May-08		12:25:59		71.6		40

		14-Apr-08		14:07:10		67.4		48		14-Apr-08		14:06:20		67.4		45.5		14-Apr-08		14:07:53		67.4		48.5		25-May-08		14:25:59		71.6		40.5

		14-Apr-08		16:07:10		67.4		46		14-Apr-08		16:06:20		66.81		43		14-Apr-08		16:07:53		66.81		47		25-May-08		16:25:59		71.6		40

		14-Apr-08		18:07:10		67.4		47		14-Apr-08		18:06:20		66.81		46.5		14-Apr-08		18:07:53		66.81		48		25-May-08		18:25:59		71.6		41

		14-Apr-08		20:07:10		67.4		47		14-Apr-08		20:06:20		66.2		50		14-Apr-08		20:07:53		66.2		48		25-May-08		20:25:59		71.6		41

		14-Apr-08		22:07:10		68		45.5		14-Apr-08		22:06:20		66.2		46		14-Apr-08		22:07:53		66.2		48		25-May-08		22:25:59		71.6		41

		15-Apr-08		0:07:10		67.4		46		15-Apr-08		0:06:20		65.6		49		15-Apr-08		0:07:53		66.81		47		26-May-08		0:25:59		71.6		40

		15-Apr-08		2:07:10		67.4		47		15-Apr-08		2:06:20		66.2		46		15-Apr-08		2:07:53		66.81		47.5		26-May-08		2:25:59		71.6		38.5

		15-Apr-08		4:07:10		67.4		44		15-Apr-08		4:06:20		65.6		45		15-Apr-08		4:07:53		66.81		47.5		26-May-08		4:25:59		71.6		37.5

		15-Apr-08		6:07:10		68		46		15-Apr-08		6:06:20		65.01		45		15-Apr-08		6:07:53		66.2		48		26-May-08		6:25:59		71.6		37

		15-Apr-08		8:07:10		67.4		45.5		15-Apr-08		8:06:20		67.4		45		15-Apr-08		8:07:53		65.6		49.5		26-May-08		8:25:59		71.6		37.5

		15-Apr-08		10:07:10		67.4		47		15-Apr-08		10:06:20		69.2		44		15-Apr-08		10:07:53		65.01		49		26-May-08		10:25:59		71.6		39.5

		15-Apr-08		12:07:10		67.4		47		15-Apr-08		12:06:20		69.8		37.5		15-Apr-08		12:07:53		65.6		49		26-May-08		12:25:59		72.21		38.5

		15-Apr-08		14:07:10		67.4		41		15-Apr-08		14:06:20		71		33.5		15-Apr-08		14:07:53		66.2		47.5		26-May-08		14:25:59		72.8		38

		15-Apr-08		16:07:10		67.4		45.5		15-Apr-08		16:06:20		70.41		32.5		15-Apr-08		16:07:53		66.81		47		26-May-08		16:25:59		73.4		36.5

		15-Apr-08		18:07:10		67.4		45.5		15-Apr-08		18:06:20		69.2		31.5		15-Apr-08		18:07:53		68		45.5		26-May-08		18:25:59		74.01		36

		15-Apr-08		20:07:10		67.4		45		15-Apr-08		20:06:20		69.2		29		15-Apr-08		20:07:53		67.4		45		26-May-08		20:25:59		74.01		35.5

		15-Apr-08		22:07:10		68		45.5		15-Apr-08		22:06:20		68		31.5		15-Apr-08		22:07:53		67.4		45		26-May-08		22:25:59		72.21		37

		16-Apr-08		0:07:10		67.4		37		16-Apr-08		0:06:20		66.81		34.5		16-Apr-08		0:07:53		67.4		45.5		27-May-08		0:25:59		72.21		37.5

		16-Apr-08		2:07:10		67.4		46.5		16-Apr-08		2:06:20		65.6		33		16-Apr-08		2:07:53		68		44.5		27-May-08		2:25:59		71.6		37.5

		16-Apr-08		4:07:10		67.4		45		16-Apr-08		4:06:20		65.01		33		16-Apr-08		4:07:53		68		45		27-May-08		4:25:59		71.6		37.5

		16-Apr-08		6:07:10		67.4		45.5		16-Apr-08		6:06:20		65.01		33.5		16-Apr-08		6:07:53		68		44.5		27-May-08		6:25:59		72.21		37.5

		16-Apr-08		8:07:10		67.4		46		16-Apr-08		8:06:20		68		32.5		16-Apr-08		8:07:53		67.4		44		27-May-08		8:25:59		71		39

		16-Apr-08		10:07:10		69.2		34		16-Apr-08		10:06:20		70.41		30		16-Apr-08		10:07:53		66.2		47.5		27-May-08		10:25:59		71		39.5

		16-Apr-08		12:07:10		69.8		44		16-Apr-08		12:06:20		68.61		27.5		16-Apr-08		12:07:53		66.2		48		27-May-08		12:25:59		72.21		40.5

		16-Apr-08		14:07:10		70.41		43		16-Apr-08		14:06:20		69.8		26		16-Apr-08		14:07:53		66.2		49.5		27-May-08		14:25:59		72.8		40

		16-Apr-08		16:07:10		70.41		46		16-Apr-08		16:06:20		69.2		28		16-Apr-08		16:07:53		67.4		47		27-May-08		16:25:59		72.8		39.5

		16-Apr-08		18:07:10		70.41		45.5		16-Apr-08		18:06:20		68.61		31		16-Apr-08		18:07:53		68		48		27-May-08		18:25:59		72.8		41

		16-Apr-08		20:07:10		69.2		44.5		16-Apr-08		20:06:20		68		30		16-Apr-08		20:07:53		67.4		44.5		27-May-08		20:25:59		72.8		40.5

		16-Apr-08		22:07:10		69.2		44.5		16-Apr-08		22:06:20		68		30		16-Apr-08		22:07:53		68		45		27-May-08		22:25:59		72.21		39.5

		17-Apr-08		0:07:10		70.41		46		17-Apr-08		0:06:20		67.4		31.5		17-Apr-08		0:07:53		68		41		28-May-08		0:25:59		72.21		39.5

		17-Apr-08		2:07:10		70.41		43.5		17-Apr-08		2:06:20		66.2		33		17-Apr-08		2:07:53		68		48.5		28-May-08		2:25:59		72.21		40

		17-Apr-08		4:07:10		69.8		46		17-Apr-08		4:06:20		65.6		34		17-Apr-08		4:07:53		68		46.5		28-May-08		4:25:59		71.6		40

		17-Apr-08		6:07:10		69.8		46		17-Apr-08		6:06:20		65.6		34.5		17-Apr-08		6:07:53		68		47		28-May-08		6:25:59		72.21		40.5

		17-Apr-08		8:07:10		71		44.5		17-Apr-08		8:06:20		69.2		33		17-Apr-08		8:07:53		67.4		48		28-May-08		8:25:59		71.6		42.5

		17-Apr-08		10:07:10		70.41		44.5		17-Apr-08		10:06:20		70.41		31.5		17-Apr-08		10:07:53		66.81		45.5		28-May-08		10:25:59		73.4		42

		17-Apr-08		12:07:10		71		45.5		17-Apr-08		12:06:20		71		29		17-Apr-08		12:07:53		68		48.5		28-May-08		12:25:59		74.01		41

		17-Apr-08		14:07:10		71		45.5		17-Apr-08		14:06:20		69.2		29.5		17-Apr-08		14:07:53		67.4		49.5		28-May-08		14:25:59		74.01		41.5

		17-Apr-08		16:07:10		71		45.5		17-Apr-08		16:06:20		68.61		31.5		17-Apr-08		16:07:53		68		48		28-May-08		16:25:59		74.6		39.5

		17-Apr-08		18:07:10		71		46.5		17-Apr-08		18:06:20		70.41		31		17-Apr-08		18:07:53		68.61		48		28-May-08		18:25:59		75.2		38

		17-Apr-08		20:07:10		71		44.5		17-Apr-08		20:06:20		69.8		34.5		17-Apr-08		20:07:53		67.4		46.5		28-May-08		20:25:59		74.6		39.5

		17-Apr-08		22:07:10		69.8		42.5		17-Apr-08		22:06:20		69.8		36.5		17-Apr-08		22:07:53		67.4		46		28-May-08		22:25:59		74.01		38

		18-Apr-08		0:07:10		70.41		45.5		18-Apr-08		0:06:20		68.61		38		18-Apr-08		0:07:53		68		48.5		29-May-08		0:25:59		72.8		38

		18-Apr-08		2:07:10		70.41		42.5		18-Apr-08		2:06:20		67.4		39		18-Apr-08		2:07:53		68		47.5		29-May-08		2:25:59		72.21		38

		18-Apr-08		4:07:10		69.8		46.5		18-Apr-08		4:06:20		66.2		39.5		18-Apr-08		4:07:53		68		47.5		29-May-08		4:25:59		72.21		38.5

		18-Apr-08		6:07:10		69.8		46		18-Apr-08		6:06:20		65.6		40		18-Apr-08		6:07:53		68		42		29-May-08		6:25:59		72.8		38.5

		18-Apr-08		8:07:10		70.41		46.5		18-Apr-08		8:06:20		68.61		39		18-Apr-08		8:07:53		67.4		49		29-May-08		8:25:59		72.8		40

		18-Apr-08		10:07:10		70.41		46		18-Apr-08		10:06:20		71		37.5		18-Apr-08		10:07:53		67.4		47.5		29-May-08		10:25:59		74.01		39

		18-Apr-08		12:07:10		71		44		18-Apr-08		12:06:20		72.21		36.5		18-Apr-08		12:07:53		68		49		29-May-08		12:25:59		74.6		39.5

		18-Apr-08		14:07:10		70.41		44.5		18-Apr-08		14:06:20		71		34.5		18-Apr-08		14:07:53		66.81		49.5		29-May-08		14:25:59		75.2		39

		18-Apr-08		16:07:10		70.41		42.5		18-Apr-08		16:06:20		71		39		18-Apr-08		16:07:53		67.4		49		29-May-08		16:25:59		74.6		39

		18-Apr-08		18:07:10		70.41		45		18-Apr-08		18:06:20		70.41		38		18-Apr-08		18:07:53		68		47.5		29-May-08		18:25:59		74.6		38

		18-Apr-08		20:07:10		70.41		44.5		18-Apr-08		20:06:20		69.8		41		18-Apr-08		20:07:53		67.4		48.5		29-May-08		20:25:59		74.6		39.5

		18-Apr-08		22:07:10		70.41		45.5		18-Apr-08		22:06:20		69.2		41		18-Apr-08		22:07:53		68		48.5		29-May-08		22:25:59		74.6		38.5

		19-Apr-08		0:07:10		69.8		44.5		19-Apr-08		0:06:20		68		42.5		19-Apr-08		0:07:53		67.4		49		30-May-08		0:25:59		74.01		38.5

		19-Apr-08		2:07:10		69.8		45		19-Apr-08		2:06:20		67.4		45		19-Apr-08		2:07:53		67.4		49		30-May-08		2:25:59		72.8		38.5

		19-Apr-08		4:07:10		69.8		40		19-Apr-08		4:06:20		66.81		45		19-Apr-08		4:07:53		68		46.5		30-May-08		4:25:59		72.21		39

		19-Apr-08		6:07:10		69.8		45.5		19-Apr-08		6:06:20		66.81		45		19-Apr-08		6:07:53		68		49		30-May-08		6:25:59		72.21		39.5

		19-Apr-08		8:07:10		69.8		45		19-Apr-08		8:06:20		71		41		19-Apr-08		8:07:53		66.81		50		30-May-08		8:25:59		72.21		41.5

		19-Apr-08		10:07:10		69.8		45		19-Apr-08		10:06:20		71.6		40.5		19-Apr-08		10:07:53		66.81		50		30-May-08		10:25:59		74.6		41.5

		19-Apr-08		12:07:10		70.41		44.5		19-Apr-08		12:06:20		71.6		39		19-Apr-08		12:07:53		66.81		50		30-May-08		12:25:59		74.6		41.5

		19-Apr-08		14:07:10		70.41		42		19-Apr-08		14:06:20		72.8		41		19-Apr-08		14:07:53		66.81		48		30-May-08		14:25:59		74.6		41.5

		19-Apr-08		16:07:10		70.41		45		19-Apr-08		16:06:20		69.8		42.5		19-Apr-08		16:07:53		67.4		48		30-May-08		16:25:59		75.2		40.5

		19-Apr-08		18:07:10		69.8		45		19-Apr-08		18:06:20		69.8		43.5		19-Apr-08		18:07:53		67.4		49.5		30-May-08		18:25:59		74.6		39

		19-Apr-08		20:07:10		69.8		42		19-Apr-08		20:06:20		68.61		41		19-Apr-08		20:07:53		67.4		46		30-May-08		20:25:59		74.6		41

		19-Apr-08		22:07:10		69.8		44.5		19-Apr-08		22:06:20		68.61		39		19-Apr-08		22:07:53		67.4		49.5		30-May-08		22:25:59		74.6		39.5

		20-Apr-08		0:07:10		69.2		44		20-Apr-08		0:06:20		67.4		40		20-Apr-08		0:07:53		67.4		49.5		31-May-08		0:25:59		74.01		39

		20-Apr-08		2:07:10		69.2		44.5		20-Apr-08		2:06:20		66.2		40		20-Apr-08		2:07:53		67.4		48		31-May-08		2:25:59		72.8		39.5

		20-Apr-08		4:07:10		68.61		45.5		20-Apr-08		4:06:20		65.01		38.5		20-Apr-08		4:07:53		66.81		48.5		31-May-08		4:25:59		72.21		40

		20-Apr-08		6:07:10		68.61		46.5		20-Apr-08		6:06:20		65.01		36		20-Apr-08		6:07:53		67.4		48.5		31-May-08		6:25:59		71.6		41

		20-Apr-08		8:07:10		68.61		47		20-Apr-08		8:06:20		65.01		33.5		20-Apr-08		8:07:53		67.4		47.5		31-May-08		8:25:59		71.6		42

		20-Apr-08		10:07:10		68.61		46		20-Apr-08		10:06:20		67.4		30		20-Apr-08		10:07:53		68		47.5		31-May-08		10:25:59		73.4		42.5

		20-Apr-08		12:07:10		69.2		43.5		20-Apr-08		12:06:20		69.2		26		20-Apr-08		12:07:53		67.4		44.5		31-May-08		12:25:59		74.6		42

		20-Apr-08		14:07:10		69.2		43.5		20-Apr-08		14:06:20		69.2		23		20-Apr-08		14:07:53		66.81		36.5		31-May-08		14:25:59		75.2		43.5

		20-Apr-08		16:07:10		69.2		45		20-Apr-08		16:06:20		69.2		23.5		20-Apr-08		16:07:53		67.4		47.5		31-May-08		16:25:59		74.6		43

		20-Apr-08		18:07:10		69.2		44		20-Apr-08		18:06:20		69.8		23		20-Apr-08		18:07:53		67.4		44.5		31-May-08		18:25:59		74.6		44.5

		20-Apr-08		20:07:10		69.2		45.5		20-Apr-08		20:06:20		68		25.5		20-Apr-08		20:07:53		67.4		47		31-May-08		20:25:59		74.6		43

		20-Apr-08		22:07:10		68.61		45		20-Apr-08		22:06:20		66.81		27.5		20-Apr-08		22:07:53		67.4		47.5		31-May-08		22:25:59		74.01		41

		21-Apr-08		0:07:10		68.61		46.5		21-Apr-08		0:06:20		65.6		29		21-Apr-08		0:07:53		67.4		48.5		1-Jun-08		0:25:59		72.8		41

		21-Apr-08		2:07:10		68		44.5		21-Apr-08		2:06:20		65.01		30.5		21-Apr-08		2:07:53		66.81		37.5		1-Jun-08		2:25:59		72.21		40.5

		21-Apr-08		4:07:10		68		46.5		21-Apr-08		4:06:20		63.8		31.5		21-Apr-08		4:07:53		66.81		47.5		1-Jun-08		4:25:59		71.6		40.5

		21-Apr-08		6:07:10		68		47.5		21-Apr-08		6:06:20		63.21		33		21-Apr-08		6:07:53		67.4		47.5		1-Jun-08		6:25:59		72.21		40.5

		21-Apr-08		8:07:10		68		44		21-Apr-08		8:06:20		63.21		33		21-Apr-08		8:07:53		67.4		47.5		1-Jun-08		8:25:59		72.21		40.5

		21-Apr-08		10:07:10		68		47.5		21-Apr-08		10:06:20		65.01		29		21-Apr-08		10:07:53		67.4		47.5		1-Jun-08		10:25:59		72.21		40.5

		21-Apr-08		12:07:10		68		42.5		21-Apr-08		12:06:20		67.4		24.5		21-Apr-08		12:07:53		67.4		42		1-Jun-08		12:25:59		73.4		41

		21-Apr-08		14:07:10		68.61		45.5		21-Apr-08		14:06:20		69.2		27.5		21-Apr-08		14:07:53		67.4		48		1-Jun-08		14:25:59		74.6		41.5

		21-Apr-08		16:07:10		68.61		45		21-Apr-08		16:06:20		69.2		29.5		21-Apr-08		16:07:53		67.4		48		1-Jun-08		16:25:59		75.81		41

		21-Apr-08		18:07:10		68.61		45		21-Apr-08		18:06:20		69.2		27		21-Apr-08		18:07:53		66.81		46.5		1-Jun-08		18:25:59		77		39.5

		21-Apr-08		20:07:10		69.2		45		21-Apr-08		20:06:20		68		30		21-Apr-08		20:07:53		67.4		48		1-Jun-08		20:25:59		76.4		39.5

		21-Apr-08		22:07:10		68.61		46.5		21-Apr-08		22:06:20		66.2		32		21-Apr-08		22:07:53		67.4		48.5		1-Jun-08		22:25:59		74.6		39

		22-Apr-08		0:07:10		68.61		45		22-Apr-08		0:06:20		65.01		30		22-Apr-08		0:07:53		67.4		48		2-Jun-08		0:25:59		72.8		39

		22-Apr-08		2:07:10		68		47		22-Apr-08		2:06:20		64.4		32		22-Apr-08		2:07:53		67.4		48		2-Jun-08		2:25:59		72.21		38.5

		22-Apr-08		4:07:10		67.4		47		22-Apr-08		4:06:20		63.8		32.5		22-Apr-08		4:07:53		66.81		41		2-Jun-08		4:25:59		72.21		38

		22-Apr-08		6:07:10		68		46.5		22-Apr-08		6:06:20		63.21		34		22-Apr-08		6:07:53		67.4		48		2-Jun-08		6:25:59		71.6		37.5

		22-Apr-08		8:07:10		68.61		47		22-Apr-08		8:06:20		66.81		33.5		22-Apr-08		8:07:53		66.81		49		2-Jun-08		8:25:59		71.6		38

		22-Apr-08		10:07:10		69.2		44.5		22-Apr-08		10:06:20		71		29.5		22-Apr-08		10:07:53		66.2		49.5		2-Jun-08		10:25:59		72.21		39

		22-Apr-08		12:07:10		69.8		44		22-Apr-08		12:06:20		71		27.5		22-Apr-08		12:07:53		66.81		48		2-Jun-08		12:25:59		73.4		38.5

		22-Apr-08		14:07:10		69.8		46		22-Apr-08		14:06:20		71		31		22-Apr-08		14:07:53		66.2		49.5		2-Jun-08		14:25:59		75.2		38

		22-Apr-08		16:07:10		69.2		44.5		22-Apr-08		16:06:20		69.8		32.5		22-Apr-08		16:07:53		67.4		47.5		2-Jun-08		16:25:59		75.81		38

		22-Apr-08		18:07:10		69.2		45		22-Apr-08		18:06:20		69.8		32		22-Apr-08		18:07:53		68		46.5		2-Jun-08		18:25:59		76.4		37

		22-Apr-08		20:07:10		69.8		45		22-Apr-08		20:06:20		69.2		31.5		22-Apr-08		20:07:53		68		46.5		2-Jun-08		20:25:59		75.81		37

		22-Apr-08		22:07:10		69.8		43.5		22-Apr-08		22:06:20		68		32		22-Apr-08		22:07:53		68		47		2-Jun-08		22:25:59		74.01		37.5

		23-Apr-08		0:07:10		69.2		45		23-Apr-08		0:06:20		66.81		32		23-Apr-08		0:07:53		67.4		47.5		3-Jun-08		0:25:59		72.21		37

		23-Apr-08		2:07:10		68.61		45		23-Apr-08		2:06:20		65.6		33		23-Apr-08		2:07:53		67.4		47		3-Jun-08		2:25:59		72.21		36.5

		23-Apr-08		4:07:10		68.61		46.5		23-Apr-08		4:06:20		65.01		34.5		23-Apr-08		4:07:53		67.4		47.5		3-Jun-08		4:25:59		71.6		36

		23-Apr-08		6:07:10		68.61		43.5		23-Apr-08		6:06:20		64.4		35.5		23-Apr-08		6:07:53		67.4		47.5		3-Jun-08		6:25:59		72.21		35.5

		23-Apr-08		8:07:10		69.2		42.5		23-Apr-08		8:06:20		66.81		35.5		23-Apr-08		8:07:53		67.4		48		3-Jun-08		8:25:59		71.6		37.5

		23-Apr-08		10:07:10		69.8		46		23-Apr-08		10:06:20		70.41		32.5		23-Apr-08		10:07:53		67.4		48		3-Jun-08		10:25:59		74.01		38

		23-Apr-08		12:07:10		69.2		45.5		23-Apr-08		12:06:20		71		35.5		23-Apr-08		12:07:53		66.81		49.5		3-Jun-08		12:25:59		74.01		39

		23-Apr-08		14:07:10		69.8		45		23-Apr-08		14:06:20		71.6		41		23-Apr-08		14:07:53		66.2		50.5		3-Jun-08		14:25:59		74.6		39.5

		23-Apr-08		16:07:10		70.41		47		23-Apr-08		16:06:20		69.8		49		23-Apr-08		16:07:53		67.4		50.5		3-Jun-08		16:25:59		74.6		39

		23-Apr-08		18:07:10		70.41		44.5		23-Apr-08		18:06:20		69.2		47.5		23-Apr-08		18:07:53		68		50		3-Jun-08		18:25:59		74.6		38.5

		23-Apr-08		20:07:10		70.41		46		23-Apr-08		20:06:20		69.8		49.5		23-Apr-08		20:07:53		68		50		3-Jun-08		20:25:59		74.6		34.5

		23-Apr-08		22:07:10		70.41		46.5		23-Apr-08		22:06:20		69.2		48.5		23-Apr-08		22:07:53		68		50		3-Jun-08		22:25:59		74.6		31.5

		24-Apr-08		0:07:10		70.41		47		24-Apr-08		0:06:20		68		47		24-Apr-08		0:07:53		68		49.5		4-Jun-08		0:25:59		73.4		32.5

		24-Apr-08		2:07:10		69.8		44.5		24-Apr-08		2:06:20		66.81		47.5		24-Apr-08		2:07:53		68		49.5		4-Jun-08		2:25:59		72.8		33.5

		24-Apr-08		4:07:10		69.8		46.5		24-Apr-08		4:06:20		66.2		46		24-Apr-08		4:07:53		68		48.5		4-Jun-08		4:25:59		72.21		34

		24-Apr-08		6:07:10		69.8		46.5		24-Apr-08		6:06:20		65.6		44.5		24-Apr-08		6:07:53		68		49		4-Jun-08		6:25:59		72.21		33.5

		24-Apr-08		8:07:10		70.41		47		24-Apr-08		8:06:20		68		44		24-Apr-08		8:07:53		67.4		50		4-Jun-08		8:25:59		72.21		37

		24-Apr-08		10:07:10		70.41		46		24-Apr-08		10:06:20		70.41		46		24-Apr-08		10:07:53		68		49.5		4-Jun-08		10:25:59		74.01		41.5

		24-Apr-08		12:07:10		70.41		46.5		24-Apr-08		12:06:20		69.8		44.5		24-Apr-08		12:07:53		68		50		4-Jun-08		12:25:59		74.01		44

		24-Apr-08		14:07:10		70.41		46		24-Apr-08		14:06:20		71		36		24-Apr-08		14:07:53		68		49		4-Jun-08		14:25:59		74.01		44.5

		24-Apr-08		16:07:10		70.41		44.5		24-Apr-08		16:06:20		69.8		32		24-Apr-08		16:07:53		68		48		4-Jun-08		16:25:59		73.4		42

		24-Apr-08		18:07:10		69.8		44		24-Apr-08		18:06:20		70.41		31		24-Apr-08		18:07:53		68		45		4-Jun-08		18:25:59		73.4		39

		24-Apr-08		20:07:10		70.41		46		24-Apr-08		20:06:20		69.8		30.5		24-Apr-08		20:07:53		69.2		46.5		4-Jun-08		20:25:59		74.6		39.5

		24-Apr-08		22:07:10		70.41		46		24-Apr-08		22:06:20		68		33		24-Apr-08		22:07:53		68		48.5		4-Jun-08		22:25:59		74.6		38

		25-Apr-08		0:07:10		69.8		45		25-Apr-08		0:06:20		66.2		34		25-Apr-08		0:07:53		68		48.5		5-Jun-08		0:25:59		74.01		37.5

		25-Apr-08		2:07:10		69.2		46		25-Apr-08		2:06:20		65.01		35.5		25-Apr-08		2:07:53		68.61		46		5-Jun-08		2:25:59		72.8		36.5

		25-Apr-08		4:07:10		69.2		45		25-Apr-08		4:06:20		63.8		36		25-Apr-08		4:07:53		68		47.5		5-Jun-08		4:25:59		72.21		36

		25-Apr-08		6:07:10		69.8		45		25-Apr-08		6:06:20		63.21		36		25-Apr-08		6:07:53		68.61		47.5		5-Jun-08		6:25:59		72.21		35.5

		25-Apr-08		8:07:10		69.8		46		25-Apr-08		8:06:20		66.81		35.5		25-Apr-08		8:07:53		68.61		47.5		5-Jun-08		8:25:59		72.21		35.5

		25-Apr-08		10:07:10		69.8		45		25-Apr-08		10:06:20		70.41		32.5		25-Apr-08		10:07:53		67.4		49.5		5-Jun-08		10:25:59		74.01		35.5

		25-Apr-08		12:07:10		70.41		42.5		25-Apr-08		12:06:20		71		28.5		25-Apr-08		12:07:53		68.61		48		5-Jun-08		12:25:59		73.4		35

		25-Apr-08		14:07:10		70.41		45.5		25-Apr-08		14:06:20		71		28		25-Apr-08		14:07:53		68		47.5		5-Jun-08		14:25:59		73.4		34

		25-Apr-08		16:07:10		70.41		46		25-Apr-08		16:06:20		71.6		32.5		25-Apr-08		16:07:53		68.61		48.5		5-Jun-08		16:25:59		74.01		34.5

		25-Apr-08		18:07:10		70.41		45.5		25-Apr-08		18:06:20		70.41		31		25-Apr-08		18:07:53		68		40.5		5-Jun-08		18:25:59		73.4		35

		25-Apr-08		20:07:10		70.41		41.5		25-Apr-08		20:06:20		71		32.5		25-Apr-08		20:07:53		68		48		5-Jun-08		20:25:59		74.01		35.5

		25-Apr-08		22:07:10		69.8		45		25-Apr-08		22:06:20		70.41		35.5		25-Apr-08		22:07:53		68		46		5-Jun-08		22:25:59		74.6		34

		26-Apr-08		0:07:10		70.41		46		26-Apr-08		0:06:20		69.2		36.5		26-Apr-08		0:07:53		68		49		6-Jun-08		0:25:59		74.01		34.5

		26-Apr-08		2:07:10		69.8		45.5		26-Apr-08		2:06:20		67.4		38.5		26-Apr-08		2:07:53		68.61		48		6-Jun-08		2:25:59		72.21		35

		26-Apr-08		4:07:10		69.8		44.5		26-Apr-08		4:06:20		66.2		39		26-Apr-08		4:07:53		68		48		6-Jun-08		4:25:59		71.6		35

		26-Apr-08		6:07:10		69.8		46		26-Apr-08		6:06:20		65.6		38.5		26-Apr-08		6:07:53		68.61		48		6-Jun-08		6:25:59		71.6		35

		26-Apr-08		8:07:10		70.41		46.5		26-Apr-08		8:06:20		68.61		37.5		26-Apr-08		8:07:53		68.61		48.5		6-Jun-08		8:25:59		72.21		37

		26-Apr-08		10:07:10		70.41		45.5		26-Apr-08		10:06:20		71		35.5		26-Apr-08		10:07:53		68		46.5		6-Jun-08		10:25:59		73.4		37.5

		26-Apr-08		12:07:10		71		46.5		26-Apr-08		12:06:20		71		32.5		26-Apr-08		12:07:53		68.61		49		6-Jun-08		12:25:59		73.4		35.5

		26-Apr-08		14:07:10		71		32		26-Apr-08		14:06:20		69.2		31		26-Apr-08		14:07:53		67.4		36		6-Jun-08		14:25:59		74.01		37.5

		26-Apr-08		16:07:10		71		35		26-Apr-08		16:06:20		68.61		36		26-Apr-08		16:07:53		67.4		39.5		6-Jun-08		16:25:59		74.01		38.5

		26-Apr-08		18:07:10		71		39.5		26-Apr-08		18:06:20		69.2		39.5		26-Apr-08		18:07:53		68.61		42.5		6-Jun-08		18:25:59		73.4		38.5

		26-Apr-08		20:07:10		70.41		38		26-Apr-08		20:06:20		69.2		41		26-Apr-08		20:07:53		68.61		41		6-Jun-08		20:25:59		74.01		41

		26-Apr-08		22:07:10		69.8		38		26-Apr-08		22:06:20		68		42		26-Apr-08		22:07:53		68.61		40.5		6-Jun-08		22:25:59		74.6		39

		27-Apr-08		0:07:10		69.8		36.5		27-Apr-08		0:06:20		68		39.5		27-Apr-08		0:07:53		68.61		39.5		7-Jun-08		0:25:59		74.01		38.5

		27-Apr-08		2:07:10		70.41		36.5		27-Apr-08		2:06:20		68		39.5		27-Apr-08		2:07:53		68.61		39.5		7-Jun-08		2:25:59		72.8		39

		27-Apr-08		4:07:10		70.41		37.5		27-Apr-08		4:06:20		66.81		42.5		27-Apr-08		4:07:53		68.61		39.5		7-Jun-08		4:25:59		71.6		38.5

		27-Apr-08		6:07:10		69.8		36		27-Apr-08		6:06:20		67.4		40.5		27-Apr-08		6:07:53		68		39		7-Jun-08		6:25:59		72.21		37.5

		27-Apr-08		8:07:10		69.8		37.5		27-Apr-08		8:06:20		68		42		27-Apr-08		8:07:53		68.61		40.5		7-Jun-08		8:25:59		72.21		38

		27-Apr-08		10:07:10		70.41		40		27-Apr-08		10:06:20		69.2		43		27-Apr-08		10:07:53		68.61		42.5		7-Jun-08		10:25:59		73.4		37.5

		27-Apr-08		12:07:10		71		40		27-Apr-08		12:06:20		69.2		42.5		27-Apr-08		12:07:53		68		44		7-Jun-08		12:25:59		73.4		36

		27-Apr-08		14:07:10		71		40		27-Apr-08		14:06:20		69.2		40.5		27-Apr-08		14:07:53		69.2		42.5		7-Jun-08		14:25:59		73.4		34

		27-Apr-08		16:07:10		71		43		27-Apr-08		16:06:20		69.2		47		27-Apr-08		16:07:53		69.2		46		7-Jun-08		16:25:59		73.4		33.5

		27-Apr-08		18:07:10		71		42.5		27-Apr-08		18:06:20		69.2		43.5		27-Apr-08		18:07:53		69.2		44		7-Jun-08		18:25:59		73.4		34

		27-Apr-08		20:07:10		71.6		38		27-Apr-08		20:06:20		68		43.5		27-Apr-08		20:07:53		68.61		42.5		7-Jun-08		20:25:59		74.01		35

		27-Apr-08		22:07:10		71		37.5		27-Apr-08		22:06:20		68		42.5		27-Apr-08		22:07:53		68.61		41		7-Jun-08		22:25:59		74.01		33.5

		28-Apr-08		0:07:10		70.41		38.5		28-Apr-08		0:06:20		68		40		28-Apr-08		0:07:53		68.61		40		8-Jun-08		0:25:59		73.4		33

		28-Apr-08		2:07:10		69.8		39.5		28-Apr-08		2:06:20		68		45		28-Apr-08		2:07:53		68.61		42		8-Jun-08		2:25:59		72.21		33

		28-Apr-08		4:07:10		69.2		39.5		28-Apr-08		4:06:20		67.4		47.5		28-Apr-08		4:07:53		68		41.5		8-Jun-08		4:25:59		71.6		33

		28-Apr-08		6:07:10		69.2		39.5		28-Apr-08		6:06:20		67.4		45		28-Apr-08		6:07:53		68		41.5		8-Jun-08		6:25:59		71.6		33

		28-Apr-08		8:07:10		70.41		40		28-Apr-08		8:06:20		68		47		28-Apr-08		8:07:53		68.61		42.5		8-Jun-08		8:25:59		71.6		33

		28-Apr-08		10:07:10		70.41		40.5		28-Apr-08		10:06:20		68		47.5		28-Apr-08		10:07:53		68.61		43		8-Jun-08		10:25:59		72.21		34

		28-Apr-08		12:07:10		71		40		28-Apr-08		12:06:20		68.61		44		28-Apr-08		12:07:53		69.2		43		8-Jun-08		12:25:59		74.6		33

		28-Apr-08		14:07:10		71		43		28-Apr-08		14:06:20		69.2		43		28-Apr-08		14:07:53		69.2		45.5		8-Jun-08		14:25:59		75.81		31.5

		28-Apr-08		16:07:10		71		44		28-Apr-08		16:06:20		68.61		52		28-Apr-08		16:07:53		69.2		47		8-Jun-08		16:25:59		77		30.5

		28-Apr-08		18:07:10		71		41.5		28-Apr-08		18:06:20		69.2		46		28-Apr-08		18:07:53		68.61		45		8-Jun-08		18:25:59		77		31.5

		28-Apr-08		20:07:10		71		39		28-Apr-08		20:06:20		68.61		45		28-Apr-08		20:07:53		68.61		43		8-Jun-08		20:25:59		77		33.5

		28-Apr-08		22:07:10		71		38.5		28-Apr-08		22:06:20		68.61		43.5		28-Apr-08		22:07:53		68.61		41.5		8-Jun-08		22:25:59		75.81		34.5

		29-Apr-08		0:07:10		69.2		38.5		29-Apr-08		0:06:20		68		45		29-Apr-08		0:07:53		68		41		9-Jun-08		0:25:59		74.6		34

		29-Apr-08		2:07:10		69.8		38		29-Apr-08		2:06:20		67.4		44.5		29-Apr-08		2:07:53		68.61		40.5		9-Jun-08		2:25:59		74.01		34.5

		29-Apr-08		4:07:10		69.8		37.5		29-Apr-08		4:06:20		66.81		44		29-Apr-08		4:07:53		68.61		40		9-Jun-08		4:25:59		72.8		35

		29-Apr-08		6:07:10		69.2		36.5		29-Apr-08		6:06:20		66.2		44		29-Apr-08		6:07:53		68.61		39		9-Jun-08		6:25:59		72.21		35.5

		29-Apr-08		8:07:10		69.8		38.5		29-Apr-08		8:06:20		68		44.5		29-Apr-08		8:07:53		68		41		9-Jun-08		8:25:59		72.21		36.5

		29-Apr-08		10:07:10		70.41		39.5		29-Apr-08		10:06:20		69.8		45		29-Apr-08		10:07:53		68		43		9-Jun-08		10:25:59		74.01		37

		29-Apr-08		12:07:10		71		42		29-Apr-08		12:06:20		70.41		48.5		29-Apr-08		12:07:53		69.2		44.5		9-Jun-08		12:25:59		76.4		36

		29-Apr-08		14:07:10		71		42.5		29-Apr-08		14:06:20		70.41		48		29-Apr-08		14:07:53		68.61		46.5		9-Jun-08		14:25:59		77.61		35

		29-Apr-08		16:07:10		71		43		29-Apr-08		16:06:20		69.8		49		29-Apr-08		16:07:53		68.61		47		9-Jun-08		16:25:59		78.8		34.5

		29-Apr-08		18:07:10		71.6		41.5		29-Apr-08		18:06:20		69.2		48.5		29-Apr-08		18:07:53		68.61		45.5		9-Jun-08		18:25:59		78.2		35.5

		29-Apr-08		20:07:10		71		40		29-Apr-08		20:06:20		69.2		46.5		29-Apr-08		20:07:53		68.61		43.5		9-Jun-08		20:25:59		78.2		35.5

		29-Apr-08		22:07:10		71		39		29-Apr-08		22:06:20		69.2		47.5		29-Apr-08		22:07:53		68.61		42.5		9-Jun-08		22:25:59		76.4		35.5

		30-Apr-08		0:07:10		69.2		33		30-Apr-08		0:06:20		68		34		30-Apr-08		0:07:53		68		35.5		10-Jun-08		0:25:59		74.6		35.5

		30-Apr-08		2:07:10		69.2		35.5		30-Apr-08		2:06:20		68.61		37.5		30-Apr-08		2:07:53		68.61		37.5		10-Jun-08		2:25:59		73.4		36

		30-Apr-08		4:07:10		69.8		35		30-Apr-08		4:06:20		67.4		38.5		30-Apr-08		4:07:53		68.61		37		10-Jun-08		4:25:59		72.8		36

		30-Apr-08		6:07:10		70.41		35		30-Apr-08		6:06:20		69.2		39		30-Apr-08		6:07:53		68.61		38		10-Jun-08		6:25:59		72.21		37

		30-Apr-08		8:07:10		70.41		34		30-Apr-08		8:06:20		69.8		34		30-Apr-08		8:07:53		68		36.5		10-Jun-08		8:25:59		72.8		39

		30-Apr-08		10:07:10		69.2		34		30-Apr-08		10:06:20		69.8		35		30-Apr-08		10:07:53		67.4		37.5		10-Jun-08		10:25:59		73.4		38.5

		30-Apr-08		12:07:10		69.8		32.5		30-Apr-08		12:06:20		69.8		35		30-Apr-08		12:07:53		68		36		10-Jun-08		12:25:59		72.8		39

		30-Apr-08		14:07:10		69.8		33.5		30-Apr-08		14:06:20		69.2		34		30-Apr-08		14:07:53		68.61		36		10-Jun-08		14:25:59		72.8		39

		30-Apr-08		16:07:10		69.8		34		30-Apr-08		16:06:20		69.2		35		30-Apr-08		16:07:53		68.61		36.5		10-Jun-08		16:25:59		72.21		40

		30-Apr-08		18:07:10		69.8		31		30-Apr-08		18:06:20		69.2		32		30-Apr-08		18:07:53		68		33.5		10-Jun-08		18:25:59		72.8		42.5

		30-Apr-08		20:07:10		68.61		31.5		30-Apr-08		20:06:20		68.61		31.5		30-Apr-08		20:07:53		68		33.5		10-Jun-08		20:25:59		74.6		43

		30-Apr-08		22:07:10		69.2		31		30-Apr-08		22:06:20		68.61		32.5		30-Apr-08		22:07:53		68.61		33.5		10-Jun-08		22:25:59		76.4		40.5

		1-May-08		0:07:10		68.61		31.5		1-May-08		0:06:20		67.4		34		1-May-08		0:07:53		68		34		11-Jun-08		0:25:59		75.81		40.5

		1-May-08		2:07:10		68.61		30.5		1-May-08		2:06:20		66.2		33		1-May-08		2:07:53		68		32.5		11-Jun-08		2:25:59		75.2		39

		1-May-08		4:07:10		68		29.5		1-May-08		4:06:20		65.6		32		1-May-08		4:07:53		68		31		11-Jun-08		4:25:59		74.01		38

		1-May-08		6:07:10		68.61		29		1-May-08		6:06:20		65.6		31.5		1-May-08		6:07:53		68		30.5		11-Jun-08		6:25:59		72.8		37.5

		1-May-08		8:07:10		69.2		28		1-May-08		8:06:20		69.2		30		1-May-08		8:07:53		68.61		30.5		11-Jun-08		8:25:59		72.21		37

		1-May-08		10:07:10		69.8		26		1-May-08		10:06:20		70.41		27.5		1-May-08		10:07:53		68.61		29		11-Jun-08		10:25:59		72.8		33

		1-May-08		12:07:10		69.8		24		1-May-08		12:06:20		70.41		24.5		1-May-08		12:07:53		68.61		27		11-Jun-08		12:25:59		72.8		30.5

		1-May-08		14:07:10		70.41		25		1-May-08		14:06:20		71		26		1-May-08		14:07:53		69.8		27		11-Jun-08		14:25:59		74.01		30.5

		1-May-08		16:07:10		71		25.5		1-May-08		16:06:20		69.8		27.5		1-May-08		16:07:53		69.2		27.5		11-Jun-08		16:25:59		74.01		30.5

		1-May-08		18:07:10		70.41		29		1-May-08		18:06:20		70.41		29.5		1-May-08		18:07:53		69.8		30		11-Jun-08		18:25:59		73.4		32

		1-May-08		20:07:10		69.2		29.5		1-May-08		20:06:20		69.2		30		1-May-08		20:07:53		69.2		31		11-Jun-08		20:25:59		74.6		32.5

		1-May-08		22:07:10		69.2		30.5		1-May-08		22:06:20		69.8		30.5		1-May-08		22:07:53		69.2		32		11-Jun-08		22:25:59		75.2		32

		2-May-08		0:07:10		69.8		30.5		2-May-08		0:06:20		68		33		2-May-08		0:07:53		69.2		32.5		12-Jun-08		0:25:59		74.6		32

		2-May-08		2:07:10		69.8		30.5		2-May-08		2:06:20		67.4		33.5		2-May-08		2:07:53		69.2		32		12-Jun-08		2:25:59		73.4		32.5

		2-May-08		4:07:10		69.2		30.5		2-May-08		4:06:20		66.81		34		2-May-08		4:07:53		69.2		31.5		12-Jun-08		4:25:59		72.21		32.5

		2-May-08		6:07:10		69.2		30		2-May-08		6:06:20		66.81		34		2-May-08		6:07:53		69.2		32		12-Jun-08		6:25:59		71.6		32.5

		2-May-08		8:07:10		69.8		30.5		2-May-08		8:06:20		69.2		33		2-May-08		8:07:53		69.8		32		12-Jun-08		8:25:59		72.21		34.5

		2-May-08		10:07:10		69.8		30		2-May-08		10:06:20		69.8		31.5		2-May-08		10:07:53		69.8		31.5		12-Jun-08		10:25:59		73.4		34.5

		2-May-08		12:07:10		70.41		27		2-May-08		12:06:20		69.8		28		2-May-08		12:07:53		70.41		29.5		12-Jun-08		12:25:59		73.4		32.5

		2-May-08		14:07:10		71		23.5		2-May-08		14:06:20		71		25.5		2-May-08		14:07:53		69.8		26		12-Jun-08		14:25:59		72.8		29

		2-May-08		16:07:10		70.41		29.5		2-May-08		16:06:20		69.8		31		2-May-08		16:07:53		69.2		31		12-Jun-08		16:25:59		73.4		27.5

		2-May-08		18:07:10		70.41		30.5		2-May-08		18:06:20		70.41		31.5		2-May-08		18:07:53		69.8		32		12-Jun-08		18:25:59		73.4		29

		2-May-08		20:07:10		71		34		2-May-08		20:06:20		70.41		34		2-May-08		20:07:53		69.8		34		12-Jun-08		20:25:59		74.6		31.5

		2-May-08		22:07:10		70.41		29		2-May-08		22:06:20		70.41		30		2-May-08		22:07:53		70.41		31		12-Jun-08		22:25:59		75.2		32.5

		3-May-08		0:07:10		69.2		30		3-May-08		0:06:20		69.2		31		3-May-08		0:07:53		69.8		31.5		13-Jun-08		0:25:59		74.6		33

		3-May-08		2:07:10		70.41		33		3-May-08		2:06:20		68.61		36		3-May-08		2:07:53		69.8		34		13-Jun-08		2:25:59		73.4		33.5

		3-May-08		4:07:10		70.41		32.5		3-May-08		4:06:20		67.4		36		3-May-08		4:07:53		69.8		33.5		13-Jun-08		4:25:59		72.8		34

		3-May-08		6:07:10		70.41		32		3-May-08		6:06:20		66.81		36.5		3-May-08		6:07:53		69.8		33.5		13-Jun-08		6:25:59		71.6		35

		3-May-08		8:07:10		70.41		33.5		3-May-08		8:06:20		69.8		35.5		3-May-08		8:07:53		69.2		35		13-Jun-08		8:25:59		72.21		37

		3-May-08		10:07:10		70.41		34		3-May-08		10:06:20		70.41		35.5		3-May-08		10:07:53		69.8		35.5		13-Jun-08		10:25:59		72.21		37

		3-May-08		12:07:10		71		33.5		3-May-08		12:06:20		71		34		3-May-08		12:07:53		69.8		34.5		13-Jun-08		12:25:59		72.21		30.5

		3-May-08		14:07:10		71		36.5		3-May-08		14:06:20		71.6		35		3-May-08		14:07:53		69.8		36.5		13-Jun-08		14:25:59		73.4		27.5

		3-May-08		16:07:10		71		34		3-May-08		16:06:20		70.41		35.5		3-May-08		16:07:53		69.8		36.5		13-Jun-08		16:25:59		73.4		30.5

		3-May-08		18:07:10		71		37.5		3-May-08		18:06:20		71		40		3-May-08		18:07:53		69.8		39		13-Jun-08		18:25:59		73.4		28.5

		3-May-08		20:07:10		71		36.5		3-May-08		20:06:20		70.41		40		3-May-08		20:07:53		69.8		38		13-Jun-08		20:25:59		74.6		29

		3-May-08		22:07:10		71		35.5		3-May-08		22:06:20		69.8		39		3-May-08		22:07:53		69.8		37		13-Jun-08		22:25:59		75.81		29.5

		4-May-08		0:07:10		71		35		4-May-08		0:06:20		68		40		4-May-08		0:07:53		69.2		37		14-Jun-08		0:25:59		75.2		30.5

		4-May-08		2:07:10		70.41		35		4-May-08		2:06:20		66.81		41		4-May-08		2:07:53		69.8		36.5		14-Jun-08		2:25:59		74.01		31.5

		4-May-08		4:07:10		70.41		34.5		4-May-08		4:06:20		66.2		41		4-May-08		4:07:53		69.2		35.5		14-Jun-08		4:25:59		72.8		32

		4-May-08		6:07:10		69.8		33.5		4-May-08		6:06:20		65.6		40		4-May-08		6:07:53		69.8		35		14-Jun-08		6:25:59		72.21		33.5

		4-May-08		8:07:10		70.41		35.5		4-May-08		8:06:20		66.81		41.5		4-May-08		8:07:53		70.41		36		14-Jun-08		8:25:59		72.21		35.5

		4-May-08		10:07:10		70.41		36		4-May-08		10:06:20		69.8		39		4-May-08		10:07:53		70.41		37.5		14-Jun-08		10:25:59		72.8		37

		4-May-08		12:07:10		71		37		4-May-08		12:06:20		71		39.5		4-May-08		12:07:53		70.41		39		14-Jun-08		12:25:59		72.8		39.5

		4-May-08		14:07:10		71		39.5		4-May-08		14:06:20		70.41		45.5		4-May-08		14:07:53		68.61		42.5		14-Jun-08		14:25:59		73.4		38

		4-May-08		16:07:10		71		39.5		4-May-08		16:06:20		70.41		44.5		4-May-08		16:07:53		68.61		43.5		14-Jun-08		16:25:59		72.8		38.5

		4-May-08		18:07:10		71		40		4-May-08		18:06:20		69.8		48		4-May-08		18:07:53		69.2		43		14-Jun-08		18:25:59		73.4		38.5

		4-May-08		20:07:10		71		38.5		4-May-08		20:06:20		69.2		47		4-May-08		20:07:53		68.61		42		14-Jun-08		20:25:59		74.01		37

		4-May-08		22:07:10		71		38		4-May-08		22:06:20		69.8		44		4-May-08		22:07:53		68.61		40.5		14-Jun-08		22:25:59		74.01		37.5

		5-May-08		0:07:10		71		37.5		5-May-08		0:06:20		68.61		44		5-May-08		0:07:53		70.41		39.5		15-Jun-08		0:25:59		72.8		37

		5-May-08		2:07:10		71		37		5-May-08		2:06:20		68		44.5		5-May-08		2:07:53		70.41		38.5		15-Jun-08		2:25:59		72.21		37.5

		5-May-08		4:07:10		70.41		36.5		5-May-08		4:06:20		66.81		44.5		5-May-08		4:07:53		69.8		37.5		15-Jun-08		4:25:59		71.6		37.5

		5-May-08		6:07:10		69.8		35		5-May-08		6:06:20		66.2		43		5-May-08		6:07:53		69.8		37		15-Jun-08		6:25:59		71.6		37.5

		5-May-08		8:07:10		69.8		37		5-May-08		8:06:20		66.2		44.5		5-May-08		8:07:53		69.8		37.5		15-Jun-08		8:25:59		72.21		38

		5-May-08		10:07:10		69.8		38		5-May-08		10:06:20		68.61		44		5-May-08		10:07:53		69.8		39		15-Jun-08		10:25:59		72.21		39

		5-May-08		12:07:10		70.41		40		5-May-08		12:06:20		70.41		45		5-May-08		12:07:53		71		40.5		15-Jun-08		12:25:59		73.4		40

		5-May-08		14:07:10		71		40		5-May-08		14:06:20		71		44.5		5-May-08		14:07:53		71		41.5		15-Jun-08		14:25:59		74.6		41

		5-May-08		16:07:10		71		38		5-May-08		16:06:20		69.8		42		5-May-08		16:07:53		70.41		40		15-Jun-08		16:25:59		75.2		41.5

		5-May-08		18:07:10		71		37.5		5-May-08		18:06:20		70.41		41.5		5-May-08		18:07:53		70.41		39		15-Jun-08		18:25:59		75.81		41

		5-May-08		20:07:10		71		37		5-May-08		20:06:20		70.41		41.5		5-May-08		20:07:53		69.8		38.5		15-Jun-08		20:25:59		75.2		40

		5-May-08		22:07:10		70.41		37		5-May-08		22:06:20		69.8		41		5-May-08		22:07:53		69.8		38.5		15-Jun-08		22:25:59		74.01		39.5

		6-May-08		0:07:10		71		36.5		6-May-08		0:06:20		69.2		42		6-May-08		0:07:53		70.41		38		16-Jun-08		0:25:59		72.8		39

		6-May-08		2:07:10		71		36.5		6-May-08		2:06:20		67.4		43		6-May-08		2:07:53		70.41		37.5		16-Jun-08		2:25:59		72.21		39

		6-May-08		4:07:10		70.41		36		6-May-08		4:06:20		66.81		43		6-May-08		4:07:53		69.8		37		16-Jun-08		4:25:59		71.6		39

		6-May-08		6:07:10		69.8		35.5		6-May-08		6:06:20		65.6		43		6-May-08		6:07:53		69.2		37		16-Jun-08		6:25:59		71		39

		6-May-08		8:07:10		70.41		38		6-May-08		8:06:20		68		43.5		6-May-08		8:07:53		68.61		42		16-Jun-08		8:25:59		70.41		39.5

		6-May-08		10:07:10		70.41		39		6-May-08		10:06:20		71		44		6-May-08		10:07:53		67.4		41.5		16-Jun-08		10:25:59		70.41		40.5

		6-May-08		12:07:10		70.41		40.5		6-May-08		12:06:20		71.6		45		6-May-08		12:07:53		67.4		44		16-Jun-08		12:25:59		72.21		41.5

		6-May-08		14:07:10		71		40.5		6-May-08		14:06:20		71		44.5		6-May-08		14:07:53		67.4		44.5		16-Jun-08		14:25:59		73.4		42.5

		6-May-08		16:07:10		71		40		6-May-08		16:06:20		70.41		46.5		6-May-08		16:07:53		68.61		43.5		16-Jun-08		16:25:59		74.6		41

		6-May-08		18:07:10		70.41		39		6-May-08		18:06:20		69.2		45.5		6-May-08		18:07:53		68.61		41		16-Jun-08		18:25:59		75.2		40

		6-May-08		20:07:10		70.41		39.5		6-May-08		20:06:20		68.61		45		6-May-08		20:07:53		68.61		41.5		16-Jun-08		20:25:59		75.2		39

		6-May-08		22:07:10		70.41		38		6-May-08		22:06:20		69.2		44		6-May-08		22:07:53		68.61		41		16-Jun-08		22:25:59		74.01		38.5

		7-May-08		0:07:10		70.41		38.5		7-May-08		0:06:20		68.61		45		7-May-08		0:07:53		68.61		41		17-Jun-08		0:25:59		72.21		38

		7-May-08		2:07:10		70.41		38.5		7-May-08		2:06:20		68		46.5		7-May-08		2:07:53		68		41.5		17-Jun-08		2:25:59		71		37.5

		7-May-08		4:07:10		69.8		38		7-May-08		4:06:20		67.4		47		7-May-08		4:07:53		68.61		40.5		17-Jun-08		4:25:59		70.41		38.5

		7-May-08		6:07:10		70.41		39		7-May-08		6:06:20		66.81		47.5		7-May-08		6:07:53		68		42		17-Jun-08		6:25:59		70.41		39.5

		7-May-08		8:07:10		70.41		39		7-May-08		8:06:20		69.8		45		7-May-08		8:07:53		68.61		41.5		17-Jun-08		8:25:59		70.41		41.5

		7-May-08		10:07:10		71		38.5		7-May-08		10:06:20		70.41		45		7-May-08		10:07:53		68		42		17-Jun-08		10:25:59		71.6		42.5

		7-May-08		12:07:10		71		40.5		7-May-08		12:06:20		70.41		47		7-May-08		12:07:53		68		43.5		17-Jun-08		12:25:59		73.4		42.5

		7-May-08		14:07:10		71		43.5		7-May-08		14:06:20		69.8		51		7-May-08		14:07:53		68.61		46.5		17-Jun-08		14:25:59		74.01		43.5

		7-May-08		16:07:10		71		43		7-May-08		16:06:20		70.41		56		7-May-08		16:07:53		68.61		46.5		17-Jun-08		16:25:59		74.6		41

		7-May-08		18:07:10		70.41		43.5		7-May-08		18:06:20		71		50		7-May-08		18:07:53		68		46.5		17-Jun-08		18:25:59		74.01		40

		7-May-08		20:07:10		71		36.5		7-May-08		20:06:20		70.41		39		7-May-08		20:07:53		68		41		17-Jun-08		20:25:59		74.01		39.5

		7-May-08		22:07:10		71		34.5		7-May-08		22:06:20		69.8		36		7-May-08		22:07:53		68		38		17-Jun-08		22:25:59		74.01		38.5

		8-May-08		0:07:10		69.8		37		8-May-08		0:06:20		69.8		40.5		8-May-08		0:07:53		68		40		18-Jun-08		0:25:59		72.8		38

		8-May-08		2:07:10		70.41		37		8-May-08		2:06:20		68.61		41		8-May-08		2:07:53		69.2		39		18-Jun-08		2:25:59		71.6		37.5

		8-May-08		4:07:10		70.41		36		8-May-08		4:06:20		68		41.5		8-May-08		4:07:53		69.8		37.5		18-Jun-08		4:25:59		70.41		38.5

		8-May-08		6:07:10		71		34.5		8-May-08		6:06:20		68		39.5		8-May-08		6:07:53		68.61		38		18-Jun-08		6:25:59		70.41		39.5

		8-May-08		8:07:10		71		34.5		8-May-08		8:06:20		69.8		37		8-May-08		8:07:53		68.61		38		18-Jun-08		8:25:59		70.41		41.5

		8-May-08		10:07:10		70.41		36		8-May-08		10:06:20		70.41		38.5		8-May-08		10:07:53		68.61		38		18-Jun-08		10:25:59		72.8		42

		8-May-08		12:07:10		70.41		37		8-May-08		12:06:20		71		38.5		8-May-08		12:07:53		67.4		40.5		18-Jun-08		12:25:59		72.8		41.5

		8-May-08		14:07:10		70.41		39		8-May-08		14:06:20		71		41		8-May-08		14:07:53		67.4		43		18-Jun-08		14:25:59		72.8		42.5

		8-May-08		16:07:10		71		38.5		8-May-08		16:06:20		70.41		43		8-May-08		16:07:53		68		41.5		18-Jun-08		16:25:59		73.4		43

		8-May-08		18:07:10		71		39		8-May-08		18:06:20		71		41.5		8-May-08		18:07:53		68.61		42		18-Jun-08		18:25:59		74.01		34.5

		8-May-08		20:07:10		71		38		8-May-08		20:06:20		70.41		43.5		8-May-08		20:07:53		68		41.5		18-Jun-08		20:25:59		74.6		32

		8-May-08		22:07:10		70.41		37		8-May-08		22:06:20		69.8		41		8-May-08		22:07:53		68		40		18-Jun-08		22:25:59		74.6		30.5

		9-May-08		0:07:10		70.41		37		9-May-08		0:06:20		68.61		41.5		9-May-08		0:07:53		68		40		19-Jun-08		0:25:59		74.01		30.5

		9-May-08		2:07:10		70.41		36.5		9-May-08		2:06:20		67.4		42		9-May-08		2:07:53		68.61		39		19-Jun-08		2:25:59		73.4		31.5

		9-May-08		4:07:10		69.8		35.5		9-May-08		4:06:20		66.81		42.5		9-May-08		4:07:53		69.2		38		19-Jun-08		4:25:59		72.21		33

		9-May-08		6:07:10		71		35.5		9-May-08		6:06:20		66.81		41.5		9-May-08		6:07:53		69.2		37.5		19-Jun-08		6:25:59		71		33.5

		9-May-08		8:07:10		71		37		9-May-08		8:06:20		69.8		42		9-May-08		8:07:53		69.2		39		19-Jun-08		8:25:59		71		35.5

		9-May-08		10:07:10		70.41		38		9-May-08		10:06:20		71		40.5		9-May-08		10:07:53		68.61		40		19-Jun-08		10:25:59		72.8		35.5

		9-May-08		12:07:10		70.41		40		9-May-08		12:06:20		71.6		43		9-May-08		12:07:53		69.2		41.5		19-Jun-08		12:25:59		73.4		33.5

		9-May-08		14:07:10		70.41		39		9-May-08		14:06:20		69.8		45.5		9-May-08		14:07:53		68		42.5		19-Jun-08		14:25:59		72.21		35.5

		9-May-08		16:07:10		70.41		38		9-May-08		16:06:20		69.2		43		9-May-08		16:07:53		67.4		42.5		19-Jun-08		16:25:59		72.21		33.5

		9-May-08		18:07:10		70.41		38.5		9-May-08		18:06:20		68.61		42.5		9-May-08		18:07:53		68.61		41.5		19-Jun-08		18:25:59		74.01		28.5

		9-May-08		20:07:10		70.41		37		9-May-08		20:06:20		68.61		42		9-May-08		20:07:53		68		40		19-Jun-08		20:25:59		74.6		29

		9-May-08		22:07:10		69.8		36.5		9-May-08		22:06:20		68		41.5		9-May-08		22:07:53		68.61		39		19-Jun-08		22:25:59		75.2		27.5

		10-May-08		0:07:10		69.8		35.5		10-May-08		0:06:20		68		40.5		10-May-08		0:07:53		68		39		20-Jun-08		0:25:59		74.6		30

		10-May-08		2:07:10		69.8		34.5		10-May-08		2:06:20		66.81		40.5		10-May-08		2:07:53		68		37.5		20-Jun-08		2:25:59		73.4		31

		10-May-08		4:07:10		69.8		34		10-May-08		4:06:20		66.2		40.5		10-May-08		4:07:53		68.61		37		20-Jun-08		4:25:59		72.8		31.5

		10-May-08		6:07:10		70.41		33.5		10-May-08		6:06:20		65.6		39.5		10-May-08		6:07:53		68.61		35.5		20-Jun-08		6:25:59		71.6		32.5

		10-May-08		8:07:10		70.41		35.5		10-May-08		8:06:20		68		41.5		10-May-08		8:07:53		67.4		38.5		20-Jun-08		8:25:59		72.21		35

		10-May-08		10:07:10		69.8		34		10-May-08		10:06:20		70.41		35		10-May-08		10:07:53		68		37.5		20-Jun-08		10:25:59		73.4		36.5

		10-May-08		12:07:10		71		33.5		10-May-08		12:06:20		71		34.5		10-May-08		12:07:53		68.61		36.5		20-Jun-08		12:25:59		72.8		35

		10-May-08		14:07:10		71.6		32		10-May-08		14:06:20		70.41		34.5		10-May-08		14:07:53		68		35.5		20-Jun-08		14:25:59		72.8		33.5

		10-May-08		16:07:10		71.6		35		10-May-08		16:06:20		69.8		38.5		10-May-08		16:07:53		67.4		40.5		20-Jun-08		16:25:59		72.8		34

		10-May-08		18:07:10		71.6		36		10-May-08		18:06:20		69.2		39.5		10-May-08		18:07:53		67.4		41.5		20-Jun-08		18:25:59		72.8		31

		10-May-08		20:07:10		71		35.5		10-May-08		20:06:20		68.61		40.5		10-May-08		20:07:53		68		39.5		20-Jun-08		20:25:59		74.6		31.5

		10-May-08		22:07:10		70.41		35.5		10-May-08		22:06:20		68.61		39.5		10-May-08		22:07:53		68		38.5		20-Jun-08		22:25:59		75.81		30.5

		11-May-08		0:07:10		70.41		35.5		11-May-08		0:06:20		68.61		39.5		11-May-08		0:07:53		68		38.5		21-Jun-08		0:25:59		75.2		31.5

		11-May-08		2:07:10		70.41		35		11-May-08		2:06:20		67.4		40		11-May-08		2:07:53		68		38		21-Jun-08		2:25:59		74.01		32

		11-May-08		4:07:10		69.8		34		11-May-08		4:06:20		66.81		40.5		11-May-08		4:07:53		68.61		37		21-Jun-08		4:25:59		73.4		32.5

		11-May-08		6:07:10		70.41		34.5		11-May-08		6:06:20		68		39		11-May-08		6:07:53		68.61		36.5		21-Jun-08		6:25:59		72.21		34

		11-May-08		8:07:10		70.41		35.5		11-May-08		8:06:20		69.8		39		11-May-08		8:07:53		68		38.5		21-Jun-08		8:25:59		72.8		35.5

		11-May-08		10:07:10		70.41		35		11-May-08		10:06:20		69.8		36.5		11-May-08		10:07:53		68.61		37.5		21-Jun-08		10:25:59		72.8		35.5

		11-May-08		12:07:10		71		35.5		11-May-08		12:06:20		70.41		38		11-May-08		12:07:53		68.61		39		21-Jun-08		12:25:59		72.8		33.5

		11-May-08		14:07:10		71.6		38		11-May-08		14:06:20		69.2		41		11-May-08		14:07:53		68.61		41.5		21-Jun-08		14:25:59		72.8		32

		11-May-08		16:07:10		71.6		37.5		11-May-08		16:06:20		68.61		40		11-May-08		16:07:53		68.61		40.5		21-Jun-08		16:25:59		73.4		30

		11-May-08		18:07:10		71.6		38.5		11-May-08		18:06:20		69.2		44		11-May-08		18:07:53		68.61		42.5		21-Jun-08		18:25:59		71.6		27

		11-May-08		20:07:10		71.6		39		11-May-08		20:06:20		69.2		50		11-May-08		20:07:53		68.61		43.5		21-Jun-08		20:25:59		74.01		26.5

		11-May-08		22:07:10		71		38.5		11-May-08		22:06:20		68.61		46.5		11-May-08		22:07:53		69.2		41.5		21-Jun-08		22:25:59		75.81		25.5

		12-May-08		0:07:10		69.8		38.5		12-May-08		0:06:20		68.61		47.5		12-May-08		0:07:53		69.2		41		22-Jun-08		0:25:59		75.81		27.5

		12-May-08		2:07:10		70.41		39		12-May-08		2:06:20		68.61		47.5		12-May-08		2:07:53		69.8		41		22-Jun-08		2:25:59		75.2		29

		12-May-08		4:07:10		70.41		38		12-May-08		4:06:20		68		47		12-May-08		4:07:53		69.8		40		22-Jun-08		4:25:59		74.01		29.5

		12-May-08		6:07:10		71		38		12-May-08		6:06:20		67.4		47		12-May-08		6:07:53		69.8		40		22-Jun-08		6:25:59		74.6		30

		12-May-08		8:07:10		71		38.5		12-May-08		8:06:20		67.4		47.5		12-May-08		8:07:53		69.8		40.5		22-Jun-08		8:25:59		75.2		30.5

		12-May-08		10:07:10		70.41		39		12-May-08		10:06:20		68.61		45		12-May-08		10:07:53		69.8		40.5		22-Jun-08		10:25:59		77		31

		12-May-08		12:07:10		70.41		40		12-May-08		12:06:20		69.2		44.5		12-May-08		12:07:53		69.8		41.5		22-Jun-08		12:25:59		78.2		29.5

		12-May-08		14:07:10		71		33		12-May-08		14:06:20		69.2		32		12-May-08		14:07:53		69.8		34.5		22-Jun-08		14:25:59		79.41		28.5

		12-May-08		16:07:10		71		29.5		12-May-08		16:06:20		69.8		29.5		12-May-08		16:07:53		69.8		31		22-Jun-08		16:25:59		79.41		27

		12-May-08		18:07:10		71.6		31.5		12-May-08		18:06:20		69.8		33		12-May-08		18:07:53		69.8		33		22-Jun-08		18:25:59		78.8		25

		12-May-08		20:07:10		71.6		30.5		12-May-08		20:06:20		69.2		33		12-May-08		20:07:53		69.8		33		22-Jun-08		20:25:59		78.8		25

		12-May-08		22:07:10		70.41		30.5		12-May-08		22:06:20		68		33		12-May-08		22:07:53		69.8		32.5		22-Jun-08		22:25:59		77.61		27

		13-May-08		0:07:10		68.61		31		13-May-08		0:06:20		68.61		32.5		13-May-08		0:07:53		68.61		32.5		23-Jun-08		0:25:59		76.4		29

		13-May-08		2:07:10		68		32		13-May-08		2:06:20		68		33		13-May-08		2:07:53		68		33		23-Jun-08		2:25:59		75.2		31

		13-May-08		4:07:10		68		31.5		13-May-08		4:06:20		68.61		32		13-May-08		4:07:53		68		32.5		23-Jun-08		4:25:59		74.01		32

		13-May-08		6:07:10		68		30.5		13-May-08		6:06:20		68.61		31		13-May-08		6:07:53		68		32		23-Jun-08		6:25:59		73.4		32.5

		13-May-08		8:07:10		68.61		29		13-May-08		8:06:20		69.2		31		13-May-08		8:07:53		68.61		31.5		23-Jun-08		8:25:59		72.8		34

		13-May-08		10:07:10		69.8		28		13-May-08		10:06:20		70.41		29.5		13-May-08		10:07:53		68.61		30.5		23-Jun-08		10:25:59		74.01		35.5

		13-May-08		12:07:10		71		27.5		13-May-08		12:06:20		71.6		29		13-May-08		12:07:53		68.61		30.5		23-Jun-08		12:25:59		75.2		35.5

		13-May-08		14:07:10		71.6		28.5		13-May-08		14:06:20		71		30		13-May-08		14:07:53		68.61		31.5		23-Jun-08		14:25:59		76.4		36

		13-May-08		16:07:10		71.6		29.5		13-May-08		16:06:20		69.2		32.5		13-May-08		16:07:53		68.61		33		23-Jun-08		16:25:59		77		36

		13-May-08		18:07:10		71.6		30.5		13-May-08		18:06:20		70.41		33		13-May-08		18:07:53		68.61		34.5		23-Jun-08		18:25:59		77.61		35.5

		13-May-08		20:07:10		71		30		13-May-08		20:06:20		69.8		31.5		13-May-08		20:07:53		68		33.5		23-Jun-08		20:25:59		77.61		34.5

		13-May-08		22:07:10		70.41		30.5		13-May-08		22:06:20		70.41		31.5		13-May-08		22:07:53		68.61		33		23-Jun-08		22:25:59		75.81		34.5

		14-May-08		0:07:10		69.2		31		14-May-08		0:06:20		69.8		32		14-May-08		0:07:53		68		33.5		24-Jun-08		0:25:59		74.6		34.5

		14-May-08		2:07:10		68		32.5		14-May-08		2:06:20		69.2		33.5		14-May-08		2:07:53		68		34.5		24-Jun-08		2:25:59		73.4		34.5

		14-May-08		4:07:10		68		33		14-May-08		4:06:20		69.2		34		14-May-08		4:07:53		68		34.5		24-Jun-08		4:25:59		72.21		34.5

		14-May-08		6:07:10		68.61		33		14-May-08		6:06:20		69.2		34		14-May-08		6:07:53		68		35		24-Jun-08		6:25:59		71		36.5

		14-May-08		8:07:10		69.2		34		14-May-08		8:06:20		70.41		36.5		14-May-08		8:07:53		68		36		24-Jun-08		8:25:59		71		39

		14-May-08		10:07:10		71		34		14-May-08		10:06:20		71		36		14-May-08		10:07:53		67.4		38		24-Jun-08		10:25:59		72.21		40.5

		14-May-08		12:07:10		71.6		28.5		14-May-08		12:06:20		70.41		31.5		14-May-08		12:07:53		68		33		24-Jun-08		12:25:59		72.21		41.5

		14-May-08		14:07:10		71.6		29.5		14-May-08		14:06:20		70.41		32		14-May-08		14:07:53		68		34		24-Jun-08		14:25:59		73.4		39.5

		14-May-08		16:07:10		71.6		26.5		14-May-08		16:06:20		71		28		14-May-08		16:07:53		68		30		24-Jun-08		16:25:59		74.01		39

		14-May-08		18:07:10		71.6		27.5		14-May-08		18:06:20		71		28		14-May-08		18:07:53		68		30.5		24-Jun-08		18:25:59		74.01		38.5

		14-May-08		20:07:10		71.6		35		14-May-08		20:06:20		70.41		39.5		14-May-08		20:07:53		68		39.5		24-Jun-08		20:25:59		74.01		39.5

		14-May-08		22:07:10		71		36		14-May-08		22:06:20		69.8		41		14-May-08		22:07:53		68		40		24-Jun-08		22:25:59		75.2		37

		15-May-08		0:07:10		70.41		36.5		15-May-08		0:06:20		69.8		41		15-May-08		0:07:53		68.61		39.5		25-Jun-08		0:25:59		73.4		37

		15-May-08		2:07:10		69.8		37		15-May-08		2:06:20		69.2		42		15-May-08		2:07:53		68.61		39.5		25-Jun-08		2:25:59		72.21		37

		15-May-08		4:07:10		69.8		38		15-May-08		4:06:20		69.8		42.5		15-May-08		4:07:53		69.2		40.5		25-Jun-08		4:25:59		71		37

		15-May-08		6:07:10		70.41		39		15-May-08		6:06:20		69.8		42.5		15-May-08		6:07:53		68.61		41		25-Jun-08		6:25:59		70.41		38

		15-May-08		8:07:10		71		40		15-May-08		8:06:20		70.41		48.5		15-May-08		8:07:53		68		43.5		25-Jun-08		8:25:59		70.41		40.5

		15-May-08		10:07:10		71.6		40.5		15-May-08		10:06:20		71		46		15-May-08		10:07:53		67.4		46.5		25-Jun-08		10:25:59		72.8		41.5

		15-May-08		12:07:10		71.6		40.5		15-May-08		12:06:20		70.41		46.5		15-May-08		12:07:53		68		46.5		25-Jun-08		12:25:59		73.4		41

		15-May-08		14:07:10		71.6		38		15-May-08		14:06:20		69.8		41		15-May-08		14:07:53		68		43		25-Jun-08		14:25:59		72.8		42

		15-May-08		16:07:10		71.6		37.5		15-May-08		16:06:20		69.8		40.5		15-May-08		16:07:53		68		42.5		25-Jun-08		16:25:59		72.8		41.5

		15-May-08		18:07:10		71.6		39		15-May-08		18:06:20		68.61		42.5		15-May-08		18:07:53		69.2		43		25-Jun-08		18:25:59		74.01		39.5

		15-May-08		20:07:10		71.6		39		15-May-08		20:06:20		68.61		44		15-May-08		20:07:53		68.61		43.5		25-Jun-08		20:25:59		74.01		41

		15-May-08		22:07:10		71.6		37.5		15-May-08		22:06:20		68		44		15-May-08		22:07:53		68.61		42		25-Jun-08		22:25:59		74.6		38.5

		16-May-08		0:07:10		72.21		37		16-May-08		0:06:20		68		42.5		16-May-08		0:07:53		68.61		41.5		26-Jun-08		0:25:59		74.01		37.5

		16-May-08		2:07:10		71.6		37		16-May-08		2:06:20		68		43		16-May-08		2:07:53		69.2		40.5		26-Jun-08		2:25:59		72.8		37.5

		16-May-08		4:07:10		71.6		36.5		16-May-08		4:06:20		68		43		16-May-08		4:07:53		69.2		40.5		26-Jun-08		4:25:59		71.6		38

		16-May-08		6:07:10		71.6		36		16-May-08		6:06:20		68.61		42		16-May-08		6:07:53		69.2		39.5		26-Jun-08		6:25:59		71		38.5

		16-May-08		8:07:10		72.21		36.5		16-May-08		8:06:20		69.8		42		16-May-08		8:07:53		68.61		41		26-Jun-08		8:25:59		71		40.5

		16-May-08		10:07:10		71.6		38		16-May-08		10:06:20		69.2		43		16-May-08		10:07:53		68		43		26-Jun-08		10:25:59		73.4		40.5

		16-May-08		12:07:10		71.6		39.5		16-May-08		12:06:20		70.41		43.5		16-May-08		12:07:53		68		44		26-Jun-08		12:25:59		72.21		43

		16-May-08		14:07:10		71.6		39		16-May-08		14:06:20		70.41		43		16-May-08		14:07:53		68		44		26-Jun-08		14:25:59		72.21		44

		16-May-08		16:07:10		71.6		40		16-May-08		16:06:20		69.2		46		16-May-08		16:07:53		68.61		45		26-Jun-08		16:25:59		72.21		43.5

		16-May-08		18:07:10		71.6		40.5		16-May-08		18:06:20		69.2		45		16-May-08		18:07:53		68.61		45		26-Jun-08		18:25:59		71.6		43

		16-May-08		20:07:10		71.6		42		16-May-08		20:06:20		69.2		48.5		16-May-08		20:07:53		69.2		46.5		26-Jun-08		20:25:59		72.8		40.5

		16-May-08		22:07:10		72.21		41		16-May-08		22:06:20		68.61		54.5		16-May-08		22:07:53		68		46.5		26-Jun-08		22:25:59		73.4		40.5

		17-May-08		0:07:10		72.21		39.5		17-May-08		0:06:20		68.61		50		17-May-08		0:07:53		68.61		44.5		27-Jun-08		0:25:59		72.8		39.5

		17-May-08		2:07:10		72.21		39		17-May-08		2:06:20		68.61		47		17-May-08		2:07:53		68.61		43.5		27-Jun-08		2:25:59		71.6		39

		17-May-08		4:07:10		71.6		39		17-May-08		4:06:20		68		51		17-May-08		4:07:53		68.61		43		27-Jun-08		4:25:59		71		39

		17-May-08		6:07:10		71.6		39		17-May-08		6:06:20		68.61		53		17-May-08		6:07:53		69.2		43		27-Jun-08		6:25:59		70.41		39.5

		17-May-08		8:07:10		72.21		40		17-May-08		8:06:20		69.8		55.5		17-May-08		8:07:53		68		45.5		27-Jun-08		8:25:59		70.41		41

		17-May-08		10:07:10		72.21		40.5		17-May-08		10:06:20		69.8		53.5		17-May-08		10:07:53		68		46		27-Jun-08		10:25:59		72.8		42.5

		17-May-08		12:07:10		71		44.5		17-May-08		12:06:20		69.8		50		17-May-08		12:07:53		68.61		49.5		27-Jun-08		12:25:59		72.21		43

		17-May-08		14:07:10		71.6		45		17-May-08		14:06:20		70.41		52.5		17-May-08		14:07:53		68		51		27-Jun-08		14:25:59		72.21		44.5

		17-May-08		16:07:10		71.6		44.5		17-May-08		16:06:20		69.8		51		17-May-08		16:07:53		68.61		49.5		27-Jun-08		16:25:59		72.8		44

		17-May-08		18:07:10		71.6		41.5		17-May-08		18:06:20		69.2		45.5		17-May-08		18:07:53		68.61		45.5		27-Jun-08		18:25:59		72.8		41

		17-May-08		20:07:10		71.6		41.5		17-May-08		20:06:20		68.61		49		17-May-08		20:07:53		68.61		46		27-Jun-08		20:25:59		73.4		41.5

		17-May-08		22:07:10		72.21		39.5		17-May-08		22:06:20		69.2		48		17-May-08		22:07:53		68		44.5		27-Jun-08		22:25:59		74.01		40

		18-May-08		0:07:10		72.21		39		18-May-08		0:06:20		68		50.5		18-May-08		0:07:53		68.61		43.5		28-Jun-08		0:25:59		73.4		39.5

		18-May-08		2:07:10		71.6		40		18-May-08		2:06:20		68		52		18-May-08		2:07:53		68.61		43.5		28-Jun-08		2:25:59		72.21		39.5

		18-May-08		4:07:10		71		40		18-May-08		4:06:20		68		52.5		18-May-08		4:07:53		69.2		43		28-Jun-08		4:25:59		71.6		39.5

		18-May-08		6:07:10		70.41		39.5		18-May-08		6:06:20		68		50.5		18-May-08		6:07:53		69.2		42		28-Jun-08		6:25:59		71		40

		18-May-08		8:07:10		71		40.5		18-May-08		8:06:20		68.61		53.5		18-May-08		8:07:53		68.61		44		28-Jun-08		8:25:59		71		42

		18-May-08		10:07:10		71.6		42.5		18-May-08		10:06:20		69.2		56.5		18-May-08		10:07:53		68.61		46.5		28-Jun-08		10:25:59		73.4		43

		18-May-08		12:07:10		71.6		44.5		18-May-08		12:06:20		69.2		53.5		18-May-08		12:07:53		68.61		49.5		28-Jun-08		12:25:59		72.8		44

		18-May-08		14:07:10		72.21		48.5		18-May-08		14:06:20		69.2		58.5		18-May-08		14:07:53		68.61		54		28-Jun-08		14:25:59		72.21		45

		18-May-08		16:07:10		72.21		45		18-May-08		16:06:20		68.61		63.5		18-May-08		16:07:53		68.61		51.5		28-Jun-08		16:25:59		72.8		45.5

		18-May-08		18:07:10		72.21		43		18-May-08		18:06:20		68.61		60.5		18-May-08		18:07:53		68.61		49.5		28-Jun-08		18:25:59		72.8		43.5

		18-May-08		20:07:10		72.21		40.5		18-May-08		20:06:20		68.61		52.5		18-May-08		20:07:53		68		46		28-Jun-08		20:25:59		72.8		43.5

		18-May-08		22:07:10		72.21		39		18-May-08		22:06:20		68		51.5		18-May-08		22:07:53		68.61		43.5		28-Jun-08		22:25:59		72.8		42.5

		19-May-08		0:07:10		71		39		19-May-08		0:06:20		68		49.5		19-May-08		0:07:53		69.2		42		29-Jun-08		0:25:59		72.21		42.5

		19-May-08		2:07:10		70.41		39.5		19-May-08		2:06:20		68		49		19-May-08		2:07:53		69.2		42		29-Jun-08		2:25:59		71.6		42.5

		19-May-08		4:07:10		70.41		39		19-May-08		4:06:20		67.4		48		19-May-08		4:07:53		69.2		41.5		29-Jun-08		4:25:59		71		43

		19-May-08		6:07:10		71		39		19-May-08		6:06:20		67.4		49		19-May-08		6:07:53		69.2		41.5		29-Jun-08		6:25:59		71		43.5

		19-May-08		8:07:10		71		39.5		19-May-08		8:06:20		68		49		19-May-08		8:07:53		69.2		42		29-Jun-08		8:25:59		71		44

		19-May-08		10:07:10		70.41		40.5		19-May-08		10:06:20		68		48.5		19-May-08		10:07:53		69.2		43		29-Jun-08		10:25:59		71.6		44.5

		19-May-08		12:07:10		71		41.5		19-May-08		12:06:20		68.61		51		19-May-08		12:07:53		69.2		44.5		29-Jun-08		12:25:59		72.21		45.5

		19-May-08		14:07:10		71.6		41.5		19-May-08		14:06:20		68		54.5		19-May-08		14:07:53		69.8		45		29-Jun-08		14:25:59		74.01		45.5

		19-May-08		16:07:10		72.21		42		19-May-08		16:06:20		68.61		51.5		19-May-08		16:07:53		69.2		46		29-Jun-08		16:25:59		75.2		44.5

		19-May-08		18:07:10		72.21		40		19-May-08		18:06:20		68		55		19-May-08		18:07:53		69.2		44.5		29-Jun-08		18:25:59		75.81		43.5

		19-May-08		20:07:10		72.21		39		19-May-08		20:06:20		68.61		50.5		19-May-08		20:07:53		69.2		43		29-Jun-08		20:25:59		75.2		43

		19-May-08		22:07:10		71		39		19-May-08		22:06:20		67.4		52.5		19-May-08		22:07:53		69.2		42		29-Jun-08		22:25:59		74.01		42.5

		20-May-08		0:07:10		71		39.5		20-May-08		0:06:20		67.4		51		20-May-08		0:07:53		69.2		42		30-Jun-08		0:25:59		72.21		42.5

		20-May-08		2:07:10		71		39.5		20-May-08		2:06:20		68		50		20-May-08		2:07:53		69.2		42		30-Jun-08		2:25:59		71.6		42.5

		20-May-08		4:07:10		70.41		39.5		20-May-08		4:06:20		67.4		49.5		20-May-08		4:07:53		69.2		41.5		30-Jun-08		4:25:59		71		42.5

		20-May-08		6:07:10		71		39.5		20-May-08		6:06:20		68		49.5		20-May-08		6:07:53		69.2		41.5		30-Jun-08		6:25:59		70.41		43

		20-May-08		8:07:10		71		39		20-May-08		8:06:20		68.61		50.5		20-May-08		8:07:53		68.61		44		30-Jun-08		8:25:59		70.41		43.5

		20-May-08		10:07:10		71		39		20-May-08		10:06:20		71		44.5		20-May-08		10:07:53		68.61		43		30-Jun-08		10:25:59		70.41		44

		20-May-08		12:07:10		71		41		20-May-08		12:06:20		71		49.5		20-May-08		12:07:53		68		45		30-Jun-08		12:25:59		72.21		44.5

		20-May-08		14:07:10		71		43		20-May-08		14:06:20		71		55.5		20-May-08		14:07:53		68		48		30-Jun-08		14:25:59		73.4		44.5

		20-May-08		16:07:10		71.6		42		20-May-08		16:06:20		70.41		49.5		20-May-08		16:07:53		68.61		46.5		30-Jun-08		16:25:59		74.6		44.5

		20-May-08		18:07:10		71.6		41		20-May-08		18:06:20		69.8		51		20-May-08		18:07:53		69.2		44.5		30-Jun-08		18:25:59		75.2		43

		20-May-08		20:07:10		71		39		20-May-08		20:06:20		69.8		48.5		20-May-08		20:07:53		69.2		42.5		30-Jun-08		20:25:59		75.2		42.5

		20-May-08		22:07:10		71		39.5		20-May-08		22:06:20		69.8		48		20-May-08		22:07:53		69.8		41.5		30-Jun-08		22:25:59		73.4		42

		21-May-08		0:07:10		70.41		40		21-May-08		0:06:20		69.2		48.5		21-May-08		0:07:53		69.2		42		1-Jul-08		0:25:59		72.21		42

		21-May-08		2:07:10		70.41		40		21-May-08		2:06:20		68.61		48.5		21-May-08		2:07:53		69.8		42		1-Jul-08		2:25:59		71.6		42

		21-May-08		4:07:10		71		39.5		21-May-08		4:06:20		68.61		48		21-May-08		4:07:53		69.2		41.5		1-Jul-08		4:25:59		71		42

		21-May-08		6:07:10		71		39.5		21-May-08		6:06:20		68		48.5		21-May-08		6:07:53		69.8		41		1-Jul-08		6:25:59		71		43

		21-May-08		8:07:10		71		39.5		21-May-08		8:06:20		70.41		48.5		21-May-08		8:07:53		68.61		42		1-Jul-08		8:25:59		70.41		45

		21-May-08		10:07:10		71		40		21-May-08		10:06:20		71		47		21-May-08		10:07:53		68		43		1-Jul-08		10:25:59		72.21		45

		21-May-08		12:07:10		71		41		21-May-08		12:06:20		71		51		21-May-08		12:07:53		68.61		44.5		1-Jul-08		12:25:59		72.21		45

		21-May-08		14:07:10		71		44		21-May-08		14:06:20		71.6		54		21-May-08		14:07:53		68		48.5		1-Jul-08		14:25:59		72.8		46.5

		21-May-08		16:07:10		71		39.5		21-May-08		16:06:20		71		45		21-May-08		16:07:53		69.2		43.5		1-Jul-08		16:25:59		72.8		46.5

		21-May-08		18:07:10		71.6		32		21-May-08		18:06:20		71		34		21-May-08		18:07:53		69.2		36.5		1-Jul-08		18:25:59		72.8		44.5

		21-May-08		20:07:10		71		30		21-May-08		20:06:20		70.41		30		21-May-08		20:07:53		69.8		31.5		1-Jul-08		20:25:59		74.01		42

		21-May-08		22:07:10		70.41		36		21-May-08		22:06:20		70.41		39		21-May-08		22:07:53		69.8		38		1-Jul-08		22:25:59		74.01		43.5

		22-May-08		0:07:10		69.2		35		22-May-08		0:06:20		69.2		37.5		22-May-08		0:07:53		68.61		37		2-Jul-08		0:25:59		73.4		43

		22-May-08		2:07:10		68.61		34.5		22-May-08		2:06:20		69.2		35.5		22-May-08		2:07:53		68.61		36.5		2-Jul-08		2:25:59		72.21		43

		22-May-08		4:07:10		68.61		34		22-May-08		4:06:20		69.2		35		22-May-08		4:07:53		68.61		35		2-Jul-08		4:25:59		72.21		43.5

		22-May-08		6:07:10		69.8		32.5		22-May-08		6:06:20		69.2		34.5		22-May-08		6:07:53		69.2		34.5		2-Jul-08		6:25:59		71.6		44.5

		22-May-08		8:07:10		69.8		32.5		22-May-08		8:06:20		71		34.5		22-May-08		8:07:53		68.61		35		2-Jul-08		8:25:59		71		46.5

		22-May-08		10:07:10		70.41		33.5		22-May-08		10:06:20		71.6		34		22-May-08		10:07:53		68.61		35.5		2-Jul-08		10:25:59		72.21		47.5

		22-May-08		12:07:10		71		33.5		22-May-08		12:06:20		70.41		35.5		22-May-08		12:07:53		69.2		36		2-Jul-08		12:25:59		72.21		46.5

		22-May-08		14:07:10		71		34.5		22-May-08		14:06:20		69.8		37		22-May-08		14:07:53		68.61		38		2-Jul-08		14:25:59		72.21		47.5

		22-May-08		16:07:10		71		35		22-May-08		16:06:20		69.2		38		22-May-08		16:07:53		68.61		38.5		2-Jul-08		16:25:59		72.8		45.5

		22-May-08		18:07:10		71		35		22-May-08		18:06:20		68.61		37.5		22-May-08		18:07:53		68		38		2-Jul-08		18:25:59		72.8		44.5

		22-May-08		20:07:10		70.41		34.5		22-May-08		20:06:20		68.61		37		22-May-08		20:07:53		68		37		2-Jul-08		20:25:59		73.4		42.5

		22-May-08		22:07:10		69.2		33.5		22-May-08		22:06:20		68		36.5		22-May-08		22:07:53		68.61		36		2-Jul-08		22:25:59		74.01		43

		23-May-08		0:07:10		68.61		33.5		23-May-08		0:06:20		68		36		23-May-08		0:07:53		68		35.5		3-Jul-08		0:25:59		72.8		42.5

		23-May-08		2:07:10		68		32.5		23-May-08		2:06:20		68		34.5		23-May-08		2:07:53		68		34.5		3-Jul-08		2:25:59		71.6		42

		23-May-08		4:07:10		68.61		31		23-May-08		4:06:20		68		32.5		23-May-08		4:07:53		68.61		33		3-Jul-08		4:25:59		71		42.5

		23-May-08		6:07:10		69.8		30		23-May-08		6:06:20		68		32		23-May-08		6:07:53		69.2		32		3-Jul-08		6:25:59		70.41		43

		23-May-08		8:07:10		69.8		30		23-May-08		8:06:20		68.61		33		23-May-08		8:07:53		69.2		32		3-Jul-08		8:25:59		71		44.5

		23-May-08		10:07:10		70.41		30		23-May-08		10:06:20		68.61		32.5		23-May-08		10:07:53		68		32		3-Jul-08		10:25:59		72.21		45

		23-May-08		12:07:10		71		25		23-May-08		12:06:20		69.2		27.5		23-May-08		12:07:53		68		28.5		3-Jul-08		12:25:59		71.6		46.5

		23-May-08		14:07:10		71		28.5		23-May-08		14:06:20		68.61		30		23-May-08		14:07:53		67.4		31		3-Jul-08		14:25:59		72.21		46

		23-May-08		16:07:10		71		29.5		23-May-08		16:06:20		68		33		23-May-08		16:07:53		68.61		32.5		3-Jul-08		16:25:59		72.21		45.5

		23-May-08		18:07:10		71		32		23-May-08		18:06:20		68.61		34.5		23-May-08		18:07:53		68.61		35		3-Jul-08		18:25:59		73.4		44

		23-May-08		20:07:10		71		33.5		23-May-08		20:06:20		69.2		36		23-May-08		20:07:53		68.61		36		3-Jul-08		20:25:59		74.01		42

		23-May-08		22:07:10		70.41		33		23-May-08		22:06:20		68.61		37		23-May-08		22:07:53		68.61		36		3-Jul-08		22:25:59		74.6		42

		24-May-08		0:07:10		69.2		33.5		24-May-08		0:06:20		68		37		24-May-08		0:07:53		68.61		36		4-Jul-08		0:25:59		73.4		41.5

		24-May-08		2:07:10		68.61		33.5		24-May-08		2:06:20		68		37		24-May-08		2:07:53		68		36		4-Jul-08		2:25:59		72.21		41.5

		24-May-08		4:07:10		69.2		33		24-May-08		4:06:20		67.4		37		24-May-08		4:07:53		68.61		35		4-Jul-08		4:25:59		71.6		41.5

		24-May-08		6:07:10		70.41		32.5		24-May-08		6:06:20		68		36		24-May-08		6:07:53		69.2		34.5		4-Jul-08		6:25:59		71		42

		24-May-08		8:07:10		70.41		32.5		24-May-08		8:06:20		67.4		38.5		24-May-08		8:07:53		68.61		35.5		4-Jul-08		8:25:59		71		44.5

		24-May-08		10:07:10		70.41		34		24-May-08		10:06:20		70.41		36		24-May-08		10:07:53		68.61		36.5		4-Jul-08		10:25:59		71.6		45

		24-May-08		12:07:10		71		35		24-May-08		12:06:20		71		36		24-May-08		12:07:53		69.2		36.5		4-Jul-08		12:25:59		72.21		48.5

		24-May-08		14:07:10		71		34		24-May-08		14:06:20		71		37		24-May-08		14:07:53		68		37.5		4-Jul-08		14:25:59		73.4		50

		24-May-08		16:07:10		71		34.5		24-May-08		16:06:20		69.8		37		24-May-08		16:07:53		69.2		37		4-Jul-08		16:25:59		72.8		49

		24-May-08		18:07:10		70.41		35.5		24-May-08		18:06:20		70.41		39		24-May-08		18:07:53		69.2		38		4-Jul-08		18:25:59		73.4		48.5

		24-May-08		20:07:10		70.41		36.5		24-May-08		20:06:20		69.8		41		24-May-08		20:07:53		68.61		39		4-Jul-08		20:25:59		74.01		46

		24-May-08		22:07:10		71		36.5		24-May-08		22:06:20		69.2		42.5		24-May-08		22:07:53		68.61		39.5		4-Jul-08		22:25:59		74.01		47

		25-May-08		0:07:10		70.41		37		25-May-08		0:06:20		69.2		42.5		25-May-08		0:07:53		69.2		39.5		5-Jul-08		0:25:59		73.4		46.5

		25-May-08		2:07:10		70.41		37		25-May-08		2:06:20		68.61		42.5		25-May-08		2:07:53		69.2		39		5-Jul-08		2:25:59		72.21		46

		25-May-08		4:07:10		70.41		37.5		25-May-08		4:06:20		68.61		43		25-May-08		4:07:53		69.2		39		5-Jul-08		4:25:59		71.6		45.5

		25-May-08		6:07:10		70.41		37.5		25-May-08		6:06:20		68.61		45		25-May-08		6:07:53		69.2		39.5		5-Jul-08		6:25:59		71		46.5

		25-May-08		8:07:10		70.41		38		25-May-08		8:06:20		68.61		45		25-May-08		8:07:53		69.2		39.5		5-Jul-08		8:25:59		71		48

		25-May-08		10:07:10		70.41		39.5		25-May-08		10:06:20		68.61		48		25-May-08		10:07:53		69.2		41.5		5-Jul-08		10:25:59		72.21		48

		25-May-08		12:07:10		70.41		40		25-May-08		12:06:20		69.2		50		25-May-08		12:07:53		69.8		42		5-Jul-08		12:25:59		72.21		48.5

		25-May-08		14:07:10		69.8		37.5		25-May-08		14:06:20		68.61		46		25-May-08		14:07:53		69.8		40		5-Jul-08		14:25:59		73.4		48

		25-May-08		16:07:10		69.8		38.5		25-May-08		16:06:20		68.61		44.5		25-May-08		16:07:53		69.2		39.5		5-Jul-08		16:25:59		73.4		47.5

		25-May-08		18:07:10		69.8		39.5		25-May-08		18:06:20		69.2		48.5		25-May-08		18:07:53		69.8		41		5-Jul-08		18:25:59		73.4		46.5

		25-May-08		20:07:10		70.41		40		25-May-08		20:06:20		69.2		50		25-May-08		20:07:53		69.2		41.5		5-Jul-08		20:25:59		72.8		45.5

		25-May-08		22:07:10		70.41		40		25-May-08		22:06:20		68.61		48		25-May-08		22:07:53		69.2		41		5-Jul-08		22:25:59		72.8		47

		26-May-08		0:07:10		70.41		39		26-May-08		0:06:20		68		47		26-May-08		0:07:53		69.2		40.5		6-Jul-08		0:25:59		72.21		46

		26-May-08		2:07:10		70.41		37.5		26-May-08		2:06:20		67.4		45		26-May-08		2:07:53		69.2		39		6-Jul-08		2:25:59		72.21		45.5

		26-May-08		4:07:10		70.41		36.5		26-May-08		4:06:20		66.81		44		26-May-08		4:07:53		69.2		38		6-Jul-08		4:25:59		71		45.5

		26-May-08		6:07:10		70.41		36.5		26-May-08		6:06:20		66.81		44.5		26-May-08		6:07:53		69.8		38		6-Jul-08		6:25:59		71		45

		26-May-08		8:07:10		70.41		38.5		26-May-08		8:06:20		67.4		45.5		26-May-08		8:07:53		69.8		39		6-Jul-08		8:25:59		70.41		45.5

		26-May-08		10:07:10		69.8		37		26-May-08		10:06:20		69.2		43		26-May-08		10:07:53		69.2		39.5		6-Jul-08		10:25:59		71.6		47.5

		26-May-08		12:07:10		69.8		37		26-May-08		12:06:20		69.2		40.5		26-May-08		12:07:53		69.2		38.5		6-Jul-08		12:25:59		73.4		48.5

		26-May-08		14:07:10		70.41		37		26-May-08		14:06:20		69.2		40		26-May-08		14:07:53		69.8		38.5		6-Jul-08		14:25:59		75.2		49

		26-May-08		16:07:10		70.41		36		26-May-08		16:06:20		69.2		39		26-May-08		16:07:53		69.2		38		6-Jul-08		16:25:59		77		47.5

		26-May-08		18:07:10		70.41		35.5		26-May-08		18:06:20		68.61		38.5		26-May-08		18:07:53		69.2		37		6-Jul-08		18:25:59		77.61		45.5

		26-May-08		20:07:10		70.41		36		26-May-08		20:06:20		69.2		38.5		26-May-08		20:07:53		69.8		37.5		6-Jul-08		20:25:59		78.2		45

		26-May-08		22:07:10		69.8		37.5		26-May-08		22:06:20		69.2		44		26-May-08		22:07:53		69.2		39.5		6-Jul-08		22:25:59		77		45.5

		27-May-08		0:07:10		70.41		38		27-May-08		0:06:20		68.61		44.5		27-May-08		0:07:53		69.8		39.5		7-Jul-08		0:25:59		75.81		45.5

		27-May-08		2:07:10		70.41		37.5		27-May-08		2:06:20		68		45		27-May-08		2:07:53		69.8		39		7-Jul-08		2:25:59		74.6		44.5

		27-May-08		4:07:10		70.41		37.5		27-May-08		4:06:20		67.4		45.5		27-May-08		4:07:53		69.8		39		7-Jul-08		4:25:59		74.01		44.5

		27-May-08		6:07:10		70.41		37		27-May-08		6:06:20		67.4		45		27-May-08		6:07:53		69.2		38.5		7-Jul-08		6:25:59		72.8		44

		27-May-08		8:07:10		70.41		38		27-May-08		8:06:20		68		45		27-May-08		8:07:53		69.2		39.5		7-Jul-08		8:25:59		72.21		44.5

		27-May-08		10:07:10		69.8		37.5		27-May-08		10:06:20		69.2		42.5		27-May-08		10:07:53		69.2		39		7-Jul-08		10:25:59		73.4		46.5

		27-May-08		12:07:10		70.41		39		27-May-08		12:06:20		69.2		45		27-May-08		12:07:53		69.2		40		7-Jul-08		12:25:59		74.6		48

		27-May-08		14:07:10		70.41		38.5		27-May-08		14:06:20		68.61		45		27-May-08		14:07:53		69.2		40.5		7-Jul-08		14:25:59		76.4		49

		27-May-08		16:07:10		70.41		39		27-May-08		16:06:20		69.2		45.5		27-May-08		16:07:53		69.2		40.5		7-Jul-08		16:25:59		77.61		47.5

		27-May-08		18:07:10		70.41		39		27-May-08		18:06:20		69.2		46		27-May-08		18:07:53		69.2		40.5		7-Jul-08		18:25:59		78.2		46

		27-May-08		20:07:10		70.41		38.5		27-May-08		20:06:20		69.2		46		27-May-08		20:07:53		69.8		40		7-Jul-08		20:25:59		78.2		44.5

		27-May-08		22:07:10		70.41		39		27-May-08		22:06:20		69.2		45		27-May-08		22:07:53		69.8		40		7-Jul-08		22:25:59		76.4		43.5

		28-May-08		0:07:10		70.41		38.5		28-May-08		0:06:20		69.2		46		28-May-08		0:07:53		69.8		40		8-Jul-08		0:25:59		75.2		42.5

		28-May-08		2:07:10		70.41		39		28-May-08		2:06:20		69.2		46.5		28-May-08		2:07:53		69.2		40.5		8-Jul-08		2:25:59		74.01		42.5

		28-May-08		4:07:10		70.41		39		28-May-08		4:06:20		68.61		47		28-May-08		4:07:53		69.8		40.5		8-Jul-08		4:25:59		72.8		42

		28-May-08		6:07:10		70.41		39.5		28-May-08		6:06:20		69.2		47.5		28-May-08		6:07:53		69.2		41		8-Jul-08		6:25:59		72.21		41.5

		28-May-08		8:07:10		70.41		39		28-May-08		8:06:20		69.2		50		28-May-08		8:07:53		69.2		41.5		8-Jul-08		8:25:59		71.6		46

		28-May-08		10:07:10		71		38.5		28-May-08		10:06:20		69.8		45		28-May-08		10:07:53		68.61		41		8-Jul-08		10:25:59		72.8		47

		28-May-08		12:07:10		71		38.5		28-May-08		12:06:20		69.8		44		28-May-08		12:07:53		69.2		41.5		8-Jul-08		12:25:59		72.8		49

		28-May-08		14:07:10		71		39		28-May-08		14:06:20		69.2		43.5		28-May-08		14:07:53		68.61		42.5		8-Jul-08		14:25:59		72.8		49

		28-May-08		16:07:10		71		38		28-May-08		16:06:20		69.8		45.5		28-May-08		16:07:53		68.61		41.5		8-Jul-08		16:25:59		73.4		48.5

		28-May-08		18:07:10		71		37.5		28-May-08		18:06:20		71		41.5		28-May-08		18:07:53		69.2		40.5		8-Jul-08		18:25:59		73.4		47

		28-May-08		20:07:10		71		37.5		28-May-08		20:06:20		70.41		42.5		28-May-08		20:07:53		69.2		40		8-Jul-08		20:25:59		74.6		45.5

		28-May-08		22:07:10		70.41		37.5		28-May-08		22:06:20		71		41.5		28-May-08		22:07:53		69.2		39		8-Jul-08		22:25:59		75.2		45

		29-May-08		0:07:10		70.41		37.5		29-May-08		0:06:20		69.8		43		29-May-08		0:07:53		69.2		39.5		9-Jul-08		0:25:59		75.2		44

		29-May-08		2:07:10		70.41		38		29-May-08		2:06:20		69.2		44		29-May-08		2:07:53		69.8		39.5		9-Jul-08		2:25:59		74.6		44

		29-May-08		4:07:10		70.41		38		29-May-08		4:06:20		68.61		45		29-May-08		4:07:53		69.8		39.5		9-Jul-08		4:25:59		74.01		43.5

		29-May-08		6:07:10		70.41		38.5		29-May-08		6:06:20		68.61		45.5		29-May-08		6:07:53		69.8		40		9-Jul-08		6:25:59		73.4		42

		29-May-08		8:07:10		71		38.5		29-May-08		8:06:20		69.8		46.5		29-May-08		8:07:53		69.2		40.5		9-Jul-08		8:25:59		72.21		45.5

		29-May-08		10:07:10		71		36.5		29-May-08		10:06:20		69.2		41.5		29-May-08		10:07:53		68.61		39.5		9-Jul-08		10:25:59		72.8		50

		29-May-08		12:07:10		71		37.5		29-May-08		12:06:20		69.8		43		29-May-08		12:07:53		69.2		40		9-Jul-08		12:25:59		72.8		50.5

		29-May-08		14:07:10		71		37.5		29-May-08		14:06:20		69.2		41.5		29-May-08		14:07:53		68.61		40.5		9-Jul-08		14:25:59		72.21		49.5

		29-May-08		16:07:10		71		37		29-May-08		16:06:20		69.8		41		29-May-08		16:07:53		68.61		40.5		9-Jul-08		16:25:59		72.8		48.5

		29-May-08		18:07:10		71		38		29-May-08		18:06:20		70.41		42.5		29-May-08		18:07:53		68.61		41		9-Jul-08		18:25:59		73.4		47.5

		29-May-08		20:07:10		71		38		29-May-08		20:06:20		70.41		44.5		29-May-08		20:07:53		69.2		40.5		9-Jul-08		20:25:59		74.01		45

		29-May-08		22:07:10		71		38		29-May-08		22:06:20		70.41		43.5		29-May-08		22:07:53		69.8		40		9-Jul-08		22:25:59		75.81		44

		30-May-08		0:07:10		69.8		38.5		30-May-08		0:06:20		69.2		47		30-May-08		0:07:53		67.4		42.5		10-Jul-08		0:25:59		75.2		44

		30-May-08		2:07:10		70.41		39		30-May-08		2:06:20		68.61		46.5		30-May-08		2:07:53		69.2		41		10-Jul-08		2:25:59		74.6		44

		30-May-08		4:07:10		71		39		30-May-08		4:06:20		68.61		47.5		30-May-08		4:07:53		69.8		40.5		10-Jul-08		4:25:59		74.01		44.5

		30-May-08		6:07:10		71		38.5		30-May-08		6:06:20		68		47.5		30-May-08		6:07:53		69.8		40.5		10-Jul-08		6:25:59		73.4		43

		30-May-08		8:07:10		70.41		39.5		30-May-08		8:06:20		70.41		48.5		30-May-08		8:07:53		68.61		42		10-Jul-08		8:25:59		73.4		46

		30-May-08		10:07:10		71		39		30-May-08		10:06:20		71		44.5		30-May-08		10:07:53		68.61		41.5		10-Jul-08		10:25:59		74.01		47.5

		30-May-08		12:07:10		71.6		39		30-May-08		12:06:20		69.2		49		30-May-08		12:07:53		69.2		41.5		10-Jul-08		12:25:59		72.8		49.5

		30-May-08		14:07:10		71		39.5		30-May-08		14:06:20		69.2		45.5		30-May-08		14:07:53		69.2		42.5		10-Jul-08		14:25:59		72.21		51

		30-May-08		16:07:10		71		39.5		30-May-08		16:06:20		69.2		49		30-May-08		16:07:53		68		44		10-Jul-08		16:25:59		72.8		50.5

		30-May-08		18:07:10		71		39		30-May-08		18:06:20		69.2		47.5		30-May-08		18:07:53		68.61		42		10-Jul-08		18:25:59		73.4		49

		30-May-08		20:07:10		71		38.5		30-May-08		20:06:20		69.2		44		30-May-08		20:07:53		69.2		41		10-Jul-08		20:25:59		74.6		46

		30-May-08		22:07:10		70.41		38.5		30-May-08		22:06:20		68.61		45		30-May-08		22:07:53		69.2		41		10-Jul-08		22:25:59		75.81		47

		31-May-08		0:07:10		71		39.5		31-May-08		0:06:20		68		49.5		31-May-08		0:07:53		69.2		42		11-Jul-08		0:25:59		75.81		46

		31-May-08		2:07:10		70.41		39		31-May-08		2:06:20		68		49.5		31-May-08		2:07:53		69.2		41		11-Jul-08		2:25:59		74.6		46.5

		31-May-08		4:07:10		70.41		39		31-May-08		4:06:20		68		49		31-May-08		4:07:53		69.8		40.5		11-Jul-08		4:25:59		74.01		46.5

		31-May-08		6:07:10		70.41		39		31-May-08		6:06:20		68		51.5		31-May-08		6:07:53		68.61		41.5		11-Jul-08		6:25:59		73.4		44.5

		31-May-08		8:07:10		71		39		31-May-08		8:06:20		68		45.5		31-May-08		8:07:53		68		42.5		11-Jul-08		8:25:59		72.21		47.5

		31-May-08		10:07:10		70.41		39.5		31-May-08		10:06:20		69.2		51		31-May-08		10:07:53		68		42.5		11-Jul-08		10:25:59		73.4		50.5

		31-May-08		12:07:10		71		40		31-May-08		12:06:20		69.2		49		31-May-08		12:07:53		68		44		11-Jul-08		12:25:59		72.8		51

		31-May-08		14:07:10		71		42		31-May-08		14:06:20		69.2		48		31-May-08		14:07:53		68.61		45.5		11-Jul-08		14:25:59		72.8		51.5

		31-May-08		16:07:10		71		40.5		31-May-08		16:06:20		69.2		51		31-May-08		16:07:53		68.61		45		11-Jul-08		16:25:59		72.8		49

		31-May-08		18:07:10		71		40.5		31-May-08		18:06:20		68.61		52.5		31-May-08		18:07:53		68		45		11-Jul-08		18:25:59		73.4		47.5

		31-May-08		20:07:10		71		39.5		31-May-08		20:06:20		68.61		52		31-May-08		20:07:53		68.61		43		11-Jul-08		20:25:59		74.01		46.5

		31-May-08		22:07:10		70.41		39		31-May-08		22:06:20		69.2		48		31-May-08		22:07:53		69.8		41		11-Jul-08		22:25:59		75.2		45

		1-Jun-08		0:07:10		70.41		39.5		1-Jun-08		0:06:20		68.61		47.5		1-Jun-08		0:07:53		68.61		41.5		12-Jul-08		0:25:59		74.6		43.5

		1-Jun-08		2:07:10		70.41		39		1-Jun-08		2:06:20		68.61		47.5		1-Jun-08		2:07:53		69.2		41		12-Jul-08		2:25:59		73.4		44

		1-Jun-08		4:07:10		70.41		39		1-Jun-08		4:06:20		68.61		47.5		1-Jun-08		4:07:53		69.2		41.5		12-Jul-08		4:25:59		72.21		44.5

		1-Jun-08		6:07:10		70.41		39		1-Jun-08		6:06:20		67.4		50.5		1-Jun-08		6:07:53		69.8		41		12-Jul-08		6:25:59		72.21		44

		1-Jun-08		8:07:10		70.41		39.5		1-Jun-08		8:06:20		67.4		51		1-Jun-08		8:07:53		69.2		41.5		12-Jul-08		8:25:59		71.6		46.5

		1-Jun-08		10:07:10		70.41		39.5		1-Jun-08		10:06:20		67.4		50		1-Jun-08		10:07:53		69.8		41		12-Jul-08		10:25:59		72.8		48

		1-Jun-08		12:07:10		70.41		39.5		1-Jun-08		12:06:20		67.4		50.5		1-Jun-08		12:07:53		69.2		42		12-Jul-08		12:25:59		74.6		46.5

		1-Jun-08		14:07:10		71		41		1-Jun-08		14:06:20		68.61		52		1-Jun-08		14:07:53		69.2		43.5		12-Jul-08		14:25:59		74.6		46.5

		1-Jun-08		16:07:10		71		40		1-Jun-08		16:06:20		69.2		50		1-Jun-08		16:07:53		69.2		43.5		12-Jul-08		16:25:59		75.81		45

		1-Jun-08		18:07:10		71.6		39.5		1-Jun-08		18:06:20		69.2		47.5		1-Jun-08		18:07:53		69.2		43		12-Jul-08		18:25:59		75.2		44.5

		1-Jun-08		20:07:10		71.6		38.5		1-Jun-08		20:06:20		68.61		47		1-Jun-08		20:07:53		69.2		42		12-Jul-08		20:25:59		75.81		41.5

		1-Jun-08		22:07:10		70.41		38.5		1-Jun-08		22:06:20		68		47.5		1-Jun-08		22:07:53		68.61		41		12-Jul-08		22:25:59		76.4		43

		2-Jun-08		0:07:10		70.41		38.5		2-Jun-08		0:06:20		68.61		46		2-Jun-08		0:07:53		68.61		41		13-Jul-08		0:25:59		76.4		43

		2-Jun-08		2:07:10		70.41		38		2-Jun-08		2:06:20		68		46		2-Jun-08		2:07:53		68.61		40.5		13-Jul-08		2:25:59		75.81		44

		2-Jun-08		4:07:10		70.41		37		2-Jun-08		4:06:20		67.4		45		2-Jun-08		4:07:53		68.61		39.5		13-Jul-08		4:25:59		75.81		44

		2-Jun-08		6:07:10		69.8		36		2-Jun-08		6:06:20		66.2		44		2-Jun-08		6:07:53		68.61		38.5		13-Jul-08		6:25:59		75.81		44.5

		2-Jun-08		8:07:10		70.41		38		2-Jun-08		8:06:20		66.81		46		2-Jun-08		8:07:53		69.2		40		13-Jul-08		8:25:59		75.81		44.5

		2-Jun-08		10:07:10		69.8		37		2-Jun-08		10:06:20		68.61		40.5		2-Jun-08		10:07:53		68.61		39.5		13-Jul-08		10:25:59		75.81		44.5

		2-Jun-08		12:07:10		70.41		38		2-Jun-08		12:06:20		69.2		41		2-Jun-08		12:07:53		69.2		39.5		13-Jul-08		12:25:59		76.4		44

		2-Jun-08		14:07:10		71		39		2-Jun-08		14:06:20		69.8		42		2-Jun-08		14:07:53		69.2		41.5		13-Jul-08		14:25:59		77.61		44.5

		2-Jun-08		16:07:10		71		38.5		2-Jun-08		16:06:20		69.2		45.5		2-Jun-08		16:07:53		65.01		46		13-Jul-08		16:25:59		78.8		43.5

		2-Jun-08		18:07:10		71		38.5		2-Jun-08		18:06:20		68.61		45		2-Jun-08		18:07:53		67.4		43		13-Jul-08		18:25:59		78.8		43

		2-Jun-08		20:07:10		71		37.5		2-Jun-08		20:06:20		67.4		47		2-Jun-08		20:07:53		66.81		43.5		13-Jul-08		20:25:59		78.8		43.5

		2-Jun-08		22:07:10		69.8		37		2-Jun-08		22:06:20		68		45		2-Jun-08		22:07:53		67.4		42		13-Jul-08		22:25:59		77.61		42.5

		3-Jun-08		0:07:10		69.8		37		3-Jun-08		0:06:20		67.4		44		3-Jun-08		0:07:53		67.4		41		14-Jul-08		0:25:59		77		42.5

		3-Jun-08		2:07:10		70.41		36.5		3-Jun-08		2:06:20		66.81		43.5		3-Jun-08		2:07:53		66.81		40.5		14-Jul-08		2:25:59		76.4		42.5

		3-Jun-08		4:07:10		69.8		35		3-Jun-08		4:06:20		66.2		43		3-Jun-08		4:07:53		67.4		39.5		14-Jul-08		4:25:59		75.81		42.5

		3-Jun-08		6:07:10		70.41		35.5		3-Jun-08		6:06:20		66.2		42.5		3-Jun-08		6:07:53		67.4		38.5		14-Jul-08		6:25:59		75.2		42

		3-Jun-08		8:07:10		70.41		37		3-Jun-08		8:06:20		68		42		3-Jun-08		8:07:53		68.61		39.5		14-Jul-08		8:25:59		74.6		42.5

		3-Jun-08		10:07:10		71		37		3-Jun-08		10:06:20		68		44.5		3-Jun-08		10:07:53		67.4		41.5		14-Jul-08		10:25:59		75.2		42.5

		3-Jun-08		12:07:10		71		37.5		3-Jun-08		12:06:20		71		41		3-Jun-08		12:07:53		68		41.5		14-Jul-08		12:25:59		76.4		43

		3-Jun-08		14:07:10		71		39.5		3-Jun-08		14:06:20		70.41		45.5		3-Jun-08		14:07:53		66.81		45		14-Jul-08		14:25:59		77		43.5

		3-Jun-08		16:07:10		71		39.5		3-Jun-08		16:06:20		69.2		44.5		3-Jun-08		16:07:53		67.4		44.5		14-Jul-08		16:25:59		78.2		43.5

		3-Jun-08		18:07:10		71		39.5		3-Jun-08		18:06:20		69.2		45		3-Jun-08		18:07:53		67.4		44.5		14-Jul-08		18:25:59		78.8		43

		3-Jun-08		20:07:10		71		30.5		3-Jun-08		20:06:20		69.2		31.5		3-Jun-08		20:07:53		67.4		34.5		14-Jul-08		20:25:59		78.8		42.5

		3-Jun-08		22:07:10		70.41		27		3-Jun-08		22:06:20		68.61		29.5		3-Jun-08		22:07:53		68		31		14-Jul-08		22:25:59		77.61		41.5

		4-Jun-08		0:07:10		69.2		34		4-Jun-08		0:06:20		68.61		37		4-Jun-08		0:07:53		68		37		15-Jul-08		0:25:59		77		41

		4-Jun-08		2:07:10		69.2		35.5		4-Jun-08		2:06:20		68		40		4-Jun-08		2:07:53		68		38		15-Jul-08		2:25:59		76.4		41

		4-Jun-08		4:07:10		68.61		35		4-Jun-08		4:06:20		67.4		39.5		4-Jun-08		4:07:53		68		37.5		15-Jul-08		4:25:59		75.81		41.5

		4-Jun-08		6:07:10		69.8		34.5		4-Jun-08		6:06:20		68		39		4-Jun-08		6:07:53		68.61		37		15-Jul-08		6:25:59		75.2		41

		4-Jun-08		8:07:10		69.8		38.5		4-Jun-08		8:06:20		68		46		4-Jun-08		8:07:53		68		40.5		15-Jul-08		8:25:59		74.01		43.5

		4-Jun-08		10:07:10		70.41		41		4-Jun-08		10:06:20		69.8		53		4-Jun-08		10:07:53		68		45		15-Jul-08		10:25:59		74.6		45

		4-Jun-08		12:07:10		71		42.5		4-Jun-08		12:06:20		69.8		50		4-Jun-08		12:07:53		68		46.5		15-Jul-08		12:25:59		75.2		44.5

		4-Jun-08		14:07:10		70.41		41.5		4-Jun-08		14:06:20		69.2		53		4-Jun-08		14:07:53		66.81		47		15-Jul-08		14:25:59		75.81		45

		4-Jun-08		16:07:10		70.41		40		4-Jun-08		16:06:20		70.41		44.5		4-Jun-08		16:07:53		67.4		44.5		15-Jul-08		16:25:59		75.81		44

		4-Jun-08		18:07:10		71		38		4-Jun-08		18:06:20		70.41		38.5		4-Jun-08		18:07:53		67.4		42		15-Jul-08		18:25:59		76.4		42.5

		4-Jun-08		20:07:10		71		38		4-Jun-08		20:06:20		70.41		42		4-Jun-08		20:07:53		67.4		43		15-Jul-08		20:25:59		77		39.5

		4-Jun-08		22:07:10		71		37.5		4-Jun-08		22:06:20		69.8		43		4-Jun-08		22:07:53		67.4		42.5		15-Jul-08		22:25:59		77		41

		5-Jun-08		0:07:10		70.41		38		5-Jun-08		0:06:20		69.2		44		5-Jun-08		0:07:53		68		41.5		16-Jul-08		0:25:59		76.4		41.5

		5-Jun-08		2:07:10		69.8		36		5-Jun-08		2:06:20		69.8		38.5		5-Jun-08		2:07:53		68.61		39		16-Jul-08		2:25:59		75.81		41.5

		5-Jun-08		4:07:10		68.61		36		5-Jun-08		4:06:20		69.2		38.5		5-Jun-08		4:07:53		68		38.5		16-Jul-08		4:25:59		75.81		42

		5-Jun-08		6:07:10		68.61		36		5-Jun-08		6:06:20		68.61		38.5		5-Jun-08		6:07:53		68		38		16-Jul-08		6:25:59		75.2		41

		5-Jun-08		8:07:10		69.2		35		5-Jun-08		8:06:20		69.2		39.5		5-Jun-08		8:07:53		68		38		16-Jul-08		8:25:59		74.6		43.5

		5-Jun-08		10:07:10		70.41		35		5-Jun-08		10:06:20		71		36.5		5-Jun-08		10:07:53		68		38.5		16-Jul-08		10:25:59		75.2		44.5

		5-Jun-08		12:07:10		70.41		34.5		5-Jun-08		12:06:20		69.8		35		5-Jun-08		12:07:53		68.61		37		16-Jul-08		12:25:59		75.2		43.5

		5-Jun-08		14:07:10		70.41		32		5-Jun-08		14:06:20		69.2		34.5		5-Jun-08		14:07:53		68.61		35		16-Jul-08		14:25:59		75.81		45

		5-Jun-08		16:07:10		70.41		34.5		5-Jun-08		16:06:20		70.41		36.5		5-Jun-08		16:07:53		68.61		37.5		16-Jul-08		16:25:59		75.2		43.5

		5-Jun-08		18:07:10		71		35		5-Jun-08		18:06:20		69.8		36		5-Jun-08		18:07:53		68.61		37.5

		5-Jun-08		20:07:10		71		35.5		5-Jun-08		20:06:20		69.2		38.5		5-Jun-08		20:07:53		69.2		38

		5-Jun-08		22:07:10		71		35		5-Jun-08		22:06:20		68.61		39		5-Jun-08		22:07:53		69.2		37.5

		6-Jun-08		0:07:10		69.8		35.5		6-Jun-08		0:06:20		68		41		6-Jun-08		0:07:53		68.61		38.5

		6-Jun-08		2:07:10		69.2		36		6-Jun-08		2:06:20		67.4		41		6-Jun-08		2:07:53		68.61		38

		6-Jun-08		4:07:10		69.2		36		6-Jun-08		4:06:20		67.4		41.5		6-Jun-08		4:07:53		68.61		38.5

		6-Jun-08		6:07:10		69.2		36		6-Jun-08		6:06:20		67.4		41.5		6-Jun-08		6:07:53		68		38.5

		6-Jun-08		8:07:10		69.8		36.5		6-Jun-08		8:06:20		68		42		6-Jun-08		8:07:53		68.61		39.5

		6-Jun-08		10:07:10		70.41		36		6-Jun-08		10:06:20		68		42		6-Jun-08		10:07:53		68		40

		6-Jun-08		12:07:10		70.41		33		6-Jun-08		12:06:20		69.8		36		6-Jun-08		12:07:53		68		37.5

		6-Jun-08		14:07:10		70.41		38.5		6-Jun-08		14:06:20		69.2		40.5		6-Jun-08		14:07:53		67.4		42

		6-Jun-08		16:07:10		70.41		39.5		6-Jun-08		16:06:20		69.8		43		6-Jun-08		16:07:53		68		43

		6-Jun-08		18:07:10		71		38.5		6-Jun-08		18:06:20		69.2		44.5		6-Jun-08		18:07:53		68		42.5

		6-Jun-08		20:07:10		71		39.5		6-Jun-08		20:06:20		69.2		47		6-Jun-08		20:07:53		68.61		43

		6-Jun-08		22:07:10		71		39		6-Jun-08		22:06:20		68.61		51.5		6-Jun-08		22:07:53		68.61		43

		7-Jun-08		0:07:10		70.41		38.5		7-Jun-08		0:06:20		68.61		45		7-Jun-08		0:07:53		69.2		41

		7-Jun-08		2:07:10		69.8		38		7-Jun-08		2:06:20		68		48.5		7-Jun-08		2:07:53		69.2		40.5

		7-Jun-08		4:07:10		69.2		38		7-Jun-08		4:06:20		67.4		45.5		7-Jun-08		4:07:53		68.61		40

		7-Jun-08		6:07:10		69.2		37.5		7-Jun-08		6:06:20		67.4		43.5		7-Jun-08		6:07:53		68.61		39.5

		7-Jun-08		8:07:10		69.8		37.5		7-Jun-08		8:06:20		68.61		44		7-Jun-08		8:07:53		68.61		39.5

		7-Jun-08		10:07:10		70.41		36		7-Jun-08		10:06:20		68.61		40		7-Jun-08		10:07:53		68		39.5

		7-Jun-08		12:07:10		70.41		34.5		7-Jun-08		12:06:20		70.41		36.5		7-Jun-08		12:07:53		69.2		37

		7-Jun-08		14:07:10		70.41		31.5		7-Jun-08		14:06:20		69.8		32.5		7-Jun-08		14:07:53		68.61		33.5

		7-Jun-08		16:07:10		71		32		7-Jun-08		16:06:20		68.61		34.5		7-Jun-08		16:07:53		68		35

		7-Jun-08		18:07:10		70.41		34.5		7-Jun-08		18:06:20		68.61		36.5		7-Jun-08		18:07:53		68.61		36.5

		7-Jun-08		20:07:10		71		34.5		7-Jun-08		20:06:20		69.2		38		7-Jun-08		20:07:53		69.2		37

		7-Jun-08		22:07:10		70.41		34		7-Jun-08		22:06:20		68.61		38		7-Jun-08		22:07:53		68.61		36.5

		8-Jun-08		0:07:10		69.8		34		8-Jun-08		0:06:20		68		38		8-Jun-08		0:07:53		68.61		36.5

		8-Jun-08		2:07:10		69.2		34		8-Jun-08		2:06:20		68		37.5		8-Jun-08		2:07:53		68.61		36

		8-Jun-08		4:07:10		69.2		34		8-Jun-08		4:06:20		68		37		8-Jun-08		4:07:53		68.61		35.5

		8-Jun-08		6:07:10		69.8		33		8-Jun-08		6:06:20		67.4		37		8-Jun-08		6:07:53		68.61		35.5

		8-Jun-08		8:07:10		69.8		33.5		8-Jun-08		8:06:20		68		36.5		8-Jun-08		8:07:53		68.61		35.5

		8-Jun-08		10:07:10		70.41		34.5		8-Jun-08		10:06:20		68		37		8-Jun-08		10:07:53		69.2		35.5

		8-Jun-08		12:07:10		71		33		8-Jun-08		12:06:20		68.61		34.5		8-Jun-08		12:07:53		69.2		35

		8-Jun-08		14:07:10		71		30.5		8-Jun-08		14:06:20		68.61		32		8-Jun-08		14:07:53		69.2		33

		8-Jun-08		16:07:10		71.6		31		8-Jun-08		16:06:20		69.2		33.5		8-Jun-08		16:07:53		68.61		34.5

		8-Jun-08		18:07:10		71.6		34.5		8-Jun-08		18:06:20		68.61		37.5		8-Jun-08		18:07:53		68.61		38

		8-Jun-08		20:07:10		71.6		36.5		8-Jun-08		20:06:20		68.61		45		8-Jun-08		20:07:53		68.61		40.5

		8-Jun-08		22:07:10		71		37		8-Jun-08		22:06:20		68.61		44		8-Jun-08		22:07:53		68.61		40

		9-Jun-08		0:07:10		71		36		9-Jun-08		0:06:20		68.61		40.5		9-Jun-08		0:07:53		69.2		38.5

		9-Jun-08		2:07:10		70.41		36.5		9-Jun-08		2:06:20		68		43		9-Jun-08		2:07:53		69.2		38

		9-Jun-08		4:07:10		69.8		36.5		9-Jun-08		4:06:20		68		43		9-Jun-08		4:07:53		69.2		38.5

		9-Jun-08		6:07:10		69.2		37		9-Jun-08		6:06:20		67.4		43.5		9-Jun-08		6:07:53		69.2		39

		9-Jun-08		8:07:10		69.8		38		9-Jun-08		8:06:20		67.4		45		9-Jun-08		8:07:53		69.2		39

		9-Jun-08		10:07:10		70.41		38.5		9-Jun-08		10:06:20		68.61		43.5		9-Jun-08		10:07:53		69.2		40

		9-Jun-08		12:07:10		71		38		9-Jun-08		12:06:20		68.61		42.5		9-Jun-08		12:07:53		69.8		40.5

		9-Jun-08		14:07:10		71		38		9-Jun-08		14:06:20		68.61		41.5		9-Jun-08		14:07:53		69.2		40.5

		9-Jun-08		16:07:10		72.21		38.5		9-Jun-08		16:06:20		68.61		44.5		9-Jun-08		16:07:53		69.8		42

		9-Jun-08		18:07:10		71.6		39		9-Jun-08		18:06:20		68.61		46.5		9-Jun-08		18:07:53		69.2		43

		9-Jun-08		20:07:10		71.6		38		9-Jun-08		20:06:20		68		48		9-Jun-08		20:07:53		69.2		41.5

		9-Jun-08		22:07:10		71		37.5		9-Jun-08		22:06:20		68		47		9-Jun-08		22:07:53		69.2		40

		10-Jun-08		0:07:10		70.41		37.5		10-Jun-08		0:06:20		68		45.5		10-Jun-08		0:07:53		69.2		39.5

		10-Jun-08		2:07:10		69.8		37		10-Jun-08		2:06:20		67.4		46		10-Jun-08		2:07:53		69.2		39.5

		10-Jun-08		4:07:10		69.8		38		10-Jun-08		4:06:20		68		47		10-Jun-08		4:07:53		69.2		39.5

		10-Jun-08		6:07:10		69.8		38		10-Jun-08		6:06:20		68		44.5		10-Jun-08		6:07:53		69.8		39.5

		10-Jun-08		8:07:10		71		38.5		10-Jun-08		8:06:20		68.61		48		10-Jun-08		8:07:53		69.2		41

		10-Jun-08		10:07:10		71		37.5		10-Jun-08		10:06:20		69.2		43		10-Jun-08		10:07:53		69.2		40.5

		10-Jun-08		12:07:10		71		38		10-Jun-08		12:06:20		70.41		40		10-Jun-08		12:07:53		69.2		40.5

		10-Jun-08		14:07:10		71		37.5		10-Jun-08		14:06:20		71.6		37.5		10-Jun-08		14:07:53		68.61		39.5

		10-Jun-08		16:07:10		70.41		40		10-Jun-08		16:06:20		70.41		41		10-Jun-08		16:07:53		68.61		42

		10-Jun-08		18:07:10		70.41		44		10-Jun-08		18:06:20		71.6		47.5		10-Jun-08		18:07:53		69.2		46.5

		10-Jun-08		20:07:10		71		42		10-Jun-08		20:06:20		71		47		10-Jun-08		20:07:53		68.61		46

		10-Jun-08		22:07:10		71.6		41		10-Jun-08		22:06:20		71		51		10-Jun-08		22:07:53		69.2		44.5

		11-Jun-08		0:07:10		71.6		40.5		11-Jun-08		0:06:20		71		47.5		11-Jun-08		0:07:53		68.61		45

		11-Jun-08		2:07:10		71.6		36.5		11-Jun-08		2:06:20		71		40.5		11-Jun-08		2:07:53		69.2		40

		11-Jun-08		4:07:10		71		37.5		11-Jun-08		4:06:20		69.8		44		11-Jun-08		4:07:53		69.2		40.5

		11-Jun-08		6:07:10		70.41		36.5		11-Jun-08		6:06:20		69.8		41		11-Jun-08		6:07:53		69.2		39

		11-Jun-08		8:07:10		71		35.5		11-Jun-08		8:06:20		70.41		39		11-Jun-08		8:07:53		68		39

		11-Jun-08		10:07:10		71		27.5		11-Jun-08		10:06:20		70.41		29.5		11-Jun-08		10:07:53		67.4		31.5

		11-Jun-08		12:07:10		71		24		11-Jun-08		12:06:20		69.8		24.5		11-Jun-08		12:07:53		68.61		27

		11-Jun-08		14:07:10		71.6		27.5		11-Jun-08		14:06:20		70.41		30.5		11-Jun-08		14:07:53		68		31.5

		11-Jun-08		16:07:10		71		28.5		11-Jun-08		16:06:20		69.8		30		11-Jun-08		16:07:53		68.61		31.5

		11-Jun-08		18:07:10		71		31.5		11-Jun-08		18:06:20		69.8		33		11-Jun-08		18:07:53		68.61		34

		11-Jun-08		20:07:10		71		33.5		11-Jun-08		20:06:20		69.8		35		11-Jun-08		20:07:53		68.61		36

		11-Jun-08		22:07:10		71.6		33.5		11-Jun-08		22:06:20		69.2		37		11-Jun-08		22:07:53		68.61		37

		12-Jun-08		0:07:10		70.41		34		12-Jun-08		0:06:20		69.2		36.5		12-Jun-08		0:07:53		68.61		36.5

		12-Jun-08		2:07:10		69.8		33.5		12-Jun-08		2:06:20		68.61		36.5		12-Jun-08		2:07:53		68.61		36

		12-Jun-08		4:07:10		69.2		34		12-Jun-08		4:06:20		68.61		37		12-Jun-08		4:07:53		68.61		36

		12-Jun-08		6:07:10		68.61		34.5		12-Jun-08		6:06:20		68		37		12-Jun-08		6:07:53		68		36.5

		12-Jun-08		8:07:10		69.8		34.5		12-Jun-08		8:06:20		69.2		37.5		12-Jun-08		8:07:53		68.61		36.5

		12-Jun-08		10:07:10		71		34		12-Jun-08		10:06:20		71		36		12-Jun-08		10:07:53		68.61		37

		12-Jun-08		12:07:10		71		29.5		12-Jun-08		12:06:20		71.6		30		12-Jun-08		12:07:53		69.8		32

		12-Jun-08		14:07:10		71		24.5		12-Jun-08		14:06:20		72.8		26		12-Jun-08		14:07:53		69.8		28.5

		12-Jun-08		16:07:10		71		26.5		12-Jun-08		16:06:20		71.6		20.5		12-Jun-08		16:07:53		69.2		28

		12-Jun-08		18:07:10		70.41		27.5		12-Jun-08		18:06:20		71		27.5		12-Jun-08		18:07:53		69.2		29.5

		12-Jun-08		20:07:10		70.41		35.5		12-Jun-08		20:06:20		71		38.5		12-Jun-08		20:07:53		69.2		38

		12-Jun-08		22:07:10		71		35.5		12-Jun-08		22:06:20		70.41		40		12-Jun-08		22:07:53		69.2		38

		13-Jun-08		0:07:10		70.41		36		13-Jun-08		0:06:20		70.41		39.5		13-Jun-08		0:07:53		69.2		37.5

		13-Jun-08		2:07:10		69.8		36		13-Jun-08		2:06:20		69.8		39.5		13-Jun-08		2:07:53		69.2		37.5

		13-Jun-08		4:07:10		69.8		36.5		13-Jun-08		4:06:20		69.8		40.5		13-Jun-08		4:07:53		69.2		38

		13-Jun-08		6:07:10		69.2		36.5		13-Jun-08		6:06:20		69.8		39.5		13-Jun-08		6:07:53		69.2		37.5

		13-Jun-08		8:07:10		70.41		37		13-Jun-08		8:06:20		70.41		39.5		13-Jun-08		8:07:53		69.2		39

		13-Jun-08		10:07:10		71		36.5		13-Jun-08		10:06:20		70.41		38.5		13-Jun-08		10:07:53		69.2		38.5

		13-Jun-08		12:07:10		71		24		13-Jun-08		12:06:20		71.6		25		13-Jun-08		12:07:53		69.8		28

		13-Jun-08		14:07:10		71		22.5		13-Jun-08		14:06:20		71.6		23.5		13-Jun-08		14:07:53		69.2		25

		13-Jun-08		16:07:10		70.41		29		13-Jun-08		16:06:20		72.21		30		13-Jun-08		16:07:53		69.8		31.5

		13-Jun-08		18:07:10		71		26.5		13-Jun-08		18:06:20		71		27		13-Jun-08		18:07:53		69.8		29

		13-Jun-08		20:07:10		71		29		13-Jun-08		20:06:20		71.6		27.5		13-Jun-08		20:07:53		68.61		29.5

		13-Jun-08		22:07:10		71.6		32.5		13-Jun-08		22:06:20		71		33.5		13-Jun-08		22:07:53		69.2		34.5

		14-Jun-08		0:07:10		71		33		14-Jun-08		0:06:20		70.41		35.5		14-Jun-08		0:07:53		69.2		35.5

		14-Jun-08		2:07:10		70.41		34.5		14-Jun-08		2:06:20		70.41		37		14-Jun-08		2:07:53		69.2		36

		14-Jun-08		4:07:10		69.8		34.5		14-Jun-08		4:06:20		69.8		38.5		14-Jun-08		4:07:53		69.2		36.5

		14-Jun-08		6:07:10		69.8		35.5		14-Jun-08		6:06:20		69.8		38.5		14-Jun-08		6:07:53		68.61		37

		14-Jun-08		8:07:10		70.41		36		14-Jun-08		8:06:20		71		38.5		14-Jun-08		8:07:53		69.2		38

		14-Jun-08		10:07:10		71		36.5		14-Jun-08		10:06:20		71		39.5		14-Jun-08		10:07:53		68.61		39.5

		14-Jun-08		12:07:10		70.41		39		14-Jun-08		12:06:20		71.6		42		14-Jun-08		12:07:53		69.2		41.5

		14-Jun-08		14:07:10		71		37.5		14-Jun-08		14:06:20		72.8		37		14-Jun-08		14:07:53		69.2		39.5

		14-Jun-08		16:07:10		70.41		39		14-Jun-08		16:06:20		71		41		14-Jun-08		16:07:53		69.8		41

		14-Jun-08		18:07:10		70.41		39		14-Jun-08		18:06:20		71		42.5		14-Jun-08		18:07:53		68.61		42

		14-Jun-08		20:07:10		70.41		38		14-Jun-08		20:06:20		70.41		45		14-Jun-08		20:07:53		68.61		41.5

		14-Jun-08		22:07:10		70.41		38		14-Jun-08		22:06:20		71		45		14-Jun-08		22:07:53		68.61		40.5

		15-Jun-08		0:07:10		70.41		38.5		15-Jun-08		0:06:20		69.8		43.5		15-Jun-08		0:07:53		68.61		40.5

		15-Jun-08		2:07:10		70.41		38		15-Jun-08		2:06:20		69.8		44		15-Jun-08		2:07:53		68.61		40.5

		15-Jun-08		4:07:10		69.8		37.5		15-Jun-08		4:06:20		69.2		44		15-Jun-08		4:07:53		68.61		40

		15-Jun-08		6:07:10		69.8		38		15-Jun-08		6:06:20		69.2		45		15-Jun-08		6:07:53		68.61		40.5

		15-Jun-08		8:07:10		70.41		39		15-Jun-08		8:06:20		69.2		45.5		15-Jun-08		8:07:53		68.61		41

		15-Jun-08		10:07:10		70.41		39		15-Jun-08		10:06:20		69.8		45		15-Jun-08		10:07:53		68.61		41

		15-Jun-08		12:07:10		70.41		40		15-Jun-08		12:06:20		70.41		46.5		15-Jun-08		12:07:53		69.2		42

		15-Jun-08		14:07:10		71		41.5		15-Jun-08		14:06:20		71		47.5		15-Jun-08		14:07:53		69.2		44

		15-Jun-08		16:07:10		71		41.5		15-Jun-08		16:06:20		70.41		51.5		15-Jun-08		16:07:53		69.2		44.5

		15-Jun-08		18:07:10		71		40.5		15-Jun-08		18:06:20		70.41		50		15-Jun-08		18:07:53		69.2		43.5

		15-Jun-08		20:07:10		71		38.5		15-Jun-08		20:06:20		69.8		47		15-Jun-08		20:07:53		69.2		41.5

		15-Jun-08		22:07:10		71		38.5		15-Jun-08		22:06:20		70.41		45.5		15-Jun-08		22:07:53		69.2		41

		16-Jun-08		0:07:10		70.41		38.5		16-Jun-08		0:06:20		69.8		44.5		16-Jun-08		0:07:53		69.2		40.5

		16-Jun-08		2:07:10		70.41		38		16-Jun-08		2:06:20		69.2		44.5		16-Jun-08		2:07:53		69.2		40

		16-Jun-08		4:07:10		70.41		38		16-Jun-08		4:06:20		68.61		45		16-Jun-08		4:07:53		69.2		40

		16-Jun-08		6:07:10		69.8		37.5		16-Jun-08		6:06:20		68.61		44.5		16-Jun-08		6:07:53		69.2		39.5

		16-Jun-08		8:07:10		69.8		38		16-Jun-08		8:06:20		68.61		44.5		16-Jun-08		8:07:53		69.2		40

		16-Jun-08		10:07:10		69.8		38.5		16-Jun-08		10:06:20		69.8		44.5		16-Jun-08		10:07:53		69.2		40

		16-Jun-08		12:07:10		70.41		40.5		16-Jun-08		12:06:20		69.8		47		16-Jun-08		12:07:53		69.2		41.5

		16-Jun-08		14:07:10		70.41		42		16-Jun-08		14:06:20		70.41		49.5		16-Jun-08		14:07:53		69.2		43.5

		16-Jun-08		16:07:10		71		40.5		16-Jun-08		16:06:20		71		46		16-Jun-08		16:07:53		69.2		43

		16-Jun-08		18:07:10		71		39.5		16-Jun-08		18:06:20		71		43.5		16-Jun-08		18:07:53		69.2		42.5

		16-Jun-08		20:07:10		71		38		16-Jun-08		20:06:20		70.41		44.5		16-Jun-08		20:07:53		69.2		41

		16-Jun-08		22:07:10		70.41		38		16-Jun-08		22:06:20		70.41		43		16-Jun-08		22:07:53		69.2		40

		17-Jun-08		0:07:10		70.41		37.5		17-Jun-08		0:06:20		69.8		42		17-Jun-08		0:07:53		69.2		39.5

		17-Jun-08		2:07:10		69.8		36.5		17-Jun-08		2:06:20		68.61		43		17-Jun-08		2:07:53		69.2		39

		17-Jun-08		4:07:10		69.8		38		17-Jun-08		4:06:20		68		45.5		17-Jun-08		4:07:53		69.2		40

		17-Jun-08		6:07:10		69.8		38		17-Jun-08		6:06:20		68		45.5		17-Jun-08		6:07:53		69.2		40

		17-Jun-08		8:07:10		70.41		38.5		17-Jun-08		8:06:20		70.41		45		17-Jun-08		8:07:53		68.61		41

		17-Jun-08		10:07:10		70.41		39		17-Jun-08		10:06:20		71		44		17-Jun-08		10:07:53		68.61		41

		17-Jun-08		12:07:10		71		39.5		17-Jun-08		12:06:20		69.8		45.5		17-Jun-08		12:07:53		69.2		42

		17-Jun-08		14:07:10		71		41.5		17-Jun-08		14:06:20		70.41		48.5		17-Jun-08		14:07:53		68		45

		17-Jun-08		16:07:10		71		40		17-Jun-08		16:06:20		70.41		45		17-Jun-08		16:07:53		69.2		43.5

		17-Jun-08		18:07:10		71		39.5		17-Jun-08		18:06:20		70.41		46		17-Jun-08		18:07:53		69.8		41.5

		17-Jun-08		20:07:10		70.41		38.5		17-Jun-08		20:06:20		69.8		44.5		17-Jun-08		20:07:53		69.8		40

		17-Jun-08		22:07:10		70.41		38		17-Jun-08		22:06:20		69.8		43		17-Jun-08		22:07:53		69.8		39.5

		18-Jun-08		0:07:10		70.41		37.5		18-Jun-08		0:06:20		69.2		43		18-Jun-08		0:07:53		69.8		39

		18-Jun-08		2:07:10		70.41		37.5		18-Jun-08		2:06:20		68		43.5		18-Jun-08		2:07:53		69.8		38.5

		18-Jun-08		4:07:10		70.41		38		18-Jun-08		4:06:20		67.4		46		18-Jun-08		4:07:53		69.8		39

		18-Jun-08		6:07:10		70.41		38		18-Jun-08		6:06:20		66.81		46.5		18-Jun-08		6:07:53		69.8		39

		18-Jun-08		8:07:10		70.41		39		18-Jun-08		8:06:20		70.41		43.5		18-Jun-08		8:07:53		69.2		40.5

		18-Jun-08		10:07:10		71		38.5		18-Jun-08		10:06:20		70.41		44.5		18-Jun-08		10:07:53		68.61		41

		18-Jun-08		12:07:10		71		39		18-Jun-08		12:06:20		69.8		44.5		18-Jun-08		12:07:53		69.8		41

		18-Jun-08		14:07:10		71		42		18-Jun-08		14:06:20		69.8		46.5		18-Jun-08		14:07:53		69.2		44.5

		18-Jun-08		16:07:10		71		43.5		18-Jun-08		16:06:20		69.8		51.5		18-Jun-08		16:07:53		69.2		46

		18-Jun-08		18:07:10		71		29		18-Jun-08		18:06:20		69.2		31		18-Jun-08		18:07:53		69.2		32

		18-Jun-08		20:07:10		71		28		18-Jun-08		20:06:20		68.61		29		18-Jun-08		20:07:53		69.2		30

		18-Jun-08		22:07:10		71		29.5		18-Jun-08		22:06:20		68.61		31		18-Jun-08		22:07:53		69.2		31.5

		19-Jun-08		0:07:10		70.41		29		19-Jun-08		0:06:20		68.61		31.5		19-Jun-08		0:07:53		69.2		31

		19-Jun-08		2:07:10		69.8		34		19-Jun-08		2:06:20		68		37		19-Jun-08		2:07:53		69.2		35.5

		19-Jun-08		4:07:10		69.2		35		19-Jun-08		4:06:20		67.4		39.5		19-Jun-08		4:07:53		68.61		36.5

		19-Jun-08		6:07:10		69.8		34		19-Jun-08		6:06:20		67.4		39		19-Jun-08		6:07:53		69.2		35.5

		19-Jun-08		8:07:10		69.8		35.5		19-Jun-08		8:06:20		68		41.5		19-Jun-08		8:07:53		69.2		37.5

		19-Jun-08		10:07:10		71		33.5		19-Jun-08		10:06:20		70.41		36.5		19-Jun-08		10:07:53		69.2		36.5

		19-Jun-08		12:07:10		71		31		19-Jun-08		12:06:20		70.41		33		19-Jun-08		12:07:53		69.8		33

		19-Jun-08		14:07:10		70.41		34.5		19-Jun-08		14:06:20		71		36		19-Jun-08		14:07:53		69.8		36

		19-Jun-08		16:07:10		70.41		31		19-Jun-08		16:06:20		69.2		32.5		19-Jun-08		16:07:53		69.8		32.5

		19-Jun-08		18:07:10		71		25		19-Jun-08		18:06:20		69.2		26		19-Jun-08		18:07:53		69.2		27

		19-Jun-08		20:07:10		71		26		19-Jun-08		20:06:20		69.2		27		19-Jun-08		20:07:53		69.2		27.5

		19-Jun-08		22:07:10		71		30.5		19-Jun-08		22:06:20		68.61		31.5		19-Jun-08		22:07:53		69.2		31.5

		20-Jun-08		0:07:10		71		33		20-Jun-08		0:06:20		68		37		20-Jun-08		0:07:53		68.61		35.5

		20-Jun-08		2:07:10		70.41		33.5		20-Jun-08		2:06:20		68		37.5		20-Jun-08		2:07:53		68.61		35.5

		20-Jun-08		4:07:10		69.8		33.5		20-Jun-08		4:06:20		68		38		20-Jun-08		4:07:53		68.61		36

		20-Jun-08		6:07:10		69.2		34.5		20-Jun-08		6:06:20		67.4		39		20-Jun-08		6:07:53		68		36.5

		20-Jun-08		8:07:10		69.8		35.5		20-Jun-08		8:06:20		68.61		39		20-Jun-08		8:07:53		68.61		37.5

		20-Jun-08		10:07:10		71		35.5		20-Jun-08		10:06:20		70.41		38		20-Jun-08		10:07:53		68.61		38

		20-Jun-08		12:07:10		70.41		34		20-Jun-08		12:06:20		72.21		34.5		20-Jun-08		12:07:53		68.61		36.5

		20-Jun-08		14:07:10		70.41		31		20-Jun-08		14:06:20		69.8		32		20-Jun-08		14:07:53		68		33.5

		20-Jun-08		16:07:10		70.41		32.5		20-Jun-08		16:06:20		71		34.5		20-Jun-08		16:07:53		68.61		35.5

		20-Jun-08		18:07:10		70.41		29		20-Jun-08		18:06:20		69.2		30		20-Jun-08		18:07:53		68.61		31

		20-Jun-08		20:07:10		71		31.5		20-Jun-08		20:06:20		68		34.5		20-Jun-08		20:07:53		68.61		34.5

		20-Jun-08		22:07:10		71		32.5		20-Jun-08		22:06:20		68		36		20-Jun-08		22:07:53		68.61		35

		21-Jun-08		0:07:10		71		34.5		21-Jun-08		0:06:20		68.61		38.5		21-Jun-08		0:07:53		68.61		37

		21-Jun-08		2:07:10		70.41		35		21-Jun-08		2:06:20		67.4		41		21-Jun-08		2:07:53		68.61		37

		21-Jun-08		4:07:10		70.41		36		21-Jun-08		4:06:20		67.4		41		21-Jun-08		4:07:53		69.2		37.5

		21-Jun-08		6:07:10		69.8		36		21-Jun-08		6:06:20		68		43		21-Jun-08		6:07:53		68.61		38.5

		21-Jun-08		8:07:10		71		36		21-Jun-08		8:06:20		68.61		43		21-Jun-08		8:07:53		68.61		39

		21-Jun-08		10:07:10		71		35		21-Jun-08		10:06:20		69.2		37		21-Jun-08		10:07:53		69.2		37

		21-Jun-08		12:07:10		70.41		30.5		21-Jun-08		12:06:20		71		31.5		21-Jun-08		12:07:53		69.2		33

		21-Jun-08		14:07:10		71		30		21-Jun-08		14:06:20		70.41		30.5		21-Jun-08		14:07:53		69.2		31.5

		21-Jun-08		16:07:10		71		26.5		21-Jun-08		16:06:20		71.6		26.5		21-Jun-08		16:07:53		68.61		29

		21-Jun-08		18:07:10		70.41		23		21-Jun-08		18:06:20		70.41		24		21-Jun-08		18:07:53		69.2		26

		21-Jun-08		20:07:10		71		22.5		21-Jun-08		20:06:20		71		22.5		21-Jun-08		20:07:53		69.2		24.5

		21-Jun-08		22:07:10		71		27.5		21-Jun-08		22:06:20		70.41		29		21-Jun-08		22:07:53		69.2		30

		22-Jun-08		0:07:10		71		31		22-Jun-08		0:06:20		70.41		34		22-Jun-08		0:07:53		68.61		34.5

		22-Jun-08		2:07:10		71		31.5		22-Jun-08		2:06:20		69.8		35		22-Jun-08		2:07:53		68.61		35.5

		22-Jun-08		4:07:10		71		32.5		22-Jun-08		4:06:20		69.8		34.5		22-Jun-08		4:07:53		68.61		35.5

		22-Jun-08		6:07:10		70.41		33		22-Jun-08		6:06:20		69.2		35.5		22-Jun-08		6:07:53		68.61		35.5

		22-Jun-08		8:07:10		71		33.5		22-Jun-08		8:06:20		69.2		36.5		22-Jun-08		8:07:53		69.8		35.5

		22-Jun-08		10:07:10		71		34.5		22-Jun-08		10:06:20		70.41		37		22-Jun-08		10:07:53		69.8		37

		22-Jun-08		12:07:10		71.6		32		22-Jun-08		12:06:20		71		34.5		22-Jun-08		12:07:53		69.2		36

		22-Jun-08		14:07:10		71.6		29.5		22-Jun-08		14:06:20		71		32.5		22-Jun-08		14:07:53		69.8		33.5

		22-Jun-08		16:07:10		72.21		26		22-Jun-08		16:06:20		70.41		29		22-Jun-08		16:07:53		69.2		30.5

		22-Jun-08		18:07:10		72.21		22.5		22-Jun-08		18:06:20		70.41		25.5		22-Jun-08		18:07:53		69.2		26.5

		22-Jun-08		20:07:10		72.21		30.5		22-Jun-08		20:06:20		70.41		31.5		22-Jun-08		20:07:53		69.8		31.5

		22-Jun-08		22:07:10		71.6		31		22-Jun-08		22:06:20		70.41		34.5		22-Jun-08		22:07:53		69.2		34

		23-Jun-08		0:07:10		71		34.5		23-Jun-08		0:06:20		69.2		39		23-Jun-08		0:07:53		69.2		36.5

		23-Jun-08		2:07:10		70.41		35.5		23-Jun-08		2:06:20		69.8		41.5		23-Jun-08		2:07:53		69.2		38

		23-Jun-08		4:07:10		70.41		36		23-Jun-08		4:06:20		69.2		42		23-Jun-08		4:07:53		69.8		38

		23-Jun-08		6:07:10		70.41		35.5		23-Jun-08		6:06:20		68.61		42		23-Jun-08		6:07:53		69.8		37.5

		23-Jun-08		8:07:10		70.41		37		23-Jun-08		8:06:20		69.2		44		23-Jun-08		8:07:53		69.8		38.5

		23-Jun-08		10:07:10		71		38		23-Jun-08		10:06:20		69.2		45		23-Jun-08		10:07:53		69.8		39.5

		23-Jun-08		12:07:10		71		38.5		23-Jun-08		12:06:20		69.8		42.5		23-Jun-08		12:07:53		69.8		39.5

		23-Jun-08		14:07:10		71		39		23-Jun-08		14:06:20		70.41		44.5		23-Jun-08		14:07:53		69.8		41

		23-Jun-08		16:07:10		71.6		39.5		23-Jun-08		16:06:20		69.8		46.5		23-Jun-08		16:07:53		69.8		42

		23-Jun-08		18:07:10		71.6		38		23-Jun-08		18:06:20		70.41		42.5		23-Jun-08		18:07:53		69.2		41

		23-Jun-08		20:07:10		71.6		37		23-Jun-08		20:06:20		69.8		43		23-Jun-08		20:07:53		69.8		39.5

		23-Jun-08		22:07:10		71		36		23-Jun-08		22:06:20		69.2		42.5		23-Jun-08		22:07:53		69.8		38.5

		24-Jun-08		0:07:10		69.8		36.5		24-Jun-08		0:06:20		69.2		42		24-Jun-08		0:07:53		69.2		38.5

		24-Jun-08		2:07:10		70.41		36.5		24-Jun-08		2:06:20		68.61		42		24-Jun-08		2:07:53		69.8		38

		24-Jun-08		4:07:10		70.41		36		24-Jun-08		4:06:20		68		42.5		24-Jun-08		4:07:53		69.8		37.5

		24-Jun-08		6:07:10		70.41		37.5		24-Jun-08		6:06:20		67.4		45.5		24-Jun-08		6:07:53		69.8		38.5

		24-Jun-08		8:07:10		70.41		38.5		24-Jun-08		8:06:20		69.8		44.5		24-Jun-08		8:07:53		69.8		40

		24-Jun-08		10:07:10		70.41		38		24-Jun-08		10:06:20		71		44		24-Jun-08		10:07:53		69.2		40.5

		24-Jun-08		12:07:10		70.41		39.5		24-Jun-08		12:06:20		71.6		42.5		24-Jun-08		12:07:53		69.8		41

		24-Jun-08		14:07:10		70.41		38.5		24-Jun-08		14:06:20		71		42.5		24-Jun-08		14:07:53		68		42.5

		24-Jun-08		16:07:10		71		39		24-Jun-08		16:06:20		69.2		47		24-Jun-08		16:07:53		68		42.5

		24-Jun-08		18:07:10		71		38.5		24-Jun-08		18:06:20		69.2		45.5		24-Jun-08		18:07:53		69.2		41.5

		24-Jun-08		20:07:10		70.41		38.5		24-Jun-08		20:06:20		68.61		47		24-Jun-08		20:07:53		69.2		40.5

		24-Jun-08		22:07:10		70.41		38		24-Jun-08		22:06:20		68.61		44		24-Jun-08		22:07:53		69.2		39.5

		25-Jun-08		0:07:10		70.41		38.5		25-Jun-08		0:06:20		68		43.5		25-Jun-08		0:07:53		69.2		40

		25-Jun-08		2:07:10		70.41		37.5		25-Jun-08		2:06:20		67.4		46.5		25-Jun-08		2:07:53		69.8		39

		25-Jun-08		4:07:10		70.41		37.5		25-Jun-08		4:06:20		67.4		45		25-Jun-08		4:07:53		69.8		39

		25-Jun-08		6:07:10		70.41		37		25-Jun-08		6:06:20		66.81		45		25-Jun-08		6:07:53		69.8		38.5

		25-Jun-08		8:07:10		69.8		38.5		25-Jun-08		8:06:20		68		44		25-Jun-08		8:07:53		68.61		40.5

		25-Jun-08		10:07:10		70.41		39		25-Jun-08		10:06:20		69.8		46.5		25-Jun-08		10:07:53		68.61		42

		25-Jun-08		12:07:10		70.41		40.5		25-Jun-08		12:06:20		69.8		44		25-Jun-08		12:07:53		68		43.5

		25-Jun-08		14:07:10		70.41		42		25-Jun-08		14:06:20		69.8		47		25-Jun-08		14:07:53		67.4		46.5

		25-Jun-08		16:07:10		70.41		41.5		25-Jun-08		16:06:20		69.8		50		25-Jun-08		16:07:53		68.61		45

		25-Jun-08		18:07:10		71		39.5		25-Jun-08		18:06:20		69.2		48		25-Jun-08		18:07:53		68.61		43.5

		25-Jun-08		20:07:10		71		38.5		25-Jun-08		20:06:20		69.2		44		25-Jun-08		20:07:53		69.2		42

		25-Jun-08		22:07:10		71		38		25-Jun-08		22:06:20		69.8		43.5		25-Jun-08		22:07:53		69.2		40.5

		26-Jun-08		0:07:10		70.41		38		26-Jun-08		0:06:20		68.61		46		26-Jun-08		0:07:53		69.2		40

		26-Jun-08		2:07:10		69.8		38		26-Jun-08		2:06:20		68.61		44.5		26-Jun-08		2:07:53		68.61		39.5

		26-Jun-08		4:07:10		70.41		38		26-Jun-08		4:06:20		68.61		44		26-Jun-08		4:07:53		69.2		39.5

		26-Jun-08		6:07:10		70.41		37.5		26-Jun-08		6:06:20		68		44.5		26-Jun-08		6:07:53		69.8		39

		26-Jun-08		8:07:10		70.41		39		26-Jun-08		8:06:20		69.2		44		26-Jun-08		8:07:53		68		41.5

		26-Jun-08		10:07:10		70.41		39		26-Jun-08		10:06:20		69.2		45		26-Jun-08		10:07:53		68.61		41.5

		26-Jun-08		12:07:10		70.41		40.5		26-Jun-08		12:06:20		71		43.5		26-Jun-08		12:07:53		68.61		43

		26-Jun-08		14:07:10		70.41		42.5		26-Jun-08		14:06:20		70.41		47.5		26-Jun-08		14:07:53		68		46

		26-Jun-08		16:07:10		70.41		42.5		26-Jun-08		16:06:20		68.61		49.5		26-Jun-08		16:07:53		68.61		45.5

		26-Jun-08		18:07:10		70.41		41.5		26-Jun-08		18:06:20		69.2		47		26-Jun-08		18:07:53		69.2		43.5

		26-Jun-08		20:07:10		70.41		40		26-Jun-08		20:06:20		69.2		47.5		26-Jun-08		20:07:53		69.2		42

		26-Jun-08		22:07:10		70.41		39		26-Jun-08		22:06:20		69.2		46.5		26-Jun-08		22:07:53		69.2		41

		27-Jun-08		0:07:10		69.8		38		27-Jun-08		0:06:20		68		47.5		27-Jun-08		0:07:53		68.61		40.5

		27-Jun-08		2:07:10		69.8		38		27-Jun-08		2:06:20		67.4		46		27-Jun-08		2:07:53		69.2		40

		27-Jun-08		4:07:10		70.41		38		27-Jun-08		4:06:20		68		45		27-Jun-08		4:07:53		69.8		39

		27-Jun-08		6:07:10		69.8		37.5		27-Jun-08		6:06:20		67.4		45		27-Jun-08		6:07:53		69.8		39

		27-Jun-08		8:07:10		70.41		39		27-Jun-08		8:06:20		68.61		49.5		27-Jun-08		8:07:53		69.2		40.5

		27-Jun-08		10:07:10		70.41		39.5		27-Jun-08		10:06:20		69.8		44.5		27-Jun-08		10:07:53		68.61		42

		27-Jun-08		12:07:10		70.41		41		27-Jun-08		12:06:20		70.41		50.5		27-Jun-08		12:07:53		69.2		43

		27-Jun-08		14:07:10		70.41		43		27-Jun-08		14:06:20		71		48.5		27-Jun-08		14:07:53		68		46

		27-Jun-08		16:07:10		70.41		42.5		27-Jun-08		16:06:20		70.41		48.5		27-Jun-08		16:07:53		68		46

		27-Jun-08		18:07:10		70.41		40		27-Jun-08		18:06:20		70.41		44		27-Jun-08		18:07:53		68.61		43

		27-Jun-08		20:07:10		70.41		39		27-Jun-08		20:06:20		70.41		44.5		27-Jun-08		20:07:53		68.61		42

		27-Jun-08		22:07:10		70.41		38.5		27-Jun-08		22:06:20		70.41		45		27-Jun-08		22:07:53		69.2		41

		28-Jun-08		0:07:10		69.8		38.5		28-Jun-08		0:06:20		69.2		46		28-Jun-08		0:07:53		68.61		41

		28-Jun-08		2:07:10		69.8		38.5		28-Jun-08		2:06:20		69.2		45		28-Jun-08		2:07:53		68.61		40.5

		28-Jun-08		4:07:10		69.2		38.5		28-Jun-08		4:06:20		69.2		44.5		28-Jun-08		4:07:53		68.61		40

		28-Jun-08		6:07:10		69.2		39.5		28-Jun-08		6:06:20		69.2		45.5		28-Jun-08		6:07:53		68.61		40.5

		28-Jun-08		8:07:10		69.8		39.5		28-Jun-08		8:06:20		70.41		44		28-Jun-08		8:07:53		68.61		41.5

		28-Jun-08		10:07:10		71		40.5		28-Jun-08		10:06:20		71		50.5		28-Jun-08		10:07:53		68.61		43

		28-Jun-08		12:07:10		70.41		42.5		28-Jun-08		12:06:20		71.6		48		28-Jun-08		12:07:53		69.8		44

		28-Jun-08		14:07:10		70.41		43.5		28-Jun-08		14:06:20		71.6		53.5		28-Jun-08		14:07:53		68.61		46

		28-Jun-08		16:07:10		70.41		44		28-Jun-08		16:06:20		71		50		28-Jun-08		16:07:53		69.2		46.5

		28-Jun-08		18:07:10		71		40.5		28-Jun-08		18:06:20		70.41		51		28-Jun-08		18:07:53		69.2		43.5

		28-Jun-08		20:07:10		71		39.5		28-Jun-08		20:06:20		70.41		49.5		28-Jun-08		20:07:53		69.2		42

		28-Jun-08		22:07:10		70.41		39.5		28-Jun-08		22:06:20		69.8		49		28-Jun-08		22:07:53		69.8		41

		29-Jun-08		0:07:10		69.8		39.5		29-Jun-08		0:06:20		69.8		49.5		29-Jun-08		0:07:53		69.2		41.5

		29-Jun-08		2:07:10		69.8		40		29-Jun-08		2:06:20		69.2		49		29-Jun-08		2:07:53		69.2		41.5

		29-Jun-08		4:07:10		69.8		40		29-Jun-08		4:06:20		69.2		50		29-Jun-08		4:07:53		69.8		41.5

		29-Jun-08		6:07:10		69.8		40		29-Jun-08		6:06:20		69.2		50.5		29-Jun-08		6:07:53		69.8		41

		29-Jun-08		8:07:10		69.8		40		29-Jun-08		8:06:20		69.8		50.5		29-Jun-08		8:07:53		69.8		41.5

		29-Jun-08		10:07:10		70.41		40.5		29-Jun-08		10:06:20		69.2		47		29-Jun-08		10:07:53		69.8		41.5

		29-Jun-08		12:07:10		70.41		41.5		29-Jun-08		12:06:20		69.2		53.5		29-Jun-08		12:07:53		69.8		42.5

		29-Jun-08		14:07:10		70.41		42.5		29-Jun-08		14:06:20		69.8		48		29-Jun-08		14:07:53		70.41		44

		29-Jun-08		16:07:10		71		43		29-Jun-08		16:06:20		69.8		52.5		29-Jun-08		16:07:53		70.41		44.5

		29-Jun-08		18:07:10		71		42		29-Jun-08		18:06:20		70.41		53		29-Jun-08		18:07:53		70.41		44

		29-Jun-08		20:07:10		71		40		29-Jun-08		20:06:20		69.2		52		29-Jun-08		20:07:53		69.8		42

		29-Jun-08		22:07:10		70.41		39.5		29-Jun-08		22:06:20		69.2		50		29-Jun-08		22:07:53		69.8		41

		30-Jun-08		0:07:10		69.2		40		30-Jun-08		0:06:20		69.2		48.5		30-Jun-08		0:07:53		69.2		41

		30-Jun-08		2:07:10		69.2		40		30-Jun-08		2:06:20		69.2		48.5		30-Jun-08		2:07:53		69.8		41

		30-Jun-08		4:07:10		69.2		40		30-Jun-08		4:06:20		69.2		49		30-Jun-08		4:07:53		69.2		41

		30-Jun-08		6:07:10		69.2		40		30-Jun-08		6:06:20		69.2		49		30-Jun-08		6:07:53		69.2		41

		30-Jun-08		8:07:10		69.2		40		30-Jun-08		8:06:20		69.2		49		30-Jun-08		8:07:53		69.8		41

		30-Jun-08		10:07:10		69.2		40		30-Jun-08		10:06:20		69.8		47.5		30-Jun-08		10:07:53		69.8		41

		30-Jun-08		12:07:10		70.41		41.5		30-Jun-08		12:06:20		69.8		49.5		30-Jun-08		12:07:53		70.41		42

		30-Jun-08		14:07:10		70.41		43		30-Jun-08		14:06:20		70.41		48		30-Jun-08		14:07:53		70.41		43.5

		30-Jun-08		16:07:10		71		43		30-Jun-08		16:06:20		70.41		50.5		30-Jun-08		16:07:53		70.41		44.5

		30-Jun-08		18:07:10		71		41.5		30-Jun-08		18:06:20		69.8		50		30-Jun-08		18:07:53		70.41		43.5

		30-Jun-08		20:07:10		71		40		30-Jun-08		20:06:20		69.8		50		30-Jun-08		20:07:53		70.41		42

		30-Jun-08		22:07:10		69.8		39.5		30-Jun-08		22:06:20		69.8		48.5		30-Jun-08		22:07:53		69.8		40.5

		1-Jul-08		0:07:10		69.8		40		1-Jul-08		0:06:20		69.2		48.5		1-Jul-08		0:07:53		69.2		41

		1-Jul-08		2:07:10		69.2		40		1-Jul-08		2:06:20		69.2		48.5		1-Jul-08		2:07:53		69.2		41

		1-Jul-08		4:07:10		69.8		40.5		1-Jul-08		4:06:20		68.61		49		1-Jul-08		4:07:53		69.8		41

		1-Jul-08		6:07:10		69.8		40		1-Jul-08		6:06:20		68.61		49.5		1-Jul-08		6:07:53		69.8		41

		1-Jul-08		8:07:10		70.41		40.5		1-Jul-08		8:06:20		71		48.5		1-Jul-08		8:07:53		69.8		41

		1-Jul-08		10:07:10		70.41		40		1-Jul-08		10:06:20		71		47.5		1-Jul-08		10:07:53		69.8		41.5

		1-Jul-08		12:07:10		70.41		42		1-Jul-08		12:06:20		70.41		46		1-Jul-08		12:07:53		70.41		43.5

		1-Jul-08		14:07:10		71		44		1-Jul-08		14:06:20		70.41		48		1-Jul-08		14:07:53		69.8		45

		1-Jul-08		16:07:10		70.41		44.5		1-Jul-08		16:06:20		70.41		57.5		1-Jul-08		16:07:53		69.2		47

		1-Jul-08		18:07:10		71		43		1-Jul-08		18:06:20		70.41		53		1-Jul-08		18:07:53		69.2		45.5

		1-Jul-08		20:07:10		71		41		1-Jul-08		20:06:20		70.41		53.5		1-Jul-08		20:07:53		69.2		44

		1-Jul-08		22:07:10		71		40		1-Jul-08		22:06:20		69.8		52		1-Jul-08		22:07:53		69.8		42

		2-Jul-08		0:07:10		70.41		40		2-Jul-08		0:06:20		69.2		52		2-Jul-08		0:07:53		69.2		41.5

		2-Jul-08		2:07:10		69.8		40		2-Jul-08		2:06:20		69.2		52		2-Jul-08		2:07:53		69.2		42

		2-Jul-08		4:07:10		69.8		40		2-Jul-08		4:06:20		69.8		51.5		2-Jul-08		4:07:53		69.8		41.5

		2-Jul-08		6:07:10		69.8		40.5		2-Jul-08		6:06:20		69.2		53		2-Jul-08		6:07:53		69.2		42

		2-Jul-08		8:07:10		70.41		41		2-Jul-08		8:06:20		70.41		49		2-Jul-08		8:07:53		69.2		42.5

		2-Jul-08		10:07:10		70.41		40.5		2-Jul-08		10:06:20		69.8		46.5		2-Jul-08		10:07:53		69.8		42

		2-Jul-08		12:07:10		71		42.5		2-Jul-08		12:06:20		70.41		54		2-Jul-08		12:07:53		69.8		43.5

		2-Jul-08		14:07:10		70.41		44.5		2-Jul-08		14:06:20		70.41		50.5		2-Jul-08		14:07:53		69.2		46.5

		2-Jul-08		16:07:10		71		44.5		2-Jul-08		16:06:20		70.41		57.5		2-Jul-08		16:07:53		69.2		47

		2-Jul-08		18:07:10		71		43		2-Jul-08		18:06:20		69.8		49		2-Jul-08		18:07:53		69.8		45

		2-Jul-08		20:07:10		71		41		2-Jul-08		20:06:20		69.8		52		2-Jul-08		20:07:53		69.8		43

		2-Jul-08		22:07:10		70.41		40		2-Jul-08		22:06:20		69.8		49.5		2-Jul-08		22:07:53		69.8		41.5

		3-Jul-08		0:07:10		69.2		40		3-Jul-08		0:06:20		69.8		49		3-Jul-08		0:07:53		69.2		41.5

		3-Jul-08		2:07:10		70.41		40		3-Jul-08		2:06:20		69.2		48		3-Jul-08		2:07:53		69.8		41

		3-Jul-08		4:07:10		70.41		40		3-Jul-08		4:06:20		68.61		49		3-Jul-08		4:07:53		69.8		41

		3-Jul-08		6:07:10		69.8		40		3-Jul-08		6:06:20		68		49.5		3-Jul-08		6:07:53		69.8		41

		3-Jul-08		8:07:10		70.41		40.5		3-Jul-08		8:06:20		69.8		49		3-Jul-08		8:07:53		69.8		41.5

		3-Jul-08		10:07:10		70.41		41		3-Jul-08		10:06:20		70.41		45		3-Jul-08		10:07:53		69.8		41.5

		3-Jul-08		12:07:10		70.41		43		3-Jul-08		12:06:20		71		45.5		3-Jul-08		12:07:53		69.8		43.5

		3-Jul-08		14:07:10		70.41		44.5		3-Jul-08		14:06:20		71		47		3-Jul-08		14:07:53		69.2		46

		3-Jul-08		16:07:10		70.41		44		3-Jul-08		16:06:20		69.8		53		3-Jul-08		16:07:53		69.2		46

		3-Jul-08		18:07:10		70.41		43		3-Jul-08		18:06:20		70.41		49		3-Jul-08		18:07:53		69.8		44.5

		3-Jul-08		20:07:10		70.41		41.5		3-Jul-08		20:06:20		70.41		51.5		3-Jul-08		20:07:53		69.8		43.5

		3-Jul-08		22:07:10		71		40		3-Jul-08		22:06:20		69.2		51		3-Jul-08		22:07:53		69.8		42

		4-Jul-08		0:07:10		69.8		39.5		4-Jul-08		0:06:20		69.2		49.5		4-Jul-08		0:07:53		69.2		41.5

		4-Jul-08		2:07:10		69.2		40.5		4-Jul-08		2:06:20		69.2		47.5		4-Jul-08		2:07:53		69.2		41.5

		4-Jul-08		4:07:10		69.8		40		4-Jul-08		4:06:20		68.61		48		4-Jul-08		4:07:53		69.2		41.5

		4-Jul-08		6:07:10		69.8		39.5		4-Jul-08		6:06:20		69.8		44		4-Jul-08		6:07:53		69.2		41.5

		4-Jul-08		8:07:10		69.8		40		4-Jul-08		8:06:20		69.8		50.5		4-Jul-08		8:07:53		69.2		41.5

		4-Jul-08		10:07:10		71		42		4-Jul-08		10:06:20		69.8		50.5		4-Jul-08		10:07:53		69.2		43

		4-Jul-08		12:07:10		70.41		47		4-Jul-08		12:06:20		71.6		55		4-Jul-08		12:07:53		69.2		48

		4-Jul-08		14:07:10		71		47.5		4-Jul-08		14:06:20		71		55		4-Jul-08		14:07:53		69.2		50

		4-Jul-08		16:07:10		71		48		4-Jul-08		16:06:20		71.6		57		4-Jul-08		16:07:53		69.2		50

		4-Jul-08		18:07:10		71.6		46		4-Jul-08		18:06:20		71.6		54		4-Jul-08		18:07:53		69.2		49.5

		4-Jul-08		20:07:10		71.6		43.5		4-Jul-08		20:06:20		71.6		59		4-Jul-08		20:07:53		69.2		46.5

		4-Jul-08		22:07:10		71		41.5		4-Jul-08		22:06:20		69.8		56.5		4-Jul-08		22:07:53		69.2		45

		5-Jul-08		0:07:10		70.41		42		5-Jul-08		0:06:20		69.8		56.5		5-Jul-08		0:07:53		68.61		44.5

		5-Jul-08		2:07:10		69.8		41		5-Jul-08		2:06:20		69.8		54.5		5-Jul-08		2:07:53		69.2		43.5

		5-Jul-08		4:07:10		69.8		41		5-Jul-08		4:06:20		69.2		53		5-Jul-08		4:07:53		69.2		42.5

		5-Jul-08		6:07:10		69.2		41.5		5-Jul-08		6:06:20		68.61		54.5		5-Jul-08		6:07:53		68.61		43

		5-Jul-08		8:07:10		69.8		42		5-Jul-08		8:06:20		69.2		55		5-Jul-08		8:07:53		69.2		44

		5-Jul-08		10:07:10		71		43		5-Jul-08		10:06:20		69.8		51.5		5-Jul-08		10:07:53		69.2		45

		5-Jul-08		12:07:10		71		45		5-Jul-08		12:06:20		69.8		53.5		5-Jul-08		12:07:53		69.2		47.5

		5-Jul-08		14:07:10		71.6		45.5		5-Jul-08		14:06:20		70.41		55		5-Jul-08		14:07:53		69.2		48.5

		5-Jul-08		16:07:10		71.6		46		5-Jul-08		16:06:20		70.41		55.5		5-Jul-08		16:07:53		69.2		49.5

		5-Jul-08		18:07:10		71.6		45		5-Jul-08		18:06:20		70.41		59.5		5-Jul-08		18:07:53		68.61		48.5

		5-Jul-08		20:07:10		71		42.5		5-Jul-08		20:06:20		69.8		58		5-Jul-08		20:07:53		69.2		46

		5-Jul-08		22:07:10		71		41.5		5-Jul-08		22:06:20		69.2		57.5		5-Jul-08		22:07:53		69.2		45

		6-Jul-08		0:07:10		70.41		41		6-Jul-08		0:06:20		69.2		56		6-Jul-08		0:07:53		69.2		43.5

		6-Jul-08		2:07:10		69.8		40.5		6-Jul-08		2:06:20		68.61		54.5		6-Jul-08		2:07:53		68.61		43

		6-Jul-08		4:07:10		69.8		40.5		6-Jul-08		4:06:20		69.2		52.5		6-Jul-08		4:07:53		68.61		42.5

		6-Jul-08		6:07:10		69.2		41.5		6-Jul-08		6:06:20		69.2		51.5		6-Jul-08		6:07:53		68.61		42.5

		6-Jul-08		8:07:10		69.8		41.5		6-Jul-08		8:06:20		69.2		53		6-Jul-08		8:07:53		68.61		43.5

		6-Jul-08		10:07:10		71		43		6-Jul-08		10:06:20		69.8		55.5		6-Jul-08		10:07:53		69.2		45

		6-Jul-08		12:07:10		71		47		6-Jul-08		12:06:20		70.41		58.5		6-Jul-08		12:07:53		69.2		49

		6-Jul-08		14:07:10		71.6		49		6-Jul-08		14:06:20		70.41		57.5		6-Jul-08		14:07:53		69.2		52

		6-Jul-08		16:07:10		72.21		46		6-Jul-08		16:06:20		70.41		54		6-Jul-08		16:07:53		69.2		51

		6-Jul-08		18:07:10		72.21		47		6-Jul-08		18:06:20		69.8		61		6-Jul-08		18:07:53		69.2		51

		6-Jul-08		20:07:10		72.21		45		6-Jul-08		20:06:20		70.41		54.5		6-Jul-08		20:07:53		69.2		50

		6-Jul-08		22:07:10		72.21		43		6-Jul-08		22:06:20		69.8		62		6-Jul-08		22:07:53		68.61		48

		7-Jul-08		0:07:10		71.6		41.5		7-Jul-08		0:06:20		69.8		57		7-Jul-08		0:07:53		69.2		45

		7-Jul-08		2:07:10		71		41		7-Jul-08		2:06:20		69.8		52		7-Jul-08		2:07:53		69.2		44.5

		7-Jul-08		4:07:10		70.41		41		7-Jul-08		4:06:20		69.2		54		7-Jul-08		4:07:53		69.2		43.5

		7-Jul-08		6:07:10		69.8		40.5		7-Jul-08		6:06:20		69.2		52.5		7-Jul-08		6:07:53		68.61		43

		7-Jul-08		8:07:10		70.41		41.5		7-Jul-08		8:06:20		69.2		53.5		7-Jul-08		8:07:53		69.2		43.5

		7-Jul-08		10:07:10		71		44		7-Jul-08		10:06:20		69.2		58		7-Jul-08		10:07:53		69.2		46

		7-Jul-08		12:07:10		71.6		47.5		7-Jul-08		12:06:20		69.8		62		7-Jul-08		12:07:53		69.2		50

		7-Jul-08		14:07:10		71.6		50.5		7-Jul-08		14:06:20		70.41		59.5		7-Jul-08		14:07:53		69.2		54

		7-Jul-08		16:07:10		72.21		48.5		7-Jul-08		16:06:20		69.8		62		7-Jul-08		16:07:53		69.8		52.5

		7-Jul-08		18:07:10		72.21		46.5		7-Jul-08		18:06:20		70.41		59.5		7-Jul-08		18:07:53		69.2		52

		7-Jul-08		20:07:10		72.21		42.5		7-Jul-08		20:06:20		69.8		55		7-Jul-08		20:07:53		68.61		47.5

		7-Jul-08		22:07:10		72.21		40.5		7-Jul-08		22:06:20		69.8		50		7-Jul-08		22:07:53		69.2		44.5

		8-Jul-08		0:07:10		71		40		8-Jul-08		0:06:20		69.2		52		8-Jul-08		0:07:53		69.2		43.5

		8-Jul-08		2:07:10		70.41		40.5		8-Jul-08		2:06:20		69.2		51		8-Jul-08		2:07:53		69.2		42.5

		8-Jul-08		4:07:10		69.8		40.5		8-Jul-08		4:06:20		68.61		51.5		8-Jul-08		4:07:53		68.61		42.5

		8-Jul-08		6:07:10		69.2		40.5		8-Jul-08		6:06:20		69.2		51.5		8-Jul-08		6:07:53		68.61		42.5

		8-Jul-08		8:07:10		70.41		41.5		8-Jul-08		8:06:20		69.8		53.5		8-Jul-08		8:07:53		68.61		44

		8-Jul-08		10:07:10		71.6		44		8-Jul-08		10:06:20		69.8		50.5		8-Jul-08		10:07:53		68.61		47.5

		8-Jul-08		12:07:10		71		49		8-Jul-08		12:06:20		69.8		54		8-Jul-08		12:07:53		69.2		51

		8-Jul-08		14:07:10		71		49.5		8-Jul-08		14:06:20		70.41		55.5		8-Jul-08		14:07:53		69.2		53.5

		8-Jul-08		16:07:10		71		50		8-Jul-08		16:06:20		70.41		58.5		8-Jul-08		16:07:53		68.61		53.5

		8-Jul-08		18:07:10		71		49		8-Jul-08		18:06:20		70.41		55.5		8-Jul-08		18:07:53		68.61		52.5

		8-Jul-08		20:07:10		71		45		8-Jul-08		20:06:20		71		57.5		8-Jul-08		20:07:53		68		50

		8-Jul-08		22:07:10		71.6		43		8-Jul-08		22:06:20		70.41		53		8-Jul-08		22:07:53		68.61		47.5

		9-Jul-08		0:07:10		71.6		42		9-Jul-08		0:06:20		70.41		52		9-Jul-08		0:07:53		69.2		46

		9-Jul-08		2:07:10		71		41.5		9-Jul-08		2:06:20		69.8		50		9-Jul-08		2:07:53		69.2		44.5

		9-Jul-08		4:07:10		71		41.5		9-Jul-08		4:06:20		69.2		53.5		9-Jul-08		4:07:53		69.2		44

		9-Jul-08		6:07:10		70.41		41		9-Jul-08		6:06:20		69.2		52.5		9-Jul-08		6:07:53		69.2		43.5

		9-Jul-08		8:07:10		71		42.5		9-Jul-08		8:06:20		70.41		56.5		9-Jul-08		8:07:53		68.61		45

		9-Jul-08		10:07:10		71		45.5		9-Jul-08		10:06:20		71		53		9-Jul-08		10:07:53		69.2		48.5

		9-Jul-08		12:07:10		71		49		9-Jul-08		12:06:20		71.6		51		9-Jul-08		12:07:53		69.8		50.5

		9-Jul-08		14:07:10		70.41		47.5		9-Jul-08		14:06:20		71.6		51		9-Jul-08		14:07:53		68.61		51

		9-Jul-08		16:07:10		70.41		49		9-Jul-08		16:06:20		71.6		52.5		9-Jul-08		16:07:53		69.8		50

		9-Jul-08		18:07:10		70.41		48.5		9-Jul-08		18:06:20		70.41		53		9-Jul-08		18:07:53		69.8		50

		9-Jul-08		20:07:10		71		44		9-Jul-08		20:06:20		71		53		9-Jul-08		20:07:53		69.2		47.5

		9-Jul-08		22:07:10		71.6		43		9-Jul-08		22:06:20		70.41		54		9-Jul-08		22:07:53		69.8		46

		10-Jul-08		0:07:10		71.6		42		10-Jul-08		0:06:20		69.8		54.5		10-Jul-08		0:07:53		69.2		45

		10-Jul-08		2:07:10		71.6		41.5		10-Jul-08		2:06:20		69.8		54		10-Jul-08		2:07:53		69.8		44

		10-Jul-08		4:07:10		71		42		10-Jul-08		4:06:20		69.2		58		10-Jul-08		4:07:53		69.8		44

		10-Jul-08		6:07:10		71		41.5		10-Jul-08		6:06:20		69.8		55.5		10-Jul-08		6:07:53		69.8		43.5

		10-Jul-08		8:07:10		71		42.5		10-Jul-08		8:06:20		69.8		58.5		10-Jul-08		8:07:53		69.8		45

		10-Jul-08		10:07:10		71		44.5		10-Jul-08		10:06:20		69.8		58.5		10-Jul-08		10:07:53		68		48.5

		10-Jul-08		12:07:10		70.41		49		10-Jul-08		12:06:20		69.8		56.5		10-Jul-08		12:07:53		69.2		50.5

		10-Jul-08		14:07:10		70.41		52.5		10-Jul-08		14:06:20		71.6		54		10-Jul-08		14:07:53		69.2		54.5

		10-Jul-08		16:07:10		70.41		51		10-Jul-08		16:06:20		71.6		60		10-Jul-08		16:07:53		68.61		54

		10-Jul-08		18:07:10		70.41		49.5		10-Jul-08		18:06:20		70.41		63		10-Jul-08		18:07:53		69.8		51

		10-Jul-08		20:07:10		71		46		10-Jul-08		20:06:20		70.41		58.5		10-Jul-08		20:07:53		69.8		48.5

		10-Jul-08		22:07:10		71.6		43.5		10-Jul-08		22:06:20		70.41		57		10-Jul-08		22:07:53		69.8		47

		11-Jul-08		0:07:10		71.6		42.5		11-Jul-08		0:06:20		69.8		61		11-Jul-08		0:07:53		69.2		46.5

		11-Jul-08		2:07:10		71.6		42.5		11-Jul-08		2:06:20		69.8		53.5		11-Jul-08		2:07:53		69.8		45.5

		11-Jul-08		4:07:10		71		42		11-Jul-08		4:06:20		69.8		53.5		11-Jul-08		4:07:53		69.2		44.5

		11-Jul-08		6:07:10		71		41.5		11-Jul-08		6:06:20		69.8		57		11-Jul-08		6:07:53		69.2		44.5

		11-Jul-08		8:07:10		71		42.5		11-Jul-08		8:06:20		71.6		49		11-Jul-08		8:07:53		69.8		45

		11-Jul-08		10:07:10		71		45.5		11-Jul-08		10:06:20		72.21		56.5		11-Jul-08		10:07:53		68.61		48

		11-Jul-08		12:07:10		71		48.5		11-Jul-08		12:06:20		69.8		63		11-Jul-08		12:07:53		69.2		50.5

		11-Jul-08		14:07:10		71		49.5		11-Jul-08		14:06:20		70.41		55.5		11-Jul-08		14:07:53		69.2		52.5

		11-Jul-08		16:07:10		71		47		11-Jul-08		16:06:20		69.8		63.5		11-Jul-08		16:07:53		69.2		49.5

		11-Jul-08		18:07:10		71		45		11-Jul-08		18:06:20		70.41		54		11-Jul-08		18:07:53		69.2		47.5

		11-Jul-08		20:07:10		71		42.5		11-Jul-08		20:06:20		70.41		53		11-Jul-08		20:07:53		69.2		45.5

		11-Jul-08		22:07:10		71		40.5		11-Jul-08		22:06:20		70.41		52.5		11-Jul-08		22:07:53		69.8		43.5

		12-Jul-08		0:07:10		70.41		41		12-Jul-08		0:06:20		69.2		53		12-Jul-08		0:07:53		69.2		43

		12-Jul-08		2:07:10		70.41		41		12-Jul-08		2:06:20		69.2		52.5		12-Jul-08		2:07:53		69.8		42.5

		12-Jul-08		4:07:10		69.8		40.5		12-Jul-08		4:06:20		69.2		52.5		12-Jul-08		4:07:53		69.2		42.5

		12-Jul-08		6:07:10		69.8		40.5		12-Jul-08		6:06:20		69.2		52.5		12-Jul-08		6:07:53		69.2		42.5

		12-Jul-08		8:07:10		70.41		41.5		12-Jul-08		8:06:20		69.2		55		12-Jul-08		8:07:53		69.2		43

		12-Jul-08		10:07:10		71		42.5		12-Jul-08		10:06:20		69.2		57.5		12-Jul-08		10:07:53		69.2		44.5

		12-Jul-08		12:07:10		71		45.5		12-Jul-08		12:06:20		68.61		53.5		12-Jul-08		12:07:53		69.8		46.5

		12-Jul-08		14:07:10		70.41		45.5		12-Jul-08		14:06:20		69.2		52.5		12-Jul-08		14:07:53		69.8		47.5

		12-Jul-08		16:07:10		70.41		45.5		12-Jul-08		16:06:20		69.2		63.5		12-Jul-08		16:07:53		69.8		47.5

		12-Jul-08		18:07:10		70.41		44.5		12-Jul-08		18:06:20		69.8		54		12-Jul-08		18:07:53		70.41		46.5

		12-Jul-08		20:07:10		71		42.5		12-Jul-08		20:06:20		70.41		54		12-Jul-08		20:07:53		70.41		45

		12-Jul-08		22:07:10		71		42.5		12-Jul-08		22:06:20		69.8		59.5		12-Jul-08		22:07:53		70.41		44.5

		13-Jul-08		0:07:10		71		42.5		13-Jul-08		0:06:20		69.8		60		13-Jul-08		0:07:53		69.8		44

		13-Jul-08		2:07:10		71		42.5		13-Jul-08		2:06:20		69.2		60.5		13-Jul-08		2:07:53		70.41		44.5

		13-Jul-08		4:07:10		71		42.5		13-Jul-08		4:06:20		69.2		60		13-Jul-08		4:07:53		70.41		44.5

		13-Jul-08		6:07:10		71		42.5		13-Jul-08		6:06:20		69.2		61		13-Jul-08		6:07:53		70.41		44.5

		13-Jul-08		8:07:10		71		42.5		13-Jul-08		8:06:20		68.61		59		13-Jul-08		8:07:53		69.8		44

		13-Jul-08		10:07:10		71		43		13-Jul-08		10:06:20		69.2		59.5		13-Jul-08		10:07:53		70.41		44.5

		13-Jul-08		12:07:10		71		45		13-Jul-08		12:06:20		69.2		59		13-Jul-08		12:07:53		69.8		46

		13-Jul-08		14:07:10		71		45		13-Jul-08		14:06:20		70.41		54		13-Jul-08		14:07:53		69.8		47

		13-Jul-08		16:07:10		71.6		44.5		13-Jul-08		16:06:20		69.8		55.5		13-Jul-08		16:07:53		69.8		47

		13-Jul-08		18:07:10		71.6		44		13-Jul-08		18:06:20		69.2		58.5		13-Jul-08		18:07:53		69.2		47

		13-Jul-08		20:07:10		71.6		43		13-Jul-08		20:06:20		69.2		57.5		13-Jul-08		20:07:53		69.8		46.5

		13-Jul-08		22:07:10		71		42.5		13-Jul-08		22:06:20		69.2		60.5		13-Jul-08		22:07:53		70.41		45.5

		14-Jul-08		0:07:10		71		42.5		14-Jul-08		0:06:20		69.2		58		14-Jul-08		0:07:53		70.41		44.5

		14-Jul-08		2:07:10		70.41		42		14-Jul-08		2:06:20		69.2		52		14-Jul-08		2:07:53		70.41		43.5

		14-Jul-08		4:07:10		70.41		42		14-Jul-08		4:06:20		69.2		57.5		14-Jul-08		4:07:53		69.8		43

		14-Jul-08		6:07:10		69.8		41		14-Jul-08		6:06:20		69.2		55.5		14-Jul-08		6:07:53		69.8		42.5

		14-Jul-08		8:07:10		69.8		42		14-Jul-08		8:06:20		69.2		56.5		14-Jul-08		8:07:53		69.8		43

		14-Jul-08		10:07:10		70.41		44		14-Jul-08		10:06:20		69.2		53.5		14-Jul-08		10:07:53		70.41		44.5

		14-Jul-08		12:07:10		70.41		47		14-Jul-08		12:06:20		69.8		62		14-Jul-08		12:07:53		70.41		47

		14-Jul-08		14:07:10		71		47		14-Jul-08		14:06:20		69.8		59.5		14-Jul-08		14:07:53		70.41		48

		14-Jul-08		16:07:10		71		47		14-Jul-08		16:06:20		69.8		60.5		14-Jul-08		16:07:53		70.41		48.5

		14-Jul-08		18:07:10		71		45		14-Jul-08		18:06:20		70.41		57		14-Jul-08		18:07:53		70.41		47

		14-Jul-08		20:07:10		71		43.5		14-Jul-08		20:06:20		69.8		59.5		14-Jul-08		20:07:53		70.41		46

		14-Jul-08		22:07:10		71		42.5		14-Jul-08		22:06:20		69.2		59.5		14-Jul-08		22:07:53		70.41		44.5

		15-Jul-08		0:07:10		70.41		42		15-Jul-08		0:06:20		69.2		57		15-Jul-08		0:07:53		70.41		43.5

		15-Jul-08		2:07:10		70.41		42		15-Jul-08		2:06:20		68.61		56		15-Jul-08		2:07:53		70.41		43.5

		15-Jul-08		4:07:10		69.8		41.5		15-Jul-08		4:06:20		68.61		59		15-Jul-08		4:07:53		69.8		43

		15-Jul-08		6:07:10		69.8		42		15-Jul-08		6:06:20		69.2		56.5		15-Jul-08		6:07:53		69.8		43

		15-Jul-08		8:07:10		70.41		42		15-Jul-08		8:06:20		68		53.5		15-Jul-08		8:07:53		69.8		43.5

		15-Jul-08		10:07:10		71		42		15-Jul-08		10:06:20		69.2		54.5		15-Jul-08		10:07:53		69.8		44

		15-Jul-08		12:07:10		71		44.5		15-Jul-08		12:06:20		69.2		60		15-Jul-08		12:07:53		69.8		45

		15-Jul-08		14:07:10		71		46.5		15-Jul-08		14:06:20		69.2		62		15-Jul-08		14:07:53		69.2		48.5

		15-Jul-08		16:07:10		70.41		45.5		15-Jul-08		16:06:20		69.2		57.5		15-Jul-08		16:07:53		69.8		47.5

		15-Jul-08		18:07:10		70.41		44.5		15-Jul-08		18:06:20		69.8		54.5		15-Jul-08		18:07:53		69.8		46

		15-Jul-08		20:07:10		71		42.5		15-Jul-08		20:06:20		70.41		53.5		15-Jul-08		20:07:53		69.8		44.5

		15-Jul-08		22:07:10		71		41.5		15-Jul-08		22:06:20		69.2		54.5		15-Jul-08		22:07:53		69.8		43.5

		16-Jul-08		0:07:10		70.41		41.5		16-Jul-08		0:06:20		69.2		57		16-Jul-08		0:07:53		69.2		43

		16-Jul-08		2:07:10		69.8		41.5		16-Jul-08		2:06:20		69.8		55.5		16-Jul-08		2:07:53		69.2		43.5

		16-Jul-08		4:07:10		69.8		41.5		16-Jul-08		4:06:20		68.61		56.5		16-Jul-08		4:07:53		69.2		43

		16-Jul-08		6:07:10		69.8		41		16-Jul-08		6:06:20		69.2		56		16-Jul-08		6:07:53		69.2		43

		16-Jul-08		8:07:10		70.41		41.5		16-Jul-08		8:06:20		68.61		58.5		16-Jul-08		8:07:53		69.2		43

		16-Jul-08		10:07:10		70.41		42		16-Jul-08		10:06:20		69.8		55		16-Jul-08		10:07:53		68.61		44.5

		16-Jul-08		12:07:10		71		42.5		16-Jul-08		12:06:20		69.8		51		16-Jul-08		12:07:53		69.2		44.5

		16-Jul-08		14:07:10		71		44.5		16-Jul-08		14:06:20		69.8		51		16-Jul-08		14:07:53		68.61		47.5

		16-Jul-08		16:07:10		71		45		16-Jul-08		16:06:20		70.41		57		16-Jul-08		16:07:53		68.61		48





		



CER 1 Temperature(°F)

CER 2 Temperature(°F)

CER 3 Temperature(°F)

Date

Temperature (Deg. F)

Figure 9.  CER Temperature



		



CER 1 Humidity(%)

CER 3 Humidity(%)

QA Humidity(%)

CER 2 Humidity(%)

Date

Humidity (%)

Figure 10.  CER Relative Humidity



		






_1294744043.xls
Chart2

		39447		39447		38807		38807		38807		38807		38807

		39478		39478		38837		38837		38837		38837		38837

		39507		39507		38929		38929		38929		38929		38929

		39538		39538		38960		38960		38960		38960		38960

		39568		39568		38990		38990		38990		38990		38990

		39599		39599		39021		39021		39021		39021		39021

		39629		39629		39051		39051		39051		39051		39051

		39660		39660		39082		39082		39082		39082		39082

		39690		39690		39113		39113		39113		39113		39113

		39721		39721		39141		39141		39141		39141		39141

						39172		39172		39172		39172		39172

						39202		39202		39202		39202		39202

						39233		39233		39233		39233		39233

						39240		39240		39240		39240		39240

						39270		39270		39270		39270		39270

						39301		39301		39301		39301		39301

						39332		39332		39332		39332		39332

						39362		39362		39362		39362		39362

						39393		39393		39393		39393		39393

						39423		39423		39423		39423		39423

						39478		39478		39478		39478		39478

						39507		39507		39507		39507		39507

						39538		39538		39538		39538		39538

						39568		39568		39568		39568		39568

						39599		39599		39599		39599		39599

						39629		39629		39629		39629		39629

						39660		39660		39660		39660		39660

						39691		39691		39691		39691		39691

						39721		39721		39721		39721		39721



Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

R&D Bio-Safety Cabinet South (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)

Date

Diff. Pressure (Water Column In.)

Mfg Bio-Safety Cabinet (cfm)

Figure 8.  Bio-Safety Cabinet Differential Pressure - Monthly Average

0.25

0.1

0.25

0.1

0.25

0.1

0.25

0.1

0.25

0.1

0.25

0.1

0.25

0.1

0.2

0.15

0.2

0.15

0.2

0.15

0.6095

0.408

0.6195833333

0.42

0.632

0.4235

0.6431578947

0.4263157895

0.2810909091

0.3094545455

0.428

62.0909090909

1180.3636363636

0.272

0.31835

0.4405

63

1193

0.2758333333

0.32

0.4541666667

62.3333333333

1196.3333333333

0.2817391304

0.32

0.4486956522

60.652173913

1194.9565217391

0.287826087

0.3182608696

0.4469565217

57.9130434783

790.7826086957

0.2854545455

0.32

0.4472727273

59.7894736842

882.5263157895

0.2723809524

0.3180952381

0.4476190476

0

0

0.259047619

0.319047619

0.439047619

0

0



Airstrip Count

		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148

		39206		39206		39206		39148		39148

		39230		39230		39230		39167		39167

		39267		39267		39267		39206		39206

		39297		39297		39297		39230		39230

		39349		39349		39349		39267		39267

		39392		39392		39392		39297		39297

		39427		39427		39427		39349		39349

		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713



CER 1

CER 2

CER3

Alert Level

Action Level

Date

Average CER Count

Figure 1.  Average Airstrip Count

3.625

6

29

10

15

5.375

7.5

28

10

15

13.125

13.25

28.75

10

15

13.25

11

27.75

10

15

4.25

5.25

24.5

10

15

4

1.75

11.75

10

15

4.25

9.25

10

15

19.5

5.5

22.5

10

15

5.75

4.25

13

10

15

3.25

1

4.75

10

15

11.625

8

18.25

10

15

3.875

1.75

10.5

10

15

4.125

2

10

35

45

1.125

0.5

3.5

35

45

3

1.25

6.5

35

45

3.25

0.75

5.25

35

45

2

0.75

2.75

35

45

6.375

1.75

8.25

35

45

13.5

1.25

10.25

35

45

2.6666666667

2.6666666667

11.25

35

45

6.2

4

3.75

35

45

6.2666666667

2

3.75

35

45

7.6666666667

3

7.5

35

45

9.4

2.8888888889

9

35

45

8.4

3.4444444444

6.5

35

45

6.5333333333

2.3333333333

8.5

35

45



Contact Plate Count

		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148

		39206		39206		39206		39148		39148

		39230		39230		39230		39167		39167

		39267		39267		39267		39206		39206

		39297		39297		39297		39230		39230

		39349		39349		39349		39267		39267

		39392		39392		39392		39297		39297

		39427		39427		39427		39392		39392

		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

Alert Level

Action Level

Date

Contact Plate Count

Figure 2. Average Contact Plate Count

1.4285714286

0.25

2.5

10

15

3.7142857143

2.75

4

10

15

1.1428571429

1.75

0.8333333333

10

15

2.4285714286

3

2.5

10

15

2.4285714286

0.75

3.1666666667

10

15

5.5714285714

3.25

5

10

15

5.2857142857

5.2

10

15

2.7142857143

1.5

2

10

15

1.1428571429

0

2

10

15

3.1428571429

1

3.25

10

15

3.4285714286

3.25

2.25

10

15

1.5714285714

0.75

1.5

10

15

1.7142857143

1

2.25

6

7

0.5714285714

0.5

2.25

6

7

1.5714285714

0.5

3

6

7

2

0.75

2.5

6

7

0.7142857143

0.25

1.75

6

7

3.4285714286

1.25

3.25

6

7

4

1

3.75

6

7

1.5333333333

1

3

6

7

2

1

2.25

6

7

1.7333333333

0.6666666667

1.5

6

7

0.9333333333

0.4444444444

1.5

6

7

0.9333333333

0.7777777778

2.5

6

7

1.1333333333

0.6666666667

1.75

6

7

0.9333333333

0.6666666667

1.5

6

7



0.5micron Count

		38776		38776		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126		39126		39126

		39148		39167		39167		39148		39148		39148		39148

		39148		39206		39206		39148		39148		39148		39148

		39167		39230		39230		39167		39167		39167		39167

		39206		39267		39267		39206		39206		39206		39206

		39230		39297		39297		39230		39230		39297		39297

		39267		39349		39349		39267		39267		39349		39349

		39297		39392		39392		39297		39297		39392		39392

		39392		39427		39427		39392		39392		39427		39427

		39545		39545		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

CER 1,3 Alert Level

CER 1,3 Action Level

CER 2 Alert Level

CER 2 Action Level

Date

0.5um/cu ft Count

Figure 3.  Average 0.5mm/cu ft Count

194

383

3263.8

5000

10000

5000

10000

339.5

338.3333333333

1210.4

5000

10000

5000

10000

362.75

719.3333333333

2800.4

5000

10000

5000

10000

688.125

416.3333333333

1999.6

5000

10000

5000

10000

618.75

336.6666666667

2033

5000

10000

5000

10000

692.625

1000

1857.4

5000

10000

5000

10000

401.375

1423.2

5000

10000

5000

10000

523.125

842

2313.2

5000

10000

5000

10000

273

292.3333333333

624.4

5000

10000

5000

10000

588.875

620

1580.4

5000

10000

5000

10000

714

474.6666666667

1255.6

5000

10000

5000

10000

755.625

587.3333333333

1139.8

5000

10000

5000

10000

772.875

643

1484

3800

4500

1250

1500

244

896.6666666667

1571.2

3800

4500

1250

1500

551.75

704.3333333333

2714

3800

4500

1250

1500

678.625

553

1781.8

3800

4500

1250

1500

369.625

300

731.6

3800

4500

1250

1500

664

478

1178.6

3800

4500

1250

1500

835.625

525

1260.6

3800

4500

1250

1500

699

83.7777777778

1354.8

3800

4500

1250

1500

635

204.4444444444

620.8

3800

4500

1250

1500

606

181.3333333333

750.8

3800

4500

1250

1500

606

109.5555555556

474.6

3800

4500

1250

1500

612.0666666667

156.7777777778

659.8

3800

4500

1250

1500

285.1333333333

190.5555555556

945.2

3800

4500

1250

1500

474

216.3333333333

768.6

3800

4500

1250

1500



5.0micron Count

		38776		38776		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148		39148		39148

		39206		39206		39206		39148		39148		39148		39148

		39230		39230		39230		39167		39167		39167		39167

		39267		39267		39267		39206		39206		39267		39267

		39297		39297		39297		39230		39230		39297		39297

		39349		39349		39349		39267		39267		39349		39349

		39392		39392		39392		39297		39297		39392		39392

		39427		39427		39427		39392		39392		39427		39427

		39545		39545		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

CER 1,3 Alert Level

CER 1,3 Action Level

CER 2 Alert Level

CER 2 Action Level

Date

5.0um/cu ft Count

Figure 4.  Average 5.0mm/cu ft Count

14.125

48.6666666667

226.8

30

50

30

50

33.625

49.3333333333

104.4

30

50

30

50

36.25

49

211.4

30

50

30

50

126.75

76.6666666667

305.2

30

50

30

50

67.875

37.3333333333

344.6

30

50

30

50

71.75

72.3333333333

166.4

30

50

30

50

43.5

235

30

50

30

50

65.125

37.3333333333

219.4

30

50

30

50

33.125

31.3333333333

50.6

30

50

30

50

47.75

50.6666666667

99.4

30

50

30

50

43.875

32.3333333333

79.2

30

50

30

50

47.125

44.3333333333

92.8

30

50

30

50

49

43.3333333333

92.2

410

500

90

105

30.75

75.6666666667

129.2

410

500

90

105

78.875

89

258.4

410

500

90

105

60

44

147

410

500

90

105

28.375

22.6666666667

53

410

500

90

105

26.125

20.3333333333

58

410

500

90

105

45.125

24.3333333333

80.8

410

500

90

105

37.3333333333

10

69.2

410

500

90

105

34.6

12.5555555556

33.2

410

500

90

105

29

9.3333333333

34

410

500

90

105

29

7.1111111111

33

410

500

90

105

30.0666666667

8.8888888889

27.6

410

500

78

83

18.7333333333

11.5555555556

43.4

410

500

78

83

24.3333333333

9.8888888889

37.6

410

500

78

83



CER 1

				AIRSTRIPS:																																																																																																		CONTACT PLATES:																																																																																																		PARTICLE COUNTS

				A						B						C						D						E						F						G						H						I						J						K						L						M						N						O						Average								A						B						C						D						E						F						G						H						I						J						K						L						M						N						O						Average								A				B				C				D				E				F				G				H				I				J				K				L				M				N				O				Average

		Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 1		Date		Alert Level		Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 1		Date		Alert Level		Action Level		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		CER 1 0.5um/ cu ft		Date		CER 1,3 Alert Level		CER 1,3 Action Level		CER 1 5.0um/cu ft		Date		CER 1,3 Alert Level		CER 1,3 Action Level

		2/28/06		2		0		2		4		0		4		5		0		5		4		0		4		8		0		8		0		0		0		3		0		3		3		0		3																																												4		2/28/06		10		15		0		0		0		0		0		0		1		0		1		0		0		0		2		0		2		0		0		0		3		0		3		4		0		4						0						0						0						0						0						0						0		1		2/28/06		10		15		207		8		291		16		133		12		278		21		134		13		25		5		262		22		222		16																														194		02/28/06		5000		10000		14		2/28/06		30		50

		3/30/06		4		0		4		4		0		4		7		0		7		6		0		6		10		0		10		2		0		2		6		0		6		4		0		4																																												5		3/30/06		10		15		1		0		1		3		0		3		6		0		6		3		0		3		2		0		2		5		0		5		3		0		3		3		0		3						0						0						0						0						0						0						0		4		3/30/06		10		15		310		48		483		69		134		18		263		24		444		31		679		40		199		8		204		31																														340		03/30/06		5000		10000		34		3/30/06		30		50

		4/28/06		4		0		4		12		0		12		12		0		12		15		0		15		17		0		17		6		4		10		12		0		12		23		0		23																																												13		4/28/06		10		15		0		0		0		2		0		2		2		0		2		0		0		0		0		0		0		0		0		0		4		0		4		0		0		0						0						0						0						0						0						0						0		1		4/28/06		10		15		487		81		221		21		261		19		390		32		480		60		287		23		321		19		455		35																														363		04/28/06		5000		10000		36		4/28/06		30		50

		5/30/06		6		0		6		10		0		10		12		0		12		17		0		17		19		0		19		9		0		9		12		0		12		21		0		21																																												13		5/30/06		10		15		1		0		1		4		0		4		3		0		3		0		0		0		1		0		1		0		0		0		7		0		7		1		0		1						0						0						0						0						0						0						0		2		5/30/06		10		15		678		124		1084		137		214		36		113		21		1478		449		220		32		1009		120		709		95																														688		05/30/06		5000		10000		127		5/30/06		30		50

		7/7/06		4		0		4		2		0		2		6		0		6		4		0		4		8		0		8		1		0		1		4		0		4		5		0		5																																												4		7/7/06		10		15		1		0		1		2		0		2		1		0		1		2		0		2		2		0		2		1		0		1		4		0		4		4		0		4						0						0						0						0						0						0						0		2		7/7/06		10		15		631		86		779		72		1234		81		282		38		464		75		694		93		564		65		302		33																														619		07/07/06		5000		10000		68		7/7/06		30		50

		9/5/06		4		0		4		4		0		4		6		0		6		5		0		5		2		0		2		2		0		2		4		0		4		5		0		5																																												4		9/5/06		10		15		4		0		4		6		0		6		4		0		4		3		0		3		6		0		6		5		0		5		5		0		5		6		0		6						0						0						0						0						0						0						0		6		9/5/06		10		15		1056		113		622		73		227		35		828		84		603		57		875		95		545		56		785		61																														693		09/05/06		5000		10000		72		9/5/06		30		50

		10/5/06		5		0		5		4		0		4		4		0		4		5		0		5		6		0		6		4		0		4		3		0		3		3		0		3																																												4		10/5/06		10		15		5		0		5		6		0		6		4		0		4		4		0		4		5		0		5		3		0		3		6		0		6		4		0		4						0						0						0						0						0						0						0		5		10/5/06		10		15		122		14		263		18		352		48		540		69		361		38		421		63		389		41		763		57																														401		10/05/06		5000		10000		44		10/5/06		30		50

		11/14/06		11		0		11		27		0		27		10		0		10		24		0		24		26		0		26		32		0		32		12		0		12		14		0		14																																												20		11/14/06		10		15		1		0		1		1		0		1		0		0		0		0		0		0		5		0		5		1		0		1		2		0		2		9		0		9						0						0						0						0						0						0						0		3		11/14/06		10		15		596		71		455		67		641		77		585		62		991		81		357		52		62		60		498		51																														523		11/14/06		5000		10000		65		11/14/06		30		50

		12/20/06		2		0		2		1		0		1		5		0		5		1		0		1		13		0		13		7		0		7		13		0		13		4		0		4																																												6		12/20/06		10		15		1		0		1		2		0		2		0		0		0		1		0		1		3		0		3		1		0		1		0		0		0		0		0		0						0						0						0						0						0						0						0		1		12/20/06		10		15		367		35		390		46		168		18		321		30		343		32		191		14		90		25		314		65																														273		12/20/06		5000		10000		33		12/20/06		30		50

		1/16/07		3		0		3		2		0		2		4		0		4		6		0		6		2		0		2		2		0		2		3		0		3		4		0		4																																												3		1/16/07		10		15		2		0		2		2		0		2		1		0		1		3		0		3		4		0		4		2		0		2		4		0		4		4		0		4						0						0						0						0						0						0						0		3		1/16/07		10		15		361		21		449		56		304		35		265		31		761		42		804		62		901		64		866		71																														589		01/16/07		5000		10000		48		1/16/07		30		50

		2/13/07		11		0		11		5		0		5		10		0		10		6		0		6		24		0		24		6		0		6		10		0		10		21		0		21																																												12		2/13/07		10		15		1		0		1		8		0		8		3		0		3		2		0		2		0		0		0		4		0		4		2		0		2		4		0		4						0						0						0						0						0						0						0		3		2/13/07		10		15		611		41		862		50		841		42		942		61		744		40		622		33		402		24		688		60																														714		02/13/07		5000		10000		44		2/13/07		30		50

		3/26/07		3		0		3		4		0		4		4		0		4		6		0		6		2		0		2		4		0		4		6		0		6		2		0		2																																												4		3/7/07		10		15		1		0		1		1		0		1		2		0		2		0		0		0		1		0		1		2		0		2		2		0		2		2		0		2						0						0						0						0						0						0						0		2		3/7/07		10		15		721		51		640		42		871		48		901		52		844		48		408		36		799		49		861		51																														756		03/07/07		5000		10000		47		3/7/07		30		50

		5/4/07		4		0		4		4		0		4		3		0		3		4		0		4		6		0		6		2		0		2		6		0		6		4		0		4																																												4		3/7/07		35		45		2		0		2		1		0		1		2		0		2		1		0		1		0		0		0		1		0		1		2		0		2		3		0		3						0						0						0						0						0						0						0		2		3/7/07		6		7		641		41		722		52		699		47		944		61		872		45		698		41		662		37		945		68																														773		03/07/07		3800		4500		49		3/7/07		410		500

		5/28/07		1		0		1		1		0		1		2		0		2		0		0		0		2		0		2		1		0		1		1		0		1		1		0		1																																												1		3/26/07		35		45		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1						0						0						0						0						0						0						0		1		3/26/07		6		7		161		17		200		21		251		36		275		28		320		53		101		15		460		55		184		21																														244		03/26/07		3800		4500		31		3/26/07		410		500

		7/4/07		2		0		2		3		0		3		3		0		3		3		0		3		2		0		2		4		0		4		4		0		4		3		0		3																																												3		5/4/07		35		45		2		0		2		2		0		2		1		0		1		0		0		0		1		0		1		1		0		1		2		0		2		2		0		2						0						0						0						0						0						0						0		2		5/4/07		6		7		346		64		339		37		537		77		301		55		492		86		292		31		896		120		1211		161																														552		05/04/07		3800		4500		79		5/4/07		410		500

		8/3/07		4		0		4		2		0		2		3		0		3		2		0		2		2		0		2		4		0		4		4		0		4		5		0		5																																												3		5/28/07		35		45		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		3		0		3		3		0		3		2		0		2						0						0						0						0						0						0						0		2		5/28/07		6		7		221		20		107		19		647		49		587		37		744		87		907		78		1241		101		975		89																														679		05/28/07		3800		4500		60		5/28/07		410		500

		9/24/07		2		0		2		1		0		1		1		0		1		2		0		2		3		0		3		3		0		3		2		0		2		2		0		2																																												2		7/4/07		35		45		0		0		0		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		2		0		2		2		0		2						0						0						0						0						0						0						0		1		7/4/07		6		7		310		27		488		31		210		20		401		29		121		18		404		31		601		41		422		30																														370		07/04/07		3800		4500		28		7/4/07		410		500

		11/6/07		6		0		6		4		0		4		4		0		4		4		0		4		8		0		8		7		0		7		8		0		8		10		0		10																																												6		8/3/07		35		45		2		0		2		2		0		2		3		0		3		1		0		1		3		0		3		5		0		5		4		0		4		4		0		4						0						0						0						0						0						0						0		3		8/3/07		6		7		523		33		678		25		498		14		671		22		687		23		721		33		856		34		678		25																														664		08/03/07		3800		4500		26		8/3/07		410		500

		12/11/07		10		0		10		9		0		9		11		0		11		12		0		12		12		0		12		15		0		15		21		0		21		18		0		18																																												14		9/24/07		35		45		2		0		2		1		0		1		3		0		3		4		0		4		4		0		4		4		0		4		3		0		3		7		0		7						0						0						0						0						0						0						0		4		11/6/07		6		7		678		36		761		31		734		34		891		44		851		33		781		33		1011		81		978		69																														836		11/06/07		3800		4500		45		11/6/07		410		500

		4/7/08		6		0		6		5		0		5		7		0		7		6		0		6		0		0		0		0		0		0		2		0		2		4		0		4		4		0		4		3		0		3		2		0		2		0		0		0		0		0		0		0		0		0		1		0		1		3		4/7/08		35		45		2		0		2		1		0		1		3		0		3		3		0		3		2		0		2		1		0		1		1		0		1		0		0		0		2		0		2		0		0		0		2		0		2		1		0		1		1		0		1		2		0		2		2		0		2		2		4/7/08		6		7		989		45		1045		58		1349		61		1305		60		689		46		430		30		1027		60		899		42		621		24		318		19		501		24		313		33		295		13		303		21		401		24		699		04/07/08		3800		4500		37		4/7/08		410		500

		5/7/08		9		0		9		8		0		8		7		0		7		8		0		8		3		0		3		3		0		3		3		0		3		7		0		7		7		0		7		4		0		4		8		0		8		4		0		4		8		0		8		9		0		9		5		0		5		6		5/7/08		35		45		3		0		3		2		0		2		2		0		2		2		0		2		3		0		3		3		0		3		2		0		2		1		0		1		1		0		1		1		0		1		2		0		2		2		0		2		2		0		2		2		0		2		2		0		2		2		5/7/08		6		7		782		44		671		39		724		41		454		22		576		33		430		30		671		32		572		28		781		37		671		32		677		33		476		41		672		31		781		43		587		33		635		05/07/08		3800		4500		35		5/7/08		410		500

		6/3/08		8		0		8		8		0		8		4		0		4		5		0		5		6		0		6		6		0		6		5		0		5		5		0		5		5		0		5		4		0		4		7		0		7		8		0		8		8		0		8		9		0		9		6		0		6		6		6/3/08		35		45		3		0		3		1		0		1		1		0		1		2		0		2		1		0		1		3		0		3		1		0		1		2		0		2		2		0		2		0		0		0		2		0		2		1		0		1		2		0		2		2		0		2		3		0		3		2		6/3/08		6		7		621		33		393		22		891		31		671		25		1192		44		671		19		781		22		245		19		1325		44		601		41		418		31		351		29		301		21		290		23		339		31		606		06/03/08		3800		4500		29		6/3/08		410		500

		7/1/08		9		0		9		9		0		9		7		0		7		9		0		9		8		0		8		5		0		5		8		0		8		8		0		8		8		0		8		6		0		6		11		0		11		6		0		6		9		0		9		9		0		9		3		0		3		8		7/1/08		35		45		1		0		1		2		0		2		0		0		0		1		0		1		1		0		1		1		0		1		0		0		0		0		0		0		2		0		2		1		0		1		1		0		1		2		0		2		0		0		0		1		0		1		1		0		1		1		7/1/08		6		7		621		33		393		22		891		31		671		25		1192		44		671		19		781		22		245		19		1325		44		601		41		418		31		351		29		301		21		290		23		339		31		606		07/01/08		3800		4500		29		7/1/08		410		500

		7/21/08		11		0		11		11		0		11		5		0		5		5		0		5		12		0		12		11		0		11		12		0		12		6		0		6		6		0		6		9		0		9		14		0		14		15		0		15		11		0		11		6		0		6		7		0		7		9		7/21/08		35		45		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		7/21/08		6		7		232		23		452		26		337		27		671		33		476		27		501		28		488		28		782		37		561		27		442		28		891		38		590		29		876		31		991		42		891		27		612		07/21/08		3800		4500		30		7/21/08		410		500

		9/4/08		10		0		10		9		0		9		6		0		6		7		0		7		7		0		7		9		0		9		6		0		6		9		0		9		11		0		11		12		0		12		10		0		10		9		0		9		6		0		6		6		0		6		9		0		9		8		9/4/08		35		45		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		9/4/08		6		7		219		19		140		14		275		16		101		9		244		16		301		21		189		19		181		17		176		17		215		21		414		24		409		21		357		21		454		19		602		27		285		09/04/08		3800		4500		19		9/4/08		410		500

		9/22/08		5		0		5		5		0		5		9		0		9		5		0		5		5		0		5		9		0		9		11		0		11		4		0		4		11		0		11		5		0		5		5		0		5		6		0		6		6		0		6		8		0		8		4		0		4		7		9/22/08		35		45		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		0		0		0		2		0		2		1		0		1		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		9/22/08		6		7		332		21		254		19		354		21		548		31		369		22		584		26		651		22		448		26		296		19		489		29		336		21		754		32		565		26		665		29		465		21		474		09/22/08		3800		4500		24		9/22/08		410		500

		11/6/08		3		0		3		3		0		3		5		0		5		4		0		4		4		0		4		3		0		3		4		0		4		4		0		4		4		0		4		5		0		5		5		0		5		3		0		3		3		0		3		3		0		3		4		0		4		4		11/6/08		35		45		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		1		0		1		0		11/6/08		6		7		721		31		867		39		253		12		458		22		357		20		445		28		432		22		685		31		591		28		241		9		219		8		473		19		501		21		765		33		801		36		521		11/06/08		3800		4500		24		11/6/08		410		500

		12/1/08		2		0		2		0		0		0		0		0		0		2		0		2		2		0		2		3		0		3		0		0		0		1		0		1		4		0		4		3		0		3		2		0		2		1		0		1		0		0		0		2		0		2		3		0		3		2		12/1/08		35		45		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		1		12/1/08		6		7		110		9		89		9		122		13		25		6		59		8		131		18		40		7		274		19		157		12		88		6		150		9		114		8		517		32		180		15		234		21		153		12/01/08		3800		4500		13		12/1/08		410		500

		12/16/08		3		0		3		2		0		2		3		0		3		2		0		2		2		0		2		3		0		3		4		0		4		3		0		3		5		0		5		4		0		4		4		0		4		3		0		3		3		0		3		3		0		3		3		0		3		3		12/16/08		35		45		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		1		0		1		1		12/16/08		6		7		291		18		178		11		271		19		189		14		177		14		276		18		198		11		187		14		278		17		91		7		87		6		287		16		376		21		301		17		227		19		228		12/16/08		3800		4500		15		12/16/08		410		500



&L&"Arial Narrow,Bold"&14CER 1&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER 2

										AIRSTRIPS:																																																												CONTACT PLATES:																																																						PARTICLE COUNTS

				A						B						C						D						E						F						G						H						I						Average						A						B						C						D						E						F						G						H						I						Average						A				B				C				D				E				F				G				H				I				Average

		Sample Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 2		Alert Level		Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 2		Total Alert Level		Total Action Level		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		CER 2 0.5um/cu ft		Date		CER 2 Alert Level		CER 2 Action Level		CER 2 5.0um/cu ft		Date		CER 2 Alert Level		CER 2 Action Level

		2/28/06								6		0		6		0		0		0		9		0		9		9		0		9																										6		10		15								0		0		0		0		0		0		1		0		1		0		0		0																										0		10		15		297		39		288		43		0		0		564		64																						383		2/28/06		5000		10000		49		02/28/06		30		50

		3/30/06								9		0		9		1		0		1		8		0		8		12		0		12																										8		10		15								2		0		2		0		0		0		6		0		6		3		0		3																										3		10		15		460		68		264		39		0		0		291		41																						338		3/30/06		5000		10000		49		03/30/06		30		50

		4/28/06								29		0		29		0		0		0		22		0		22		2		0		2																										13		10		15								2		0		2		2		0		2		0		0		0		3		0		3																										2		10		15		1084		67		543		41		0		0		531		39																						719		4/28/06		5000		10000		49		04/28/06		30		50

		5/30/06								21		0		21		0		0		0		19		0		19		4		0		4																										11		10		15								4		0		4		2		0		2		1		0		1		5		0		5																										3		10		15		435		87		354		66		0		0		460		77																						416		5/30/06		5000		10000		77		05/30/06		30		50

		7/7/06								5		0		5		0		0		0		8		0		8		8		0		8																										5		10		15								0		0		0		0		0		0		2		0		2		1		0		1																										1		10		15		232		33		299		39		0		0		479		40																						337		7/7/06		5000		10000		37		07/07/06		30		50

		9/5/06								3		0		3		0		0		0		2		0		2		2		0		2																										2		10		15								4		0		4		0		0		0		4		0		4		5		0		5																										3		10		15		1289		79		289		30		0		0		1422		108																						1000		9/5/06		5000		10000		72		09/05/06		30		50

		10/5/06																																																																																																																																																																10/5/06		5000		10000				10/05/06		30		50

		11/14/06								16		0		16		0		0		0		4		0		4		2		0		2																										6		10		15								1		0		1		0		0		0		4		0		4		1		0		1																										2		10		15		961		41		877		40		0		0		688		31																						842		11/14/06		5000		10000		37		11/14/06		30		50

		12/20/06								5		0		5		4		0		4		6		0		6		2		0		2																										4		10		15								0		0		0		0		0		0		0		0		0		0		0		0																										0		10		15		463		36		141		17		0		0		273		41																						292		12/20/06		5000		10000		31		12/20/06		30		50

		1/16/07								2		0		2		0		0		0		1		0		1		1		0		1																										1		10		15								1		0		1		0		0		0		1		0		1		2		0		2																										1		10		15		781		62		451		32		0		0		628		58																						620		1/16/07		5000		10000		51		01/16/07		30		50

		2/13/07								12		0		12		0		0		0		10		0		10		10		0		10																										8		10		15								4		0		4		0		0		0		4		0		4		4		1		5																										3		10		15		640		31		285		44		0		0		499		22																						475		2/13/07		5000		10000		32		02/13/07		30		50

		3/26/07								2		0		2		0		0		0		2		0		2		3		0		3																										2		35		45								1		0		1		0		0		0		1		0		1		1		0		1																										1		6		7		490		40		684		51		0		0		588		42																						587		3/7/07		5000		10000		44		03/07/07		30		50

		5/4/07								2		0		2		0		0		0		3		0		3		3		0		3																										2		35		45								1		0		1		0		0		0		1		0		1		2		0		2																										1		6		7		640		41		585		37		0		0		704		52																						643		3/7/07		1250		1500		43		03/07/07		90		105

		5/28/07								0		0		0		0		0		0		1		0		1		1		0		1																										1		35		45								1		0		1		0		0		0		0		0		0		1		0		1																										1		6		7		1104		101		944		81		0		0		642		45																						897		3/26/07		1250		1500		76		03/26/07		90		105

		7/4/07								1		0		1		0		0		0		2		0		2		2		0		2																										1		35		45								0		0		0		0		0		0		1		0		1		1		0		1																										1		6		7		10		0		962		123		0		0		1141		132																						704		5/4/07		1250		1500		89		07/04/07		90		105

		8/3/07								0		0		0		0		0		0		1		0		1		2		0		2																										1		35		45								1		0		1		0		0		0		1		0		1		1		0		1																										1		6		7		0		0		784		61		0		0		875		71																						553		8/3/07		1250		1500		44		08/03/07		90		105

		9/24/07								1		0		1		0		0		0		1		0		1		1		0		1																										1		35		45								0		0		0		0		0		0		0		0		0		1		0		1																										0		6		7		0		0		199		19		0		0		701		49																						300		9/24/07		1250		1500		23		09/24/07		90		105

		11/6/07								1		0		1		0		0		0		3		0		3		3		0		3																										2		35		45								1		0		1		0		0		0		2		0		2		2		0		2																										1		6		7		4		0		563		22		0		0		867		39																						478		11/6/07		1250		1500		20		11/06/07		90		105

		12/11/07								0		0		0		0		0		0		2		0		2		3		0		3																										1		35		45								0		0		0		0		0		0		3		0		3		1		0		1																										1		6		7		2		0		672		36		0		0		901		37																						525		12/11/07		1250		1500		24		12/11/07		90		105

		4/7/08		0		0		0		4		0		4		7		0		7		0		0		0		4		0		4		0		0		0		6		0		6		3		0		3		0		0		0		3		35		45		0		0		0		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		2		0		2		2		0		2		0		0		0		1		6		7		0		0		162		23		208		25		0		0		93		19		0		0		90		6		201		17		0		0		84		4/7/08		1250		1500		10		04/07/08		90		105

		5/7/08		0		0		0		3		0		3		9		0		9		0		0		0		8		0		8		0		0		0		8		0		8		8		0		8		0		0		0		4		35		45		0		0		0		2		0		2		3		0		3		0		0		0		2		0		2		0		0		0		1		0		1		1		0		1		0		0		0		1		6		7		0		0		401		24		489		25		0		0		281		22		0		0		187		18		482		24		0		0		204		5/7/08		1250		1500		13		05/07/08		90		105

		6/3/08		0		0		0		3		0		3		3		0		3		0		0		0		5		0		5		0		0		0		5		0		5		2		0		2		0		0		0		2		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		0		1		0		0		0		1		6		7		0		0		267		10		498		22		0		0		268		22		0		0		301		19		298		11		0		0		181		6/3/08		1250		1500		9		06/03/08		90		105

		7/1/08		0		0		0		8		0		8		0		0		0		8		0		8		6		0		6		0		0		0		3		0		3		2		0		2		0		0		0		3		35		45		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		0		6		7		0		0		403		22		0		0		153		11		287		19		1		0		21		1		121		11		0		0		110		7/1/08		1250		1500		7		07/01/08		90		105

		7/21/08		0		0		0		6		0		6		0		0		0		7		0		7		7		0		7		0		0		0		4		0		4		2		0		2		0		0		0		3		35		45		0		0		0		2		0		2		0		0		0		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		0		0		0		1		6		7		0		0		376		19		0		0		298		17		337		21		0		0		109		8		291		15		0		0		157		7/21/08		1250		1500		9		07/21/08		78		83

		9/4/08		0		0		0		7		0		7		9		0		9		0		0		0		4		0		4		0		0		0		4		0		4		4		0		4		3		0		3		3		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		6		7		0		0		210		19		175		11		0		0		361		18		0		0		101		7		162		9		706		40		191		9/4/08		1250		1500		12		09/04/08		78		83

		9/22/08		0		0		0		5		0		5		4		0		4		0		0		0		4		0		4		0		0		0		2		0		2		4		0		4		2		0		2		2		35		45		0		0		0		2		0		2		0		0		0		0		0		0		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		1		6		7		0		0		332		21		296		15		0		0		194		9		0		0		265		11		295		11		565		22		216		9/22/08		1250		1500		10		09/22/08		78		83

		11/6/08		0		0		0		2		0		2		3		0		3		0		0		0		2		0		2		0		0		0		3		0		3		3		0		3		2		0		2		2		35		45		0		0		0		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		6		7		0		0		776		22		409		19		0		0		292		8		0		0		301		16		228		11		220		9		247		11/6/08		1250		1500		9		11/06/08		78		83

		12/1/08		0		0		0		3		0		3		2		0		2		0		0		0		3		0		3		0		0		0		2		0		2		0		0		0		1		0		1		1		35		45		0		0		0		1		0		1		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		6		7		0		0		290		12		203		11		0		0		221		12		0		0		313		21		19		3		148		10		133		12/1/08		1250		1500		8		12/01/08		78		83

		12/16/08		0		0		0		4		0		4		3		0		3		0		0		0		3		0		3		0		0		0		3		0		3		0		0		0		1		0		1		2		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		6		7		0		0		199		9		289		16		0		0		167		7		0		0		267		17		89		6		177		11		132		12/16/08		1250		1500		7		12/16/08		78		83



&L&"Arial Narrow,Bold"&14CER 2&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER 3

				AIRSTRIPS:																														CONTACT PLATES:																																				PARTICLE COUNTS

				A						B						D						E						Average						A						B						C						D						E						Average						A				B				C				D				E				Average

		Sample Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER3		Total Alert Level		Total Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 3		Total Alert Level		Total Action Level		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		CER 3 0.5um/cu ft		0.5um/cu ft Alert Level		0.5um/cu ft Action Level		CER 3 5.0um/cu ft		5.0um/cu ft Alert Level		5.0um/cu ft Action Level

		2/28/06		29		1		30		21		0		21		28		0		28		37		0		37		29		10		15		3		0		3		3		0		3		3		0		3		2		0		2		4		0		4		3		10		15		4411		344		3943		271		3664		229		3068		212		1233		78		3264		5000		10000		227		30		50

		3/30/06		32		1		33		26		0		26		21		0		21		32		0		32		28		10		15		5		0		5		4		0		4		6		0		6		4		0		4		5		0		5		4		10		15		1261		119		979		81		1461		101		1721		120		630		101		1210		5000		10000		104		30		50

		4/28/06		29		2		31		32		0		32		23		0		23		29		0		29		29		10		15		2		0		2		3		0		3		0		0		0		0		0		0		0		0		0		1		10		15		4536		307		3293		245		2424		222		2637		211		1112		72		2800		5000		10000		211		30		50

		5/30/06		31		0		31		29		0		29		21		1		22		29		0		29		28		10		15		4		0		4		5		0		5		2		0		2		1		0		1		3		0		3		3		10		15		1914		327		2122		327		2561		413		1572		207		1829		252		2000		5000		10000		305		30		50

		7/7/06		26		0		26		19		0		19		22		0		22		31		0		31		25		10		15		4		0		4		5		0		5		3		0		3		2		0		2		5		0		5		3		10		15		2150		382		2668		423		2561		401		2022		399		764		118		2033		5000		10000		345		30		50

		9/5/06		10		0		10		12		0		12		11		0		11		14		0		14		12		10		15		6		0		6		4		0		4		4		0		4		6		0		6		5		0		5		5		10		15		2286		180		2142		171		1829		162		1749		171		1281		148		1857		5000		10000		166		30		50

		10/5/06		9		0		9		10		0		10		10		0		10		8		0		8		9		10		15		7		0		7		5		0		5		6		0		6		4		0		4		4		0		4		5		10		15		1679		346		793		137		1841		241		1429		248		1374		203		1423		5000		10000		235		30		50

		11/14/06		19		2		21		26		0		26		26		0		26		17		0		17		23		10		15		2		0		2		1		0		1		0		0		0		1		0		1		6		0		6		2		10		15		2241		243		2301		231		1974		198		2475		224		2575		201		2313		5000		10000		219		30		50

		12/20/06		10		0		10		13		0		13		13		0		13		16		0		16		13		10		15		5		0		5		1		0		1		0		0		0		3		0		3		1		0		1		2		10		15		406		33		727		46		923		94		604		41		462		39		624		5000		10000		51		30		50

		1/16/07		4		0		4		5		0		5		7		0		7		3		0		3		5		10		15		3		0		3		2		0		2		3		0		3		4		0		4		4		0		4		3		10		15		485		41		1785		101		1986		128		1785		109		1861		118		1580		5000		10000		99		30		50

		2/13/07		12		0		12		22		0		22		18		0		18		21		0		21		18		10		15		2		0		2		4		0		4		2		0		2		1		0		1		2		0		2		2		10		15		1261		87		1641		98		901		62		988		61		1487		88		1256		5000		10000		79		30		50

		3/26/07		11		0		11		12		0		12		10		0		10		9		0		9		11		35		45		2		0		2		1		0		1		2		0		2		1		0		1		2		0		2		2		6		7		1421		109		1221		101		866		71		949		82		1242		101		1140		3800		4500		93		410		500

		5/4/07		10		0		10		10		0		10		9		0		9		11		0		11		10		35		45		2		0		2		3		0		3		1		0		1		2		0		2		2		0		2		2		6		7		1741		110		1444		91		1235		81		1479		87		1521		92		1484		3800		4500		92		410		500

		5/28/07		6		0		6		4		0		4		2		0		2		2		0		2		4		35		45		4		0		4		2		0		2		1		0		1		1		0		1		2		0		2		2		6		7		1421		102		1387		100		1842		169		1785		154		1421		121		1571		3800		4500		129		410		500

		7/4/07		7		0		7		6		0		6		6		0		6		7		0		7		7		35		45		4		0		4		3		0		3		2		0		2		1		0		1		4		0		4		3		6		7		3950		375		2745		292		1658		177		2431		201		2786		247		2714		3800		4500		258		410		500

		8/3/07		6		0		6		6		0		6		4		0		4		5		0		5		5		35		45		3		0		3		3		0		3		2		0		2		2		0		2		2		0		2		3		6		7		1672		145		1897		152		1866		149		1987		151		1487		138		1782		3800		4500		147		410		500

		9/24/07		4		0		4		3		0		3		2		0		2		2		0		2		3		35		45		2		0		2		2		0		2		2		0		2		1		0		1		2		0		2		2		6		7		781		61		1011		72		689		49		768		52		409		31		732		3800		4500		53		410		500

		11/6/07		7		0		7		9		0		9		8		0		8		9		0		9		8		35		45		3		0		3		3		0		3		5		0		5		1		0		1		6		0		6		3		6		7		1276		78		1454		65		1109		55		987		45		1067		47		1179		3800		4500		58		410		500

		12/11/07		9		0		9		12		0		12		9		0		9		11		0		11		10		35		45		2		0		2		4		0		4		4		0		4		5		0		5		4		0		4		4		6		7		1853		101		1321		99		901		45		1241		87		987		72		1261		3800		4500		81		410		500

		4/7/08		8		0		8		15		0		15		12		0		12		10		0		10		11		35		45		2		0		2		3		0		3		2		0		2		3		0		3		4		0		4		3		6		7		1047		69		1642		79		1421		67		1677		71		987		60		1355		3800		4500		69		410		500

		5/7/08		3		0		3		4		0		4		4		0		4		4		0		4		4		35		45		4		0		4		3		0		3		4		0		4		1		0		1		1		0		1		2		6		7		561		31		761		44		660		39		451		21		671		31		621		3800		4500		33		410		500

		6/3/08		3		0		3		4		0		4		4		0		4		4		0		4		4		35		45		2		0		2		2		0		2		2		0		2		1		0		1		1		0		1		2		6		7		409		26		391		33		782		34		891		33		1281		44		751		3800		4500		34		410		500

		7/1/08		7		0		7		7		0		7		8		0		8		8		0		8		8		35		45		2		0		2		2		0		2		1		0		1		1		0		1		1		0		1		2		6		7		1121		81		677		42		339		22		125		11		111		9		475		3800		4500		33		410		500

		7/21/08		9		0		9		8		0		8		8		0		8		11		0		11		9		35		45		3		0		3		3		0		3		2		0		2		2		0		2		2		0		2		3		6		7		891		41		781		33		789		31		499		21		339		12		660		3800		4500		28		410		500

		9/4/08		6		0		6		9		0		9		4		0		4		7		0		7		7		35		45		2		0		2		2		0		2		1		0		1		2		0		2		1		0		1		2		6		7		793		37		1044		44		977		39		1011		57		901		40		945		3800		4500		43		410		500

		9/22/08		9		0		9		9		0		9		9		0		9		7		0		7		9		35		45		1		0		1		2		0		2		2		0		2		2		0		2		1		0		1		2		6		7		984		44		564		31		965		33		698		41		632		39		769		3800		4500		38		410		500

		11/6/08		6		0		6		6		0		6		4		0		4		3		0		3		5		35		45		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		1		6		7		1198		81		901		67		789		43		761		41		904		61		911		3800		4500		59		410		500

		12/1/08		7		0		7		7		0		7		6		0		6		7		0		7		7		35		45		2		0		2		1		0		1		2		0		2		1		0		1		1		0		1		1		6		7		1198		81		901		67		789		43		761		41		904		61		911		3800		4500		59		410		500

		12/16/08		8		0		8		8		0		8		6		0		6		9		0		9		8		35		45		1		0		1		2		0		2		1		0		1		1		0		1		1		0		1		1		6		7		892		41		1098		69		892		34		901		44		1167		72		990		3800		4500		52		410		500



&L&"Arial Narrow,Bold"&14CER 3&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER Pressure

		Daily				Monthly				Daily				Monthly				Daily																		Monthly																		Daily								Monthly								Specs

		Date		CER1		Month		CER1		Date		CER Change Room		Month		CER Change Room		Date		CER2		Temp (F)		Relative Humidity (%)		R&D Bio-Safety Cabinet North (left axis)		R&D Bio-Safety Cabinet South (left axis)		Mfg Bio-Safety Cabinet North (left axis)		Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)		Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)		Month		CER 2		Temp (F)		Relative Humidity (%)		R&D Bio-Safety Cabinet North (left axis)		R&D Bio-Safety Cabinet South (left axis)		Mfg Bio-Safety Cabinet North (left axis)		Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)		Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)		Date		CER3		Temp (ºF)		Humidity (%RH)		Month		CER 3		Temp (ºF)		Humidity (%RH)		Date		CER Alert Level		CER Action Level		Bio-Safety Cabinet Alert Level (left axis)		Bio-Safety Cabinet Action  Level (left axis)		Mfg Bio-Safety Cabinet South Alert Level (right axis)		Mfg Bio-Safety Cabinet South Alarm Level (right axis)

		4/24/06		0.05		April-06		0.045		3/31/06		0.05		March-06		0.055		3/31/06		0.09																March-06		0.090																6/19/06		0.05						June-06		0.051						4/30/06		0.05		0.03

		4/24/06		0.05		May-06		0.022		3/31/06		0.06		April-06		0.053		3/31/06		0.09																April-06		0.089																6/19/06		0.06						July-06		0.061						5/31/06		0.05		0.03

		4/25/06		0.05		June-06		0.013		4/4/06		0.05		May-06		0.050		4/4/06		0.09																July-06		0.076																6/28/06		0.03						August-06		0.055						6/30/06		0.05		0.03

		4/25/06		0.04		July-06		0.041		4/4/06		0.05		June-06		0.046		4/4/06		0.09																August-06		0.068																6/28/06		0.06						September-06		0.052						7/31/06		0.05		0.03

		4/26/06		0.06		August-06		0.033		4/5/06		0.05		July-06		0.048		4/5/06		0.09																September-06		0.062																6/29/06		0.03						October-06		0.051						8/31/06		0.05		0.03

		4/26/06		0.04		September-06		0.027		4/5/06		0.06		August-06		0.050		4/5/06		0.09																October-06		0.034																6/29/06		0.06						November-06		0.053						9/30/06		0.05		0.03

		4/27/06		0.04		October-06		0.033		4/6/06		0.05		September-06		0.048		4/6/06		0.09																November-06		0.020																6/30/06		0.06						December-06		0.051						10/31/06		0.05		0.03

		4/27/06		0.045		November-06		0.028		4/6/06		0.06		October-06		0.053		4/6/06		0.09																December-06		0.012																6/30/06		0.06						February-07		0.040						11/30/06		0.05		0.03

		4/28/06		0.05		December-06		0.030		4/7/06		0.055		November-06		0.035		4/7/06		0.09																January-07		0.011																7/5/06		0.03						March-07		0.037						12/31/06		0.05		0.03

		4/28/06		0.04		January-07		0.030		4/7/06		0.05		December-06		0.031		4/7/06		0.09																February-07		0.013																7/5/06		0.03						April-07		0.038						1/31/07		0.05		0.03

		4/29/06		0.035		February-07		0.038		4/10/06		0.055		January-07		0.031		4/10/06		0.095																March-07		0.031																7/6/06		0.06						May-07		0.038						1/28/07		0.05		0.03

		4/29/06		0.035		March-07		0.037		4/10/06		0.055		February-07		0.035		4/10/06		0.09																April-07		0.033																7/6/06		0.06						June-07		0.040						3/7/07		0.05		0.03

		5/1/06		0.025		April-07		0.031		4/11/06		0.055		March-07		0.036		4/11/06		0.095																May-07		0.044																7/7/06		0.06						July-07		0.057						3/7/07		0.03		0.005

		5/1/06		0.03		May-07		0.027		4/11/06		0.055		April-07		0.035		4/11/06		0.095																June-07		0.048																7/7/06		0.06						August-07		0.053						4/30/07		0.03		0.005

		5/2/06		0.025		June-07		0.027		4/12/06		0.055		May-07		0.032		4/12/06		0.09																July-07		0.050																7/10/06		0.06						September-07		0.050						5/16/07		0.03		0.005

		5/2/06		0.03		July-07		0.035		4/12/06		0.055		June-07		0.028		4/12/06		0.09																August-07		0.042																7/10/06		0.06						October-07		0.049						5/16/07		0.015		0.005

		5/3/06		0.015		August-07		0.032		4/13/06		0.055		July-07		0.030		4/13/06		0.09																September-07		0.046						0.610		0.408								7/11/06		0.06						November-07		0.047						5/31/07		0.015		0.005

		5/4/06		0.03		September-07		0.030		4/13/06		0.055		August-07		0.032		4/13/06		0.095																October-07		0.041						0.620		0.420								7/11/06		0.06						December-07		0.043						6/30/07		0.015		0.005

		5/5/06		0.03		October-07		0.030		4/17/06		0.06		September-07		0.029		4/17/06		0.095																November-07		0.035						0.632		0.424								7/12/06		0.06						January-08		0.040						7/31/07		0.015		0.005

		5/5/06		0.03		November-07		0.065		4/17/06		0.055		October-07		0.027		4/17/06		0.09																December-07		0.030						0.643		0.426								7/12/06		0.06						February-08		0.040						8/31/07		0.015		0.005

		5/6/06		0.03		December-07		0.077		4/18/06		0.055		November-07		0.044		4/18/06		0.095																January-08																		7/13/06		0.06						March-08		0.040						9/5/07		0.015		0.005		0.25		0.1

		5/6/06		0.025		January-08		0.088		4/18/06		0.06		December-07		0.043		4/18/06		0.09																February-08		0.049		69.778		46.100		0.281		0.309		0.428		62.091		1180.364		7/13/06		0.06						April-08		0.048		70.864		42.636		9/30/07		0.015		0.005		0.25		0.1

		5/7/06		0.03		February-08		0.035		4/19/06		0.045		January-08		0.032		4/19/06		0.085																March-08		0.063		70.000		39.750		0.272		0.318		0.441		63.000		1193.000		7/14/06		0.06						May-08		0.040		72.696		37.435		10/31/07		0.015		0.005		0.25		0.1

		5/8/06		0.03		March-08		0.041		4/19/06		0.05		February-08		0.035		4/19/06		0.09																April-08		0.053		71.045		41.000		0.276		0.320		0.454		62.333		1196.333		7/14/06		0.06						June-08		0.025		72.136		33.909		11/30/07		0.015		0.005		0.25		0.1

		5/8/06		0.03		April-08		0.043		4/20/06		0.055		March-08		0.039		4/20/06		0.079																May-08		0.043		72.304		35.913		0.282		0.320		0.449		60.652		1194.957		7/17/06		0.06						July-08		0.059		71.920		39.400		12/31/07		0.015		0.005		0.25		0.1

		5/9/06		0.025		May-08		0.041		4/20/06		0.05		April-08		0.040		4/20/06		0.08																June-08		0.043		71.826		33.522		0.288		0.318		0.447		57.913		790.783		7/17/06		0.06						August-08		0.057		71.600		40.040		1/31/08		0.015		0.005		0.25		0.1

		5/9/06		0.025		June-08		0.039		4/24/06		0.06		May-08		0.040		4/21/06		0.085																July-08		0.077		71.800		38.360		0.285		0.320		0.447		59.789		882.526		7/18/06		0.06						September-08		0.059		71.240		38.000		2/29/08		0.015		0.005		0.25		0.1

		5/10/06		0.025		July-08		0.027		4/24/06		0.06		June-08		0.037		4/21/06		0.085																August-08		0.061		71.440		38.480		0.272		0.318		0.448		0.000		0.000		7/18/06		0.06														3/31/08		0.015		0.005		0.25		0.1

		5/10/06		0.025		August-08		0.031		4/25/06		0.06		July-08		0.040		4/25/06		0.086																September-08		0.059		70.640		38.280		0.259		0.319		0.439		0.000		0.000		7/19/06		0.06														4/30/08		0.015		0.005		0.25		0.1

		5/11/06		0.015		September-08		0.030		4/25/06		0.06		August-08		0.041		4/25/06		0.085																																		7/19/06		0.06														5/31/08		0.015		0.005		0.25		0.1

		5/11/06		0.025						4/26/06		0.05		September-08		0.041		4/26/06		0.085																																		7/20/06		0.07														6/30/08		0.015		0.005		0.25		0.1

		5/12/06		0.025						4/26/06		0.02						4/26/06		0.087																																		7/20/06		0.07														7/31/08		0.015		0.005		0.2		0.15

		5/12/06		0.02						4/27/06		0.06						4/27/06		0.085																																		7/21/06		0.07														8/30/08		0.015		0.005		0.2		0.15

		5/15/06		0.02						4/27/06		0.055						4/27/06		0.085																																		7/21/06		0.07														9/30/08		0.015		0.005		0.2		0.15

		5/15/06		0.025						4/28/06		0.04						4/28/06		0.09																																		7/22/06		0.07

		5/16/06		0.01						4/28/06		0.055						4/28/06		0.08																																		7/22/06		0.07

		5/16/06		0.01						4/29/06		0.05						7/25/06		0.085																																		7/24/06		0.07

		5/17/06		0.01						4/29/06		0.05						7/25/06		0.085																																		7/24/06		0.07

		5/17/06		0.025						5/1/06		0.05						7/26/06		0.085																																		7/25/06		0.06

		5/18/06		0.02						5/1/06		0.055						7/26/06		0.075																																		7/25/06		0.06

		5/18/06		0.02						5/2/06		0.05						7/27/06		0.08																																		7/26/06		0.06

		5/19/06		0.03						5/2/06		0.055						7/27/06		0.08																																		7/26/06		0.06

		5/19/06		0.02						5/3/06		0.05						7/28/06		0.075																																		7/27/06		0.06

		5/20/06		0.01						5/4/06		0.045						7/28/06		0.079																																		7/27/06		0.06

		5/20/06		0.02						5/5/06		0.055						7/29/06		0.069																																		8/1/06		0.06

		5/22/06		0.015						5/5/06		0.05						7/29/06		0.07																																		8/1/06		0.06

		5/22/06		0.015						5/6/06		0.065						7/30/06		0.069																																		8/2/06		0.06

		5/23/06		0.015						5/6/06		0.055						7/30/06		0.069																																		8/2/06		0.06

		5/23/06		0.015						5/7/06		0.05						7/31/06		0.075																																		8/3/06		0.06

		5/24/06		0.015						5/8/06		0.05						7/31/06		0.073																																		8/3/06		0.06

		5/24/06		0.015						5/8/06		0.05						8/1/06		0.07																																		8/4/06		0.06

		5/25/06		0.015						5/9/06		0.05						8/1/06		0.075																																		8/4/06		0.06

		5/25/06		0.03						5/9/06		0.055						8/2/06		0.07																																		8/7/06		0.055

		5/30/06		0.015						5/10/06		0.045						8/2/06		0.07																																		8/7/06		0.06

		5/30/06		0.02						5/10/06		0.04						8/3/06		0.07																																		8/8/06		0.06

		6/1/06		0.01						5/11/06		0.045						8/3/06		0.074																																		8/8/06		0.06

		6/1/06		0.01						5/11/06		0.055						8/4/06		0.074																																		8/9/06		0.06

		6/2/06		0.015						5/12/06		0.05						8/4/06		0.074																																		8/9/06		0.06

		6/5/06		0.01						5/12/06		0.06						8/7/06		0.073																																		8/10/06		0.055

		6/5/06		0.013						5/15/06		0.045						8/7/06		0.073																																		8/10/06		0.055

		6/6/06		0.01						5/15/06		0.055						8/8/06		0.073																																		8/11/06		0.055

		6/6/06		0.01						5/16/06		0.05						8/8/06		0.073																																		8/11/06		0.055

		6/7/06		0.01						5/16/06		0.055						8/10/06		0.074																																		8/14/06		0.055

		6/7/06		0.01						5/17/06		0.04						8/10/06		0.071																																		8/14/06		0.055

		6/8/06		0.01						5/17/06		0.045						8/14/06		0.07																																		8/15/06		0.055

		6/8/06		0.01						5/18/06		0.05						8/15/06		0.069																																		8/15/06		0.055

		6/9/06		0.01						5/18/06		0.055						8/16/06		0.069																																		8/16/06		0.055

		6/9/06		0.01						5/19/06		0.04						8/16/06		0.07																																		8/16/06		0.055

		6/12/06		0.03						5/19/06		0.045						8/17/06		0.069																																		8/17/06		0.055

		6/12/06		0.01						5/20/06		0.04						8/17/06		0.069																																		8/17/06		0.06

		6/13/06		0.03						5/20/06		0.043						8/18/06		0.07																																		8/18/06		0.05

		6/13/06		0.01						5/22/06		0.05						8/18/06		0.068																																		8/18/06		0.065

		6/16/06		0.01						5/22/06		0.05						8/21/06		0.065																																		8/19/06		0.05

		6/16/06		0.01						5/23/06		0.05						8/22/06		0.06																																		8/19/06		0.055

		7/6/06		0.05						5/23/06		0.05						8/22/06		0.065																																		8/21/06		0.055

		7/6/06		0.04						5/24/06		0.045						8/23/06		0.065																																		8/21/06		0.05

		7/7/06		0.04						5/24/06		0.05						8/23/06		0.068																																		8/22/06		0.05

		7/8/06		0.04						5/25/06		0.05						8/24/06		0.065																																		8/22/06		0.056

		7/10/06		0.05						5/25/06		0.05						8/24/06		0.055																																		8/23/06		0.055

		7/11/06		0.04						5/30/06		0.045						8/25/06		0.065																																		8/23/06		0.055

		7/12/06		0.05						5/30/06		0.05						8/25/06		0.065																																		8/24/06		0.05

		7/13/06		0.05						6/1/06		0.045						8/28/06		0.065																																		8/24/06		0.05

		7/17/06		0.06						6/1/06		0.05						8/28/06		0.065																																		8/25/06		0.05

		7/18/06		0.04						6/2/06		0.04						8/30/06		0.065																																		8/25/06		0.055

		7/19/06		0.04						6/5/06		0.05						8/30/06		0.063																																		8/26/06		0.05

		7/20/06		0.04						6/5/06		0.055						8/31/06		0.065																																		8/26/06		0.05

		7/21/06		0.033						6/6/06		0.055						8/31/06		0.065																																		8/28/06		0.05

		7/22/06		0.04						6/6/06		0.05						9/1/06		0.06																																		8/28/06		0.05

		7/23/06		0.04						6/7/06		0.055						9/1/06		0.065																																		8/29/06		0.05

		7/24/06		0.04						6/7/06		0.05						9/5/06		0.065																																		8/29/06		0.05

		7/25/06		0.04						6/8/06		0.05						9/5/06		0.065																																		8/30/06		0.05

		7/26/06		0.035						6/8/06		0.05						9/6/06		0.055																																		8/30/06		0.05

		7/26/06		0.04						6/9/06		0.045						9/6/06		0.065																																		8/31/06		0.05

		7/27/06		0.03						6/9/06		0.05						9/7/06		0.055																																		8/31/06		0.05

		7/27/06		0.04						6/12/06		0.01						9/7/06		0.063																																		9/1/06		0.055

		7/28/06		0.04						6/12/06		0.05						9/8/06		0.06																																		9/6/06		0.05

		7/31/06		0.03						6/13/06		0.01						9/8/06		0.063																																		9/6/06		0.05

		8/1/06		0.035						6/13/06		0.05						9/11/06		0.06																																		9/7/06		0.05

		8/2/06		0.03						6/14/06		0.05						9/11/06		0.065																																		9/7/06		0.05

		8/3/06		0.03						6/14/06		0.055						9/12/06		0.06																																		9/8/06		0.05

		8/4/06		0.03						6/15/06		0.055						9/12/06		0.065																																		9/8/06		0.05

		8/7/06		0.03						6/15/06		0.06						9/13/06		0.06																																		9/11/06		0.05

		8/8/06		0.03						6/16/06		0.05						9/13/06		0.065																																		9/11/06		0.05

		8/10/06		0.03						6/16/06		0.04						9/14/06		0.06																																		9/12/06		0.05

		8/10/06		0.05						6/17/06		0.045						9/14/06		0.065																																		9/12/06		0.06

		8/11/06		0.03						6/17/06		0.05						9/15/06		0.06																																		9/13/06		0.05

		8/11/06		0.05						6/19/06		0.05						9/15/06		0.065																																		9/13/06		0.055

		8/14/06		0.03						6/19/06		0.05						9/18/06		0.06																																		9/14/06		0.05

		8/15/06		0.03						6/20/06		0.05						9/18/06		0.063																																		9/14/06		0.04

		8/16/06		0.05						6/20/06		0.05						9/19/06		0.065																																		9/15/06		0.05

		8/16/06		0.03						6/21/06		0.04						9/19/06		0.055																																		9/15/06		0.05

		8/17/06		0.035						6/21/06		0.05						9/20/06		0.065																																		9/18/06		0.055

		8/17/06		0.03						6/22/06		0.04						9/20/06		0.06																																		9/18/06		0.06

		8/18/06		0.03						6/22/06		0.045						9/21/06		0.065																																		9/19/06		0.05

		8/18/06		0.03						6/26/06		0.04						9/21/06		0.062																																		9/19/06		0.055

		8/19/06		0.035						6/27/06		0.04						9/23/06		0.065																																		9/20/06		0.05

		8/19/06		0.03						6/28/06		0.04						9/23/06		0.062																																		9/20/06		0.05

		8/20/06		0.035						6/29/06		0.04						9/25/06		0.059																																		9/21/06		0.055

		8/21/06		0.03						7/5/06		0.04						9/25/06		0.06																																		9/21/06		0.055

		8/21/06		0.03						7/6/06		0.04						10/2/06		0.06																																		9/22/06		0.05

		8/22/06		0.025						7/7/06		0.05						10/2/06		0.05																																		9/22/06		0.055

		8/22/06		0.035						7/8/06		0.05						10/3/06		0.048																																		9/23/06		0.06

		8/23/06		0.035						7/10/06		0.03						10/3/06		0.042																																		9/23/06		0.06

		8/23/06		0.035						7/11/06		0.05						10/4/06		0.048																																		9/25/06		0.05

		8/24/06		0.035						7/12/06		0.04						10/6/06		0.038																																		9/25/06		0.055

		8/24/06		0.035						7/13/06		0.0425						10/9/06		0.055																																		9/26/06		0.05

		8/25/06		0.035						7/17/06		0.04						10/9/06		0.036																																		9/26/06		0.05

		8/25/06		0.035						7/18/06		0.05						10/10/06		0.037																																		9/27/06		0.05

		8/26/06		0.03						7/19/06		0.05						10/10/06		0.032																																		9/27/06		0.05

		8/26/06		0.035						7/20/06		0.05						10/11/06		0.032																																		9/28/06		0.05

		8/28/06		0.03						7/21/06		0.055						10/11/06		0.032																																		9/28/06		0.05

		8/28/06		0.03						7/22/06		0.055						10/12/06		0.033																																		9/29/06		0.05

		8/29/06		0.03						7/23/06		0.055						10/12/06		0.03																																		9/29/06		0.05

		8/29/06		0.03						7/24/06		0.055						10/13/06		0.031																																		10/2/06		0.055

		8/30/06		0.03						7/25/06		0.05						10/13/06		0.03																																		10/2/06		0.06

		8/30/06		0.035						7/26/06		0.055						10/16/06		0.033																																		10/3/06		0.05

		8/31/06		0.03						7/26/06		0.05						10/16/06		0.032																																		10/3/06		0.05

		8/31/06		0.03						7/27/06		0.05						10/17/06		0.032																																		10/4/06		0.055

		9/1/06		0.03						7/27/06		0.05						10/17/06		0.03																																		10/4/06		0.05

		9/5/06		0.03						7/28/06		0.05						10/18/06		0.033																																		10/5/06		0.05

		9/5/06		0.03						7/31/06		0.05						10/18/06		0.03																																		10/5/06		0.05

		9/6/06		0.02						8/1/06		0.05						10/19/06		0.025																																		10/9/06		0.05

		9/7/06		0.02						8/2/06		0.05						10/19/06		0.03																																		10/9/06		0.05

		9/8/06		0.03						8/3/06		0.05						10/20/06		0.03																																		10/10/06		0.05

		9/11/06		0.03						8/4/06		0.05						10/20/06		0.035																																		10/10/06		0.05

		9/11/06		0.03						8/7/06		0.05						10/23/06		0.032																																		10/11/06		0.05

		9/12/06		0.03						8/8/06		0.05						10/23/06		0.026																																		10/11/06		0.05

		9/12/06		0.03						8/11/06		0.03						10/24/06		0.029																																		10/12/06		0.05

		9/13/06		0.025						8/11/06		0.05						10/24/06		0.029																																		10/12/06		0.05

		9/13/06		0.03						8/14/06		0.05						10/26/06		0.03																																		10/13/06		0.05

		9/14/06		0.03						8/15/06		0.035						10/26/06		0.03																																		10/13/06		0.05

		9/15/06		0.03						8/16/06		0.05						10/30/06		0.025																																		10/14/06		0.05

		9/18/06		0.03						8/17/06		0.05						10/30/06		0.023																																		10/14/06		0.05

		9/19/06		0.03						8/17/06		0.05						10/31/06		0.025																																		10/16/06		0.05

		9/19/06		0.03						8/18/06		0.05						10/31/06		0.015																																		10/16/06		0.05

		9/20/06		0.03						8/18/06		0.05						11/1/06		0.026																																		10/17/06		0.05

		9/20/06		0.03						8/19/06		0.05						11/1/06		0.022																																		10/17/06		0.05

		9/21/06		0.02						8/19/06		0.05						11/2/06		0.025																																		10/18/06		0.05

		9/21/06		0.02						8/20/06		0.05						11/2/06		0.015																																		10/18/06		0.05

		9/22/06		0.02						8/21/06		0.05						11/3/06		0.025																																		10/19/06		0.05

		9/22/06		0.02						8/21/06		0.05						11/3/06		0.015																																		10/19/06		0.05

		9/23/06		0.02						8/22/06		0.045						11/6/06		0.025																																		10/20/06		0.05

		9/23/06		0.03						8/22/06		0.05						11/6/06		0.023																																		10/20/06		0.05

		9/25/06		0.02						8/23/06		0.05						11/7/06		0.02																																		10/23/06		0.05

		9/25/06		0.02						8/23/06		0.055						11/7/06		0.018																																		10/23/06		0.055

		9/26/06		0.02						8/24/06		0.05						11/8/06		0.04																																		10/24/06		0.05

		9/26/06		0.02						8/24/06		0.055						11/8/06		0.018																																		10/24/06		0.05

		9/27/06		0.02						8/25/06		0.05						11/9/06		0.02																																		10/25/06		0.05

		9/27/06		0.05						8/25/06		0.055						11/9/06		0.019																																		10/25/06		0.05

		9/28/06		0.03						8/26/06		0.05						11/10/06		0.02																																		10/26/06		0.05

		9/28/06		0.03						8/26/06		0.05						11/10/06		0.015																																		10/26/06		0.05

		9/29/06		0.02						8/28/06		0.05						11/13/06		0.02																																		10/27/06		0.05

		9/29/06		0.03						8/28/06		0.055						11/13/06		0.02																																		10/27/06		0.05

		10/2/06		0.04						8/29/06		0.05						11/14/06		0.02																																		10/28/06		0.05

		10/3/06		0.03						8/29/06		0.05						11/14/06		0.02																																		10/28/06		0.05

		10/3/06		0.03						8/30/06		0.05						11/15/06		0.02																																		10/30/06		0.05

		10/4/06		0.03						8/30/06		0.05						11/15/06		0.02																																		10/30/06		0.05

		10/4/06		0.03						8/31/06		0.05						11/16/06		0.02																																		10/31/06		0.05

		10/5/06		0.04						8/31/06		0.055						11/17/06		0.02																																		10/31/06		0.05

		10/5/06		0.03						9/1/06		0.05						11/17/06		0.018																																		11/1/06		0.05

		10/6/06		0.02						9/5/06		0.045						11/20/06		0.02																																		11/1/06		0.05

		10/7/06		0.05						9/5/06		0.05						11/20/06		0.015																																		11/2/06		0.05

		10/7/06		0.05						9/6/06		0.045						11/21/06		0.02																																		11/2/06		0.055

		10/9/06		0.04						9/7/06		0.05						11/21/06		0.012																																		11/3/06		0.045

		10/9/06		0.04						9/8/06		0.05						11/22/06		0.02																																		11/3/06		0.05

		10/10/06		0.02						9/11/06		0.05						11/22/06		0.02																																		11/6/06		0.05

		10/10/06		0.02						9/11/06		0.05						11/27/06		0.02																																		11/6/06		0.05

		10/11/06		0.03						9/12/06		0.05						11/27/06		0.04																																		11/7/06		0.05

		10/11/06		0.04						9/12/06		0.05						11/28/06		0.02																																		11/7/06		0.055

		10/12/06		0.035						9/13/06		0.05						11/28/06		0.01																																		11/8/06		0.05

		10/12/06		0.035						9/13/06		0.05						11/29/06		0.02																																		11/8/06		0.06

		10/13/06		0.04						9/14/06		0.05						11/29/06		0.015																																		11/9/06		0.05

		10/13/06		0.04						9/15/06		0.05						11/30/06		0.02																																		11/9/06		0.05

		10/14/06		0.04						9/18/06		0.05						11/30/06		0.015																																		11/10/06		0.05

		10/14/06		0.035						9/19/06		0.05						12/1/06		0.01																																		11/10/06		0.05

		10/16/06		0.04						9/19/06		0.05						12/1/06		0.012																																		11/13/06		0.05

		10/16/06		0.035						9/20/06		0.05						12/4/06		0.01																																		11/13/06		0.06

		10/17/06		0.03						9/20/06		0.05						12/4/06		0.015																																		11/14/06		0.06

		10/17/06		0.04						9/21/06		0.05						12/5/06		0.01																																		11/14/06		0.05

		10/18/06		0.03						9/21/06		0.05						12/5/06		0.015																																		11/15/06		0.055

		10/18/06		0.03						9/22/06		0.05						12/6/06		0.01																																		11/15/06		0.05

		10/19/06		0.025						9/22/06		0.05						12/6/06		0.01																																		11/16/06		0.055

		10/19/06		0.02						9/23/06		0.05						12/7/06		0.02																																		11/16/06		0.055

		10/20/06		0.035						9/23/06		0.05						12/7/06		0.01																																		11/17/06		0.05

		10/20/06		0.05						9/25/06		0.05						12/8/06		0.01																																		11/17/06		0.055

		10/21/06		0.04						9/25/06		0.05						12/8/06		0.01																																		11/18/06		0.05

		10/21/06		0.03						9/26/06		0.05						12/11/06		0.01																																		11/18/06		0.065

		10/23/06		0.035						9/26/06		0.05						12/11/06		0.015																																		11/20/06		0.05

		10/23/06		0.04						9/27/06		0.05						12/12/06		0.01																																		11/20/06		0.06

		10/24/06		0.02						9/27/06		0.02						12/12/06		0.015																																		11/21/06		0.05

		10/24/06		0.02						9/28/06		0.03						12/13/06		0.01																																		11/21/06		0.06

		10/25/06		0.035						9/28/06		0.03						12/13/06		0.015																																		11/22/06		0.05

		10/25/06		0.035						9/29/06		0.05						12/14/06		0.02																																		11/22/06		0.05

		10/26/06		0.025						9/29/06		0.05						12/18/06		0.01																																		11/27/06		0.05

		10/26/06		0.045						10/2/06		0.04						12/18/06		0.01																																		11/27/06		0.05

		10/27/06		0.03						10/3/06		0.05						12/19/06		0.01																																		11/28/06		0.055

		10/27/06		0.03						10/3/06		0.05						12/19/06		0.009																																		11/28/06		0.06

		10/28/06		0.03						10/4/06		0.05						12/20/06		0.01																																		11/29/06		0.05

		10/28/06		0.025						10/4/06		0.05						12/20/06		0.01																																		11/29/06		0.055

		10/30/06		0.035						10/5/06		0.04						12/21/06		0.01																																		11/30/06		0.05

		10/30/06		0.035						10/5/06		0.04						12/21/06		0.008																																		11/30/06		0.05

		10/31/06		0.03						10/6/06		0.03						12/22/06		0.01																																		12/1/06		0.05

		11/1/06		0.025						10/7/06		0.03						12/27/06		0.03																																		12/1/06		0.065

		11/2/06		0.035						10/7/06		0.03						12/28/06		0.01																																		12/2/06		0.05

		11/2/06		0.03						10/9/06		0.03						12/28/06		0.01																																		12/2/06		0.065

		11/3/06		0.02						10/9/06		0.03						12/29/06		0.01																																		12/4/06		0.045

		11/6/06		0.015						10/10/06		0.05						12/29/06		0.01																																		12/4/06		0.05

		11/7/06		0.02						10/10/06		0.05						1/2/07		0.01																																		12/5/06		0.045

		11/8/06		0.025						10/11/06		0.03						1/2/07		0.01																																		12/5/06		0.05

		11/9/06		0.03						10/11/06		0.04						1/3/07		0.01																																		12/6/06		0.05

		11/10/06		0.025						10/12/06		0.035						1/3/07		0.01																																		12/6/06		0.05

		11/11/06		0.035						10/12/06		0.035						1/4/07		0.01																																		12/7/06		0.05

		11/13/06		0.035						10/13/06		0.03						1/4/07		0.01																																		12/7/06		0.05

		11/13/06		0.02						10/13/06		0.04						1/5/07		0.01																																		12/8/06		0.05

		11/14/06		0.02						10/14/06		0.03						1/5/07		0.01																																		12/8/06		0.05

		11/14/06		0.02						10/14/06		0.035						1/8/07		0.01																																		12/9/06		0.05

		11/15/06		0.03						10/16/06		0.04						1/8/07		0.01																																		12/9/06		0.05

		11/15/06		0.035						10/16/06		0.04						1/9/07		0.01																																		12/11/06		0.05

		11/16/06		0.035						10/17/06		0.04						1/9/07		0.01																																		12/11/06		0.05

		11/17/06		0.03						10/17/06		0.04						1/10/07		0.01																																		12/12/06		0.05

		11/17/06		0.035						10/18/06		0.04						1/10/07		0.01																																		12/12/06		0.05

		11/18/06		0.03						10/18/06		0.04						1/11/07		0.02																																		12/13/06		0.055

		11/18/06		0.03						10/19/06		0.04						1/11/07		0.01																																		12/13/06		0.055

		11/20/06		0.045						10/19/06		0.04						1/12/07		0.01																																		12/14/06		0.04

		11/21/06		0.035						10/20/06		0.04						1/12/07		0.01																																		12/14/06		0.05

		11/22/06		0.025						10/20/06		0.04						1/15/07		0.02																																		12/15/06		0.05

		11/22/06		0.035						10/21/06		0.03						1/15/07		0.01																																		12/15/06		0.05

		11/27/06		0.03						10/21/06		0.04						1/16/07		0.01																																		2/28/07		0.04

		11/27/06		0.035						10/23/06		0.035						1/16/07		0.015																																		2/28/07		0.04

		11/28/06		0.015						10/23/06		0.04						1/17/07		0.01																																		3/1/07		0.04

		11/29/06		0.015						10/24/06		0.035						1/17/07		0.01																																		3/2/07		0.04

		11/30/06		0.025						10/24/06		0.035						1/18/07		0.01																																		3/3/07		0.04

		12/1/06		0.025						10/25/06		0.03						1/18/07		0.01																																		3/5/07		0.04

		12/2/06		0.025						10/25/06		0.045						1/19/07		0.01																																		3/6/07		0.04

		12/4/06		0.025						10/26/06		0.045						1/19/07		0.01																																		3/7/07		0.04

		12/5/06		0.03						10/26/06		0.04						1/22/07		0.01																																		3/8/07		0.04

		12/6/06		0.03						10/27/06		0.035						1/22/07		0.02																																		3/9/07		0.04

		12/6/06		0.03						10/27/06		0.03						1/23/07		0.01																																		3/12/07		0.045

		12/7/06		0.03						10/28/06		0.03						1/23/07		0.01																																		3/13/07		0.04

		12/7/06		0.035						10/28/06		0.05						1/24/07		0.01																																		3/14/07		0.04

		12/8/06		0.03						10/30/06		0.035						1/24/07		0.005																																		3/15/07		0.03

		12/8/06		0.03						10/30/06		0.035						1/25/07		0.01																																		3/16/07		0.04

		12/9/06		0.03						10/31/06		0.035						1/25/07		0.01																																		3/17/07		0.04

		12/11/06		0.03						11/1/06		0.035						1/26/07		0.01																																		3/19/07		0.03

		12/11/06		0.03						11/2/06		0.035						1/26/07		0.01																																		3/20/07		0.04

		12/12/06		0.03						11/2/06		0.04						1/29/07		0.01																																		3/21/07		0.04

		12/12/06		0.035						11/3/06		0.035						1/29/07		0.01																																		3/22/07		0.03

		12/13/06		0.03						11/6/06		0.05						1/30/07		0.01																																		3/23/07		0.03

		12/13/06		0.03						11/7/06		0.035						1/30/07		0.01																																		3/26/07		0.04

		12/14/06		0.03						11/8/06		0.04						1/31/07		0.01																																		3/27/07		0.03

		12/14/06		0.03						11/9/06		0.035						1/31/07		0.01																																		3/28/07		0.04

		12/15/06		0.03						11/10/06		0.045						2/1/07		0.01																																		3/29/07		0.03

		12/15/06		0.03						11/11/06		0.04						2/1/07		0.005																																		3/30/07		0.04

		12/18/06		0.03						11/13/06		0.04						2/2/07		0.01																																		3/31/07		0.03

		12/18/06		0.03						11/13/06		0.05						2/2/07		0.005																																		4/2/07		0.03

		12/19/06		0.03						11/14/06		0.04						2/5/07		0.01																																		4/3/07		0.045

		12/19/06		0.03						11/14/06		0.04						2/5/07		0.005																																		4/4/07		0.04

		12/20/06		0.03						11/15/06		0.03						2/6/07		0.01																																		4/5/07		0.04

		12/21/06		0.03						11/15/06		0.03						2/6/07		0.005																																		4/6/07		0.04

		12/21/06		0.03						11/16/06		0.03						2/7/07		0.01																																		4/9/07		0.04

		12/22/06		0.02						11/17/06		0.03						2/7/07		0.005																																		4/10/07		0.03

		12/22/06		0.035						11/17/06		0.035						2/8/07		0.01																																		4/11/07		0.04

		12/27/06		0.03						11/18/06		0.03						2/8/07		0.015																																		4/12/07		0.04

		12/27/06		0.03						11/18/06		0.03						2/9/07		0.01																																		4/13/07		0.035

		12/28/06		0.03						11/20/06		0.015						2/9/07		0.018																																		4/16/07		0.035

		12/28/06		0.03						11/21/06		0.03						2/12/07		0.01																																		4/17/07		0.04

		12/29/06		0.03						11/22/06		0.035						2/12/07		0.012																																		4/18/07		0.035

		12/29/06		0.035						11/22/06		0.035						2/13/07		0.01																																		4/19/07		0.04

		1/2/07		0.03						11/27/06		0.035						2/13/07		0.02																																		4/20/07		0.04

		1/2/07		0.03						11/27/06		0.03						2/14/07		0.02																																		4/23/07		0.03

		1/3/07		0.03						11/28/06		0.035						2/14/07		0.015																																		4/24/07		0.04

		1/3/07		0.03						11/29/06		0.035						2/15/07		0.02																																		4/25/07		0.035

		1/4/07		0.03						11/30/06		0.035						2/16/07		0.01																																		4/26/07		0.035

		1/5/07		0.03						12/1/06		0.03						2/20/07		0.015																																		4/27/07		0.035

		1/5/07		0.03						12/2/06		0.03						2/20/07		0.015																																		4/28/07		0.045

		1/8/07		0.03						12/4/06		0.03						2/21/07		0.02																																		4/30/07		0.04

		1/8/07		0.03						12/5/06		0.03						2/21/07		0.015																																		5/1/07		0.04

		1/9/07		0.03						12/6/06		0.03						2/22/07		0.02																																		5/2/07		0.04

		1/9/07		0.03						12/6/06		0.035						2/22/07		0.018																																		5/3/07		0.04

		1/10/07		0.03						12/7/06		0.03						2/23/07		0.02																																		5/4/07		0.04

		1/10/07		0.03						12/7/06		0.03						2/23/07		0.016																																		5/5/07		0.04

		1/11/07		0.03						12/8/06		0.03						2/26/07		0.015																																		5/7/07		0.035

		1/11/07		0.03						12/8/06		0.035						2/26/07		0.014																																		5/8/07		0.04

		1/12/07		0.03						12/9/06		0.03						2/27/07		0.015																																		5/9/07		0.045

		1/13/07		0.03						12/11/06		0.03						2/27/07		0.014																																		5/10/07		0.04

		1/13/07		0.03						12/11/06		0.03						2/28/07		0.01																																		5/11/07		0.035

		1/15/07		0.03						12/12/06		0.03						3/1/07		0.015																																		5/14/07		0.03

		1/15/07		0.03						12/12/06		0.03						3/2/07		0.015																																		5/15/07		0.035

		1/16/07		0.03						12/13/06		0.03						3/5/07		0.01																																		5/16/07		0.045

		1/16/07		0.025						12/13/06		0.03						3/6/07		0.01																																		5/17/07		0.035

		1/17/07		0.02						12/14/06		0.03						3/7/07		0.04																																		5/18/07		0.04

		1/18/07		0.02						12/14/06		0.035						3/8/07		0.04																																		5/19/07		0.04

		1/19/07		0.03						12/15/06		0.03						3/9/07		0.04																																		5/21/07		0.04

		1/19/07		0.03						12/15/06		0.035						3/12/07		0.04																																		5/22/07		0.04

		1/20/07		0.03						12/18/06		0.03						3/13/07		0.04																																		5/23/07		0.045

		1/22/07		0.03						12/18/06		0.03						3/14/07		0.04																																		5/24/07		0.04

		1/23/07		0.03						12/19/06		0.03						3/15/07		0.035																																		5/29/07		0.03

		1/24/07		0.03						12/19/06		0.03						3/16/07		0.04																																		5/30/07		0.03

		1/24/07		0.03						12/20/06		0.03						3/19/07		0.035																																		5/31/07		0.035

		1/25/07		0.03						12/21/06		0.03						3/20/07		0.035																																		6/1/07		0.035

		1/25/07		0.03						12/21/06		0.035						3/21/07		0.035																																		6/2/07		0.05

		1/26/07		0.03						12/22/06		0.03						3/22/07		0.032																																		6/4/07		0.035

		1/26/07		0.035						12/22/06		0.03						3/23/07		0.03																																		6/5/07		0.04

		1/29/07		0.03						12/27/06		0.03						3/26/07		0.03																																		6/6/07		0.04

		1/29/07		0.035						12/27/06		0.03						3/27/07		0.03																																		6/7/07		0.04

		1/30/07		0.035						12/28/06		0.03						3/28/07		0.035																																		6/8/07		0.045

		1/30/07		0.035						12/28/06		0.035						3/29/07		0.035																																		6/9/07		0.04

		1/31/07		0.03						12/29/06		0.03						3/30/07		0.03																																		6/11/07		0.04

		1/31/07		0.035						12/29/06		0.035						4/2/07		0.03																																		6/12/07		0.04

		2/1/07		0.03						1/2/07		0.03						4/3/07		0.025																																		6/13/07		0.04

		2/1/07		0.03						1/2/07		0.03						4/4/07		0.03																																		6/14/07		0.035

		2/2/07		0.03						1/3/07		0.03						4/5/07		0.025																																		6/15/07		0.045

		2/2/07		0.03						1/3/07		0.03						4/6/07		0.03																																		6/16/07		0.05

		2/3/07		0.03						1/4/07		0.03						4/9/07		0.025																																		6/19/07		0.04

		2/3/07		0.035						1/5/07		0.03						4/10/07		0.03																																		6/20/07		0.04

		2/5/07		0.03						1/5/07		0.03						4/11/07		0.03																																		6/21/07		0.035

		2/5/07		0.03						1/8/07		0.03						4/12/07		0.03																																		6/22/07		0.04

		2/6/07		0.03						1/8/07		0.03						4/13/07		0.028																																		6/23/07		0.04

		2/6/07		0.03						1/9/07		0.03						4/16/07		0.032																																		6/25/07		0.04

		2/7/07		0.05						1/9/07		0.03						4/17/07		0.03																																		6/26/07		0.04

		2/7/07		0.04						1/10/07		0.03						4/18/07		0.025																																		6/27/07		0.04

		2/8/07		0.04						1/10/07		0.035						4/19/07		0.025																																		6/28/07		0.04

		2/8/07		0.03						1/11/07		0.03						4/23/07		0.04																																		6/29/07		0.04

		2/10/07		0.03						1/11/07		0.03						4/24/07		0.044																																		7/2/07		0.04

		2/10/07		0.05						1/12/07		0.03						4/25/07		0.049																																		7/3/07		0.045

		2/12/07		0.03						1/13/07		0.03						4/26/07		0.049																																		7/5/07		0.05

		2/13/07		0.035						1/13/07		0.03						4/27/07		0.045																																		7/6/07		0.05

		2/13/07		0.04						1/15/07		0.03						4/30/07		0.045																																		7/9/07		0.045

		2/14/07		0.04						1/15/07		0.03						5/1/07		0.042																																		7/10/07		0.07

		2/14/07		0.04						1/16/07		0.03						5/2/07		0.045																																		7/11/07		0.045

		2/15/07		0.05						1/16/07		0.03						5/3/07		0.042																																		7/12/07		0.055

		2/15/07		0.04						1/17/07		0.03						5/4/07		0.045																																		7/13/07		0.05

		2/16/07		0.04						1/18/07		0.03						5/7/07		0.045																																		7/14/07		0.05

		2/16/07		0.04						1/19/07		0.035						5/8/07		0.045																																		7/16/07		0.055

		2/20/07		0.05						1/19/07		0.03						5/9/07		0.045																																		7/17/07		0.05

		2/20/07		0.05						1/20/07		0.03						5/10/07		0.045																																		7/18/07		0.075

		2/21/07		0.04						1/22/07		0.03						5/11/07		0.045																																		7/19/07		0.07

		2/21/07		0.055						1/23/07		0.03						5/14/07		0.046																																		7/20/07		0.07

		2/22/07		0.04						1/24/07		0.03						5/15/07		0.05																																		7/23/07		0.07

		2/22/07		0.05						1/24/07		0.03						5/16/07		0.055																																		7/24/07		0.07

		2/23/07		0.03						1/25/07		0.03						5/17/07		0.045																																		7/25/07		0.065

		2/23/07		0.05						1/25/07		0.03						5/18/07		0.04																																		7/26/07		0.055

		2/26/07		0.05						1/26/07		0.03						5/21/07		0.044																																		7/27/07		0.06

		2/26/07		0.04						1/26/07		0.035						5/22/07		0.045																																		7/28/07		0.065

		2/27/07		0.03						1/29/07		0.035						5/23/07		0.045																																		7/30/07		0.05

		2/27/07		0.04						1/29/07		0.035						5/24/07		0.04																																		7/31/07		0.06

		2/28/07		0.03						1/30/07		0.03						5/24/07		0.04																																		8/1/07		0.06

		2/28/07		0.03						1/30/07		0.03						5/29/07		0.025																																		8/2/07		0.06

		3/1/07		0.04						1/31/07		0.03						5/30/07		0.045																																		8/3/07		0.06

		3/2/07		0.04						1/31/07		0.035						5/31/07		0.05																																		8/6/07		0.06

		3/5/07		0.04						2/1/07		0.035						6/1/07		0.051																																		8/7/07		0.06

		3/6/07		0.04						2/1/07		0.03						6/4/07		0.044																																		8/8/07		0.05

		3/7/07		0.04						2/2/07		0.03						6/5/07		0.047																																		8/9/07		0.05

		3/8/07		0.04						2/2/07		0.03						6/6/07		0.046																																		8/10/07		0.05

		3/9/07		0.04						2/3/07		0.03						6/7/07		0.05																																		8/11/07		0.05

		3/12/07		0.04						2/3/07		0.03						6/8/07		0.048																																		8/13/07		0.06

		3/13/07		0.03						2/5/07		0.03						6/9/07		0.049																																		8/14/07		0.05

		3/14/07		0.03						2/5/07		0.03						6/11/07		0.049																																		8/15/07		0.05

		3/15/07		0.04						2/6/07		0.03						6/12/07		0.05																																		8/16/07		0.055

		3/16/07		0.04						2/6/07		0.035						6/13/07		0.045																																		8/17/07		0.055

		3/19/07		0.03						2/7/07		0.03						6/14/07		0.048																																		8/20/07		0.05

		3/20/07		0.04						2/7/07		0.03						6/15/07		0.045																																		8/21/07		0.05

		3/21/07		0.035						2/8/07		0.03						6/18/07		0.045																																		8/22/07		0.05

		3/22/07		0.04						2/8/07		0.03						6/19/07		0.045																																		8/23/07		0.05

		3/23/07		0.04						2/10/07		0.03						6/20/07		0.045																																		8/24/07		0.05

		3/26/07		0.035						2/10/07		0.04						6/21/07		0.045																																		8/27/07		0.05

		3/27/07		0.04						2/12/07		0.03						6/25/07		0.042																																		8/28/07		0.05

		3/28/07		0.035						2/13/07		0.035						6/26/07		0.045																																		8/29/07		0.05

		3/29/07		0.035						2/13/07		0.05						6/27/07		0.04																																		8/30/07		0.05

		3/30/07		0.03						2/14/07		0.04						6/28/07		0.063																																		8/31/07		0.05

		3/31/07		0.035						2/14/07		0.04						6/29/07		0.061																																		9/4/07		0.05

		4/2/07		0.04						2/15/07		0.05						7/2/07		0.06																																		9/5/07		0.05

		4/3/07		0.035						2/15/07		0.04						7/3/07		0.062																																		9/6/07		0.05

		4/4/07		0.035						2/16/07		0.04						7/5/07		0.06																																		9/7/07		0.055

		4/5/07		0.035						2/16/07		0.04						7/6/07		0.058																																		9/10/07		0.045

		4/6/07		0.035						2/20/07		0.05						7/9/07		0.06																																		9/11/07		0.05

		4/9/07		0.035						2/20/07		0.05						7/10/07		0.06																																		9/12/07		0.05

		4/10/07		0.03						2/21/07		0.04						7/11/07		0.055																																		9/13/07		0.045

		4/11/07		0.03						2/21/07		0.035						7/12/07		0.056																																		9/14/07		0.05

		4/12/07		0.03						2/22/07		0.04						7/13/07		0.056																																		9/17/07		0.05

		4/13/07		0.03						2/22/07		0.04						7/16/07		0.055																																		9/18/07		0.045

		4/14/07		0.03						2/23/07		0.03						7/17/07		0.05																																		9/19/07		0.05

		4/16/07		0.03						2/23/07		0.04						7/18/07		0.045																																		9/20/07		0.05

		4/17/07		0.03						2/26/07		0.03						7/19/07		0.045																																		9/21/07		0.05

		4/18/07		0.025						2/26/07		0.035						7/20/07		0.04																																		9/22/07		0.05

		4/19/07		0.03						2/27/07		0.03						7/23/07		0.04																																		9/24/07		0.05

		4/20/07		0.035						2/27/07		0.03						7/24/07		0.04																																		9/25/07		0.05

		4/21/07		0.035						2/28/07		0.03						7/25/07		0.04																																		9/26/07		0.05

		4/23/07		0.025						3/1/07		0.03						7/26/07		0.04																																		9/27/07		0.05

		4/24/07		0.02						3/2/07		0.03						7/28/07		0.04																																		9/28/07		0.05

		4/25/07		0.03						3/5/07		0.03						7/30/07		0.044																																		10/1/07		0.05

		4/26/07		0.04						3/6/07		0.03						7/31/07		0.044																																		10/2/07		0.06

		4/27/07		0.025						3/7/07		0.04						8/1/07		0.04																																		10/3/07		0.05

		4/30/07		0.025						3/8/07		0.04						8/2/07		0.04																																		10/4/07		0.05

		5/1/07		0.03						3/9/07		0.04						8/3/07		0.04																																		10/5/07		0.045

		5/2/07		0.02						3/12/07		0.04						8/4/07		0.042																																		10/8/07		0.05

		5/3/07		0.02						3/13/07		0.04						8/6/07		0.04																																		10/9/07		0.05

		5/4/07		0.02						3/14/07		0.03						8/7/07		0.04																																		10/10/07		0.05

		5/5/07		0.02						3/15/07		0.035						8/8/07		0.034																																		10/11/07		0.05

		5/7/07		0.02						3/16/07		0.035						8/9/07		0.032																																		10/12/07		0.05

		5/8/07		0.025						3/19/07		0.035						8/10/07		0.043																																		10/15/07		0.05

		5/9/07		0.03						3/20/07		0.04						8/13/07		0.045																																		10/16/07		0.045

		5/10/07		0.025						3/21/07		0.04						8/14/07		0.045																																		10/17/07		0.05

		5/11/07		0.005						3/22/07		0.04						8/15/07		0.043																																		10/18/07		0.05

		5/14/07		0.035						3/23/07		0.035						8/16/07		0.04																																		10/19/07		0.045

		5/15/07		0.035						3/26/07		0.035						8/17/07		0.04																																		10/22/07		0.05

		5/16/07		0.03						3/27/07		0.04						8/20/07		0.04																																		10/23/07		0.05

		5/17/07		0.03						3/28/07		0.04						8/21/07		0.03																																		10/24/07		0.045

		5/18/07		0.03						3/29/07		0.035						8/22/07		0.04																																		10/25/07		0.045

		5/19/07		0.03						3/30/07		0.03						8/23/07		0.04																																		10/26/07		0.05

		5/21/07		0.025						3/31/07		0.035						8/24/07		0.04																																		10/29/07		0.05

		5/22/07		0.025						4/2/07		0.035						8/27/07		0.045																																		10/30/07		0.045

		5/23/07		0.025						4/3/07		0.035						8/28/07		0.04																																		10/31/07		0.05

		5/24/07		0.02						4/4/07		0.04						8/29/07		0.055																																		11/1/07		0.045

		5/25/07		0.025						4/5/07		0.04						8/30/07		0.055																																		11/2/07		0.05

		5/29/07		0.025						4/6/07		0.04						8/31/07		0.05																																		11/5/07		0.05

		5/30/07		0.048						4/9/07		0.035						9/4/07		0.05																																		11/6/07		0.045

		5/31/07		0.04						4/10/07		0.035						9/5/07		0.04						0.61		0.4																										11/7/07		0.05

		6/1/07		0.025						4/11/07		0.04						9/6/07		0.05						0.61		0.41																										11/8/07		0.05

		6/2/07		0.03						4/12/07		0.035						9/7/07		0.045						0.6		0.41																										11/9/07		0.05

		6/4/07		0.03						4/13/07		0.035						9/8/07		0.04						0.6		0.41																										11/12/07		0.045

		6/5/07		0.0175						4/14/07		0.03						9/10/07		0.055						0.61		0.41																										11/13/07		0.05

		6/6/07		0.03						4/16/07		0.035						9/11/07		0.05						0.61		0.41																										11/14/07		0.045

		6/7/07		0.04						4/17/07		0.035						9/12/07		0.05						0.61		0.41																										11/15/07		0.045

		6/8/07		0.025						4/18/07		0.04						9/13/07		0.05						0.61		0.41																										11/16/07		0.045

		6/9/07		0.02						4/19/07		0.035						9/14/07		0.05						0.6		0.42																										11/19/07		0.045

		6/11/07		0.04						4/20/07		0.04						9/15/07		0.05						0.6		0.4																										11/20/07		0.045

		6/12/07		0.02						4/21/07		0.035						9/17/07		0.054						0.6		0.41																										11/21/07		0.045

		6/13/07		0.03						4/23/07		0.035						9/18/07		0.054						0.61		0.41																										11/26/07		0.045

		6/14/07		0.025						4/24/07		0.02						9/19/07		0.045						0.65		0.4																										11/27/07		0.045

		6/15/07		0.02						4/25/07		0.04						9/20/07		0.045						0.61		0.41																										11/28/07		0.045

		6/18/07		0.025						4/26/07		0.035						9/21/07		0.04						0.6		0.4																										11/29/07		0.045

		6/19/07		0.02						4/27/07		0.04						9/24/07		0.035						0.6		0.4																										11/30/07		0.045

		6/20/07		0.03						4/30/07		0.025						9/25/07		0.04						0.62		0.4																										12/1/07		0.045

		6/21/07		0.016						5/1/07		0.03						9/26/07		0.04						0.62		0.42																										12/3/07		0.045

		6/22/07		0.025						5/2/07		0.03						9/27/07		0.04						0.62		0.42																										12/4/07		0.045

		6/25/07		0.02						5/3/07		0.03						9/28/07		0.05						0.6		0.4																										12/5/07		0.045

		6/26/07		0.025						5/4/07		0.035						10/1/07		0.04						0.62		0.42																										12/6/07		0.045

		6/27/07		0.03						5/5/07		0.035						10/2/07		0.045						0.62		0.42																										12/7/07		0.045

		6/28/07		0.045						5/7/07		0.04						10/3/07		0.045						0.62		0.42																										12/8/07		0.045

		6/29/07		0.025						5/8/07		0.045						10/4/07		0.05						0.61		0.42																										12/10/07		0.045

		7/2/07		0.04						5/9/07		0.03						10/5/07		0.05						0.62		0.42																										12/11/07		0.04

		7/3/07		0.04						5/10/07		0.04						10/8/07		0.05						0.62		0.42																										12/12/07		0.04

		7/5/07		0.04						5/11/07		0.03						10/9/07		0.04						0.62		0.42																										12/13/07		0.04

		7/6/07		0.04						5/14/07		0.03						10/10/07		0.04						0.62		0.42																										12/14/07		0.04

		7/9/07		0.04						5/15/07		0.03						10/11/07		0.05						0.62		0.42																										12/17/07		0.04

		7/10/07		0.03						5/16/07		0.03						10/12/07		0.045						0.62		0.42																										12/18/07		0.045

		7/11/07		0.035						5/17/07		0.03						10/13/07		0.04						0.62		0.42																										12/19/07		0.04

		7/12/07		0.035						5/18/07		0.03						10/15/07		0.04						0.61		0.41																										12/20/07		0.04

		7/13/07		0.03						5/19/07		0.03						10/16/07		0.04						0.62		0.42																										12/26/07		0.04

		7/16/07		0.03						5/21/07		0.03						10/17/07		0.04						0.61		0.41																										12/27/07		0.04

		7/17/07		0.035						5/22/07		0.03						10/18/07		0.04						0.62		0.42																										12/28/07		0.04

		7/18/07		0.03						5/23/07		0.03						10/19/07		0.04						0.62		0.42																										12/31/07		0.05

		7/19/07		0.03						5/24/07		0.03						10/22/07		0.045						0.62		0.42																										1/2/08		0.04

		7/20/07		0.03						5/25/07		0.03						10/23/07		0.05						0.64		0.44																										1/3/08		0.04

		7/23/07		0.04						5/29/07		0.035						10/24/07		0.045						0.62		0.42																										1/4/08		0.04

		7/24/07		0.035						5/30/07		0.02						10/25/07		0.03						0.62		0.42																										1/7/08		0.04

		7/25/07		0.035						5/31/07		0.03						10/26/07		0.035						0.62		0.42																										1/8/08		0.04

		7/26/07		0.04						6/1/07		0.03						10/29/07		0.03						0.62		0.42																										1/9/08		0.04

		7/27/07		0.04						6/2/07		0.03						10/30/07		0.025						0.62		0.42																										1/10/08		0.04

		7/30/07		0.035						6/4/07		0.03						10/31/07		0.03						0.62		0.42																										1/11/08		0.04

		7/31/07		0.035						6/5/07		0.04						11/1/07		0.035						0.62		0.42																										1/14/08		0.04

		8/1/07		0.03						6/6/07		0.025						11/2/07		0.035						0.62		0.42																										1/15/08		0.04

		8/2/07		0.035						6/7/07		0.03						11/5/07		0.025						0.62		0.4																										1/16/08		0.04

		8/3/07		0.04						6/8/07		0.03						11/6/07		0.04						0.62		0.41																										1/17/08		0.04

		8/4/07		0.03						6/9/07		0.025						11/7/07		0.02						0.62		0.42																										1/18/08		0.04

		8/6/07		0.03						6/11/07		0.03						11/8/07		0.03						0.62		0.42																										1/21/08		0.04

		8/7/07		0.035						6/12/07		0.02						11/9/07		0.02						0.62		0.42																										1/22/08		0.04

		8/8/07		0.03						6/13/07		0.03						11/12/07		0.035						0.62		0.42																										1/23/08		0.04

		8/9/07		0.03						6/14/07		0.025						11/13/07		0.04						0.62		0.4																										1/24/08		0.04

		8/10/07		0.04						6/15/07		0.025						11/14/07		0.04						0.62		0.42																										1/25/08		0.045

		8/13/07		0.03						6/18/07		0.03						11/15/07		0.04						0.62		0.42																										1/28/08		0.04

		8/14/07		0.03						6/19/07		0.025						11/16/07		0.035						0.62		0.42																										1/29/08		0.04

		8/15/07		0.03						6/20/07		0.03						11/19/07		0.045						0.66		0.44																										1/30/08		0.04

		8/17/07		0.03						6/21/07		0.03						11/20/07		0.04						0.64		0.42																										1/31/08		0.04

		8/20/07		0.03						6/22/07		0.02						11/21/07		0.04						0.64		0.42																										2/1/08		0.04

		8/21/07		0.03						6/25/07		0.02						11/26/07		0.04						0.66		0.44																										2/4/08		0.04

		8/22/07		0.03						6/26/07		0.02						11/27/07		0.042						0.66		0.44																										2/5/08		0.04

		8/23/07		0.03						6/27/07		0.03						11/28/07		0.04						0.66		0.44																										2/6/08		0.04

		8/24/07		0.03						6/28/07		0.03						11/29/07		0.03						0.64		0.44																										2/7/08		0.04

		8/25/07		0.02						6/29/07		0.04						11/30/07		0.03						0.64		0.44																										2/8/08		0.04

		8/27/07		0.04						7/2/07		0.03						12/3/07		0.04						0.64		0.44																										2/11/08		0.04

		8/28/07		0.035						7/3/07		0.025						12/4/07		0.03						0.64		0.42																										2/12/08		0.04

		8/29/07		0.04						7/5/07		0.03						12/5/07		0.03						0.64		0.44																										2/13/08		0.04

		8/30/07		0.03						7/6/07		0.025						12/6/07		0.03						0.64		0.42																										2/14/08		0.04

		8/31/07		0.03						7/9/07		0.025						12/7/07		0.03						0.64		0.44																										2/15/08		0.04

		9/4/07		0.03						7/10/07		0.03						12/10/07		0.03						0.64		0.44																										2/16/08		0.04

		9/5/07		0.03						7/11/07		0.035						12/11/07		0.03						0.66		0.42																										2/19/08		0.04

		9/6/07		0.035						7/12/07		0.035						12/12/07		0.03						0.6		0.42																										2/20/08		0.045

		9/7/07		0.02						7/13/07		0.03						12/13/07		0.045						0.66		0.42																										2/21/08		0.04

		9/8/07		0.04						7/16/07		0.03						12/14/07		0.03						0.66		0.42																										2/22/08		0.04

		9/10/07		0.025						7/17/07		0.03						12/17/07		0.03						0.64		0.42																										2/25/08		0.04

		9/11/07		0.035						7/18/07		0.025						12/18/07		0.03						0.66		0.4																										2/26/08		0.04

		9/12/07		0.035						7/19/07		0.025						12/19/07		0.02						0.66		0.42																										2/27/08		0.04

		9/13/07		0.03						7/20/07		0.035						12/20/07		0.03						0.64		0.42																										2/28/08		0.04

		9/14/07		0.03						7/23/07		0.03						12/21/07		0.04						0.66		0.42																										2/29/08		0.04

		9/17/07		0.03						7/24/07		0.025						12/26/07		0.03						0.64		0.42																										3/1/08		0.04

		9/18/07		0.025						7/25/07		0.035						12/27/07		0.025						0.62		0.44																										3/2/08		0.04

		9/19/07		0.04						7/26/07		0.03						12/28/07		0.025						0.64		0.44																										3/3/08		0.04

		9/20/07		0.04						7/27/07		0.03						12/31/07		0.02						0.64		0.44																										3/4/08		0.04

		9/21/07		0.03						7/30/07		0.035																																										3/5/08		0.04

		9/24/07		0.025						7/31/07		0.04						2/14/08		0.04						0.292		0.309		0.485		61		1180																				3/6/08		0.04

		9/25/07		0.035						8/1/07		0.03						2/15/08		0.037		69		50		0.28		0.31		0.414		61		1172																				3/7/08		0.04

		9/26/07		0.025						8/2/07		0.035						2/19/08		0.035		69		48		0.293		0.309		0.426		60		1184																				3/8/08		0.04

		9/27/07		0.02						8/3/07		0.03						2/20/08		0.03		70		46		0.26		0.309		0.41		63		1184																				3/10/08		0.04

		9/28/07		0.02						8/4/07		0.03						2/21/08		0.032		70		46		0.29		0.305		0.441		62		1164																				3/11/08		0.04

		9/29/07		0.02						8/6/07		0.03						2/22/08		0.031		70		45		0.281		0.307		0.419		62		1184																				3/12/08		0.04

		10/1/07		0.015						8/7/07		0.025						2/25/08		0.069		70		46		0.288		0.311		0.421		63		1184																				3/13/08		0.04

		10/2/07		0.035						8/8/07		0.03						2/26/08		0.068		70		44		0.281		0.312		0.413		64		1192																				3/14/08		0.04

		10/3/07		0.03						8/9/07		0.045						2/27/08		0.067		70		45		0.288		0.311		0.413		62		1184																				3/15/08		0.04

		10/4/07		0.04						8/10/07		0.04						2/28/08		0.063		70		46		0.283		0.31		0.457		62		1172																				3/17/08		0.04

		10/5/07		0.025						8/13/07		0.04						2/29/08		0.064		70		45		0.256		0.311		0.409		63		1184																				3/18/08		0.04

		10/8/07		0.03						8/14/07		0.04						3/3/08		0.07		70		33		0.285		0.311		0.435		63		1204																				3/19/08		0.04

		10/9/07		0.03						8/15/07		0.04						3/4/08		0.07		70		44		0.261		0.311		0.438		63		1184																				3/20/08		0.04

		10/10/07		0.03						8/17/07		0.04						3/5/08		0.069		70		44		0.291		0.311		0.445		63		1184																				3/21/08		0.04

		10/11/07		0.03						8/20/07		0.03						3/6/08		0.068		70		44		0.281		0.311		0.458		61		1184																				3/22/08		0.04

		10/12/07		0.02						8/21/07		0.03						3/7/08		0.067		70		44		0.282		0.322		0.455		63		1192																				3/24/08		0.04

		10/15/07		0.03						8/22/07		0.035						3/10/08		0.069		70		46		0.264		0.321		0.428		64		1184																				3/25/08		0.04

		10/16/07		0.02						8/23/07		0.03						3/11/08		0.071		70		43		0.285		0.322		0.438		63		1204																				3/26/08		0.045

		10/17/07		0.04						8/24/07		0.035						3/12/08		0.056		70		44		0.261		0.312		0.422		62		1188																				3/27/08		0.04		70		25

		10/18/07		0.04						8/25/07		0.02						3/14/08		0.067		70		43		0.261		0.321		0.451		63		1184																				3/28/08		0.04		70		41

		10/19/07		0.025						8/27/07		0.025						3/17/08		0.069		70		45		0.26		0.32		0.439		63		1196																				3/31/08		0.04		70		28

		10/22/07		0.03						8/28/07		0.025						3/18/08		0.062		70		47		0.279		0.32		0.422		63		1196																				4/1/08		0.04		70		29

		10/23/07		0.03						8/29/07		0.03						3/19/08		0.053		70		44		0.273		0.321		0.419		64		1192																				4/2/08		0.055		70		36

		10/24/07		0.04						8/30/07		0.03						3/20/08		0.064		70		33		0.262		0.321		0.431		64		1192																				4/3/08		0.04		69		40

		10/25/07		0.035						8/31/07		0.03						3/21/08		0.063		70		35		0.277		0.322		0.439		63		1196																				4/4/08		0.045		70		44

		10/26/07		0.045						9/4/07		0.03						3/24/08		0.052		70		42		0.238		0.321		0.418		63		1184																				4/5/08		0.04		70		41

		10/29/07		0.02						9/5/07		0.03						3/25/08		0.057		70		38		0.264		0.319		0.445		63		1192																				4/7/08		0.05		70		44

		10/30/07		0.02						9/6/07		0.03						3/26/08		0.056		70		35		0.276		0.321		0.447		63		1204																				4/8/08		0.05		70		44

		10/31/07		0.02						9/7/07		0.03						3/27/08		0.07		70		24		0.28		0.32		0.46		63		1204																				4/9/08		0.05		70		44

		11/1/07		0.03						9/8/07		0.03						3/28/08		0.05		70		40		0.26		0.32		0.44		63		1192																				4/10/08		0.05		70		44

		11/2/07		0.025						9/10/07		0.02						3/31/08		0.06		70		27		0.3		0.32		0.48		63		1204																				4/11/08		0.05		70		46

		11/5/07		0.03						9/11/07		0.02						4/1/08		0.06		70		28		0.28		0.32		0.46		61		1192																				4/14/08		0.05		72		41

		11/6/07		0.025						9/12/07		0.03						4/2/08		0.06		70		30		0.28		0.32		0.44		63		1204																				4/15/08		0.05		74		42

		11/7/07		0.025						9/13/07		0.02						4/3/08		0.06		70		38		0.28		0.32		0.44		64		1192																				4/16/08		0.05		70		45

		11/8/07		0.085						9/14/07		0.035						4/4/08		0.05		70		44		0.26		0.32		0.44		63		1196																				4/17/08		0.045		72		46

		11/9/07		0.08						9/17/07		0.03						4/5/08		0.05		70		40		0.26		0.32		0.44		63		1196																				4/18/08		0.04		70		48

		11/12/07		0.075						9/18/07		0.03						4/7/08		0.055		70		44		0.26		0.32		0.46		65		1204																				4/19/08		0.05		69		48

		11/13/07		0.08						9/19/07		0.04						4/8/08		0.055		70		44		0.28		0.32		0.44		61		1192																				4/21/08		0.05		73		47

		11/14/07		0.075						9/20/07		0.04						4/9/08		0.055		70		46		0.28		0.32		0.44		63		1196																				4/22/08		0.045		77		46

		11/15/07		0.075						9/21/07		0.03						4/10/08		0.05		70		45		0.28		0.32		0.44		61		1204																				4/23/08		0.05		71		45

		11/16/07		0.07						9/24/07		0.025						4/11/08		0.05		70		42		0.28		0.32		0.44		61		1192																				4/24/08		0.045		73		46

		11/19/07		0.075						9/25/07		0.025						4/14/08		0.05		70		43		0.28		0.32		0.46		61		1196																				4/25/08		0.04		70		46

		11/20/07		0.07						9/26/07		0.03						4/15/08		0.05		73		41		0.28		0.32		0.44		62		1196																				4/30/08		0.06		69		26

		11/21/07		0.075						9/27/07		0.03						4/16/08		0.05		72		43		0.28		0.32		0.48		62		1196																				5/1/08		0.04		75		42

		11/26/07		0.08						9/28/07		0.03						4/17/08		0.05		72		44		0.28		0.32		0.48		62		1196																				5/2/08		0.04		72		35

		11/27/07		0.08						9/29/07		0.025						4/18/08		0.05		72		45		0.28		0.32		0.48		62		1196																				5/3/08		0.04		78		34

		11/28/07		0.08						10/1/07		0.03						4/19/08		0.06		72		44		0.28		0.32		0.48		62		1196																				5/5/08		0.04		71		40

		11/29/07		0.075						10/2/07		0.025						4/21/08		0.055		71		45		0.28		0.32		0.46		64		1196																				5/6/08		0.045		75		40

		11/30/07		0.08						10/3/07		0.03						4/22/08		0.05		72		43		0.28		0.32		0.46		64		1196																				5/7/08		0.05		72		36

		12/3/07		0.07						10/4/07		0.03						4/23/08		0.05		73		42		0.28		0.32		0.48		63		1196																				5/8/08		0.045		72		38

		12/4/07		0.08						10/5/07		0.02						4/24/08		0.055		73		45		0.28		0.32		0.46		63		1196																				5/9/08		0.04		74		34

		12/5/07		0.07						10/8/07		0.03						4/25/08		0.05		73		41		0.26		0.32		0.44		63		1204																				5/10/08		0.045		72		34

		12/6/07		0.08						10/9/07		0.02						4/28/08								0.26		0.32		0.44		63		1204																				5/12/08		0.055		69		28

		12/7/07		0.075						10/10/07		0.025						4/29/08								0.28		0.32		0.44		60		1184																				5/13/08		0.04		75		31

		12/10/07		0.075						10/11/07		0.03						4/30/08		0.06		70		25		0.28		0.32		0.46		60		1192																				5/14/08		0.05		71		38

		12/11/07		0.075						10/12/07		0.02						5/1/08		0.055		73		39		0.28		0.32		0.46		60		1196																				5/15/08		0.04		72		42

		12/12/07		0.075						10/15/07		0.025						5/2/08		0.045		72		34		0.28		0.32		0.46		60		1210																				5/16/08		0.04		71		48

		12/13/07		0.075						10/16/07		0.025						5/3/08		0.05		73		38		0.28		0.32		0.46		60		1210																				5/19/08		0.04		75		42

		12/14/07		0.075						10/17/07		0.03						5/5/08		0.04		72		38		0.28		0.32		0.44		60		1192																				5/20/08		0.04		73		44

		12/17/07		0.08						10/18/07		0.025						5/6/08		0.04		73		42		0.28		0.32		0.44		60		1184																				5/21/08		0.04		71		36

		12/18/07		0.075						10/19/07		0.025						5/7/08		0.04		73		37		0.28		0.32		0.44		62		1196																				5/22/08		0.04		73		30

		12/19/07		0.08						10/22/07		0.025						5/8/08		0.04		73		35		0.28		0.32		0.44		60		1196																				5/23/08		0.04		71		36

		12/20/07		0.08						10/23/07		0.02						5/9/08		0.04		72		34		0.3		0.32		0.46		62		1204																				5/27/08		0.02		73		37

		12/21/07		0.08						10/24/07		0.035						5/10/08		0.04		72		32		0.3		0.32		0.46		62		1204																				5/28/08		0.03		71		39

		12/26/07		0.08						10/25/07		0.025						5/12/08		0.055		68		28		0.26		0.32		0.42		60		1196																				5/29/08		0.03		74		39

		12/27/07		0.08						10/26/07		0.035						5/13/08		0.04		73		31		0.26		0.32		0.46		61		1192																				5/30/08		0.04		72		38

		12/28/07		0.075						10/29/07		0.025						5/14/08		0.045		73		25		0.3		0.32		0.46		60		1184																				5/31/08		0.025		72		39

		12/31/07		0.08						10/30/07		0.03						5/15/08		0.035		73		39		0.3		0.32		0.46		60		1196																				6/2/08		0.025		74		27

		1/2/08		0.09						10/31/07		0.03						5/16/08		0.035		73		45		0.3		0.32		0.44		60		1184																				6/3/08		0.02		71		34

		1/3/08		0.075						11/1/07		0.04						5/19/08		0.045		72		41		0.28		0.32		0.44		60		1204																				6/4/08		0.025		69		33

		1/4/08		0.09						11/2/07		0.03						5/20/08		0.045		73		42		0.28		0.32		0.44		62		1196																				6/5/08		0.025		71		39

		1/7/08		0.125						11/5/07		0.025						5/21/08		0.045		70		35		0.28		0.32		0.46		60		1196																				6/6/08		0.025		71		32

		1/8/08		0.08						11/6/07		0.03						5/22/08		0.045		72		30		0.28		0.32		0.42		61		1176																				6/9/08		0.03		72		43

		1/9/08		0.08						11/7/07		0.035						5/23/08		0.045		73		34		0.28		0.32		0.46		61		1172																				6/10/08		0.03		73		33

		1/10/08		0.08						11/8/07		0.05						5/27/08		0.035		73		36		0.28		0.32		0.44		61		1196																				6/11/08		0.025		70		33

		1/11/08		0.08						11/9/07		0.05						5/28/08		0.04		72		37		0.28		0.32		0.44		61		1204																				6/12/08		0.025		71		35

		1/14/08		0.09						11/12/07		0.03						5/29/08		0.04		73		37		0.26		0.32		0.44		61		1200																				6/13/08		0.025		75		32

		1/15/08		0.085						11/13/07		0.05						5/30/08		0.04		72		37		0.28		0.32		0.48		61		1196																				6/16/08		0.025		72		37

		1/16/08		0.09						11/14/07		0.05						6/2/08		0.04		71		30		0.28		0.28		0.44		60		1200																				6/17/08		0.03		72		26

		1/17/08		0.08						11/15/07		0.05						6/3/08		0.035		72		35		0.28		0.32		0.42		61		1196																				6/18/08		0.025		73		33

		1/18/08		0.09						11/16/07		0.05						6/4/08		0.035		70		33		0.28		0.32		0.44		61		1188																				6/19/08		0.025		71		29

		1/21/08		0.04						11/19/07		0.05						6/5/08		0.035		71		37		0.3		0.32		0.44		61		1192																				6/20/08		0.02		73		33

		1/22/08		0.11						11/20/07		0.05						6/6/08		0.035		71		31		0.28		0.32		0.44		61		1188																				6/21/08		0.025		74		27

		1/23/08		0.09						11/21/07		0.05						6/9/08		0.04		72		40		0.32		0.32		0.48		61		1188																				6/23/08		0.02		72		37

		1/24/08		0.09						11/26/07		0.05						6/10/08		0.04		72		31		0.3		0.32		0.44		55		1172																				6/24/08		0.025		73		35

		1/25/08		0.095						11/27/07		0.05						6/11/08		0.04		70		34		0.3		0.32		0.48		55		1196																				6/25/08		0.03		72		36

		1/28/08		0.09						11/28/07		0.05						6/12/08		0.04		72		31		0.3		0.32		0.48		55		1196																				6/26/08		0.03		74		35

		1/29/08		0.09						11/29/07		0.045						6/13/08		0.05		71		36		0.26		0.32		0.44		55		1208																				6/27/08		0.02		71		39

		1/30/08		0.1						11/30/07		0.05						6/16/08		0.05		73		34		0.3		0.32		0.46		55		1204																				6/30/08		0.02		73		38

		1/31/08		0.105						12/3/07		0.05						6/17/08		0.05		73		24		0.28		0.32		0.44		55		1216																				7/1/08		0.055		73		39

		2/1/08		0.09						12/4/07		0.05						6/18/08		0.05		73		31		0.3		0.32		0.44		55		1196																				7/2/08		0.055		73		38

		2/4/08		0.03						12/5/07		0.045						6/19/08		0.05		71		30		0.28		0.32		0.46		55		1196																				7/3/08		0.065		71		39

		2/5/08		0.04						12/6/07		0.05						6/20/08		0.05		73		28		0.28		0.32		0.46		55		1196																				7/7/08		0.055		75		38

		2/6/08		0.025						12/7/07		0.045						6/21/08		0.045		72		30		0.26		0.32		0.46		55		32																				7/8/08		0.05		72		40

		2/7/08		0.02						12/10/07		0.05						6/23/08		0.05		73		39		0.28		0.32		0.44		57		32																				7/9/08		0.06		73		39

		2/8/08		0.04						12/11/07		0.045						6/24/08		0.05		72		34		0.28		0.32		0.42		60		32																				7/10/08		0.06		74		39

		2/9/08		0.05						12/12/07		0.045						6/25/08		0.04		73		36		0.28		0.32		0.44		60		32																				7/11/08		0.06		71		40

		2/11/08		0.02						12/13/07		0.045						6/26/08		0.04		72		34		0.28		0.32		0.44		60		32																				7/12/08		0.06		73		42

		2/12/08		0.035						12/14/07		0.045						6/27/08		0.04		71		38		0.32		0.32		0.44		60		32																				7/14/08		0.06		72		41

		2/13/08		0.025						12/17/07		0.045						6/30/08		0.04		73		37		0.3		0.32		0.44		60		32																				7/15/08		0.06		71		41

		2/14/08		0.025						12/18/07		0.04						7/1/08		0.035		71		38		0.28		0.32		0.44		60		32																				7/16/08		0.065		72		40

		2/15/08		0.03						12/19/07		0.04						7/2/08		0.07		72		38		0.3		0.32		0.46		60		32																				7/17/08		0.05		71		41

		2/19/08		0.03						12/20/07		0.03						7/3/08		0.08		72		38		0.32		0.32		0.48		57		32																				7/18/08		0.065		72		40

		2/20/08		0.05						12/21/07		0.04						7/7/08		0.06		73		40		0.28		0.32		0.44		57		32																				7/19/08		0.06		72		39

		2/21/08		0.03						12/26/07		0.04						7/8/08		0.06		72		38		0.28		0.32		0.42		60		32																				7/21/08		0.06		71		40

		2/22/08		0.03						12/27/07		0.04						7/9/08		0.06		73		39		0.28		0.32		0.42																								7/22/08		0.05		74		36

		2/23/08		0.035						12/28/07		0.04						7/10/08		0.07		72		40		0.32		0.32		0.48		55		1104																				7/23/08		0.07		72		39

		2/24/08		0.035						12/31/07		0.04						7/11/08		0.065		71		39		0.3		0.32		0.48		55		1104																				7/24/08		0.05		72		37

		2/25/08		0.03						1/2/08		0.04						7/12/08		0.08		73		40																														7/25/08		0.06		71		38

		2/26/08		0.035						1/3/08		0.04						7/14/08		0.08		72		40		0.3		0.32		0.48		61		1200																				7/26/08		0.07		71		38

		2/27/08		0.03						1/4/08		0.04						7/15/08		0.09		71		40		0.28		0.32		0.42		61		1200																				7/28/08		0.06		70		41

		2/28/08		0.03						1/7/08		0.025						7/16/08		0.09		72		39		0.28		0.32		0.42		61		1200																				7/29/08		0.06		70		41

		2/29/08		0.03						1/8/08		0.03						7/17/08		0.08		72		39		0.28		0.32		0.44		61		1200																				7/30/08		0.06		71		39

		3/1/08		0.035						1/9/08		0.03						7/18/08		0.09		72		38		0.3		0.32		0.48		61		1200																				7/31/08		0.065		71		40

		3/3/08		0.03						1/10/08		0.03						7/19/08		0.09		73		37																														8/1/08		0.06		73		36

		3/4/08		0.035						1/11/08		0.03						7/21/08		0.09		72		38		0.28		0.32		0.4		61		1200																				8/2/08		0.06		71		40

		3/5/08		0.043						1/14/08		0.025						7/22/08		0.08		73		37		0.24		0.32		0.42		61		1200																				8/4/08		0.06		72		40

		3/6/08		0.043						1/15/08		0.03						7/23/08		0.09		71		38		0.28		0.32		0.44		61		1200																				8/5/08		0.06		73		39

		3/7/08		0.043						1/16/08		0.03						7/24/08		0.09		72		36		0.26		0.32		0.46		61		1200																				8/6/08		0.06		71		41

		3/10/08		0.043						1/17/08		0.03						7/25/08		0.09		72		36		0.24		0.32		0.42		61		1200																				8/7/08		0.06		72		39

		3/11/08		0.042						1/18/08		0.025						7/26/08		0.09		71		37		0.28		0.32		0.46		61		1200																				8/8/08		0.05		72		40

		3/12/08		0.039						1/21/08		0.035						7/28/08		0.09		71		38		0.3		0.32		0.46		61		1200																				8/9/08		0.055		71		40

		3/13/08		0.03						1/22/08		0.03						7/29/08		0.06		70		40		0.3		0.32		0.44																								8/11/08		0.06		71		39

		3/14/08		0.041						1/23/08		0.035						7/30/08		0.07		71		38		0.3		0.32		0.48																								8/12/08		0.065		71		41

		3/17/08		0.047						1/24/08		0.03						7/31/08		0.075		71		38																														8/13/08		0.055		71		41

		3/18/08		0.048						1/25/08		0.035						8/1/08		0.07		72		37		0.3		0.32		0.48																								8/14/08		0.05		71		41

		3/19/08		0.047						1/28/08		0.035						8/2/08		0.07		72		38																														8/15/08		0.05		72		39

		3/20/08		0.042						1/29/08		0.035						8/4/08		0.07		73		37		0.28		0.32		0.44																								8/16/08		0.06		72		40

		3/21/08		0.043						1/30/08		0.025						8/5/08		0.06		73		37		0.28		0.34		0.48																								8/18/08		0.06		72		41

		3/22/08		0.045						1/31/08		0.03						8/6/08		0.07		71		38		0.28		0.32		0.48																								8/19/08		0.06		72		41

		3/24/08		0.043						2/1/08		0.03						8/7/08		0.06		71		38		0.32		0.32		0.48																								8/20/08		0.06		71		40

		3/25/08		0.045						2/4/08		0.035						8/8/08		0.06		72		38		0.26		0.32		0.44																								8/21/08		0.05		73		44

		3/26/08		0.043						2/5/08		0.025						8/9/08		0.06		71		40																														8/22/08		0.05		72		40

		3/27/08		0.04						2/6/08		0.035						8/11/08		0.07		71		38		0.28		0.32		0.44																								8/23/08		0.05		72		41

		3/28/08		0.04						2/7/08		0.025						8/12/08		0.07		71		40		0.28		0.32		0.44																								8/25/08		0.06		71		40

		3/31/08		0.045						2/8/08		0.02						8/13/08		0.065		71		40		0.28		0.3		0.46																								8/26/08		0.06		70		39

		4/1/08		0.045						2/9/08		0.02						8/14/08		0.05		71		39		0.26		0.32		0.42																								8/27/08		0.05		71		40

		4/2/08		0.045						2/14/08		0.035						8/15/08		0.06		71		38		0.26		0.32		0.42																								8/28/08		0.055		71		40

		4/3/08		0.04						2/15/08		0.033						8/16/08		0.06		71		40																														8/29/08		0.055		72		39

		4/4/08		0.045						2/19/08		0.036						8/18/08		0.065		71		41		0.26		0.32		0.42																								9/2/08		0.055		69		32

		4/5/08		0.045						2/20/08		0.037						8/19/08		0.06		72		40		0.28		0.32		0.44																								9/3/08		0.055		72		39

		4/7/08		0.045						2/21/08		0.037						8/20/08		0.06		71		31		0.26		0.32		0.42																								9/4/08		0.055		70		38

		4/8/08		0.04						2/22/08		0.034						8/21/08		0.05		73		42		0.28		0.32		0.48																								9/5/08		0.06		71		36

		4/9/08		0.04						2/25/08		0.044						8/22/08		0.06		71		38		0.24		0.32		0.44																								9/6/08		0.06		71		39

		4/10/08		0.04						2/26/08		0.043						8/23/08		0.06		72		40																														9/8/08		0.06		74		38

		4/11/08		0.045						2/27/08		0.043						8/25/08		0.06		71		40		0.26		0.32		0.46																								9/9/08		0.06		72		40

		4/14/08		0.045						2/28/08		0.044						8/26/08		0.06		70		38		0.26		0.32		0.44																								9/10/08		0.06		72		40

		4/15/08		0.04						2/29/08		0.046						8/27/08		0.05		71		38		0.26		0.32		0.44																								9/11/08		0.06		71		41

		4/16/08		0.04						3/3/08		0.045						8/28/08		0.05		71		38		0.26		0.3		0.44																								9/12/08		0.06		70		40

		4/17/08		0.04						3/4/08		0.044						8/29/08		0.065		72		38		0.28		0.3		0.44																								9/13/08		0.06		70		41

		4/18/08		0.04						3/5/08		0.039						9/2/08		0.06		69		31		0.24		0.32		0.42																								9/15/08		0.06		70		40

		4/19/08		0.05						3/6/08		0.039						9/3/08		0.06		72		40		0.28		0.32		0.44																								9/16/08		0.06		71		40

		4/21/08		0.05						3/7/08		0.038						9/4/08		0.06		70		37		0.26		0.32		0.44																								9/17/08		0.06		70		30

		4/22/08		0.045						3/10/08		0.037						9/5/08		0.06		70		36		0.26		0.32		0.44																								9/18/08		0.06		71		37

		4/23/08		0.04						3/11/08		0.04						9/6/08		0.06		70		38																														9/19/08		0.06		72		43

		4/24/08		0.04						3/12/08		0.036						9/8/08		0.06		72		41		0.24		0.32		0.42																								9/20/08		0.06		72		42

		4/25/08		0.04						3/14/08		0.039						9/9/08		0.06		71		40		0.24		0.32		0.44																								9/22/08		0.06		71		39

		4/30/08		0.04						3/17/08		0.038						9/10/08		0.06		70		41		0.28		0.32		0.46																								9/23/08		0.065		72		37

		5/1/08		0.04						3/18/08		0.038						9/11/08		0.06		70		41		0.26		0.32		0.42																								9/24/08		0.055		70		33

		5/2/08		0.04						3/19/08		0.037						9/12/08		0.06		70		40		0.28		0.32		0.48																								9/25/08		0.06		72		32

		5/3/08		0.045						3/20/08		0.039						9/13/08		0.06		70		40																														9/26/08		0.06		72		43

		5/5/08		0.04						3/21/08		0.038						9/15/08		0.06		69		41		0.3		0.32		0.44																								9/27/08		0.06		70		37

		5/6/08		0.04						3/24/08		0.038						9/16/08		0.06		69		41		0.24		0.3		0.42																								9/29/08		0.06		71		40

		5/7/08		0.045						3/25/08		0.038						9/17/08		0.07		69		38		0.26		0.32		0.46																								9/30/08		0.06		75		33

		5/8/08		0.04						3/26/08		0.039						9/18/08		0.06		70		38		0.26		0.32		0.42

		5/9/08		0.04						3/27/08		0.045						9/19/08		0.06		73		42		0.26		0.32		0.42

		5/10/08		0.04						3/28/08		0.04						9/20/08		0.05		73		41

		5/12/08		0.04						3/31/08		0.04						9/22/08		0.06		71		38		0.24		0.32		0.44

		5/13/08		0.04						4/1/08		0.04						9/23/08		0.065		71		37		0.26		0.32		0.44

		5/14/08		0.04						4/2/08		0.04						9/24/08		0.055		71		32		0.26		0.32		0.42

		5/15/08		0.04						4/3/08		0.035						9/25/08		0.06		71		32		0.28		0.32		0.48

		5/16/08		0.04						4/4/08		0.04						9/26/08		0.055		73		41		0.24		0.32		0.44

		5/19/08		0.04						4/5/08		0.035						9/27/08		0.06		71		35

		5/20/08		0.04						4/7/08		0.04						9/29/08		0.06		70		40		0.26		0.32		0.44

		5/21/08		0.04						4/8/08		0.04						9/30/08		0.05		71		36		0.24		0.32		0.44

		5/22/08		0.04						4/9/08		0.035						10/1/08								0.24		0.32		0.44

		5/23/08		0.04						4/10/08		0.04						10/2/08								0.24		0.32		0.44

		5/27/08		0.04						4/11/08		0.04

		5/28/08		0.04						4/14/08		0.04

		5/29/08		0.05						4/15/08		0.04

		5/30/08		0.04						4/16/08		0.04

		5/31/08		0.045						4/17/08		0.04

		6/2/08		0.04						4/18/08		0.035

		6/3/08		0.04						4/19/08		0.05

		6/4/08		0.04						4/21/08		0.05

		6/5/08		0.04						4/22/08		0.04

		6/6/08		0.04						4/23/08		0.04

		6/9/08		0.04						4/24/08		0.04

		6/10/08		0.04						4/25/08		0.04

		6/11/08		0.04						4/30/08		0.04

		6/12/08		0.04						5/1/08		0.04

		6/13/08		0.04						5/2/08		0.04

		6/16/08		0.04						5/3/08		0.04

		6/17/08		0.04						5/5/08		0.04

		6/18/08		0.04						5/6/08		0.04

		6/19/08		0.04						5/7/08		0.04

		6/20/08		0.04						5/8/08		0.04

		6/21/08		0.035						5/9/08		0.04

		6/23/08		0.035						5/10/08		0.04

		6/24/08		0.04						5/12/08		0.04

		6/25/08		0.035						5/13/08		0.04

		6/26/08		0.035						5/14/08		0.04

		6/27/08		0.035						5/15/08		0.04

		6/30/08		0.035						5/16/08		0.04

		7/1/08		0.03						5/19/08		0.04

		7/2/08		0.03						5/20/08		0.04

		7/3/08		0.035						5/21/08		0.04

		7/7/08		0.03						5/22/08		0.04

		7/8/08		0.03						5/23/08		0.04

		7/9/08		0.035						5/27/08		0.04

		7/10/08		0.035						5/28/08		0.04

		7/11/08		0.035						5/29/08		0.04

		7/12/08		0.03						5/30/08		0.04

		7/14/08		0.025						6/2/08		0.04

		7/15/08		0.03						6/3/08		0.035

		7/16/08		0.03						6/4/08		0.035

		7/17/08		0.03						6/5/08		0.035

		7/18/08		0.04						6/6/08		0.035

		7/19/08		0.03						6/9/08		0.035

		7/21/08		0.03						6/10/08		0.035

		7/22/08		0.03						6/11/08		0.035

		7/23/08		0.02						6/12/08		0.035

		7/24/08		0.025						6/13/08		0.04

		7/25/08		0.01						6/16/08		0.035

		7/26/08		0.01						6/17/08		0.045

		7/28/08		0.01						6/18/08		0.045

		7/29/08		0.03						6/19/08		0.045

		7/30/08		0.01						6/20/08		0.035

		7/31/08		0.015						6/21/08		0.035

		8/1/08		0.025						6/23/08		0.035

		8/2/08		0.03						6/24/08		0.045

		8/4/08		0.03						6/25/08		0.035

		8/5/08		0.03						6/26/08		0.035

		8/6/08		0.04						6/27/08		0.035

		8/7/08		0.035						6/30/08		0.035

		8/8/08		0.03						7/1/08		0.04

		8/9/08		0.03						7/2/08		0.04

		8/11/08		0.035						7/3/08		0.04

		8/12/08		0.035						7/7/08		0.04

		8/13/08		0.035						7/8/08		0.04

		8/14/08		0.03						7/9/08		0.04

		8/15/08		0.03						7/10/08		0.04

		8/16/08		0.03						7/11/08		0.04

		8/18/08		0.03						7/12/08		0.04

		8/19/08		0.04						7/14/08		0.04

		8/20/08		0.03						7/15/08		0.04

		8/21/08		0.03						7/16/08		0.04

		8/22/08		0.03						7/17/08		0.04

		8/23/08		0.03						7/18/08		0.04

		8/25/08		0.03						7/19/08		0.04

		8/26/08		0.03						7/21/08		0.04

		8/27/08		0.03						7/22/08		0.04

		8/28/08		0.03						7/23/08		0.04

		8/29/08		0.03						7/24/08		0.04

		9/2/08		0.03						7/25/08		0.04

		9/3/08		0.03						7/26/08		0.04

		9/4/08		0.03						7/28/08		0.04

		9/5/08		0.03						7/29/08		0.04

		9/6/08		0.03						7/30/08		0.04

		9/8/08		0.03						7/31/08		0.04

		9/9/08		0.03						8/1/08		0.045

		9/10/08		0.03						8/2/08		0.04

		9/11/08		0.03						8/4/08		0.04

		9/12/08		0.03						8/5/08		0.04

		9/13/08		0.03						8/6/08		0.05

		9/15/08		0.035						8/7/08		0.04

		9/16/08		0.03						8/8/08		0.04

		9/17/08		0.03						8/9/08		0.04

		9/18/08		0.03						8/11/08		0.04

		9/19/08		0.03						8/12/08		0.04

		9/20/08		0.03						8/13/08		0.04

		9/22/08		0.03						8/14/08		0.04

		9/23/08		0.03						8/15/08		0.04

		9/24/08		0.025						8/16/08		0.04

		9/25/08		0.03						8/18/08		0.04

		9/26/08		0.03						8/19/08		0.04

		9/27/08		0.03						8/20/08		0.04

		9/29/08		0.03						8/21/08		0.04

		9/30/08		0.03						8/22/08		0.04

		10/1/08		0.03						8/23/08		0.04

		10/2/08		0.03						8/25/08		0.04

		10/3/08		0.03						8/26/08		0.04

		10/4/08		0.03						8/27/08		0.04

		10/6/08		0.03						8/28/08		0.04

		10/7/08		0.04						8/29/08		0.04

		10/8/08		0.03						9/2/08		0.04

		10/9/08		0.03						9/3/08		0.04

		10/10/08		0.03						9/4/08		0.04

		10/11/08		0.03						9/5/08		0.04

		10/13/08		0.03						9/6/08		0.04

		10/14/08		0.03						9/8/08		0.04

		10/15/08		0.03						9/9/08		0.04

		10/16/08		0.04						9/10/08		0.04

		10/17/08		0.03						9/11/08		0.04

		10/18/08		0.03						9/12/08		0.04

		10/20/08		0.03						9/13/08		0.04

		10/21/08		0.03						9/15/08		0.04

		10/22/08		0.03						9/16/08		0.04

		10/23/08		0.03						9/17/08		0.04

		10/24/08		0.03						9/18/08		0.04

		10/25/08		0.03						9/19/08		0.04

		10/27/08		0.03						9/20/08		0.04

		10/28/08		0.03						9/22/08		0.04

		10/29/08		0.03						9/23/08		0.045

		10/30/08		0.03						9/24/08		0.045

		10/31/08		0.03						9/25/08		0.045

		11/3/08		0.03						9/26/08		0.04

		11/4/08		0.03						9/27/08		0.04

		11/5/08		0.03						9/29/08		0.04

		11/6/08		0.04						9/30/08		0.04

		11/7/08		0.035						10/1/08		0.04

		11/8/08		0.04						10/2/08		0.04

		11/10/08		0.04						10/3/08		0.04

		11/11/08		0.04						10/4/08		0.04

		11/12/08		0.04						10/6/08		0.04

		11/13/08		0.04						10/7/08		0.05

		11/14/08		0.04						10/8/08		0.045

		11/15/08		0.035						10/9/08		0.04

		11/17/08		0.04						10/10/08		0.04

		11/18/08		0.05						10/11/08		0.04

		11/19/08		0.04						10/13/08		0.045

		11/20/08		0.04						10/14/08		0.04

		11/21/08		0.035						10/15/08		0.045

		11/22/08		0.03						10/16/08		0.04

		11/24/08		0.03						10/17/08		0.04

		11/25/08		0.03						10/18/08		0.04

		11/26/08		0.03						10/20/08		0.04

		12/1/08		0.03						10/21/08		0.04

		12/2/08		0.04						10/22/08		0.04

		12/3/08		0.03						10/23/08		0.04

		12/4/08		0.03						10/24/08		0.04

		12/5/08		0.03						10/25/08		0.04

		12/6/08		0.03						10/27/08		0.04

		12/8/08		0.03						10/28/08		0.04

		12/9/08		0.04						10/29/08		0.04

		12/10/08		0.03						10/30/08		0.04

		12/11/08		0.03						10/31/08		0.04

		12/12/08		0.035						11/3/08		0.04

		12/13/08		0.03						11/4/08		0.04

		12/15/08		0.04						11/5/08		0.05

		12/16/08		0.03						11/6/08		0.04

		12/17/08		0.03						11/7/08		0.04

		12/18/08		0.03						11/8/08		0.045

		12/19/08		0.04						11/10/08		0.04

		1/12/09		0.035						11/11/08		0.04

		1/13/09		0.02						11/12/08		0.04

		1/14/09		0.035						11/13/08		0.04

										11/14/08		0.04

										11/15/08		0.04

										11/17/08		0.04

										11/18/08		0.04

										11/19/08		0.04

										11/20/08		0.045

										11/21/08		0.045

										11/22/08		0.04

										11/24/08		0.04

										11/25/08		0.04

										11/26/08		0.04

										12/1/08		0.04





CER Pressure

		



Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)

R&D Bio-Safety Cabinet South (left axis)

Date

Diff. Pressure (Water Column In.)

Mfg Bio-Safety Cabinet South CFM

Figure 7.  CER2 Bio-Safety Cabinet Differential Pressure Daily Run Chart



Conf-Rel

		



Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

R&D Bio-Safety Cabinet South (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)

Date

Diff. Pressure (Water Column In.)

Mfg Bio-Safety Cabinet (cfm)

Figure 8.  Bio-Safety Cabinet Differential Pressure - Monthly Average



Temp-Humid

		



CER1

CER Change Room

CER2

CER3

CER Alert Level

CER Action Level

Date

Diff. Pressure (Water Column In.)

Figure 5.  CER Differential Pressure Daily Run Chart



Sheet1

		



CER1

CER Change Room

CER 2

CER 3

CER Alert Level

CER Action Level

Date

Diff. Pressure (Water Column In.)

Figure 6.  CER Differential Pressure - Monthly Average



		TO:		DCN 0273 File

		FROM:		Andy Pearson

		DATE:		3/3/07

		RE:		Confidence and Reliability Levels for CER Monitoring

		The table below shows 95/95, and 95/99 confidence/reliability levels for  CER and Change Room

		monitoring carried out from Feb 06 to Feb 07.

		Recommended action and alert levels correspond to worst case 95/95 (alert) and 95/99 (action) values.

						95/95 Limit		Recommended Alert Level		95/99 Limit		95/99 Limit		Recommended Action Level

		Airstrips (utl)		CER1		17		35		21		21		45

				CER2		15				20		20

				CER3		34				43		43

		Contact Plates (utl)		CER1		5		6		6		6		7

				CER2		4				5		5

				CER3		6				7		7

		0.5um Particle Counts (utl)		CER1		1092		3800		1324		1324		4500

				CER3		3797				4549		4549

				CER2		1232		1250		1495		1495		1500

		5.0um Particle Counts (utl)		CER1		159		410		200		200		500

				CER3		410				497		497

				CER2		91		90		107		107		105

		Pressure Differential (ltl)		CER1		0.011		0.030		0.003		0.003		0.005

				CER1/2 Chg Rm		0.021				0.013		0.013

				CER2		-0.021				-0.045		-0.045

				CER3		0.040				0.035		0.035

		Andy Pearson

		Sr.Quality Engineer





		CER2								CER1								CER3								QA

		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 2 Temperature(°F)		CER 2 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 1 Temperature(°F)		CER 1 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 3 Temperature(°F)		CER 3 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		QA Temperature(°F)		QA Humidity(%)

		29-Aug-07		16:07:10		75.81		46.5		29-Aug-07		16:06:20		76.4		48		29-Aug-07		16:07:53		75.81		74		9-Oct-07		16:25:59		78.2		33

		29-Aug-07		18:07:10		74.01		40.5		29-Aug-07		18:06:20		70.41		41.5		29-Aug-07		18:07:53		74.6		41.5		9-Oct-07		18:25:59		75.81		35.5

		29-Aug-07		20:07:10		74.6		40.5		29-Aug-07		20:06:20		71.6		43.5		29-Aug-07		20:07:53		73.4		43		9-Oct-07		20:25:59		75.2		34.5

		29-Aug-07		22:07:10		75.81		40.5		29-Aug-07		22:06:20		71.6		46.5		29-Aug-07		22:07:53		74.6		42		9-Oct-07		22:25:59		74.6		35

		30-Aug-07		0:07:10		75.81		40.5		30-Aug-07		0:06:20		71.6		47.5		30-Aug-07		0:07:53		75.2		41.5		10-Oct-07		0:25:59		73.4		36

		30-Aug-07		2:07:10		75.81		41		30-Aug-07		2:06:20		71		49		30-Aug-07		2:07:53		75.81		41.5		10-Oct-07		2:25:59		72.8		37

		30-Aug-07		4:07:10		75.2		42.5		30-Aug-07		4:06:20		71		51		30-Aug-07		4:07:53		75.2		41.5		10-Oct-07		4:25:59		72.21		38

		30-Aug-07		6:07:10		75.81		41		30-Aug-07		6:06:20		71.6		46.5		30-Aug-07		6:07:53		75.2		42		10-Oct-07		6:25:59		72.21		39

		30-Aug-07		8:07:10		75.81		45.5		30-Aug-07		8:06:20		72.21		55.5		30-Aug-07		8:07:53		75.2		44		10-Oct-07		8:25:59		71.6		41.5

		30-Aug-07		10:07:10		74.6		43.5		30-Aug-07		10:06:20		72.21		41.5		30-Aug-07		10:07:53		74.6		45		10-Oct-07		10:25:59		72.8		42.5

		30-Aug-07		12:07:10		74.6		43.5		30-Aug-07		12:06:20		71.6		46		30-Aug-07		12:07:53		72.8		45.5		10-Oct-07		12:25:59		74.01		42.5

		30-Aug-07		14:07:10		74.6		43		30-Aug-07		14:06:20		72.21		43		30-Aug-07		14:07:53		72.21		44.5		10-Oct-07		14:25:59		75.2		43

		30-Aug-07		16:07:10		75.2		43.5		30-Aug-07		16:06:20		72.21		43.5		30-Aug-07		16:07:53		72.8		44.5		10-Oct-07		16:25:59		75.2		42

		30-Aug-07		18:07:10		75.2		45		30-Aug-07		18:06:20		70.41		49.5		30-Aug-07		18:07:53		71.6		46		10-Oct-07		18:25:59		75.2		41

		30-Aug-07		20:07:10		75.2		45.5		30-Aug-07		20:06:20		71.6		52		30-Aug-07		20:07:53		75.81		45		10-Oct-07		20:25:59		74.01		42.5

		30-Aug-07		22:07:10		76.4		45		30-Aug-07		22:06:20		71		53.5		30-Aug-07		22:07:53		75.2		45		10-Oct-07		22:25:59		73.4		43.5

		31-Aug-07		0:07:10		76.4		44.5		31-Aug-07		0:06:20		71		53.5		31-Aug-07		0:07:53		75.2		44.5		11-Oct-07		0:25:59		72.8		44.5

		31-Aug-07		2:07:10		75.81		44.5		31-Aug-07		2:06:20		71.6		53		31-Aug-07		2:07:53		75.2		45.5		11-Oct-07		2:25:59		72.21		45

		31-Aug-07		4:07:10		75.81		45		31-Aug-07		4:06:20		71.6		53		31-Aug-07		4:07:53		72.8		41.5		11-Oct-07		4:25:59		71.6		45.5

		31-Aug-07		6:07:10		75.81		45.5		31-Aug-07		6:06:20		72.21		54		31-Aug-07		6:07:53		71		54.5		11-Oct-07		6:25:59		72.21		45

		31-Aug-07		8:07:10		75.2		44		31-Aug-07		8:06:20		72.21		43.5		31-Aug-07		8:07:53		71.6		50.5		11-Oct-07		8:25:59		71.6		46.5

		31-Aug-07		10:07:10		74.6		45.5		31-Aug-07		10:06:20		72.21		49.5		31-Aug-07		10:07:53		72.21		44.5		11-Oct-07		10:25:59		72.8		48.5

		31-Aug-07		12:07:10		74.6		49.5		31-Aug-07		12:06:20		71.6		60.5		31-Aug-07		12:07:53		72.21		45		11-Oct-07		12:25:59		74.6		44.5

		31-Aug-07		14:07:10		74.6		45.5		31-Aug-07		14:06:20		71.6		44		31-Aug-07		14:07:53		72.8		47		11-Oct-07		14:25:59		75.81		42.5

		31-Aug-07		16:07:10		74.6		48		31-Aug-07		16:06:20		71.6		56.5		31-Aug-07		16:07:53		72.8		43.5		11-Oct-07		16:25:59		76.4		42.5

		31-Aug-07		18:07:10		75.2		46.5		31-Aug-07		18:06:20		70.41		54.5		31-Aug-07		18:07:53		71		50		11-Oct-07		18:25:59		76.4		41

		31-Aug-07		20:07:10		75.2		46		31-Aug-07		20:06:20		71.6		53		31-Aug-07		20:07:53		74.6		50		11-Oct-07		20:25:59		74.6		41.5

		31-Aug-07		22:07:10		76.4		44		31-Aug-07		22:06:20		71.6		48.5		31-Aug-07		22:07:53		75.2		47		11-Oct-07		22:25:59		74.6		41

		1-Sep-07		0:07:10		76.4		42.5		1-Sep-07		0:06:20		71.6		46.5		1-Sep-07		0:07:53		75.2		45.5		12-Oct-07		0:25:59		73.4		41

		1-Sep-07		2:07:10		76.4		44		1-Sep-07		2:06:20		71.6		53		1-Sep-07		2:07:53		74.6		45.5		12-Oct-07		2:25:59		71.6		41

		1-Sep-07		4:07:10		76.4		44		1-Sep-07		4:06:20		71.6		53		1-Sep-07		4:07:53		72.8		50		12-Oct-07		4:25:59		71		41.5

		1-Sep-07		6:07:10		76.4		45		1-Sep-07		6:06:20		73.4		56.5		1-Sep-07		6:07:53		71.6		45		12-Oct-07		6:25:59		70.41		41.5

		1-Sep-07		8:07:10		75.2		42.5		1-Sep-07		8:06:20		72.21		41		1-Sep-07		8:07:53		71.6		53		12-Oct-07		8:25:59		69.8		41.5

		1-Sep-07		10:07:10		74.6		43.5		1-Sep-07		10:06:20		71.6		42		1-Sep-07		10:07:53		72.21		43.5		12-Oct-07		10:25:59		71.6		44.5

		1-Sep-07		12:07:10		74.6		51.5		1-Sep-07		12:06:20		70.41		64		1-Sep-07		12:07:53		71.6		45.5		12-Oct-07		12:25:59		74.6		43.5

		1-Sep-07		14:07:10		74.6		52		1-Sep-07		14:06:20		70.41		64.5		1-Sep-07		14:07:53		71		50.5		12-Oct-07		14:25:59		75.2		42.5

		1-Sep-07		16:07:10		74.6		46.5		1-Sep-07		16:06:20		70.41		52.5		1-Sep-07		16:07:53		71		57.5		12-Oct-07		16:25:59		75.2		42.5

		1-Sep-07		18:07:10		74.6		45.5		1-Sep-07		18:06:20		70.41		50.5		1-Sep-07		18:07:53		71		58.5		12-Oct-07		18:25:59		74.6		40

		1-Sep-07		20:07:10		74.6		49.5		1-Sep-07		20:06:20		71		56		1-Sep-07		20:07:53		71		55.5		12-Oct-07		20:25:59		74.01		40.5

		1-Sep-07		22:07:10		75.2		47		1-Sep-07		22:06:20		71		56		1-Sep-07		22:07:53		72.21		50.5		12-Oct-07		22:25:59		74.01		40

		2-Sep-07		0:07:10		75.2		45		2-Sep-07		0:06:20		71.6		52.5		2-Sep-07		0:07:53		72.21		50		13-Oct-07		0:25:59		72.8		40.5

		2-Sep-07		2:07:10		75.2		44.5		2-Sep-07		2:06:20		71		51		2-Sep-07		2:07:53		71.6		50		13-Oct-07		2:25:59		71.6		41

		2-Sep-07		4:07:10		74.6		44		2-Sep-07		4:06:20		70.41		51.5		2-Sep-07		4:07:53		70.41		49.5		13-Oct-07		4:25:59		71		42.5

		2-Sep-07		6:07:10		74.01		41.5		2-Sep-07		6:06:20		71		45.5		2-Sep-07		6:07:53		69.2		48.5		13-Oct-07		6:25:59		71.6		43

		2-Sep-07		8:07:10		73.4		44		2-Sep-07		8:06:20		69.8		51		2-Sep-07		8:07:53		69.2		51		13-Oct-07		8:25:59		71		46

		2-Sep-07		10:07:10		74.01		48.5		2-Sep-07		10:06:20		70.41		57.5		2-Sep-07		10:07:53		71		48.5		13-Oct-07		10:25:59		72.21		47.5

		2-Sep-07		12:07:10		74.6		49.5		2-Sep-07		12:06:20		70.41		59.5		2-Sep-07		12:07:53		71		53		13-Oct-07		12:25:59		72.8		47

		2-Sep-07		14:07:10		75.81		49.5		2-Sep-07		14:06:20		70.41		60.5		2-Sep-07		14:07:53		71		60		13-Oct-07		14:25:59		72.21		47.5

		2-Sep-07		16:07:10		76.4		43.5		2-Sep-07		16:06:20		70.41		47.5		2-Sep-07		16:07:53		71		46.5		13-Oct-07		16:25:59		74.01		47

		2-Sep-07		18:07:10		76.4		46.5		2-Sep-07		18:06:20		69.8		55.5		2-Sep-07		18:07:53		71		58		13-Oct-07		18:25:59		74.6		44.5

		2-Sep-07		20:07:10		77		44		2-Sep-07		20:06:20		71		52.5		2-Sep-07		20:07:53		74.01		47		13-Oct-07		20:25:59		72.8		45.5

		2-Sep-07		22:07:10		77		41.5		2-Sep-07		22:06:20		71.6		51		2-Sep-07		22:07:53		74.6		44.5		13-Oct-07		22:25:59		71.6		45

		3-Sep-07		0:07:10		76.4		41		3-Sep-07		0:06:20		71		50.5		3-Sep-07		0:07:53		74.01		44.5		14-Oct-07		0:25:59		71		45

		3-Sep-07		2:07:10		75.81		40		3-Sep-07		2:06:20		71		44		3-Sep-07		2:07:53		72.21		45.5		14-Oct-07		2:25:59		69.8		43.5

		3-Sep-07		4:07:10		75.2		39		3-Sep-07		4:06:20		71		41.5		3-Sep-07		4:07:53		71		46.5		14-Oct-07		4:25:59		69.2		43

		3-Sep-07		6:07:10		75.2		40		3-Sep-07		6:06:20		71.6		46		3-Sep-07		6:07:53		69.2		47.5		14-Oct-07		6:25:59		69.2		42.5

		3-Sep-07		8:07:10		74.01		42		3-Sep-07		8:06:20		69.8		49		3-Sep-07		8:07:53		68.61		49.5		14-Oct-07		8:25:59		69.2		41

		3-Sep-07		10:07:10		74.01		43		3-Sep-07		10:06:20		70.41		48		3-Sep-07		10:07:53		70.41		52		14-Oct-07		10:25:59		71		44

		3-Sep-07		12:07:10		74.6		41.5		3-Sep-07		12:06:20		70.41		43.5		3-Sep-07		12:07:53		71		43.5		14-Oct-07		12:25:59		72.21		45

		3-Sep-07		14:07:10		75.2		43		3-Sep-07		14:06:20		70.41		47		3-Sep-07		14:07:53		71.6		52		14-Oct-07		14:25:59		74.01		44.5

		3-Sep-07		16:07:10		75.81		44.5		3-Sep-07		16:06:20		69.8		49.5		3-Sep-07		16:07:53		71.6		52		14-Oct-07		16:25:59		75.2		44.5

		3-Sep-07		18:07:10		76.4		40.5		3-Sep-07		18:06:20		70.41		47		3-Sep-07		18:07:53		71		45		14-Oct-07		18:25:59		75.81		44

		3-Sep-07		20:07:10		77.61		40		3-Sep-07		20:06:20		71.6		45.5		3-Sep-07		20:07:53		75.81		42		14-Oct-07		20:25:59		74.6		44.5

		3-Sep-07		22:07:10		77		41		3-Sep-07		22:06:20		71.6		50.5		3-Sep-07		22:07:53		74.6		43.5		14-Oct-07		22:25:59		73.4		45

		4-Sep-07		0:07:10		76.4		40.5		4-Sep-07		0:06:20		71		50		4-Sep-07		0:07:53		74.6		43.5		15-Oct-07		0:25:59		72.8		45.5

		4-Sep-07		2:07:10		75.81		40		4-Sep-07		2:06:20		71		49.5		4-Sep-07		2:07:53		72.8		44		15-Oct-07		2:25:59		72.21		46

		4-Sep-07		4:07:10		75.81		39.5		4-Sep-07		4:06:20		71.6		47		4-Sep-07		4:07:53		71.6		45		15-Oct-07		4:25:59		71.6		46

		4-Sep-07		6:07:10		74.6		40		4-Sep-07		6:06:20		71		47.5		4-Sep-07		6:07:53		69.8		46.5		15-Oct-07		6:25:59		71		46.5

		4-Sep-07		8:07:10		74.01		39.5		4-Sep-07		8:06:20		70.41		42		4-Sep-07		8:07:53		69.8		48.5		15-Oct-07		8:25:59		70.41		47

		4-Sep-07		10:07:10		74.01		45.5		4-Sep-07		10:06:20		69.8		53.5		4-Sep-07		10:07:53		71		52		15-Oct-07		10:25:59		69.8		47.5

		4-Sep-07		12:07:10		74.01		48		4-Sep-07		12:06:20		69.8		55		4-Sep-07		12:07:53		71		45.5		15-Oct-07		12:25:59		70.41		48.5

		4-Sep-07		14:07:10		74.01		49		4-Sep-07		14:06:20		70.41		52		4-Sep-07		14:07:53		71		58.5		15-Oct-07		14:25:59		71.6		49

		4-Sep-07		16:07:10		74.6		47.5		4-Sep-07		16:06:20		70.41		50		4-Sep-07		16:07:53		71		49		15-Oct-07		16:25:59		73.4		48

		4-Sep-07		18:07:10		74.6		47.5		4-Sep-07		18:06:20		70.41		50		4-Sep-07		18:07:53		71		49.5		15-Oct-07		18:25:59		74.6		45.5

		4-Sep-07		20:07:10		75.2		50		4-Sep-07		20:06:20		71		58.5		4-Sep-07		20:07:53		71.6		55.5		15-Oct-07		20:25:59		72.8		46

		4-Sep-07		22:07:10		75.81		47.5		4-Sep-07		22:06:20		71.6		56		4-Sep-07		22:07:53		74.01		50		15-Oct-07		22:25:59		71.6		46

		5-Sep-07		0:07:10		75.81		46.5		5-Sep-07		0:06:20		71		56.5		5-Sep-07		0:07:53		74.01		49.5		16-Oct-07		0:25:59		71		46

		5-Sep-07		2:07:10		75.81		44.5		5-Sep-07		2:06:20		71		47.5		5-Sep-07		2:07:53		72.8		50.5		16-Oct-07		2:25:59		70.41		46.5

		5-Sep-07		4:07:10		75.2		45.5		5-Sep-07		4:06:20		71		55		5-Sep-07		4:07:53		71.6		49		16-Oct-07		4:25:59		69.8		46

		5-Sep-07		6:07:10		75.2		47		5-Sep-07		6:06:20		71.6		55		5-Sep-07		6:07:53		70.41		48		16-Oct-07		6:25:59		70.41		46.5

		5-Sep-07		8:07:10		75.2		45		5-Sep-07		8:06:20		72.21		45.5		5-Sep-07		8:07:53		71		53		16-Oct-07		8:25:59		69.8		47.5

		5-Sep-07		10:07:10		74.6		51.5		5-Sep-07		10:06:20		72.21		55		5-Sep-07		10:07:53		72.8		46.5		16-Oct-07		10:25:59		71		49.5

		5-Sep-07		12:07:10		74.01		50.5		5-Sep-07		12:06:20		71		56		5-Sep-07		12:07:53		72.21		57.5		16-Oct-07		12:25:59		72.21		52

		5-Sep-07		14:07:10		74.01		48		5-Sep-07		14:06:20		71.6		54.5		5-Sep-07		14:07:53		72.21		54		16-Oct-07		14:25:59		73.4		52.5

		5-Sep-07		16:07:10		74.01		49		5-Sep-07		16:06:20		71		54		5-Sep-07		16:07:53		72.21		51		16-Oct-07		16:25:59		75.2		47.5

		5-Sep-07		18:07:10		74.6		49		5-Sep-07		18:06:20		70.41		60		5-Sep-07		18:07:53		71.6		48.5		16-Oct-07		18:25:59		75.81		47.5

		5-Sep-07		20:07:10		74.6		48		5-Sep-07		20:06:20		71.6		55		5-Sep-07		20:07:53		71		58		16-Oct-07		20:25:59		74.01		48.5

		5-Sep-07		22:07:10		75.81		46.5		5-Sep-07		22:06:20		71		55.5		5-Sep-07		22:07:53		75.2		47		16-Oct-07		22:25:59		73.4		49

		6-Sep-07		0:07:10		75.81		43.5		6-Sep-07		0:06:20		71.6		50.5		6-Sep-07		0:07:53		74.6		47		17-Oct-07		0:25:59		72.21		49

		6-Sep-07		2:07:10		75.2		44.5		6-Sep-07		2:06:20		71		52.5		6-Sep-07		2:07:53		73.4		47		17-Oct-07		2:25:59		71		48

		6-Sep-07		4:07:10		75.2		43.5		6-Sep-07		4:06:20		71.6		51		6-Sep-07		4:07:53		72.21		48.5		17-Oct-07		4:25:59		70.41		47.5

		6-Sep-07		6:07:10		75.2		42.5		6-Sep-07		6:06:20		71.6		48.5		6-Sep-07		6:07:53		71		50.5		17-Oct-07		6:25:59		69.8		46

		6-Sep-07		8:07:10		75.2		45.5		6-Sep-07		8:06:20		72.21		52		6-Sep-07		8:07:53		71.6		48.5		17-Oct-07		8:25:59		69.2		46.5

		6-Sep-07		10:07:10		75.2		43.5		6-Sep-07		10:06:20		72.21		46		6-Sep-07		10:07:53		72.21		49.5		17-Oct-07		10:25:59		70.41		49

		6-Sep-07		12:07:10		74.6		41.5		6-Sep-07		12:06:20		71.6		42.5		6-Sep-07		12:07:53		72.21		52		17-Oct-07		12:25:59		71.6		51.5

		6-Sep-07		14:07:10		74.01		40		6-Sep-07		14:06:20		71.6		40.5		6-Sep-07		14:07:53		72.21		42		17-Oct-07		14:25:59		72.21		53

		6-Sep-07		16:07:10		74.6		40		6-Sep-07		16:06:20		71.6		43		6-Sep-07		16:07:53		72.21		40		17-Oct-07		16:25:59		72.8		54

		6-Sep-07		18:07:10		74.6		38		6-Sep-07		18:06:20		69.8		42		6-Sep-07		18:07:53		72.21		37.5		17-Oct-07		18:25:59		74.01		50.5

		6-Sep-07		20:07:10		75.2		38		6-Sep-07		20:06:20		71.6		43		6-Sep-07		20:07:53		75.2		39.5		17-Oct-07		20:25:59		72.21		48.5

		6-Sep-07		22:07:10		75.81		38.5		6-Sep-07		22:06:20		71.6		45.5		6-Sep-07		22:07:53		75.2		39.5		17-Oct-07		22:25:59		71		48

		7-Sep-07		0:07:10		75.81		39		7-Sep-07		0:06:20		71.6		46.5		7-Sep-07		0:07:53		75.2		39.5		18-Oct-07		0:25:59		70.41		47

		7-Sep-07		2:07:10		75.81		39		7-Sep-07		2:06:20		71.6		46		7-Sep-07		2:07:53		74.01		41		18-Oct-07		2:25:59		69.2		45.5

		7-Sep-07		4:07:10		75.2		39		7-Sep-07		4:06:20		71		46		7-Sep-07		4:07:53		72.21		37		18-Oct-07		4:25:59		68.61		45

		7-Sep-07		6:07:10		75.81		38		7-Sep-07		6:06:20		71.6		44		7-Sep-07		6:07:53		71		45.5		18-Oct-07		6:25:59		69.2		46

		7-Sep-07		8:07:10		75.81		41		7-Sep-07		8:06:20		71.6		50		7-Sep-07		8:07:53		71.6		39.5		18-Oct-07		8:25:59		69.2		47

		7-Sep-07		10:07:10		75.2		38.5		7-Sep-07		10:06:20		71.6		40.5		7-Sep-07		10:07:53		72.21		40		18-Oct-07		10:25:59		70.41		50

		7-Sep-07		12:07:10		74.6		40		7-Sep-07		12:06:20		71		42.5		7-Sep-07		12:07:53		72.21		51.5		18-Oct-07		12:25:59		72.8		48.5

		7-Sep-07		14:07:10		74.6		43		7-Sep-07		14:06:20		71.6		42		7-Sep-07		14:07:53		71.6		42.5		18-Oct-07		14:25:59		74.6		45

		7-Sep-07		16:07:10		75.81		46		7-Sep-07		16:06:20		71		61		7-Sep-07		16:07:53		71.6		44.5		18-Oct-07		16:25:59		75.81		43

		7-Sep-07		18:07:10		75.2		45.5		7-Sep-07		18:06:20		71		48		7-Sep-07		18:07:53		71		53.5		18-Oct-07		18:25:59		75.81		43

		7-Sep-07		20:07:10		75.81		49		7-Sep-07		20:06:20		71.6		57		7-Sep-07		20:07:53		71.6		55		18-Oct-07		20:25:59		74.6		43.5

		7-Sep-07		22:07:10		75.81		48.5		7-Sep-07		22:06:20		71.6		58		7-Sep-07		22:07:53		72.8		52		18-Oct-07		22:25:59		73.4		44

		8-Sep-07		0:07:10		75.2		47.5		8-Sep-07		0:06:20		71		56.5		8-Sep-07		0:07:53		72.8		51		19-Oct-07		0:25:59		72.21		44.5

		8-Sep-07		2:07:10		75.2		47		8-Sep-07		2:06:20		71.6		55		8-Sep-07		2:07:53		72.21		51.5		19-Oct-07		2:25:59		71		44.5

		8-Sep-07		4:07:10		75.2		47		8-Sep-07		4:06:20		71		55.5		8-Sep-07		4:07:53		71.6		51		19-Oct-07		4:25:59		70.41		45

		8-Sep-07		6:07:10		75.81		47		8-Sep-07		6:06:20		71.6		54.5		8-Sep-07		6:07:53		71		55		19-Oct-07		6:25:59		70.41		45.5

		8-Sep-07		8:07:10		75.2		47.5		8-Sep-07		8:06:20		72.21		56		8-Sep-07		8:07:53		71.6		57		19-Oct-07		8:25:59		70.41		46.5

		8-Sep-07		10:07:10		74.6		44.5		8-Sep-07		10:06:20		72.21		45		8-Sep-07		10:07:53		72.21		46.5		19-Oct-07		10:25:59		71.6		47.5

		8-Sep-07		12:07:10		74.6		50.5		8-Sep-07		12:06:20		71		57		8-Sep-07		12:07:53		72.21		45		19-Oct-07		12:25:59		73.4		46

		8-Sep-07		14:07:10		74.01		46		8-Sep-07		14:06:20		72.21		46		8-Sep-07		14:07:53		71.6		46.5		19-Oct-07		14:25:59		75.2		45.5

		8-Sep-07		16:07:10		74.01		53		8-Sep-07		16:06:20		71		67		8-Sep-07		16:07:53		71.6		50.5		19-Oct-07		16:25:59		74.6		49

		8-Sep-07		18:07:10		74.01		53		8-Sep-07		18:06:20		70.41		63		8-Sep-07		18:07:53		71		53.5		19-Oct-07		18:25:59		74.6		50.5

		8-Sep-07		20:07:10		74.6		51		8-Sep-07		20:06:20		71		58		8-Sep-07		20:07:53		70.41		57		19-Oct-07		20:25:59		74.01		51.5

		8-Sep-07		22:07:10		74.6		48		8-Sep-07		22:06:20		71		55		8-Sep-07		22:07:53		70.41		54		19-Oct-07		22:25:59		74.01		51

		9-Sep-07		0:07:10		74.6		45		9-Sep-07		0:06:20		71		46		9-Sep-07		0:07:53		69.8		53		20-Oct-07		0:25:59		73.4		51.5

		9-Sep-07		2:07:10		74.01		45.5		9-Sep-07		2:06:20		71		52.5		9-Sep-07		2:07:53		69.2		52.5		20-Oct-07		2:25:59		72.8		52.5

		9-Sep-07		4:07:10		74.01		46.5		9-Sep-07		4:06:20		71		53.5		9-Sep-07		4:07:53		69.2		55		20-Oct-07		4:25:59		72.8		53

		9-Sep-07		6:07:10		74.01		48.5		9-Sep-07		6:06:20		71.6		56		9-Sep-07		6:07:53		68.61		56		20-Oct-07		6:25:59		72.8		54

		9-Sep-07		8:07:10		74.01		46		9-Sep-07		8:06:20		71		50		9-Sep-07		8:07:53		68.61		57		20-Oct-07		8:25:59		72.8		56.5

		9-Sep-07		10:07:10		73.4		50.5		9-Sep-07		10:06:20		70.41		57.5		9-Sep-07		10:07:53		68.61		58		20-Oct-07		10:25:59		74.01		57.5

		9-Sep-07		12:07:10		73.4		51.5		9-Sep-07		12:06:20		70.41		56.5		9-Sep-07		12:07:53		69.8		57.5		20-Oct-07		12:25:59		75.2		57.5

		9-Sep-07		14:07:10		73.4		55		9-Sep-07		14:06:20		70.41		63.5		9-Sep-07		14:07:53		70.41		54.5		20-Oct-07		14:25:59		75.81		57

		9-Sep-07		16:07:10		74.6		54		9-Sep-07		16:06:20		70.41		64.5		9-Sep-07		16:07:53		71		51		20-Oct-07		16:25:59		75.81		57

		9-Sep-07		18:07:10		75.2		50		9-Sep-07		18:06:20		70.41		55		9-Sep-07		18:07:53		70.41		60		20-Oct-07		18:25:59		75.81		56

		9-Sep-07		20:07:10		75.2		44.5		9-Sep-07		20:06:20		71.6		47		9-Sep-07		20:07:53		70.41		55		20-Oct-07		20:25:59		74.01		54.5

		9-Sep-07		22:07:10		74.6		47		9-Sep-07		22:06:20		71		54.5		9-Sep-07		22:07:53		69.8		54		20-Oct-07		22:25:59		72.8		53

		10-Sep-07		0:07:10		74.6		46		10-Sep-07		0:06:20		71		52.5		10-Sep-07		0:07:53		69.2		53.5		21-Oct-07		0:25:59		71.6		51

		10-Sep-07		2:07:10		74.6		45.5		10-Sep-07		2:06:20		71.6		51		10-Sep-07		2:07:53		68.61		53.5		21-Oct-07		2:25:59		71		50

		10-Sep-07		4:07:10		74.01		45		10-Sep-07		4:06:20		71.6		50		10-Sep-07		4:07:53		68.61		54		21-Oct-07		4:25:59		70.41		49.5

		10-Sep-07		6:07:10		74.01		45		10-Sep-07		6:06:20		71		51		10-Sep-07		6:07:53		68		54.5		21-Oct-07		6:25:59		69.8		47.5

		10-Sep-07		8:07:10		72.8		44.5		10-Sep-07		8:06:20		69.8		50.5		10-Sep-07		8:07:53		67.4		54.5		21-Oct-07		8:25:59		69.2		45.5

		10-Sep-07		10:07:10		72.8		45.5		10-Sep-07		10:06:20		69.8		46.5		10-Sep-07		10:07:53		67.4		55		21-Oct-07		10:25:59		69.2		48

		10-Sep-07		12:07:10		72.8		46		10-Sep-07		12:06:20		70.41		49.5		10-Sep-07		12:07:53		68.61		56		21-Oct-07		12:25:59		70.41		45.5

		10-Sep-07		14:07:10		73.4		49		10-Sep-07		14:06:20		70.41		56.5		10-Sep-07		14:07:53		69.8		59.5		21-Oct-07		14:25:59		71		42

		10-Sep-07		16:07:10		74.01		53.5		10-Sep-07		16:06:20		70.41		62.5		10-Sep-07		16:07:53		70.41		49		21-Oct-07		16:25:59		72.21		39

		10-Sep-07		18:07:10		74.6		52.5		10-Sep-07		18:06:20		70.41		63		10-Sep-07		18:07:53		71		56		21-Oct-07		18:25:59		73.4		36.5

		10-Sep-07		20:07:10		75.2		49		10-Sep-07		20:06:20		71.6		55.5		10-Sep-07		20:07:53		71.6		54.5		21-Oct-07		20:25:59		72.21		38

		10-Sep-07		22:07:10		74.6		48		10-Sep-07		22:06:20		71		56		10-Sep-07		22:07:53		70.41		54		21-Oct-07		22:25:59		71		40

		11-Sep-07		0:07:10		74.6		47		11-Sep-07		0:06:20		71		54.5		11-Sep-07		0:07:53		69.8		53.5		22-Oct-07		0:25:59		69.8		39.5

		11-Sep-07		2:07:10		74.01		45.5		11-Sep-07		2:06:20		71		52		11-Sep-07		2:07:53		68.61		53.5		22-Oct-07		2:25:59		69.2		39.5

		11-Sep-07		4:07:10		74.01		44.5		11-Sep-07		4:06:20		71.6		48.5		11-Sep-07		4:07:53		68		53.5		22-Oct-07		4:25:59		69.2		39

		11-Sep-07		6:07:10		74.01		43		11-Sep-07		6:06:20		71		48		11-Sep-07		6:07:53		68.61		52		22-Oct-07		6:25:59		68.61		38.5

		11-Sep-07		8:07:10		74.01		43.5		11-Sep-07		8:06:20		70.41		45		11-Sep-07		8:07:53		71.6		51.5		22-Oct-07		8:25:59		68		37.5

		11-Sep-07		10:07:10		74.6		46.5		11-Sep-07		10:06:20		71		45.5		11-Sep-07		10:07:53		71.6		48		22-Oct-07		10:25:59		68		37.5

		11-Sep-07		12:07:10		74.01		52.5		11-Sep-07		12:06:20		71		63		11-Sep-07		12:07:53		72.21		46		22-Oct-07		12:25:59		69.2		36

		11-Sep-07		14:07:10		74.6		46.5		11-Sep-07		14:06:20		71.6		45		11-Sep-07		14:07:53		71.6		45		22-Oct-07		14:25:59		72.21		33

		11-Sep-07		16:07:10		75.2		48.5		11-Sep-07		16:06:20		70.41		52		11-Sep-07		16:07:53		71		63		22-Oct-07		16:25:59		72.8		33

		11-Sep-07		18:07:10		74.6		49.5		11-Sep-07		18:06:20		70.41		54		11-Sep-07		18:07:53		71		60.5		22-Oct-07		18:25:59		72.8		32.5

		11-Sep-07		20:07:10		75.2		50.5		11-Sep-07		20:06:20		71		58.5		11-Sep-07		20:07:53		70.41		57.5		22-Oct-07		20:25:59		72.8		31.5

		11-Sep-07		22:07:10		75.2		45.5		11-Sep-07		22:06:20		71.6		51.5		11-Sep-07		22:07:53		72.21		52		22-Oct-07		22:25:59		72.21		35

		12-Sep-07		0:07:10		74.6		46.5		12-Sep-07		0:06:20		71.6		53		12-Sep-07		0:07:53		71.6		51		23-Oct-07		0:25:59		71.6		36

		12-Sep-07		2:07:10		74.6		45.5		12-Sep-07		2:06:20		71.6		51.5		12-Sep-07		2:07:53		71		51		23-Oct-07		2:25:59		70.41		37

		12-Sep-07		4:07:10		74.01		46.5		12-Sep-07		4:06:20		70.41		53.5		12-Sep-07		4:07:53		70.41		52		23-Oct-07		4:25:59		69.8		36.5

		12-Sep-07		6:07:10		74.6		46.5		12-Sep-07		6:06:20		71		53		12-Sep-07		6:07:53		70.41		50		23-Oct-07		6:25:59		69.8		36.5

		12-Sep-07		8:07:10		74.01		45.5		12-Sep-07		8:06:20		71.6		44.5		12-Sep-07		8:07:53		71		48.5		23-Oct-07		8:25:59		68.61		37.5

		12-Sep-07		10:07:10		74.01		47.5		12-Sep-07		10:06:20		72.21		55		12-Sep-07		10:07:53		71.6		56		23-Oct-07		10:25:59		71.6		39

		12-Sep-07		12:07:10		74.6		47		12-Sep-07		12:06:20		71.6		53		12-Sep-07		12:07:53		72.21		52		23-Oct-07		12:25:59		74.6		37.5

		12-Sep-07		14:07:10		74.01		46		12-Sep-07		14:06:20		71.6		43		12-Sep-07		14:07:53		71.6		54		23-Oct-07		14:25:59		75.2		37

		12-Sep-07		16:07:10		74.6		49		12-Sep-07		16:06:20		71		53		12-Sep-07		16:07:53		71.6		46.5		23-Oct-07		16:25:59		75.81		36.5

		12-Sep-07		18:07:10		74.6		53		12-Sep-07		18:06:20		70.41		65		12-Sep-07		18:07:53		71		62.5		23-Oct-07		18:25:59		75.81		35.5

		12-Sep-07		20:07:10		74.6		52		12-Sep-07		20:06:20		71		60.5		12-Sep-07		20:07:53		71		54.5		23-Oct-07		20:25:59		74.6		36

		12-Sep-07		22:07:10		74.6		49		12-Sep-07		22:06:20		71.6		56.5		12-Sep-07		22:07:53		72.8		52.5		23-Oct-07		22:25:59		74.01		37.5

		13-Sep-07		0:07:10		75.2		49		13-Sep-07		0:06:20		71.6		56.5		13-Sep-07		0:07:53		72.8		53		24-Oct-07		0:25:59		73.4		38.5

		13-Sep-07		2:07:10		75.2		48.5		13-Sep-07		2:06:20		71		57		13-Sep-07		2:07:53		72.21		53		24-Oct-07		2:25:59		72.21		39

		13-Sep-07		4:07:10		74.6		48.5		13-Sep-07		4:06:20		70.41		58.5		13-Sep-07		4:07:53		71.6		56		24-Oct-07		4:25:59		71		39.5

		13-Sep-07		6:07:10		75.2		49		13-Sep-07		6:06:20		71		58		13-Sep-07		6:07:53		70.41		50.5		24-Oct-07		6:25:59		71		39

		13-Sep-07		8:07:10		74.6		50		13-Sep-07		8:06:20		71		52.5		13-Sep-07		8:07:53		71		56		24-Oct-07		8:25:59		69.8		39.5

		13-Sep-07		10:07:10		74.01		45.5		13-Sep-07		10:06:20		71.6		44.5		13-Sep-07		10:07:53		71.6		57		24-Oct-07		10:25:59		72.21		42.5

		13-Sep-07		12:07:10		74.6		48		13-Sep-07		12:06:20		71.6		52.5		13-Sep-07		12:07:53		71.6		48		24-Oct-07		12:25:59		75.2		41

		13-Sep-07		14:07:10		74.6		45.5		13-Sep-07		14:06:20		71.6		44		13-Sep-07		14:07:53		70.41		61.5		24-Oct-07		14:25:59		75.81		40.5

		13-Sep-07		16:07:10		74.6		52.5		13-Sep-07		16:06:20		70.41		58		13-Sep-07		16:07:53		71		61.5		24-Oct-07		16:25:59		76.4		40.5

		13-Sep-07		18:07:10		75.2		47		13-Sep-07		18:06:20		70.41		51		13-Sep-07		18:07:53		70.41		59.5		24-Oct-07		18:25:59		75.81		42.5

		13-Sep-07		20:07:10		75.2		48		13-Sep-07		20:06:20		71.6		55.5		13-Sep-07		20:07:53		71.6		55		24-Oct-07		20:25:59		75.2		45

		13-Sep-07		22:07:10		74.6		47.5		13-Sep-07		22:06:20		71		54.5		13-Sep-07		22:07:53		71.6		52.5		24-Oct-07		22:25:59		75.81		44.5

		14-Sep-07		0:07:10		74.6		46.5		14-Sep-07		0:06:20		71.6		53		14-Sep-07		0:07:53		71.6		51.5		25-Oct-07		0:25:59		74.6		43

		14-Sep-07		2:07:10		74.6		46.5		14-Sep-07		2:06:20		71		51.5		14-Sep-07		2:07:53		71.6		51.5		25-Oct-07		2:25:59		73.4		43

		14-Sep-07		4:07:10		74.6		44.5		14-Sep-07		4:06:20		71.6		50		14-Sep-07		4:07:53		71		45		25-Oct-07		4:25:59		72.21		43

		14-Sep-07		6:07:10		74.6		43.5		14-Sep-07		6:06:20		71		49.5		14-Sep-07		6:07:53		71		51		25-Oct-07		6:25:59		71.6		43

		14-Sep-07		8:07:10		74.01		46		14-Sep-07		8:06:20		71.6		54		14-Sep-07		8:07:53		71		53		25-Oct-07		8:25:59		71		42.5

		14-Sep-07		10:07:10		74.6		46.5		14-Sep-07		10:06:20		71.6		55.5		14-Sep-07		10:07:53		72.21		47.5		25-Oct-07		10:25:59		73.4		44

		14-Sep-07		12:07:10		74.01		47.5		14-Sep-07		12:06:20		70.41		53		14-Sep-07		12:07:53		72.21		43		25-Oct-07		12:25:59		75.2		44

		14-Sep-07		14:07:10		74.6		49		14-Sep-07		14:06:20		71.6		56		14-Sep-07		14:07:53		71.6		48		25-Oct-07		14:25:59		75.81		43

		14-Sep-07		16:07:10		75.2		46.5		14-Sep-07		16:06:20		71		53		14-Sep-07		16:07:53		71.6		58.5		25-Oct-07		16:25:59		75.81		41

		14-Sep-07		18:07:10		75.2		50.5		14-Sep-07		18:06:20		71		64.5		14-Sep-07		18:07:53		71		62		25-Oct-07		18:25:59		75.81		44.5

		14-Sep-07		20:07:10		75.2		50		14-Sep-07		20:06:20		71.6		59		14-Sep-07		20:07:53		72.8		55.5		25-Oct-07		20:25:59		75.2		43.5

		14-Sep-07		22:07:10		75.2		50.5		14-Sep-07		22:06:20		71.6		59.5		14-Sep-07		22:07:53		74.01		52.5		25-Oct-07		22:25:59		74.6		42.5

		15-Sep-07		0:07:10		75.2		48.5		15-Sep-07		0:06:20		71		51.5		15-Sep-07		0:07:53		73.4		52		26-Oct-07		0:25:59		73.4		42.5

		15-Sep-07		2:07:10		74.6		48		15-Sep-07		2:06:20		71.6		56		15-Sep-07		2:07:53		73.4		52		26-Oct-07		2:25:59		72.21		43

		15-Sep-07		4:07:10		74.6		48.5		15-Sep-07		4:06:20		71.6		55.5		15-Sep-07		4:07:53		72.21		54.5		26-Oct-07		4:25:59		71		42.5

		15-Sep-07		6:07:10		75.2		49.5		15-Sep-07		6:06:20		71.6		58.5		15-Sep-07		6:07:53		71		51		26-Oct-07		6:25:59		70.41		41.5

		15-Sep-07		8:07:10		75.2		46		15-Sep-07		8:06:20		72.21		49		15-Sep-07		8:07:53		71.6		56		26-Oct-07		8:25:59		69.2		41

		15-Sep-07		10:07:10		74.6		50		15-Sep-07		10:06:20		71.6		57.5		15-Sep-07		10:07:53		71.6		50		26-Oct-07		10:25:59		71		44.5

		15-Sep-07		12:07:10		74.01		51		15-Sep-07		12:06:20		71		51		15-Sep-07		12:07:53		72.21		49.5		26-Oct-07		12:25:59		74.6		43.5

		15-Sep-07		14:07:10		74.6		46.5		15-Sep-07		14:06:20		71.6		47.5		15-Sep-07		14:07:53		71.6		54		26-Oct-07		14:25:59		75.81		43.5

		15-Sep-07		16:07:10		74.6		45.5		15-Sep-07		16:06:20		69.2		50.5		15-Sep-07		16:07:53		71.6		53		26-Oct-07		16:25:59		76.4		43.5

		15-Sep-07		18:07:10		73.4		46		15-Sep-07		18:06:20		68		50		15-Sep-07		18:07:53		71		48.5		26-Oct-07		18:25:59		75.81		44

		15-Sep-07		20:07:10		74.6		45		15-Sep-07		20:06:20		71		52		15-Sep-07		20:07:53		71		50.5		26-Oct-07		20:25:59		74.6		43

		15-Sep-07		22:07:10		75.2		44.5		15-Sep-07		22:06:20		71.6		52		15-Sep-07		22:07:53		72.8		48		26-Oct-07		22:25:59		73.4		42.5

		16-Sep-07		0:07:10		75.2		44		16-Sep-07		0:06:20		71		51.5		16-Sep-07		0:07:53		72.8		48		27-Oct-07		0:25:59		72.21		43

		16-Sep-07		2:07:10		75.2		43		16-Sep-07		2:06:20		71.6		49.5		16-Sep-07		2:07:53		72.21		47.5		27-Oct-07		2:25:59		71		44

		16-Sep-07		4:07:10		74.6		44		16-Sep-07		4:06:20		71		51		16-Sep-07		4:07:53		71		48.5		27-Oct-07		4:25:59		70.41		44.5

		16-Sep-07		6:07:10		74.01		43		16-Sep-07		6:06:20		69.8		44		16-Sep-07		6:07:53		71		49		27-Oct-07		6:25:59		70.41		45.5

		16-Sep-07		8:07:10		73.4		44		16-Sep-07		8:06:20		68.61		54		16-Sep-07		8:07:53		70.41		48		27-Oct-07		8:25:59		70.41		46

		16-Sep-07		10:07:10		73.4		45.5		16-Sep-07		10:06:20		68.61		57		16-Sep-07		10:07:53		69.8		52.5		27-Oct-07		10:25:59		72.21		45.5

		16-Sep-07		12:07:10		72.8		46		16-Sep-07		12:06:20		68.61		47.5		16-Sep-07		12:07:53		70.41		56		27-Oct-07		12:25:59		74.6		44

		16-Sep-07		14:07:10		73.4		44.5		16-Sep-07		14:06:20		68.61		47		16-Sep-07		14:07:53		71		51		27-Oct-07		14:25:59		75.2		42.5

		16-Sep-07		16:07:10		74.6		45		16-Sep-07		16:06:20		68.61		52		16-Sep-07		16:07:53		71		50.5		27-Oct-07		16:25:59		75.2		43.5

		16-Sep-07		18:07:10		74.6		46		16-Sep-07		18:06:20		68.61		59		16-Sep-07		18:07:53		70.41		53		27-Oct-07		18:25:59		74.6		44

		16-Sep-07		20:07:10		75.81		45		16-Sep-07		20:06:20		71		54		16-Sep-07		20:07:53		71.6		51.5		27-Oct-07		20:25:59		72.21		43.5

		16-Sep-07		22:07:10		75.2		44.5		16-Sep-07		22:06:20		71		52.5		16-Sep-07		22:07:53		72.21		49.5		27-Oct-07		22:25:59		71.6		44

		17-Sep-07		0:07:10		75.2		43		17-Sep-07		0:06:20		71		51.5		17-Sep-07		0:07:53		71.6		49		28-Oct-07		0:25:59		70.41		43.5

		17-Sep-07		2:07:10		74.6		42.5		17-Sep-07		2:06:20		70.41		49.5		17-Sep-07		2:07:53		70.41		48.5		28-Oct-07		2:25:59		69.2		42.5

		17-Sep-07		4:07:10		74.01		41.5		17-Sep-07		4:06:20		70.41		47		17-Sep-07		4:07:53		69.8		48		28-Oct-07		4:25:59		68.61		42

		17-Sep-07		6:07:10		73.4		41.5		17-Sep-07		6:06:20		69.8		42		17-Sep-07		6:07:53		69.2		49		28-Oct-07		6:25:59		68.61		41.5

		17-Sep-07		8:07:10		72.21		44.5		17-Sep-07		8:06:20		68		52.5		17-Sep-07		8:07:53		69.2		50		28-Oct-07		8:25:59		68		42

		17-Sep-07		10:07:10		72.8		47.5		17-Sep-07		10:06:20		68.61		57.5		17-Sep-07		10:07:53		70.41		49.5		28-Oct-07		10:25:59		67.4		44.5

		17-Sep-07		12:07:10		72.8		50.5		17-Sep-07		12:06:20		68.61		61		17-Sep-07		12:07:53		71		49.5		28-Oct-07		12:25:59		68.61		45.5

		17-Sep-07		14:07:10		74.01		45.5		17-Sep-07		14:06:20		69.2		52		17-Sep-07		14:07:53		71		57		28-Oct-07		14:25:59		69.8		46

		17-Sep-07		16:07:10		74.6		49.5		17-Sep-07		16:06:20		68.61		58		17-Sep-07		16:07:53		71		51.5		28-Oct-07		16:25:59		71.6		47

		17-Sep-07		18:07:10		74.6		48.5		17-Sep-07		18:06:20		68.61		61.5		17-Sep-07		18:07:53		71		50		28-Oct-07		18:25:59		71.6		45

		17-Sep-07		20:07:10		75.81		46		17-Sep-07		20:06:20		71		55		17-Sep-07		20:07:53		74.01		48		28-Oct-07		20:25:59		70.41		45

		17-Sep-07		22:07:10		75.81		44		17-Sep-07		22:06:20		71.6		52		17-Sep-07		22:07:53		74.6		46.5		28-Oct-07		22:25:59		69.8		44.5

		18-Sep-07		0:07:10		75.2		42.5		18-Sep-07		0:06:20		71		50		18-Sep-07		0:07:53		73.4		45.5		29-Oct-07		0:25:59		69.2		44

		18-Sep-07		2:07:10		75.2		41.5		18-Sep-07		2:06:20		71.6		48		18-Sep-07		2:07:53		72.21		45.5		29-Oct-07		2:25:59		68.61		44

		18-Sep-07		4:07:10		74.6		40.5		18-Sep-07		4:06:20		71		46.5		18-Sep-07		4:07:53		71		45.5		29-Oct-07		4:25:59		68.61		44

		18-Sep-07		6:07:10		74.6		39.5		18-Sep-07		6:06:20		69.8		45		18-Sep-07		6:07:53		70.41		45.5		29-Oct-07		6:25:59		68		43.5

		18-Sep-07		8:07:10		72.8		40		18-Sep-07		8:06:20		69.2		39.5		18-Sep-07		8:07:53		71		44.5		29-Oct-07		8:25:59		67.4		43

		18-Sep-07		10:07:10		73.4		42.5		18-Sep-07		10:06:20		70.41		46.5		18-Sep-07		10:07:53		71.6		42.5		29-Oct-07		10:25:59		68.61		45.5

		18-Sep-07		12:07:10		73.4		44.5		18-Sep-07		12:06:20		69.8		51		18-Sep-07		12:07:53		72.21		43.5		29-Oct-07		12:25:59		70.41		46.5

		18-Sep-07		14:07:10		73.4		42.5		18-Sep-07		14:06:20		69.8		42		18-Sep-07		14:07:53		71.6		43.5		29-Oct-07		14:25:59		72.21		47.5

		18-Sep-07		16:07:10		74.01		47.5		18-Sep-07		16:06:20		69.2		61		18-Sep-07		16:07:53		71		49.5		29-Oct-07		16:25:59		74.6		47.5

		18-Sep-07		18:07:10		74.01		43.5		18-Sep-07		18:06:20		69.2		49.5		18-Sep-07		18:07:53		71		43		29-Oct-07		18:25:59		75.2		47

		18-Sep-07		20:07:10		74.6		44		18-Sep-07		20:06:20		71.6		50		18-Sep-07		20:07:53		71.6		51.5		29-Oct-07		20:25:59		74.01		46

		18-Sep-07		22:07:10		75.2		42.5		18-Sep-07		22:06:20		71.6		50.5		18-Sep-07		22:07:53		73.4		46		29-Oct-07		22:25:59		72.8		46

		19-Sep-07		0:07:10		75.2		42.5		19-Sep-07		0:06:20		71		49.5		19-Sep-07		0:07:53		73.4		44.5		30-Oct-07		0:25:59		71.6		46

		19-Sep-07		2:07:10		74.6		41		19-Sep-07		2:06:20		71		48		19-Sep-07		2:07:53		72.8		44		30-Oct-07		2:25:59		71		46

		19-Sep-07		4:07:10		74.6		40		19-Sep-07		4:06:20		71		46		19-Sep-07		4:07:53		71		44		30-Oct-07		4:25:59		69.8		45.5

		19-Sep-07		6:07:10		74.01		38.5		19-Sep-07		6:06:20		70.41		41.5		19-Sep-07		6:07:53		70.41		43.5		30-Oct-07		6:25:59		69.8		46

		19-Sep-07		8:07:10		72.8		41		19-Sep-07		8:06:20		69.8		48		19-Sep-07		8:07:53		71		42.5		30-Oct-07		8:25:59		69.2		48

		19-Sep-07		10:07:10		72.8		43.5		19-Sep-07		10:06:20		70.41		51.5		19-Sep-07		10:07:53		71.6		45.5		30-Oct-07		10:25:59		71		48

		19-Sep-07		12:07:10		73.4		45.5		19-Sep-07		12:06:20		70.41		56		19-Sep-07		12:07:53		72.21		53		30-Oct-07		12:25:59		72.8		49

		19-Sep-07		14:07:10		74.6		43.5		19-Sep-07		14:06:20		72.21		49		19-Sep-07		14:07:53		71.6		41		30-Oct-07		14:25:59		74.6		48

		19-Sep-07		16:07:10		73.4		42.5		19-Sep-07		16:06:20		68.61		45		19-Sep-07		16:07:53		72.21		48		30-Oct-07		16:25:59		75.2		47.5

		19-Sep-07		18:07:10		73.4		42		19-Sep-07		18:06:20		68.61		43		19-Sep-07		18:07:53		71		50		30-Oct-07		18:25:59		75.2		45

		19-Sep-07		20:07:10		74.6		42		19-Sep-07		20:06:20		70.41		49		19-Sep-07		20:07:53		71		47.5		30-Oct-07		20:25:59		72.8		45.5

		19-Sep-07		22:07:10		74.6		39.5		19-Sep-07		22:06:20		70.41		46.5		19-Sep-07		22:07:53		72.21		42.5		30-Oct-07		22:25:59		71.6		46.5

		20-Sep-07		0:07:10		74.6		38		20-Sep-07		0:06:20		70.41		44		20-Sep-07		0:07:53		71.6		41		31-Oct-07		0:25:59		71		46.5

		20-Sep-07		2:07:10		74.01		37		20-Sep-07		2:06:20		70.41		42		20-Sep-07		2:07:53		71		40.5		31-Oct-07		2:25:59		70.41		47.5

		20-Sep-07		4:07:10		73.4		36		20-Sep-07		4:06:20		70.41		41		20-Sep-07		4:07:53		69.8		40.5		31-Oct-07		4:25:59		70.41		48

		20-Sep-07		6:07:10		72.8		36		20-Sep-07		6:06:20		69.8		40		20-Sep-07		6:07:53		69.8		40		31-Oct-07		6:25:59		70.41		48.5

		20-Sep-07		8:07:10		72.8		37.5		20-Sep-07		8:06:20		69.8		44		20-Sep-07		8:07:53		71		39.5		31-Oct-07		8:25:59		69.8		48

		20-Sep-07		10:07:10		73.4		37.5		20-Sep-07		10:06:20		70.41		45.5		20-Sep-07		10:07:53		71.6		35.5		31-Oct-07		10:25:59		71.6		48

		20-Sep-07		12:07:10		73.4		36		20-Sep-07		12:06:20		69.2		35.5		20-Sep-07		12:07:53		72.21		34.5		31-Oct-07		12:25:59		72.21		47.5

		20-Sep-07		14:07:10		73.4		34		20-Sep-07		14:06:20		69.8		36		20-Sep-07		14:07:53		71.6		39.5		31-Oct-07		14:25:59		73.4		46.5

		20-Sep-07		16:07:10		73.4		34		20-Sep-07		16:06:20		68.61		37.5		20-Sep-07		16:07:53		71		33		31-Oct-07		16:25:59		74.6		46

		20-Sep-07		18:07:10		74.01		34.5		20-Sep-07		18:06:20		68		41.5		20-Sep-07		18:07:53		70.41		38.5		31-Oct-07		18:25:59		75.2		44.5

		20-Sep-07		20:07:10		74.6		36		20-Sep-07		20:06:20		69.8		41		20-Sep-07		20:07:53		72.8		37.5		31-Oct-07		20:25:59		72.8		44.5

		20-Sep-07		22:07:10		74.6		34		20-Sep-07		22:06:20		70.41		39.5		20-Sep-07		22:07:53		72.21		36.5		31-Oct-07		22:25:59		72.21		45.5

		21-Sep-07		0:07:10		74.01		34.5		21-Sep-07		0:06:20		69.8		40.5		21-Sep-07		0:07:53		71.6		37.5		1-Nov-07		0:25:59		70.41		46

		21-Sep-07		2:07:10		74.01		33.5		21-Sep-07		2:06:20		70.41		36		21-Sep-07		2:07:53		71		37		1-Nov-07		2:25:59		69.8		47

		21-Sep-07		4:07:10		73.4		33		21-Sep-07		4:06:20		70.41		38		21-Sep-07		4:07:53		69.8		37		1-Nov-07		4:25:59		69.8		48

		21-Sep-07		6:07:10		73.4		34.5		21-Sep-07		6:06:20		69.8		39.5		21-Sep-07		6:07:53		69.8		39		1-Nov-07		6:25:59		69.8		48.5

		21-Sep-07		8:07:10		72.8		37.5		21-Sep-07		8:06:20		69.8		44.5		21-Sep-07		8:07:53		71		39		1-Nov-07		8:25:59		69.8		48.5

		21-Sep-07		10:07:10		72.8		38.5		21-Sep-07		10:06:20		69.8		41.5		21-Sep-07		10:07:53		71.6		42		1-Nov-07		10:25:59		72.21		48

		21-Sep-07		12:07:10		74.6		37		21-Sep-07		12:06:20		73.4		36		21-Sep-07		12:07:53		71.6		36.5		1-Nov-07		12:25:59		72.8		48.5

		21-Sep-07		14:07:10		74.6		38.5		21-Sep-07		14:06:20		71.6		45		21-Sep-07		14:07:53		71		41.5		1-Nov-07		14:25:59		73.4		48.5

		21-Sep-07		16:07:10		74.6		38		21-Sep-07		16:06:20		70.41		45.5		21-Sep-07		16:07:53		71		41		1-Nov-07		16:25:59		74.01		49.5

		21-Sep-07		18:07:10		74.6		37.5		21-Sep-07		18:06:20		70.41		44		21-Sep-07		18:07:53		71		40.5		1-Nov-07		18:25:59		74.01		48

		21-Sep-07		20:07:10		75.81		35		21-Sep-07		20:06:20		72.21		39		21-Sep-07		20:07:53		71.6		39		1-Nov-07		20:25:59		72.21		48

		21-Sep-07		22:07:10		75.81		33.5		21-Sep-07		22:06:20		72.8		37.5		21-Sep-07		22:07:53		71		38		1-Nov-07		22:25:59		71.6		49

		22-Sep-07		0:07:10		75.2		33		22-Sep-07		0:06:20		72.21		37		22-Sep-07		0:07:53		70.41		38.5		2-Nov-07		0:25:59		71		49

		22-Sep-07		2:07:10		74.6		32.5		22-Sep-07		2:06:20		71.6		36.5		22-Sep-07		2:07:53		68.61		38.5		2-Nov-07		2:25:59		70.41		49.5

		22-Sep-07		4:07:10		73.4		33		22-Sep-07		4:06:20		70.41		37.5		22-Sep-07		4:07:53		68		39.5		2-Nov-07		4:25:59		69.8		49

		22-Sep-07		6:07:10		72.8		33.5		22-Sep-07		6:06:20		69.8		37.5		22-Sep-07		6:07:53		67.4		40.5		2-Nov-07		6:25:59		69.8		48

		22-Sep-07		8:07:10		72.8		33.5		22-Sep-07		8:06:20		71.6		37.5		22-Sep-07		8:07:53		69.2		40		2-Nov-07		8:25:59		71.6		46.5

		22-Sep-07		10:07:10		73.4		36		22-Sep-07		10:06:20		72.21		39		22-Sep-07		10:07:53		71.6		43.5		2-Nov-07		10:25:59		71.6		48

		22-Sep-07		12:07:10		73.4		36.5		22-Sep-07		12:06:20		71.6		40.5		22-Sep-07		12:07:53		71.6		44.5		2-Nov-07		12:25:59		73.4		48

		22-Sep-07		14:07:10		74.01		38		22-Sep-07		14:06:20		71		40.5		22-Sep-07		14:07:53		72.21		43		2-Nov-07		14:25:59		75.2		48

		22-Sep-07		16:07:10		74.6		40.5		22-Sep-07		16:06:20		70.41		47		22-Sep-07		16:07:53		71.6		47		2-Nov-07		16:25:59		75.2		49.5

		22-Sep-07		18:07:10		74.6		38.5		22-Sep-07		18:06:20		70.41		45		22-Sep-07		18:07:53		71		38.5		2-Nov-07		18:25:59		75.2		50

		22-Sep-07		20:07:10		75.2		37.5		22-Sep-07		20:06:20		72.21		42		22-Sep-07		20:07:53		70.41		44		2-Nov-07		20:25:59		74.6		46

		22-Sep-07		22:07:10		75.81		37.5		22-Sep-07		22:06:20		72.8		42.5		22-Sep-07		22:07:53		71.6		43		2-Nov-07		22:25:59		73.4		45.5

		23-Sep-07		0:07:10		75.81		38.5		23-Sep-07		0:06:20		73.4		43.5		23-Sep-07		0:07:53		71.6		44.5		3-Nov-07		0:25:59		71.6		45

		23-Sep-07		2:07:10		75.2		40		23-Sep-07		2:06:20		72.21		46.5		23-Sep-07		2:07:53		71		46.5		3-Nov-07		2:25:59		69.8		44

		23-Sep-07		4:07:10		75.2		41		23-Sep-07		4:06:20		72.8		46		23-Sep-07		4:07:53		71		47.5		3-Nov-07		4:25:59		69.2		43

		23-Sep-07		6:07:10		74.6		42		23-Sep-07		6:06:20		71.6		44		23-Sep-07		6:07:53		71.6		48		3-Nov-07		6:25:59		69.2		42

		23-Sep-07		8:07:10		74.01		44.5		23-Sep-07		8:06:20		69.8		52		23-Sep-07		8:07:53		71		43.5		3-Nov-07		8:25:59		71.6		39.5

		23-Sep-07		10:07:10		73.4		44.5		23-Sep-07		10:06:20		70.41		50.5		23-Sep-07		10:07:53		71.6		56		3-Nov-07		10:25:59		71.6		42.5

		23-Sep-07		12:07:10		74.01		44.5		23-Sep-07		12:06:20		70.41		48		23-Sep-07		12:07:53		71		49		3-Nov-07		12:25:59		75.2		42.5

		23-Sep-07		14:07:10		73.4		48.5		23-Sep-07		14:06:20		70.41		56.5		23-Sep-07		14:07:53		71		54		3-Nov-07		14:25:59		76.4		42.5

		23-Sep-07		16:07:10		74.01		50.5		23-Sep-07		16:06:20		70.41		60		23-Sep-07		16:07:53		70.41		51		3-Nov-07		16:25:59		75.81		42

		23-Sep-07		18:07:10		73.4		50.5		23-Sep-07		18:06:20		70.41		59		23-Sep-07		18:07:53		69.8		56.5		3-Nov-07		18:25:59		75.81		43.5

		23-Sep-07		20:07:10		74.6		49.5		23-Sep-07		20:06:20		72.21		55		23-Sep-07		20:07:53		69.8		56		3-Nov-07		20:25:59		74.6		43

		23-Sep-07		22:07:10		74.6		48		23-Sep-07		22:06:20		72.21		52.5		23-Sep-07		22:07:53		70.41		55.5		3-Nov-07		22:25:59		73.4		43.5

		24-Sep-07		0:07:10		74.6		47.5		24-Sep-07		0:06:20		72.21		52		24-Sep-07		0:07:53		69.8		54.5		4-Nov-07		0:25:59		71.6		43

		24-Sep-07		2:07:10		74.6		47.5		24-Sep-07		2:06:20		72.21		52		24-Sep-07		2:07:53		69.8		55		4-Nov-07		2:25:59		70.41		42

		24-Sep-07		4:07:10		74.6		47		24-Sep-07		4:06:20		72.21		51.5		24-Sep-07		4:07:53		69.8		54.5		4-Nov-07		4:25:59		69.2		41

		24-Sep-07		6:07:10		74.01		46.5		24-Sep-07		6:06:20		71.6		46		24-Sep-07		6:07:53		69.8		54.5		4-Nov-07		6:25:59		68.61		40

		24-Sep-07		8:07:10		73.4		49		24-Sep-07		8:06:20		70.41		56		24-Sep-07		8:07:53		69.2		55		4-Nov-07		8:25:59		67.4		38.5

		24-Sep-07		10:07:10		72.8		50.5		24-Sep-07		10:06:20		69.8		56.5		24-Sep-07		10:07:53		69.8		55.5		4-Nov-07		10:25:59		68		40.5

		24-Sep-07		12:07:10		72.8		51		24-Sep-07		12:06:20		69.2		55.5		24-Sep-07		12:07:53		69.8		56		4-Nov-07		12:25:59		69.2		42.5

		24-Sep-07		14:07:10		73.4		50		24-Sep-07		14:06:20		69.8		56.5		24-Sep-07		14:07:53		70.41		51.5		4-Nov-07		14:25:59		71		43

		24-Sep-07		16:07:10		74.01		46		24-Sep-07		16:06:20		69.8		44		24-Sep-07		16:07:53		70.41		48		4-Nov-07		16:25:59		72.21		43

		24-Sep-07		18:07:10		74.01		45		24-Sep-07		18:06:20		69.8		51		24-Sep-07		18:07:53		71		46.5		4-Nov-07		18:25:59		72.8		41.5

		24-Sep-07		20:07:10		75.2		40		24-Sep-07		20:06:20		72.8		39.5		24-Sep-07		20:07:53		72.21		45		4-Nov-07		20:25:59		71.6		39

		24-Sep-07		22:07:10		75.81		40		24-Sep-07		22:06:20		73.4		43.5		24-Sep-07		22:07:53		71.6		45.5		4-Nov-07		22:25:59		70.41		39.5

		25-Sep-07		0:07:10		74.6		39		25-Sep-07		0:06:20		72.21		43		25-Sep-07		0:07:53		70.41		45		5-Nov-07		0:25:59		69.8		40

		25-Sep-07		2:07:10		74.01		37.5		25-Sep-07		2:06:20		71.6		41		25-Sep-07		2:07:53		69.2		44		5-Nov-07		2:25:59		68.61		40

		25-Sep-07		4:07:10		73.4		37		25-Sep-07		4:06:20		71		40		25-Sep-07		4:07:53		68		43		5-Nov-07		4:25:59		68		39

		25-Sep-07		6:07:10		72.8		36.5		25-Sep-07		6:06:20		69.8		38.5		25-Sep-07		6:07:53		68.61		42		5-Nov-07		6:25:59		67.4		38.5

		25-Sep-07		8:07:10		72.8		37		25-Sep-07		8:06:20		71		41		25-Sep-07		8:07:53		69.2		41		5-Nov-07		8:25:59		66.2		37.5

		25-Sep-07		10:07:10		74.01		38		25-Sep-07		10:06:20		72.21		40		25-Sep-07		10:07:53		71		48		5-Nov-07		10:25:59		67.4		39.5

		25-Sep-07		12:07:10		74.6		39		25-Sep-07		12:06:20		71.6		43		25-Sep-07		12:07:53		71.6		43		5-Nov-07		12:25:59		69.2		40.5

		25-Sep-07		14:07:10		74.01		34.5		25-Sep-07		14:06:20		71.6		37.5		25-Sep-07		14:07:53		71.6		35		5-Nov-07		14:25:59		71		41.5

		25-Sep-07		16:07:10		74.6		36.5		25-Sep-07		16:06:20		70.41		40.5		25-Sep-07		16:07:53		72.21		39		5-Nov-07		16:25:59		72.21		41.5

		25-Sep-07		18:07:10		74.01		33.5		25-Sep-07		18:06:20		70.41		36		25-Sep-07		18:07:53		71.6		37		5-Nov-07		18:25:59		72.8		41

		25-Sep-07		20:07:10		75.81		36.5		25-Sep-07		20:06:20		72.8		40.5		25-Sep-07		20:07:53		71		42.5		5-Nov-07		20:25:59		71.6		42.5

		25-Sep-07		22:07:10		75.81		36		25-Sep-07		22:06:20		72.8		40		25-Sep-07		22:07:53		72.8		40		5-Nov-07		22:25:59		71		43

		26-Sep-07		0:07:10		75.81		35		26-Sep-07		0:06:20		72.8		39		26-Sep-07		0:07:53		71.6		40		6-Nov-07		0:25:59		69.8		42

		26-Sep-07		2:07:10		75.2		34.5		26-Sep-07		2:06:20		72.21		39		26-Sep-07		2:07:53		69.8		40		6-Nov-07		2:25:59		69.2		41.5

		26-Sep-07		4:07:10		74.01		34		26-Sep-07		4:06:20		71		38		26-Sep-07		4:07:53		68.61		40		6-Nov-07		4:25:59		68		40.5

		26-Sep-07		6:07:10		72.8		33.5		26-Sep-07		6:06:20		70.41		36		26-Sep-07		6:07:53		68.61		39.5		6-Nov-07		6:25:59		68		39.5

		26-Sep-07		8:07:10		73.4		33		26-Sep-07		8:06:20		71.6		36.5		26-Sep-07		8:07:53		70.41		37.5		6-Nov-07		8:25:59		69.8		37

		26-Sep-07		10:07:10		74.01		37		26-Sep-07		10:06:20		71.6		38.5		26-Sep-07		10:07:53		71.6		34.5		6-Nov-07		10:25:59		71		39.5

		26-Sep-07		12:07:10		74.6		34.5		26-Sep-07		12:06:20		71.6		36		26-Sep-07		12:07:53		71.6		35.5		6-Nov-07		12:25:59		73.4		39.5

		26-Sep-07		14:07:10		74.6		33		26-Sep-07		14:06:20		71.6		35.5		26-Sep-07		14:07:53		71.6		34		6-Nov-07		14:25:59		75.2		39.5

		26-Sep-07		16:07:10		75.2		32.5		26-Sep-07		16:06:20		71		35.5		26-Sep-07		16:07:53		71.6		34.5		6-Nov-07		16:25:59		75.81		42.5

		26-Sep-07		18:07:10		74.6		31		26-Sep-07		18:06:20		69.8		34.5		26-Sep-07		18:07:53		71		34.5		6-Nov-07		18:25:59		75.2		41.5

		26-Sep-07		20:07:10		75.81		32		26-Sep-07		20:06:20		72.8		35.5		26-Sep-07		20:07:53		71		33.5		6-Nov-07		20:25:59		72.8		41

		26-Sep-07		22:07:10		76.4		31		26-Sep-07		22:06:20		72.8		35.5		26-Sep-07		22:07:53		73.4		34.5		6-Nov-07		22:25:59		71.6		42

		27-Sep-07		0:07:10		76.4		31		27-Sep-07		0:06:20		72.8		35.5		27-Sep-07		0:07:53		72.8		34.5		7-Nov-07		0:25:59		71		43

		27-Sep-07		2:07:10		75.81		30.5		27-Sep-07		2:06:20		72.21		35		27-Sep-07		2:07:53		71.6		34.5		7-Nov-07		2:25:59		69.8		43

		27-Sep-07		4:07:10		75.2		30		27-Sep-07		4:06:20		72.21		34		27-Sep-07		4:07:53		70.41		35		7-Nov-07		4:25:59		69.2		43.5

		27-Sep-07		6:07:10		75.2		30.5		27-Sep-07		6:06:20		72.21		33		27-Sep-07		6:07:53		70.41		35.5		7-Nov-07		6:25:59		69.2		44

		27-Sep-07		8:07:10		74.6		31.5		27-Sep-07		8:06:20		71.6		35		27-Sep-07		8:07:53		71.6		33		7-Nov-07		8:25:59		71		43

		27-Sep-07		10:07:10		74.6		32		27-Sep-07		10:06:20		72.21		37.5		27-Sep-07		10:07:53		71.6		36.5		7-Nov-07		10:25:59		71.6		42.5

		27-Sep-07		12:07:10		74.6		34		27-Sep-07		12:06:20		71.6		37		27-Sep-07		12:07:53		72.21		39		7-Nov-07		12:25:59		72.8		42

		27-Sep-07		14:07:10		74.6		34		27-Sep-07		14:06:20		71		35.5		27-Sep-07		14:07:53		72.21		34		7-Nov-07		14:25:59		74.01		42.5

		27-Sep-07		16:07:10		75.2		33		27-Sep-07		16:06:20		70.41		37.5		27-Sep-07		16:07:53		71.6		34.5		7-Nov-07		16:25:59		74.6		44

		27-Sep-07		18:07:10		75.2		32.5		27-Sep-07		18:06:20		71		36		27-Sep-07		18:07:53		71.6		35.5		7-Nov-07		18:25:59		74.6		43

		27-Sep-07		20:07:10		76.4		30.5		27-Sep-07		20:06:20		72.8		33.5		27-Sep-07		20:07:53		74.6		31.5		7-Nov-07		20:25:59		72.21		42.5

		27-Sep-07		22:07:10		76.4		30.5		27-Sep-07		22:06:20		72.8		34.5		27-Sep-07		22:07:53		75.2		32		7-Nov-07		22:25:59		71.6		42

		28-Sep-07		0:07:10		76.4		30		28-Sep-07		0:06:20		72.8		34.5		28-Sep-07		0:07:53		74.6		32.5		8-Nov-07		0:25:59		69.8		42.5

		28-Sep-07		2:07:10		75.81		29.5		28-Sep-07		2:06:20		72.8		33		28-Sep-07		2:07:53		72.8		33		8-Nov-07		2:25:59		69.2		43

		28-Sep-07		4:07:10		75.2		30		28-Sep-07		4:06:20		72.8		34		28-Sep-07		4:07:53		71.6		34		8-Nov-07		4:25:59		68.61		42.5

		28-Sep-07		6:07:10		75.2		30.5		28-Sep-07		6:06:20		72.8		32.5		28-Sep-07		6:07:53		70.41		35		8-Nov-07		6:25:59		68.61		43

		28-Sep-07		8:07:10		74.6		31.5		28-Sep-07		8:06:20		71		37		28-Sep-07		8:07:53		71.6		31.5		8-Nov-07		8:25:59		71.6		40.5

		28-Sep-07		10:07:10		74.6		32.5		28-Sep-07		10:06:20		71.6		39		28-Sep-07		10:07:53		71.6		38.5		8-Nov-07		10:25:59		71		41.5

		28-Sep-07		12:07:10		74.6		33		28-Sep-07		12:06:20		71.6		36.5		28-Sep-07		12:07:53		72.21		34.5		8-Nov-07		12:25:59		72.8		43.5

		28-Sep-07		14:07:10		74.01		36		28-Sep-07		14:06:20		71		36		28-Sep-07		14:07:53		71.6		40		8-Nov-07		14:25:59		74.01		42.5

		28-Sep-07		16:07:10		75.2		37.5		28-Sep-07		16:06:20		71		44		28-Sep-07		16:07:53		71.6		41.5		8-Nov-07		16:25:59		75.2		43.5

		28-Sep-07		18:07:10		74.6		39		28-Sep-07		18:06:20		70.41		46.5		28-Sep-07		18:07:53		71		45		8-Nov-07		18:25:59		74.01		43

		28-Sep-07		20:07:10		75.81		37		28-Sep-07		20:06:20		72.8		42		28-Sep-07		20:07:53		71.6		42		8-Nov-07		20:25:59		72.21		43.5

		28-Sep-07		22:07:10		75.81		36.5		28-Sep-07		22:06:20		72.8		42		28-Sep-07		22:07:53		72.21		41		8-Nov-07		22:25:59		72.21		45.5

		29-Sep-07		0:07:10		75.2		36.5		29-Sep-07		0:06:20		72.21		42		29-Sep-07		0:07:53		71.6		42		9-Nov-07		0:25:59		71		44.5

		29-Sep-07		2:07:10		75.2		37		29-Sep-07		2:06:20		72.8		42		29-Sep-07		2:07:53		71		42.5		9-Nov-07		2:25:59		69.8		44.5

		29-Sep-07		4:07:10		75.2		37		29-Sep-07		4:06:20		72.8		41		29-Sep-07		4:07:53		71		42.5		9-Nov-07		4:25:59		69.2		45

		29-Sep-07		6:07:10		75.2		35		29-Sep-07		6:06:20		72.8		35		29-Sep-07		6:07:53		69.8		45.5		9-Nov-07		6:25:59		69.2		46.5

		29-Sep-07		8:07:10		74.6		39		29-Sep-07		8:06:20		71.6		42		29-Sep-07		8:07:53		71		45.5		9-Nov-07		8:25:59		71		45

		29-Sep-07		10:07:10		74.01		40.5		29-Sep-07		10:06:20		71		42		29-Sep-07		10:07:53		71.6		46		9-Nov-07		10:25:59		71		46

		29-Sep-07		12:07:10		74.6		39		29-Sep-07		12:06:20		71.6		38.5		29-Sep-07		12:07:53		71.6		48.5		9-Nov-07		12:25:59		72.21		47

		29-Sep-07		14:07:10		74.01		45		29-Sep-07		14:06:20		71.6		54		29-Sep-07		14:07:53		71.6		47		9-Nov-07		14:25:59		74.01		44.5

		29-Sep-07		16:07:10		74.6		42		29-Sep-07		16:06:20		71.6		48.5		29-Sep-07		16:07:53		71.6		52		9-Nov-07		16:25:59		74.01		44.5

		29-Sep-07		18:07:10		74.6		43.5		29-Sep-07		18:06:20		70.41		53		29-Sep-07		18:07:53		71		52		9-Nov-07		18:25:59		74.01		43.5

		29-Sep-07		20:07:10		75.2		36		29-Sep-07		20:06:20		72.21		38		29-Sep-07		20:07:53		70.41		42		9-Nov-07		20:25:59		73.4		43

		29-Sep-07		22:07:10		75.2		32.5		29-Sep-07		22:06:20		72.8		35		29-Sep-07		22:07:53		71		36.5		9-Nov-07		22:25:59		72.21		45

		30-Sep-07		0:07:10		75.2		31		30-Sep-07		0:06:20		73.4		33.5		30-Sep-07		0:07:53		70.41		35.5		10-Nov-07		0:25:59		71		45

		30-Sep-07		2:07:10		74.6		30.5		30-Sep-07		2:06:20		72.8		32.5		30-Sep-07		2:07:53		69.8		34.5		10-Nov-07		2:25:59		69.8		45.5

		30-Sep-07		4:07:10		74.01		30		30-Sep-07		4:06:20		71.6		32.5		30-Sep-07		4:07:53		68.61		34.5		10-Nov-07		4:25:59		69.2		46

		30-Sep-07		6:07:10		73.4		29.5		30-Sep-07		6:06:20		72.21		32.5		30-Sep-07		6:07:53		68		34.5		10-Nov-07		6:25:59		69.2		45.5

		30-Sep-07		8:07:10		72.21		30.5		30-Sep-07		8:06:20		71		34		30-Sep-07		8:07:53		68		34.5		10-Nov-07		8:25:59		71		42.5

		30-Sep-07		10:07:10		72.8		31		30-Sep-07		10:06:20		71.6		34.5		30-Sep-07		10:07:53		70.41		34.5		10-Nov-07		10:25:59		73.4		43

		30-Sep-07		12:07:10		73.4		31		30-Sep-07		12:06:20		71		33.5		30-Sep-07		12:07:53		70.41		32		10-Nov-07		12:25:59		74.01		43

		30-Sep-07		14:07:10		73.4		29		30-Sep-07		14:06:20		70.41		31.5		30-Sep-07		14:07:53		71		31		10-Nov-07		14:25:59		74.6		42

		30-Sep-07		16:07:10		74.01		30		30-Sep-07		16:06:20		69.8		34.5		30-Sep-07		16:07:53		71		31		10-Nov-07		16:25:59		75.2		43

		30-Sep-07		18:07:10		74.01		29		30-Sep-07		18:06:20		69.8		32.5		30-Sep-07		18:07:53		71		31		10-Nov-07		18:25:59		74.6		44

		30-Sep-07		20:07:10		75.2		28		30-Sep-07		20:06:20		72.21		31		30-Sep-07		20:07:53		71.6		32		10-Nov-07		20:25:59		72.8		44.5

		30-Sep-07		22:07:10		75.81		27.5		30-Sep-07		22:06:20		72.8		31		30-Sep-07		22:07:53		71.6		31.5		10-Nov-07		22:25:59		72.21		45.5

		1-Oct-07		0:07:10		75.2		27		1-Oct-07		0:06:20		72.8		30		1-Oct-07		0:07:53		70.41		32		11-Nov-07		0:25:59		70.41		44

		1-Oct-07		2:07:10		74.01		27.5		1-Oct-07		2:06:20		71.6		30.5		1-Oct-07		2:07:53		68.61		32		11-Nov-07		2:25:59		69.2		43

		1-Oct-07		4:07:10		72.8		27.5		1-Oct-07		4:06:20		70.41		30.5		1-Oct-07		4:07:53		68		32.5		11-Nov-07		4:25:59		68.61		43

		1-Oct-07		6:07:10		72.21		27.5		1-Oct-07		6:06:20		69.8		30		1-Oct-07		6:07:53		66.2		33		11-Nov-07		6:25:59		68		43.5

		1-Oct-07		8:07:10		71		28.5		1-Oct-07		8:06:20		68.61		31.5		1-Oct-07		8:07:53		68		32		11-Nov-07		8:25:59		68		44.5

		1-Oct-07		10:07:10		71.6		30		1-Oct-07		10:06:20		69.8		31.5		1-Oct-07		10:07:53		68.61		33.5		11-Nov-07		10:25:59		69.2		46.5

		1-Oct-07		12:07:10		72.21		30		1-Oct-07		12:06:20		70.41		32		1-Oct-07		12:07:53		70.41		33.5		11-Nov-07		12:25:59		69.2		49

		1-Oct-07		14:07:10		73.4		28.5		1-Oct-07		14:06:20		69.8		30		1-Oct-07		14:07:53		70.41		31.5		11-Nov-07		14:25:59		69.8		50.5

		1-Oct-07		16:07:10		73.4		27		1-Oct-07		16:06:20		69.8		29.5		1-Oct-07		16:07:53		70.41		30.5		11-Nov-07		16:25:59		69.8		52

		1-Oct-07		18:07:10		74.01		30		1-Oct-07		18:06:20		69.8		35.5		1-Oct-07		18:07:53		71		32		11-Nov-07		18:25:59		69.8		53

		1-Oct-07		20:07:10		75.81		33		1-Oct-07		20:06:20		72.8		38		1-Oct-07		20:07:53		72.21		37.5		11-Nov-07		20:25:59		69.2		54

		1-Oct-07		22:07:10		75.2		35.5		1-Oct-07		22:06:20		72.21		41		1-Oct-07		22:07:53		72.21		39.5		11-Nov-07		22:25:59		69.2		55

		2-Oct-07		0:07:10		75.2		35.5		2-Oct-07		0:06:20		72.8		41		2-Oct-07		0:07:53		71.6		41		12-Nov-07		0:25:59		69.2		55.5

		2-Oct-07		2:07:10		75.2		36.5		2-Oct-07		2:06:20		72.8		41		2-Oct-07		2:07:53		71		42.5		12-Nov-07		2:25:59		69.2		55.5

		2-Oct-07		4:07:10		75.2		40		2-Oct-07		4:06:20		72.8		46		2-Oct-07		4:07:53		71		46.5		12-Nov-07		4:25:59		69.2		54

		2-Oct-07		6:07:10		75.2		39		2-Oct-07		6:06:20		72.8		41		2-Oct-07		6:07:53		70.41		53.5		12-Nov-07		6:25:59		68.61		50.5

		2-Oct-07		8:07:10		74.6		44.5		2-Oct-07		8:06:20		71.6		46.5		2-Oct-07		8:07:53		71		51.5		12-Nov-07		8:25:59		68		47.5

		2-Oct-07		10:07:10		74.6		40.5		2-Oct-07		10:06:20		71.6		44.5		2-Oct-07		10:07:53		72.21		41		12-Nov-07		10:25:59		68		47.5

		2-Oct-07		12:07:10		74.6		44.5		2-Oct-07		12:06:20		71		47.5		2-Oct-07		12:07:53		72.21		51.5		12-Nov-07		12:25:59		69.2		46

		2-Oct-07		14:07:10		74.6		42		2-Oct-07		14:06:20		71.6		51		2-Oct-07		14:07:53		71.6		50		12-Nov-07		14:25:59		70.41		44

		2-Oct-07		16:07:10		75.2		38.5		2-Oct-07		16:06:20		71.6		46		2-Oct-07		16:07:53		71		46		12-Nov-07		16:25:59		71		42.5

		2-Oct-07		18:07:10		74.6		34		2-Oct-07		18:06:20		71		39.5		2-Oct-07		18:07:53		71		36		12-Nov-07		18:25:59		71		42.5

		2-Oct-07		20:07:10		75.81		37		2-Oct-07		20:06:20		72.8		41.5		2-Oct-07		20:07:53		70.41		44.5		12-Nov-07		20:25:59		69.8		42.5

		2-Oct-07		22:07:10		76.4		36.5		2-Oct-07		22:06:20		72.8		41.5		2-Oct-07		22:07:53		72.8		41		12-Nov-07		22:25:59		68.61		43

		3-Oct-07		0:07:10		75.81		35.5		3-Oct-07		0:06:20		72.8		40		3-Oct-07		0:07:53		72.21		40		13-Nov-07		0:25:59		68		42.5

		3-Oct-07		2:07:10		75.81		34.5		3-Oct-07		2:06:20		72.8		38		3-Oct-07		2:07:53		71		39.5		13-Nov-07		2:25:59		67.4		42.5

		3-Oct-07		4:07:10		74.6		34.5		3-Oct-07		4:06:20		71.6		38.5		3-Oct-07		4:07:53		69.8		39.5		13-Nov-07		4:25:59		67.4		42

		3-Oct-07		6:07:10		74.01		34.5		3-Oct-07		6:06:20		71.6		37.5		3-Oct-07		6:07:53		69.8		40		13-Nov-07		6:25:59		67.4		42.5

		3-Oct-07		8:07:10		73.4		36.5		3-Oct-07		8:06:20		71.6		42		3-Oct-07		8:07:53		71.6		39.5		13-Nov-07		8:25:59		71		40.5

		3-Oct-07		10:07:10		74.6		39		3-Oct-07		10:06:20		71.6		45		3-Oct-07		10:07:53		71.6		43.5		13-Nov-07		10:25:59		71		41

		3-Oct-07		12:07:10		74.6		38.5		3-Oct-07		12:06:20		71.6		37.5		3-Oct-07		12:07:53		72.21		43		13-Nov-07		12:25:59		74.6		39.5

		3-Oct-07		14:07:10		74.6		39		3-Oct-07		14:06:20		71.6		38		3-Oct-07		14:07:53		72.21		42		13-Nov-07		14:25:59		74.6		38.5

		3-Oct-07		16:07:10		74.6		37		3-Oct-07		16:06:20		71		41.5		3-Oct-07		16:07:53		71		42.5		13-Nov-07		16:25:59		75.2		37.5

		3-Oct-07		18:07:10		74.6		38.5		3-Oct-07		18:06:20		69.8		47.5		3-Oct-07		18:07:53		71		38		13-Nov-07		18:25:59		75.2		35.5

		3-Oct-07		20:07:10		75.81		37.5		3-Oct-07		20:06:20		72.8		43		3-Oct-07		20:07:53		71		44		13-Nov-07		20:25:59		73.4		38.5

		3-Oct-07		22:07:10		76.4		36.5		3-Oct-07		22:06:20		72.8		40		3-Oct-07		22:07:53		71.6		41.5		13-Nov-07		22:25:59		72.21		41

		4-Oct-07		0:07:10		75.81		35		4-Oct-07		0:06:20		72.8		39.5		4-Oct-07		0:07:53		71.6		40.5		14-Nov-07		0:25:59		71.6		43

		4-Oct-07		2:07:10		75.2		34.5		4-Oct-07		2:06:20		72.21		38.5		4-Oct-07		2:07:53		70.41		40.5		14-Nov-07		2:25:59		70.41		44.5

		4-Oct-07		4:07:10		74.01		34		4-Oct-07		4:06:20		71		38.5		4-Oct-07		4:07:53		69.2		40		14-Nov-07		4:25:59		69.8		45

		4-Oct-07		6:07:10		74.01		33.5		4-Oct-07		6:06:20		70.41		37		4-Oct-07		6:07:53		68.61		39.5		14-Nov-07		6:25:59		69.8		47

		4-Oct-07		8:07:10		74.01		34.5		4-Oct-07		8:06:20		71.6		39		4-Oct-07		8:07:53		70.41		38		14-Nov-07		8:25:59		73.4		46

		4-Oct-07		10:07:10		74.6		36		4-Oct-07		10:06:20		72.21		41		4-Oct-07		10:07:53		71.6		35.5		14-Nov-07		10:25:59		74.6		47

		4-Oct-07		12:07:10		76.4		36		4-Oct-07		12:06:20		72.21		41.5		4-Oct-07		12:07:53		71.6		45.5		14-Nov-07		12:25:59		74.6		48.5

		4-Oct-07		14:07:10		75.81		35		4-Oct-07		14:06:20		72.21		36		4-Oct-07		14:07:53		72.21		35.5		14-Nov-07		14:25:59		75.2		49.5

		4-Oct-07		16:07:10		76.4		38.5		4-Oct-07		16:06:20		71		41.5		4-Oct-07		16:07:53		71		49		14-Nov-07		16:25:59		75.2		49.5

		4-Oct-07		18:07:10		76.4		33.5		4-Oct-07		18:06:20		70.41		40		4-Oct-07		18:07:53		70.41		41		14-Nov-07		18:25:59		75.2		49.5

		4-Oct-07		20:07:10		76.4		34		4-Oct-07		20:06:20		72.8		38.5		4-Oct-07		20:07:53		72.8		37.5		14-Nov-07		20:25:59		74.6		49

		4-Oct-07		22:07:10		76.4		31.5		4-Oct-07		22:06:20		72.8		35.5		4-Oct-07		22:07:53		72.8		35		14-Nov-07		22:25:59		74.01		52

		5-Oct-07		0:07:10		75.81		30.5		5-Oct-07		0:06:20		72.8		34.5		5-Oct-07		0:07:53		72.21		34.5		15-Nov-07		0:25:59		72.8		50.5

		5-Oct-07		2:07:10		75.2		29		5-Oct-07		2:06:20		72.8		32.5		5-Oct-07		2:07:53		71		33.5		15-Nov-07		2:25:59		71.6		51

		5-Oct-07		4:07:10		74.6		28.5		5-Oct-07		4:06:20		72.8		31		5-Oct-07		4:07:53		69.8		32.5		15-Nov-07		4:25:59		71		50

		5-Oct-07		6:07:10		74.6		29		5-Oct-07		6:06:20		72.21		31.5		5-Oct-07		6:07:53		69.8		33.5		15-Nov-07		6:25:59		69.8		49

		5-Oct-07		8:07:10		74.01		30.5		5-Oct-07		8:06:20		71.6		33.5		5-Oct-07		8:07:53		71		34		15-Nov-07		8:25:59		72.8		44.5

		5-Oct-07		10:07:10		74.6		31.5		5-Oct-07		10:06:20		72.21		36.5		5-Oct-07		10:07:53		71.6		32.5		15-Nov-07		10:25:59		74.6		47

		5-Oct-07		12:07:10		75.2		32		5-Oct-07		12:06:20		71.6		34		5-Oct-07		12:07:53		71.6		33		15-Nov-07		12:25:59		74.6		48.5

		5-Oct-07		14:07:10		75.2		33		5-Oct-07		14:06:20		72.21		39.5		5-Oct-07		14:07:53		71.6		38.5		15-Nov-07		14:25:59		75.2		48

		5-Oct-07		16:07:10		75.81		32		5-Oct-07		16:06:20		70.41		39.5		5-Oct-07		16:07:53		71		35.5		15-Nov-07		16:25:59		75.2		49

		5-Oct-07		18:07:10		75.2		30		5-Oct-07		18:06:20		69.8		35		5-Oct-07		18:07:53		70.41		34.5		15-Nov-07		18:25:59		74.6		50

		5-Oct-07		20:07:10		75.81		29.5		5-Oct-07		20:06:20		72.21		33.5		5-Oct-07		20:07:53		70.41		34.5		15-Nov-07		20:25:59		74.01		50

		5-Oct-07		22:07:10		75.2		29.5		5-Oct-07		22:06:20		72.21		33.5		5-Oct-07		22:07:53		69.8		34.5		15-Nov-07		22:25:59		74.01		49.5

		6-Oct-07		0:07:10		75.2		29.5		6-Oct-07		0:06:20		72.21		33.5		6-Oct-07		0:07:53		69.2		35		16-Nov-07		0:25:59		72.21		49.5

		6-Oct-07		2:07:10		74.01		30		6-Oct-07		2:06:20		71.6		33.5		6-Oct-07		2:07:53		68		35.5		16-Nov-07		2:25:59		71		48.5

		6-Oct-07		4:07:10		72.8		29.5		6-Oct-07		4:06:20		70.41		33		6-Oct-07		4:07:53		66.81		36		16-Nov-07		4:25:59		69.8		48

		6-Oct-07		6:07:10		72.8		29		6-Oct-07		6:06:20		72.21		30		6-Oct-07		6:07:53		68		34.5		16-Nov-07		6:25:59		69.8		47

		6-Oct-07		8:07:10		72.8		29.5		6-Oct-07		8:06:20		71.6		34.5		6-Oct-07		8:07:53		69.2		33		16-Nov-07		8:25:59		72.8		42.5

		6-Oct-07		10:07:10		73.4		30.5		6-Oct-07		10:06:20		71.6		33.5		6-Oct-07		10:07:53		71.6		31		16-Nov-07		10:25:59		74.01		44

		6-Oct-07		12:07:10		74.01		30.5		6-Oct-07		12:06:20		70.41		36		6-Oct-07		12:07:53		71.6		34.5		16-Nov-07		12:25:59		74.6		47

		6-Oct-07		14:07:10		75.2		28		6-Oct-07		14:06:20		69.2		32.5		6-Oct-07		14:07:53		71		30.5		16-Nov-07		14:25:59		74.6		49.5

		6-Oct-07		16:07:10		75.2		27		6-Oct-07		16:06:20		69.2		31.5		6-Oct-07		16:07:53		70.41		31.5		16-Nov-07		16:25:59		75.81		49.5

		6-Oct-07		18:07:10		75.81		27.5		6-Oct-07		18:06:20		69.2		33		6-Oct-07		18:07:53		71		30		16-Nov-07		18:25:59		75.81		49.5

		6-Oct-07		20:07:10		76.4		27.5		6-Oct-07		20:06:20		72.21		31.5		6-Oct-07		20:07:53		70.41		33.5		16-Nov-07		20:25:59		74.01		50

		6-Oct-07		22:07:10		75.81		27		6-Oct-07		22:06:20		73.4		31.5		6-Oct-07		22:07:53		70.41		33		16-Nov-07		22:25:59		73.4		51.5

		7-Oct-07		0:07:10		75.2		27		7-Oct-07		0:06:20		72.8		30.5		7-Oct-07		0:07:53		69.8		32.5		17-Nov-07		0:25:59		72.21		51

		7-Oct-07		2:07:10		74.6		27		7-Oct-07		2:06:20		72.21		31		7-Oct-07		2:07:53		68.61		33		17-Nov-07		2:25:59		71		51.5

		7-Oct-07		4:07:10		74.01		28		7-Oct-07		4:06:20		71.6		31.5		7-Oct-07		4:07:53		68		34		17-Nov-07		4:25:59		70.41		51.5

		7-Oct-07		6:07:10		72.8		28.5		7-Oct-07		6:06:20		71		32		7-Oct-07		6:07:53		66.81		35		17-Nov-07		6:25:59		70.41		52

		7-Oct-07		8:07:10		72.21		29		7-Oct-07		8:06:20		69.2		32.5		7-Oct-07		8:07:53		67.4		34		17-Nov-07		8:25:59		71		50.5

		7-Oct-07		10:07:10		71.6		31		7-Oct-07		10:06:20		68.61		34.5		7-Oct-07		10:07:53		68.61		35		17-Nov-07		10:25:59		71.6		50.5

		7-Oct-07		12:07:10		72.21		29		7-Oct-07		12:06:20		68.61		31		7-Oct-07		12:07:53		70.41		31.5		17-Nov-07		12:25:59		72.8		50

		7-Oct-07		14:07:10		72.8		26.5		7-Oct-07		14:06:20		69.2		28.5		7-Oct-07		14:07:53		70.41		29		17-Nov-07		14:25:59		75.2		49.5

		7-Oct-07		16:07:10		73.4		27		7-Oct-07		16:06:20		69.2		31		7-Oct-07		16:07:53		70.41		30.5		17-Nov-07		16:25:59		75.2		48

		7-Oct-07		18:07:10		74.01		26		7-Oct-07		18:06:20		69.8		29.5		7-Oct-07		18:07:53		71		29		17-Nov-07		18:25:59		74.6		49

		7-Oct-07		20:07:10		75.2		25		7-Oct-07		20:06:20		72.21		28.5		7-Oct-07		20:07:53		71		29		17-Nov-07		20:25:59		72.8		48.5

		7-Oct-07		22:07:10		75.2		26.5		7-Oct-07		22:06:20		72.8		31		7-Oct-07		22:07:53		70.41		31.5		17-Nov-07		22:25:59		72.21		49

		8-Oct-07		0:07:10		74.6		26.5		8-Oct-07		0:06:20		72.21		30.5		8-Oct-07		0:07:53		69.2		31.5		18-Nov-07		0:25:59		71		52

		8-Oct-07		2:07:10		73.4		25.5		8-Oct-07		2:06:20		71		29		8-Oct-07		2:07:53		68		31		18-Nov-07		2:25:59		70.41		51

		8-Oct-07		4:07:10		72.8		26		8-Oct-07		4:06:20		69.8		29		8-Oct-07		4:07:53		66.81		31.5		18-Nov-07		4:25:59		69.8		50.5

		8-Oct-07		6:07:10		71.6		26		8-Oct-07		6:06:20		69.2		29.5		8-Oct-07		6:07:53		65.6		32		18-Nov-07		6:25:59		69.2		51

		8-Oct-07		8:07:10		71		27		8-Oct-07		8:06:20		68.61		30		8-Oct-07		8:07:53		67.4		31		18-Nov-07		8:25:59		68.61		50.5

		8-Oct-07		10:07:10		71.6		28.5		8-Oct-07		10:06:20		68.61		32		8-Oct-07		10:07:53		68		32.5		18-Nov-07		10:25:59		68.61		51

		8-Oct-07		12:07:10		72.21		29.5		8-Oct-07		12:06:20		69.2		33		8-Oct-07		12:07:53		69.8		33		18-Nov-07		12:25:59		69.2		51.5

		8-Oct-07		14:07:10		72.8		31		8-Oct-07		14:06:20		69.2		34.5		8-Oct-07		14:07:53		70.41		34.5		18-Nov-07		14:25:59		69.8		52

		8-Oct-07		16:07:10		73.4		30.5		8-Oct-07		16:06:20		69.2		35.5		8-Oct-07		16:07:53		70.41		35.5		18-Nov-07		16:25:59		71.6		54

		8-Oct-07		18:07:10		74.01		31.5		8-Oct-07		18:06:20		69.2		35		8-Oct-07		18:07:53		71		34		18-Nov-07		18:25:59		72.21		54

		8-Oct-07		20:07:10		75.2		33.5		8-Oct-07		20:06:20		72.21		36		8-Oct-07		20:07:53		71.6		38.5		18-Nov-07		20:25:59		71		53

		8-Oct-07		22:07:10		75.2		34.5		8-Oct-07		22:06:20		72.21		39.5		8-Oct-07		22:07:53		71		40		18-Nov-07		22:25:59		69.8		53

		9-Oct-07		0:07:10		74.6		34		9-Oct-07		0:06:20		72.21		38.5		9-Oct-07		0:07:53		69.8		40		19-Nov-07		0:25:59		69.2		53

		9-Oct-07		2:07:10		74.01		33.5		9-Oct-07		2:06:20		71.6		37.5		9-Oct-07		2:07:53		68.61		40		19-Nov-07		2:25:59		69.2		53

		9-Oct-07		4:07:10		73.4		33		9-Oct-07		4:06:20		71		36.5		9-Oct-07		4:07:53		67.4		39.5		19-Nov-07		4:25:59		68.61		53

		9-Oct-07		6:07:10		73.4		32.5		9-Oct-07		6:06:20		69.8		36		9-Oct-07		6:07:53		68.61		37.5		19-Nov-07		6:25:59		68.61		53

		9-Oct-07		8:07:10		72.8		33.5		9-Oct-07		8:06:20		69.8		38.5		9-Oct-07		8:07:53		70.41		36		19-Nov-07		8:25:59		68		53

		9-Oct-07		10:07:10		73.4		37.5		9-Oct-07		10:06:20		71		45		9-Oct-07		10:07:53		71.6		37		19-Nov-07		10:25:59		68.61		53

		9-Oct-07		12:07:10		74.6		35.5		9-Oct-07		12:06:20		71		41		9-Oct-07		12:07:53		71.6		42		19-Nov-07		12:25:59		68.61		55

		9-Oct-07		14:07:10		74.6		36		9-Oct-07		14:06:20		71		41		9-Oct-07		14:07:53		71.6		38.5		19-Nov-07		14:25:59		69.8		56

		9-Oct-07		16:07:10		75.2		34		9-Oct-07		16:06:20		69.8		42		9-Oct-07		16:07:53		71.6		37		19-Nov-07		16:25:59		71		57.5

		9-Oct-07		18:07:10		74.01		36.5		9-Oct-07		18:06:20		69.2		44.5		9-Oct-07		18:07:53		71		41.5		19-Nov-07		18:25:59		71.6		56.5

		9-Oct-07		20:07:10		75.81		32		9-Oct-07		20:06:20		72.8		35.5		9-Oct-07		20:07:53		71		37.5		19-Nov-07		20:25:59		71		55

		9-Oct-07		22:07:10		76.4		33.5		9-Oct-07		22:06:20		73.4		38.5		9-Oct-07		22:07:53		71.6		39		19-Nov-07		22:25:59		70.41		54.5

		10-Oct-07		0:07:10		75.81		34.5		10-Oct-07		0:06:20		72.8		39.5		10-Oct-07		0:07:53		70.41		41		20-Nov-07		0:25:59		69.2		53.5

		10-Oct-07		2:07:10		75.2		35.5		10-Oct-07		2:06:20		72.21		40.5		10-Oct-07		2:07:53		69.8		42		20-Nov-07		2:25:59		68.61		52.5

		10-Oct-07		4:07:10		74.6		36		10-Oct-07		4:06:20		72.21		40.5		10-Oct-07		4:07:53		69.2		43		20-Nov-07		4:25:59		68		53

		10-Oct-07		6:07:10		74.6		37.5		10-Oct-07		6:06:20		71		44.5		10-Oct-07		6:07:53		69.2		45		20-Nov-07		6:25:59		68.61		54.5

		10-Oct-07		8:07:10		74.01		39		10-Oct-07		8:06:20		71		38.5		10-Oct-07		8:07:53		71.6		44		20-Nov-07		8:25:59		71.6		54

		10-Oct-07		10:07:10		74.01		43		10-Oct-07		10:06:20		69.8		48.5		10-Oct-07		10:07:53		71		44		20-Nov-07		10:25:59		74.01		55

		10-Oct-07		12:07:10		74.6		42.5		10-Oct-07		12:06:20		70.41		48.5		10-Oct-07		12:07:53		71.6		43		20-Nov-07		12:25:59		74.01		53.5

		10-Oct-07		14:07:10		74.6		44.5		10-Oct-07		14:06:20		71		50.5		10-Oct-07		14:07:53		71		51.5		20-Nov-07		14:25:59		73.4		48.5

		10-Oct-07		16:07:10		74.6		42		10-Oct-07		16:06:20		69.8		57		10-Oct-07		16:07:53		70.41		49		20-Nov-07		16:25:59		74.01		45

		10-Oct-07		18:07:10		74.01		41		10-Oct-07		18:06:20		69.8		51		10-Oct-07		18:07:53		70.41		48		20-Nov-07		18:25:59		74.01		43

		10-Oct-07		20:07:10		75.2		41		10-Oct-07		20:06:20		72.21		47		10-Oct-07		20:07:53		69.8		50		20-Nov-07		20:25:59		72.21		43

		10-Oct-07		22:07:10		75.2		43		10-Oct-07		22:06:20		72.21		50.5		10-Oct-07		22:07:53		69.8		50		20-Nov-07		22:25:59		71		44.5

		11-Oct-07		0:07:10		74.6		44		11-Oct-07		0:06:20		72.21		51		11-Oct-07		0:07:53		69.8		51		21-Nov-07		0:25:59		69.8		44

		11-Oct-07		2:07:10		74.6		44		11-Oct-07		2:06:20		71.6		50.5		11-Oct-07		2:07:53		69.2		51		21-Nov-07		2:25:59		68.61		43

		11-Oct-07		4:07:10		74.01		44		11-Oct-07		4:06:20		71.6		49.5		11-Oct-07		4:07:53		69.2		51.5		21-Nov-07		4:25:59		68		42.5

		11-Oct-07		6:07:10		74.01		44		11-Oct-07		6:06:20		71		50.5		11-Oct-07		6:07:53		69.2		51		21-Nov-07		6:25:59		68		41

		11-Oct-07		8:07:10		73.4		44.5		11-Oct-07		8:06:20		70.41		45		11-Oct-07		8:07:53		71		49		21-Nov-07		8:25:59		71.6		37

		11-Oct-07		10:07:10		73.4		43		11-Oct-07		10:06:20		71.6		45		11-Oct-07		10:07:53		71		48		21-Nov-07		10:25:59		71.6		38

		11-Oct-07		12:07:10		74.01		46		11-Oct-07		12:06:20		70.41		51		11-Oct-07		12:07:53		71.6		49		21-Nov-07		12:25:59		72.21		38.5

		11-Oct-07		14:07:10		74.6		41.5		11-Oct-07		14:06:20		71		41		11-Oct-07		14:07:53		71		49.5		21-Nov-07		14:25:59		72.8		37.5

		11-Oct-07		16:07:10		75.2		46.5		11-Oct-07		16:06:20		69.2		59.5		11-Oct-07		16:07:53		70.41		53		21-Nov-07		16:25:59		73.4		37

		11-Oct-07		18:07:10		74.6		39.5		11-Oct-07		18:06:20		69.8		45		11-Oct-07		18:07:53		70.41		47		21-Nov-07		18:25:59		73.4		38

		11-Oct-07		20:07:10		75.2		40		11-Oct-07		20:06:20		72.21		45		11-Oct-07		20:07:53		70.41		46		21-Nov-07		20:25:59		71.6		38

		11-Oct-07		22:07:10		74.6		39.5		11-Oct-07		22:06:20		72.21		44		11-Oct-07		22:07:53		69.8		45.5		21-Nov-07		22:25:59		69.8		38.5

		12-Oct-07		0:07:10		74.01		38.5		12-Oct-07		0:06:20		72.21		42.5		12-Oct-07		0:07:53		68.61		45		22-Nov-07		0:25:59		68.61		38.5

		12-Oct-07		2:07:10		73.4		38		12-Oct-07		2:06:20		71.6		42		12-Oct-07		2:07:53		67.4		45.5		22-Nov-07		2:25:59		67.4		37.5

		12-Oct-07		4:07:10		72.21		38.5		12-Oct-07		4:06:20		71		42.5		12-Oct-07		4:07:53		66.81		46.5		22-Nov-07		4:25:59		66.81		36.5

		12-Oct-07		6:07:10		72.21		38		12-Oct-07		6:06:20		70.41		41.5		12-Oct-07		6:07:53		68.61		44		22-Nov-07		6:25:59		67.4		35

		12-Oct-07		8:07:10		72.21		38		12-Oct-07		8:06:20		70.41		43.5		12-Oct-07		8:07:53		69.8		42		22-Nov-07		8:25:59		70.41		32.5

		12-Oct-07		10:07:10		72.8		43.5		12-Oct-07		10:06:20		71		51.5		12-Oct-07		10:07:53		71.6		40		22-Nov-07		10:25:59		71.6		33.5

		12-Oct-07		12:07:10		73.4		40.5		12-Oct-07		12:06:20		70.41		45.5		12-Oct-07		12:07:53		71.6		49		22-Nov-07		12:25:59		72.21		35

		12-Oct-07		14:07:10		73.4		43.5		12-Oct-07		14:06:20		69.8		41		12-Oct-07		14:07:53		71		44.5		22-Nov-07		14:25:59		73.4		34

		12-Oct-07		16:07:10		74.01		45		12-Oct-07		16:06:20		69.2		56.5		12-Oct-07		16:07:53		71		46.5		22-Nov-07		16:25:59		72.8		32.5

		12-Oct-07		18:07:10		74.01		39.5		12-Oct-07		18:06:20		69.8		46.5		12-Oct-07		18:07:53		70.41		44.5		22-Nov-07		18:25:59		72.8		34.5

		12-Oct-07		20:07:10		74.6		38.5		12-Oct-07		20:06:20		72.21		42		12-Oct-07		20:07:53		70.41		44		22-Nov-07		20:25:59		71		34

		12-Oct-07		22:07:10		75.2		37		12-Oct-07		22:06:20		72.8		40.5		12-Oct-07		22:07:53		69.8		43.5		22-Nov-07		22:25:59		69.2		35

		13-Oct-07		0:07:10		74.6		36.5		13-Oct-07		0:06:20		72.21		40		13-Oct-07		0:07:53		68.61		44		23-Nov-07		0:25:59		68		35

		13-Oct-07		2:07:10		74.01		38		13-Oct-07		2:06:20		72.21		42		13-Oct-07		2:07:53		68		46		23-Nov-07		2:25:59		66.81		34.5

		13-Oct-07		4:07:10		74.01		39.5		13-Oct-07		4:06:20		72.21		44		13-Oct-07		4:07:53		67.4		48.5		23-Nov-07		4:25:59		66.2		34

		13-Oct-07		6:07:10		73.4		40		13-Oct-07		6:06:20		71		46		13-Oct-07		6:07:53		68.61		48		23-Nov-07		6:25:59		66.81		32.5

		13-Oct-07		8:07:10		72.8		44		13-Oct-07		8:06:20		71		45		13-Oct-07		8:07:53		70.41		48.5		23-Nov-07		8:25:59		69.2		30.5

		13-Oct-07		10:07:10		72.8		44		13-Oct-07		10:06:20		71		43		13-Oct-07		10:07:53		71		50		23-Nov-07		10:25:59		71.6		31

		13-Oct-07		12:07:10		73.4		44		13-Oct-07		12:06:20		70.41		54.5		13-Oct-07		12:07:53		71.6		52		23-Nov-07		12:25:59		70.41		33

		13-Oct-07		14:07:10		73.4		46.5		13-Oct-07		14:06:20		70.41		51		13-Oct-07		14:07:53		71		50		23-Nov-07		14:25:59		71		33.5

		13-Oct-07		16:07:10		72.8		49.5		13-Oct-07		16:06:20		69.2		61		13-Oct-07		16:07:53		71		53		23-Nov-07		16:25:59		71		32.5

		13-Oct-07		18:07:10		72.8		44		13-Oct-07		18:06:20		69.8		50		13-Oct-07		18:07:53		70.41		50.5		23-Nov-07		18:25:59		71		34

		13-Oct-07		20:07:10		73.4		43.5		13-Oct-07		20:06:20		71		48		13-Oct-07		20:07:53		69.8		48.5		23-Nov-07		20:25:59		70.41		34.5

		13-Oct-07		22:07:10		73.4		42.5		13-Oct-07		22:06:20		71.6		46.5		13-Oct-07		22:07:53		68.61		49		23-Nov-07		22:25:59		68.61		34.5

		14-Oct-07		0:07:10		72.21		41.5		14-Oct-07		0:06:20		71		45		14-Oct-07		0:07:53		67.4		49		24-Nov-07		0:25:59		67.4		34.5

		14-Oct-07		2:07:10		71.6		40.5		14-Oct-07		2:06:20		69.8		43.5		14-Oct-07		2:07:53		66.2		48		24-Nov-07		2:25:59		66.81		34

		14-Oct-07		4:07:10		71		40		14-Oct-07		4:06:20		69.2		42.5		14-Oct-07		4:07:53		65.6		47.5		24-Nov-07		4:25:59		66.2		33.5

		14-Oct-07		6:07:10		70.41		39		14-Oct-07		6:06:20		68.61		41		14-Oct-07		6:07:53		65.6		46		24-Nov-07		6:25:59		66.81		32.5

		14-Oct-07		8:07:10		71		37.5		14-Oct-07		8:06:20		68.61		40.5		14-Oct-07		8:07:53		67.4		41.5		24-Nov-07		8:25:59		68.61		29.5

		14-Oct-07		10:07:10		71.6		43.5		14-Oct-07		10:06:20		68.61		49		14-Oct-07		10:07:53		68.61		48.5		24-Nov-07		10:25:59		70.41		25.5

		14-Oct-07		12:07:10		72.21		46		14-Oct-07		12:06:20		68.61		49.5		14-Oct-07		12:07:53		69.8		49.5		24-Nov-07		12:25:59		69.8		24

		14-Oct-07		14:07:10		72.8		47		14-Oct-07		14:06:20		69.2		54		14-Oct-07		14:07:53		70.41		50		24-Nov-07		14:25:59		70.41		23

		14-Oct-07		16:07:10		72.8		45.5		14-Oct-07		16:06:20		69.2		45.5		14-Oct-07		16:07:53		70.41		45.5		24-Nov-07		16:25:59		71.6		22.5

		14-Oct-07		18:07:10		73.4		46		14-Oct-07		18:06:20		69.2		53.5		14-Oct-07		18:07:53		70.41		52.5		24-Nov-07		18:25:59		71		22.5

		14-Oct-07		20:07:10		74.6		44.5		14-Oct-07		20:06:20		71.6		49		14-Oct-07		20:07:53		69.8		50.5		24-Nov-07		20:25:59		69.8		24.5

		14-Oct-07		22:07:10		74.01		43		14-Oct-07		22:06:20		72.21		47		14-Oct-07		22:07:53		69.2		50		24-Nov-07		22:25:59		68.61		27

		15-Oct-07		0:07:10		74.01		43		15-Oct-07		0:06:20		72.21		47		15-Oct-07		0:07:53		68.61		51.5		25-Nov-07		0:25:59		67.4		28

		15-Oct-07		2:07:10		74.01		43.5		15-Oct-07		2:06:20		72.21		47		15-Oct-07		2:07:53		68		52		25-Nov-07		2:25:59		66.81		28.5

		15-Oct-07		4:07:10		73.4		43.5		15-Oct-07		4:06:20		71.6		47		15-Oct-07		4:07:53		67.4		52		25-Nov-07		4:25:59		66.2		28.5

		15-Oct-07		6:07:10		72.8		43.5		15-Oct-07		6:06:20		71		43		15-Oct-07		6:07:53		66.81		52.5		25-Nov-07		6:25:59		65.6		28.5

		15-Oct-07		8:07:10		71.6		45		15-Oct-07		8:06:20		69.2		50		15-Oct-07		8:07:53		68.61		49.5		25-Nov-07		8:25:59		65.6		28

		15-Oct-07		10:07:10		71		46.5		15-Oct-07		10:06:20		68.61		52		15-Oct-07		10:07:53		68		52		25-Nov-07		10:25:59		65.6		29

		15-Oct-07		12:07:10		71		46		15-Oct-07		12:06:20		69.2		52		15-Oct-07		12:07:53		68		53		25-Nov-07		12:25:59		66.2		30.5

		15-Oct-07		14:07:10		71.6		48		15-Oct-07		14:06:20		69.2		45		15-Oct-07		14:07:53		69.2		53		25-Nov-07		14:25:59		68		30

		15-Oct-07		16:07:10		72.21		49.5		15-Oct-07		16:06:20		69.2		49.5		15-Oct-07		16:07:53		69.8		53.5		25-Nov-07		16:25:59		68		30.5

		15-Oct-07		18:07:10		72.8		48		15-Oct-07		18:06:20		69.2		54.5		15-Oct-07		18:07:53		69.8		53.5		25-Nov-07		18:25:59		68		31.5

		15-Oct-07		20:07:10		74.01		44		15-Oct-07		20:06:20		71.6		48		15-Oct-07		20:07:53		69.8		50		25-Nov-07		20:25:59		67.4		32

		15-Oct-07		22:07:10		73.4		42.5		15-Oct-07		22:06:20		71.6		45.5		15-Oct-07		22:07:53		68		50		25-Nov-07		22:25:59		66.81		33

		16-Oct-07		0:07:10		72.8		42		16-Oct-07		0:06:20		71		45.5		16-Oct-07		0:07:53		66.81		50.5		26-Nov-07		0:25:59		66.81		33.5

		16-Oct-07		2:07:10		72.21		42		16-Oct-07		2:06:20		71		45.5		16-Oct-07		2:07:53		66.2		51		26-Nov-07		2:25:59		66.2		33.5

		16-Oct-07		4:07:10		72.21		42.5		16-Oct-07		4:06:20		70.41		46		16-Oct-07		4:07:53		65.6		51.5		26-Nov-07		4:25:59		66.2		34

		16-Oct-07		6:07:10		72.21		43		16-Oct-07		6:06:20		70.41		46.5		16-Oct-07		6:07:53		68.61		48.5		26-Nov-07		6:25:59		66.2		34

		16-Oct-07		8:07:10		72.21		45.5		16-Oct-07		8:06:20		70.41		51.5		16-Oct-07		8:07:53		68.61		49.5		26-Nov-07		8:25:59		65.6		34.5

		16-Oct-07		10:07:10		72.8		45.5		16-Oct-07		10:06:20		71.6		54.5		16-Oct-07		10:07:53		71		49.5		26-Nov-07		10:25:59		65.6		35.5

		16-Oct-07		12:07:10		72.8		48.5		16-Oct-07		12:06:20		69.8		44.5		16-Oct-07		12:07:53		71.6		53		26-Nov-07		12:25:59		66.2		36.5

		16-Oct-07		14:07:10		72.8		53		16-Oct-07		14:06:20		71		54		16-Oct-07		14:07:53		71		57.5		26-Nov-07		14:25:59		66.2		35.5

		16-Oct-07		16:07:10		74.01		48.5		16-Oct-07		16:06:20		69.8		59.5		16-Oct-07		16:07:53		70.41		55.5		26-Nov-07		16:25:59		66.81		35

		16-Oct-07		18:07:10		73.4		47.5		16-Oct-07		18:06:20		70.41		57.5		16-Oct-07		18:07:53		69.8		54.5		26-Nov-07		18:25:59		67.4		35.5

		16-Oct-07		20:07:10		74.6		48		16-Oct-07		20:06:20		72.21		53		16-Oct-07		20:07:53		70.41		54.5		26-Nov-07		20:25:59		66.81		36

		16-Oct-07		22:07:10		74.6		47		16-Oct-07		22:06:20		72.21		51		16-Oct-07		22:07:53		69.8		54		26-Nov-07		22:25:59		66.2		35.5

		17-Oct-07		0:07:10		74.01		45		17-Oct-07		0:06:20		72.8		48.5		17-Oct-07		0:07:53		69.2		52.5		27-Nov-07		0:25:59		65.6		35.5

		17-Oct-07		2:07:10		73.4		43		17-Oct-07		2:06:20		71.6		45.5		17-Oct-07		2:07:53		68		51		27-Nov-07		2:25:59		65.6		34.5

		17-Oct-07		4:07:10		72.8		42.5		17-Oct-07		4:06:20		71		45		17-Oct-07		4:07:53		66.81		50.5		27-Nov-07		4:25:59		65.01		34

		17-Oct-07		6:07:10		72.8		43		17-Oct-07		6:06:20		70.41		44.5		17-Oct-07		6:07:53		68		49		27-Nov-07		6:25:59		66.2		32.5

		17-Oct-07		8:07:10		71.6		43.5		17-Oct-07		8:06:20		69.8		48		17-Oct-07		8:07:53		69.8		46		27-Nov-07		8:25:59		68.61		30.5

		17-Oct-07		10:07:10		72.8		43.5		17-Oct-07		10:06:20		71		52.5		17-Oct-07		10:07:53		71		46		27-Nov-07		10:25:59		70.41		32.5

		17-Oct-07		12:07:10		73.4		46		17-Oct-07		12:06:20		71		55.5		17-Oct-07		12:07:53		71.6		46		27-Nov-07		12:25:59		72.21		33.5

		17-Oct-07		14:07:10		73.4		47		17-Oct-07		14:06:20		71		41		17-Oct-07		14:07:53		71		52.5		27-Nov-07		14:25:59		72.8		34.5

		17-Oct-07		16:07:10		72.8		53		17-Oct-07		16:06:20		69.2		55.5		17-Oct-07		16:07:53		70.41		60.5		27-Nov-07		16:25:59		73.4		35.5

		17-Oct-07		18:07:10		72.8		52		17-Oct-07		18:06:20		69.2		60		17-Oct-07		18:07:53		69.8		55.5		27-Nov-07		18:25:59		72.8		37

		17-Oct-07		20:07:10		72.8		46.5		17-Oct-07		20:06:20		71		49.5		17-Oct-07		20:07:53		69.8		51.5		27-Nov-07		20:25:59		71		37

		17-Oct-07		22:07:10		72.21		44		17-Oct-07		22:06:20		71		46.5		17-Oct-07		22:07:53		68		49.5		27-Nov-07		22:25:59		69.8		36.5

		18-Oct-07		0:07:10		71		42		18-Oct-07		0:06:20		69.8		44		18-Oct-07		0:07:53		66.81		48.5		28-Nov-07		0:25:59		68.61		36.5

		18-Oct-07		2:07:10		70.41		41		18-Oct-07		2:06:20		69.2		43		18-Oct-07		2:07:53		66.2		47.5		28-Nov-07		2:25:59		67.4		36.5

		18-Oct-07		4:07:10		70.41		41.5		18-Oct-07		4:06:20		69.2		44		18-Oct-07		4:07:53		66.2		48.5		28-Nov-07		4:25:59		66.81		36.5

		18-Oct-07		6:07:10		71		43.5		18-Oct-07		6:06:20		69.8		46		18-Oct-07		6:07:53		68		48		28-Nov-07		6:25:59		67.4		36

		18-Oct-07		8:07:10		71.6		44.5		18-Oct-07		8:06:20		71		49.5		18-Oct-07		8:07:53		69.8		46		28-Nov-07		8:25:59		69.8		35

		18-Oct-07		10:07:10		74.01		45.5		18-Oct-07		10:06:20		74.01		41.5		18-Oct-07		10:07:53		71		51.5		28-Nov-07		10:25:59		73.4		36

		18-Oct-07		12:07:10		74.6		44		18-Oct-07		12:06:20		73.4		46.5		18-Oct-07		12:07:53		71.6		50.5		28-Nov-07		12:25:59		72.8		38.5

		18-Oct-07		14:07:10		75.2		41.5		18-Oct-07		14:06:20		74.6		37.5		18-Oct-07		14:07:53		71.6		45		28-Nov-07		14:25:59		73.4		35

		18-Oct-07		16:07:10		75.2		41		18-Oct-07		16:06:20		72.21		41.5		18-Oct-07		16:07:53		70.41		47		28-Nov-07		16:25:59		74.01		34

		18-Oct-07		18:07:10		74.6		41.5		18-Oct-07		18:06:20		71.6		42.5		18-Oct-07		18:07:53		70.41		48.5		28-Nov-07		18:25:59		74.01		35.5

		18-Oct-07		20:07:10		74.6		41		18-Oct-07		20:06:20		72.8		44		18-Oct-07		20:07:53		69.8		47		28-Nov-07		20:25:59		72.21		37

		18-Oct-07		22:07:10		73.4		40.5		18-Oct-07		22:06:20		72.21		43		18-Oct-07		22:07:53		68.61		47.5		28-Nov-07		22:25:59		71		37

		19-Oct-07		0:07:10		72.8		41		19-Oct-07		0:06:20		72.21		43.5		19-Oct-07		0:07:53		67.4		48.5		29-Nov-07		0:25:59		69.8		37

		19-Oct-07		2:07:10		72.21		41.5		19-Oct-07		2:06:20		71		43.5		19-Oct-07		2:07:53		66.81		49.5		29-Nov-07		2:25:59		68.61		37

		19-Oct-07		4:07:10		71.6		42.5		19-Oct-07		4:06:20		71		44.5		19-Oct-07		4:07:53		66.2		52		29-Nov-07		4:25:59		67.4		36.5

		19-Oct-07		6:07:10		71.6		43		19-Oct-07		6:06:20		71		45.5		19-Oct-07		6:07:53		68		49		29-Nov-07		6:25:59		67.4		34.5

		19-Oct-07		8:07:10		72.21		44		19-Oct-07		8:06:20		72.21		47		19-Oct-07		8:07:53		69.2		48		29-Nov-07		8:25:59		69.8		32

		19-Oct-07		10:07:10		72.8		43.5		19-Oct-07		10:06:20		72.21		40		19-Oct-07		10:07:53		71		49.5		29-Nov-07		10:25:59		72.21		33

		19-Oct-07		12:07:10		74.01		44.5		19-Oct-07		12:06:20		72.21		49.5		19-Oct-07		12:07:53		71.6		51		29-Nov-07		12:25:59		72.21		33

		19-Oct-07		14:07:10		75.2		47		19-Oct-07		14:06:20		72.8		47		19-Oct-07		14:07:53		71		54		29-Nov-07		14:25:59		73.4		32.5

		19-Oct-07		16:07:10		74.6		47		19-Oct-07		16:06:20		71.6		45.5		19-Oct-07		16:07:53		71		48		29-Nov-07		16:25:59		73.4		32

		19-Oct-07		18:07:10		74.6		51.5		19-Oct-07		18:06:20		71		56.5		19-Oct-07		18:07:53		70.41		58.5		29-Nov-07		18:25:59		72.8		30.5

		19-Oct-07		20:07:10		74.6		51.5		19-Oct-07		20:06:20		72.8		57		19-Oct-07		20:07:53		70.41		58		29-Nov-07		20:25:59		71		32

		19-Oct-07		22:07:10		74.01		52.5		19-Oct-07		22:06:20		73.4		56		19-Oct-07		22:07:53		70.41		59		29-Nov-07		22:25:59		69.8		32.5

		20-Oct-07		0:07:10		74.01		53		20-Oct-07		0:06:20		72.8		57.5		20-Oct-07		0:07:53		70.41		60.5		30-Nov-07		0:25:59		69.2		33

		20-Oct-07		2:07:10		73.4		55.5		20-Oct-07		2:06:20		72.8		59		20-Oct-07		2:07:53		69.8		61.5		30-Nov-07		2:25:59		68		32.5

		20-Oct-07		4:07:10		73.4		56		20-Oct-07		4:06:20		72.8		59.5		20-Oct-07		4:07:53		69.8		62		30-Nov-07		4:25:59		67.4		32.5

		20-Oct-07		6:07:10		74.01		56		20-Oct-07		6:06:20		72.8		59		20-Oct-07		6:07:53		70.41		65		30-Nov-07		6:25:59		67.4		31.5

		20-Oct-07		8:07:10		73.4		52.5		20-Oct-07		8:06:20		71		55		20-Oct-07		8:07:53		71		63.5		30-Nov-07		8:25:59		69.2		29.5

		20-Oct-07		10:07:10		73.4		54.5		20-Oct-07		10:06:20		71		54		20-Oct-07		10:07:53		71.6		63.5		30-Nov-07		10:25:59		72.21		31.5

		20-Oct-07		12:07:10		74.6		53		20-Oct-07		12:06:20		71		59.5		20-Oct-07		12:07:53		71.6		58		30-Nov-07		12:25:59		71.6		33

		20-Oct-07		14:07:10		75.2		54.5		20-Oct-07		14:06:20		71		48.5		20-Oct-07		14:07:53		71		62		30-Nov-07		14:25:59		74.01		31.5

		20-Oct-07		16:07:10		74.6		56.5		20-Oct-07		16:06:20		69.8		67		20-Oct-07		16:07:53		70.41		70		30-Nov-07		16:25:59		74.6		30.5

		20-Oct-07		18:07:10		73.4		57.5		20-Oct-07		18:06:20		69.2		61		20-Oct-07		18:07:53		70.41		59.5		30-Nov-07		18:25:59		74.01		29

		20-Oct-07		20:07:10		74.6		53.5		20-Oct-07		20:06:20		72.21		58		20-Oct-07		20:07:53		69.8		61.5		30-Nov-07		20:25:59		72.8		27.5

		20-Oct-07		22:07:10		74.01		49		20-Oct-07		22:06:20		72.21		51.5		20-Oct-07		22:07:53		69.2		56.5		30-Nov-07		22:25:59		71		30

		21-Oct-07		0:07:10		73.4		45		21-Oct-07		0:06:20		71.6		46.5		21-Oct-07		0:07:53		68		53		1-Dec-07		0:25:59		69.2		31

		21-Oct-07		2:07:10		72.21		44.5		21-Oct-07		2:06:20		71		47		21-Oct-07		2:07:53		66.81		53.5		1-Dec-07		2:25:59		68		31

		21-Oct-07		4:07:10		71.6		45		21-Oct-07		4:06:20		71		47		21-Oct-07		4:07:53		66.2		54		1-Dec-07		4:25:59		67.4		31

		21-Oct-07		6:07:10		71		43		21-Oct-07		6:06:20		70.41		45		21-Oct-07		6:07:53		65.6		52		1-Dec-07		6:25:59		68		29.5

		21-Oct-07		8:07:10		70.41		42		21-Oct-07		8:06:20		68.61		44		21-Oct-07		8:07:53		68		46		1-Dec-07		8:25:59		71		28

		21-Oct-07		10:07:10		70.41		45		21-Oct-07		10:06:20		69.2		50		21-Oct-07		10:07:53		67.4		52		1-Dec-07		10:25:59		72.8		28

		21-Oct-07		12:07:10		71		41.5		21-Oct-07		12:06:20		68.61		42.5		21-Oct-07		12:07:53		69.2		45		1-Dec-07		12:25:59		74.01		26.5

		21-Oct-07		14:07:10		71		37.5		21-Oct-07		14:06:20		69.2		37		21-Oct-07		14:07:53		69.2		40.5		1-Dec-07		14:25:59		74.01		27

		21-Oct-07		16:07:10		71		36		21-Oct-07		16:06:20		68.61		38		21-Oct-07		16:07:53		69.2		38		1-Dec-07		16:25:59		74.6		26

		21-Oct-07		18:07:10		71.6		35		21-Oct-07		18:06:20		68.61		37		21-Oct-07		18:07:53		69.8		37		1-Dec-07		18:25:59		75.2		26.5

		21-Oct-07		20:07:10		72.21		35.5		21-Oct-07		20:06:20		70.41		38		21-Oct-07		20:07:53		68.61		40		1-Dec-07		20:25:59		74.01		25

		21-Oct-07		22:07:10		72.21		36		21-Oct-07		22:06:20		71		38		21-Oct-07		22:07:53		67.4		42		1-Dec-07		22:25:59		70.41		27

		22-Oct-07		0:07:10		71.6		36		22-Oct-07		0:06:20		70.41		38		22-Oct-07		0:07:53		66.2		42.5		2-Dec-07		0:25:59		68.61		28

		22-Oct-07		2:07:10		71		35.5		22-Oct-07		2:06:20		69.8		37.5		22-Oct-07		2:07:53		65.01		43		2-Dec-07		2:25:59		67.4		27.5

		22-Oct-07		4:07:10		70.41		35.5		22-Oct-07		4:06:20		69.8		37		22-Oct-07		4:07:53		64.4		43		2-Dec-07		4:25:59		66.2		27.5

		22-Oct-07		6:07:10		69.8		34.5		22-Oct-07		6:06:20		69.2		36.5		22-Oct-07		6:07:53		63.8		42.5		2-Dec-07		6:25:59		66.2		27

		22-Oct-07		8:07:10		69.2		34.5		22-Oct-07		8:06:20		68.61		36.5		22-Oct-07		8:07:53		68		37.5		2-Dec-07		8:25:59		66.2		26

		22-Oct-07		10:07:10		69.8		33.5		22-Oct-07		10:06:20		68.61		35		22-Oct-07		10:07:53		67.4		37.5		2-Dec-07		10:25:59		66.2		26.5

		22-Oct-07		12:07:10		69.8		33		22-Oct-07		12:06:20		68.61		34		22-Oct-07		12:07:53		68.61		35.5		2-Dec-07		12:25:59		66.81		29

		22-Oct-07		14:07:10		71		31		22-Oct-07		14:06:20		68.61		32		22-Oct-07		14:07:53		69.8		34		2-Dec-07		14:25:59		67.4		29.5

		22-Oct-07		16:07:10		72.21		30.5		22-Oct-07		16:06:20		68.61		31		22-Oct-07		16:07:53		70.41		33.5		2-Dec-07		16:25:59		68		30

		22-Oct-07		18:07:10		72.21		30.5		22-Oct-07		18:06:20		69.2		32.5		22-Oct-07		18:07:53		70.41		33.5		2-Dec-07		18:25:59		67.4		30

		22-Oct-07		20:07:10		74.01		28		22-Oct-07		20:06:20		72.21		29.5		22-Oct-07		20:07:53		71.6		31		2-Dec-07		20:25:59		66.81		31

		22-Oct-07		22:07:10		74.01		32		22-Oct-07		22:06:20		72.8		35		22-Oct-07		22:07:53		71		36.5		2-Dec-07		22:25:59		66.2		31

		23-Oct-07		0:07:10		73.4		33		23-Oct-07		0:06:20		72.21		36		23-Oct-07		0:07:53		69.2		38		3-Dec-07		0:25:59		66.2		30.5

		23-Oct-07		2:07:10		72.8		33.5		23-Oct-07		2:06:20		71.6		36.5		23-Oct-07		2:07:53		68.61		39		3-Dec-07		2:25:59		66.2		31

		23-Oct-07		4:07:10		72.21		34		23-Oct-07		4:06:20		71		36.5		23-Oct-07		4:07:53		66.81		40		3-Dec-07		4:25:59		66.2		32.5

		23-Oct-07		6:07:10		71.6		34.5		23-Oct-07		6:06:20		69.8		36.5		23-Oct-07		6:07:53		68		39.5		3-Dec-07		6:25:59		66.2		34.5

		23-Oct-07		8:07:10		71.6		35.5		23-Oct-07		8:06:20		69.8		38.5		23-Oct-07		8:07:53		69.2		38		3-Dec-07		8:25:59		66.2		35.5

		23-Oct-07		10:07:10		72.21		37.5		23-Oct-07		10:06:20		70.41		43.5		23-Oct-07		10:07:53		70.41		42		3-Dec-07		10:25:59		66.81		35.5

		23-Oct-07		12:07:10		72.8		35		23-Oct-07		12:06:20		70.41		36.5		23-Oct-07		12:07:53		71.6		34.5		3-Dec-07		12:25:59		67.4		36.5

		23-Oct-07		14:07:10		74.6		38.5		23-Oct-07		14:06:20		69.8		45		23-Oct-07		14:07:53		71.6		41		3-Dec-07		14:25:59		67.4		37.5

		23-Oct-07		16:07:10		75.81		35		23-Oct-07		16:06:20		71		41.5		23-Oct-07		16:07:53		71.6		42.5		3-Dec-07		16:25:59		68		39

		23-Oct-07		18:07:10		75.2		34		23-Oct-07		18:06:20		71.6		36		23-Oct-07		18:07:53		71		36		3-Dec-07		18:25:59		68		39.5

		23-Oct-07		20:07:10		75.81		34.5		23-Oct-07		20:06:20		72.8		38		23-Oct-07		20:07:53		70.41		40.5		3-Dec-07		20:25:59		68		40

		23-Oct-07		22:07:10		75.2		36		23-Oct-07		22:06:20		72.21		40		23-Oct-07		22:07:53		71.6		40.5		3-Dec-07		22:25:59		68		42

		24-Oct-07		0:07:10		74.6		36.5		24-Oct-07		0:06:20		72.21		40.5		24-Oct-07		0:07:53		71		42		4-Dec-07		0:25:59		68		42

		24-Oct-07		2:07:10		74.01		36.5		24-Oct-07		2:06:20		72.21		40		24-Oct-07		2:07:53		69.2		42.5		4-Dec-07		2:25:59		68		41.5

		24-Oct-07		4:07:10		73.4		36.5		24-Oct-07		4:06:20		72.21		39		24-Oct-07		4:07:53		68.61		42.5		4-Dec-07		4:25:59		67.4		41.5

		24-Oct-07		6:07:10		73.4		35.5		24-Oct-07		6:06:20		72.21		38		24-Oct-07		6:07:53		68		42.5		4-Dec-07		6:25:59		68.61		41

		24-Oct-07		8:07:10		73.4		36		24-Oct-07		8:06:20		71.6		40		24-Oct-07		8:07:53		69.8		40		4-Dec-07		8:25:59		72.8		37

		24-Oct-07		10:07:10		75.2		39		24-Oct-07		10:06:20		72.21		40.5		24-Oct-07		10:07:53		71.6		46.5		4-Dec-07		10:25:59		74.6		38

		24-Oct-07		12:07:10		75.81		39.5		24-Oct-07		12:06:20		72.21		38		24-Oct-07		12:07:53		71.6		49		4-Dec-07		12:25:59		75.2		36

		24-Oct-07		14:07:10		75.81		39		24-Oct-07		14:06:20		72.8		46.5		24-Oct-07		14:07:53		71.6		49		4-Dec-07		14:25:59		74.6		37

		24-Oct-07		16:07:10		76.4		40		24-Oct-07		16:06:20		71.6		50		24-Oct-07		16:07:53		71.6		45		4-Dec-07		16:25:59		74.6		38

		24-Oct-07		18:07:10		74.6		41		24-Oct-07		18:06:20		69.8		42		24-Oct-07		18:07:53		71		53.5		4-Dec-07		18:25:59		74.6		39

		24-Oct-07		20:07:10		75.81		43.5		24-Oct-07		20:06:20		73.4		48.5		24-Oct-07		20:07:53		70.41		55.5		4-Dec-07		20:25:59		74.01		39.5

		24-Oct-07		22:07:10		75.81		43.5		24-Oct-07		22:06:20		72.8		48		24-Oct-07		22:07:53		72.8		48		4-Dec-07		22:25:59		72.8		41

		25-Oct-07		0:07:10		75.2		41.5		25-Oct-07		0:06:20		72.8		45.5		25-Oct-07		0:07:53		72.21		46		5-Dec-07		0:25:59		71.6		44.5

		25-Oct-07		2:07:10		74.6		40		25-Oct-07		2:06:20		72.8		43.5		25-Oct-07		2:07:53		71.6		45		5-Dec-07		2:25:59		70.41		45

		25-Oct-07		4:07:10		74.01		39		25-Oct-07		4:06:20		72.8		41.5		25-Oct-07		4:07:53		69.8		44		5-Dec-07		4:25:59		69.8		45.5

		25-Oct-07		6:07:10		73.4		39		25-Oct-07		6:06:20		71.6		42		25-Oct-07		6:07:53		69.2		45		5-Dec-07		6:25:59		70.41		50

		25-Oct-07		8:07:10		72.8		39.5		25-Oct-07		8:06:20		71		45.5		25-Oct-07		8:07:53		71		42.5		5-Dec-07		8:25:59		74.6		47

		25-Oct-07		10:07:10		72.8		43.5		25-Oct-07		10:06:20		70.41		52.5		25-Oct-07		10:07:53		71.6		49.5		5-Dec-07		10:25:59		75.81		48

		25-Oct-07		12:07:10		73.4		43.5		25-Oct-07		12:06:20		70.41		52		25-Oct-07		12:07:53		71.6		44		5-Dec-07		12:25:59		75.2		50

		25-Oct-07		14:07:10		74.01		42		25-Oct-07		14:06:20		71		39.5		25-Oct-07		14:07:53		71.6		47		5-Dec-07		14:25:59		74.6		51.5

		25-Oct-07		16:07:10		74.6		46		25-Oct-07		16:06:20		69.8		54		25-Oct-07		16:07:53		71.6		50.5		5-Dec-07		16:25:59		74.6		50

		25-Oct-07		18:07:10		74.6		47		25-Oct-07		18:06:20		69.2		56.5		25-Oct-07		18:07:53		71		48.5		5-Dec-07		18:25:59		74.6		49.5

		25-Oct-07		20:07:10		75.81		42		25-Oct-07		20:06:20		72.8		46.5		25-Oct-07		20:07:53		72.8		46.5		5-Dec-07		20:25:59		74.6		48.5

		25-Oct-07		22:07:10		75.2		40.5		25-Oct-07		22:06:20		72.8		43.5		25-Oct-07		22:07:53		72.8		44.5		5-Dec-07		22:25:59		72.8		50

		26-Oct-07		0:07:10		74.6		39.5		26-Oct-07		0:06:20		72.8		43.5		26-Oct-07		0:07:53		71.6		44		6-Dec-07		0:25:59		72.21		51.5

		26-Oct-07		2:07:10		74.01		39		26-Oct-07		2:06:20		72.21		42		26-Oct-07		2:07:53		69.8		44		6-Dec-07		2:25:59		71		51.5

		26-Oct-07		4:07:10		72.8		38		26-Oct-07		4:06:20		71		40.5		26-Oct-07		4:07:53		68.61		43.5		6-Dec-07		4:25:59		70.41		52

		26-Oct-07		6:07:10		72.8		37.5		26-Oct-07		6:06:20		70.41		39.5		26-Oct-07		6:07:53		68		43.5		6-Dec-07		6:25:59		70.41		52

		26-Oct-07		8:07:10		72.21		38		26-Oct-07		8:06:20		69.8		42.5		26-Oct-07		8:07:53		69.2		40.5		6-Dec-07		8:25:59		74.6		46.5

		26-Oct-07		10:07:10		72.8		38.5		26-Oct-07		10:06:20		71		40		26-Oct-07		10:07:53		71		47.5		6-Dec-07		10:25:59		75.81		45

		26-Oct-07		12:07:10		73.4		44.5		26-Oct-07		12:06:20		70.41		50.5		26-Oct-07		12:07:53		71.6		44.5		6-Dec-07		12:25:59		75.2		47

		26-Oct-07		14:07:10		74.6		40		26-Oct-07		14:06:20		71		39.5		26-Oct-07		14:07:53		71.6		48.5		6-Dec-07		14:25:59		74.6		49

		26-Oct-07		16:07:10		74.6		47		26-Oct-07		16:06:20		69.8		58.5		26-Oct-07		16:07:53		71		56		6-Dec-07		16:25:59		74.6		47

		26-Oct-07		18:07:10		74.01		47.5		26-Oct-07		18:06:20		69.2		56		26-Oct-07		18:07:53		70.41		52.5		6-Dec-07		18:25:59		74.6		40.5

		26-Oct-07		20:07:10		74.6		41.5		26-Oct-07		20:06:20		71		47.5		26-Oct-07		20:07:53		71		47.5		6-Dec-07		20:25:59		74.01		39.5

		26-Oct-07		22:07:10		74.01		40.5		26-Oct-07		22:06:20		71		40.5		26-Oct-07		22:07:53		70.41		45.5		6-Dec-07		22:25:59		72.21		42

		27-Oct-07		0:07:10		73.4		40.5		27-Oct-07		0:06:20		71.6		44.5		27-Oct-07		0:07:53		69.2		46		7-Dec-07		0:25:59		71		44

		27-Oct-07		2:07:10		72.8		41.5		27-Oct-07		2:06:20		70.41		46.5		27-Oct-07		2:07:53		68		48		7-Dec-07		2:25:59		70.41		43.5

		27-Oct-07		4:07:10		72.21		42		27-Oct-07		4:06:20		70.41		46		27-Oct-07		4:07:53		68		48.5		7-Dec-07		4:25:59		70.41		44

		27-Oct-07		6:07:10		72.8		42		27-Oct-07		6:06:20		71		45.5		27-Oct-07		6:07:53		68		49		7-Dec-07		6:25:59		70.41		44.5

		27-Oct-07		8:07:10		72.21		41		27-Oct-07		8:06:20		71		45.5		27-Oct-07		8:07:53		71		46.5		7-Dec-07		8:25:59		74.6		41

		27-Oct-07		10:07:10		72.8		45		27-Oct-07		10:06:20		71		45.5		27-Oct-07		10:07:53		71		37.5		7-Dec-07		10:25:59		74.6		42

		27-Oct-07		12:07:10		73.4		45		27-Oct-07		12:06:20		70.41		53.5		27-Oct-07		12:07:53		71		52.5		7-Dec-07		12:25:59		72.8		45.5

		27-Oct-07		14:07:10		73.4		42.5		27-Oct-07		14:06:20		71		47.5		27-Oct-07		14:07:53		71		51		7-Dec-07		14:25:59		72.8		46.5

		27-Oct-07		16:07:10		73.4		46		27-Oct-07		16:06:20		68.61		46		27-Oct-07		16:07:53		71		46.5		7-Dec-07		16:25:59		72.8		47.5

		27-Oct-07		18:07:10		73.4		44.5		27-Oct-07		18:06:20		68		46.5		27-Oct-07		18:07:53		69.8		49.5		7-Dec-07		18:25:59		72.8		46

		27-Oct-07		20:07:10		72.8		42		27-Oct-07		20:06:20		69.2		47.5		27-Oct-07		20:07:53		69.8		46.5		7-Dec-07		20:25:59		72.21		46

		27-Oct-07		22:07:10		72.21		41.5		27-Oct-07		22:06:20		69.2		46		27-Oct-07		22:07:53		68.61		46		7-Dec-07		22:25:59		69.8		47.5

		28-Oct-07		0:07:10		71.6		40		28-Oct-07		0:06:20		68.61		44.5		28-Oct-07		0:07:53		67.4		45		8-Dec-07		0:25:59		68.61		48

		28-Oct-07		2:07:10		71		39		28-Oct-07		2:06:20		68.61		43		28-Oct-07		2:07:53		66.2		45		8-Dec-07		2:25:59		68		47

		28-Oct-07		4:07:10		70.41		38.5		28-Oct-07		4:06:20		68.61		41.5		28-Oct-07		4:07:53		65.01		45.5		8-Dec-07		4:25:59		67.4		46.5

		28-Oct-07		6:07:10		69.8		38		28-Oct-07		6:06:20		68		41.5		28-Oct-07		6:07:53		63.8		46		8-Dec-07		6:25:59		68		45.5

		28-Oct-07		8:07:10		69.2		39.5		28-Oct-07		8:06:20		68		43.5		28-Oct-07		8:07:53		66.81		43.5		8-Dec-07		8:25:59		71.6		40

		28-Oct-07		10:07:10		69.2		42		28-Oct-07		10:06:20		68		47		28-Oct-07		10:07:53		66.81		46.5		8-Dec-07		10:25:59		72.21		39.5

		28-Oct-07		12:07:10		69.2		44.5		28-Oct-07		12:06:20		67.4		50		28-Oct-07		12:07:53		67.4		48		8-Dec-07		12:25:59		71.6		40

		28-Oct-07		14:07:10		69.8		47		28-Oct-07		14:06:20		67.4		53		28-Oct-07		14:07:53		68.61		50		8-Dec-07		14:25:59		72.21		39.5

		28-Oct-07		16:07:10		70.41		49.5		28-Oct-07		16:06:20		67.4		49		28-Oct-07		16:07:53		69.2		52		8-Dec-07		16:25:59		72.21		38

		28-Oct-07		18:07:10		71		43		28-Oct-07		18:06:20		68		46.5		28-Oct-07		18:07:53		69.2		47.5		8-Dec-07		18:25:59		71.6		37.5

		28-Oct-07		20:07:10		71		43.5		28-Oct-07		20:06:20		68.61		47		28-Oct-07		20:07:53		68.61		47		8-Dec-07		20:25:59		70.41		36.5

		28-Oct-07		22:07:10		71		41		28-Oct-07		22:06:20		69.2		44.5		28-Oct-07		22:07:53		67.4		46.5		8-Dec-07		22:25:59		69.8		36.5

		29-Oct-07		0:07:10		70.41		41.5		29-Oct-07		0:06:20		68.61		44.5		29-Oct-07		0:07:53		66.2		47		9-Dec-07		0:25:59		68		37

		29-Oct-07		2:07:10		70.41		41.5		29-Oct-07		2:06:20		68.61		44.5		29-Oct-07		2:07:53		65.6		48		9-Dec-07		2:25:59		66.81		37

		29-Oct-07		4:07:10		69.8		40.5		29-Oct-07		4:06:20		68		44		29-Oct-07		4:07:53		65.01		48		9-Dec-07		4:25:59		66.2		36.5

		29-Oct-07		6:07:10		69.8		40.5		29-Oct-07		6:06:20		68		43.5		29-Oct-07		6:07:53		64.4		48		9-Dec-07		6:25:59		66.2		36

		29-Oct-07		8:07:10		69.2		40		29-Oct-07		8:06:20		68		43		29-Oct-07		8:07:53		67.4		43.5		9-Dec-07		8:25:59		66.2		35.5

		29-Oct-07		10:07:10		69.2		43.5		29-Oct-07		10:06:20		68		49.5		29-Oct-07		10:07:53		67.4		48		9-Dec-07		10:25:59		66.2		34

		29-Oct-07		12:07:10		69.8		47.5		29-Oct-07		12:06:20		68		53.5		29-Oct-07		12:07:53		69.2		50		9-Dec-07		12:25:59		66.2		34

		29-Oct-07		14:07:10		71		48.5		29-Oct-07		14:06:20		68		48.5		29-Oct-07		14:07:53		69.8		54.5		9-Dec-07		14:25:59		66.81		33.5

		29-Oct-07		16:07:10		71.6		48.5		29-Oct-07		16:06:20		68.61		55		29-Oct-07		16:07:53		70.41		45.5		9-Dec-07		16:25:59		66.81		33

		29-Oct-07		18:07:10		72.21		50.5		29-Oct-07		18:06:20		68.61		62.5		29-Oct-07		18:07:53		70.41		55.5		9-Dec-07		18:25:59		66.81		31

		29-Oct-07		20:07:10		72.8		48.5		29-Oct-07		20:06:20		69.2		46		29-Oct-07		20:07:53		71.6		50		9-Dec-07		20:25:59		65.6		30.5

		29-Oct-07		22:07:10		72.21		46		29-Oct-07		22:06:20		69.2		51.5		29-Oct-07		22:07:53		70.41		48.5		9-Dec-07		22:25:59		65.01		31.5

		30-Oct-07		0:07:10		71.6		45		30-Oct-07		0:06:20		68.61		50.5		30-Oct-07		0:07:53		69.2		48		10-Dec-07		0:25:59		64.4		31

		30-Oct-07		2:07:10		71.6		44.5		30-Oct-07		2:06:20		68.61		46.5		30-Oct-07		2:07:53		68.61		48.5		10-Dec-07		2:25:59		63.8		31

		30-Oct-07		4:07:10		71		43.5		30-Oct-07		4:06:20		69.2		48		30-Oct-07		4:07:53		67.4		49		10-Dec-07		4:25:59		63.21		31

		30-Oct-07		6:07:10		71.6		43.5		30-Oct-07		6:06:20		69.2		46.5		30-Oct-07		6:07:53		68		49		10-Dec-07		6:25:59		62.6		31

		30-Oct-07		8:07:10		71		46		30-Oct-07		8:06:20		68.61		44.5		30-Oct-07		8:07:53		69.2		47.5		10-Dec-07		8:25:59		63.21		31

		30-Oct-07		10:07:10		72.21		46		30-Oct-07		10:06:20		69.2		55.5		30-Oct-07		10:07:53		71.6		47.5		10-Dec-07		10:25:59		64.4		31

		30-Oct-07		12:07:10		72.21		49		30-Oct-07		12:06:20		69.8		56		30-Oct-07		12:07:53		71		49		10-Dec-07		12:25:59		65.6		31.5

		30-Oct-07		14:07:10		73.4		47		30-Oct-07		14:06:20		70.41		53.5		30-Oct-07		14:07:53		71		55		10-Dec-07		14:25:59		66.2		32

		30-Oct-07		16:07:10		73.4		48.5		30-Oct-07		16:06:20		68.61		61.5		30-Oct-07		16:07:53		70.41		54		10-Dec-07		16:25:59		66.81		32.5

		30-Oct-07		18:07:10		72.8		45		30-Oct-07		18:06:20		69.2		54.5		30-Oct-07		18:07:53		70.41		51.5		10-Dec-07		18:25:59		66.81		33

		30-Oct-07		20:07:10		72.21		46		30-Oct-07		20:06:20		68.61		53		30-Oct-07		20:07:53		69.8		48.5		10-Dec-07		20:25:59		66.2		34

		30-Oct-07		22:07:10		71.6		45.5		30-Oct-07		22:06:20		68.61		51.5		30-Oct-07		22:07:53		69.2		49		10-Dec-07		22:25:59		65.01		35

		31-Oct-07		0:07:10		71.6		45		31-Oct-07		0:06:20		69.2		50		31-Oct-07		0:07:53		68.61		49.5		11-Dec-07		0:25:59		64.4		36.5

		31-Oct-07		2:07:10		71		46.5		31-Oct-07		2:06:20		68.61		52		31-Oct-07		2:07:53		68		51		11-Dec-07		2:25:59		63.21		36.5

		31-Oct-07		4:07:10		71		47		31-Oct-07		4:06:20		68.61		52		31-Oct-07		4:07:53		67.4		52.5		11-Dec-07		4:25:59		63.21		36

		31-Oct-07		6:07:10		71.6		47		31-Oct-07		6:06:20		68.61		52		31-Oct-07		6:07:53		72.21		48		11-Dec-07		6:25:59		64.4		34.5

		31-Oct-07		8:07:10		71.6		47.5		31-Oct-07		8:06:20		69.8		48.5		31-Oct-07		8:07:53		71		43.5		11-Dec-07		8:25:59		66.81		31.5

		31-Oct-07		10:07:10		72.21		48		31-Oct-07		10:06:20		69.8		51.5		31-Oct-07		10:07:53		71.6		49.5		11-Dec-07		10:25:59		69.8		31.5

		31-Oct-07		12:07:10		72.8		46.5		31-Oct-07		12:06:20		69.2		45.5		31-Oct-07		12:07:53		72.21		48		11-Dec-07		12:25:59		74.01		32

		31-Oct-07		14:07:10		72.8		46.5		31-Oct-07		14:06:20		70.41		45.5		31-Oct-07		14:07:53		71		52		11-Dec-07		14:25:59		71.6		33.5

		31-Oct-07		16:07:10		73.4		47		31-Oct-07		16:06:20		68		51		31-Oct-07		16:07:53		71		45.5		11-Dec-07		16:25:59		71.6		34.5

		31-Oct-07		18:07:10		72.8		47		31-Oct-07		18:06:20		68.61		48		31-Oct-07		18:07:53		70.41		51.5		11-Dec-07		18:25:59		71.6		33.5

		31-Oct-07		20:07:10		72.21		45		31-Oct-07		20:06:20		68.61		51.5		31-Oct-07		20:07:53		69.8		48		11-Dec-07		20:25:59		69.8		33.5

		31-Oct-07		22:07:10		72.21		44.5		31-Oct-07		22:06:20		69.2		49.5		31-Oct-07		22:07:53		68.61		49.5		11-Dec-07		22:25:59		67.4		33

		1-Nov-07		0:07:10		71.6		44.5		1-Nov-07		0:06:20		69.2		49.5		1-Nov-07		0:07:53		67.4		50		12-Dec-07		0:25:59		66.2		33.5

		1-Nov-07		2:07:10		71.6		45.5		1-Nov-07		2:06:20		69.2		50		1-Nov-07		2:07:53		66.81		51.5		12-Dec-07		2:25:59		65.01		31

		1-Nov-07		4:07:10		71		46.5		1-Nov-07		4:06:20		68.61		52		1-Nov-07		4:07:53		66.81		53		12-Dec-07		4:25:59		63.8		29

		1-Nov-07		6:07:10		71.6		47.5		1-Nov-07		6:06:20		69.2		53.5		1-Nov-07		6:07:53		68.61		51		12-Dec-07		6:25:59		65.6		24

		1-Nov-07		8:07:10		72.21		44.5		1-Nov-07		8:06:20		69.8		53.5		1-Nov-07		8:07:53		70.41		49		12-Dec-07		8:25:59		69.8		21.5

		1-Nov-07		10:07:10		72.21		47		1-Nov-07		10:06:20		68.61		51.5		1-Nov-07		10:07:53		71		48.5		12-Dec-07		10:25:59		72.21		23

		1-Nov-07		12:07:10		72.8		45.5		1-Nov-07		12:06:20		69.8		44		1-Nov-07		12:07:53		71.6		45.5		12-Dec-07		12:25:59		71.6		22

		1-Nov-07		14:07:10		72.8		46.5		1-Nov-07		14:06:20		68.61		47.5		1-Nov-07		14:07:53		71		51		12-Dec-07		14:25:59		72.21		21

		1-Nov-07		16:07:10		72.8		51.5		1-Nov-07		16:06:20		68.61		60.5		1-Nov-07		16:07:53		70.41		55.5		12-Dec-07		16:25:59		72.21		20.5

		1-Nov-07		18:07:10		72.8		50		1-Nov-07		18:06:20		68.61		59		1-Nov-07		18:07:53		69.8		54.5		12-Dec-07		18:25:59		71.6		23

		1-Nov-07		20:07:10		72.21		47.5		1-Nov-07		20:06:20		68.61		53.5		1-Nov-07		20:07:53		69.8		50.5		12-Dec-07		20:25:59		69.8		24

		1-Nov-07		22:07:10		71.6		47.5		1-Nov-07		22:06:20		69.2		52		1-Nov-07		22:07:53		69.2		51		12-Dec-07		22:25:59		68.61		25.5

		2-Nov-07		0:07:10		71		48		2-Nov-07		0:06:20		68.61		52.5		2-Nov-07		0:07:53		68.61		51.5		13-Dec-07		0:25:59		66.2		26.5

		2-Nov-07		2:07:10		71		48		2-Nov-07		2:06:20		68.61		52.5		2-Nov-07		2:07:53		68		52.5		13-Dec-07		2:25:59		64.4		27

		2-Nov-07		4:07:10		70.41		47.5		2-Nov-07		4:06:20		68.61		52		2-Nov-07		4:07:53		67.4		52.5		13-Dec-07		4:25:59		63.21		27.5

		2-Nov-07		6:07:10		71		46		2-Nov-07		6:06:20		69.2		49		2-Nov-07		6:07:53		68		51.5		13-Dec-07		6:25:59		64.4		28

		2-Nov-07		8:07:10		72.21		46.5		2-Nov-07		8:06:20		68.61		54.5		2-Nov-07		8:07:53		69.8		48		13-Dec-07		8:25:59		68		27.5

		2-Nov-07		10:07:10		73.4		46		2-Nov-07		10:06:20		69.2		53		2-Nov-07		10:07:53		71.6		46.5		13-Dec-07		10:25:59		70.41		28.5

		2-Nov-07		12:07:10		74.01		47		2-Nov-07		12:06:20		69.8		56.5		2-Nov-07		12:07:53		71.6		47.5		13-Dec-07		12:25:59		71.6		29

		2-Nov-07		14:07:10		74.01		44		2-Nov-07		14:06:20		71		48.5		2-Nov-07		14:07:53		71		44		13-Dec-07		14:25:59		71.6		26

		2-Nov-07		16:07:10		74.01		52.5		2-Nov-07		16:06:20		69.2		58		2-Nov-07		16:07:53		71		56.5		13-Dec-07		16:25:59		71.6		25.5

		2-Nov-07		18:07:10		74.01		49.5		2-Nov-07		18:06:20		69.2		49.5		2-Nov-07		18:07:53		70.41		50		13-Dec-07		18:25:59		71.6		26

		2-Nov-07		20:07:10		73.4		46.5		2-Nov-07		20:06:20		69.2		51.5		2-Nov-07		20:07:53		70.41		51		13-Dec-07		20:25:59		71		27.5

		2-Nov-07		22:07:10		72.8		42		2-Nov-07		22:06:20		69.8		47.5		2-Nov-07		22:07:53		69.8		47		13-Dec-07		22:25:59		68		28.5

		3-Nov-07		0:07:10		71.6		42		3-Nov-07		0:06:20		69.2		46		3-Nov-07		0:07:53		68		46.5		14-Dec-07		0:25:59		66.2		29.5

		3-Nov-07		2:07:10		71		40.5		3-Nov-07		2:06:20		69.2		43.5		3-Nov-07		2:07:53		66.81		46.5		14-Dec-07		2:25:59		64.4		29.5

		3-Nov-07		4:07:10		70.41		40		3-Nov-07		4:06:20		68		42.5		3-Nov-07		4:07:53		66.81		45		14-Dec-07		4:25:59		63.8		30

		3-Nov-07		6:07:10		70.41		38		3-Nov-07		6:06:20		67.4		40.5		3-Nov-07		6:07:53		67.4		42.5		14-Dec-07		6:25:59		65.01		29

		3-Nov-07		8:07:10		72.8		36.5		3-Nov-07		8:06:20		69.2		42		3-Nov-07		8:07:53		68.61		39		14-Dec-07		8:25:59		66.81		27

		3-Nov-07		10:07:10		74.01		39.5		3-Nov-07		10:06:20		71.6		46		3-Nov-07		10:07:53		70.41		47		14-Dec-07		10:25:59		70.41		28.5

		3-Nov-07		12:07:10		74.6		40		3-Nov-07		12:06:20		71.6		46.5		3-Nov-07		12:07:53		71.6		45.5		14-Dec-07		12:25:59		72.21		28.5

		3-Nov-07		14:07:10		74.6		42		3-Nov-07		14:06:20		70.41		50		3-Nov-07		14:07:53		71		52		14-Dec-07		14:25:59		72.21		29.5

		3-Nov-07		16:07:10		74.01		42.5		3-Nov-07		16:06:20		69.8		50.5		3-Nov-07		16:07:53		71		49.5		14-Dec-07		16:25:59		72.21		30.5

		3-Nov-07		18:07:10		74.01		47.5		3-Nov-07		18:06:20		69.2		59.5		3-Nov-07		18:07:53		71		47		14-Dec-07		18:25:59		72.8		31.5

		3-Nov-07		20:07:10		74.6		42		3-Nov-07		20:06:20		71		47.5		3-Nov-07		20:07:53		70.41		48.5		14-Dec-07		20:25:59		71		31.5

		3-Nov-07		22:07:10		74.01		40.5		3-Nov-07		22:06:20		71		45		3-Nov-07		22:07:53		69.8		45.5		14-Dec-07		22:25:59		68.61		31

		4-Nov-07		0:07:10		72.8		38.5		4-Nov-07		0:06:20		69.8		42		4-Nov-07		0:07:53		68		44.5		15-Dec-07		0:25:59		66.2		31.5

		4-Nov-07		2:07:10		71.6		37.5		4-Nov-07		2:06:20		69.8		40		4-Nov-07		2:07:53		66.81		44		15-Dec-07		2:25:59		64.4		31.5

		4-Nov-07		4:07:10		71		36.5		4-Nov-07		4:06:20		69.2		39		4-Nov-07		4:07:53		65.01		43.5		15-Dec-07		4:25:59		63.21		31

		4-Nov-07		6:07:10		69.8		35.5		4-Nov-07		6:06:20		68.61		38		4-Nov-07		6:07:53		63.8		43.5		15-Dec-07		6:25:59		64.4		30

		4-Nov-07		8:07:10		69.2		35		4-Nov-07		8:06:20		67.4		38		4-Nov-07		8:07:53		66.81		39		15-Dec-07		8:25:59		66.81		28.5

		4-Nov-07		10:07:10		69.8		37.5		4-Nov-07		10:06:20		68.61		40.5		4-Nov-07		10:07:53		67.4		41		15-Dec-07		10:25:59		69.2		30

		4-Nov-07		12:07:10		70.41		40.5		4-Nov-07		12:06:20		68.61		43		4-Nov-07		12:07:53		68.61		43.5		15-Dec-07		12:25:59		72.21		31

		4-Nov-07		14:07:10		71		41		4-Nov-07		14:06:20		69.2		39.5		4-Nov-07		14:07:53		70.41		41		15-Dec-07		14:25:59		71.6		32

		4-Nov-07		16:07:10		72.21		42.5		4-Nov-07		16:06:20		69.2		41.5		4-Nov-07		16:07:53		70.41		46.5		15-Dec-07		16:25:59		72.21		31.5

		4-Nov-07		18:07:10		72.8		38.5		4-Nov-07		18:06:20		69.2		41		4-Nov-07		18:07:53		69.8		44		15-Dec-07		18:25:59		71.6		34

		4-Nov-07		20:07:10		72.8		36		4-Nov-07		20:06:20		70.41		39		4-Nov-07		20:07:53		70.41		40		15-Dec-07		20:25:59		71		34.5

		4-Nov-07		22:07:10		72.8		35.5		4-Nov-07		22:06:20		70.41		39		4-Nov-07		22:07:53		69.2		40		15-Dec-07		22:25:59		68.61		34

		5-Nov-07		0:07:10		72.21		36.5		5-Nov-07		0:06:20		70.41		40		5-Nov-07		0:07:53		67.4		42		16-Dec-07		0:25:59		67.4		35

		5-Nov-07		2:07:10		71.6		36		5-Nov-07		2:06:20		70.41		38.5		5-Nov-07		2:07:53		65.6		42		16-Dec-07		2:25:59		66.81		35

		5-Nov-07		4:07:10		70.41		35.5		5-Nov-07		4:06:20		69.2		37.5		5-Nov-07		4:07:53		64.4		42.5		16-Dec-07		4:25:59		66.2		35.5

		5-Nov-07		6:07:10		69.8		34.5		5-Nov-07		6:06:20		68.61		37		5-Nov-07		6:07:53		64.4		41.5		16-Dec-07		6:25:59		66.2		35.5

		5-Nov-07		8:07:10		69.2		34		5-Nov-07		8:06:20		67.4		37		5-Nov-07		8:07:53		66.81		37.5		16-Dec-07		8:25:59		65.6		35.5

		5-Nov-07		10:07:10		69.2		37		5-Nov-07		10:06:20		68		40		5-Nov-07		10:07:53		67.4		40.5		16-Dec-07		10:25:59		65.6		36

		5-Nov-07		12:07:10		69.8		39		5-Nov-07		12:06:20		68.61		39		5-Nov-07		12:07:53		68		42		16-Dec-07		12:25:59		66.2		37.5

		5-Nov-07		14:07:10		71		40.5		5-Nov-07		14:06:20		68.61		43		5-Nov-07		14:07:53		69.8		42.5		16-Dec-07		14:25:59		66.2		38.5

		5-Nov-07		16:07:10		71.6		41.5		5-Nov-07		16:06:20		69.2		40.5		5-Nov-07		16:07:53		69.8		45		16-Dec-07		16:25:59		66.2		40

		5-Nov-07		18:07:10		72.21		40.5		5-Nov-07		18:06:20		68.61		45		5-Nov-07		18:07:53		70.41		43.5		16-Dec-07		18:25:59		65.6		41.5

		5-Nov-07		20:07:10		72.8		40		5-Nov-07		20:06:20		71		43		5-Nov-07		20:07:53		70.41		44.5		16-Dec-07		20:25:59		65.01		42

		5-Nov-07		22:07:10		72.21		40.5		5-Nov-07		22:06:20		70.41		44.5		5-Nov-07		22:07:53		69.2		44.5		16-Dec-07		22:25:59		65.01		42

		6-Nov-07		0:07:10		71.6		39		6-Nov-07		0:06:20		70.41		41.5		6-Nov-07		0:07:53		67.4		44		17-Dec-07		0:25:59		64.4		42.5

		6-Nov-07		2:07:10		71		38		6-Nov-07		2:06:20		69.8		40		6-Nov-07		2:07:53		66.2		44		17-Dec-07		2:25:59		63.8		43.5

		6-Nov-07		4:07:10		69.8		36		6-Nov-07		4:06:20		68.61		38		6-Nov-07		4:07:53		65.01		42.5		17-Dec-07		4:25:59		63.8		43.5

		6-Nov-07		6:07:10		69.2		35		6-Nov-07		6:06:20		67.4		37		6-Nov-07		6:07:53		67.4		38		17-Dec-07		6:25:59		63.21		43

		6-Nov-07		8:07:10		71.6		33.5		6-Nov-07		8:06:20		68		36		6-Nov-07		8:07:53		68		37		17-Dec-07		8:25:59		64.4		44

		6-Nov-07		10:07:10		72.8		35.5		6-Nov-07		10:06:20		70.41		42.5		6-Nov-07		10:07:53		70.41		35.5		17-Dec-07		10:25:59		65.6		43.5

		6-Nov-07		12:07:10		74.01		38.5		6-Nov-07		12:06:20		70.41		47.5		6-Nov-07		12:07:53		70.41		46.5		17-Dec-07		12:25:59		66.2		43.5

		6-Nov-07		14:07:10		74.01		37		6-Nov-07		14:06:20		71		39		6-Nov-07		14:07:53		70.41		49.5		17-Dec-07		14:25:59		66.2		42

		6-Nov-07		16:07:10		74.6		44		6-Nov-07		16:06:20		70.41		48.5		6-Nov-07		16:07:53		71		49		17-Dec-07		16:25:59		66.81		41.5

		6-Nov-07		18:07:10		74.6		41.5		6-Nov-07		18:06:20		69.2		43		6-Nov-07		18:07:53		70.41		46.5		17-Dec-07		18:25:59		66.81		41.5

		6-Nov-07		20:07:10		73.4		39.5		6-Nov-07		20:06:20		70.41		44.5		6-Nov-07		20:07:53		69.8		44.5		17-Dec-07		20:25:59		65.6		41.5

		6-Nov-07		22:07:10		72.8		40		6-Nov-07		22:06:20		70.41		44		6-Nov-07		22:07:53		68		46		17-Dec-07		22:25:59		65.01		43.5

		7-Nov-07		0:07:10		72.21		40.5		7-Nov-07		0:06:20		70.41		44.5		7-Nov-07		0:07:53		67.4		47		18-Dec-07		0:25:59		64.4		44.5

		7-Nov-07		2:07:10		71.6		41		7-Nov-07		2:06:20		70.41		44		7-Nov-07		2:07:53		66.2		48		18-Dec-07		2:25:59		63.8		45

		7-Nov-07		4:07:10		71		41		7-Nov-07		4:06:20		69.8		43.5		7-Nov-07		4:07:53		65.6		48.5		18-Dec-07		4:25:59		63.8		44

		7-Nov-07		6:07:10		70.41		41.5		7-Nov-07		6:06:20		69.8		43.5		7-Nov-07		6:07:53		67.4		45		18-Dec-07		6:25:59		65.6		46

		7-Nov-07		8:07:10		71.6		41.5		7-Nov-07		8:06:20		68.61		45		7-Nov-07		8:07:53		70.41		43.5		18-Dec-07		8:25:59		68		45

		7-Nov-07		10:07:10		72.8		41		7-Nov-07		10:06:20		70.41		47.5		7-Nov-07		10:07:53		71		44		18-Dec-07		10:25:59		71		45

		7-Nov-07		12:07:10		72.8		40		7-Nov-07		12:06:20		71		38.5		7-Nov-07		12:07:53		70.41		45.5		18-Dec-07		12:25:59		71.6		44

		7-Nov-07		14:07:10		73.4		42.5		7-Nov-07		14:06:20		71		50.5		7-Nov-07		14:07:53		70.41		45.5		18-Dec-07		14:25:59		71.6		45.5

		7-Nov-07		16:07:10		74.01		46		7-Nov-07		16:06:20		70.41		46		7-Nov-07		16:07:53		71		53		18-Dec-07		16:25:59		71.6		45

		7-Nov-07		18:07:10		74.01		43.5		7-Nov-07		18:06:20		69.2		51.5		7-Nov-07		18:07:53		69.8		50		18-Dec-07		18:25:59		72.21		44

		7-Nov-07		20:07:10		72.8		40.5		7-Nov-07		20:06:20		70.41		44		7-Nov-07		20:07:53		69.2		45.5		18-Dec-07		20:25:59		70.41		43

		7-Nov-07		22:07:10		72.21		39		7-Nov-07		22:06:20		70.41		41		7-Nov-07		22:07:53		68		44		18-Dec-07		22:25:59		68.61		44

		8-Nov-07		0:07:10		71.6		40		8-Nov-07		0:06:20		70.41		42.5		8-Nov-07		0:07:53		66.81		46.5		19-Dec-07		0:25:59		67.4		45

		8-Nov-07		2:07:10		71		40.5		8-Nov-07		2:06:20		70.41		42		8-Nov-07		2:07:53		65.6		47.5		19-Dec-07		2:25:59		66.2		46

		8-Nov-07		4:07:10		70.41		39.5		8-Nov-07		4:06:20		69.8		40.5		8-Nov-07		4:07:53		65.01		47		19-Dec-07		4:25:59		65.01		46.5

		8-Nov-07		6:07:10		69.8		39.5		8-Nov-07		6:06:20		69.8		40		8-Nov-07		6:07:53		67.4		43		19-Dec-07		6:25:59		65.6		49

		8-Nov-07		8:07:10		71.6		38.5		8-Nov-07		8:06:20		68.61		42.5		8-Nov-07		8:07:53		69.2		41.5		19-Dec-07		8:25:59		69.2		46.5

		8-Nov-07		10:07:10		71		40		8-Nov-07		10:06:20		67.4		47		8-Nov-07		10:07:53		71		41		19-Dec-07		10:25:59		71.6		47

		8-Nov-07		12:07:10		72.21		43		8-Nov-07		12:06:20		70.41		46.5		8-Nov-07		12:07:53		70.41		47		19-Dec-07		12:25:59		72.21		46.5

		8-Nov-07		14:07:10		71.6		41		8-Nov-07		14:06:20		68		43		8-Nov-07		14:07:53		71.6		45.5		19-Dec-07		14:25:59		72.21		49.5

		8-Nov-07		16:07:10		74.01		43.5		8-Nov-07		16:06:20		71.6		43		8-Nov-07		16:07:53		70.41		53		19-Dec-07		16:25:59		72.8		46.5

		8-Nov-07		18:07:10		73.4		43		8-Nov-07		18:06:20		71		47.5		8-Nov-07		18:07:53		69.8		48		19-Dec-07		18:25:59		72.21		44.5

		8-Nov-07		20:07:10		71.6		43		8-Nov-07		20:06:20		69.2		46.5		8-Nov-07		20:07:53		69.8		47		19-Dec-07		20:25:59		71.6		42

		8-Nov-07		22:07:10		71.6		44		8-Nov-07		22:06:20		68.61		48		8-Nov-07		22:07:53		68.61		48		19-Dec-07		22:25:59		69.2		43

		9-Nov-07		0:07:10		71		43		9-Nov-07		0:06:20		68.61		46.5		9-Nov-07		0:07:53		68		47		20-Dec-07		0:25:59		68		42.5

		9-Nov-07		2:07:10		70.41		44		9-Nov-07		2:06:20		68.61		47.5		9-Nov-07		2:07:53		67.4		48.5		20-Dec-07		2:25:59		67.4		42.5

		9-Nov-07		4:07:10		70.41		44.5		9-Nov-07		4:06:20		68.61		47.5		9-Nov-07		4:07:53		66.81		49.5		20-Dec-07		4:25:59		66.81		42.5

		9-Nov-07		6:07:10		69.8		44		9-Nov-07		6:06:20		68.61		46.5		9-Nov-07		6:07:53		68		47		20-Dec-07		6:25:59		67.4		42.5

		9-Nov-07		8:07:10		71.6		43		9-Nov-07		8:06:20		69.8		46		9-Nov-07		8:07:53		70.41		47		20-Dec-07		8:25:59		69.8		41.5

		9-Nov-07		10:07:10		71.6		44.5		9-Nov-07		10:06:20		71		48		9-Nov-07		10:07:53		71.6		47.5		20-Dec-07		10:25:59		71.6		41.5

		9-Nov-07		12:07:10		72.21		45		9-Nov-07		12:06:20		71		49		9-Nov-07		12:07:53		70.41		48		20-Dec-07		12:25:59		72.8		41

		9-Nov-07		14:07:10		74.01		42.5		9-Nov-07		14:06:20		71.6		44.5		9-Nov-07		14:07:53		71		49.5		20-Dec-07		14:25:59		72.8		42.5

		9-Nov-07		16:07:10		74.01		44		9-Nov-07		16:06:20		71.6		49		9-Nov-07		16:07:53		69.8		49.5		20-Dec-07		16:25:59		72.8		43.5

		9-Nov-07		18:07:10		72.8		42.5		9-Nov-07		18:06:20		70.41		46.5		9-Nov-07		18:07:53		69.8		50		20-Dec-07		18:25:59		72.8		43

		9-Nov-07		20:07:10		72.8		42.5		9-Nov-07		20:06:20		69.8		46		9-Nov-07		20:07:53		69.2		47		20-Dec-07		20:25:59		71.6		43

		9-Nov-07		22:07:10		71.6		43.5		9-Nov-07		22:06:20		69.2		47		9-Nov-07		22:07:53		69.2		47.5		20-Dec-07		22:25:59		70.41		45

		10-Nov-07		0:07:10		71		44.5		10-Nov-07		0:06:20		69.2		48.5		10-Nov-07		0:07:53		68.61		48.5		21-Dec-07		0:25:59		69.2		45.5

		10-Nov-07		2:07:10		71		45		10-Nov-07		2:06:20		68.61		49.5		10-Nov-07		2:07:53		68		49.5		21-Dec-07		2:25:59		68.61		46.5

		10-Nov-07		4:07:10		70.41		45		10-Nov-07		4:06:20		68.61		48		10-Nov-07		4:07:53		67.4		49.5		21-Dec-07		4:25:59		68.61		46.5

		10-Nov-07		6:07:10		69.8		42		10-Nov-07		6:06:20		68.61		45		10-Nov-07		6:07:53		66.81		47		21-Dec-07		6:25:59		68.61		46

		10-Nov-07		8:07:10		72.21		40		10-Nov-07		8:06:20		68.61		44		10-Nov-07		8:07:53		69.8		44		21-Dec-07		8:25:59		70.41		41

		10-Nov-07		10:07:10		74.01		39.5		10-Nov-07		10:06:20		71		42		10-Nov-07		10:07:53		70.41		47		21-Dec-07		10:25:59		72.8		40.5

		10-Nov-07		12:07:10		73.4		41		10-Nov-07		12:06:20		71		48.5		10-Nov-07		12:07:53		70.41		47		21-Dec-07		12:25:59		72.21		38.5

		10-Nov-07		14:07:10		73.4		40		10-Nov-07		14:06:20		71.6		41		10-Nov-07		14:07:53		71		51		21-Dec-07		14:25:59		72.8		37

		10-Nov-07		16:07:10		74.01		44		10-Nov-07		16:06:20		71		50		10-Nov-07		16:07:53		70.41		41.5		21-Dec-07		16:25:59		72.21		35.5

		10-Nov-07		18:07:10		73.4		44.5		10-Nov-07		18:06:20		69.8		51		10-Nov-07		18:07:53		70.41		52.5		21-Dec-07		18:25:59		71.6		34.5

		10-Nov-07		20:07:10		72.8		44		10-Nov-07		20:06:20		69.2		48.5		10-Nov-07		20:07:53		69.8		48.5		21-Dec-07		20:25:59		69.8		34.5

		10-Nov-07		22:07:10		71.6		42.5		10-Nov-07		22:06:20		68.61		46.5		10-Nov-07		22:07:53		69.2		46.5		21-Dec-07		22:25:59		68.61		35

		11-Nov-07		0:07:10		71		41		11-Nov-07		0:06:20		68.61		44.5		11-Nov-07		0:07:53		68		45		22-Dec-07		0:25:59		68		35

		11-Nov-07		2:07:10		70.41		40		11-Nov-07		2:06:20		68		43		11-Nov-07		2:07:53		66.2		45		22-Dec-07		2:25:59		67.4		34.5

		11-Nov-07		4:07:10		69.8		40		11-Nov-07		4:06:20		68		44		11-Nov-07		4:07:53		65.6		46.5		22-Dec-07		4:25:59		66.2		34

		11-Nov-07		6:07:10		69.8		41		11-Nov-07		6:06:20		68		45.5		11-Nov-07		6:07:53		65.01		48		22-Dec-07		6:25:59		66.81		33

		11-Nov-07		8:07:10		69.8		43		11-Nov-07		8:06:20		68		47.5		11-Nov-07		8:07:53		67.4		47		22-Dec-07		8:25:59		69.2		30.5

		11-Nov-07		10:07:10		69.8		46		11-Nov-07		10:06:20		68		51		11-Nov-07		10:07:53		68		48.5		22-Dec-07		10:25:59		70.41		31

		11-Nov-07		12:07:10		69.8		50		11-Nov-07		12:06:20		68		55		11-Nov-07		12:07:53		67.4		53.5		22-Dec-07		12:25:59		71		30

		11-Nov-07		14:07:10		70.41		52.5		11-Nov-07		14:06:20		68.61		57.5		11-Nov-07		14:07:53		68		54.5		22-Dec-07		14:25:59		70.41		30

		11-Nov-07		16:07:10		70.41		53.5		11-Nov-07		16:06:20		68.61		58.5		11-Nov-07		16:07:53		68		55.5		22-Dec-07		16:25:59		71.6		29.5

		11-Nov-07		18:07:10		70.41		54.5		11-Nov-07		18:06:20		68.61		59		11-Nov-07		18:07:53		68.61		56.5		22-Dec-07		18:25:59		70.41		30

		11-Nov-07		20:07:10		70.41		54.5		11-Nov-07		20:06:20		68.61		59		11-Nov-07		20:07:53		68.61		56		22-Dec-07		20:25:59		69.2		30.5

		11-Nov-07		22:07:10		70.41		55		11-Nov-07		22:06:20		68.61		59.5		11-Nov-07		22:07:53		68		56.5		22-Dec-07		22:25:59		66.81		31.5

		12-Nov-07		0:07:10		70.41		55		12-Nov-07		0:06:20		68.61		59		12-Nov-07		0:07:53		68		57		23-Dec-07		0:25:59		64.4		32

		12-Nov-07		2:07:10		70.41		55		12-Nov-07		2:06:20		68.61		59		12-Nov-07		2:07:53		68		57.5		23-Dec-07		2:25:59		63.21		32.5

		12-Nov-07		4:07:10		69.8		50.5		12-Nov-07		4:06:20		68.61		52		12-Nov-07		4:07:53		67.4		55.5		23-Dec-07		4:25:59		62.6		31.5

		12-Nov-07		6:07:10		69.8		45.5		12-Nov-07		6:06:20		68.61		46		12-Nov-07		6:07:53		66.2		51.5		23-Dec-07		6:25:59		62		31

		12-Nov-07		8:07:10		69.2		43.5		12-Nov-07		8:06:20		68		45.5		12-Nov-07		8:07:53		67.4		47		23-Dec-07		8:25:59		62.6		31

		12-Nov-07		10:07:10		69.2		44		12-Nov-07		10:06:20		68.61		46		12-Nov-07		10:07:53		68		47		23-Dec-07		10:25:59		62.6		32

		12-Nov-07		12:07:10		70.41		43		12-Nov-07		12:06:20		69.2		43.5		12-Nov-07		12:07:53		68		46.5		23-Dec-07		12:25:59		62.6		33.5

		12-Nov-07		14:07:10		71		39.5		12-Nov-07		14:06:20		69.2		39		12-Nov-07		14:07:53		69.2		43		23-Dec-07		14:25:59		65.01		35

		12-Nov-07		16:07:10		71		38.5		12-Nov-07		16:06:20		69.2		38.5		12-Nov-07		16:07:53		69.8		42.5		23-Dec-07		16:25:59		65.01		34

		12-Nov-07		18:07:10		71.6		39		12-Nov-07		18:06:20		69.8		38.5		12-Nov-07		18:07:53		69.8		42.5		23-Dec-07		18:25:59		64.4		34

		12-Nov-07		20:07:10		71		39.5		12-Nov-07		20:06:20		68.61		42		12-Nov-07		20:07:53		69.2		43		23-Dec-07		20:25:59		63.21		35.5

		12-Nov-07		22:07:10		70.41		39		12-Nov-07		22:06:20		68.61		41.5		12-Nov-07		22:07:53		67.4		43		23-Dec-07		22:25:59		62.6		35.5

		13-Nov-07		0:07:10		69.8		38.5		13-Nov-07		0:06:20		68		41		13-Nov-07		0:07:53		65.6		43.5		24-Dec-07		0:25:59		62.6		36

		13-Nov-07		2:07:10		69.2		38		13-Nov-07		2:06:20		68		40.5		13-Nov-07		2:07:53		64.4		44.5		24-Dec-07		2:25:59		62		36

		13-Nov-07		4:07:10		69.2		38		13-Nov-07		4:06:20		68		40.5		13-Nov-07		4:07:53		63.8		45		24-Dec-07		4:25:59		62		36

		13-Nov-07		6:07:10		68.61		39		13-Nov-07		6:06:20		68		41.5		13-Nov-07		6:07:53		66.81		43		24-Dec-07		6:25:59		62		36

		13-Nov-07		8:07:10		71.6		38		13-Nov-07		8:06:20		69.2		41		13-Nov-07		8:07:53		69.2		41.5		24-Dec-07		8:25:59		62		36

		13-Nov-07		10:07:10		72.8		38		13-Nov-07		10:06:20		70.41		42.5		13-Nov-07		10:07:53		71		41		24-Dec-07		10:25:59		62		36.5

		13-Nov-07		12:07:10		75.2		37.5		13-Nov-07		12:06:20		71		40		13-Nov-07		12:07:53		70.41		42.5		24-Dec-07		12:25:59		62		38

		13-Nov-07		14:07:10		74.6		35		13-Nov-07		14:06:20		71.6		38.5		13-Nov-07		14:07:53		71.6		42		24-Dec-07		14:25:59		63.21		41.5

		13-Nov-07		16:07:10		74.01		34.5		13-Nov-07		16:06:20		71.6		37.5		13-Nov-07		16:07:53		70.41		41		24-Dec-07		16:25:59		64.4		42.5

		13-Nov-07		18:07:10		74.01		32		13-Nov-07		18:06:20		69.8		31.5		13-Nov-07		18:07:53		70.41		38		24-Dec-07		18:25:59		65.6		43

		13-Nov-07		20:07:10		73.4		37		13-Nov-07		20:06:20		69.8		42		13-Nov-07		20:07:53		70.41		42		24-Dec-07		20:25:59		65.01		45.5

		13-Nov-07		22:07:10		72.8		40		13-Nov-07		22:06:20		69.8		45		13-Nov-07		22:07:53		69.8		44		24-Dec-07		22:25:59		64.4		44.5

		14-Nov-07		0:07:10		72.21		42		14-Nov-07		0:06:20		69.2		47.5		14-Nov-07		0:07:53		69.8		45		25-Dec-07		0:25:59		63.8		45

		14-Nov-07		2:07:10		72.21		43		14-Nov-07		2:06:20		69.8		48		14-Nov-07		2:07:53		69.2		47.5		25-Dec-07		2:25:59		63.8		45

		14-Nov-07		4:07:10		71.6		44.5		14-Nov-07		4:06:20		69.2		50		14-Nov-07		4:07:53		68.61		48.5		25-Dec-07		4:25:59		63.21		44.5

		14-Nov-07		6:07:10		71		46		14-Nov-07		6:06:20		69.2		51.5		14-Nov-07		6:07:53		68.61		50		25-Dec-07		6:25:59		64.4		44

		14-Nov-07		8:07:10		73.4		45		14-Nov-07		8:06:20		69.8		51.5		14-Nov-07		8:07:53		70.41		44		25-Dec-07		8:25:59		66.81		40.5

		14-Nov-07		10:07:10		74.01		46		14-Nov-07		10:06:20		71.6		54.5		14-Nov-07		10:07:53		70.41		53		25-Dec-07		10:25:59		69.2		36.5

		14-Nov-07		12:07:10		74.01		47.5		14-Nov-07		12:06:20		72.21		54		14-Nov-07		12:07:53		70.41		47		25-Dec-07		12:25:59		70.41		34.5

		14-Nov-07		14:07:10		74.01		48		14-Nov-07		14:06:20		72.21		45		14-Nov-07		14:07:53		70.41		47		25-Dec-07		14:25:59		71		33

		14-Nov-07		16:07:10		74.6		49.5		14-Nov-07		16:06:20		71.6		44.5		14-Nov-07		16:07:53		71		59.5		25-Dec-07		16:25:59		70.41		33.5

		14-Nov-07		18:07:10		74.6		49.5		14-Nov-07		18:06:20		71		49		14-Nov-07		18:07:53		71		53.5		25-Dec-07		18:25:59		68.61		33.5

		14-Nov-07		20:07:10		74.01		49		14-Nov-07		20:06:20		70.41		52.5		14-Nov-07		20:07:53		70.41		57.5		25-Dec-07		20:25:59		66.81		35

		14-Nov-07		22:07:10		73.4		52		14-Nov-07		22:06:20		69.8		61		14-Nov-07		22:07:53		71		55.5		25-Dec-07		22:25:59		64.4		35.5

		15-Nov-07		0:07:10		72.8		52		15-Nov-07		0:06:20		69.8		57		15-Nov-07		0:07:53		71		54		26-Dec-07		0:25:59		63.21		35

		15-Nov-07		2:07:10		72.21		50.5		15-Nov-07		2:06:20		69.8		56		15-Nov-07		2:07:53		70.41		53.5		26-Dec-07		2:25:59		62.6		34

		15-Nov-07		4:07:10		71.6		47		15-Nov-07		4:06:20		68.61		50.5		15-Nov-07		4:07:53		69.8		50.5		26-Dec-07		4:25:59		62		33.5

		15-Nov-07		6:07:10		71		45.5		15-Nov-07		6:06:20		68.61		49		15-Nov-07		6:07:53		68.61		49.5		26-Dec-07		6:25:59		62		33

		15-Nov-07		8:07:10		72.21		43.5		15-Nov-07		8:06:20		69.2		47		15-Nov-07		8:07:53		70.41		47.5		26-Dec-07		8:25:59		62.6		32.5

		15-Nov-07		10:07:10		74.01		44.5		15-Nov-07		10:06:20		71.6		56		15-Nov-07		10:07:53		71		46.5		26-Dec-07		10:25:59		62		32.5

		15-Nov-07		12:07:10		74.01		46.5		15-Nov-07		12:06:20		71.6		54		15-Nov-07		12:07:53		71.6		50.5		26-Dec-07		12:25:59		62		33.5

		15-Nov-07		14:07:10		74.01		47.5		15-Nov-07		14:06:20		71.6		56		15-Nov-07		14:07:53		71		52		26-Dec-07		14:25:59		62.6		34.5

		15-Nov-07		16:07:10		74.6		50		15-Nov-07		16:06:20		71.6		45.5		15-Nov-07		16:07:53		70.41		56		26-Dec-07		16:25:59		63.8		35.5

		15-Nov-07		18:07:10		74.01		51		15-Nov-07		18:06:20		70.41		51		15-Nov-07		18:07:53		70.41		56		26-Dec-07		18:25:59		63.8		37

		15-Nov-07		20:07:10		73.4		50		15-Nov-07		20:06:20		69.8		56.5		15-Nov-07		20:07:53		71		55.5		26-Dec-07		20:25:59		63.21		38

		15-Nov-07		22:07:10		73.4		48.5		15-Nov-07		22:06:20		69.8		54.5		15-Nov-07		22:07:53		71.6		51.5		26-Dec-07		22:25:59		62.6		37.5

		16-Nov-07		0:07:10		72.8		46.5		16-Nov-07		0:06:20		69.8		51		16-Nov-07		0:07:53		71		50		27-Dec-07		0:25:59		62		38.5

		16-Nov-07		2:07:10		71.6		45.5		16-Nov-07		2:06:20		68.61		49.5		16-Nov-07		2:07:53		69.2		49		27-Dec-07		2:25:59		62		39

		16-Nov-07		4:07:10		71		45.5		16-Nov-07		4:06:20		68.61		49.5		16-Nov-07		4:07:53		68.61		49.5		27-Dec-07		4:25:59		62		38

		16-Nov-07		6:07:10		70.41		44		16-Nov-07		6:06:20		68.61		47.5		16-Nov-07		6:07:53		67.4		49		27-Dec-07		6:25:59		62		37.5

		16-Nov-07		8:07:10		71.6		42.5		16-Nov-07		8:06:20		68.61		46		16-Nov-07		8:07:53		70.41		46		27-Dec-07		8:25:59		63.21		36.5

		16-Nov-07		10:07:10		72.8		44.5		16-Nov-07		10:06:20		71		49.5		16-Nov-07		10:07:53		72.21		47		27-Dec-07		10:25:59		67.4		35

		16-Nov-07		12:07:10		73.4		45		16-Nov-07		12:06:20		71.6		50.5		16-Nov-07		12:07:53		71		47		27-Dec-07		12:25:59		72.21		30.5

		16-Nov-07		14:07:10		74.01		46.5		16-Nov-07		14:06:20		71.6		53.5		16-Nov-07		14:07:53		71.6		51.5		27-Dec-07		14:25:59		71		28

		16-Nov-07		16:07:10		74.01		50		16-Nov-07		16:06:20		71.6		52		16-Nov-07		16:07:53		71		60.5		27-Dec-07		16:25:59		71		26

		16-Nov-07		18:07:10		74.01		49.5		16-Nov-07		18:06:20		70.41		62		16-Nov-07		18:07:53		70.41		53.5		27-Dec-07		18:25:59		70.41		26

		16-Nov-07		20:07:10		73.4		51		16-Nov-07		20:06:20		69.8		57.5		16-Nov-07		20:07:53		70.41		57		27-Dec-07		20:25:59		69.2		26.5

		16-Nov-07		22:07:10		72.8		51		16-Nov-07		22:06:20		69.8		56.5		16-Nov-07		22:07:53		70.41		55.5		27-Dec-07		22:25:59		66.2		31.5

		17-Nov-07		0:07:10		72.21		50.5		17-Nov-07		0:06:20		69.8		56		17-Nov-07		0:07:53		70.41		54		28-Dec-07		0:25:59		63.8		29.5

		17-Nov-07		2:07:10		71.6		50.5		17-Nov-07		2:06:20		69.2		56		17-Nov-07		2:07:53		69.8		53.5		28-Dec-07		2:25:59		62.6		29.5

		17-Nov-07		4:07:10		71.6		50.5		17-Nov-07		4:06:20		69.2		55.5		17-Nov-07		4:07:53		69.2		54		28-Dec-07		4:25:59		62.6		29.5

		17-Nov-07		6:07:10		71		49.5		17-Nov-07		6:06:20		68		54		17-Nov-07		6:07:53		68.61		53.5		28-Dec-07		6:25:59		62.6		29

		17-Nov-07		8:07:10		71.6		49.5		17-Nov-07		8:06:20		68		55		17-Nov-07		8:07:53		71		53		28-Dec-07		8:25:59		65.01		28.5

		17-Nov-07		10:07:10		72.21		47.5		17-Nov-07		10:06:20		71		51.5		17-Nov-07		10:07:53		71		49.5		28-Dec-07		10:25:59		68.61		28

		17-Nov-07		12:07:10		73.4		47.5		17-Nov-07		12:06:20		72.21		55		17-Nov-07		12:07:53		71.6		55.5		28-Dec-07		12:25:59		71.6		27

		17-Nov-07		14:07:10		74.01		49.5		17-Nov-07		14:06:20		71		46		17-Nov-07		14:07:53		71		57.5		28-Dec-07		14:25:59		71		28.5

		17-Nov-07		16:07:10		74.6		50		17-Nov-07		16:06:20		71.6		48		17-Nov-07		16:07:53		70.41		58		28-Dec-07		16:25:59		71		28.5

		17-Nov-07		18:07:10		74.6		48.5		17-Nov-07		18:06:20		69.8		55		17-Nov-07		18:07:53		70.41		50		28-Dec-07		18:25:59		72.21		29.5

		17-Nov-07		20:07:10		72.8		47.5		17-Nov-07		20:06:20		69.8		52		17-Nov-07		20:07:53		69.8		52		28-Dec-07		20:25:59		71		32

		17-Nov-07		22:07:10		71.6		48		17-Nov-07		22:06:20		69.2		53.5		17-Nov-07		22:07:53		69.2		51.5		28-Dec-07		22:25:59		68		34.5

		18-Nov-07		0:07:10		71.6		49.5		18-Nov-07		0:06:20		68.61		54		18-Nov-07		0:07:53		69.2		53		29-Dec-07		0:25:59		65.6		35

		18-Nov-07		2:07:10		71		49		18-Nov-07		2:06:20		68		54.5		18-Nov-07		2:07:53		68		53		29-Dec-07		2:25:59		64.4		36

		18-Nov-07		4:07:10		70.41		50		18-Nov-07		4:06:20		68		55		18-Nov-07		4:07:53		67.4		53.5		29-Dec-07		4:25:59		63.21		37

		18-Nov-07		6:07:10		69.8		49.5		18-Nov-07		6:06:20		67.4		54.5		18-Nov-07		6:07:53		66.81		54		29-Dec-07		6:25:59		64.4		37.5

		18-Nov-07		8:07:10		69.8		49.5		18-Nov-07		8:06:20		67.4		54.5		18-Nov-07		8:07:53		67.4		53		29-Dec-07		8:25:59		66.81		36.5

		18-Nov-07		10:07:10		69.2		49.5		18-Nov-07		10:06:20		67.4		54.5		18-Nov-07		10:07:53		67.4		53		29-Dec-07		10:25:59		69.8		36

		18-Nov-07		12:07:10		69.8		51.5		18-Nov-07		12:06:20		67.4		56.5		18-Nov-07		12:07:53		67.4		55.5		29-Dec-07		12:25:59		72.8		34

		18-Nov-07		14:07:10		70.41		52		18-Nov-07		14:06:20		68.61		55.5		18-Nov-07		14:07:53		68		55.5		29-Dec-07		14:25:59		72.8		34

		18-Nov-07		16:07:10		71		53.5		18-Nov-07		16:06:20		69.2		53.5		18-Nov-07		16:07:53		69.8		58		29-Dec-07		16:25:59		73.4		33

		18-Nov-07		18:07:10		71.6		55		18-Nov-07		18:06:20		69.2		56		18-Nov-07		18:07:53		69.8		58.5		29-Dec-07		18:25:59		72.21		33.5

		18-Nov-07		20:07:10		71		52		18-Nov-07		20:06:20		69.2		55.5		18-Nov-07		20:07:53		69.8		54.5		29-Dec-07		20:25:59		71		34

		18-Nov-07		22:07:10		70.41		52		18-Nov-07		22:06:20		68.61		56		18-Nov-07		22:07:53		68.61		55		29-Dec-07		22:25:59		67.4		36

		19-Nov-07		0:07:10		70.41		52		19-Nov-07		0:06:20		68		56		19-Nov-07		0:07:53		68.61		54.5		30-Dec-07		0:25:59		65.01		37.5

		19-Nov-07		2:07:10		69.8		51		19-Nov-07		2:06:20		67.4		56		19-Nov-07		2:07:53		68		55		30-Dec-07		2:25:59		63.8		38

		19-Nov-07		4:07:10		69.8		51		19-Nov-07		4:06:20		67.4		56.5		19-Nov-07		4:07:53		67.4		55.5		30-Dec-07		4:25:59		63.21		39

		19-Nov-07		6:07:10		69.8		51		19-Nov-07		6:06:20		67.4		55.5		19-Nov-07		6:07:53		66.81		56		30-Dec-07		6:25:59		62.6		39.5

		19-Nov-07		8:07:10		69.2		51		19-Nov-07		8:06:20		67.4		55.5		19-Nov-07		8:07:53		67.4		54		30-Dec-07		8:25:59		62.6		40.5

		19-Nov-07		10:07:10		69.2		52		19-Nov-07		10:06:20		67.4		56.5		19-Nov-07		10:07:53		67.4		55.5		30-Dec-07		10:25:59		63.21		42.5

		19-Nov-07		12:07:10		69.8		54.5		19-Nov-07		12:06:20		68		60		19-Nov-07		12:07:53		67.4		58		30-Dec-07		12:25:59		63.21		43.5

		19-Nov-07		14:07:10		70.41		56.5		19-Nov-07		14:06:20		68.61		60		19-Nov-07		14:07:53		68.61		59.5		30-Dec-07		14:25:59		63.8		44.5

		19-Nov-07		16:07:10		71		59		19-Nov-07		16:06:20		69.2		65		19-Nov-07		16:07:53		69.2		61.5		30-Dec-07		16:25:59		63.21		45

		19-Nov-07		18:07:10		71		55		19-Nov-07		18:06:20		69.8		54		19-Nov-07		18:07:53		69.8		59		30-Dec-07		18:25:59		63.21		46

		19-Nov-07		20:07:10		71.6		53		19-Nov-07		20:06:20		69.8		55		19-Nov-07		20:07:53		69.8		56		30-Dec-07		20:25:59		62.6		46.5

		19-Nov-07		22:07:10		71		52		19-Nov-07		22:06:20		69.2		54.5		19-Nov-07		22:07:53		69.2		54.5		30-Dec-07		22:25:59		62.6		47

		20-Nov-07		0:07:10		70.41		50		20-Nov-07		0:06:20		68		53.5		20-Nov-07		0:07:53		68.61		53		31-Dec-07		0:25:59		62.6		47.5

		20-Nov-07		2:07:10		69.8		48.5		20-Nov-07		2:06:20		68		52.5		20-Nov-07		2:07:53		67.4		52.5		31-Dec-07		2:25:59		62.6		48

		20-Nov-07		4:07:10		69.2		50		20-Nov-07		4:06:20		67.4		54.5		20-Nov-07		4:07:53		66.81		54		31-Dec-07		4:25:59		62.6		48.5

		20-Nov-07		6:07:10		69.2		52.5		20-Nov-07		6:06:20		67.4		58		20-Nov-07		6:07:53		67.4		54.5		31-Dec-07		6:25:59		62		48

		20-Nov-07		8:07:10		71		54.5		20-Nov-07		8:06:20		68.61		60		20-Nov-07		8:07:53		69.8		56.5		31-Dec-07		8:25:59		63.21		46

		20-Nov-07		10:07:10		72.8		56		20-Nov-07		10:06:20		70.41		58		20-Nov-07		10:07:53		71		50		31-Dec-07		10:25:59		63.8		44

		20-Nov-07		12:07:10		74.6		50.5		20-Nov-07		12:06:20		71		58.5		20-Nov-07		12:07:53		71.6		58		31-Dec-07		12:25:59		65.01		42.5

		20-Nov-07		14:07:10		74.6		45.5		20-Nov-07		14:06:20		71.6		52		20-Nov-07		14:07:53		71		52		31-Dec-07		14:25:59		65.6		41.5

		20-Nov-07		16:07:10		74.01		41		20-Nov-07		16:06:20		72.21		44		20-Nov-07		16:07:53		70.41		51.5		31-Dec-07		16:25:59		65.6		40.5

		20-Nov-07		18:07:10		73.4		40.5		20-Nov-07		18:06:20		69.8		42.5		20-Nov-07		18:07:53		70.41		48		31-Dec-07		18:25:59		65.6		39

		20-Nov-07		20:07:10		72.8		40		20-Nov-07		20:06:20		69.8		42		20-Nov-07		20:07:53		69.2		45.5		31-Dec-07		20:25:59		64.4		38.5

		20-Nov-07		22:07:10		71.6		39.5		20-Nov-07		22:06:20		68.61		42.5		20-Nov-07		22:07:53		68.61		44		31-Dec-07		22:25:59		62.6		38.5

		21-Nov-07		0:07:10		71		39		21-Nov-07		0:06:20		68.61		40.5		21-Nov-07		0:07:53		68		43		1-Jan-08		0:25:59		62.6		37

		21-Nov-07		2:07:10		70.41		38.5		21-Nov-07		2:06:20		68		40.5		21-Nov-07		2:07:53		66.2		43.5		1-Jan-08		2:25:59		62		36

		21-Nov-07		4:07:10		69.8		37		21-Nov-07		4:06:20		68		39.5		21-Nov-07		4:07:53		65.01		43.5		1-Jan-08		4:25:59		62		35

		21-Nov-07		6:07:10		69.2		36.5		21-Nov-07		6:06:20		68		38.5		21-Nov-07		6:07:53		67.4		39.5		1-Jan-08		6:25:59		62.6		33.5

		21-Nov-07		8:07:10		71		35.5		21-Nov-07		8:06:20		68		37		21-Nov-07		8:07:53		68.61		38		1-Jan-08		8:25:59		65.01		32.5

		21-Nov-07		10:07:10		71.6		35.5		21-Nov-07		10:06:20		69.8		34.5		21-Nov-07		10:07:53		71.6		37		1-Jan-08		10:25:59		68		31

		21-Nov-07		12:07:10		72.8		33.5		21-Nov-07		12:06:20		70.41		34.5		21-Nov-07		12:07:53		70.41		38.5		1-Jan-08		12:25:59		72.21		30.5

		21-Nov-07		14:07:10		73.4		33.5		21-Nov-07		14:06:20		71		35		21-Nov-07		14:07:53		71.6		34.5		1-Jan-08		14:25:59		71.6		31.5

		21-Nov-07		16:07:10		74.6		33.5		21-Nov-07		16:06:20		71		36		21-Nov-07		16:07:53		71		37.5		1-Jan-08		16:25:59		72.21		30.5

		21-Nov-07		18:07:10		74.01		35		21-Nov-07		18:06:20		69.8		37.5		21-Nov-07		18:07:53		70.41		38.5		1-Jan-08		18:25:59		71		31.5

		21-Nov-07		20:07:10		72.8		34		21-Nov-07		20:06:20		69.2		36		21-Nov-07		20:07:53		70.41		38		1-Jan-08		20:25:59		70.41		31.5

		21-Nov-07		22:07:10		71		34		21-Nov-07		22:06:20		68.61		36.5		21-Nov-07		22:07:53		68		37.5		1-Jan-08		22:25:59		66.2		32.5

		22-Nov-07		0:07:10		70.41		33.5		22-Nov-07		0:06:20		68		35.5		22-Nov-07		0:07:53		65.6		38		2-Jan-08		0:25:59		63.8		33

		22-Nov-07		2:07:10		69.8		32		22-Nov-07		2:06:20		68		34		22-Nov-07		2:07:53		64.4		38		2-Jan-08		2:25:59		62.6		33

		22-Nov-07		4:07:10		69.2		31		22-Nov-07		4:06:20		67.4		33		22-Nov-07		4:07:53		63.21		37.5		2-Jan-08		4:25:59		62		32.5

		22-Nov-07		6:07:10		68.61		31		22-Nov-07		6:06:20		68		32.5		22-Nov-07		6:07:53		66.81		33.5		2-Jan-08		6:25:59		62.6		31.5

		22-Nov-07		8:07:10		70.41		30.5		22-Nov-07		8:06:20		69.8		31.5		22-Nov-07		8:07:53		69.2		32		2-Jan-08		8:25:59		63.8		31

		22-Nov-07		10:07:10		71.6		31.5		22-Nov-07		10:06:20		70.41		33.5		22-Nov-07		10:07:53		71.6		33		2-Jan-08		10:25:59		64.4		31

		22-Nov-07		12:07:10		72.21		32.5		22-Nov-07		12:06:20		71		34		22-Nov-07		12:07:53		70.41		35.5		2-Jan-08		12:25:59		66.81		32.5

		22-Nov-07		14:07:10		73.4		31.5		22-Nov-07		14:06:20		71		32.5		22-Nov-07		14:07:53		71.6		33.5		2-Jan-08		14:25:59		68.61		34

		22-Nov-07		16:07:10		73.4		29		22-Nov-07		16:06:20		69.8		29		22-Nov-07		16:07:53		71.6		33		2-Jan-08		16:25:59		70.41		34.5

		22-Nov-07		18:07:10		74.01		31.5		22-Nov-07		18:06:20		69.8		34		22-Nov-07		18:07:53		70.41		36		2-Jan-08		18:25:59		71		33.5

		22-Nov-07		20:07:10		71.6		31		22-Nov-07		20:06:20		68.61		33		22-Nov-07		20:07:53		69.8		34.5		2-Jan-08		20:25:59		70.41		33

		22-Nov-07		22:07:10		70.41		31.5		22-Nov-07		22:06:20		66.81		34.5		22-Nov-07		22:07:53		66.81		35.5		2-Jan-08		22:25:59		66.2		34.5

		23-Nov-07		0:07:10		69.2		31.5		23-Nov-07		0:06:20		66.2		35		23-Nov-07		0:07:53		64.4		37		3-Jan-08		0:25:59		64.4		35.5

		23-Nov-07		2:07:10		68.61		31		23-Nov-07		2:06:20		66.2		34		23-Nov-07		2:07:53		63.21		37		3-Jan-08		2:25:59		62.6		35.5

		23-Nov-07		4:07:10		68		31		23-Nov-07		4:06:20		66.2		33.5		23-Nov-07		4:07:53		62		36.5		3-Jan-08		4:25:59		62		36

		23-Nov-07		6:07:10		67.4		30		23-Nov-07		6:06:20		66.2		31.5		23-Nov-07		6:07:53		66.2		32.5		3-Jan-08		6:25:59		63.8		36

		23-Nov-07		8:07:10		69.2		28.5		23-Nov-07		8:06:20		67.4		30		23-Nov-07		8:07:53		67.4		31		3-Jan-08		8:25:59		65.01		34.5

		23-Nov-07		10:07:10		69.8		30		23-Nov-07		10:06:20		68		33		23-Nov-07		10:07:53		68		32.5		3-Jan-08		10:25:59		67.4		35

		23-Nov-07		12:07:10		70.41		31.5		23-Nov-07		12:06:20		68.61		33		23-Nov-07		12:07:53		68.61		33.5		3-Jan-08		12:25:59		72.8		33.5

		23-Nov-07		14:07:10		71		31		23-Nov-07		14:06:20		69.2		32		23-Nov-07		14:07:53		69.2		34		3-Jan-08		14:25:59		73.4		33

		23-Nov-07		16:07:10		71.6		29.5		23-Nov-07		16:06:20		69.2		29		23-Nov-07		16:07:53		69.8		32.5		3-Jan-08		16:25:59		72.8		34

		23-Nov-07		18:07:10		71.6		31.5		23-Nov-07		18:06:20		69.8		31.5		23-Nov-07		18:07:53		69.8		34		3-Jan-08		18:25:59		72.8		34.5

		23-Nov-07		20:07:10		71.6		32		23-Nov-07		20:06:20		68.61		35		23-Nov-07		20:07:53		68.61		36		3-Jan-08		20:25:59		71.6		35

		23-Nov-07		22:07:10		69.8		32		23-Nov-07		22:06:20		67.4		35.5		23-Nov-07		22:07:53		66.81		36		3-Jan-08		22:25:59		68		36

		24-Nov-07		0:07:10		68.61		32		24-Nov-07		0:06:20		66.2		35.5		24-Nov-07		0:07:53		65.01		36.5		4-Jan-08		0:25:59		65.6		36.5

		24-Nov-07		2:07:10		68		31.5		24-Nov-07		2:06:20		66.2		33.5		24-Nov-07		2:07:53		63.8		36.5		4-Jan-08		2:25:59		64.4		38

		24-Nov-07		4:07:10		67.4		30.5		24-Nov-07		4:06:20		66.2		31.5		24-Nov-07		4:07:53		62.6		35.5		4-Jan-08		4:25:59		63.8		39

		24-Nov-07		6:07:10		67.4		30.5		24-Nov-07		6:06:20		66.2		32.5		24-Nov-07		6:07:53		66.81		32		4-Jan-08		6:25:59		65.01		41

		24-Nov-07		8:07:10		69.2		27		24-Nov-07		8:06:20		68		28		24-Nov-07		8:07:53		68		30		4-Jan-08		8:25:59		68.61		40

		24-Nov-07		10:07:10		70.41		23.5		24-Nov-07		10:06:20		69.2		22		24-Nov-07		10:07:53		68		26		4-Jan-08		10:25:59		71.6		41

		24-Nov-07		12:07:10		71		20.5		24-Nov-07		12:06:20		69.2		18.5		24-Nov-07		12:07:53		68.61		24		4-Jan-08		12:25:59		74.01		40.5

		24-Nov-07		14:07:10		71		19		24-Nov-07		14:06:20		69.2		16		24-Nov-07		14:07:53		69.2		23		4-Jan-08		14:25:59		73.4		42.5

		24-Nov-07		16:07:10		71.6		18.5		24-Nov-07		16:06:20		69.2		16.5		24-Nov-07		16:07:53		69.8		22		4-Jan-08		16:25:59		74.01		41.5

		24-Nov-07		18:07:10		71.6		18.5		24-Nov-07		18:06:20		69.2		17		24-Nov-07		18:07:53		70.41		22		4-Jan-08		18:25:59		73.4		42

		24-Nov-07		20:07:10		71.6		21		24-Nov-07		20:06:20		69.2		22		24-Nov-07		20:07:53		69.2		24.5		4-Jan-08		20:25:59		72.8		43

		24-Nov-07		22:07:10		69.8		24.5		24-Nov-07		22:06:20		67.4		28		24-Nov-07		22:07:53		67.4		28		4-Jan-08		22:25:59		69.8		44

		25-Nov-07		0:07:10		69.2		25.5		25-Nov-07		0:06:20		66.81		29		25-Nov-07		0:07:53		65.6		29.5		5-Jan-08		0:25:59		68		45

		25-Nov-07		2:07:10		68		25.5		25-Nov-07		2:06:20		66.2		28.5		25-Nov-07		2:07:53		63.8		30.5		5-Jan-08		2:25:59		67.4		45.5

		25-Nov-07		4:07:10		67.4		26		25-Nov-07		4:06:20		66.2		28.5		25-Nov-07		4:07:53		62.6		30.5		5-Jan-08		4:25:59		66.81		46

		25-Nov-07		6:07:10		66.81		25.5		25-Nov-07		6:06:20		66.2		28		25-Nov-07		6:07:53		62		31		5-Jan-08		6:25:59		67.4		49

		25-Nov-07		8:07:10		67.4		24.5		25-Nov-07		8:06:20		67.4		26		25-Nov-07		8:07:53		66.81		26.5		5-Jan-08		8:25:59		71.6		48.5

		25-Nov-07		10:07:10		68		26.5		25-Nov-07		10:06:20		68		29		25-Nov-07		10:07:53		67.4		28		5-Jan-08		10:25:59		73.4		48.5

		25-Nov-07		12:07:10		68.61		27.5		25-Nov-07		12:06:20		68		29		25-Nov-07		12:07:53		67.4		30		5-Jan-08		12:25:59		72.8		48.5

		25-Nov-07		14:07:10		69.2		26		25-Nov-07		14:06:20		69.2		26		25-Nov-07		14:07:53		68		29		5-Jan-08		14:25:59		72.21		46

		25-Nov-07		16:07:10		69.8		27.5		25-Nov-07		16:06:20		69.2		28.5		25-Nov-07		16:07:53		68.61		30.5		5-Jan-08		16:25:59		72.8		44.5

		25-Nov-07		18:07:10		70.41		29.5		25-Nov-07		18:06:20		69.2		30.5		25-Nov-07		18:07:53		68.61		31.5		5-Jan-08		18:25:59		73.4		42

		25-Nov-07		20:07:10		69.2		29.5		25-Nov-07		20:06:20		68		32		25-Nov-07		20:07:53		67.4		32.5		5-Jan-08		20:25:59		72.21		41.5

		25-Nov-07		22:07:10		68.61		32		25-Nov-07		22:06:20		66.81		35.5		25-Nov-07		22:07:53		66.2		35		5-Jan-08		22:25:59		68.61		43.5

		26-Nov-07		0:07:10		68		32		26-Nov-07		0:06:20		66.2		35.5		26-Nov-07		0:07:53		65.01		36		6-Jan-08		0:25:59		67.4		44

		26-Nov-07		2:07:10		68		32.5		26-Nov-07		2:06:20		66.2		35.5		26-Nov-07		2:07:53		63.8		37		6-Jan-08		2:25:59		66.2		43.5

		26-Nov-07		4:07:10		67.4		32.5		26-Nov-07		4:06:20		66.2		35.5		26-Nov-07		4:07:53		63.21		37.5		6-Jan-08		4:25:59		65.6		43.5

		26-Nov-07		6:07:10		67.4		33		26-Nov-07		6:06:20		66.2		35.5		26-Nov-07		6:07:53		62.6		38		6-Jan-08		6:25:59		65.01		43.5

		26-Nov-07		8:07:10		68		32.5		26-Nov-07		8:06:20		67.4		34.5		26-Nov-07		8:07:53		67.4		34		6-Jan-08		8:25:59		64.4		43.5

		26-Nov-07		10:07:10		68		34		26-Nov-07		10:06:20		67.4		36.5		26-Nov-07		10:07:53		67.4		36		6-Jan-08		10:25:59		64.4		44.5

		26-Nov-07		12:07:10		68.61		34.5		26-Nov-07		12:06:20		67.4		37		26-Nov-07		12:07:53		68		35.5		6-Jan-08		12:25:59		64.4		45.5

		26-Nov-07		14:07:10		68.61		32		26-Nov-07		14:06:20		68		32		26-Nov-07		14:07:53		68		34		6-Jan-08		14:25:59		64.4		47

		26-Nov-07		16:07:10		69.2		32		26-Nov-07		16:06:20		68.61		33		26-Nov-07		16:07:53		67.4		34.5		6-Jan-08		16:25:59		65.01		47.5

		26-Nov-07		18:07:10		69.2		33		26-Nov-07		18:06:20		68		35		26-Nov-07		18:07:53		68		35.5		6-Jan-08		18:25:59		64.4		47.5

		26-Nov-07		20:07:10		68.61		34		26-Nov-07		20:06:20		67.4		36.5		26-Nov-07		20:07:53		66.81		36.5		6-Jan-08		20:25:59		64.4		47.5

		26-Nov-07		22:07:10		68		33.5		26-Nov-07		22:06:20		66.2		36		26-Nov-07		22:07:53		64.4		37.5		6-Jan-08		22:25:59		64.4		46.5

		27-Nov-07		0:07:10		67.4		33		27-Nov-07		0:06:20		66.2		36		27-Nov-07		0:07:53		63.8		38		7-Jan-08		0:25:59		64.4		46

		27-Nov-07		2:07:10		66.81		32		27-Nov-07		2:06:20		66.2		34		27-Nov-07		2:07:53		62.6		36.5		7-Jan-08		2:25:59		63.8		45

		27-Nov-07		4:07:10		66.81		31.5		27-Nov-07		4:06:20		65.6		32.5		27-Nov-07		4:07:53		62		36.5		7-Jan-08		4:25:59		63.8		44.5

		27-Nov-07		6:07:10		66.81		30.5		27-Nov-07		6:06:20		65.6		32		27-Nov-07		6:07:53		66.81		32		7-Jan-08		6:25:59		63.21		43.5

		27-Nov-07		8:07:10		69.2		28.5		27-Nov-07		8:06:20		67.4		30.5		27-Nov-07		8:07:53		68.61		30.5		7-Jan-08		8:25:59		63.21		43

		27-Nov-07		10:07:10		69.8		31		27-Nov-07		10:06:20		69.8		32.5		27-Nov-07		10:07:53		69.2		32		7-Jan-08		10:25:59		63.8		42

		27-Nov-07		12:07:10		71		32.5		27-Nov-07		12:06:20		71.6		34		27-Nov-07		12:07:53		71		33.5		7-Jan-08		12:25:59		63.8		43

		27-Nov-07		14:07:10		71.6		34		27-Nov-07		14:06:20		71		35.5		27-Nov-07		14:07:53		71		34.5		7-Jan-08		14:25:59		65.01		44.5

		27-Nov-07		16:07:10		72.21		34		27-Nov-07		16:06:20		71.6		37.5		27-Nov-07		16:07:53		70.41		38		7-Jan-08		16:25:59		65.01		44.5

		27-Nov-07		18:07:10		72.21		36.5		27-Nov-07		18:06:20		69.8		39.5		27-Nov-07		18:07:53		69.8		39		7-Jan-08		18:25:59		65.6		44

		27-Nov-07		20:07:10		71.6		36.5		27-Nov-07		20:06:20		68.61		40		27-Nov-07		20:07:53		69.2		39.5		7-Jan-08		20:25:59		64.4		44.5

		27-Nov-07		22:07:10		69.8		35		27-Nov-07		22:06:20		67.4		38.5		27-Nov-07		22:07:53		67.4		38.5		7-Jan-08		22:25:59		63.8		45

		28-Nov-07		0:07:10		69.2		35		28-Nov-07		0:06:20		66.81		38.5		28-Nov-07		0:07:53		66.2		38.5		8-Jan-08		0:25:59		63.8		45.5

		28-Nov-07		2:07:10		68		34.5		28-Nov-07		2:06:20		66.2		38		28-Nov-07		2:07:53		65.01		39		8-Jan-08		2:25:59		63.8		45.5

		28-Nov-07		4:07:10		68		34		28-Nov-07		4:06:20		66.2		37		28-Nov-07		4:07:53		63.8		39		8-Jan-08		4:25:59		63.8		46

		28-Nov-07		6:07:10		67.4		34.5		28-Nov-07		6:06:20		66.2		37.5		28-Nov-07		6:07:53		67.4		35.5		8-Jan-08		6:25:59		65.01		45

		28-Nov-07		8:07:10		69.8		34		28-Nov-07		8:06:20		68		36.5		28-Nov-07		8:07:53		69.2		36.5		8-Jan-08		8:25:59		67.4		40.5

		28-Nov-07		10:07:10		71		34.5		28-Nov-07		10:06:20		70.41		36.5		28-Nov-07		10:07:53		71.6		36		8-Jan-08		10:25:59		69.8		39

		28-Nov-07		12:07:10		72.21		39		28-Nov-07		12:06:20		71		43.5		28-Nov-07		12:07:53		71		41		8-Jan-08		12:25:59		73.4		39

		28-Nov-07		14:07:10		72.8		34		28-Nov-07		14:06:20		71		34		28-Nov-07		14:07:53		71		39		8-Jan-08		14:25:59		72.8		37

		28-Nov-07		16:07:10		72.8		33.5		28-Nov-07		16:06:20		71.6		34.5		28-Nov-07		16:07:53		71		37.5		8-Jan-08		16:25:59		72.21		36

		28-Nov-07		18:07:10		72.8		35		28-Nov-07		18:06:20		70.41		37.5		28-Nov-07		18:07:53		71		37.5		8-Jan-08		18:25:59		72.21		35.5

		28-Nov-07		20:07:10		72.8		35		28-Nov-07		20:06:20		69.8		37.5		28-Nov-07		20:07:53		70.41		38.5		8-Jan-08		20:25:59		71.6		34.5

		28-Nov-07		22:07:10		71.6		35		28-Nov-07		22:06:20		68.61		38		28-Nov-07		22:07:53		69.2		38		8-Jan-08		22:25:59		68		37.5

		29-Nov-07		0:07:10		70.41		35.5		29-Nov-07		0:06:20		67.4		38.5		29-Nov-07		0:07:53		68		38		9-Jan-08		0:25:59		66.81		38

		29-Nov-07		2:07:10		69.2		34		29-Nov-07		2:06:20		66.81		37		29-Nov-07		2:07:53		66.2		38		9-Jan-08		2:25:59		65.6		39

		29-Nov-07		4:07:10		68.61		33		29-Nov-07		4:06:20		66.81		35.5		29-Nov-07		4:07:53		65.01		37.5		9-Jan-08		4:25:59		65.01		39.5

		29-Nov-07		6:07:10		68.61		32		29-Nov-07		6:06:20		66.2		33.5		29-Nov-07		6:07:53		66.81		34.5		9-Jan-08		6:25:59		65.6		39.5

		29-Nov-07		8:07:10		70.41		30.5		29-Nov-07		8:06:20		68		32		29-Nov-07		8:07:53		68		33.5		9-Jan-08		8:25:59		68.61		38

		29-Nov-07		10:07:10		71.6		32.5		29-Nov-07		10:06:20		71		34.5		29-Nov-07		10:07:53		70.41		34		9-Jan-08		10:25:59		71		40

		29-Nov-07		12:07:10		72.8		31		29-Nov-07		12:06:20		71.6		32.5		29-Nov-07		12:07:53		71		33		9-Jan-08		12:25:59		73.4		39

		29-Nov-07		14:07:10		72.8		31		29-Nov-07		14:06:20		71.6		32.5		29-Nov-07		14:07:53		71.6		31		9-Jan-08		14:25:59		74.01		40

		29-Nov-07		16:07:10		72.8		30.5		29-Nov-07		16:06:20		71.6		31.5		29-Nov-07		16:07:53		71		35		9-Jan-08		16:25:59		74.6		41

		29-Nov-07		18:07:10		72.8		28		29-Nov-07		18:06:20		69.2		29		29-Nov-07		18:07:53		71		32		9-Jan-08		18:25:59		75.2		41.5

		29-Nov-07		20:07:10		72.21		30		29-Nov-07		20:06:20		69.2		31		29-Nov-07		20:07:53		69.8		32.5		9-Jan-08		20:25:59		73.4		41.5

		29-Nov-07		22:07:10		70.41		31		29-Nov-07		22:06:20		67.4		34		29-Nov-07		22:07:53		68		34		9-Jan-08		22:25:59		69.8		42.5

		30-Nov-07		0:07:10		69.2		31		30-Nov-07		0:06:20		66.81		34		30-Nov-07		0:07:53		66.2		34.5		10-Jan-08		0:25:59		68		44

		30-Nov-07		2:07:10		68.61		30.5		30-Nov-07		2:06:20		66.2		33.5		30-Nov-07		2:07:53		65.01		35		10-Jan-08		2:25:59		66.81		44.5

		30-Nov-07		4:07:10		68		30		30-Nov-07		4:06:20		65.6		33		30-Nov-07		4:07:53		63.21		35		10-Jan-08		4:25:59		66.2		45

		30-Nov-07		6:07:10		67.4		30		30-Nov-07		6:06:20		66.2		32		30-Nov-07		6:07:53		67.4		31		10-Jan-08		6:25:59		68		45

		30-Nov-07		8:07:10		69.8		28		30-Nov-07		8:06:20		68.61		30.5		30-Nov-07		8:07:53		68		31		10-Jan-08		8:25:59		71.6		41.5

		30-Nov-07		10:07:10		71		30		30-Nov-07		10:06:20		70.41		33		30-Nov-07		10:07:53		70.41		32		10-Jan-08		10:25:59		73.4		40.5

		30-Nov-07		12:07:10		71.6		31.5		30-Nov-07		12:06:20		71		31		30-Nov-07		12:07:53		71.6		31.5		10-Jan-08		12:25:59		74.6		39.5

		30-Nov-07		14:07:10		72.8		30		30-Nov-07		14:06:20		71		31		30-Nov-07		14:07:53		71		35		10-Jan-08		14:25:59		74.6		39

		30-Nov-07		16:07:10		73.4		28		30-Nov-07		16:06:20		71		29		30-Nov-07		16:07:53		71		32.5		10-Jan-08		16:25:59		74.6		39

		30-Nov-07		18:07:10		73.4		26.5		30-Nov-07		18:06:20		69.8		26.5		30-Nov-07		18:07:53		69.8		31		10-Jan-08		18:25:59		73.4		39.5

		30-Nov-07		20:07:10		72.21		26		30-Nov-07		20:06:20		69.2		27.5		30-Nov-07		20:07:53		69.2		29		10-Jan-08		20:25:59		74.01		38.5

		30-Nov-07		22:07:10		71		27.5		30-Nov-07		22:06:20		68		30.5		30-Nov-07		22:07:53		68		31		10-Jan-08		22:25:59		70.41		43

		1-Dec-07		0:07:10		69.8		28.5		1-Dec-07		0:06:20		67.4		32		1-Dec-07		0:07:53		66.81		32.5		11-Jan-08		0:25:59		68.61		42.5

		1-Dec-07		2:07:10		69.2		28.5		1-Dec-07		2:06:20		66.81		31.5		1-Dec-07		2:07:53		65.01		33		11-Jan-08		2:25:59		67.4		43.5

		1-Dec-07		4:07:10		68.61		28		1-Dec-07		4:06:20		66.2		30.5		1-Dec-07		4:07:53		64.4		33		11-Jan-08		4:25:59		66.2		44

		1-Dec-07		6:07:10		68.61		28		1-Dec-07		6:06:20		66.2		30.5		1-Dec-07		6:07:53		66.81		30.5		11-Jan-08		6:25:59		68		44.5

		1-Dec-07		8:07:10		70.41		27		1-Dec-07		8:06:20		68		29		1-Dec-07		8:07:53		69.2		29.5		11-Jan-08		8:25:59		71.6		42

		1-Dec-07		10:07:10		71		27.5		1-Dec-07		10:06:20		70.41		29.5		1-Dec-07		10:07:53		71		29		11-Jan-08		10:25:59		74.01		41.5

		1-Dec-07		12:07:10		72.21		26.5		1-Dec-07		12:06:20		71.6		27		1-Dec-07		12:07:53		71		29.5		11-Jan-08		12:25:59		74.6		41

		1-Dec-07		14:07:10		72.8		24.5		1-Dec-07		14:06:20		71		26		1-Dec-07		14:07:53		70.41		29		11-Jan-08		14:25:59		74.01		43

		1-Dec-07		16:07:10		72.8		24.5		1-Dec-07		16:06:20		71		25.5		1-Dec-07		16:07:53		70.41		28		11-Jan-08		16:25:59		73.4		44.5

		1-Dec-07		18:07:10		72.8		26.5		1-Dec-07		18:06:20		69.8		28.5		1-Dec-07		18:07:53		70.41		30.5		11-Jan-08		18:25:59		71.6		45.5

		1-Dec-07		20:07:10		71.6		24.5		1-Dec-07		20:06:20		68		26		1-Dec-07		20:07:53		68.61		28		11-Jan-08		20:25:59		69.2		46.5

		1-Dec-07		22:07:10		69.8		24.5		1-Dec-07		22:06:20		66.81		27.5		1-Dec-07		22:07:53		66.2		28.5		11-Jan-08		22:25:59		68.61		47

		2-Dec-07		0:07:10		68.61		26		2-Dec-07		0:06:20		66.2		28		2-Dec-07		0:07:53		64.4		31.5		12-Jan-08		0:25:59		67.4		47.5

		2-Dec-07		2:07:10		68		25		2-Dec-07		2:06:20		65.6		28		2-Dec-07		2:07:53		63.21		30.5		12-Jan-08		2:25:59		66.81		48

		2-Dec-07		4:07:10		67.4		24.5		2-Dec-07		4:06:20		65.6		26.5		2-Dec-07		4:07:53		62		29.5		12-Jan-08		4:25:59		66.2		48

		2-Dec-07		6:07:10		66.81		24		2-Dec-07		6:06:20		65.6		26		2-Dec-07		6:07:53		61.41		29		12-Jan-08		6:25:59		66.2		49

		2-Dec-07		8:07:10		67.4		23		2-Dec-07		8:06:20		67.4		24.5		2-Dec-07		8:07:53		66.81		25.5		12-Jan-08		8:25:59		69.8		44.5

		2-Dec-07		10:07:10		67.4		24.5		2-Dec-07		10:06:20		67.4		26		2-Dec-07		10:07:53		68.61		25		12-Jan-08		10:25:59		71.6		43.5

		2-Dec-07		12:07:10		68		27		2-Dec-07		12:06:20		68		28.5		2-Dec-07		12:07:53		68.61		28		12-Jan-08		12:25:59		70.41		45

		2-Dec-07		14:07:10		68.61		27.5		2-Dec-07		14:06:20		68		28.5		2-Dec-07		14:07:53		69.2		29		12-Jan-08		14:25:59		71		44.5

		2-Dec-07		16:07:10		69.2		28		2-Dec-07		16:06:20		68		29.5		2-Dec-07		16:07:53		68		30		12-Jan-08		16:25:59		70.41		44

		2-Dec-07		18:07:10		69.2		28.5		2-Dec-07		18:06:20		68		30		2-Dec-07		18:07:53		67.4		31		12-Jan-08		18:25:59		69.8		44

		2-Dec-07		20:07:10		68		30		2-Dec-07		20:06:20		66.81		33		2-Dec-07		20:07:53		67.4		31		12-Jan-08		20:25:59		68.61		44.5

		2-Dec-07		22:07:10		67.4		29.5		2-Dec-07		22:06:20		66.2		32.5		2-Dec-07		22:07:53		63.8		33.5		12-Jan-08		22:25:59		67.4		46

		3-Dec-07		0:07:10		66.81		29.5		3-Dec-07		0:06:20		65.6		32		3-Dec-07		0:07:53		62.6		33.5		13-Jan-08		0:25:59		66.2		46.5

		3-Dec-07		2:07:10		66.81		30		3-Dec-07		2:06:20		66.2		33		3-Dec-07		2:07:53		62		34.5		13-Jan-08		2:25:59		66.2		47

		3-Dec-07		4:07:10		66.81		32.5		3-Dec-07		4:06:20		66.2		36		3-Dec-07		4:07:53		62.6		37.5		13-Jan-08		4:25:59		65.6		47

		3-Dec-07		6:07:10		66.81		35		3-Dec-07		6:06:20		66.2		39		3-Dec-07		6:07:53		62.6		40		13-Jan-08		6:25:59		65.01		47

		3-Dec-07		8:07:10		68		35.5		3-Dec-07		8:06:20		67.4		38		3-Dec-07		8:07:53		68.61		36		13-Jan-08		8:25:59		65.01		47.5

		3-Dec-07		10:07:10		68		35		3-Dec-07		10:06:20		67.4		37		3-Dec-07		10:07:53		68		36.5		13-Jan-08		10:25:59		65.01		48.5

		3-Dec-07		12:07:10		68		36		3-Dec-07		12:06:20		67.4		38		3-Dec-07		12:07:53		67.4		37.5		13-Jan-08		12:25:59		65.01		50

		3-Dec-07		14:07:10		68.61		36.5		3-Dec-07		14:06:20		68		39		3-Dec-07		14:07:53		68		38		13-Jan-08		14:25:59		65.6		51

		3-Dec-07		16:07:10		69.2		39		3-Dec-07		16:06:20		68		42.5		3-Dec-07		16:07:53		67.4		41		13-Jan-08		16:25:59		66.81		50

		3-Dec-07		18:07:10		69.2		39.5		3-Dec-07		18:06:20		68		42.5		3-Dec-07		18:07:53		67.4		42		13-Jan-08		18:25:59		67.4		49.5

		3-Dec-07		20:07:10		68.61		41		3-Dec-07		20:06:20		67.4		44.5		3-Dec-07		20:07:53		67.4		43		13-Jan-08		20:25:59		66.2		49.5

		3-Dec-07		22:07:10		68.61		44.5		3-Dec-07		22:06:20		66.81		50		3-Dec-07		22:07:53		66.2		47.5		13-Jan-08		22:25:59		65.6		49

		4-Dec-07		0:07:10		68.61		43		4-Dec-07		0:06:20		66.81		47		4-Dec-07		0:07:53		66.2		46.5		14-Jan-08		0:25:59		65.01		48

		4-Dec-07		2:07:10		68.61		42		4-Dec-07		2:06:20		66.81		45.5		4-Dec-07		2:07:53		66.2		45.5		14-Jan-08		2:25:59		64.4		48.5

		4-Dec-07		4:07:10		68.61		40.5		4-Dec-07		4:06:20		67.4		43		4-Dec-07		4:07:53		66.2		44.5		14-Jan-08		4:25:59		64.4		49

		4-Dec-07		6:07:10		68.61		40		4-Dec-07		6:06:20		67.4		42		4-Dec-07		6:07:53		66.2		44		14-Jan-08		6:25:59		64.4		49.5

		4-Dec-07		8:07:10		71.6		37		4-Dec-07		8:06:20		69.2		39		4-Dec-07		8:07:53		69.2		41		14-Jan-08		8:25:59		65.01		50.5

		4-Dec-07		10:07:10		72.8		39		4-Dec-07		10:06:20		71		42		4-Dec-07		10:07:53		70.41		43.5		14-Jan-08		10:25:59		65.6		49.5

		4-Dec-07		12:07:10		74.6		37.5		4-Dec-07		12:06:20		71.6		39		4-Dec-07		12:07:53		71		38.5		14-Jan-08		12:25:59		66.2		49

		4-Dec-07		14:07:10		73.4		38		4-Dec-07		14:06:20		71		42.5		4-Dec-07		14:07:53		71		39.5		14-Jan-08		14:25:59		66.81		48.5

		4-Dec-07		16:07:10		74.01		39.5		4-Dec-07		16:06:20		71.6		41.5		4-Dec-07		16:07:53		70.41		40		14-Jan-08		16:25:59		66.81		49

		4-Dec-07		18:07:10		74.01		40		4-Dec-07		18:06:20		70.41		42		4-Dec-07		18:07:53		71		45		14-Jan-08		18:25:59		66.81		49.5

		4-Dec-07		20:07:10		72.8		40.5		4-Dec-07		20:06:20		69.8		44		4-Dec-07		20:07:53		70.41		44		14-Jan-08		20:25:59		66.2		49

		4-Dec-07		22:07:10		72.21		44		4-Dec-07		22:06:20		69.8		50.5		4-Dec-07		22:07:53		69.8		46.5		14-Jan-08		22:25:59		65.01		49

		5-Dec-07		0:07:10		72.21		47		5-Dec-07		0:06:20		69.2		53.5		5-Dec-07		0:07:53		69.8		49.5		15-Jan-08		0:25:59		64.4		47.5

		5-Dec-07		2:07:10		71.6		48.5		5-Dec-07		2:06:20		69.2		54.5		5-Dec-07		2:07:53		69.2		51		15-Jan-08		2:25:59		63.8		47

		5-Dec-07		4:07:10		71		49.5		5-Dec-07		4:06:20		69.2		55		5-Dec-07		4:07:53		68.61		52.5		15-Jan-08		4:25:59		63.8		46.5

		5-Dec-07		6:07:10		71		50.5		5-Dec-07		6:06:20		68.61		56		5-Dec-07		6:07:53		68		53.5		15-Jan-08		6:25:59		64.4		46.5

		5-Dec-07		8:07:10		73.4		50		5-Dec-07		8:06:20		69.8		57.5		5-Dec-07		8:07:53		71		53		15-Jan-08		8:25:59		67.4		44

		5-Dec-07		10:07:10		74.01		49		5-Dec-07		10:06:20		71		44		5-Dec-07		10:07:53		71		57.5		15-Jan-08		10:25:59		71		43.5

		5-Dec-07		12:07:10		74.01		48		5-Dec-07		12:06:20		71.6		54		5-Dec-07		12:07:53		71		51		15-Jan-08		12:25:59		70.41		43

		5-Dec-07		14:07:10		74.01		49		5-Dec-07		14:06:20		71.6		54		5-Dec-07		14:07:53		71		48.5		15-Jan-08		14:25:59		69.8		44

		5-Dec-07		16:07:10		74.01		51		5-Dec-07		16:06:20		71.6		54		5-Dec-07		16:07:53		71		59.5		15-Jan-08		16:25:59		70.41		45

		5-Dec-07		18:07:10		73.4		50.5		5-Dec-07		18:06:20		69.8		57		5-Dec-07		18:07:53		71		47.5		15-Jan-08		18:25:59		71.6		43.5

		5-Dec-07		20:07:10		73.4		50		5-Dec-07		20:06:20		69.8		56		5-Dec-07		20:07:53		71		54.5		15-Jan-08		20:25:59		69.2		43

		5-Dec-07		22:07:10		72.8		50.5		5-Dec-07		22:06:20		69.8		56.5		5-Dec-07		22:07:53		70.41		55		15-Jan-08		22:25:59		66.81		43.5

		6-Dec-07		0:07:10		72.21		51.5		6-Dec-07		0:06:20		69.2		57		6-Dec-07		0:07:53		70.41		54.5		16-Jan-08		0:25:59		65.01		43.5

		6-Dec-07		2:07:10		71.6		51.5		6-Dec-07		2:06:20		69.2		57		6-Dec-07		2:07:53		69.8		54		16-Jan-08		2:25:59		64.4		43.5

		6-Dec-07		4:07:10		71.6		52		6-Dec-07		4:06:20		68.61		57.5		6-Dec-07		4:07:53		69.8		54		16-Jan-08		4:25:59		63.8		43.5

		6-Dec-07		6:07:10		71		50		6-Dec-07		6:06:20		68		54		6-Dec-07		6:07:53		69.2		53		16-Jan-08		6:25:59		64.4		42.5

		6-Dec-07		8:07:10		72.8		47.5		6-Dec-07		8:06:20		69.8		52		6-Dec-07		8:07:53		71		52		16-Jan-08		8:25:59		66.81		39.5

		6-Dec-07		10:07:10		74.01		45.5		6-Dec-07		10:06:20		71		45		6-Dec-07		10:07:53		71		50		16-Jan-08		10:25:59		70.41		38

		6-Dec-07		12:07:10		74.01		46		6-Dec-07		12:06:20		71		55		6-Dec-07		12:07:53		71		48		16-Jan-08		12:25:59		71		39.5

		6-Dec-07		14:07:10		74.01		46		6-Dec-07		14:06:20		71		57		6-Dec-07		14:07:53		71		54.5		16-Jan-08		14:25:59		72.21		40.5

		6-Dec-07		16:07:10		74.6		47.5		6-Dec-07		16:06:20		71		47.5		6-Dec-07		16:07:53		70.41		51.5		16-Jan-08		16:25:59		72.21		43

		6-Dec-07		18:07:10		74.01		39		6-Dec-07		18:06:20		69.8		41		6-Dec-07		18:07:53		69.8		45		16-Jan-08		18:25:59		72.8		41.5

		6-Dec-07		20:07:10		73.4		38		6-Dec-07		20:06:20		69.8		40		6-Dec-07		20:07:53		69.8		43.5		16-Jan-08		20:25:59		71		41.5

		6-Dec-07		22:07:10		72.21		40		6-Dec-07		22:06:20		69.2		44		6-Dec-07		22:07:53		70.41		44		16-Jan-08		22:25:59		68.61		41.5

		7-Dec-07		0:07:10		71.6		42		7-Dec-07		0:06:20		68		47		7-Dec-07		0:07:53		69.8		44.5		17-Jan-08		0:25:59		66.2		41.5

		7-Dec-07		2:07:10		70.41		42.5		7-Dec-07		2:06:20		67.4		48		7-Dec-07		2:07:53		69.2		45		17-Jan-08		2:25:59		65.01		41.5

		7-Dec-07		4:07:10		69.8		43		7-Dec-07		4:06:20		66.81		48.5		7-Dec-07		4:07:53		68.61		45.5		17-Jan-08		4:25:59		64.4		41.5

		7-Dec-07		6:07:10		69.8		43.5		7-Dec-07		6:06:20		66.81		49		7-Dec-07		6:07:53		68		46.5		17-Jan-08		6:25:59		65.01		39.5

		7-Dec-07		8:07:10		72.21		42		7-Dec-07		8:06:20		68.61		47.5		7-Dec-07		8:07:53		70.41		45		17-Jan-08		8:25:59		66.81		36.5

		7-Dec-07		10:07:10		73.4		42.5		7-Dec-07		10:06:20		71		49.5		7-Dec-07		10:07:53		71		48		17-Jan-08		10:25:59		71		33

		7-Dec-07		12:07:10		72.8		45		7-Dec-07		12:06:20		71		44.5		7-Dec-07		12:07:53		70.41		50.5		17-Jan-08		12:25:59		71.6		27

		7-Dec-07		14:07:10		72.21		47		7-Dec-07		14:06:20		71		47		7-Dec-07		14:07:53		71.6		52.5		17-Jan-08		14:25:59		72.8		25.5

		7-Dec-07		16:07:10		72.21		46		7-Dec-07		16:06:20		71		50		7-Dec-07		16:07:53		70.41		50		17-Jan-08		16:25:59		72.21		23.5

		7-Dec-07		18:07:10		72.21		45.5		7-Dec-07		18:06:20		69.2		50.5		7-Dec-07		18:07:53		70.41		51.5		17-Jan-08		18:25:59		72.21		23

		7-Dec-07		20:07:10		71		47		7-Dec-07		20:06:20		68.61		51		7-Dec-07		20:07:53		69.8		49		17-Jan-08		20:25:59		71.6		23

		7-Dec-07		22:07:10		69.8		47.5		7-Dec-07		22:06:20		67.4		52.5		7-Dec-07		22:07:53		69.8		48.5		17-Jan-08		22:25:59		69.2		24.5

		8-Dec-07		0:07:10		69.2		48		8-Dec-07		0:06:20		66.81		52.5		8-Dec-07		0:07:53		69.2		49		18-Jan-08		0:25:59		67.4		25.5

		8-Dec-07		2:07:10		68.61		44.5		8-Dec-07		2:06:20		66.81		47		8-Dec-07		2:07:53		68		46.5		18-Jan-08		2:25:59		66.2		26

		8-Dec-07		4:07:10		68.61		44		8-Dec-07		4:06:20		66.2		47		8-Dec-07		4:07:53		66.81		47		18-Jan-08		4:25:59		65.01		26

		8-Dec-07		6:07:10		68		43		8-Dec-07		6:06:20		66.2		45.5		8-Dec-07		6:07:53		67.4		45		18-Jan-08		6:25:59		66.2		26.5

		8-Dec-07		8:07:10		71		39		8-Dec-07		8:06:20		68		41		8-Dec-07		8:07:53		69.8		42		18-Jan-08		8:25:59		68.61		26

		8-Dec-07		10:07:10		72.21		37		8-Dec-07		10:06:20		69.8		40.5		8-Dec-07		10:07:53		71.6		40.5		18-Jan-08		10:25:59		72.21		27.5

		8-Dec-07		12:07:10		71.6		37.5		8-Dec-07		12:06:20		71		40.5		8-Dec-07		12:07:53		71		41		18-Jan-08		12:25:59		71.6		28

		8-Dec-07		14:07:10		71.6		36.5		8-Dec-07		14:06:20		71		40		8-Dec-07		14:07:53		71		35		18-Jan-08		14:25:59		72.21		29.5

		8-Dec-07		16:07:10		71.6		35.5		8-Dec-07		16:06:20		71		38		8-Dec-07		16:07:53		70.41		38.5		18-Jan-08		16:25:59		72.8		29

		8-Dec-07		18:07:10		71.6		35.5		8-Dec-07		18:06:20		69.8		35.5		8-Dec-07		18:07:53		69.8		37.5		18-Jan-08		18:25:59		72.21		30

		8-Dec-07		20:07:10		70.41		35		8-Dec-07		20:06:20		67.4		36.5		8-Dec-07		20:07:53		69.2		37		18-Jan-08		20:25:59		71.6		31.5

		8-Dec-07		22:07:10		69.2		33.5		8-Dec-07		22:06:20		66.81		36		8-Dec-07		22:07:53		67.4		37		18-Jan-08		22:25:59		68.61		32

		9-Dec-07		0:07:10		68.61		33.5		9-Dec-07		0:06:20		66.81		35.5		9-Dec-07		0:07:53		66.2		37		19-Jan-08		0:25:59		66.81		32.5

		9-Dec-07		2:07:10		68		33		9-Dec-07		2:06:20		66.2		35		9-Dec-07		2:07:53		65.6		37		19-Jan-08		2:25:59		65.01		33

		9-Dec-07		4:07:10		68		32.5		9-Dec-07		4:06:20		66.2		34		9-Dec-07		4:07:53		64.4		37		19-Jan-08		4:25:59		64.4		33

		9-Dec-07		6:07:10		67.4		32		9-Dec-07		6:06:20		66.2		33.5		9-Dec-07		6:07:53		63.8		36.5		19-Jan-08		6:25:59		66.2		32

		9-Dec-07		8:07:10		68		30.5		9-Dec-07		8:06:20		67.4		31.5		9-Dec-07		8:07:53		67.4		33		19-Jan-08		8:25:59		68.61		30

		9-Dec-07		10:07:10		68.61		30.5		9-Dec-07		10:06:20		68		31		9-Dec-07		10:07:53		68.61		31.5		19-Jan-08		10:25:59		70.41		31

		9-Dec-07		12:07:10		68.61		29.5		9-Dec-07		12:06:20		68.61		29		9-Dec-07		12:07:53		69.8		30		19-Jan-08		12:25:59		71		32.5

		9-Dec-07		14:07:10		68.61		28.5		9-Dec-07		14:06:20		68		28		9-Dec-07		14:07:53		70.41		30		19-Jan-08		14:25:59		71.6		33

		9-Dec-07		16:07:10		69.2		25		9-Dec-07		16:06:20		68		22.5		9-Dec-07		16:07:53		69.2		28.5		19-Jan-08		16:25:59		72.8		32.5

		9-Dec-07		18:07:10		69.2		24		9-Dec-07		18:06:20		68		23		9-Dec-07		18:07:53		68.61		27.5		19-Jan-08		18:25:59		72.8		33

		9-Dec-07		20:07:10		68.61		24		9-Dec-07		20:06:20		67.4		23.5		9-Dec-07		20:07:53		67.4		27		19-Jan-08		20:25:59		72.21		32

		9-Dec-07		22:07:10		68		24		9-Dec-07		22:06:20		66.81		24		9-Dec-07		22:07:53		66.2		27		19-Jan-08		22:25:59		68		34.5

		10-Dec-07		0:07:10		67.4		24		10-Dec-07		0:06:20		66.2		24.5		10-Dec-07		0:07:53		65.6		27.5		20-Jan-08		0:25:59		66.2		34.5

		10-Dec-07		2:07:10		67.4		24.5		10-Dec-07		2:06:20		66.2		25		10-Dec-07		2:07:53		64.4		28		20-Jan-08		2:25:59		65.01		34.5

		10-Dec-07		4:07:10		66.81		25		10-Dec-07		4:06:20		65.6		26.5		10-Dec-07		4:07:53		63.8		28.5		20-Jan-08		4:25:59		63.8		34

		10-Dec-07		6:07:10		66.2		26		10-Dec-07		6:06:20		65.6		28		10-Dec-07		6:07:53		63.21		29.5		20-Jan-08		6:25:59		63.21		33.5

		10-Dec-07		8:07:10		66.81		26		10-Dec-07		8:06:20		67.4		27		10-Dec-07		8:07:53		68.61		26.5		20-Jan-08		8:25:59		63.21		32.5

		10-Dec-07		10:07:10		67.4		26.5		10-Dec-07		10:06:20		67.4		27.5		10-Dec-07		10:07:53		67.4		27.5		20-Jan-08		10:25:59		63.21		33

		10-Dec-07		12:07:10		68		27.5		10-Dec-07		12:06:20		68		28		10-Dec-07		12:07:53		68		29		20-Jan-08		12:25:59		63.8		37

		10-Dec-07		14:07:10		68.61		28.5		10-Dec-07		14:06:20		68		29.5		10-Dec-07		14:07:53		68		30		20-Jan-08		14:25:59		65.01		39

		10-Dec-07		16:07:10		69.2		28.5		10-Dec-07		16:06:20		68.61		29		10-Dec-07		16:07:53		68		31.5		20-Jan-08		16:25:59		66.2		37.5

		10-Dec-07		18:07:10		69.2		30		10-Dec-07		18:06:20		68		31.5		10-Dec-07		18:07:53		67.4		32.5		20-Jan-08		18:25:59		66.81		37

		10-Dec-07		20:07:10		68.61		31		10-Dec-07		20:06:20		66.81		33.5		10-Dec-07		20:07:53		66.81		33.5		20-Jan-08		20:25:59		65.6		37

		10-Dec-07		22:07:10		68		32.5		10-Dec-07		22:06:20		66.2		35.5		10-Dec-07		22:07:53		65.6		35		20-Jan-08		22:25:59		65.01		37

		11-Dec-07		0:07:10		67.4		33.5		11-Dec-07		0:06:20		66.2		36.5		11-Dec-07		0:07:53		65.01		36.5		21-Jan-08		0:25:59		64.4		37

		11-Dec-07		2:07:10		66.81		32		11-Dec-07		2:06:20		66.2		34.5		11-Dec-07		2:07:53		64.4		36		21-Jan-08		2:25:59		63.8		38

		11-Dec-07		4:07:10		66.81		31.5		11-Dec-07		4:06:20		66.2		33		11-Dec-07		4:07:53		63.21		35.5		21-Jan-08		4:25:59		63.8		38.5

		11-Dec-07		6:07:10		66.81		30.5		11-Dec-07		6:06:20		66.2		32		11-Dec-07		6:07:53		67.4		31.5		21-Jan-08		6:25:59		63.21		38

		11-Dec-07		8:07:10		68.61		28.5		11-Dec-07		8:06:20		67.4		30		11-Dec-07		8:07:53		68		30.5		21-Jan-08		8:25:59		63.21		38

		11-Dec-07		10:07:10		69.2		30		11-Dec-07		10:06:20		69.8		31.5		11-Dec-07		10:07:53		69.2		31		21-Jan-08		10:25:59		63.8		38

		11-Dec-07		12:07:10		71.6		31.5		11-Dec-07		12:06:20		70.41		34		11-Dec-07		12:07:53		71.6		32.5		21-Jan-08		12:25:59		65.01		39

		11-Dec-07		14:07:10		71.6		32.5		11-Dec-07		14:06:20		70.41		34		11-Dec-07		14:07:53		71		35.5		21-Jan-08		14:25:59		65.6		36

		11-Dec-07		16:07:10		72.21		32.5		11-Dec-07		16:06:20		69.8		34.5		11-Dec-07		16:07:53		71		35		21-Jan-08		16:25:59		65.6		36

		11-Dec-07		18:07:10		72.21		31		11-Dec-07		18:06:20		69.8		31		11-Dec-07		18:07:53		71		34.5		21-Jan-08		18:25:59		65.6		35.5

		11-Dec-07		20:07:10		70.41		32.5		11-Dec-07		20:06:20		67.4		36		11-Dec-07		20:07:53		70.41		33.5		21-Jan-08		20:25:59		65.01		36

		11-Dec-07		22:07:10		69.2		27		11-Dec-07		22:06:20		66.81		26.5		11-Dec-07		22:07:53		68		31		21-Jan-08		22:25:59		63.8		36.5

		12-Dec-07		0:07:10		68.61		25		12-Dec-07		0:06:20		66.81		24		12-Dec-07		0:07:53		66.81		29		22-Jan-08		0:25:59		63.21		36

		12-Dec-07		2:07:10		68		22		12-Dec-07		2:06:20		66.81		20		12-Dec-07		2:07:53		66.2		26		22-Jan-08		2:25:59		63.21		35

		12-Dec-07		4:07:10		67.4		19.5		12-Dec-07		4:06:20		66.2		17		12-Dec-07		4:07:53		65.6		23.5		22-Jan-08		4:25:59		62.6		33.5

		12-Dec-07		6:07:10		67.4		18.5		12-Dec-07		6:06:20		66.2		16.5		12-Dec-07		6:07:53		65.01		22.5		22-Jan-08		6:25:59		64.4		32.5

		12-Dec-07		8:07:10		69.8		17.5		12-Dec-07		8:06:20		68		16		12-Dec-07		8:07:53		68		20.5		22-Jan-08		8:25:59		66.81		31

		12-Dec-07		10:07:10		71.6		19.5		12-Dec-07		10:06:20		70.41		20		12-Dec-07		10:07:53		71		22		22-Jan-08		10:25:59		69.8		31.5

		12-Dec-07		12:07:10		72.21		18.5		12-Dec-07		12:06:20		71		18		12-Dec-07		12:07:53		71		22.5		22-Jan-08		12:25:59		74.6		30.5

		12-Dec-07		14:07:10		72.21		17.5		12-Dec-07		14:06:20		71		18.5		12-Dec-07		14:07:53		71.6		23		22-Jan-08		14:25:59		72.8		34

		12-Dec-07		16:07:10		72.21		17		12-Dec-07		16:06:20		71		19		12-Dec-07		16:07:53		70.41		22		22-Jan-08		16:25:59		73.4		34.5

		12-Dec-07		18:07:10		72.21		19		12-Dec-07		18:06:20		69.2		19		12-Dec-07		18:07:53		70.41		23.5		22-Jan-08		18:25:59		73.4		33.5

		12-Dec-07		20:07:10		70.41		22		12-Dec-07		20:06:20		67.4		24		12-Dec-07		20:07:53		69.8		24		22-Jan-08		20:25:59		72.21		34

		12-Dec-07		22:07:10		69.2		22.5		12-Dec-07		22:06:20		66.81		26		12-Dec-07		22:07:53		68.61		25		22-Jan-08		22:25:59		67.4		36

		13-Dec-07		0:07:10		68.61		23		13-Dec-07		0:06:20		66.2		26		13-Dec-07		0:07:53		66.81		25.5		23-Jan-08		0:25:59		65.6		37.5

		13-Dec-07		2:07:10		67.4		23		13-Dec-07		2:06:20		66.2		26		13-Dec-07		2:07:53		65.01		26.5		23-Jan-08		2:25:59		64.4		38

		13-Dec-07		4:07:10		66.81		23.5		13-Dec-07		4:06:20		66.2		25.5		13-Dec-07		4:07:53		63.8		27.5		23-Jan-08		4:25:59		63.8		38

		13-Dec-07		6:07:10		67.4		24.5		13-Dec-07		6:06:20		66.2		27		13-Dec-07		6:07:53		67.4		25.5		23-Jan-08		6:25:59		66.2		37.5

		13-Dec-07		8:07:10		70.41		24.5		13-Dec-07		8:06:20		68		27		13-Dec-07		8:07:53		68.61		26.5		23-Jan-08		8:25:59		68.61		34.5

		13-Dec-07		10:07:10		71.6		25		13-Dec-07		10:06:20		70.41		27.5		13-Dec-07		10:07:53		70.41		27.5		23-Jan-08		10:25:59		72.21		33

		13-Dec-07		12:07:10		72.21		26.5		13-Dec-07		12:06:20		71		28.5		13-Dec-07		12:07:53		70.41		30		23-Jan-08		12:25:59		74.01		31.5

		13-Dec-07		14:07:10		72.21		25.5		13-Dec-07		14:06:20		71		27		13-Dec-07		14:07:53		70.41		30.5		23-Jan-08		14:25:59		72.8		31.5

		13-Dec-07		16:07:10		72.21		22.5		13-Dec-07		16:06:20		71		23.5		13-Dec-07		16:07:53		70.41		28		23-Jan-08		16:25:59		72.21		31.5

		13-Dec-07		18:07:10		72.8		23.5		13-Dec-07		18:06:20		69.8		24		13-Dec-07		18:07:53		69.8		27.5		23-Jan-08		18:25:59		72.8		30.5

		13-Dec-07		20:07:10		70.41		25.5		13-Dec-07		20:06:20		67.4		28.5		13-Dec-07		20:07:53		69.2		28		23-Jan-08		20:25:59		72.8		30

		13-Dec-07		22:07:10		69.2		25.5		13-Dec-07		22:06:20		66.81		29		13-Dec-07		22:07:53		68		28.5		23-Jan-08		22:25:59		68		32

		14-Dec-07		0:07:10		68		26		14-Dec-07		0:06:20		66.2		29		14-Dec-07		0:07:53		66.2		29		24-Jan-08		0:25:59		65.6		33

		14-Dec-07		2:07:10		67.4		26.5		14-Dec-07		2:06:20		66.2		29		14-Dec-07		2:07:53		64.4		30		24-Jan-08		2:25:59		64.4		34

		14-Dec-07		4:07:10		66.81		26		14-Dec-07		4:06:20		66.2		28.5		14-Dec-07		4:07:53		63.21		30.5		24-Jan-08		4:25:59		63.8		35

		14-Dec-07		6:07:10		66.81		25.5		14-Dec-07		6:06:20		66.2		27		14-Dec-07		6:07:53		66.2		27		24-Jan-08		6:25:59		65.6		36

		14-Dec-07		8:07:10		69.2		24		14-Dec-07		8:06:20		67.4		26		14-Dec-07		8:07:53		68.61		26.5		24-Jan-08		8:25:59		68		34.5

		14-Dec-07		10:07:10		69.8		26		14-Dec-07		10:06:20		69.8		28		14-Dec-07		10:07:53		69.8		27.5		24-Jan-08		10:25:59		71.6		34.5

		14-Dec-07		12:07:10		71		28		14-Dec-07		12:06:20		70.41		30.5		14-Dec-07		12:07:53		71.6		28.5		24-Jan-08		12:25:59		74.01		33.5

		14-Dec-07		14:07:10		71.6		28		14-Dec-07		14:06:20		71		29.5		14-Dec-07		14:07:53		71		28.5		24-Jan-08		14:25:59		71.6		35

		14-Dec-07		16:07:10		72.21		29		14-Dec-07		16:06:20		71.6		30		14-Dec-07		16:07:53		69.8		32		24-Jan-08		16:25:59		72.21		34.5

		14-Dec-07		18:07:10		73.4		30		14-Dec-07		18:06:20		69.8		33		14-Dec-07		18:07:53		70.41		33.5		24-Jan-08		18:25:59		72.21		33.5

		14-Dec-07		20:07:10		71		30.5		14-Dec-07		20:06:20		69.2		33		14-Dec-07		20:07:53		69.2		32		24-Jan-08		20:25:59		72.21		33.5

		14-Dec-07		22:07:10		69.2		29.5		14-Dec-07		22:06:20		66.81		32.5		14-Dec-07		22:07:53		68		31.5		24-Jan-08		22:25:59		68		36

		15-Dec-07		0:07:10		68		29		15-Dec-07		0:06:20		66.2		32		15-Dec-07		0:07:53		65.6		32		25-Jan-08		0:25:59		65.6		36.5

		15-Dec-07		2:07:10		67.4		28		15-Dec-07		2:06:20		66.2		30.5		15-Dec-07		2:07:53		63.8		32		25-Jan-08		2:25:59		65.01		37.5

		15-Dec-07		4:07:10		66.81		27		15-Dec-07		4:06:20		65.6		29		15-Dec-07		4:07:53		63.21		31.5		25-Jan-08		4:25:59		64.4		38.5

		15-Dec-07		6:07:10		66.81		27		15-Dec-07		6:06:20		66.2		28.5		15-Dec-07		6:07:53		67.4		27.5		25-Jan-08		6:25:59		66.2		38

		15-Dec-07		8:07:10		68.61		25		15-Dec-07		8:06:20		67.4		26		15-Dec-07		8:07:53		68.61		27		25-Jan-08		8:25:59		69.2		36

		15-Dec-07		10:07:10		70.41		27		15-Dec-07		10:06:20		69.8		28.5		15-Dec-07		10:07:53		70.41		28.5		25-Jan-08		10:25:59		72.8		36

		15-Dec-07		12:07:10		71.6		29.5		15-Dec-07		12:06:20		71		29.5		15-Dec-07		12:07:53		71.6		30		25-Jan-08		12:25:59		74.01		34.5

		15-Dec-07		14:07:10		71.6		30.5		15-Dec-07		14:06:20		71		31.5		15-Dec-07		14:07:53		70.41		30		25-Jan-08		14:25:59		73.4		35

		15-Dec-07		16:07:10		71.6		30.5		15-Dec-07		16:06:20		71		31.5		15-Dec-07		16:07:53		71		32.5		25-Jan-08		16:25:59		74.01		35.5

		15-Dec-07		18:07:10		72.8		33		15-Dec-07		18:06:20		69.8		37		15-Dec-07		18:07:53		70.41		35.5		25-Jan-08		18:25:59		72.8		35

		15-Dec-07		20:07:10		71		34.5		15-Dec-07		20:06:20		67.4		39		15-Dec-07		20:07:53		69.2		35.5		25-Jan-08		20:25:59		72.21		34

		15-Dec-07		22:07:10		69.2		33.5		15-Dec-07		22:06:20		66.81		37.5		15-Dec-07		22:07:53		67.4		35.5		25-Jan-08		22:25:59		69.2		36

		16-Dec-07		0:07:10		68.61		34		16-Dec-07		0:06:20		66.2		38		16-Dec-07		0:07:53		66.2		36.5		26-Jan-08		0:25:59		67.4		36.5

		16-Dec-07		2:07:10		68		34		16-Dec-07		2:06:20		66.2		38		16-Dec-07		2:07:53		65.6		37.5		26-Jan-08		2:25:59		66.2		37

		16-Dec-07		4:07:10		68		35		16-Dec-07		4:06:20		66.2		39		16-Dec-07		4:07:53		65.01		38.5		26-Jan-08		4:25:59		65.6		37

		16-Dec-07		6:07:10		67.4		35		16-Dec-07		6:06:20		66.2		38		16-Dec-07		6:07:53		64.4		39		26-Jan-08		6:25:59		66.81		37

		16-Dec-07		8:07:10		68		34		16-Dec-07		8:06:20		67.4		36.5		16-Dec-07		8:07:53		66.81		37		26-Jan-08		8:25:59		70.41		37

		16-Dec-07		10:07:10		68		34.5		16-Dec-07		10:06:20		67.4		36.5		16-Dec-07		10:07:53		66.81		36		26-Jan-08		10:25:59		73.4		38

		16-Dec-07		12:07:10		68		35		16-Dec-07		12:06:20		68		37		16-Dec-07		12:07:53		67.4		36.5		26-Jan-08		12:25:59		72.8		39

		16-Dec-07		14:07:10		68.61		37		16-Dec-07		14:06:20		68		39.5		16-Dec-07		14:07:53		66.81		39		26-Jan-08		14:25:59		73.4		39.5

		16-Dec-07		16:07:10		69.2		39		16-Dec-07		16:06:20		68		42.5		16-Dec-07		16:07:53		67.4		41.5		26-Jan-08		16:25:59		73.4		39.5

		16-Dec-07		18:07:10		69.2		40.5		16-Dec-07		18:06:20		68		44		16-Dec-07		18:07:53		68		42.5		26-Jan-08		18:25:59		73.4		40

		16-Dec-07		20:07:10		68.61		40.5		16-Dec-07		20:06:20		66.81		44		16-Dec-07		20:07:53		67.4		42		26-Jan-08		20:25:59		72.8		41

		16-Dec-07		22:07:10		68		40.5		16-Dec-07		22:06:20		66.81		44		16-Dec-07		22:07:53		66.2		43		26-Jan-08		22:25:59		69.8		43

		17-Dec-07		0:07:10		68		41		17-Dec-07		0:06:20		66.2		44.5		17-Dec-07		0:07:53		66.2		43.5		27-Jan-08		0:25:59		68		44

		17-Dec-07		2:07:10		67.4		41		17-Dec-07		2:06:20		66.2		44.5		17-Dec-07		2:07:53		65.6		44		27-Jan-08		2:25:59		67.4		45.5

		17-Dec-07		4:07:10		67.4		40.5		17-Dec-07		4:06:20		66.2		44.5		17-Dec-07		4:07:53		65.01		44		27-Jan-08		4:25:59		66.81		46.5

		17-Dec-07		6:07:10		66.81		40.5		17-Dec-07		6:06:20		66.2		43.5		17-Dec-07		6:07:53		65.01		43.5		27-Jan-08		6:25:59		66.2		47

		17-Dec-07		8:07:10		68		40		17-Dec-07		8:06:20		67.4		42.5		17-Dec-07		8:07:53		66.81		41.5		27-Jan-08		8:25:59		66.2		46.5

		17-Dec-07		10:07:10		68		40.5		17-Dec-07		10:06:20		67.4		43		17-Dec-07		10:07:53		67.4		42		27-Jan-08		10:25:59		66.2		45.5

		17-Dec-07		12:07:10		68		40.5		17-Dec-07		12:06:20		67.4		42.5		17-Dec-07		12:07:53		67.4		42.5		27-Jan-08		12:25:59		66.81		45

		17-Dec-07		14:07:10		68.61		37		17-Dec-07		14:06:20		68		37		17-Dec-07		14:07:53		67.4		40		27-Jan-08		14:25:59		67.4		46

		17-Dec-07		16:07:10		68.61		37.5		17-Dec-07		16:06:20		67.4		39.5		17-Dec-07		16:07:53		67.4		40.5		27-Jan-08		16:25:59		68		45.5

		17-Dec-07		18:07:10		68.61		38		17-Dec-07		18:06:20		68		39.5		17-Dec-07		18:07:53		67.4		40		27-Jan-08		18:25:59		67.4		44.5

		17-Dec-07		20:07:10		68		40		17-Dec-07		20:06:20		66.81		43.5		17-Dec-07		20:07:53		66.81		42		27-Jan-08		20:25:59		66.81		44

		17-Dec-07		22:07:10		68		42.5		17-Dec-07		22:06:20		66.2		47		17-Dec-07		22:07:53		65.6		45		27-Jan-08		22:25:59		66.2		44

		18-Dec-07		0:07:10		67.4		43.5		18-Dec-07		0:06:20		66.2		48.5		18-Dec-07		0:07:53		65.6		46.5		28-Jan-08		0:25:59		66.2		44.5

		18-Dec-07		2:07:10		67.4		43.5		18-Dec-07		2:06:20		66.81		46.5		18-Dec-07		2:07:53		65.6		46.5		28-Jan-08		2:25:59		66.2		46

		18-Dec-07		4:07:10		67.4		42		18-Dec-07		4:06:20		66.2		44.5		18-Dec-07		4:07:53		65.01		45.5		28-Jan-08		4:25:59		65.6		46.5

		18-Dec-07		6:07:10		67.4		43		18-Dec-07		6:06:20		66.2		46		18-Dec-07		6:07:53		66.81		43.5		28-Jan-08		6:25:59		65.6		47

		18-Dec-07		8:07:10		69.8		41		18-Dec-07		8:06:20		68		44.5		18-Dec-07		8:07:53		69.2		43		28-Jan-08		8:25:59		65.6		47.5

		18-Dec-07		10:07:10		71		42		18-Dec-07		10:06:20		71		39		18-Dec-07		10:07:53		71.6		41.5		28-Jan-08		10:25:59		66.81		47.5

		18-Dec-07		12:07:10		71.6		41		18-Dec-07		12:06:20		71.6		43.5		18-Dec-07		12:07:53		71.6		43.5		28-Jan-08		12:25:59		68		47

		18-Dec-07		14:07:10		71.6		41		18-Dec-07		14:06:20		71		45		18-Dec-07		14:07:53		71		45.5		28-Jan-08		14:25:59		68.61		46.5

		18-Dec-07		16:07:10		72.21		44		18-Dec-07		16:06:20		71		39.5		18-Dec-07		16:07:53		71		46		28-Jan-08		16:25:59		68.61		46.5

		18-Dec-07		18:07:10		72.21		42		18-Dec-07		18:06:20		69.2		45		18-Dec-07		18:07:53		71.6		40.5		28-Jan-08		18:25:59		69.2		46.5

		18-Dec-07		20:07:10		71		41.5		18-Dec-07		20:06:20		68		45		18-Dec-07		20:07:53		70.41		42.5		28-Jan-08		20:25:59		67.4		47.5

		18-Dec-07		22:07:10		69.8		43		18-Dec-07		22:06:20		66.81		48.5		18-Dec-07		22:07:53		68.61		44.5		28-Jan-08		22:25:59		66.2		46

		19-Dec-07		0:07:10		69.2		44		19-Dec-07		0:06:20		66.81		48.5		19-Dec-07		0:07:53		68		45.5		29-Jan-08		0:25:59		65.01		42.5

		19-Dec-07		2:07:10		68.61		44.5		19-Dec-07		2:06:20		66.81		49		19-Dec-07		2:07:53		67.4		46.5		29-Jan-08		2:25:59		64.4		41

		19-Dec-07		4:07:10		68.61		44.5		19-Dec-07		4:06:20		66.81		48.5		19-Dec-07		4:07:53		66.81		47.5		29-Jan-08		4:25:59		64.4		40.5

		19-Dec-07		6:07:10		68		45		19-Dec-07		6:06:20		66.81		48.5		19-Dec-07		6:07:53		68		46		29-Jan-08		6:25:59		66.2		39

		19-Dec-07		8:07:10		70.41		43		19-Dec-07		8:06:20		68.61		46		19-Dec-07		8:07:53		69.8		44.5		29-Jan-08		8:25:59		68.61		37

		19-Dec-07		10:07:10		71.6		42		19-Dec-07		10:06:20		71		48.5		19-Dec-07		10:07:53		71		43.5		29-Jan-08		10:25:59		73.4		35.5

		19-Dec-07		12:07:10		72.21		44		19-Dec-07		12:06:20		71.6		49.5		19-Dec-07		12:07:53		70.41		50		29-Jan-08		12:25:59		71		37

		19-Dec-07		14:07:10		72.21		45.5		19-Dec-07		14:06:20		71		53.5		19-Dec-07		14:07:53		69.8		49.5		29-Jan-08		14:25:59		71.6		36

		19-Dec-07		16:07:10		72.8		45.5		19-Dec-07		16:06:20		71		47		19-Dec-07		16:07:53		70.41		47		29-Jan-08		16:25:59		72.8		35.5

		19-Dec-07		18:07:10		72.21		41.5		19-Dec-07		18:06:20		69.2		44		19-Dec-07		18:07:53		69.8		44.5		29-Jan-08		18:25:59		72.21		35.5

		19-Dec-07		20:07:10		71		41		19-Dec-07		20:06:20		67.4		44.5		19-Dec-07		20:07:53		69.2		43		29-Jan-08		20:25:59		72.21		33.5

		19-Dec-07		22:07:10		69.8		39		19-Dec-07		22:06:20		66.81		42		19-Dec-07		22:07:53		68		42		29-Jan-08		22:25:59		68		36

		20-Dec-07		0:07:10		68.61		38.5		20-Dec-07		0:06:20		66.2		42		20-Dec-07		0:07:53		66.2		42		30-Jan-08		0:25:59		66.2		36

		20-Dec-07		2:07:10		68.61		39		20-Dec-07		2:06:20		66.2		43		20-Dec-07		2:07:53		65.6		43		30-Jan-08		2:25:59		65.01		36

		20-Dec-07		4:07:10		68		40		20-Dec-07		4:06:20		66.2		43.5		20-Dec-07		4:07:53		65.01		44		30-Jan-08		4:25:59		63.8		35

		20-Dec-07		6:07:10		68		40		20-Dec-07		6:06:20		66.2		43.5		20-Dec-07		6:07:53		67.4		41.5		30-Jan-08		6:25:59		66.2		34

		20-Dec-07		8:07:10		70.41		39		20-Dec-07		8:06:20		68		42.5		20-Dec-07		8:07:53		69.8		41		30-Jan-08		8:25:59		69.2		33

		20-Dec-07		10:07:10		72.21		39		20-Dec-07		10:06:20		70.41		42		20-Dec-07		10:07:53		71.6		39.5		30-Jan-08		10:25:59		72.8		33.5

		20-Dec-07		12:07:10		72.21		41		20-Dec-07		12:06:20		71		45.5		20-Dec-07		12:07:53		71.6		43		30-Jan-08		12:25:59		73.4		34

		20-Dec-07		14:07:10		72.8		39.5		20-Dec-07		14:06:20		70.41		47.5		20-Dec-07		14:07:53		71.6		42		30-Jan-08		14:25:59		72.8		37.5

		20-Dec-07		16:07:10		72.21		43		20-Dec-07		16:06:20		70.41		43		20-Dec-07		16:07:53		70.41		46		30-Jan-08		16:25:59		72.8		39.5

		20-Dec-07		18:07:10		72.8		41.5		20-Dec-07		18:06:20		69.2		45.5		20-Dec-07		18:07:53		70.41		44.5		30-Jan-08		18:25:59		72.21		37.5

		20-Dec-07		20:07:10		71.6		42.5		20-Dec-07		20:06:20		68.61		47.5		20-Dec-07		20:07:53		69.8		45		30-Jan-08		20:25:59		72.21		34.5

		20-Dec-07		22:07:10		70.41		44.5		20-Dec-07		22:06:20		68		49.5		20-Dec-07		22:07:53		69.2		46.5		30-Jan-08		22:25:59		69.2		36

		21-Dec-07		0:07:10		69.8		46		21-Dec-07		0:06:20		67.4		51.5		21-Dec-07		0:07:53		68		47.5		31-Jan-08		0:25:59		67.4		36.5

		21-Dec-07		2:07:10		69.2		46		21-Dec-07		2:06:20		67.4		51		21-Dec-07		2:07:53		68		49		31-Jan-08		2:25:59		66.2		36.5

		21-Dec-07		4:07:10		69.2		46.5		21-Dec-07		4:06:20		66.81		51.5		21-Dec-07		4:07:53		67.4		49		31-Jan-08		4:25:59		65.6		37

		21-Dec-07		6:07:10		68.61		44.5		21-Dec-07		6:06:20		66.81		47		21-Dec-07		6:07:53		67.4		47		31-Jan-08		6:25:59		66.81		36

		21-Dec-07		8:07:10		71		38.5		21-Dec-07		8:06:20		68		39		21-Dec-07		8:07:53		69.8		42		31-Jan-08		8:25:59		70.41		34.5

		21-Dec-07		10:07:10		71.6		38.5		21-Dec-07		10:06:20		69.8		38		21-Dec-07		10:07:53		71.6		39.5		31-Jan-08		10:25:59		74.01		34

		21-Dec-07		12:07:10		72.21		37		21-Dec-07		12:06:20		69.8		38.5		21-Dec-07		12:07:53		71		40		31-Jan-08		12:25:59		71		36

		21-Dec-07		14:07:10		72.21		35.5		21-Dec-07		14:06:20		70.41		35		21-Dec-07		14:07:53		71		40.5		31-Jan-08		14:25:59		72.21		35.5

		21-Dec-07		16:07:10		72.21		33		21-Dec-07		16:06:20		70.41		32.5		21-Dec-07		16:07:53		71		35.5		31-Jan-08		16:25:59		72.21		35

		21-Dec-07		18:07:10		71.6		31.5		21-Dec-07		18:06:20		69.2		30.5		21-Dec-07		18:07:53		70.41		34		31-Jan-08		18:25:59		72.21		35.5

		21-Dec-07		20:07:10		69.8		32		21-Dec-07		20:06:20		67.4		34		21-Dec-07		20:07:53		69.2		33.5		31-Jan-08		20:25:59		72.21		35.5

		21-Dec-07		22:07:10		69.2		32		21-Dec-07		22:06:20		66.81		34		21-Dec-07		22:07:53		67.4		34.5		31-Jan-08		22:25:59		69.2		38

		22-Dec-07		0:07:10		68.61		31.5		22-Dec-07		0:06:20		66.2		33.5		22-Dec-07		0:07:53		65.6		35		1-Feb-08		0:25:59		67.4		38.5

		22-Dec-07		2:07:10		68		31		22-Dec-07		2:06:20		66.2		33		22-Dec-07		2:07:53		64.4		35		1-Feb-08		2:25:59		66.2		39

		22-Dec-07		4:07:10		67.4		30		22-Dec-07		4:06:20		66.2		31.5		22-Dec-07		4:07:53		63.21		35		1-Feb-08		4:25:59		65.6		40

		22-Dec-07		6:07:10		67.4		29.5		22-Dec-07		6:06:20		66.2		30.5		22-Dec-07		6:07:53		66.2		31.5		1-Feb-08		6:25:59		66.81		40

		22-Dec-07		8:07:10		69.2		28		22-Dec-07		8:06:20		69.2		29		22-Dec-07		8:07:53		68.61		31.5		1-Feb-08		8:25:59		70.41		39

		22-Dec-07		10:07:10		71		28		22-Dec-07		10:06:20		70.41		30		22-Dec-07		10:07:53		70.41		31		1-Feb-08		10:25:59		73.4		40

		22-Dec-07		12:07:10		71		28.5		22-Dec-07		12:06:20		70.41		29.5		22-Dec-07		12:07:53		71.6		28.5		1-Feb-08		12:25:59		72.21		41

		22-Dec-07		14:07:10		71		26.5		22-Dec-07		14:06:20		69.2		26		22-Dec-07		14:07:53		69.8		30		1-Feb-08		14:25:59		72.8		42.5

		22-Dec-07		16:07:10		71		26.5		22-Dec-07		16:06:20		69.2		26		22-Dec-07		16:07:53		69.2		29.5		1-Feb-08		16:25:59		72.8		44

		22-Dec-07		18:07:10		70.41		26.5		22-Dec-07		18:06:20		69.2		26		22-Dec-07		18:07:53		69.2		29.5		1-Feb-08		18:25:59		72.21		45.5

		22-Dec-07		20:07:10		69.8		28		22-Dec-07		20:06:20		66.81		31		22-Dec-07		20:07:53		68		31.5		1-Feb-08		20:25:59		72.8		41

		22-Dec-07		22:07:10		68.61		28.5		22-Dec-07		22:06:20		66.2		31		22-Dec-07		22:07:53		66.2		31.5		1-Feb-08		22:25:59		69.8		42

		23-Dec-07		0:07:10		68		28		23-Dec-07		0:06:20		65.6		31		23-Dec-07		0:07:53		64.4		31.5		2-Feb-08		0:25:59		67.4		41.5

		23-Dec-07		2:07:10		66.81		27.5		23-Dec-07		2:06:20		65.6		30		23-Dec-07		2:07:53		63.21		32		2-Feb-08		2:25:59		65.6		40.5

		23-Dec-07		4:07:10		66.81		27		23-Dec-07		4:06:20		65.6		29.5		23-Dec-07		4:07:53		62		31.5		2-Feb-08		4:25:59		64.4		39.5

		23-Dec-07		6:07:10		66.2		26.5		23-Dec-07		6:06:20		65.6		28		23-Dec-07		6:07:53		61.41		31.5		2-Feb-08		6:25:59		65.6		37

		23-Dec-07		8:07:10		66.81		26.5		23-Dec-07		8:06:20		66.81		28		23-Dec-07		8:07:53		67.4		28		2-Feb-08		8:25:59		68		34.5

		23-Dec-07		10:07:10		67.4		28		23-Dec-07		10:06:20		67.4		29.5		23-Dec-07		10:07:53		68		28		2-Feb-08		10:25:59		71		38.5

		23-Dec-07		12:07:10		67.4		30		23-Dec-07		12:06:20		67.4		31.5		23-Dec-07		12:07:53		68		30.5		2-Feb-08		12:25:59		71.6		37

		23-Dec-07		14:07:10		68		29.5		23-Dec-07		14:06:20		67.4		30.5		23-Dec-07		14:07:53		68		31		2-Feb-08		14:25:59		71.6		39

		23-Dec-07		16:07:10		68		29.5		23-Dec-07		16:06:20		68		30.5		23-Dec-07		16:07:53		68		31.5		2-Feb-08		16:25:59		71.6		39

		23-Dec-07		18:07:10		68.61		29.5		23-Dec-07		18:06:20		67.4		30		23-Dec-07		18:07:53		68		31.5		2-Feb-08		18:25:59		71.6		39

		23-Dec-07		20:07:10		68		31.5		23-Dec-07		20:06:20		66.2		34		23-Dec-07		20:07:53		68.61		31.5		2-Feb-08		20:25:59		71.6		38.5

		23-Dec-07		22:07:10		67.4		32		23-Dec-07		22:06:20		66.2		34.5		23-Dec-07		22:07:53		68.61		32		2-Feb-08		22:25:59		68.61		39.5

		24-Dec-07		0:07:10		66.81		32		24-Dec-07		0:06:20		65.6		34.5		24-Dec-07		0:07:53		68.61		31.5		3-Feb-08		0:25:59		66.81		40.5

		24-Dec-07		2:07:10		66.81		31.5		24-Dec-07		2:06:20		66.2		33.5		24-Dec-07		2:07:53		68.61		31.5		3-Feb-08		2:25:59		66.2		41

		24-Dec-07		4:07:10		66.81		31.5		24-Dec-07		4:06:20		65.6		34		24-Dec-07		4:07:53		68.61		31.5		3-Feb-08		4:25:59		65.6		42

		24-Dec-07		6:07:10		66.81		31.5		24-Dec-07		6:06:20		65.6		33		24-Dec-07		6:07:53		68		31		3-Feb-08		6:25:59		65.01		42.5

		24-Dec-07		8:07:10		67.4		31		24-Dec-07		8:06:20		67.4		32		24-Dec-07		8:07:53		69.2		30.5		3-Feb-08		8:25:59		65.01		43

		24-Dec-07		10:07:10		67.4		32		24-Dec-07		10:06:20		67.4		33.5		24-Dec-07		10:07:53		69.2		31		3-Feb-08		10:25:59		66.2		43

		24-Dec-07		12:07:10		68		32.5		24-Dec-07		12:06:20		67.4		33.5		24-Dec-07		12:07:53		68.61		32		3-Feb-08		12:25:59		66.81		45

		24-Dec-07		14:07:10		68.61		36		24-Dec-07		14:06:20		68		38.5		24-Dec-07		14:07:53		69.2		35.5		3-Feb-08		14:25:59		67.4		46

		24-Dec-07		16:07:10		69.2		40		24-Dec-07		16:06:20		68.61		44		24-Dec-07		16:07:53		69.8		39.5		3-Feb-08		16:25:59		67.4		48.5

		24-Dec-07		18:07:10		69.8		43		24-Dec-07		18:06:20		68.61		48		24-Dec-07		18:07:53		69.8		43		3-Feb-08		18:25:59		66.81		50.5

		24-Dec-07		20:07:10		68.61		43		24-Dec-07		20:06:20		66.81		47.5		24-Dec-07		20:07:53		69.2		42.5		3-Feb-08		20:25:59		66.81		50

		24-Dec-07		22:07:10		68		41.5		24-Dec-07		22:06:20		66.2		46		24-Dec-07		22:07:53		69.8		40.5		3-Feb-08		22:25:59		66.2		51.5

		25-Dec-07		0:07:10		68		41.5		25-Dec-07		0:06:20		66.2		45		25-Dec-07		0:07:53		69.8		40		4-Feb-08		0:25:59		66.2		52.5

		25-Dec-07		2:07:10		67.4		40.5		25-Dec-07		2:06:20		66.2		44.5		25-Dec-07		2:07:53		69.8		39		4-Feb-08		2:25:59		66.2		51.5

		25-Dec-07		4:07:10		67.4		40.5		25-Dec-07		4:06:20		66.2		43.5		25-Dec-07		4:07:53		69.8		38		4-Feb-08		4:25:59		65.6		49.5

		25-Dec-07		6:07:10		67.4		39.5		25-Dec-07		6:06:20		66.2		42		25-Dec-07		6:07:53		69.8		37		4-Feb-08		6:25:59		65.6		48.5

		25-Dec-07		8:07:10		69.2		37.5		25-Dec-07		8:06:20		67.4		40		25-Dec-07		8:07:53		69.2		38		4-Feb-08		8:25:59		65.6		47

		25-Dec-07		10:07:10		69.8		33.5		25-Dec-07		10:06:20		68		34.5		25-Dec-07		10:07:53		68.61		35		4-Feb-08		10:25:59		66.2		46

		25-Dec-07		12:07:10		71		31.5		25-Dec-07		12:06:20		69.2		31		25-Dec-07		12:07:53		69.2		33.5		4-Feb-08		12:25:59		66.81		46.5

		25-Dec-07		14:07:10		70.41		30		25-Dec-07		14:06:20		69.2		28		25-Dec-07		14:07:53		69.8		31.5		4-Feb-08		14:25:59		67.4		46

		25-Dec-07		16:07:10		70.41		27.5		25-Dec-07		16:06:20		68.61		26		25-Dec-07		16:07:53		70.41		30.5		4-Feb-08		16:25:59		67.4		45.5

		25-Dec-07		18:07:10		70.41		29.5		25-Dec-07		18:06:20		68.61		29		25-Dec-07		18:07:53		70.41		30.5		4-Feb-08		18:25:59		67.4		45

		25-Dec-07		20:07:10		69.2		32		25-Dec-07		20:06:20		66.81		34.5		25-Dec-07		20:07:53		69.2		33		4-Feb-08		20:25:59		66.2		45

		25-Dec-07		22:07:10		68		30		25-Dec-07		22:06:20		66.2		31.5		25-Dec-07		22:07:53		67.4		32		4-Feb-08		22:25:59		65.6		45

		26-Dec-07		0:07:10		67.4		29.5		26-Dec-07		0:06:20		65.6		31		26-Dec-07		0:07:53		65.6		31.5		5-Feb-08		0:25:59		65.6		44.5

		26-Dec-07		2:07:10		66.81		28.5		26-Dec-07		2:06:20		65.6		30		26-Dec-07		2:07:53		64.4		31.5		5-Feb-08		2:25:59		65.01		44.5

		26-Dec-07		4:07:10		66.2		28		26-Dec-07		4:06:20		65.6		29.5		26-Dec-07		4:07:53		62.6		31		5-Feb-08		4:25:59		65.01		44

		26-Dec-07		6:07:10		66.2		27.5		26-Dec-07		6:06:20		65.6		29		26-Dec-07		6:07:53		66.81		28.5		5-Feb-08		6:25:59		66.2		42.5

		26-Dec-07		8:07:10		66.81		26.5		26-Dec-07		8:06:20		66.81		27		26-Dec-07		8:07:53		68		27.5		5-Feb-08		8:25:59		69.8		39.5

		26-Dec-07		10:07:10		67.4		26.5		26-Dec-07		10:06:20		67.4		27.5		26-Dec-07		10:07:53		68.61		27.5		5-Feb-08		10:25:59		72.8		37.5

		26-Dec-07		12:07:10		67.4		27.5		26-Dec-07		12:06:20		67.4		28		26-Dec-07		12:07:53		68.61		28.5		5-Feb-08		12:25:59		71.6		37.5

		26-Dec-07		14:07:10		68		28		26-Dec-07		14:06:20		68		28		26-Dec-07		14:07:53		68.61		29.5		5-Feb-08		14:25:59		71.6		36

		26-Dec-07		16:07:10		68.61		29.5		26-Dec-07		16:06:20		68		30.5		26-Dec-07		16:07:53		68.61		31		5-Feb-08		16:25:59		72.8		34.5

		26-Dec-07		18:07:10		68.61		32.5		26-Dec-07		18:06:20		68		35		26-Dec-07		18:07:53		68.61		34		5-Feb-08		18:25:59		72.8		34.5

		26-Dec-07		20:07:10		68		33.5		26-Dec-07		20:06:20		66.81		36		26-Dec-07		20:07:53		69.2		34		5-Feb-08		20:25:59		72.21		34

		26-Dec-07		22:07:10		67.4		34		26-Dec-07		22:06:20		66.2		36.5		26-Dec-07		22:07:53		67.4		34.5		5-Feb-08		22:25:59		69.2		36

		27-Dec-07		0:07:10		66.81		34.5		27-Dec-07		0:06:20		66.2		38		27-Dec-07		0:07:53		66.2		36		6-Feb-08		0:25:59		67.4		37

		27-Dec-07		2:07:10		66.81		34		27-Dec-07		2:06:20		66.2		36		27-Dec-07		2:07:53		65.01		36		6-Feb-08		2:25:59		66.2		38

		27-Dec-07		4:07:10		66.2		32.5		27-Dec-07		4:06:20		65.6		34		27-Dec-07		4:07:53		63.8		35		6-Feb-08		4:25:59		65.6		38

		27-Dec-07		6:07:10		66.2		31.5		27-Dec-07		6:06:20		65.6		32.5		27-Dec-07		6:07:53		68		31.5		6-Feb-08		6:25:59		66.81		39.5

		27-Dec-07		8:07:10		68		30		27-Dec-07		8:06:20		67.4		31		27-Dec-07		8:07:53		70.41		30.5		6-Feb-08		8:25:59		70.41		36.5

		27-Dec-07		10:07:10		69.2		30.5		27-Dec-07		10:06:20		69.8		31.5		27-Dec-07		10:07:53		71		30.5		6-Feb-08		10:25:59		72.8		35.5

		27-Dec-07		12:07:10		71		28.5		27-Dec-07		12:06:20		70.41		28.5		27-Dec-07		12:07:53		71		29		6-Feb-08		12:25:59		71		37

		27-Dec-07		14:07:10		70.41		25.5		27-Dec-07		14:06:20		70.41		24.5		27-Dec-07		14:07:53		71		25.5		6-Feb-08		14:25:59		72.21		37

		27-Dec-07		16:07:10		71		22.5		27-Dec-07		16:06:20		71		22		27-Dec-07		16:07:53		69.8		24		6-Feb-08		16:25:59		72.8		34.5

		27-Dec-07		18:07:10		70.41		23		27-Dec-07		18:06:20		68.61		23.5		27-Dec-07		18:07:53		69.2		24.5		6-Feb-08		18:25:59		72.8		35

		27-Dec-07		20:07:10		69.8		24		27-Dec-07		20:06:20		66.81		26		27-Dec-07		20:07:53		68		26		6-Feb-08		20:25:59		72.8		37

		27-Dec-07		22:07:10		68		24		27-Dec-07		22:06:20		66.2		26		27-Dec-07		22:07:53		66.2		27		6-Feb-08		22:25:59		69.8		38

		28-Dec-07		0:07:10		67.4		24.5		28-Dec-07		0:06:20		65.6		26		28-Dec-07		0:07:53		65.01		27.5		7-Feb-08		0:25:59		68		38.5

		28-Dec-07		2:07:10		66.81		24		28-Dec-07		2:06:20		65.6		26		28-Dec-07		2:07:53		63.21		28		7-Feb-08		2:25:59		66.81		38.5

		28-Dec-07		4:07:10		66.2		24		28-Dec-07		4:06:20		65.6		25.5		28-Dec-07		4:07:53		62.6		28		7-Feb-08		4:25:59		66.2		38.5

		28-Dec-07		6:07:10		66.2		24.5		28-Dec-07		6:06:20		65.6		25.5		28-Dec-07		6:07:53		66.2		26		7-Feb-08		6:25:59		67.4		38.5

		28-Dec-07		8:07:10		68		23.5		28-Dec-07		8:06:20		67.4		24.5		28-Dec-07		8:07:53		68		25.5		7-Feb-08		8:25:59		71.6		38

		28-Dec-07		10:07:10		69.2		24		28-Dec-07		10:06:20		69.2		25.5		28-Dec-07		10:07:53		69.8		25		7-Feb-08		10:25:59		72.21		37.5

		28-Dec-07		12:07:10		70.41		25		28-Dec-07		12:06:20		70.41		26		28-Dec-07		12:07:53		71		26		7-Feb-08		12:25:59		71.6		40.5

		28-Dec-07		14:07:10		70.41		25.5		28-Dec-07		14:06:20		70.41		26		28-Dec-07		14:07:53		71		27		7-Feb-08		14:25:59		71.6		40

		28-Dec-07		16:07:10		71		26.5		28-Dec-07		16:06:20		70.41		27.5		28-Dec-07		16:07:53		71		25		7-Feb-08		16:25:59		72.8		38

		28-Dec-07		18:07:10		71		28.5		28-Dec-07		18:06:20		68.61		31.5		28-Dec-07		18:07:53		71		29.5		7-Feb-08		18:25:59		72.8		37.5

		28-Dec-07		20:07:10		71		31.5		28-Dec-07		20:06:20		66.81		37		28-Dec-07		20:07:53		69.8		32.5		7-Feb-08		20:25:59		72.21		36

		28-Dec-07		22:07:10		69.8		33		28-Dec-07		22:06:20		66.2		38.5		28-Dec-07		22:07:53		68		34.5		7-Feb-08		22:25:59		69.2		37.5

		29-Dec-07		0:07:10		68.61		34		29-Dec-07		0:06:20		66.2		39		29-Dec-07		0:07:53		66.81		36		8-Feb-08		0:25:59		67.4		38.5

		29-Dec-07		2:07:10		68		34		29-Dec-07		2:06:20		66.2		37.5		29-Dec-07		2:07:53		66.2		36.5		8-Feb-08		2:25:59		66.81		39

		29-Dec-07		4:07:10		67.4		34		29-Dec-07		4:06:20		66.2		38		29-Dec-07		4:07:53		65.01		37		8-Feb-08		4:25:59		65.6		39.5

		29-Dec-07		6:07:10		68		33.5		29-Dec-07		6:06:20		65.6		36.5		29-Dec-07		6:07:53		66.81		35.5		8-Feb-08		6:25:59		67.4		39.5

		29-Dec-07		8:07:10		69.8		32		29-Dec-07		8:06:20		68		34.5		29-Dec-07		8:07:53		68.61		35.5		8-Feb-08		8:25:59		71		37.5

		29-Dec-07		10:07:10		70.41		32		29-Dec-07		10:06:20		69.8		33		29-Dec-07		10:07:53		70.41		33.5		8-Feb-08		10:25:59		71.6		38

		29-Dec-07		12:07:10		72.21		33		29-Dec-07		12:06:20		70.41		35		29-Dec-07		12:07:53		71.6		34		8-Feb-08		12:25:59		71		39

		29-Dec-07		14:07:10		72.8		32.5		29-Dec-07		14:06:20		71		34		29-Dec-07		14:07:53		71.6		34		8-Feb-08		14:25:59		72.21		40

		29-Dec-07		16:07:10		72.8		32		29-Dec-07		16:06:20		71		35		29-Dec-07		16:07:53		70.41		34.5		8-Feb-08		16:25:59		73.4		41

		29-Dec-07		18:07:10		72.21		32		29-Dec-07		18:06:20		69.2		35		29-Dec-07		18:07:53		69.2		35.5		8-Feb-08		18:25:59		74.01		40

		29-Dec-07		20:07:10		71		33		29-Dec-07		20:06:20		67.4		37.5		29-Dec-07		20:07:53		68		36.5		8-Feb-08		20:25:59		72.21		40.5

		29-Dec-07		22:07:10		69.2		34		29-Dec-07		22:06:20		66.81		38.5		29-Dec-07		22:07:53		66.2		37.5		8-Feb-08		22:25:59		70.41		41.5

		30-Dec-07		0:07:10		68		34.5		30-Dec-07		0:06:20		66.2		38.5		30-Dec-07		0:07:53		65.01		38.5		9-Feb-08		0:25:59		69.2		41.5

		30-Dec-07		2:07:10		67.4		35.5		30-Dec-07		2:06:20		65.6		39		30-Dec-07		2:07:53		63.8		40		9-Feb-08		2:25:59		68		41

		30-Dec-07		4:07:10		67.4		36		30-Dec-07		4:06:20		66.2		39.5		30-Dec-07		4:07:53		63.8		41		9-Feb-08		4:25:59		66.2		40.5

		30-Dec-07		6:07:10		66.81		37		30-Dec-07		6:06:20		65.6		40.5		30-Dec-07		6:07:53		63.21		42		9-Feb-08		6:25:59		67.4		39.5

		30-Dec-07		8:07:10		67.4		37		30-Dec-07		8:06:20		67.4		39		30-Dec-07		8:07:53		69.2		37		9-Feb-08		8:25:59		71		36.5

		30-Dec-07		10:07:10		68		37.5		30-Dec-07		10:06:20		67.4		40		30-Dec-07		10:07:53		67.4		39.5		9-Feb-08		10:25:59		71		37.5

		30-Dec-07		12:07:10		68		39		30-Dec-07		12:06:20		67.4		41.5		30-Dec-07		12:07:53		67.4		39.5		9-Feb-08		12:25:59		70.41		39

		30-Dec-07		14:07:10		68		40		30-Dec-07		14:06:20		67.4		42.5		30-Dec-07		14:07:53		67.4		40.5		9-Feb-08		14:25:59		71.6		37.5

		30-Dec-07		16:07:10		68		41		30-Dec-07		16:06:20		67.4		43.5		30-Dec-07		16:07:53		66.81		42.5		9-Feb-08		16:25:59		72.8		34

		30-Dec-07		18:07:10		68		41.5		30-Dec-07		18:06:20		67.4		44		30-Dec-07		18:07:53		66.81		43.5		9-Feb-08		18:25:59		73.4		33.5

		30-Dec-07		20:07:10		67.4		42.5		30-Dec-07		20:06:20		66.2		46		30-Dec-07		20:07:53		67.4		43		9-Feb-08		20:25:59		71.6		37.5

		30-Dec-07		22:07:10		66.81		43		30-Dec-07		22:06:20		66.2		46.5		30-Dec-07		22:07:53		65.01		45.5		9-Feb-08		22:25:59		69.8		38.5

		31-Dec-07		0:07:10		66.81		43.5		31-Dec-07		0:06:20		66.2		46.5		31-Dec-07		0:07:53		64.4		47		10-Feb-08		0:25:59		68		39

		31-Dec-07		2:07:10		66.81		44		31-Dec-07		2:06:20		66.2		47		31-Dec-07		2:07:53		63.8		48		10-Feb-08		2:25:59		66.2		39

		31-Dec-07		4:07:10		66.81		44		31-Dec-07		4:06:20		66.2		47		31-Dec-07		4:07:53		63.21		49		10-Feb-08		4:25:59		65.6		39.5

		31-Dec-07		6:07:10		66.81		42.5		31-Dec-07		6:06:20		65.6		44		31-Dec-07		6:07:53		63.21		48		10-Feb-08		6:25:59		64.4		40

		31-Dec-07		8:07:10		66.81		39.5		31-Dec-07		8:06:20		67.4		40		31-Dec-07		8:07:53		66.2		42		10-Feb-08		8:25:59		64.4		39.5

		31-Dec-07		10:07:10		67.4		38		31-Dec-07		10:06:20		67.4		38.5		31-Dec-07		10:07:53		68		38.5		10-Feb-08		10:25:59		65.01		40.5

		31-Dec-07		12:07:10		67.4		36.5		31-Dec-07		12:06:20		67.4		37		31-Dec-07		12:07:53		66.81		38		10-Feb-08		12:25:59		66.81		43

		31-Dec-07		14:07:10		68		34.5		31-Dec-07		14:06:20		68		34		31-Dec-07		14:07:53		67.4		36.5		10-Feb-08		14:25:59		68.61		44

		31-Dec-07		16:07:10		68		32		31-Dec-07		16:06:20		67.4		31.5		31-Dec-07		16:07:53		67.4		35		10-Feb-08		16:25:59		69.8		42

		31-Dec-07		18:07:10		68		30.5		31-Dec-07		18:06:20		68		30		31-Dec-07		18:07:53		67.4		33.5		10-Feb-08		18:25:59		71		42.5

		31-Dec-07		20:07:10		67.4		31		31-Dec-07		20:06:20		66.2		31.5		31-Dec-07		20:07:53		65.6		33.5		10-Feb-08		20:25:59		69.8		42.5

		31-Dec-07		22:07:10		66.81		31.5		31-Dec-07		22:06:20		65.6		33		31-Dec-07		22:07:53		63.8		35		10-Feb-08		22:25:59		68		43

		1-Jan-08		0:07:10		66.2		30.5		1-Jan-08		0:06:20		65.6		31.5		1-Jan-08		0:07:53		63.21		34.5		11-Feb-08		0:25:59		66.81		43

		1-Jan-08		2:07:10		66.2		29.5		1-Jan-08		2:06:20		65.6		30		1-Jan-08		2:07:53		62		33.5		11-Feb-08		2:25:59		65.6		43

		1-Jan-08		4:07:10		66.2		29		1-Jan-08		4:06:20		65.6		29.5		1-Jan-08		4:07:53		61.41		33.5		11-Feb-08		4:25:59		65.01		43

		1-Jan-08		6:07:10		66.2		28.5		1-Jan-08		6:06:20		65.6		29.5		1-Jan-08		6:07:53		67.4		29		11-Feb-08		6:25:59		64.4		42.5

		1-Jan-08		8:07:10		67.4		27		1-Jan-08		8:06:20		68.61		27.5		1-Jan-08		8:07:53		69.2		28.5		11-Feb-08		8:25:59		64.4		41.5

		1-Jan-08		10:07:10		68.61		27.5		1-Jan-08		10:06:20		69.2		28.5		1-Jan-08		10:07:53		69.8		29		11-Feb-08		10:25:59		65.6		41.5

		1-Jan-08		12:07:10		69.8		29		1-Jan-08		12:06:20		69.2		28.5		1-Jan-08		12:07:53		71.6		29		11-Feb-08		12:25:59		68		45

		1-Jan-08		14:07:10		71		29.5		1-Jan-08		14:06:20		70.41		30.5		1-Jan-08		14:07:53		71		31.5		11-Feb-08		14:25:59		69.2		45

		1-Jan-08		16:07:10		71.6		28.5		1-Jan-08		16:06:20		69.2		29		1-Jan-08		16:07:53		69.8		30.5		11-Feb-08		16:25:59		70.41		44.5

		1-Jan-08		18:07:10		71.6		29		1-Jan-08		18:06:20		69.2		30		1-Jan-08		18:07:53		69.8		31.5		11-Feb-08		18:25:59		71		45

		1-Jan-08		20:07:10		70.41		28.5		1-Jan-08		20:06:20		67.4		31		1-Jan-08		20:07:53		68.61		31.5		11-Feb-08		20:25:59		69.8		45

		1-Jan-08		22:07:10		68.61		28.5		1-Jan-08		22:06:20		66.81		31		1-Jan-08		22:07:53		66.2		31.5		11-Feb-08		22:25:59		68		45.5

		2-Jan-08		0:07:10		67.4		28.5		2-Jan-08		0:06:20		66.2		30.5		2-Jan-08		0:07:53		63.8		32		12-Feb-08		0:25:59		66.81		45.5

		2-Jan-08		2:07:10		66.81		29		2-Jan-08		2:06:20		65.6		31		2-Jan-08		2:07:53		62		33		12-Feb-08		2:25:59		65.6		45

		2-Jan-08		4:07:10		66.2		27.5		2-Jan-08		4:06:20		65.6		29.5		2-Jan-08		4:07:53		60.8		33		12-Feb-08		4:25:59		65.01		45

		2-Jan-08		6:07:10		66.81		27		2-Jan-08		6:06:20		65.6		29		2-Jan-08		6:07:53		66.81		28.5		12-Feb-08		6:25:59		66.2		44

		2-Jan-08		8:07:10		67.4		26		2-Jan-08		8:06:20		66.81		27.5		2-Jan-08		8:07:53		67.4		27.5		12-Feb-08		8:25:59		69.2		40.5

		2-Jan-08		10:07:10		68		26.5		2-Jan-08		10:06:20		67.4		28		2-Jan-08		10:07:53		67.4		28		12-Feb-08		10:25:59		72.8		40

		2-Jan-08		12:07:10		69.2		29.5		2-Jan-08		12:06:20		68		31.5		2-Jan-08		12:07:53		67.4		31		12-Feb-08		12:25:59		71.6		43

		2-Jan-08		14:07:10		70.41		31.5		2-Jan-08		14:06:20		68.61		33.5		2-Jan-08		14:07:53		68		33.5		12-Feb-08		14:25:59		72.8		43.5

		2-Jan-08		16:07:10		71.6		32		2-Jan-08		16:06:20		69.2		34		2-Jan-08		16:07:53		69.2		34.5		12-Feb-08		16:25:59		74.01		43.5

		2-Jan-08		18:07:10		72.21		31		2-Jan-08		18:06:20		69.2		33		2-Jan-08		18:07:53		68.61		34.5		12-Feb-08		18:25:59		74.01		44.5

		2-Jan-08		20:07:10		71.6		31		2-Jan-08		20:06:20		68		34		2-Jan-08		20:07:53		68		34.5		12-Feb-08		20:25:59		71.6		43.5

		2-Jan-08		22:07:10		69.2		31		2-Jan-08		22:06:20		66.81		35.5		2-Jan-08		22:07:53		66.81		34.5		12-Feb-08		22:25:59		70.41		44.5

		3-Jan-08		0:07:10		68		32		3-Jan-08		0:06:20		66.2		35.5		3-Jan-08		0:07:53		64.4		36		13-Feb-08		0:25:59		68.61		44.5

		3-Jan-08		2:07:10		66.81		31.5		3-Jan-08		2:06:20		66.2		34		3-Jan-08		2:07:53		63.21		36.5		13-Feb-08		2:25:59		67.4		44

		3-Jan-08		4:07:10		66.2		31.5		3-Jan-08		4:06:20		66.2		34		3-Jan-08		4:07:53		62		36.5		13-Feb-08		4:25:59		66.2		44

		3-Jan-08		6:07:10		66.81		31.5		3-Jan-08		6:06:20		65.6		34		3-Jan-08		6:07:53		66.81		33.5		13-Feb-08		6:25:59		66.81		43.5

		3-Jan-08		8:07:10		68.61		29.5		3-Jan-08		8:06:20		67.4		31.5		3-Jan-08		8:07:53		68		32.5		13-Feb-08		8:25:59		72.21		39.5

		3-Jan-08		10:07:10		69.2		30.5		3-Jan-08		10:06:20		69.8		32.5		3-Jan-08		10:07:53		69.8		32		13-Feb-08		10:25:59		71.6		40.5

		3-Jan-08		12:07:10		71.6		32		3-Jan-08		12:06:20		71		32.5		3-Jan-08		12:07:53		72.21		32.5		13-Feb-08		12:25:59		72.21		43

		3-Jan-08		14:07:10		72.8		31		3-Jan-08		14:06:20		71		30.5		3-Jan-08		14:07:53		71		35		13-Feb-08		14:25:59		74.01		43.5

		3-Jan-08		16:07:10		72.21		32.5		3-Jan-08		16:06:20		71		34.5		3-Jan-08		16:07:53		70.41		33.5		13-Feb-08		16:25:59		74.6		44.5

		3-Jan-08		18:07:10		72.21		32.5		3-Jan-08		18:06:20		69.2		35		3-Jan-08		18:07:53		70.41		35.5		13-Feb-08		18:25:59		74.01		44

		3-Jan-08		20:07:10		71.6		34		3-Jan-08		20:06:20		68		39		3-Jan-08		20:07:53		69.8		36.5		13-Feb-08		20:25:59		72.21		43.5

		3-Jan-08		22:07:10		70.41		33.5		3-Jan-08		22:06:20		66.81		37.5		3-Jan-08		22:07:53		68		36.5		13-Feb-08		22:25:59		71		43.5

		4-Jan-08		0:07:10		69.2		33		4-Jan-08		0:06:20		66.2		37		4-Jan-08		0:07:53		66.2		36.5		14-Feb-08		0:25:59		68.61		43.5

		4-Jan-08		2:07:10		68.61		34.5		4-Jan-08		2:06:20		66.2		39		4-Jan-08		2:07:53		65.01		38.5		14-Feb-08		2:25:59		67.4		43.5

		4-Jan-08		4:07:10		68		35		4-Jan-08		4:06:20		66.2		39.5		4-Jan-08		4:07:53		65.01		39.5		14-Feb-08		4:25:59		66.2		43.5

		4-Jan-08		6:07:10		68.61		36.5		4-Jan-08		6:06:20		66.2		41		4-Jan-08		6:07:53		66.81		40		14-Feb-08		6:25:59		66.81		44

		4-Jan-08		8:07:10		71		37.5		4-Jan-08		8:06:20		68.61		42		4-Jan-08		8:07:53		70.41		39.5		14-Feb-08		8:25:59		70.41		41

		4-Jan-08		10:07:10		72.21		39		4-Jan-08		10:06:20		70.41		40		4-Jan-08		10:07:53		71.6		40.5		14-Feb-08		10:25:59		71.6		37

		4-Jan-08		12:07:10		73.4		40		4-Jan-08		12:06:20		71		46.5		4-Jan-08		12:07:53		71		45.5		14-Feb-08		12:25:59		71.6		36.5

		4-Jan-08		14:07:10		72.8		42.5		4-Jan-08		14:06:20		71		47.5		4-Jan-08		14:07:53		71		45.5		14-Feb-08		14:25:59		72.8		36

		4-Jan-08		16:07:10		73.4		43.5		4-Jan-08		16:06:20		70.41		49		4-Jan-08		16:07:53		71.6		41.5		14-Feb-08		16:25:59		73.4		32

		4-Jan-08		18:07:10		72.8		42.5		4-Jan-08		18:06:20		69.8		47.5		4-Jan-08		18:07:53		71		42		14-Feb-08		18:25:59		73.4		29

		4-Jan-08		20:07:10		71.6		42.5		4-Jan-08		20:06:20		69.2		48		4-Jan-08		20:07:53		69.8		45.5		14-Feb-08		20:25:59		71.6		28

		4-Jan-08		22:07:10		71		43		4-Jan-08		22:06:20		68		49.5		4-Jan-08		22:07:53		69.2		46.5		14-Feb-08		22:25:59		70.41		31.5

		5-Jan-08		0:07:10		69.8		43.5		5-Jan-08		0:06:20		67.4		50.5		5-Jan-08		0:07:53		69.2		46.5		15-Feb-08		0:25:59		68.61		32.5

		5-Jan-08		2:07:10		69.2		44		5-Jan-08		2:06:20		67.4		51		5-Jan-08		2:07:53		68.61		47		15-Feb-08		2:25:59		67.4		33

		5-Jan-08		4:07:10		69.2		45		5-Jan-08		4:06:20		67.4		52.5		5-Jan-08		4:07:53		68.61		48		15-Feb-08		4:25:59		66.2		33.5

		5-Jan-08		6:07:10		68.61		46		5-Jan-08		6:06:20		67.4		53.5		5-Jan-08		6:07:53		68		49		15-Feb-08		6:25:59		66.81		33.5

		5-Jan-08		8:07:10		69.8		47		5-Jan-08		8:06:20		69.2		53.5		5-Jan-08		8:07:53		70.41		53		15-Feb-08		8:25:59		70.41		32

		5-Jan-08		10:07:10		71		49.5		5-Jan-08		10:06:20		70.41		56.5		5-Jan-08		10:07:53		71		49		15-Feb-08		10:25:59		71.6		30.5

		5-Jan-08		12:07:10		71		49.5		5-Jan-08		12:06:20		71		51		5-Jan-08		12:07:53		71		54.5		15-Feb-08		12:25:59		72.21		30

		5-Jan-08		14:07:10		70.41		46		5-Jan-08		14:06:20		70.41		47		5-Jan-08		14:07:53		72.21		45.5		15-Feb-08		14:25:59		72.8		30.5

		5-Jan-08		16:07:10		69.8		45.5		5-Jan-08		16:06:20		71		46		5-Jan-08		16:07:53		71		46		15-Feb-08		16:25:59		73.4		29.5

		5-Jan-08		18:07:10		73.4		41.5		5-Jan-08		18:06:20		74.01		42		5-Jan-08		18:07:53		74.01		42.5		15-Feb-08		18:25:59		74.01		30

		5-Jan-08		20:07:10		69.2		42.5		5-Jan-08		20:06:20		68		44.5		5-Jan-08		20:07:53		69.2		43.5		15-Feb-08		20:25:59		71		30

		5-Jan-08		22:07:10		68		41.5		5-Jan-08		22:06:20		66.81		43.5		5-Jan-08		22:07:53		68		44		15-Feb-08		22:25:59		69.2		31.5

		6-Jan-08		0:07:10		67.4		41		6-Jan-08		0:06:20		66.81		42.5		6-Jan-08		0:07:53		67.4		43.5		16-Feb-08		0:25:59		68		33

		6-Jan-08		2:07:10		66.81		39.5		6-Jan-08		2:06:20		66.81		39.5		6-Jan-08		2:07:53		66.2		42.5		16-Feb-08		2:25:59		66.2		34

		6-Jan-08		4:07:10		66.2		41		6-Jan-08		4:06:20		66.2		42		6-Jan-08		4:07:53		65.6		43		16-Feb-08		4:25:59		65.6		35

		6-Jan-08		6:07:10		65.6		41		6-Jan-08		6:06:20		66.2		41		6-Jan-08		6:07:53		65.01		43.5		16-Feb-08		6:25:59		66.2		36

		6-Jan-08		8:07:10		65.6		42		6-Jan-08		8:06:20		68		40		6-Jan-08		8:07:53		66.81		41		16-Feb-08		8:25:59		69.2		34

		6-Jan-08		10:07:10		65.6		43.5		6-Jan-08		10:06:20		68		42.5		6-Jan-08		10:07:53		66.81		42.5		16-Feb-08		10:25:59		71.6		34.5

		6-Jan-08		12:07:10		65.6		44.5		6-Jan-08		12:06:20		68		42.5		6-Jan-08		12:07:53		67.4		43		16-Feb-08		12:25:59		72.21		34

		6-Jan-08		14:07:10		65.6		45.5		6-Jan-08		14:06:20		68		44		6-Jan-08		14:07:53		67.4		45		16-Feb-08		14:25:59		72.8		34

		6-Jan-08		16:07:10		66.2		45		6-Jan-08		16:06:20		68		43.5		6-Jan-08		16:07:53		68		44.5		16-Feb-08		16:25:59		74.6		37

		6-Jan-08		18:07:10		66.2		45		6-Jan-08		18:06:20		68		44		6-Jan-08		18:07:53		67.4		45		16-Feb-08		18:25:59		74.01		37

		6-Jan-08		20:07:10		66.2		45		6-Jan-08		20:06:20		66.81		44.5		6-Jan-08		20:07:53		67.4		44		16-Feb-08		20:25:59		71.6		37.5

		6-Jan-08		22:07:10		65.6		43		6-Jan-08		22:06:20		66.81		42.5		6-Jan-08		22:07:53		66.2		43.5		16-Feb-08		22:25:59		69.2		38

		7-Jan-08		0:07:10		65.01		42.5		7-Jan-08		0:06:20		66.2		41.5		7-Jan-08		0:07:53		65.6		43		17-Feb-08		0:25:59		68		39

		7-Jan-08		2:07:10		65.01		42.5		7-Jan-08		2:06:20		66.2		41		7-Jan-08		2:07:53		65.6		43		17-Feb-08		2:25:59		67.4		39.5

		7-Jan-08		4:07:10		64.4		41.5		7-Jan-08		4:06:20		66.2		40		7-Jan-08		4:07:53		65.01		42		17-Feb-08		4:25:59		66.81		40.5

		7-Jan-08		6:07:10		64.4		40		7-Jan-08		6:06:20		66.2		38		7-Jan-08		6:07:53		64.4		41		17-Feb-08		6:25:59		66.81		41

		7-Jan-08		8:07:10		64.4		40.5		7-Jan-08		8:06:20		67.4		37		7-Jan-08		8:07:53		66.81		38.5		17-Feb-08		8:25:59		66.2		41

		7-Jan-08		10:07:10		64.4		39		7-Jan-08		10:06:20		67.4		35.5		7-Jan-08		10:07:53		67.4		36.5		17-Feb-08		10:25:59		66.2		41

		7-Jan-08		12:07:10		64.4		41		7-Jan-08		12:06:20		68		38.5		7-Jan-08		12:07:53		67.4		38.5		17-Feb-08		12:25:59		66.81		42

		7-Jan-08		14:07:10		65.01		43		7-Jan-08		14:06:20		68		41		7-Jan-08		14:07:53		67.4		41		17-Feb-08		14:25:59		67.4		43

		7-Jan-08		16:07:10		65.6		42.5		7-Jan-08		16:06:20		68		39.5		7-Jan-08		16:07:53		68		40.5		17-Feb-08		16:25:59		68.61		42

		7-Jan-08		18:07:10		65.6		41.5		7-Jan-08		18:06:20		68		39.5		7-Jan-08		18:07:53		68		40		17-Feb-08		18:25:59		69.2		41

		7-Jan-08		20:07:10		65.6		42		7-Jan-08		20:06:20		66.81		41.5		7-Jan-08		20:07:53		66.81		41		17-Feb-08		20:25:59		68		41.5

		7-Jan-08		22:07:10		65.01		43.5		7-Jan-08		22:06:20		66.81		42.5		7-Jan-08		22:07:53		65.6		43		17-Feb-08		22:25:59		67.4		42

		8-Jan-08		0:07:10		65.01		44.5		8-Jan-08		0:06:20		66.81		43		8-Jan-08		0:07:53		65.6		44		18-Feb-08		0:25:59		66.2		42

		8-Jan-08		2:07:10		64.4		44		8-Jan-08		2:06:20		66.81		42.5		8-Jan-08		2:07:53		65.01		44		18-Feb-08		2:25:59		65.6		42.5

		8-Jan-08		4:07:10		64.4		44.5		8-Jan-08		4:06:20		66.2		42.5		8-Jan-08		4:07:53		65.01		44		18-Feb-08		4:25:59		65.01		43.5

		8-Jan-08		6:07:10		64.4		44		8-Jan-08		6:06:20		66.2		41.5		8-Jan-08		6:07:53		66.81		41.5		18-Feb-08		6:25:59		65.01		44

		8-Jan-08		8:07:10		65.6		41		8-Jan-08		8:06:20		68		37.5		8-Jan-08		8:07:53		69.2		38.5		18-Feb-08		8:25:59		65.6		43

		8-Jan-08		10:07:10		66.2		39.5		8-Jan-08		10:06:20		69.8		35.5		8-Jan-08		10:07:53		71		36.5		18-Feb-08		10:25:59		66.2		42.5

		8-Jan-08		12:07:10		67.4		42		8-Jan-08		12:06:20		71.6		40.5		8-Jan-08		12:07:53		72.21		39		18-Feb-08		12:25:59		67.4		42

		8-Jan-08		14:07:10		68		38.5		8-Jan-08		14:06:20		71.6		35.5		8-Jan-08		14:07:53		70.41		40.5		18-Feb-08		14:25:59		68		42.5

		8-Jan-08		16:07:10		68.61		35.5		8-Jan-08		16:06:20		71		33.5		8-Jan-08		16:07:53		71		35.5		18-Feb-08		16:25:59		68		43.5

		8-Jan-08		18:07:10		68.61		34		8-Jan-08		18:06:20		69.2		34		8-Jan-08		18:07:53		70.41		36		18-Feb-08		18:25:59		68		43.5

		8-Jan-08		20:07:10		68		34.5		8-Jan-08		20:06:20		67.4		36		8-Jan-08		20:07:53		69.2		36		18-Feb-08		20:25:59		67.4		43.5

		8-Jan-08		22:07:10		67.4		35.5		8-Jan-08		22:06:20		66.81		36.5		8-Jan-08		22:07:53		67.4		38		18-Feb-08		22:25:59		66.2		43.5

		9-Jan-08		0:07:10		66.81		36.5		9-Jan-08		0:06:20		66.81		37		9-Jan-08		0:07:53		65.6		38.5		19-Feb-08		0:25:59		65.6		44.5

		9-Jan-08		2:07:10		65.6		37.5		9-Jan-08		2:06:20		66.81		37.5		9-Jan-08		2:07:53		64.4		39.5		19-Feb-08		2:25:59		65.6		45

		9-Jan-08		4:07:10		65.01		38		9-Jan-08		4:06:20		66.2		38		9-Jan-08		4:07:53		63.21		41		19-Feb-08		4:25:59		65.01		45.5

		9-Jan-08		6:07:10		65.01		39		9-Jan-08		6:06:20		66.2		38.5		9-Jan-08		6:07:53		67.4		38		19-Feb-08		6:25:59		66.2		45

		9-Jan-08		8:07:10		65.6		39		9-Jan-08		8:06:20		68		37.5		9-Jan-08		8:07:53		68.61		39		19-Feb-08		8:25:59		69.8		42.5

		9-Jan-08		10:07:10		66.81		41		9-Jan-08		10:06:20		71		37.5		9-Jan-08		10:07:53		70.41		39.5		19-Feb-08		10:25:59		72.21		40.5

		9-Jan-08		12:07:10		67.4		42.5		9-Jan-08		12:06:20		71		42		9-Jan-08		12:07:53		71		41.5		19-Feb-08		12:25:59		71.6		40.5

		9-Jan-08		14:07:10		68.61		44.5		9-Jan-08		14:06:20		72.8		43.5		9-Jan-08		14:07:53		71.6		42.5		19-Feb-08		14:25:59		71.6		40.5

		9-Jan-08		16:07:10		69.2		46		9-Jan-08		16:06:20		74.01		42.5		9-Jan-08		16:07:53		71		44		19-Feb-08		16:25:59		72.21		40.5

		9-Jan-08		18:07:10		69.8		46		9-Jan-08		18:06:20		71		46		9-Jan-08		18:07:53		71.6		38.5		19-Feb-08		18:25:59		71.6		41

		9-Jan-08		20:07:10		70.41		45		9-Jan-08		20:06:20		69.8		45		9-Jan-08		20:07:53		70.41		44.5		19-Feb-08		20:25:59		71.6		41

		9-Jan-08		22:07:10		69.2		42.5		9-Jan-08		22:06:20		68		44.5		9-Jan-08		22:07:53		68.61		43.5		19-Feb-08		22:25:59		69.2		41.5

		10-Jan-08		0:07:10		68		44		10-Jan-08		0:06:20		66.81		46.5		10-Jan-08		0:07:53		67.4		45		20-Feb-08		0:25:59		67.4		42

		10-Jan-08		2:07:10		67.4		45		10-Jan-08		2:06:20		66.81		47		10-Jan-08		2:07:53		66.2		46.5		20-Feb-08		2:25:59		66.81		42.5

		10-Jan-08		4:07:10		66.81		45.5		10-Jan-08		4:06:20		66.81		46		10-Jan-08		4:07:53		65.6		47		20-Feb-08		4:25:59		66.2		43.5

		10-Jan-08		6:07:10		66.2		46		10-Jan-08		6:06:20		67.4		45.5		10-Jan-08		6:07:53		66.81		45.5		20-Feb-08		6:25:59		66.81		43.5

		10-Jan-08		8:07:10		66.81		45		10-Jan-08		8:06:20		69.8		41.5		10-Jan-08		8:07:53		70.41		43		20-Feb-08		8:25:59		71.6		42

		10-Jan-08		10:07:10		68		44.5		10-Jan-08		10:06:20		70.41		41		10-Jan-08		10:07:53		72.21		41.5		20-Feb-08		10:25:59		72.8		41

		10-Jan-08		12:07:10		68.61		43.5		10-Jan-08		12:06:20		70.41		39		10-Jan-08		12:07:53		71.6		42		20-Feb-08		12:25:59		72.8		41.5

		10-Jan-08		14:07:10		69.2		43.5		10-Jan-08		14:06:20		70.41		45		10-Jan-08		14:07:53		71.6		44		20-Feb-08		14:25:59		72.21		43.5

		10-Jan-08		16:07:10		69.2		43		10-Jan-08		16:06:20		70.41		39.5		10-Jan-08		16:07:53		71		43		20-Feb-08		16:25:59		72.21		45.5

		10-Jan-08		18:07:10		69.2		43		10-Jan-08		18:06:20		68.61		44		10-Jan-08		18:07:53		70.41		43.5		20-Feb-08		18:25:59		71.6		45.5

		10-Jan-08		20:07:10		69.2		42.5		10-Jan-08		20:06:20		68		44.5		10-Jan-08		20:07:53		69.2		42.5		20-Feb-08		20:25:59		71.6		45.5

		10-Jan-08		22:07:10		68.61		43		10-Jan-08		22:06:20		67.4		45		10-Jan-08		22:07:53		68		44		20-Feb-08		22:25:59		70.41		45.5

		11-Jan-08		0:07:10		68		43.5		11-Jan-08		0:06:20		67.4		44.5		11-Jan-08		0:07:53		67.4		44.5		21-Feb-08		0:25:59		68.61		46

		11-Jan-08		2:07:10		67.4		44		11-Jan-08		2:06:20		67.4		45.5		11-Jan-08		2:07:53		66.81		45.5		21-Feb-08		2:25:59		68		46

		11-Jan-08		4:07:10		67.4		44		11-Jan-08		4:06:20		67.4		45		11-Jan-08		4:07:53		65.6		46.5		21-Feb-08		4:25:59		66.81		46.5

		11-Jan-08		6:07:10		66.81		44.5		11-Jan-08		6:06:20		67.4		45		11-Jan-08		6:07:53		68		45		21-Feb-08		6:25:59		66.81		47

		11-Jan-08		8:07:10		67.4		45		11-Jan-08		8:06:20		67.4		45		11-Jan-08		8:07:53		69.8		44		21-Feb-08		8:25:59		71		44.5

		11-Jan-08		10:07:10		68		46		11-Jan-08		10:06:20		72.21		42.5		11-Jan-08		10:07:53		71.6		43		21-Feb-08		10:25:59		72.21		44

		11-Jan-08		12:07:10		69.2		46.5		11-Jan-08		12:06:20		72.8		44		11-Jan-08		12:07:53		71.6		47		21-Feb-08		12:25:59		72.8		43.5

		11-Jan-08		14:07:10		70.41		47.5		11-Jan-08		14:06:20		72.8		46		11-Jan-08		14:07:53		71		41.5		21-Feb-08		14:25:59		73.4		42

		11-Jan-08		16:07:10		70.41		47		11-Jan-08		16:06:20		73.4		40		11-Jan-08		16:07:53		71		48.5		21-Feb-08		16:25:59		74.01		40.5

		11-Jan-08		18:07:10		70.41		47		11-Jan-08		18:06:20		71		46.5		11-Jan-08		18:07:53		70.41		44.5		21-Feb-08		18:25:59		73.4		41

		11-Jan-08		20:07:10		69.8		46		11-Jan-08		20:06:20		69.2		48		11-Jan-08		20:07:53		70.41		44.5		21-Feb-08		20:25:59		72.21		40.5

		11-Jan-08		22:07:10		68.61		47		11-Jan-08		22:06:20		68		49.5		11-Jan-08		22:07:53		69.2		47		21-Feb-08		22:25:59		71		41

		12-Jan-08		0:07:10		68		48		12-Jan-08		0:06:20		68		49.5		12-Jan-08		0:07:53		68		48		22-Feb-08		0:25:59		69.8		41

		12-Jan-08		2:07:10		67.4		49		12-Jan-08		2:06:20		68		50		12-Jan-08		2:07:53		67.4		49		22-Feb-08		2:25:59		68.61		42

		12-Jan-08		4:07:10		66.81		48.5		12-Jan-08		4:06:20		67.4		48.5		12-Jan-08		4:07:53		66.81		49		22-Feb-08		4:25:59		67.4		43

		12-Jan-08		6:07:10		66.81		47.5		12-Jan-08		6:06:20		67.4		46.5		12-Jan-08		6:07:53		67.4		47.5		22-Feb-08		6:25:59		67.4		43.5

		12-Jan-08		8:07:10		66.81		46		12-Jan-08		8:06:20		69.2		43		12-Jan-08		8:07:53		69.8		45		22-Feb-08		8:25:59		71.6		42

		12-Jan-08		10:07:10		68		45.5		12-Jan-08		10:06:20		72.8		38		12-Jan-08		10:07:53		71.6		43		22-Feb-08		10:25:59		72.8		41

		12-Jan-08		12:07:10		68		45.5		12-Jan-08		12:06:20		71		45		12-Jan-08		12:07:53		71		41		22-Feb-08		12:25:59		72.8		42.5

		12-Jan-08		14:07:10		68		44.5		12-Jan-08		14:06:20		70.41		42		12-Jan-08		14:07:53		69.8		44		22-Feb-08		14:25:59		72.21		42

		12-Jan-08		16:07:10		68		45		12-Jan-08		16:06:20		68.61		44		12-Jan-08		16:07:53		70.41		43.5		22-Feb-08		16:25:59		72.21		43.5

		12-Jan-08		18:07:10		67.4		45		12-Jan-08		18:06:20		68.61		44.5		12-Jan-08		18:07:53		69.8		43.5		22-Feb-08		18:25:59		72.21		44

		12-Jan-08		20:07:10		67.4		45.5		12-Jan-08		20:06:20		68		45.5		12-Jan-08		20:07:53		69.2		44		22-Feb-08		20:25:59		72.21		43.5

		12-Jan-08		22:07:10		66.81		45.5		12-Jan-08		22:06:20		66.81		46.5		12-Jan-08		22:07:53		69.2		44.5		22-Feb-08		22:25:59		70.41		44.5

		13-Jan-08		0:07:10		65.6		47		13-Jan-08		0:06:20		66.2		48		13-Jan-08		0:07:53		69.2		43.5		23-Feb-08		0:25:59		68.61		45

		13-Jan-08		2:07:10		65.01		47.5		13-Jan-08		2:06:20		66.2		47.5		13-Jan-08		2:07:53		69.2		43		23-Feb-08		2:25:59		68		45.5

		13-Jan-08		4:07:10		65.01		48		13-Jan-08		4:06:20		66.2		47		13-Jan-08		4:07:53		69.8		42.5		23-Feb-08		4:25:59		67.4		45.5

		13-Jan-08		6:07:10		64.4		49		13-Jan-08		6:06:20		66.2		48		13-Jan-08		6:07:53		69.8		43		23-Feb-08		6:25:59		67.4		45

		13-Jan-08		8:07:10		64.4		49		13-Jan-08		8:06:20		67.4		45.5		13-Jan-08		8:07:53		69.8		42.5		23-Feb-08		8:25:59		72.8		42.5

		13-Jan-08		10:07:10		64.4		49.5		13-Jan-08		10:06:20		68		45.5		13-Jan-08		10:07:53		69.8		42.5		23-Feb-08		10:25:59		72.8		42.5

		13-Jan-08		12:07:10		65.01		50		13-Jan-08		12:06:20		68		47		13-Jan-08		12:07:53		69.8		45		23-Feb-08		12:25:59		71.6		42.5

		13-Jan-08		14:07:10		65.6		49.5		13-Jan-08		14:06:20		68.61		46		13-Jan-08		14:07:53		69.8		44		23-Feb-08		14:25:59		71.6		43

		13-Jan-08		16:07:10		66.2		49.5		13-Jan-08		16:06:20		69.2		46		13-Jan-08		16:07:53		69.8		45.5		23-Feb-08		16:25:59		72.8		41

		13-Jan-08		18:07:10		66.81		49.5		13-Jan-08		18:06:20		69.2		45		13-Jan-08		18:07:53		69.8		46.5		23-Feb-08		18:25:59		72.8		38.5

		13-Jan-08		20:07:10		66.81		48.5		13-Jan-08		20:06:20		68		47.5		13-Jan-08		20:07:53		69.2		45.5		23-Feb-08		20:25:59		71.6		38

		13-Jan-08		22:07:10		66.2		47		13-Jan-08		22:06:20		66.2		46		13-Jan-08		22:07:53		69.2		43		23-Feb-08		22:25:59		69.2		38.5

		14-Jan-08		0:07:10		65.01		46.5		14-Jan-08		0:06:20		65.6		45.5		14-Jan-08		0:07:53		69.2		41		24-Feb-08		0:25:59		66.81		39.5

		14-Jan-08		2:07:10		64.4		48		14-Jan-08		2:06:20		65.6		47		14-Jan-08		2:07:53		69.8		41.5		24-Feb-08		2:25:59		65.6		40

		14-Jan-08		4:07:10		64.4		49.5		14-Jan-08		4:06:20		65.6		48		14-Jan-08		4:07:53		69.8		42		24-Feb-08		4:25:59		64.4		40

		14-Jan-08		6:07:10		64.4		50.5		14-Jan-08		6:06:20		66.2		49		14-Jan-08		6:07:53		69.8		42.5		24-Feb-08		6:25:59		64.4		40.5

		14-Jan-08		8:07:10		64.4		51.5		14-Jan-08		8:06:20		68		47		14-Jan-08		8:07:53		69.8		43		24-Feb-08		8:25:59		65.01		40.5

		14-Jan-08		10:07:10		64.4		50		14-Jan-08		10:06:20		68		45.5		14-Jan-08		10:07:53		69.8		42		24-Feb-08		10:25:59		65.01		41.5

		14-Jan-08		12:07:10		65.01		49		14-Jan-08		12:06:20		68		44.5		14-Jan-08		12:07:53		70.41		39.5		24-Feb-08		12:25:59		65.6		42.5

		14-Jan-08		14:07:10		65.01		49		14-Jan-08		14:06:20		68		45		14-Jan-08		14:07:53		69.8		38.5		24-Feb-08		14:25:59		66.2		43.5

		14-Jan-08		16:07:10		65.6		49.5		14-Jan-08		16:06:20		68.61		46.5		14-Jan-08		16:07:53		69.8		42.5		24-Feb-08		16:25:59		65.6		43.5

		14-Jan-08		18:07:10		66.2		49.5		14-Jan-08		18:06:20		68.61		47		14-Jan-08		18:07:53		69.8		45		24-Feb-08		18:25:59		65.01		44

		14-Jan-08		20:07:10		66.2		48.5		14-Jan-08		20:06:20		67.4		47		14-Jan-08		20:07:53		69.8		44		24-Feb-08		20:25:59		64.4		45

		14-Jan-08		22:07:10		65.6		47		14-Jan-08		22:06:20		66.2		46		14-Jan-08		22:07:53		69.8		41.5		24-Feb-08		22:25:59		64.4		46

		15-Jan-08		0:07:10		64.4		44		15-Jan-08		0:06:20		65.6		42		15-Jan-08		0:07:53		69.2		39		25-Feb-08		0:25:59		64.4		47.5

		15-Jan-08		2:07:10		63.8		45		15-Jan-08		2:06:20		65.6		43		15-Jan-08		2:07:53		69.8		38.5		25-Feb-08		2:25:59		64.4		48

		15-Jan-08		4:07:10		63.8		45		15-Jan-08		4:06:20		65.6		42.5		15-Jan-08		4:07:53		69.8		38		25-Feb-08		4:25:59		64.4		49

		15-Jan-08		6:07:10		63.21		46		15-Jan-08		6:06:20		65.6		44		15-Jan-08		6:07:53		69.8		38.5		25-Feb-08		6:25:59		64.4		49.5

		15-Jan-08		8:07:10		63.8		47		15-Jan-08		8:06:20		67.4		42.5		15-Jan-08		8:07:53		71		39.5		25-Feb-08		8:25:59		65.01		49.5

		15-Jan-08		10:07:10		65.01		47.5		15-Jan-08		10:06:20		70.41		41.5		15-Jan-08		10:07:53		71		37		25-Feb-08		10:25:59		66.2		49.5

		15-Jan-08		12:07:10		65.6		47.5		15-Jan-08		12:06:20		70.41		43		15-Jan-08		12:07:53		71		43.5		25-Feb-08		12:25:59		66.81		49.5

		15-Jan-08		14:07:10		66.2		48		15-Jan-08		14:06:20		70.41		46.5		15-Jan-08		14:07:53		71		43.5		25-Feb-08		14:25:59		67.4		50

		15-Jan-08		16:07:10		66.81		49.5		15-Jan-08		16:06:20		71		44		15-Jan-08		16:07:53		70.41		45		25-Feb-08		16:25:59		67.4		50

		15-Jan-08		18:07:10		66.81		48		15-Jan-08		18:06:20		69.2		44		15-Jan-08		18:07:53		70.41		43.5		25-Feb-08		18:25:59		67.4		49.5

		15-Jan-08		20:07:10		66.81		45.5		15-Jan-08		20:06:20		67.4		44		15-Jan-08		20:07:53		69.8		41.5		25-Feb-08		20:25:59		66.81		49

		15-Jan-08		22:07:10		65.6		43.5		15-Jan-08		22:06:20		65.6		42.5		15-Jan-08		22:07:53		68.61		41		25-Feb-08		22:25:59		66.2		49

		16-Jan-08		0:07:10		65.01		43		16-Jan-08		0:06:20		65.6		41		16-Jan-08		0:07:53		66.81		40		26-Feb-08		0:25:59		65.6		49.5

		16-Jan-08		2:07:10		64.4		42.5		16-Jan-08		2:06:20		65.01		41.5		16-Jan-08		2:07:53		65.6		41		26-Feb-08		2:25:59		65.01		50

		16-Jan-08		4:07:10		63.8		42.5		16-Jan-08		4:06:20		65.6		40		16-Jan-08		4:07:53		64.4		41		26-Feb-08		4:25:59		64.4		49.5

		16-Jan-08		6:07:10		63.21		42		16-Jan-08		6:06:20		65.01		40		16-Jan-08		6:07:53		67.4		38		26-Feb-08		6:25:59		66.2		48

		16-Jan-08		8:07:10		63.8		41		16-Jan-08		8:06:20		67.4		37		16-Jan-08		8:07:53		69.2		36.5		26-Feb-08		8:25:59		69.8		45

		16-Jan-08		10:07:10		65.01		41		16-Jan-08		10:06:20		70.41		36		16-Jan-08		10:07:53		71		36		26-Feb-08		10:25:59		72.21		44

		16-Jan-08		12:07:10		65.6		42.5		16-Jan-08		12:06:20		71		35		16-Jan-08		12:07:53		71.6		36		26-Feb-08		12:25:59		72.21		43.5

		16-Jan-08		14:07:10		66.81		44.5		16-Jan-08		14:06:20		71		39		16-Jan-08		14:07:53		70.41		43.5		26-Feb-08		14:25:59		72.8		43

		16-Jan-08		16:07:10		68		46		16-Jan-08		16:06:20		71.6		40.5		16-Jan-08		16:07:53		69.8		44.5		26-Feb-08		16:25:59		73.4		42

		16-Jan-08		18:07:10		68		44.5		16-Jan-08		18:06:20		69.8		42		16-Jan-08		18:07:53		69.8		43.5		26-Feb-08		18:25:59		73.4		42.5

		16-Jan-08		20:07:10		68		44		16-Jan-08		20:06:20		68.61		43.5		16-Jan-08		20:07:53		69.2		43		26-Feb-08		20:25:59		72.21		42.5

		16-Jan-08		22:07:10		67.4		42		16-Jan-08		22:06:20		66.81		43		16-Jan-08		22:07:53		68.61		40.5		26-Feb-08		22:25:59		70.41		43.5

		17-Jan-08		0:07:10		66.2		40.5		17-Jan-08		0:06:20		65.6		41		17-Jan-08		0:07:53		66.81		39.5		27-Feb-08		0:25:59		68		43.5

		17-Jan-08		2:07:10		65.01		40.5		17-Jan-08		2:06:20		65.6		39		17-Jan-08		2:07:53		65.6		39.5		27-Feb-08		2:25:59		66.81		43.5

		17-Jan-08		4:07:10		63.8		40		17-Jan-08		4:06:20		65.6		38.5		17-Jan-08		4:07:53		64.4		39.5		27-Feb-08		4:25:59		65.6		43.5

		17-Jan-08		6:07:10		63.8		39.5		17-Jan-08		6:06:20		65.6		37		17-Jan-08		6:07:53		66.2		37		27-Feb-08		6:25:59		66.81		43.5

		17-Jan-08		8:07:10		64.4		38.5		17-Jan-08		8:06:20		68		34.5		17-Jan-08		8:07:53		69.2		35.5		27-Feb-08		8:25:59		71.6		41

		17-Jan-08		10:07:10		65.01		35		17-Jan-08		10:06:20		70.41		29.5		17-Jan-08		10:07:53		71.6		31		27-Feb-08		10:25:59		72.21		41

		17-Jan-08		12:07:10		66.2		29		17-Jan-08		12:06:20		71		21.5		17-Jan-08		12:07:53		69.8		23.5		27-Feb-08		12:25:59		72.21		42.5

		17-Jan-08		14:07:10		67.4		27		17-Jan-08		14:06:20		71		22.5		17-Jan-08		14:07:53		71		23.5		27-Feb-08		14:25:59		74.01		40

		17-Jan-08		16:07:10		68		25		17-Jan-08		16:06:20		70.41		21.5		17-Jan-08		16:07:53		70.41		24.5		27-Feb-08		16:25:59		74.01		40

		17-Jan-08		18:07:10		68.61		24		17-Jan-08		18:06:20		69.8		19		17-Jan-08		18:07:53		69.8		22.5		27-Feb-08		18:25:59		74.01		41.5

		17-Jan-08		20:07:10		68.61		22		17-Jan-08		20:06:20		69.8		18		17-Jan-08		20:07:53		70.41		23		27-Feb-08		20:25:59		72.8		42.5

		17-Jan-08		22:07:10		68.61		20.5		17-Jan-08		22:06:20		69.2		17.5		17-Jan-08		22:07:53		70.41		24		27-Feb-08		22:25:59		71.6		43

		18-Jan-08		0:07:10		68		20		18-Jan-08		0:06:20		68		18		18-Jan-08		0:07:53		69.2		23		28-Feb-08		0:25:59		69.8		43

		18-Jan-08		2:07:10		67.4		21.5		18-Jan-08		2:06:20		66.2		22		18-Jan-08		2:07:53		68		24		28-Feb-08		2:25:59		68.61		44

		18-Jan-08		4:07:10		66.2		21		18-Jan-08		4:06:20		66.2		20		18-Jan-08		4:07:53		66.81		23.5		28-Feb-08		4:25:59		67.4		44

		18-Jan-08		6:07:10		65.6		24.5		18-Jan-08		6:06:20		65.6		26		18-Jan-08		6:07:53		65.6		26		28-Feb-08		6:25:59		67.4		43.5

		18-Jan-08		8:07:10		65.6		26.5		18-Jan-08		8:06:20		67.4		26		18-Jan-08		8:07:53		69.8		26		28-Feb-08		8:25:59		71		41

		18-Jan-08		10:07:10		66.81		29		18-Jan-08		10:06:20		70.41		27.5		18-Jan-08		10:07:53		71.6		27		28-Feb-08		10:25:59		72.21		41

		18-Jan-08		12:07:10		67.4		28.5		18-Jan-08		12:06:20		71		26.5		18-Jan-08		12:07:53		71		28		28-Feb-08		12:25:59		72.8		42.5

		18-Jan-08		14:07:10		68		29		18-Jan-08		14:06:20		71		28		18-Jan-08		14:07:53		71		29		28-Feb-08		14:25:59		74.01		42.5

		18-Jan-08		16:07:10		68.61		29		18-Jan-08		16:06:20		70.41		29.5		18-Jan-08		16:07:53		71		31.5		28-Feb-08		16:25:59		75.2		43.5

		18-Jan-08		18:07:10		69.2		30		18-Jan-08		18:06:20		69.8		29.5		18-Jan-08		18:07:53		70.41		31.5		28-Feb-08		18:25:59		74.6		43.5

		18-Jan-08		20:07:10		69.2		32		18-Jan-08		20:06:20		68.61		34		18-Jan-08		20:07:53		71		32.5		28-Feb-08		20:25:59		72.21		44

		18-Jan-08		22:07:10		68		32		18-Jan-08		22:06:20		66.81		34.5		18-Jan-08		22:07:53		69.8		32		28-Feb-08		22:25:59		71.6		44.5

		19-Jan-08		0:07:10		66.81		32.5		19-Jan-08		0:06:20		66.2		34		19-Jan-08		0:07:53		68		32.5		29-Feb-08		0:25:59		69.2		44

		19-Jan-08		2:07:10		66.2		32.5		19-Jan-08		2:06:20		65.6		33		19-Jan-08		2:07:53		66.2		32.5		29-Feb-08		2:25:59		68		43.5

		19-Jan-08		4:07:10		65.01		32.5		19-Jan-08		4:06:20		65.6		32.5		19-Jan-08		4:07:53		65.01		32.5		29-Feb-08		4:25:59		66.81		43

		19-Jan-08		6:07:10		64.4		32.5		19-Jan-08		6:06:20		65.6		32		19-Jan-08		6:07:53		67.4		30		29-Feb-08		6:25:59		67.4		42.5

		19-Jan-08		8:07:10		65.01		32		19-Jan-08		8:06:20		68		29.5		19-Jan-08		8:07:53		69.2		31		29-Feb-08		8:25:59		70.41		40

		19-Jan-08		10:07:10		65.6		33		19-Jan-08		10:06:20		68.61		31		19-Jan-08		10:07:53		71.6		30		29-Feb-08		10:25:59		72.21		40.5

		19-Jan-08		12:07:10		65.6		35.5		19-Jan-08		12:06:20		70.41		33.5		19-Jan-08		12:07:53		71		30.5		29-Feb-08		12:25:59		73.4		42

		19-Jan-08		14:07:10		66.2		35.5		19-Jan-08		14:06:20		70.41		33.5		19-Jan-08		14:07:53		71		34.5		29-Feb-08		14:25:59		74.6		41.5

		19-Jan-08		16:07:10		67.4		35		19-Jan-08		16:06:20		71		32		19-Jan-08		16:07:53		71		34.5		29-Feb-08		16:25:59		74.6		41.5

		19-Jan-08		18:07:10		68		35.5		19-Jan-08		18:06:20		69.8		34		19-Jan-08		18:07:53		70.41		35		29-Feb-08		18:25:59		74.01		43.5

		19-Jan-08		20:07:10		68		34		19-Jan-08		20:06:20		68		34.5		19-Jan-08		20:07:53		69.8		34		29-Feb-08		20:25:59		72.21		42.5

		19-Jan-08		22:07:10		67.4		34.5		19-Jan-08		22:06:20		66.2		36.5		19-Jan-08		22:07:53		68.61		35		29-Feb-08		22:25:59		71		43.5

		20-Jan-08		0:07:10		66.2		34		20-Jan-08		0:06:20		65.6		35		20-Jan-08		0:07:53		67.4		34		1-Mar-08		0:25:59		69.8		43

		20-Jan-08		2:07:10		65.6		34		20-Jan-08		2:06:20		65.6		34		20-Jan-08		2:07:53		65.6		34		1-Mar-08		2:25:59		68.61		43.5

		20-Jan-08		4:07:10		64.4		33		20-Jan-08		4:06:20		65.6		33		20-Jan-08		4:07:53		64.4		33.5		1-Mar-08		4:25:59		68		44

		20-Jan-08		6:07:10		63.8		32.5		20-Jan-08		6:06:20		65.6		31		20-Jan-08		6:07:53		63.21		33.5		1-Mar-08		6:25:59		68		44.5

		20-Jan-08		8:07:10		63.8		31.5		20-Jan-08		8:06:20		67.4		28		20-Jan-08		8:07:53		67.4		29		1-Mar-08		8:25:59		71.6		42

		20-Jan-08		10:07:10		63.8		32		20-Jan-08		10:06:20		68		30		20-Jan-08		10:07:53		66.81		29.5		1-Mar-08		10:25:59		72.8		41.5

		20-Jan-08		12:07:10		64.4		36.5		20-Jan-08		12:06:20		68.61		35		20-Jan-08		12:07:53		67.4		33		1-Mar-08		12:25:59		72.21		43

		20-Jan-08		14:07:10		65.01		37		20-Jan-08		14:06:20		68.61		35		20-Jan-08		14:07:53		67.4		35.5		1-Mar-08		14:25:59		72.8		44

		20-Jan-08		16:07:10		66.2		36.5		20-Jan-08		16:06:20		69.8		33.5		20-Jan-08		16:07:53		68.61		35.5		1-Mar-08		16:25:59		74.01		45

		20-Jan-08		18:07:10		66.81		36.5		20-Jan-08		18:06:20		69.2		34.5		20-Jan-08		18:07:53		69.8		35.5		1-Mar-08		18:25:59		73.4		43.5

		20-Jan-08		20:07:10		66.81		34.5		20-Jan-08		20:06:20		68		33.5		20-Jan-08		20:07:53		69.2		34		1-Mar-08		20:25:59		72.21		43

		20-Jan-08		22:07:10		66.2		35		20-Jan-08		22:06:20		66.2		35.5		20-Jan-08		22:07:53		67.4		34.5		1-Mar-08		22:25:59		71		43

		21-Jan-08		0:07:10		65.01		35		21-Jan-08		0:06:20		65.6		35		21-Jan-08		0:07:53		65.6		34.5		2-Mar-08		0:25:59		69.2		43

		21-Jan-08		2:07:10		64.4		38.5		21-Jan-08		2:06:20		65.6		39		21-Jan-08		2:07:53		65.01		37		2-Mar-08		2:25:59		68.61		44

		21-Jan-08		4:07:10		64.4		38.5		21-Jan-08		4:06:20		65.6		38		21-Jan-08		4:07:53		64.4		38		2-Mar-08		4:25:59		67.4		44.5

		21-Jan-08		6:07:10		63.8		37		21-Jan-08		6:06:20		65.6		36		21-Jan-08		6:07:53		63.8		37.5		2-Mar-08		6:25:59		67.4		44.5

		21-Jan-08		8:07:10		63.8		38		21-Jan-08		8:06:20		67.4		35		21-Jan-08		8:07:53		66.81		34.5		2-Mar-08		8:25:59		67.4		44

		21-Jan-08		10:07:10		63.8		38.5		21-Jan-08		10:06:20		68		35		21-Jan-08		10:07:53		66.81		35.5		2-Mar-08		10:25:59		68		43.5

		21-Jan-08		12:07:10		64.4		40		21-Jan-08		12:06:20		68		36.5		21-Jan-08		12:07:53		67.4		36		2-Mar-08		12:25:59		69.2		42

		21-Jan-08		14:07:10		64.4		35		21-Jan-08		14:06:20		68		31		21-Jan-08		14:07:53		67.4		33.5		2-Mar-08		14:25:59		70.41		40.5

		21-Jan-08		16:07:10		65.01		34.5		21-Jan-08		16:06:20		68		32		21-Jan-08		16:07:53		67.4		34		2-Mar-08		16:25:59		69.8		39

		21-Jan-08		18:07:10		65.6		33.5		21-Jan-08		18:06:20		68		31		21-Jan-08		18:07:53		67.4		33.5		2-Mar-08		18:25:59		69.8		38

		21-Jan-08		20:07:10		65.6		34.5		21-Jan-08		20:06:20		66.2		34		21-Jan-08		20:07:53		66.81		34		2-Mar-08		20:25:59		68.61		39

		21-Jan-08		22:07:10		65.01		34.5		21-Jan-08		22:06:20		65.6		34		21-Jan-08		22:07:53		65.01		34.5		2-Mar-08		22:25:59		67.4		39.5

		22-Jan-08		0:07:10		64.4		34.5		22-Jan-08		0:06:20		65.6		33.5		22-Jan-08		0:07:53		63.8		35		3-Mar-08		0:25:59		66.81		40

		22-Jan-08		2:07:10		63.8		34		22-Jan-08		2:06:20		65.01		32		22-Jan-08		2:07:53		62.6		34		3-Mar-08		2:25:59		65.6		40

		22-Jan-08		4:07:10		63.21		32.5		22-Jan-08		4:06:20		65.01		30.5		22-Jan-08		4:07:53		61.41		33.5		3-Mar-08		4:25:59		65.01		39.5

		22-Jan-08		6:07:10		62.6		31.5		22-Jan-08		6:06:20		65.01		30		22-Jan-08		6:07:53		66.81		29.5		3-Mar-08		6:25:59		64.4		39.5

		22-Jan-08		8:07:10		63.21		32		22-Jan-08		8:06:20		67.4		28.5		22-Jan-08		8:07:53		68		30		3-Mar-08		8:25:59		65.01		38.5

		22-Jan-08		10:07:10		64.4		33.5		22-Jan-08		10:06:20		69.2		30		22-Jan-08		10:07:53		70.41		30.5		3-Mar-08		10:25:59		66.2		38

		22-Jan-08		12:07:10		65.01		36		22-Jan-08		12:06:20		70.41		32.5		22-Jan-08		12:07:53		71.6		31		3-Mar-08		12:25:59		66.81		38

		22-Jan-08		14:07:10		66.2		37.5		22-Jan-08		14:06:20		71		35.5		22-Jan-08		14:07:53		71		36		3-Mar-08		14:25:59		67.4		35.5

		22-Jan-08		16:07:10		66.81		39		22-Jan-08		16:06:20		71		34.5		22-Jan-08		16:07:53		70.41		37		3-Mar-08		16:25:59		68.61		33.5

		22-Jan-08		18:07:10		67.4		37		22-Jan-08		18:06:20		68.61		36		22-Jan-08		18:07:53		69.8		36		3-Mar-08		18:25:59		68.61		31.5

		22-Jan-08		20:07:10		67.4		36.5		22-Jan-08		20:06:20		68		36.5		22-Jan-08		20:07:53		69.8		35		3-Mar-08		20:25:59		68.61		31

		22-Jan-08		22:07:10		66.81		37		22-Jan-08		22:06:20		67.4		36.5		22-Jan-08		22:07:53		67.4		36		3-Mar-08		22:25:59		68		33

		23-Jan-08		0:07:10		65.6		37.5		23-Jan-08		0:06:20		67.4		36.5		23-Jan-08		0:07:53		65.6		37.5		4-Mar-08		0:25:59		66.81		35

		23-Jan-08		2:07:10		65.01		37		23-Jan-08		2:06:20		67.4		35.5		23-Jan-08		2:07:53		65.01		38		4-Mar-08		2:25:59		66.2		37

		23-Jan-08		4:07:10		64.4		37.5		23-Jan-08		4:06:20		66.81		35.5		23-Jan-08		4:07:53		63.8		38.5		4-Mar-08		4:25:59		65.6		37.5

		23-Jan-08		6:07:10		64.4		37		23-Jan-08		6:06:20		66.81		35		23-Jan-08		6:07:53		67.4		35.5		4-Mar-08		6:25:59		66.2		37.5

		23-Jan-08		8:07:10		65.01		36		23-Jan-08		8:06:20		68		33		23-Jan-08		8:07:53		69.2		34		4-Mar-08		8:25:59		69.2		35.5

		23-Jan-08		10:07:10		65.6		36.5		23-Jan-08		10:06:20		69.2		34		23-Jan-08		10:07:53		71		35		4-Mar-08		10:25:59		71.6		36.5

		23-Jan-08		12:07:10		66.2		36		23-Jan-08		12:06:20		69.8		33		23-Jan-08		12:07:53		71		34		4-Mar-08		12:25:59		72.21		36.5

		23-Jan-08		14:07:10		66.81		34.5		23-Jan-08		14:06:20		70.41		32		23-Jan-08		14:07:53		70.41		35		4-Mar-08		14:25:59		73.4		33.5

		23-Jan-08		16:07:10		66.81		33.5		23-Jan-08		16:06:20		69.8		31.5		23-Jan-08		16:07:53		70.41		32		4-Mar-08		16:25:59		74.01		33.5

		23-Jan-08		18:07:10		66.81		33		23-Jan-08		18:06:20		69.2		31		23-Jan-08		18:07:53		69.2		32		4-Mar-08		18:25:59		74.01		33

		23-Jan-08		20:07:10		66.81		32.5		23-Jan-08		20:06:20		68		31		23-Jan-08		20:07:53		68		32.5		4-Mar-08		20:25:59		72.21		32

		23-Jan-08		22:07:10		66.2		32.5		23-Jan-08		22:06:20		67.4		32		23-Jan-08		22:07:53		68		32.5		4-Mar-08		22:25:59		71		33.5

		24-Jan-08		0:07:10		65.6		33.5		24-Jan-08		0:06:20		66.81		32.5		24-Jan-08		0:07:53		66.2		33		5-Mar-08		0:25:59		69.2		34.5

		24-Jan-08		2:07:10		65.01		34		24-Jan-08		2:06:20		67.4		32.5		24-Jan-08		2:07:53		64.4		34.5		5-Mar-08		2:25:59		68		35.5

		24-Jan-08		4:07:10		64.4		35.5		24-Jan-08		4:06:20		67.4		34		24-Jan-08		4:07:53		63.8		36		5-Mar-08		4:25:59		66.81		36

		24-Jan-08		6:07:10		64.4		37		24-Jan-08		6:06:20		66.81		35		24-Jan-08		6:07:53		68		34		5-Mar-08		6:25:59		66.81		36.5

		24-Jan-08		8:07:10		65.01		37		24-Jan-08		8:06:20		68		35		24-Jan-08		8:07:53		69.2		35.5		5-Mar-08		8:25:59		69.8		34

		24-Jan-08		10:07:10		65.6		38		24-Jan-08		10:06:20		71		33.5		24-Jan-08		10:07:53		71		35		5-Mar-08		10:25:59		72.21		36

		24-Jan-08		12:07:10		66.81		39		24-Jan-08		12:06:20		71		36		24-Jan-08		12:07:53		71		37		5-Mar-08		12:25:59		72.8		36.5

		24-Jan-08		14:07:10		68		38		24-Jan-08		14:06:20		71		37		24-Jan-08		14:07:53		71		38.5		5-Mar-08		14:25:59		74.01		36.5

		24-Jan-08		16:07:10		68		36		24-Jan-08		16:06:20		71		34		24-Jan-08		16:07:53		71.6		35		5-Mar-08		16:25:59		74.6		35.5

		24-Jan-08		18:07:10		68.61		34.5		24-Jan-08		18:06:20		68.61		33.5		24-Jan-08		18:07:53		71		34		5-Mar-08		18:25:59		74.6		36.5

		24-Jan-08		20:07:10		68		35.5		24-Jan-08		20:06:20		68		36.5		24-Jan-08		20:07:53		69.8		35		5-Mar-08		20:25:59		72.8		37

		24-Jan-08		22:07:10		67.4		36.5		24-Jan-08		22:06:20		67.4		37		24-Jan-08		22:07:53		68		36		5-Mar-08		22:25:59		71		37

		25-Jan-08		0:07:10		66.2		36.5		25-Jan-08		0:06:20		67.4		36		25-Jan-08		0:07:53		66.2		37		6-Mar-08		0:25:59		69.2		37

		25-Jan-08		2:07:10		65.6		37.5		25-Jan-08		2:06:20		66.81		37		25-Jan-08		2:07:53		65.01		38		6-Mar-08		2:25:59		68		37.5

		25-Jan-08		4:07:10		65.01		39		25-Jan-08		4:06:20		67.4		37.5		25-Jan-08		4:07:53		64.4		39.5		6-Mar-08		4:25:59		66.81		38

		25-Jan-08		6:07:10		64.4		39.5		25-Jan-08		6:06:20		67.4		38		25-Jan-08		6:07:53		66.81		38		6-Mar-08		6:25:59		66.81		37.5

		25-Jan-08		8:07:10		65.01		39		25-Jan-08		8:06:20		68		36.5		25-Jan-08		8:07:53		69.2		36		6-Mar-08		8:25:59		70.41		35.5

		25-Jan-08		10:07:10		65.6		40.5		25-Jan-08		10:06:20		69.8		37		25-Jan-08		10:07:53		71.6		36		6-Mar-08		10:25:59		71.6		36.5

		25-Jan-08		12:07:10		66.81		39.5		25-Jan-08		12:06:20		69.8		37.5		25-Jan-08		12:07:53		72.21		36		6-Mar-08		12:25:59		72.8		35.5

		25-Jan-08		14:07:10		67.4		38		25-Jan-08		14:06:20		69.8		37.5		25-Jan-08		14:07:53		71		37.5		6-Mar-08		14:25:59		74.01		32.5

		25-Jan-08		16:07:10		68.61		37.5		25-Jan-08		16:06:20		70.41		37		25-Jan-08		16:07:53		70.41		38		6-Mar-08		16:25:59		74.6		31

		25-Jan-08		18:07:10		68.61		36		25-Jan-08		18:06:20		68		36.5		25-Jan-08		18:07:53		69.8		36		6-Mar-08		18:25:59		68.61		44.5

		25-Jan-08		20:07:10		68.61		35		25-Jan-08		20:06:20		67.4		37		25-Jan-08		20:07:53		68.61		36		6-Mar-08		20:25:59		68.61		44

		25-Jan-08		22:07:10		68		35.5		25-Jan-08		22:06:20		66.81		37		25-Jan-08		22:07:53		67.4		37.5		6-Mar-08		22:25:59		68.61		42.5

		26-Jan-08		0:07:10		67.4		35.5		26-Jan-08		0:06:20		66.81		36		26-Jan-08		0:07:53		66.81		37.5		7-Mar-08		0:25:59		68.61		44

		26-Jan-08		2:07:10		66.81		36		26-Jan-08		2:06:20		66.81		36.5		26-Jan-08		2:07:53		65.6		37.5		7-Mar-08		2:25:59		68		43

		26-Jan-08		4:07:10		66.2		35		26-Jan-08		4:06:20		66.81		35		26-Jan-08		4:07:53		65.6		37.5		7-Mar-08		4:25:59		69.2		44

		26-Jan-08		6:07:10		65.6		37.5		26-Jan-08		6:06:20		66.81		38		26-Jan-08		6:07:53		68.61		36.5		7-Mar-08		6:25:59		68.61		43.5

		26-Jan-08		8:07:10		66.2		39.5		26-Jan-08		8:06:20		67.4		40		26-Jan-08		8:07:53		69.2		38.5		7-Mar-08		8:25:59		68.61		44.5

		26-Jan-08		10:07:10		67.4		42		26-Jan-08		10:06:20		69.8		42		26-Jan-08		10:07:53		71.6		40.5		7-Mar-08		10:25:59		68.61		44.5

		26-Jan-08		12:07:10		68.61		41		26-Jan-08		12:06:20		69.2		42.5		26-Jan-08		12:07:53		71		43		7-Mar-08		12:25:59		68.61		45

		26-Jan-08		14:07:10		69.8		42		26-Jan-08		14:06:20		71		44		26-Jan-08		14:07:53		71		38.5		7-Mar-08		14:25:59		68.61		45

		26-Jan-08		16:07:10		70.41		43.5		26-Jan-08		16:06:20		70.41		46.5		26-Jan-08		16:07:53		70.41		44.5		7-Mar-08		16:25:59		68.61		44

		26-Jan-08		18:07:10		69.8		42.5		26-Jan-08		18:06:20		68.61		45.5		26-Jan-08		18:07:53		69.2		44		7-Mar-08		18:25:59		68.61		44.5

		26-Jan-08		20:07:10		69.2		44.5		26-Jan-08		20:06:20		68		48		26-Jan-08		20:07:53		68.61		45.5		7-Mar-08		20:25:59		68.61		46.5

		26-Jan-08		22:07:10		68.61		46.5		26-Jan-08		22:06:20		68		49.5		26-Jan-08		22:07:53		68		47.5		7-Mar-08		22:25:59		68.61		45.5

		27-Jan-08		0:07:10		68.61		47.5		27-Jan-08		0:06:20		67.4		51		27-Jan-08		0:07:53		67.4		48		8-Mar-08		0:25:59		68.61		44.5

		27-Jan-08		2:07:10		68		48.5		27-Jan-08		2:06:20		67.4		51.5		27-Jan-08		2:07:53		67.4		48.5		8-Mar-08		2:25:59		68		45

		27-Jan-08		4:07:10		68		49		27-Jan-08		4:06:20		67.4		51		27-Jan-08		4:07:53		67.4		49		8-Mar-08		4:25:59		68		44

		27-Jan-08		6:07:10		67.4		48		27-Jan-08		6:06:20		67.4		49		27-Jan-08		6:07:53		66.81		49		8-Mar-08		6:25:59		68		45

		27-Jan-08		8:07:10		67.4		44.5		27-Jan-08		8:06:20		68		43.5		27-Jan-08		8:07:53		68		45.5		8-Mar-08		8:25:59		68.61		45

		27-Jan-08		10:07:10		67.4		40.5		27-Jan-08		10:06:20		67.4		39.5		27-Jan-08		10:07:53		68		43		8-Mar-08		10:25:59		68.61		45

		27-Jan-08		12:07:10		67.4		39.5		27-Jan-08		12:06:20		67.4		39		27-Jan-08		12:07:53		67.4		42		8-Mar-08		12:25:59		68.61		45

		27-Jan-08		14:07:10		67.4		39		27-Jan-08		14:06:20		68		38.5		27-Jan-08		14:07:53		68		42		8-Mar-08		14:25:59		68.61		45

		27-Jan-08		16:07:10		67.4		39.5		27-Jan-08		16:06:20		68		39		27-Jan-08		16:07:53		68		41		8-Mar-08		16:25:59		68.61		45

		27-Jan-08		18:07:10		68		40		27-Jan-08		18:06:20		68.61		40.5		27-Jan-08		18:07:53		68.61		41.5		8-Mar-08		18:25:59		68.61		44.5

		27-Jan-08		20:07:10		68		39.5		27-Jan-08		20:06:20		67.4		40.5		27-Jan-08		20:07:53		68		42		8-Mar-08		20:25:59		68.61		45.5

		27-Jan-08		22:07:10		67.4		41		27-Jan-08		22:06:20		67.4		42		27-Jan-08		22:07:53		67.4		42.5		8-Mar-08		22:25:59		68.61		45

		28-Jan-08		0:07:10		67.4		43.5		28-Jan-08		0:06:20		67.4		46.5		28-Jan-08		0:07:53		67.4		44		9-Mar-08		0:25:59		68		45

		28-Jan-08		2:07:10		66.81		47.5		28-Jan-08		2:06:20		67.4		49		28-Jan-08		2:07:53		66.81		46.5		9-Mar-08		2:25:59		68		45

		28-Jan-08		4:07:10		66.81		46.5		28-Jan-08		4:06:20		67.4		47		28-Jan-08		4:07:53		66.81		46.5		9-Mar-08		4:25:59		68.61		45

		28-Jan-08		6:07:10		66.81		47.5		28-Jan-08		6:06:20		67.4		48.5		28-Jan-08		6:07:53		66.81		47.5		9-Mar-08		6:25:59		68.61		44.5

		28-Jan-08		8:07:10		66.81		48.5		28-Jan-08		8:06:20		68		48.5		28-Jan-08		8:07:53		67.4		47		9-Mar-08		8:25:59		68.61		45.5

		28-Jan-08		10:07:10		66.81		49.5		28-Jan-08		10:06:20		68		49		28-Jan-08		10:07:53		67.4		47.5		9-Mar-08		10:25:59		68.61		45

		28-Jan-08		12:07:10		66.81		48		28-Jan-08		12:06:20		68		47.5		28-Jan-08		12:07:53		68		47.5		9-Mar-08		12:25:59		68.61		45.5

		28-Jan-08		14:07:10		66.81		45.5		28-Jan-08		14:06:20		68		45		28-Jan-08		14:07:53		68		46		9-Mar-08		14:25:59		68.61		45

		28-Jan-08		16:07:10		67.4		47.5		28-Jan-08		16:06:20		68		49		28-Jan-08		16:07:53		68		47.5		9-Mar-08		16:25:59		68.61		45

		28-Jan-08		18:07:10		68		48.5		28-Jan-08		18:06:20		68		49		28-Jan-08		18:07:53		67.4		48.5		9-Mar-08		18:25:59		68.61		45

		28-Jan-08		20:07:10		68		49		28-Jan-08		20:06:20		67.4		50.5		28-Jan-08		20:07:53		67.4		49		9-Mar-08		20:25:59		68.61		46

		28-Jan-08		22:07:10		67.4		40.5		28-Jan-08		22:06:20		66.81		37.5		28-Jan-08		22:07:53		66.2		41.5		9-Mar-08		22:25:59		68.61		45

		29-Jan-08		0:07:10		66.2		36.5		29-Jan-08		0:06:20		66.2		35		29-Jan-08		0:07:53		63.8		38		10-Mar-08		0:25:59		68		45

		29-Jan-08		2:07:10		65.6		36.5		29-Jan-08		2:06:20		66.81		35.5		29-Jan-08		2:07:53		63.21		39		10-Mar-08		2:25:59		68.61		45

		29-Jan-08		4:07:10		65.6		36.5		29-Jan-08		4:06:20		66.81		35		29-Jan-08		4:07:53		62.6		39.5		10-Mar-08		4:25:59		68.61		45.5

		29-Jan-08		6:07:10		65.6		36		29-Jan-08		6:06:20		66.81		35		29-Jan-08		6:07:53		66.81		36.5		10-Mar-08		6:25:59		68.61		45.5

		29-Jan-08		8:07:10		65.6		36		29-Jan-08		8:06:20		67.4		34.5		29-Jan-08		8:07:53		69.2		35		10-Mar-08		8:25:59		68		45.5

		29-Jan-08		10:07:10		66.2		37.5		29-Jan-08		10:06:20		69.8		34.5		29-Jan-08		10:07:53		70.41		36.5		10-Mar-08		10:25:59		68		45.5

		29-Jan-08		12:07:10		67.4		37.5		29-Jan-08		12:06:20		70.41		35.5		29-Jan-08		12:07:53		71		37		10-Mar-08		12:25:59		68.61		45.5

		29-Jan-08		14:07:10		68.61		35		29-Jan-08		14:06:20		71		31		29-Jan-08		14:07:53		70.41		38		10-Mar-08		14:25:59		68.61		45

		29-Jan-08		16:07:10		69.2		34.5		29-Jan-08		16:06:20		69.8		34		29-Jan-08		16:07:53		70.41		35.5		10-Mar-08		16:25:59		68.61		45.5

		29-Jan-08		18:07:10		69.8		33.5		29-Jan-08		18:06:20		69.2		34		29-Jan-08		18:07:53		69.8		35		10-Mar-08		18:25:59		68.61		45

		29-Jan-08		20:07:10		69.2		32.5		29-Jan-08		20:06:20		67.4		33.5		29-Jan-08		20:07:53		68		35		10-Mar-08		20:25:59		68.61		45

		29-Jan-08		22:07:10		68.61		32.5		29-Jan-08		22:06:20		67.4		33.5		29-Jan-08		22:07:53		66.2		35.5		10-Mar-08		22:25:59		68		45

		30-Jan-08		0:07:10		68		31.5		30-Jan-08		0:06:20		66.81		32.5		30-Jan-08		0:07:53		65.01		35.5		11-Mar-08		0:25:59		68.61		45

		30-Jan-08		2:07:10		67.4		30.5		30-Jan-08		2:06:20		66.81		30.5		30-Jan-08		2:07:53		63.21		34.5		11-Mar-08		2:25:59		68.61		45

		30-Jan-08		4:07:10		66.81		30		30-Jan-08		4:06:20		66.81		30		30-Jan-08		4:07:53		62		34		11-Mar-08		4:25:59		68.61		46

		30-Jan-08		6:07:10		66.81		31		30-Jan-08		6:06:20		66.81		31		30-Jan-08		6:07:53		67.4		31.5		11-Mar-08		6:25:59		68.61		45.5

		30-Jan-08		8:07:10		66.81		31.5		30-Jan-08		8:06:20		67.4		31.5		30-Jan-08		8:07:53		69.2		33		11-Mar-08		8:25:59		68.61		44.5

		30-Jan-08		10:07:10		67.4		33.5		30-Jan-08		10:06:20		69.8		32.5		30-Jan-08		10:07:53		70.41		35		11-Mar-08		10:25:59		68		45

		30-Jan-08		12:07:10		68.61		36		30-Jan-08		12:06:20		71		36		30-Jan-08		12:07:53		71		37.5		11-Mar-08		12:25:59		68.61		46

		30-Jan-08		14:07:10		69.8		39		30-Jan-08		14:06:20		71.6		40.5		30-Jan-08		14:07:53		71		42		11-Mar-08		14:25:59		68		49.5

		30-Jan-08		16:07:10		71.6		40.5		30-Jan-08		16:06:20		71.6		43		30-Jan-08		16:07:53		71		42		11-Mar-08		16:25:59		68.61		46

		30-Jan-08		18:07:10		71		36		30-Jan-08		18:06:20		68.61		36.5		30-Jan-08		18:07:53		69.8		38		11-Mar-08		18:25:59		68		45

		30-Jan-08		20:07:10		70.41		33		30-Jan-08		20:06:20		68		34		30-Jan-08		20:07:53		68.61		36.5		11-Mar-08		20:25:59		68.61		45

		30-Jan-08		22:07:10		69.8		31.5		30-Jan-08		22:06:20		68		32.5		30-Jan-08		22:07:53		67.4		36		11-Mar-08		22:25:59		68.61		45.5

		31-Jan-08		0:07:10		69.2		32		31-Jan-08		0:06:20		68		33.5		31-Jan-08		0:07:53		65.6		36.5		12-Mar-08		0:25:59		68.61		45

		31-Jan-08		2:07:10		68.61		33		31-Jan-08		2:06:20		68		34		31-Jan-08		2:07:53		65.01		37		12-Mar-08		2:25:59		68		45

		31-Jan-08		4:07:10		68.61		33.5		31-Jan-08		4:06:20		68		34.5		31-Jan-08		4:07:53		64.4		38		12-Mar-08		4:25:59		68		46

		31-Jan-08		6:07:10		68		33.5		31-Jan-08		6:06:20		68		34.5		31-Jan-08		6:07:53		66.81		36		12-Mar-08		6:25:59		68		45

		31-Jan-08		8:07:10		69.8		32.5		31-Jan-08		8:06:20		68		34		31-Jan-08		8:07:53		68.61		35.5		12-Mar-08		8:25:59		68.61		46

		31-Jan-08		10:07:10		71.6		33		31-Jan-08		10:06:20		71		34.5		31-Jan-08		10:07:53		71.6		36.5		12-Mar-08		10:25:59		68.61		45.5

		31-Jan-08		12:07:10		71.6		33.5		31-Jan-08		12:06:20		71		33.5		31-Jan-08		12:07:53		70.41		38		12-Mar-08		12:25:59		68		46

		31-Jan-08		14:07:10		71.6		33.5		31-Jan-08		14:06:20		71		36		31-Jan-08		14:07:53		71.6		36		12-Mar-08		14:25:59		68		46.5

		31-Jan-08		16:07:10		71.6		33.5		31-Jan-08		16:06:20		71		35.5		31-Jan-08		16:07:53		69.8		37		12-Mar-08		16:25:59		68.61		48.5

		31-Jan-08		18:07:10		71		34		31-Jan-08		18:06:20		68.61		37		31-Jan-08		18:07:53		71		36.5		12-Mar-08		18:25:59		68.61		47.5

		31-Jan-08		20:07:10		69.2		36		31-Jan-08		20:06:20		68.61		38		31-Jan-08		20:07:53		70.41		37.5		12-Mar-08		20:25:59		68.61		45.5

		31-Jan-08		22:07:10		67.4		37.5		31-Jan-08		22:06:20		68		38		31-Jan-08		22:07:53		69.2		38.5		12-Mar-08		22:25:59		68.61		45.5

		1-Feb-08		0:07:10		66.2		39		1-Feb-08		0:06:20		68		38		1-Feb-08		0:07:53		67.4		39		13-Mar-08		0:25:59		68		46

		1-Feb-08		2:07:10		65.01		40.5		1-Feb-08		2:06:20		68		38		1-Feb-08		2:07:53		66.2		40		13-Mar-08		2:25:59		68		45

		1-Feb-08		4:07:10		64.4		42		1-Feb-08		4:06:20		68		39		1-Feb-08		4:07:53		65.6		41		13-Mar-08		4:25:59		68.61		45

		1-Feb-08		6:07:10		63.8		43		1-Feb-08		6:06:20		68		39		1-Feb-08		6:07:53		66.81		40.5		13-Mar-08		6:25:59		68.61		45

		1-Feb-08		8:07:10		66.2		42		1-Feb-08		8:06:20		68		40.5		1-Feb-08		8:07:53		69.8		40		13-Mar-08		8:25:59		68.61		45.5

		1-Feb-08		10:07:10		68.61		42		1-Feb-08		10:06:20		71		41.5		1-Feb-08		10:07:53		71.6		42		13-Mar-08		10:25:59		68		45.5

		1-Feb-08		12:07:10		69.2		43		1-Feb-08		12:06:20		71		43		1-Feb-08		12:07:53		71		46		13-Mar-08		12:25:59		68.61		45

		1-Feb-08		14:07:10		69.8		45		1-Feb-08		14:06:20		71		44		1-Feb-08		14:07:53		71		40		13-Mar-08		14:25:59		68.61		47

		1-Feb-08		16:07:10		70.41		46.5		1-Feb-08		16:06:20		71		45		1-Feb-08		16:07:53		70.41		48		13-Mar-08		16:25:59		68.61		47

		1-Feb-08		18:07:10		69.2		48.5		1-Feb-08		18:06:20		69.2		50		1-Feb-08		18:07:53		70.41		48		13-Mar-08		18:25:59		68		45.5

		1-Feb-08		20:07:10		68		44.5		1-Feb-08		20:06:20		68.61		43.5		1-Feb-08		20:07:53		70.41		43.5		13-Mar-08		20:25:59		68.61		45

		1-Feb-08		22:07:10		66.81		41.5		1-Feb-08		22:06:20		68		39.5		1-Feb-08		22:07:53		69.2		41		13-Mar-08		22:25:59		68.61		45.5

		2-Feb-08		0:07:10		65.6		40		2-Feb-08		0:06:20		68		37.5		2-Feb-08		0:07:53		66.81		40		14-Mar-08		0:25:59		68.61		47.5

		2-Feb-08		2:07:10		64.4		38		2-Feb-08		2:06:20		68		34		2-Feb-08		2:07:53		64.4		39		14-Mar-08		2:25:59		68		46

		2-Feb-08		4:07:10		63.21		37.5		2-Feb-08		4:06:20		68		33		2-Feb-08		4:07:53		62.6		38		14-Mar-08		4:25:59		68		47

		2-Feb-08		6:07:10		62.6		36.5		2-Feb-08		6:06:20		68		32		2-Feb-08		6:07:53		67.4		33.5		14-Mar-08		6:25:59		68		46.5

		2-Feb-08		8:07:10		63.8		35		2-Feb-08		8:06:20		67.4		31.5		2-Feb-08		8:07:53		68		33.5		14-Mar-08		8:25:59		68.61		47.5

		2-Feb-08		10:07:10		66.2		36		2-Feb-08		10:06:20		71		33		2-Feb-08		10:07:53		70.41		35.5		14-Mar-08		10:25:59		68		48

		2-Feb-08		12:07:10		68.61		38		2-Feb-08		12:06:20		72.8		36		2-Feb-08		12:07:53		71		39.5		14-Mar-08		12:25:59		68.61		45.5

		2-Feb-08		14:07:10		69.2		38		2-Feb-08		14:06:20		71.6		36.5		2-Feb-08		14:07:53		69.8		39.5		14-Mar-08		14:25:59		68.61		45

		2-Feb-08		16:07:10		68.61		38		2-Feb-08		16:06:20		71		36.5		2-Feb-08		16:07:53		69.8		39		14-Mar-08		16:25:59		68.61		45

		2-Feb-08		18:07:10		68		37.5		2-Feb-08		18:06:20		71		35.5		2-Feb-08		18:07:53		71		39		14-Mar-08		18:25:59		68.61		45

		2-Feb-08		20:07:10		67.4		37		2-Feb-08		20:06:20		68.61		35.5		2-Feb-08		20:07:53		69.2		40		14-Mar-08		20:25:59		68.61		45

		2-Feb-08		22:07:10		66.81		36.5		2-Feb-08		22:06:20		68		34		2-Feb-08		22:07:53		67.4		44		14-Mar-08		22:25:59		68.61		45

		3-Feb-08		0:07:10		66.81		35.5		3-Feb-08		0:06:20		68		33		3-Feb-08		0:07:53		66.81		41		15-Mar-08		0:25:59		68.61		45.5

		3-Feb-08		2:07:10		66.2		35		3-Feb-08		2:06:20		68		33		3-Feb-08		2:07:53		65.6		42		15-Mar-08		2:25:59		68.61		46

		3-Feb-08		4:07:10		66.2		34.5		3-Feb-08		4:06:20		68		33		3-Feb-08		4:07:53		65.01		43		15-Mar-08		4:25:59		68.61		45.5

		3-Feb-08		6:07:10		66.2		34.5		3-Feb-08		6:06:20		68		33.5		3-Feb-08		6:07:53		64.4		44		15-Mar-08		6:25:59		68.61		46

		3-Feb-08		8:07:10		66.2		35.5		3-Feb-08		8:06:20		69.8		33		3-Feb-08		8:07:53		67.4		41.5		15-Mar-08		8:25:59		68.61		45.5

		3-Feb-08		10:07:10		66.2		36.5		3-Feb-08		10:06:20		66.81		36.5		3-Feb-08		10:07:53		67.4		42		15-Mar-08		10:25:59		68.61		45

		3-Feb-08		12:07:10		66.81		40		3-Feb-08		12:06:20		65.6		44.5		3-Feb-08		12:07:53		68		47.5		15-Mar-08		12:25:59		68.61		45

		3-Feb-08		14:07:10		66.2		43.5		3-Feb-08		14:06:20		66.2		47.5		3-Feb-08		14:07:53		67.4		49		15-Mar-08		14:25:59		68.61		44.5

		3-Feb-08		16:07:10		66.2		46		3-Feb-08		16:06:20		66.2		49		3-Feb-08		16:07:53		68		49		15-Mar-08		16:25:59		68		44.5

		3-Feb-08		18:07:10		66.2		47.5		3-Feb-08		18:06:20		66.2		50		3-Feb-08		18:07:53		68.61		51		15-Mar-08		18:25:59		68		44.5

		3-Feb-08		20:07:10		66.2		49.5		3-Feb-08		20:06:20		66.81		52		3-Feb-08		20:07:53		67.4		51.5		15-Mar-08		20:25:59		68.61		45

		3-Feb-08		22:07:10		66.2		51.5		3-Feb-08		22:06:20		66.81		53.5		3-Feb-08		22:07:53		68		54		15-Mar-08		22:25:59		68		45

		4-Feb-08		0:07:10		66.2		51.5		4-Feb-08		0:06:20		67.4		52.5		4-Feb-08		0:07:53		68		54		16-Mar-08		0:25:59		68		44.5

		4-Feb-08		2:07:10		66.2		49		4-Feb-08		2:06:20		66.81		48		4-Feb-08		2:07:53		67.4		50.5		16-Mar-08		2:25:59		68.61		44.5

		4-Feb-08		4:07:10		66.2		45		4-Feb-08		4:06:20		65.6		45		4-Feb-08		4:07:53		66.81		47.5		16-Mar-08		4:25:59		68		46

		4-Feb-08		6:07:10		65.6		43		4-Feb-08		6:06:20		65.6		44		4-Feb-08		6:07:53		66.81		47.5		16-Mar-08		6:25:59		68		39

		4-Feb-08		8:07:10		65.6		40.5		4-Feb-08		8:06:20		65.01		41		4-Feb-08		8:07:53		68		45.5		16-Mar-08		8:25:59		68.61		45.5

		4-Feb-08		10:07:10		65.6		41		4-Feb-08		10:06:20		65.6		42.5		4-Feb-08		10:07:53		68.61		45		16-Mar-08		10:25:59		68.61		45.5

		4-Feb-08		12:07:10		65.6		41.5		4-Feb-08		12:06:20		66.2		41		4-Feb-08		12:07:53		68		46		16-Mar-08		12:25:59		68.61		45.5

		4-Feb-08		14:07:10		65.6		40.5		4-Feb-08		14:06:20		66.81		38		4-Feb-08		14:07:53		68		46		16-Mar-08		14:25:59		68.61		35

		4-Feb-08		16:07:10		66.2		39		4-Feb-08		16:06:20		66.81		38		4-Feb-08		16:07:53		68		45		16-Mar-08		16:25:59		68.61		45

		4-Feb-08		18:07:10		66.2		38.5		4-Feb-08		18:06:20		66.81		36.5		4-Feb-08		18:07:53		68		45		16-Mar-08		18:25:59		68.61		45

		4-Feb-08		20:07:10		66.2		37.5		4-Feb-08		20:06:20		65.6		38		4-Feb-08		20:07:53		68		45.5		16-Mar-08		20:25:59		68.61		45

		4-Feb-08		22:07:10		65.6		37.5		4-Feb-08		22:06:20		65.6		38.5		4-Feb-08		22:07:53		67.4		46		16-Mar-08		22:25:59		68		46

		5-Feb-08		0:07:10		65.6		37		5-Feb-08		0:06:20		65.01		38		5-Feb-08		0:07:53		66.81		46.5		17-Mar-08		0:25:59		68.61		44

		5-Feb-08		2:07:10		65.6		36		5-Feb-08		2:06:20		65.6		35.5		5-Feb-08		2:07:53		66.81		46		17-Mar-08		2:25:59		68.61		44

		5-Feb-08		4:07:10		65.6		34.5		5-Feb-08		4:06:20		65.01		35		5-Feb-08		4:07:53		66.2		46		17-Mar-08		4:25:59		68.61		45

		5-Feb-08		6:07:10		65.6		33.5		5-Feb-08		6:06:20		65.01		33		5-Feb-08		6:07:53		66.81		46		17-Mar-08		6:25:59		68		43.5

		5-Feb-08		8:07:10		65.6		33		5-Feb-08		8:06:20		65.01		33.5		5-Feb-08		8:07:53		70.41		39.5		17-Mar-08		8:25:59		68.61		44

		5-Feb-08		10:07:10		65.6		34.5		5-Feb-08		10:06:20		68.61		32.5		5-Feb-08		10:07:53		71		41.5		17-Mar-08		10:25:59		68.61		43

		5-Feb-08		12:07:10		66.2		34.5		5-Feb-08		12:06:20		71		30.5		5-Feb-08		12:07:53		70.41		42.5		17-Mar-08		12:25:59		68		35.5

		5-Feb-08		14:07:10		66.81		32		5-Feb-08		14:06:20		70.41		29.5		5-Feb-08		14:07:53		71		39.5		17-Mar-08		14:25:59		68.61		27.5

		5-Feb-08		16:07:10		67.4		31		5-Feb-08		16:06:20		70.41		28.5		5-Feb-08		16:07:53		71		34.5		17-Mar-08		16:25:59		68.61		26

		5-Feb-08		18:07:10		68		34		5-Feb-08		18:06:20		69.8		29		5-Feb-08		18:07:53		70.41		37.5		17-Mar-08		18:25:59		68		34

		5-Feb-08		20:07:10		67.4		41.5		5-Feb-08		20:06:20		68		32		5-Feb-08		20:07:53		71		36		17-Mar-08		20:25:59		68		44

		5-Feb-08		22:07:10		66.81		35.5		5-Feb-08		22:06:20		67.4		33		5-Feb-08		22:07:53		69.8		39		17-Mar-08		22:25:59		68.61		44

		6-Feb-08		0:07:10		66.81		34.5		6-Feb-08		0:06:20		67.4		33.5		6-Feb-08		0:07:53		68		36.5		18-Mar-08		0:25:59		68.61		37.5

		6-Feb-08		2:07:10		66.81		34		6-Feb-08		2:06:20		67.4		33		6-Feb-08		2:07:53		66.81		36.5		18-Mar-08		2:25:59		68.61		36.5

		6-Feb-08		4:07:10		66.2		34		6-Feb-08		4:06:20		67.4		32.5		6-Feb-08		4:07:53		66.2		37		18-Mar-08		4:25:59		68		44.5

		6-Feb-08		6:07:10		66.2		33		6-Feb-08		6:06:20		68		31.5		6-Feb-08		6:07:53		67.4		36		18-Mar-08		6:25:59		68		42

		6-Feb-08		8:07:10		66.2		32		6-Feb-08		8:06:20		68		30.5		6-Feb-08		8:07:53		68		35		18-Mar-08		8:25:59		68.61		43.5

		6-Feb-08		10:07:10		66.81		34		6-Feb-08		10:06:20		69.8		31.5		6-Feb-08		10:07:53		70.41		36.5		18-Mar-08		10:25:59		68		39.5

		6-Feb-08		12:07:10		67.4		34.5		6-Feb-08		12:06:20		71		31.5		6-Feb-08		12:07:53		69.8		39.5		18-Mar-08		12:25:59		68.61		43.5

		6-Feb-08		14:07:10		67.4		34.5		6-Feb-08		14:06:20		69.2		34.5		6-Feb-08		14:07:53		71		36		18-Mar-08		14:25:59		68		40

		6-Feb-08		16:07:10		68.61		33		6-Feb-08		16:06:20		71		31		6-Feb-08		16:07:53		71		35		18-Mar-08		16:25:59		68.61		46

		6-Feb-08		18:07:10		68		37		6-Feb-08		18:06:20		69.8		33		6-Feb-08		18:07:53		71		38		18-Mar-08		18:25:59		68.61		44.5

		6-Feb-08		20:07:10		66.81		41		6-Feb-08		20:06:20		68		37.5		6-Feb-08		20:07:53		70.41		39		18-Mar-08		20:25:59		68.61		44.5

		6-Feb-08		22:07:10		66.2		44		6-Feb-08		22:06:20		67.4		38		6-Feb-08		22:07:53		69.8		39		18-Mar-08		22:25:59		68.61		44.5

		7-Feb-08		0:07:10		66.2		45		7-Feb-08		0:06:20		68		36		7-Feb-08		0:07:53		68.61		39.5		19-Mar-08		0:25:59		68		41

		7-Feb-08		2:07:10		65.6		46		7-Feb-08		2:06:20		67.4		35.5		7-Feb-08		2:07:53		67.4		40		19-Mar-08		2:25:59		68		45

		7-Feb-08		4:07:10		65.6		46		7-Feb-08		4:06:20		68		34		7-Feb-08		4:07:53		66.81		40		19-Mar-08		4:25:59		68		45

		7-Feb-08		6:07:10		65.6		46.5		7-Feb-08		6:06:20		68		33		7-Feb-08		6:07:53		66.81		39.5		19-Mar-08		6:25:59		68.61		44.5

		7-Feb-08		8:07:10		65.6		47		7-Feb-08		8:06:20		67.4		33		7-Feb-08		8:07:53		69.8		38		19-Mar-08		8:25:59		68.61		44.5

		7-Feb-08		10:07:10		65.6		46.5		7-Feb-08		10:06:20		72.21		33.5		7-Feb-08		10:07:53		71.6		37.5		19-Mar-08		10:25:59		68.61		46.5

		7-Feb-08		12:07:10		66.81		46		7-Feb-08		12:06:20		74.01		36.5		7-Feb-08		12:07:53		69.8		44.5		19-Mar-08		12:25:59		68.61		47.5

		7-Feb-08		14:07:10		67.4		46		7-Feb-08		14:06:20		71.6		34		7-Feb-08		14:07:53		71		47		19-Mar-08		14:25:59		68.61		45

		7-Feb-08		16:07:10		67.4		46		7-Feb-08		16:06:20		69.8		37		7-Feb-08		16:07:53		70.41		43.5		19-Mar-08		16:25:59		68.61		44.5

		7-Feb-08		18:07:10		67.4		46		7-Feb-08		18:06:20		69.2		34		7-Feb-08		18:07:53		70.41		41		19-Mar-08		18:25:59		68.61		47.5

		7-Feb-08		20:07:10		66.2		46.5		7-Feb-08		20:06:20		69.2		34		7-Feb-08		20:07:53		69.8		39		19-Mar-08		20:25:59		68		48

		7-Feb-08		22:07:10		66.2		47		7-Feb-08		22:06:20		66.81		36		7-Feb-08		22:07:53		69.8		38		19-Mar-08		22:25:59		68.61		45

		8-Feb-08		0:07:10		65.6		48		8-Feb-08		0:06:20		65.6		37.5		8-Feb-08		0:07:53		68.61		38.5		20-Mar-08		0:25:59		68.61		45

		8-Feb-08		2:07:10		65.01		48.5		8-Feb-08		2:06:20		65.6		37.5		8-Feb-08		2:07:53		67.4		39		20-Mar-08		2:25:59		68		40

		8-Feb-08		4:07:10		65.01		49		8-Feb-08		4:06:20		65.6		36.5		8-Feb-08		4:07:53		66.81		39.5		20-Mar-08		4:25:59		68		39

		8-Feb-08		6:07:10		65.01		49		8-Feb-08		6:06:20		65.6		36		8-Feb-08		6:07:53		66.81		39		20-Mar-08		6:25:59		68.61		38.5

		8-Feb-08		8:07:10		65.01		48.5		8-Feb-08		8:06:20		68		33.5		8-Feb-08		8:07:53		69.8		37		20-Mar-08		8:25:59		68		44.5

		8-Feb-08		10:07:10		65.01		49		8-Feb-08		10:06:20		70.41		35		8-Feb-08		10:07:53		71.6		38		20-Mar-08		10:25:59		68.61		45

		8-Feb-08		12:07:10		66.2		48		8-Feb-08		12:06:20		70.41		35.5		8-Feb-08		12:07:53		70.41		39		20-Mar-08		12:25:59		68.61		45.5

		8-Feb-08		14:07:10		66.81		48.5		8-Feb-08		14:06:20		71		38.5		8-Feb-08		14:07:53		71.6		46.5		20-Mar-08		14:25:59		68.61		46

		8-Feb-08		16:07:10		68.61		49.5		8-Feb-08		16:06:20		71		39		8-Feb-08		16:07:53		69.8		49		20-Mar-08		16:25:59		68		47

		8-Feb-08		18:07:10		68.61		44.5		8-Feb-08		18:06:20		69.8		41		8-Feb-08		18:07:53		71		47		20-Mar-08		18:25:59		68.61		45

		8-Feb-08		20:07:10		68.61		42.5		8-Feb-08		20:06:20		69.8		40.5		8-Feb-08		20:07:53		69.8		44.5		20-Mar-08		20:25:59		68.61		45

		8-Feb-08		22:07:10		68		45		8-Feb-08		22:06:20		68		44		8-Feb-08		22:07:53		70.41		42.5		20-Mar-08		22:25:59		68.61		44.5

		9-Feb-08		0:07:10		66.81		44		9-Feb-08		0:06:20		66.2		44		9-Feb-08		0:07:53		69.8		41		21-Mar-08		0:25:59		68.61		45

		9-Feb-08		2:07:10		66.2		44		9-Feb-08		2:06:20		66.2		40.5		9-Feb-08		2:07:53		68.61		40		21-Mar-08		2:25:59		68		45.5

		9-Feb-08		4:07:10		66.2		42		9-Feb-08		4:06:20		66.2		37		9-Feb-08		4:07:53		67.4		38.5		21-Mar-08		4:25:59		68		36.5

		9-Feb-08		6:07:10		65.6		40.5		9-Feb-08		6:06:20		66.2		36		9-Feb-08		6:07:53		67.4		37.5		21-Mar-08		6:25:59		68		45.5

		9-Feb-08		8:07:10		65.6		39.5		9-Feb-08		8:06:20		68		32		9-Feb-08		8:07:53		69.2		36		21-Mar-08		8:25:59		68		36

		9-Feb-08		10:07:10		66.2		40		9-Feb-08		10:06:20		71		35		9-Feb-08		10:07:53		71.6		35.5		21-Mar-08		10:25:59		67.4		46.5

		9-Feb-08		12:07:10		67.4		46.5		9-Feb-08		12:06:20		69.2		33.5		9-Feb-08		12:07:53		71		38.5		21-Mar-08		12:25:59		68.61		42

		9-Feb-08		14:07:10		69.8		47.5		9-Feb-08		14:06:20		68.61		33		9-Feb-08		14:07:53		71		34.5		21-Mar-08		14:25:59		68.61		32.5

		9-Feb-08		16:07:10		72.8		42		9-Feb-08		16:06:20		68.61		28.5		9-Feb-08		16:07:53		71		38.5		21-Mar-08		16:25:59		68		32.5

		9-Feb-08		18:07:10		71		48		9-Feb-08		18:06:20		68		29		9-Feb-08		18:07:53		70.41		35.5		21-Mar-08		18:25:59		68		42.5

		9-Feb-08		20:07:10		67.4		48.5		9-Feb-08		20:06:20		68.61		38.5		9-Feb-08		20:07:53		69.8		39.5		21-Mar-08		20:25:59		68.61		37

		9-Feb-08		22:07:10		65.6		51		9-Feb-08		22:06:20		67.4		38.5		9-Feb-08		22:07:53		69.8		38.5		21-Mar-08		22:25:59		68.61		36.5

		10-Feb-08		0:07:10		65.01		49.5		10-Feb-08		0:06:20		66.2		39		10-Feb-08		0:07:53		69.2		37.5		22-Mar-08		0:25:59		68		34.5

		10-Feb-08		2:07:10		65.01		49		10-Feb-08		2:06:20		65.6		38		10-Feb-08		2:07:53		68		37.5		22-Mar-08		2:25:59		68		42.5

		10-Feb-08		4:07:10		65.01		50		10-Feb-08		4:06:20		65.6		36.5		10-Feb-08		4:07:53		66.81		37.5		22-Mar-08		4:25:59		68		38

		10-Feb-08		6:07:10		65.01		51		10-Feb-08		6:06:20		65.6		35.5		10-Feb-08		6:07:53		66.2		38		22-Mar-08		6:25:59		68		35

		10-Feb-08		8:07:10		65.01		50		10-Feb-08		8:06:20		66.2		34		10-Feb-08		8:07:53		66.81		37		22-Mar-08		8:25:59		68		43.5

		10-Feb-08		10:07:10		65.01		49.5		10-Feb-08		10:06:20		67.4		36		10-Feb-08		10:07:53		68		37		22-Mar-08		10:25:59		68		41

		10-Feb-08		12:07:10		66.2		51		10-Feb-08		12:06:20		67.4		40.5		10-Feb-08		12:07:53		69.8		38.5		22-Mar-08		12:25:59		68.61		43.5

		10-Feb-08		14:07:10		68.61		49.5		10-Feb-08		14:06:20		68		41.5		10-Feb-08		14:07:53		70.41		41		22-Mar-08		14:25:59		68		37

		10-Feb-08		16:07:10		69.8		49		10-Feb-08		16:06:20		68		44		10-Feb-08		16:07:53		70.41		45		22-Mar-08		16:25:59		68.61		45

		10-Feb-08		18:07:10		69.8		49.5		10-Feb-08		18:06:20		68		39.5		10-Feb-08		18:07:53		70.41		42		22-Mar-08		18:25:59		68		44.5

		10-Feb-08		20:07:10		67.4		47.5		10-Feb-08		20:06:20		68.61		39.5		10-Feb-08		20:07:53		69.8		46.5		22-Mar-08		20:25:59		68		38.5

		10-Feb-08		22:07:10		66.2		49.5		10-Feb-08		22:06:20		68		39.5		10-Feb-08		22:07:53		70.41		42		22-Mar-08		22:25:59		68		38.5

		11-Feb-08		0:07:10		65.6		49.5		11-Feb-08		0:06:20		66.2		42		11-Feb-08		0:07:53		69.8		41.5		23-Mar-08		0:25:59		68		39

		11-Feb-08		2:07:10		65.01		50		11-Feb-08		2:06:20		66.2		42		11-Feb-08		2:07:53		68.61		42		23-Mar-08		2:25:59		68.61		36.5

		11-Feb-08		4:07:10		65.01		50		11-Feb-08		4:06:20		65.6		40		11-Feb-08		4:07:53		68		41.5		23-Mar-08		4:25:59		68		35.5

		11-Feb-08		6:07:10		65.01		50.5		11-Feb-08		6:06:20		65.6		38		11-Feb-08		6:07:53		67.4		42.5		23-Mar-08		6:25:59		68.61		43.5

		11-Feb-08		8:07:10		65.01		50		11-Feb-08		8:06:20		66.2		36.5		11-Feb-08		8:07:53		68		41.5		23-Mar-08		8:25:59		68		36

		11-Feb-08		10:07:10		65.01		51		11-Feb-08		10:06:20		66.81		39		11-Feb-08		10:07:53		68		42.5		23-Mar-08		10:25:59		68.61		44

		11-Feb-08		12:07:10		66.2		51.5		11-Feb-08		12:06:20		68		41.5		11-Feb-08		12:07:53		69.8		41.5		23-Mar-08		12:25:59		68		40

		11-Feb-08		14:07:10		68		51		11-Feb-08		14:06:20		67.4		43.5		11-Feb-08		14:07:53		69.8		44		23-Mar-08		14:25:59		68.61		44.5

		11-Feb-08		16:07:10		70.41		51		11-Feb-08		16:06:20		68		42		11-Feb-08		16:07:53		70.41		46.5		23-Mar-08		16:25:59		68.61		33

		11-Feb-08		18:07:10		69.8		50.5		11-Feb-08		18:06:20		68		48.5		11-Feb-08		18:07:53		70.41		46		23-Mar-08		18:25:59		68.61		44.5

		11-Feb-08		20:07:10		66.2		52		11-Feb-08		20:06:20		68.61		45.5		11-Feb-08		20:07:53		70.41		46		23-Mar-08		20:25:59		68.61		43.5

		11-Feb-08		22:07:10		65.6		52		11-Feb-08		22:06:20		67.4		44.5		11-Feb-08		22:07:53		70.41		43.5		23-Mar-08		22:25:59		68		45

		12-Feb-08		0:07:10		65.6		51.5		12-Feb-08		0:06:20		66.2		44.5		12-Feb-08		0:07:53		69.2		41.5		24-Mar-08		0:25:59		68		38.5

		12-Feb-08		2:07:10		65.01		50		12-Feb-08		2:06:20		66.2		42		12-Feb-08		2:07:53		68.61		41		24-Mar-08		2:25:59		68.61		39.5

		12-Feb-08		4:07:10		65.01		52		12-Feb-08		4:06:20		65.6		41.5		12-Feb-08		4:07:53		68		41		24-Mar-08		4:25:59		68.61		36

		12-Feb-08		6:07:10		65.01		50		12-Feb-08		6:06:20		65.6		40.5		12-Feb-08		6:07:53		67.4		41		24-Mar-08		6:25:59		68		35.5

		12-Feb-08		8:07:10		65.01		51		12-Feb-08		8:06:20		66.81		37.5		12-Feb-08		8:07:53		69.8		38		24-Mar-08		8:25:59		68.61		33.5

		12-Feb-08		10:07:10		65.6		49.5		12-Feb-08		10:06:20		71		39		12-Feb-08		10:07:53		71		41.5		24-Mar-08		10:25:59		68		37.5

		12-Feb-08		12:07:10		67.4		49.5		12-Feb-08		12:06:20		72.21		42.5		12-Feb-08		12:07:53		70.41		39.5		24-Mar-08		12:25:59		68.61		37.5

		12-Feb-08		14:07:10		70.41		50		12-Feb-08		14:06:20		72.8		41.5		12-Feb-08		14:07:53		71		44		24-Mar-08		14:25:59		68.61		38.5

		12-Feb-08		16:07:10		72.8		49.5		12-Feb-08		16:06:20		71.6		38.5		12-Feb-08		16:07:53		70.41		47.5		24-Mar-08		16:25:59		68		45

		12-Feb-08		18:07:10		71.6		49.5		12-Feb-08		18:06:20		70.41		48.5		12-Feb-08		18:07:53		70.41		50.5		24-Mar-08		18:25:59		68		42.5

		12-Feb-08		20:07:10		67.4		51		12-Feb-08		20:06:20		69.8		43.5		12-Feb-08		20:07:53		69.8		49		24-Mar-08		20:25:59		68		44.5

		12-Feb-08		22:07:10		66.2		52		12-Feb-08		22:06:20		69.2		43.5		12-Feb-08		22:07:53		70.41		45.5		24-Mar-08		22:25:59		68.61		40

		13-Feb-08		0:07:10		66.2		48.5		13-Feb-08		0:06:20		68.61		42.5		13-Feb-08		0:07:53		69.8		42.5		25-Mar-08		0:25:59		68.61		44

		13-Feb-08		2:07:10		65.6		49		13-Feb-08		2:06:20		68.61		40.5		13-Feb-08		2:07:53		69.2		41.5		25-Mar-08		2:25:59		68		38

		13-Feb-08		4:07:10		65.6		48.5		13-Feb-08		4:06:20		68.61		38		13-Feb-08		4:07:53		68.61		40.5		25-Mar-08		4:25:59		68.61		44.5

		13-Feb-08		6:07:10		65.6		50.5		13-Feb-08		6:06:20		68.61		36.5		13-Feb-08		6:07:53		67.4		41		25-Mar-08		6:25:59		68		37.5

		13-Feb-08		8:07:10		65.6		50		13-Feb-08		8:06:20		69.2		36.5		13-Feb-08		8:07:53		69.8		40		25-Mar-08		8:25:59		68		38

		13-Feb-08		10:07:10		66.2		50.5		13-Feb-08		10:06:20		70.41		37.5		13-Feb-08		10:07:53		71.6		42		25-Mar-08		10:25:59		67.4		42.5

		13-Feb-08		12:07:10		67.4		50.5		13-Feb-08		12:06:20		71		43		13-Feb-08		12:07:53		71		47		25-Mar-08		12:25:59		68		44.5

		13-Feb-08		14:07:10		73.4		46		13-Feb-08		14:06:20		71.6		43.5		13-Feb-08		14:07:53		71		52.5		25-Mar-08		14:25:59		68		46

		13-Feb-08		16:07:10		73.4		48.5		13-Feb-08		16:06:20		71.6		40		13-Feb-08		16:07:53		71		50.5		25-Mar-08		16:25:59		68		45.5

		13-Feb-08		18:07:10		71		48		13-Feb-08		18:06:20		70.41		45		13-Feb-08		18:07:53		70.41		47		25-Mar-08		18:25:59		68		44

		13-Feb-08		20:07:10		66.2		53		13-Feb-08		20:06:20		69.8		44		13-Feb-08		20:07:53		70.41		42.5		25-Mar-08		20:25:59		68		42.5

		13-Feb-08		22:07:10		65.6		53		13-Feb-08		22:06:20		69.2		43.5		13-Feb-08		22:07:53		70.41		44		25-Mar-08		22:25:59		68.61		41.5

		14-Feb-08		0:07:10		65.6		50.5		14-Feb-08		0:06:20		68.61		41		14-Feb-08		0:07:53		70.41		42		26-Mar-08		0:25:59		68.61		40.5

		14-Feb-08		2:07:10		65.01		51		14-Feb-08		2:06:20		68.61		39		14-Feb-08		2:07:53		69.2		40		26-Mar-08		2:25:59		68.61		40

		14-Feb-08		4:07:10		65.01		49		14-Feb-08		4:06:20		68.61		39		14-Feb-08		4:07:53		68.61		40.5		26-Mar-08		4:25:59		68.61		39

		14-Feb-08		6:07:10		65.01		51		14-Feb-08		6:06:20		68.61		38.5		14-Feb-08		6:07:53		68		40.5		26-Mar-08		6:25:59		68.61		40

		14-Feb-08		8:07:10		65.6		49.5		14-Feb-08		8:06:20		68.61		37		14-Feb-08		8:07:53		71		40		26-Mar-08		8:25:59		68		41.5

		14-Feb-08		10:07:10		67.4		46.5		14-Feb-08		10:06:20		69.8		30		14-Feb-08		10:07:53		70.41		39		26-Mar-08		10:25:59		68		42.5

		14-Feb-08		12:07:10		68		46.5		14-Feb-08		12:06:20		70.41		30.5		14-Feb-08		12:07:53		71		33		26-Mar-08		12:25:59		68.61		43.5

		14-Feb-08		14:07:10		66.2		46.5		14-Feb-08		14:06:20		72.21		28.5		14-Feb-08		14:07:53		71		38.5		26-Mar-08		14:25:59		68		43

		14-Feb-08		16:07:10		65.6		47		14-Feb-08		16:06:20		72.8		24		14-Feb-08		16:07:53		71		37.5		26-Mar-08		16:25:59		68		42

		14-Feb-08		18:07:10		65.01		49		14-Feb-08		18:06:20		71.6		16.5		14-Feb-08		18:07:53		71		30.5		26-Mar-08		18:25:59		68		40.5

		14-Feb-08		20:07:10		64.4		47		14-Feb-08		20:06:20		71		17		14-Feb-08		20:07:53		70.41		30		26-Mar-08		20:25:59		68.61		38

		14-Feb-08		22:07:10		64.4		49		14-Feb-08		22:06:20		70.41		27.5		14-Feb-08		22:07:53		71		32		26-Mar-08		22:25:59		68		37.5

		15-Feb-08		0:07:10		64.4		49		15-Feb-08		0:06:20		70.41		26		15-Feb-08		0:07:53		70.41		32		27-Mar-08		0:25:59		68		38

		15-Feb-08		2:07:10		64.4		46.5		15-Feb-08		2:06:20		70.41		23.5		15-Feb-08		2:07:53		69.2		31		27-Mar-08		2:25:59		67.4		37.5

		15-Feb-08		4:07:10		64.4		50.5		15-Feb-08		4:06:20		70.41		21		15-Feb-08		4:07:53		68.61		31		27-Mar-08		4:25:59		67.4		36.5

		15-Feb-08		6:07:10		64.4		49		15-Feb-08		6:06:20		70.41		19.5		15-Feb-08		6:07:53		68		30.5		27-Mar-08		6:25:59		67.4		35

		15-Feb-08		8:07:10		64.4		50.5		15-Feb-08		8:06:20		70.41		19.5		15-Feb-08		8:07:53		70.41		31		27-Mar-08		8:25:59		68		35.5

		15-Feb-08		10:07:10		65.01		33.5		15-Feb-08		10:06:20		72.21		19.5		15-Feb-08		10:07:53		71		30.5		27-Mar-08		10:25:59		67.4		37

		15-Feb-08		12:07:10		65.6		48		15-Feb-08		12:06:20		72.8		19		15-Feb-08		12:07:53		71		29.5		27-Mar-08		12:25:59		68		36.5

		15-Feb-08		14:07:10		65.6		49		15-Feb-08		14:06:20		72.8		19.5		15-Feb-08		14:07:53		71		34.5		27-Mar-08		14:25:59		68		39

		15-Feb-08		16:07:10		65.6		48.5		15-Feb-08		16:06:20		73.4		19		15-Feb-08		16:07:53		71		34		27-Mar-08		16:25:59		68		39.5

		15-Feb-08		18:07:10		65.6		49.5		15-Feb-08		18:06:20		71.6		20.5		15-Feb-08		18:07:53		70.41		32		27-Mar-08		18:25:59		68.61		37.5

		15-Feb-08		20:07:10		65.01		43.5		15-Feb-08		20:06:20		71		24.5		15-Feb-08		20:07:53		70.41		31.5		27-Mar-08		20:25:59		68.61		37

		15-Feb-08		22:07:10		65.01		49		15-Feb-08		22:06:20		70.41		26.5		15-Feb-08		22:07:53		69.8		31.5		27-Mar-08		22:25:59		68.61		34.5

		16-Feb-08		0:07:10		65.6		50		16-Feb-08		0:06:20		70.41		26.5		16-Feb-08		0:07:53		69.2		32		28-Mar-08		0:25:59		68		34.5

		16-Feb-08		2:07:10		65.01		50		16-Feb-08		2:06:20		70.41		26.5		16-Feb-08		2:07:53		68.61		33		28-Mar-08		2:25:59		67.4		33

		16-Feb-08		4:07:10		65.01		51		16-Feb-08		4:06:20		70.41		27		16-Feb-08		4:07:53		68		33.5		28-Mar-08		4:25:59		66.81		31.5

		16-Feb-08		6:07:10		65.01		50		16-Feb-08		6:06:20		70.41		26.5		16-Feb-08		6:07:53		66.81		34		28-Mar-08		6:25:59		67.4		31.5

		16-Feb-08		8:07:10		65.01		51		16-Feb-08		8:06:20		70.41		27		16-Feb-08		8:07:53		69.2		33		28-Mar-08		8:25:59		68		30.5

		16-Feb-08		10:07:10		65.6		51		16-Feb-08		10:06:20		71.6		27.5		16-Feb-08		10:07:53		71.6		33.5		28-Mar-08		10:25:59		68		29

		16-Feb-08		12:07:10		65.01		50		16-Feb-08		12:06:20		73.4		28		16-Feb-08		12:07:53		70.41		39		28-Mar-08		12:25:59		68		26

		16-Feb-08		14:07:10		65.6		50		16-Feb-08		14:06:20		73.4		27		16-Feb-08		14:07:53		71		33		28-Mar-08		14:25:59		68.61		25.5

		16-Feb-08		16:07:10		65.6		51.5		16-Feb-08		16:06:20		73.4		37.5		16-Feb-08		16:07:53		71.6		36.5		28-Mar-08		16:25:59		68		23.5

		16-Feb-08		18:07:10		65.01		51		16-Feb-08		18:06:20		67.4		41		16-Feb-08		18:07:53		70.41		40		28-Mar-08		18:25:59		68.61		23.5

		16-Feb-08		20:07:10		65.01		50.5		16-Feb-08		20:06:20		66.2		43		16-Feb-08		20:07:53		71		39.5		28-Mar-08		20:25:59		68		26.5

		16-Feb-08		22:07:10		65.01		52		16-Feb-08		22:06:20		66.81		41		16-Feb-08		22:07:53		70.41		39		28-Mar-08		22:25:59		68		32.5

		17-Feb-08		0:07:10		65.01		52		17-Feb-08		0:06:20		66.2		40		17-Feb-08		0:07:53		69.8		38		29-Mar-08		0:25:59		67.4		33.5

		17-Feb-08		2:07:10		65.01		52.5		17-Feb-08		2:06:20		66.2		40.5		17-Feb-08		2:07:53		69.2		39.5		29-Mar-08		2:25:59		67.4		34

		17-Feb-08		4:07:10		65.01		53		17-Feb-08		4:06:20		66.2		41.5		17-Feb-08		4:07:53		68.61		39.5		29-Mar-08		4:25:59		66.81		34

		17-Feb-08		6:07:10		65.01		53		17-Feb-08		6:06:20		66.2		41		17-Feb-08		6:07:53		68.61		40		29-Mar-08		6:25:59		67.4		33.5

		17-Feb-08		8:07:10		65.01		52		17-Feb-08		8:06:20		65.6		40		17-Feb-08		8:07:53		70.41		39		29-Mar-08		8:25:59		68		34

		17-Feb-08		10:07:10		65.01		52		17-Feb-08		10:06:20		65.6		40.5		17-Feb-08		10:07:53		71		37.5		29-Mar-08		10:25:59		67.4		30.5

		17-Feb-08		12:07:10		65.01		52.5		17-Feb-08		12:06:20		66.81		40.5		17-Feb-08		12:07:53		71		38.5		29-Mar-08		12:25:59		68		37

		17-Feb-08		14:07:10		65.01		52		17-Feb-08		14:06:20		67.4		40.5		17-Feb-08		14:07:53		70.41		41.5		29-Mar-08		14:25:59		68		39.5

		17-Feb-08		16:07:10		65.01		53		17-Feb-08		16:06:20		68		38		17-Feb-08		16:07:53		71		43.5		29-Mar-08		16:25:59		68		42

		17-Feb-08		18:07:10		65.01		52.5		17-Feb-08		18:06:20		66.81		42.5		17-Feb-08		18:07:53		70.41		41.5		29-Mar-08		18:25:59		68		42.5

		17-Feb-08		20:07:10		65.01		52.5		17-Feb-08		20:06:20		66.81		42.5		17-Feb-08		20:07:53		69.8		40.5		29-Mar-08		20:25:59		68		43

		17-Feb-08		22:07:10		65.01		53		17-Feb-08		22:06:20		66.81		40.5		17-Feb-08		22:07:53		69.8		39		29-Mar-08		22:25:59		68		43.5

		18-Feb-08		0:07:10		65.01		52		18-Feb-08		0:06:20		66.2		39.5		18-Feb-08		0:07:53		69.2		38.5		30-Mar-08		0:25:59		68		43.5

		18-Feb-08		2:07:10		65.01		52.5		18-Feb-08		2:06:20		66.2		42.5		18-Feb-08		2:07:53		68.61		40		30-Mar-08		2:25:59		68.61		42.5

		18-Feb-08		4:07:10		65.01		52		18-Feb-08		4:06:20		65.6		41.5		18-Feb-08		4:07:53		68		40.5		30-Mar-08		4:25:59		68.61		41.5

		18-Feb-08		6:07:10		65.01		51.5		18-Feb-08		6:06:20		65.6		41.5		18-Feb-08		6:07:53		68		40.5		30-Mar-08		6:25:59		68.61		40

		18-Feb-08		8:07:10		65.01		52		18-Feb-08		8:06:20		65.6		40		18-Feb-08		8:07:53		67.4		40.5		30-Mar-08		8:25:59		68.61		39

		18-Feb-08		10:07:10		65.01		51.5		18-Feb-08		10:06:20		65.6		41		18-Feb-08		10:07:53		67.4		40.5		30-Mar-08		10:25:59		68.61		39

		18-Feb-08		12:07:10		65.01		52		18-Feb-08		12:06:20		66.2		41.5		18-Feb-08		12:07:53		67.4		41		30-Mar-08		12:25:59		68.61		40

		18-Feb-08		14:07:10		65.01		52.5		18-Feb-08		14:06:20		67.4		42		18-Feb-08		14:07:53		68.61		41.5		30-Mar-08		14:25:59		68.61		40.5

		18-Feb-08		16:07:10		65.01		53.5		18-Feb-08		16:06:20		66.81		45.5		18-Feb-08		16:07:53		69.8		42		30-Mar-08		16:25:59		68.61		40

		18-Feb-08		18:07:10		65.01		54		18-Feb-08		18:06:20		66.2		45		18-Feb-08		18:07:53		69.8		42.5		30-Mar-08		18:25:59		68.61		38.5

		18-Feb-08		20:07:10		65.01		52.5		18-Feb-08		20:06:20		66.81		41.5		18-Feb-08		20:07:53		69.2		41		30-Mar-08		20:25:59		68.61		37

		18-Feb-08		22:07:10		65.01		53		18-Feb-08		22:06:20		66.2		42.5		18-Feb-08		22:07:53		68.61		40.5		30-Mar-08		22:25:59		68.61		32.5

		19-Feb-08		0:07:10		65.01		51		19-Feb-08		0:06:20		66.2		41.5		19-Feb-08		0:07:53		68.61		41		31-Mar-08		0:25:59		68.61		32

		19-Feb-08		2:07:10		65.01		52.5		19-Feb-08		2:06:20		66.2		42.5		19-Feb-08		2:07:53		68		41.5		31-Mar-08		2:25:59		67.4		33

		19-Feb-08		4:07:10		65.01		51		19-Feb-08		4:06:20		66.2		43		19-Feb-08		4:07:53		68		41.5		31-Mar-08		4:25:59		66.81		33.5

		19-Feb-08		6:07:10		65.01		53		19-Feb-08		6:06:20		66.2		43		19-Feb-08		6:07:53		68		42		31-Mar-08		6:25:59		67.4		32.5

		19-Feb-08		8:07:10		65.01		52		19-Feb-08		8:06:20		66.81		42.5		19-Feb-08		8:07:53		68		42.5		31-Mar-08		8:25:59		68		32

		19-Feb-08		10:07:10		65.01		52.5		19-Feb-08		10:06:20		66.2		43.5		19-Feb-08		10:07:53		68.61		42.5		31-Mar-08		10:25:59		68.61		28.5

		19-Feb-08		12:07:10		65.01		52.5		19-Feb-08		12:06:20		66.2		43.5		19-Feb-08		12:07:53		69.2		42.5		31-Mar-08		12:25:59		67.4		25.5

		19-Feb-08		14:07:10		65.01		52		19-Feb-08		14:06:20		66.81		43		19-Feb-08		14:07:53		69.8		42		31-Mar-08		14:25:59		68		24

		19-Feb-08		16:07:10		65.01		52.5		19-Feb-08		16:06:20		66.2		44.5		19-Feb-08		16:07:53		69.8		42.5		31-Mar-08		16:25:59		68.61		24.5

		19-Feb-08		18:07:10		65.01		51.5		19-Feb-08		18:06:20		66.81		43		19-Feb-08		18:07:53		69.8		42		31-Mar-08		18:25:59		68		27.5

		19-Feb-08		20:07:10		65.01		52		19-Feb-08		20:06:20		66.2		43		19-Feb-08		20:07:53		69.8		41.5		31-Mar-08		20:25:59		68		27

		19-Feb-08		22:07:10		65.01		52		19-Feb-08		22:06:20		66.2		42		19-Feb-08		22:07:53		69.8		40.5		31-Mar-08		22:25:59		68		27.5

		20-Feb-08		0:07:10		65.01		52.5		20-Feb-08		0:06:20		66.81		39.5		20-Feb-08		0:07:53		69.8		40		1-Apr-08		0:25:59		67.4		29

		20-Feb-08		2:07:10		65.01		52		20-Feb-08		2:06:20		66.81		40.5		20-Feb-08		2:07:53		69.2		40		1-Apr-08		2:25:59		67.4		29

		20-Feb-08		4:07:10		65.01		52		20-Feb-08		4:06:20		66.81		40.5		20-Feb-08		4:07:53		69.2		40		1-Apr-08		4:25:59		68		28

		20-Feb-08		6:07:10		65.01		52.5		20-Feb-08		6:06:20		66.81		41		20-Feb-08		6:07:53		69.2		40.5		1-Apr-08		6:25:59		68.61		28.5

		20-Feb-08		8:07:10		65.6		51.5		20-Feb-08		8:06:20		67.4		41		20-Feb-08		8:07:53		71		41		1-Apr-08		8:25:59		68		30

		20-Feb-08		10:07:10		65.6		51.5		20-Feb-08		10:06:20		66.81		42		20-Feb-08		10:07:53		71		39.5		1-Apr-08		10:25:59		67.4		31

		20-Feb-08		12:07:10		66.2		51		20-Feb-08		12:06:20		66.81		48.5		20-Feb-08		12:07:53		71		42.5		1-Apr-08		12:25:59		68		25

		20-Feb-08		14:07:10		65.6		52.5		20-Feb-08		14:06:20		66.81		51.5		20-Feb-08		14:07:53		71		39		1-Apr-08		14:25:59		68		29.5

		20-Feb-08		16:07:10		66.81		52.5		20-Feb-08		16:06:20		67.4		48.5		20-Feb-08		16:07:53		70.41		43.5		1-Apr-08		16:25:59		68		31

		20-Feb-08		18:07:10		66.2		52		20-Feb-08		18:06:20		67.4		51.5		20-Feb-08		18:07:53		70.41		48		1-Apr-08		18:25:59		68		29.5

		20-Feb-08		20:07:10		66.2		51		20-Feb-08		20:06:20		66.2		55		20-Feb-08		20:07:53		70.41		47		1-Apr-08		20:25:59		67.4		30.5

		20-Feb-08		22:07:10		66.2		52.5		20-Feb-08		22:06:20		67.4		51.5		20-Feb-08		22:07:53		71		45.5		1-Apr-08		22:25:59		68		29.5

		21-Feb-08		0:07:10		66.2		52.5		21-Feb-08		0:06:20		67.4		50.5		21-Feb-08		0:07:53		70.41		45.5		2-Apr-08		0:25:59		68		32.5

		21-Feb-08		2:07:10		65.6		52.5		21-Feb-08		2:06:20		66.81		47		21-Feb-08		2:07:53		69.8		44		2-Apr-08		2:25:59		68		33.5

		21-Feb-08		4:07:10		65.6		52		21-Feb-08		4:06:20		66.81		47.5		21-Feb-08		4:07:53		69.2		44		2-Apr-08		4:25:59		68		33

		21-Feb-08		6:07:10		65.6		52.5		21-Feb-08		6:06:20		66.81		47		21-Feb-08		6:07:53		68.61		44.5		2-Apr-08		6:25:59		68		31

		21-Feb-08		8:07:10		66.2		52		21-Feb-08		8:06:20		67.4		47		21-Feb-08		8:07:53		71		41.5		2-Apr-08		8:25:59		68		33.5

		21-Feb-08		10:07:10		66.2		52		21-Feb-08		10:06:20		67.4		48.5		21-Feb-08		10:07:53		72.21		44.5		2-Apr-08		10:25:59		68		33

		21-Feb-08		12:07:10		65.6		51.5		21-Feb-08		12:06:20		66.81		49.5		21-Feb-08		12:07:53		70.41		48		2-Apr-08		12:25:59		68.61		33

		21-Feb-08		14:07:10		65.6		51		21-Feb-08		14:06:20		68		41		21-Feb-08		14:07:53		71.6		48.5		2-Apr-08		14:25:59		68		36.5

		21-Feb-08		16:07:10		66.81		50.5		21-Feb-08		16:06:20		68		40.5		21-Feb-08		16:07:53		71		47.5		2-Apr-08		16:25:59		68		34

		21-Feb-08		18:07:10		66.2		52		21-Feb-08		18:06:20		67.4		42.5		21-Feb-08		18:07:53		70.41		45.5		2-Apr-08		18:25:59		68		34

		21-Feb-08		20:07:10		66.2		52.5		21-Feb-08		20:06:20		66.81		44.5		21-Feb-08		20:07:53		70.41		43.5		2-Apr-08		20:25:59		68		37

		21-Feb-08		22:07:10		66.2		51.5		21-Feb-08		22:06:20		67.4		45		21-Feb-08		22:07:53		71		42.5		2-Apr-08		22:25:59		68.61		36.5

		22-Feb-08		0:07:10		66.2		49.5		22-Feb-08		0:06:20		66.81		43		22-Feb-08		0:07:53		70.41		41.5		3-Apr-08		0:25:59		68.61		36.5

		22-Feb-08		2:07:10		65.6		51.5		22-Feb-08		2:06:20		66.81		43.5		22-Feb-08		2:07:53		69.8		41		3-Apr-08		2:25:59		68		36

		22-Feb-08		4:07:10		65.6		52		22-Feb-08		4:06:20		66.81		43.5		22-Feb-08		4:07:53		69.2		41.5		3-Apr-08		4:25:59		67.4		35

		22-Feb-08		6:07:10		66.2		51.5		22-Feb-08		6:06:20		66.81		44		22-Feb-08		6:07:53		69.2		42		3-Apr-08		6:25:59		69.2		34

		22-Feb-08		8:07:10		66.2		51		22-Feb-08		8:06:20		66.2		46		22-Feb-08		8:07:53		71		44		3-Apr-08		8:25:59		67.4		36.5

		22-Feb-08		10:07:10		66.81		48		22-Feb-08		10:06:20		66.2		48		22-Feb-08		10:07:53		71.6		43		3-Apr-08		10:25:59		68		36.5

		22-Feb-08		12:07:10		66.81		48.5		22-Feb-08		12:06:20		67.4		43.5		22-Feb-08		12:07:53		71		39		3-Apr-08		12:25:59		68		37.5

		22-Feb-08		14:07:10		66.81		49		22-Feb-08		14:06:20		68		44.5		22-Feb-08		14:07:53		71		44		3-Apr-08		14:25:59		68		39

		22-Feb-08		16:07:10		66.2		50		22-Feb-08		16:06:20		68		48		22-Feb-08		16:07:53		71		40		3-Apr-08		16:25:59		68		37.5

		22-Feb-08		18:07:10		66.2		51.5		22-Feb-08		18:06:20		66.81		48		22-Feb-08		18:07:53		71		46.5		3-Apr-08		18:25:59		68.61		35

		22-Feb-08		20:07:10		66.2		49		22-Feb-08		20:06:20		67.4		49.5		22-Feb-08		20:07:53		70.41		42		3-Apr-08		20:25:59		68		35.5

		22-Feb-08		22:07:10		66.2		51		22-Feb-08		22:06:20		66.81		51.5		22-Feb-08		22:07:53		70.41		45.5		3-Apr-08		22:25:59		68.61		34

		23-Feb-08		0:07:10		65.6		50.5		23-Feb-08		0:06:20		66.81		49.5		23-Feb-08		0:07:53		70.41		44.5		4-Apr-08		0:25:59		68		34

		23-Feb-08		2:07:10		65.6		49		23-Feb-08		2:06:20		67.4		48		23-Feb-08		2:07:53		69.8		43.5		4-Apr-08		2:25:59		68		33.5

		23-Feb-08		4:07:10		65.6		49		23-Feb-08		4:06:20		67.4		46		23-Feb-08		4:07:53		69.8		43		4-Apr-08		4:25:59		68		35

		23-Feb-08		6:07:10		65.6		46.5		23-Feb-08		6:06:20		66.81		47		23-Feb-08		6:07:53		69.2		43		4-Apr-08		6:25:59		68.61		36.5

		23-Feb-08		8:07:10		66.2		48.5		23-Feb-08		8:06:20		66.2		48		23-Feb-08		8:07:53		71		40.5		4-Apr-08		8:25:59		68		38

		23-Feb-08		10:07:10		66.2		49.5		23-Feb-08		10:06:20		67.4		48		23-Feb-08		10:07:53		71.6		48.5		4-Apr-08		10:25:59		67.4		39

		23-Feb-08		12:07:10		66.81		48.5		23-Feb-08		12:06:20		67.4		47.5		23-Feb-08		12:07:53		71		49.5		4-Apr-08		12:25:59		73.4		36.5

		23-Feb-08		14:07:10		66.81		48.5		23-Feb-08		14:06:20		67.4		47		23-Feb-08		14:07:53		71		45.5		4-Apr-08		14:25:59		74.01		36

		23-Feb-08		16:07:10		66.81		44		23-Feb-08		16:06:20		68		41.5		23-Feb-08		16:07:53		71.6		45.5		4-Apr-08		16:25:59		74.6		37.5

		23-Feb-08		18:07:10		66.2		48		23-Feb-08		18:06:20		67.4		39.5		23-Feb-08		18:07:53		71		42.5		4-Apr-08		18:25:59		74.01		36.5

		23-Feb-08		20:07:10		66.2		48		23-Feb-08		20:06:20		66.81		38		23-Feb-08		20:07:53		70.41		40		4-Apr-08		20:25:59		73.4		36.5

		23-Feb-08		22:07:10		66.2		48.5		23-Feb-08		22:06:20		66.2		38.5		23-Feb-08		22:07:53		69.8		40.5		4-Apr-08		22:25:59		71.6		37

		24-Feb-08		0:07:10		65.6		49.5		24-Feb-08		0:06:20		65.01		38		24-Feb-08		0:07:53		69.2		38		5-Apr-08		0:25:59		70.41		36.5

		24-Feb-08		2:07:10		65.6		41.5		24-Feb-08		2:06:20		64.4		38		24-Feb-08		2:07:53		68		38		5-Apr-08		2:25:59		69.2		36.5

		24-Feb-08		4:07:10		65.6		48		24-Feb-08		4:06:20		63.8		37		24-Feb-08		4:07:53		66.81		37.5		5-Apr-08		4:25:59		68.61		38

		24-Feb-08		6:07:10		65.6		48		24-Feb-08		6:06:20		63.8		38		24-Feb-08		6:07:53		66.2		38.5		5-Apr-08		6:25:59		69.2		37.5

		24-Feb-08		8:07:10		66.2		48		24-Feb-08		8:06:20		64.4		38.5		24-Feb-08		8:07:53		68		38		5-Apr-08		8:25:59		70.41		38.5

		24-Feb-08		10:07:10		66.81		43		24-Feb-08		10:06:20		65.01		42		24-Feb-08		10:07:53		67.4		39.5		5-Apr-08		10:25:59		71.6		38.5

		24-Feb-08		12:07:10		66.81		47		24-Feb-08		12:06:20		66.2		42		24-Feb-08		12:07:53		68		40		5-Apr-08		12:25:59		72.8		38.5

		24-Feb-08		14:07:10		66.2		48		24-Feb-08		14:06:20		66.2		42.5		24-Feb-08		14:07:53		68		41		5-Apr-08		14:25:59		73.4		38.5

		24-Feb-08		16:07:10		66.2		48		24-Feb-08		16:06:20		65.6		44.5		24-Feb-08		16:07:53		68		42		5-Apr-08		16:25:59		74.01		38.5

		24-Feb-08		18:07:10		66.2		49		24-Feb-08		18:06:20		65.01		41.5		24-Feb-08		18:07:53		67.4		41.5		5-Apr-08		18:25:59		73.4		37.5

		24-Feb-08		20:07:10		65.6		45		24-Feb-08		20:06:20		65.6		44		24-Feb-08		20:07:53		66.81		42.5		5-Apr-08		20:25:59		72.8		37

		24-Feb-08		22:07:10		66.2		49		24-Feb-08		22:06:20		65.6		48		24-Feb-08		22:07:53		66.81		44.5		5-Apr-08		22:25:59		71.6		36.5

		25-Feb-08		0:07:10		66.2		49		25-Feb-08		0:06:20		66.2		47.5		25-Feb-08		0:07:53		67.4		45		6-Apr-08		0:25:59		69.8		36

		25-Feb-08		2:07:10		66.2		49		25-Feb-08		2:06:20		66.81		48		25-Feb-08		2:07:53		67.4		45.5		6-Apr-08		2:25:59		68		36.5

		25-Feb-08		4:07:10		66.2		49.5		25-Feb-08		4:06:20		66.81		49		25-Feb-08		4:07:53		67.4		46		6-Apr-08		4:25:59		67.4		37

		25-Feb-08		6:07:10		66.2		48		25-Feb-08		6:06:20		66.81		50		25-Feb-08		6:07:53		67.4		47		6-Apr-08		6:25:59		66.81		36.5

		25-Feb-08		8:07:10		66.2		49.5		25-Feb-08		8:06:20		66.81		51		25-Feb-08		8:07:53		67.4		48		6-Apr-08		8:25:59		66.81		36.5

		25-Feb-08		10:07:10		66.2		51.5		25-Feb-08		10:06:20		67.4		51.5		25-Feb-08		10:07:53		67.4		49.5		6-Apr-08		10:25:59		68.61		38

		25-Feb-08		12:07:10		66.2		52		25-Feb-08		12:06:20		66.81		52.5		25-Feb-08		12:07:53		68		49		6-Apr-08		12:25:59		70.41		38.5

		25-Feb-08		14:07:10		66.2		53		25-Feb-08		14:06:20		67.4		52		25-Feb-08		14:07:53		68		49.5		6-Apr-08		14:25:59		71.6		37.5

		25-Feb-08		16:07:10		66.2		49.5		25-Feb-08		16:06:20		66.2		52.5		25-Feb-08		16:07:53		68		49		6-Apr-08		16:25:59		72.21		37

		25-Feb-08		18:07:10		66.2		50.5		25-Feb-08		18:06:20		67.4		49.5		25-Feb-08		18:07:53		68		48		6-Apr-08		18:25:59		72.8		36.5

		25-Feb-08		20:07:10		66.2		50		25-Feb-08		20:06:20		67.4		47.5		25-Feb-08		20:07:53		68		47.5		6-Apr-08		20:25:59		72.21		36.5

		25-Feb-08		22:07:10		66.2		50		25-Feb-08		22:06:20		66.81		48		25-Feb-08		22:07:53		68		47		6-Apr-08		22:25:59		71		37

		26-Feb-08		0:07:10		66.2		49.5		26-Feb-08		0:06:20		66.81		49.5		26-Feb-08		0:07:53		68		47		7-Apr-08		0:25:59		69.2		37

		26-Feb-08		2:07:10		65.6		50.5		26-Feb-08		2:06:20		66.2		49		26-Feb-08		2:07:53		67.4		47		7-Apr-08		2:25:59		68.61		37.5

		26-Feb-08		4:07:10		65.6		49		26-Feb-08		4:06:20		65.6		47		26-Feb-08		4:07:53		67.4		45.5		7-Apr-08		4:25:59		67.4		37.5

		26-Feb-08		6:07:10		65.6		49		26-Feb-08		6:06:20		65.6		48		26-Feb-08		6:07:53		66.81		45.5		7-Apr-08		6:25:59		66.81		38

		26-Feb-08		8:07:10		66.2		49		26-Feb-08		8:06:20		66.2		46.5		26-Feb-08		8:07:53		69.8		44		7-Apr-08		8:25:59		66.81		38.5

		26-Feb-08		10:07:10		66.81		49		26-Feb-08		10:06:20		66.81		48.5		26-Feb-08		10:07:53		71.6		42		7-Apr-08		10:25:59		68		39.5

		26-Feb-08		12:07:10		66.81		49.5		26-Feb-08		12:06:20		67.4		46.5		26-Feb-08		12:07:53		70.41		49.5		7-Apr-08		12:25:59		68.61		40

		26-Feb-08		14:07:10		66.81		48		26-Feb-08		14:06:20		67.4		45.5		26-Feb-08		14:07:53		71.6		51		7-Apr-08		14:25:59		69.8		39

		26-Feb-08		16:07:10		66.81		47.5		26-Feb-08		16:06:20		67.4		44.5		26-Feb-08		16:07:53		71		50.5		7-Apr-08		16:25:59		70.41		37.5

		26-Feb-08		18:07:10		66.2		49		26-Feb-08		18:06:20		67.4		47		26-Feb-08		18:07:53		71		50.5		7-Apr-08		18:25:59		71		36

		26-Feb-08		20:07:10		66.2		48.5		26-Feb-08		20:06:20		66.2		48.5		26-Feb-08		20:07:53		70.41		46		7-Apr-08		20:25:59		69.8		35

		26-Feb-08		22:07:10		65.6		50		26-Feb-08		22:06:20		66.81		46		26-Feb-08		22:07:53		70.41		44.5		7-Apr-08		22:25:59		68.61		35

		27-Feb-08		0:07:10		65.6		47.5		27-Feb-08		0:06:20		66.2		45		27-Feb-08		0:07:53		69.8		41.5		8-Apr-08		0:25:59		68		35.5

		27-Feb-08		2:07:10		65.6		49		27-Feb-08		2:06:20		65.01		43.5		27-Feb-08		2:07:53		68.61		41		8-Apr-08		2:25:59		66.81		36.5

		27-Feb-08		4:07:10		66.2		49		27-Feb-08		4:06:20		65.01		43.5		27-Feb-08		4:07:53		68		41		8-Apr-08		4:25:59		66.2		37

		27-Feb-08		6:07:10		66.2		48		27-Feb-08		6:06:20		65.01		44		27-Feb-08		6:07:53		67.4		41.5		8-Apr-08		6:25:59		67.4		36

		27-Feb-08		8:07:10		66.2		47.5		27-Feb-08		8:06:20		65.6		41		27-Feb-08		8:07:53		69.8		40		8-Apr-08		8:25:59		68.61		35.5

		27-Feb-08		10:07:10		66.2		47		27-Feb-08		10:06:20		66.81		44.5		27-Feb-08		10:07:53		71.6		38		8-Apr-08		10:25:59		71.6		36

		27-Feb-08		12:07:10		66.81		48.5		27-Feb-08		12:06:20		68		44.5		27-Feb-08		12:07:53		71		40.5		8-Apr-08		12:25:59		72.8		35

		27-Feb-08		14:07:10		66.81		46.5		27-Feb-08		14:06:20		67.4		44		27-Feb-08		14:07:53		70.41		39.5		8-Apr-08		14:25:59		74.01		33.5

		27-Feb-08		16:07:10		66.81		47		27-Feb-08		16:06:20		68.61		42		27-Feb-08		16:07:53		70.41		49.5		8-Apr-08		16:25:59		74.01		35.5

		27-Feb-08		18:07:10		66.2		50		27-Feb-08		18:06:20		68		48.5		27-Feb-08		18:07:53		70.41		42.5		8-Apr-08		18:25:59		73.4		34.5

		27-Feb-08		20:07:10		66.2		49.5		27-Feb-08		20:06:20		66.81		51.5		27-Feb-08		20:07:53		70.41		42.5		8-Apr-08		20:25:59		72.8		34.5

		27-Feb-08		22:07:10		66.2		49.5		27-Feb-08		22:06:20		66.81		50		27-Feb-08		22:07:53		71		46		8-Apr-08		22:25:59		72.21		34

		28-Feb-08		0:07:10		66.2		48.5		28-Feb-08		0:06:20		66.2		49.5		28-Feb-08		0:07:53		71		43		9-Apr-08		0:25:59		70.41		35

		28-Feb-08		2:07:10		66.2		49		28-Feb-08		2:06:20		66.81		47.5		28-Feb-08		2:07:53		70.41		42.5		9-Apr-08		2:25:59		69.2		35

		28-Feb-08		4:07:10		65.6		49		28-Feb-08		4:06:20		66.2		46.5		28-Feb-08		4:07:53		69.8		41.5		9-Apr-08		4:25:59		68.61		35.5

		28-Feb-08		6:07:10		65.6		50		28-Feb-08		6:06:20		65.6		45		28-Feb-08		6:07:53		69.2		41		9-Apr-08		6:25:59		69.2		36

		28-Feb-08		8:07:10		66.2		48		28-Feb-08		8:06:20		65.6		42.5		28-Feb-08		8:07:53		70.41		41.5		9-Apr-08		8:25:59		70.41		36.5

		28-Feb-08		10:07:10		66.2		47.5		28-Feb-08		10:06:20		67.4		46		28-Feb-08		10:07:53		71		39		9-Apr-08		10:25:59		72.8		35.5

		28-Feb-08		12:07:10		66.81		49		28-Feb-08		12:06:20		68		48		28-Feb-08		12:07:53		71		41		9-Apr-08		12:25:59		74.01		35

		28-Feb-08		14:07:10		66.81		49.5		28-Feb-08		14:06:20		68.61		47		28-Feb-08		14:07:53		71		40		9-Apr-08		14:25:59		74.01		34

		28-Feb-08		16:07:10		66.81		51.5		28-Feb-08		16:06:20		67.4		56		28-Feb-08		16:07:53		71		51.5		9-Apr-08		16:25:59		74.01		34.5

		28-Feb-08		18:07:10		66.2		51.5		28-Feb-08		18:06:20		68		49.5		28-Feb-08		18:07:53		71		52		9-Apr-08		18:25:59		74.01		34.5

		28-Feb-08		20:07:10		66.2		48.5		28-Feb-08		20:06:20		66.81		53		28-Feb-08		20:07:53		71.6		47		9-Apr-08		20:25:59		72.8		33.5

		28-Feb-08		22:07:10		66.2		50		28-Feb-08		22:06:20		67.4		49.5		28-Feb-08		22:07:53		72.21		44		9-Apr-08		22:25:59		71		33.5

		29-Feb-08		0:07:10		65.6		49		29-Feb-08		0:06:20		66.81		48		29-Feb-08		0:07:53		71.6		42.5		10-Apr-08		0:25:59		69.2		33.5

		29-Feb-08		2:07:10		65.6		49		29-Feb-08		2:06:20		66.2		46		29-Feb-08		2:07:53		70.41		41.5		10-Apr-08		2:25:59		68		34.5

		29-Feb-08		4:07:10		66.2		49		29-Feb-08		4:06:20		65.01		44.5		29-Feb-08		4:07:53		69.2		40.5		10-Apr-08		4:25:59		66.81		35

		29-Feb-08		6:07:10		65.6		48.5		29-Feb-08		6:06:20		65.01		42		29-Feb-08		6:07:53		68.61		39.5		10-Apr-08		6:25:59		68		34.5

		29-Feb-08		8:07:10		66.2		48		29-Feb-08		8:06:20		65.01		40		29-Feb-08		8:07:53		71		38		10-Apr-08		8:25:59		69.2		35

		29-Feb-08		10:07:10		66.2		48		29-Feb-08		10:06:20		66.81		45.5		29-Feb-08		10:07:53		72.21		42.5		10-Apr-08		10:25:59		72.21		36

		29-Feb-08		12:07:10		66.81		48.5		29-Feb-08		12:06:20		66.81		47.5		29-Feb-08		12:07:53		71.6		47		10-Apr-08		12:25:59		74.01		35.5

		29-Feb-08		14:07:10		66.81		50.5		29-Feb-08		14:06:20		68.61		47.5		29-Feb-08		14:07:53		71		45		10-Apr-08		14:25:59		74.6		36.5

		29-Feb-08		16:07:10		66.81		51.5		29-Feb-08		16:06:20		68		45.5		29-Feb-08		16:07:53		70.41		44		10-Apr-08		16:25:59		74.01		37

		29-Feb-08		18:07:10		66.2		52		29-Feb-08		18:06:20		67.4		54		29-Feb-08		18:07:53		71		52		10-Apr-08		18:25:59		73.4		34.5

		29-Feb-08		20:07:10		66.2		49		29-Feb-08		20:06:20		67.4		48.5		29-Feb-08		20:07:53		69.8		50		10-Apr-08		20:25:59		72.8		35

		29-Feb-08		22:07:10		65.6		50		29-Feb-08		22:06:20		66.81		49.5		29-Feb-08		22:07:53		71.6		44.5		10-Apr-08		22:25:59		71.6		35

		1-Mar-08		0:07:10		65.6		48.5		1-Mar-08		0:06:20		66.81		47		1-Mar-08		0:07:53		71.6		42		11-Apr-08		0:25:59		70.41		35.5

		1-Mar-08		2:07:10		65.6		48.5		1-Mar-08		2:06:20		66.2		49		1-Mar-08		2:07:53		71		42		11-Apr-08		2:25:59		69.2		35

		1-Mar-08		4:07:10		65.6		49.5		1-Mar-08		4:06:20		66.2		48.5		1-Mar-08		4:07:53		70.41		42.5		11-Apr-08		4:25:59		68.61		35.5

		1-Mar-08		6:07:10		65.6		49		1-Mar-08		6:06:20		65.6		48		1-Mar-08		6:07:53		70.41		42.5		11-Apr-08		6:25:59		69.2		35.5

		1-Mar-08		8:07:10		66.2		48.5		1-Mar-08		8:06:20		66.2		46.5		1-Mar-08		8:07:53		71		43.5		11-Apr-08		8:25:59		71		36

		1-Mar-08		10:07:10		66.2		48.5		1-Mar-08		10:06:20		67.4		45		1-Mar-08		10:07:53		71		46		11-Apr-08		10:25:59		72.8		36.5

		1-Mar-08		12:07:10		66.81		49.5		1-Mar-08		12:06:20		66.81		49.5		1-Mar-08		12:07:53		71		48		11-Apr-08		12:25:59		74.6		36.5

		1-Mar-08		14:07:10		66.81		49		1-Mar-08		14:06:20		68		51.5		1-Mar-08		14:07:53		71		40		11-Apr-08		14:25:59		74.6		36

		1-Mar-08		16:07:10		66.81		51.5		1-Mar-08		16:06:20		68		56		1-Mar-08		16:07:53		71		51.5		11-Apr-08		16:25:59		74.6		36.5

		1-Mar-08		18:07:10		66.2		49		1-Mar-08		18:06:20		66.81		50.5		1-Mar-08		18:07:53		70.41		48.5		11-Apr-08		18:25:59		74.01		36

		1-Mar-08		20:07:10		65.6		49.5		1-Mar-08		20:06:20		66.81		49		1-Mar-08		20:07:53		69.8		46.5		11-Apr-08		20:25:59		74.01		36

		1-Mar-08		22:07:10		65.6		49		1-Mar-08		22:06:20		66.81		47		1-Mar-08		22:07:53		69.8		44		11-Apr-08		22:25:59		72.8		36.5

		2-Mar-08		0:07:10		65.6		49		2-Mar-08		0:06:20		66.81		48.5		2-Mar-08		0:07:53		69.8		43.5		12-Apr-08		0:25:59		71.6		37

		2-Mar-08		2:07:10		65.6		49		2-Mar-08		2:06:20		66.81		48.5		2-Mar-08		2:07:53		69.8		43.5		12-Apr-08		2:25:59		69.8		37

		2-Mar-08		4:07:10		65.6		49		2-Mar-08		4:06:20		66.2		48.5		2-Mar-08		4:07:53		69.2		43.5		12-Apr-08		4:25:59		69.2		37.5

		2-Mar-08		6:07:10		65.6		49		2-Mar-08		6:06:20		66.2		48		2-Mar-08		6:07:53		69.2		43.5		12-Apr-08		6:25:59		69.8		37

		2-Mar-08		8:07:10		65.6		49		2-Mar-08		8:06:20		66.81		45		2-Mar-08		8:07:53		71.6		41		12-Apr-08		8:25:59		71		37

		2-Mar-08		10:07:10		66.2		48.5		2-Mar-08		10:06:20		68		42		2-Mar-08		10:07:53		71		36.5		12-Apr-08		10:25:59		73.4		39

		2-Mar-08		12:07:10		66.2		49		2-Mar-08		12:06:20		67.4		35.5		2-Mar-08		12:07:53		70.41		40.5		12-Apr-08		12:25:59		74.6		38.5

		2-Mar-08		14:07:10		65.6		48		2-Mar-08		14:06:20		66.81		34.5		2-Mar-08		14:07:53		71		36.5		12-Apr-08		14:25:59		75.2		36.5

		2-Mar-08		16:07:10		65.6		47		2-Mar-08		16:06:20		67.4		35.5		2-Mar-08		16:07:53		70.41		35		12-Apr-08		16:25:59		74.6		36

		2-Mar-08		18:07:10		65.6		48.5		2-Mar-08		18:06:20		66.2		34.5		2-Mar-08		18:07:53		69.8		34.5		12-Apr-08		18:25:59		74.01		35

		2-Mar-08		20:07:10		65.6		47.5		2-Mar-08		20:06:20		66.2		36.5		2-Mar-08		20:07:53		69.8		35.5		12-Apr-08		20:25:59		73.4		33

		2-Mar-08		22:07:10		65.6		48		2-Mar-08		22:06:20		66.81		37.5		2-Mar-08		22:07:53		69.2		36.5		12-Apr-08		22:25:59		72.8		34.5

		3-Mar-08		0:07:10		65.6		47		3-Mar-08		0:06:20		66.2		37		3-Mar-08		0:07:53		68.61		36.5		13-Apr-08		0:25:59		71.6		35.5

		3-Mar-08		2:07:10		65.6		46.5		3-Mar-08		2:06:20		65.6		35		3-Mar-08		2:07:53		68		36.5		13-Apr-08		2:25:59		70.41		36.5

		3-Mar-08		4:07:10		65.6		49.5		3-Mar-08		4:06:20		65.01		34.5		3-Mar-08		4:07:53		67.4		36		13-Apr-08		4:25:59		69.8		36.5

		3-Mar-08		6:07:10		65.6		48.5		3-Mar-08		6:06:20		65.01		33		3-Mar-08		6:07:53		66.81		36		13-Apr-08		6:25:59		69.8		36.5

		3-Mar-08		8:07:10		66.2		47.5		3-Mar-08		8:06:20		65.01		32.5		3-Mar-08		8:07:53		67.4		34.5		13-Apr-08		8:25:59		69.8		36.5

		3-Mar-08		10:07:10		65.01		47		3-Mar-08		10:06:20		66.2		30.5		3-Mar-08		10:07:53		68		34		13-Apr-08		10:25:59		71.6		38.5

		3-Mar-08		12:07:10		65.6		48		3-Mar-08		12:06:20		67.4		27.5		3-Mar-08		12:07:53		69.2		31.5		13-Apr-08		12:25:59		74.01		37.5

		3-Mar-08		14:07:10		66.2		44.5		3-Mar-08		14:06:20		68		21.5		3-Mar-08		14:07:53		69.8		29		13-Apr-08		14:25:59		74.01		37.5

		3-Mar-08		16:07:10		66.2		44.5		3-Mar-08		16:06:20		68		19		3-Mar-08		16:07:53		69.8		29		13-Apr-08		16:25:59		72.8		38

		3-Mar-08		18:07:10		66.2		45		3-Mar-08		18:06:20		67.4		19		3-Mar-08		18:07:53		69.2		29.5		13-Apr-08		18:25:59		72.8		37.5

		3-Mar-08		20:07:10		65.6		46		3-Mar-08		20:06:20		66.81		19.5		3-Mar-08		20:07:53		70.41		28		13-Apr-08		20:25:59		72.8		37

		3-Mar-08		22:07:10		65.6		47.5		3-Mar-08		22:06:20		67.4		26		3-Mar-08		22:07:53		70.41		29.5		13-Apr-08		22:25:59		72.8		39.5

		4-Mar-08		0:07:10		65.6		48		4-Mar-08		0:06:20		66.2		34		4-Mar-08		0:07:53		69.8		32		14-Apr-08		0:25:59		71.6		39.5

		4-Mar-08		2:07:10		65.6		48.5		4-Mar-08		2:06:20		65.6		35.5		4-Mar-08		2:07:53		69.2		33.5		14-Apr-08		2:25:59		71		39

		4-Mar-08		4:07:10		65.6		46.5		4-Mar-08		4:06:20		65.01		35.5		4-Mar-08		4:07:53		68		34		14-Apr-08		4:25:59		69.8		38.5

		4-Mar-08		6:07:10		66.2		47.5		4-Mar-08		6:06:20		64.4		35		4-Mar-08		6:07:53		67.4		34.5		14-Apr-08		6:25:59		69.2		38.5

		4-Mar-08		8:07:10		66.2		47.5		4-Mar-08		8:06:20		65.01		34		4-Mar-08		8:07:53		69.2		34		14-Apr-08		8:25:59		68.61		39

		4-Mar-08		10:07:10		66.2		46		4-Mar-08		10:06:20		67.4		35.5		4-Mar-08		10:07:53		72.21		36		14-Apr-08		10:25:59		71		40.5

		4-Mar-08		12:07:10		66.81		47		4-Mar-08		12:06:20		68		34.5		4-Mar-08		12:07:53		71		40.5		14-Apr-08		12:25:59		72.8		40

		4-Mar-08		14:07:10		66.81		46		4-Mar-08		14:06:20		68		29		4-Mar-08		14:07:53		71		40		14-Apr-08		14:25:59		74.01		39

		4-Mar-08		16:07:10		66.81		47		4-Mar-08		16:06:20		68.61		31		4-Mar-08		16:07:53		70.41		37		14-Apr-08		16:25:59		74.01		39

		4-Mar-08		18:07:10		66.2		47.5		4-Mar-08		18:06:20		68		30		4-Mar-08		18:07:53		70.41		34.5		14-Apr-08		18:25:59		72.8		39.5

		4-Mar-08		20:07:10		66.2		45.5		4-Mar-08		20:06:20		67.4		30		4-Mar-08		20:07:53		69.8		34		14-Apr-08		20:25:59		72.8		40

		4-Mar-08		22:07:10		65.6		48		4-Mar-08		22:06:20		66.2		32		4-Mar-08		22:07:53		70.41		34		14-Apr-08		22:25:59		71.6		39.5

		5-Mar-08		0:07:10		65.6		47		5-Mar-08		0:06:20		67.4		33		5-Mar-08		0:07:53		71		33.5		15-Apr-08		0:25:59		71		39.5

		5-Mar-08		2:07:10		65.6		47.5		5-Mar-08		2:06:20		65.6		34.5		5-Mar-08		2:07:53		69.8		33.5		15-Apr-08		2:25:59		69.8		39

		5-Mar-08		4:07:10		65.6		48.5		5-Mar-08		4:06:20		65.01		35.5		5-Mar-08		4:07:53		68.61		33.5		15-Apr-08		4:25:59		68.61		39

		5-Mar-08		6:07:10		66.2		49		5-Mar-08		6:06:20		64.4		35		5-Mar-08		6:07:53		67.4		34		15-Apr-08		6:25:59		69.2		39

		5-Mar-08		8:07:10		66.2		47		5-Mar-08		8:06:20		65.01		34.5		5-Mar-08		8:07:53		69.8		33		15-Apr-08		8:25:59		70.41		39.5

		5-Mar-08		10:07:10		66.2		46		5-Mar-08		10:06:20		66.81		37.5		5-Mar-08		10:07:53		72.21		34.5		15-Apr-08		10:25:59		72.8		40.5

		5-Mar-08		12:07:10		66.81		46.5		5-Mar-08		12:06:20		68		38		5-Mar-08		12:07:53		71		42.5		15-Apr-08		12:25:59		74.6		38.5

		5-Mar-08		14:07:10		66.81		47		5-Mar-08		14:06:20		68		38		5-Mar-08		14:07:53		71		36.5		15-Apr-08		14:25:59		74.6		37

		5-Mar-08		16:07:10		66.81		45.5		5-Mar-08		16:06:20		68		35.5		5-Mar-08		16:07:53		70.41		37		15-Apr-08		16:25:59		74.01		36.5

		5-Mar-08		18:07:10		66.81		47.5		5-Mar-08		18:06:20		68		38.5		5-Mar-08		18:07:53		69.8		43		15-Apr-08		18:25:59		73.4		35

		5-Mar-08		20:07:10		66.2		48		5-Mar-08		20:06:20		67.4		42		5-Mar-08		20:07:53		70.41		41.5		15-Apr-08		20:25:59		72.21		34

		5-Mar-08		22:07:10		66.2		48		5-Mar-08		22:06:20		67.4		36.5		5-Mar-08		22:07:53		70.41		39		15-Apr-08		22:25:59		71		33.5

		6-Mar-08		0:07:10		65.6		48.5		6-Mar-08		0:06:20		66.2		38		6-Mar-08		0:07:53		70.41		36.5		16-Apr-08		0:25:59		69.2		33.5

		6-Mar-08		2:07:10		65.6		48.5		6-Mar-08		2:06:20		65.6		38		6-Mar-08		2:07:53		69.8		36		16-Apr-08		2:25:59		68		34

		6-Mar-08		4:07:10		65.6		48.5		6-Mar-08		4:06:20		65.01		37.5		6-Mar-08		4:07:53		68.61		36		16-Apr-08		4:25:59		67.4		35

		6-Mar-08		6:07:10		66.2		48.5		6-Mar-08		6:06:20		65.01		36		6-Mar-08		6:07:53		67.4		36		16-Apr-08		6:25:59		68		34

		6-Mar-08		8:07:10		66.2		47.5		6-Mar-08		8:06:20		65.01		35		6-Mar-08		8:07:53		70.41		34.5		16-Apr-08		8:25:59		70.41		34.5

		6-Mar-08		10:07:10		66.81		46		6-Mar-08		10:06:20		67.4		36.5		6-Mar-08		10:07:53		71.6		35		16-Apr-08		10:25:59		72.8		35

		6-Mar-08		12:07:10		66.81		46.5		6-Mar-08		12:06:20		68		34.5		6-Mar-08		12:07:53		70.41		44.5		16-Apr-08		12:25:59		74.6		34.5

		6-Mar-08		14:07:10		66.81		46.5		6-Mar-08		14:06:20		68.61		28		6-Mar-08		14:07:53		70.41		41		16-Apr-08		14:25:59		74.6		33.5

		6-Mar-08		16:07:10		66.81		43.5		6-Mar-08		16:06:20		68.61		25		6-Mar-08		16:07:53		70.41		39		16-Apr-08		16:25:59		74.01		33.5

		6-Mar-08		18:07:10		66.2		41.5		6-Mar-08		18:06:20		68		29.5		6-Mar-08		18:07:53		69.8		38.5		16-Apr-08		18:25:59		73.4		33

		6-Mar-08		20:07:10		66.2		48.5		6-Mar-08		20:06:20		66.81		37.5		6-Mar-08		20:07:53		71		37.5		16-Apr-08		20:25:59		72.8		32

		6-Mar-08		22:07:10		65.6		47		6-Mar-08		22:06:20		66.81		40		6-Mar-08		22:07:53		71.6		37		16-Apr-08		22:25:59		71.6		32

		7-Mar-08		0:07:10		65.6		48.5		7-Mar-08		0:06:20		66.2		39		7-Mar-08		0:07:53		70.41		36.5		17-Apr-08		0:25:59		69.8		32.5

		7-Mar-08		2:07:10		65.6		48.5		7-Mar-08		2:06:20		65.01		38		7-Mar-08		2:07:53		69.2		36		17-Apr-08		2:25:59		68.61		34

		7-Mar-08		4:07:10		65.6		42.5		7-Mar-08		4:06:20		64.4		37.5		7-Mar-08		4:07:53		68.61		36		17-Apr-08		4:25:59		68		34.5

		7-Mar-08		6:07:10		65.6		47		7-Mar-08		6:06:20		63.8		36.5		7-Mar-08		6:07:53		67.4		36		17-Apr-08		6:25:59		69.2		34

		7-Mar-08		8:07:10		66.2		48		7-Mar-08		8:06:20		65.01		35.5		7-Mar-08		8:07:53		70.41		35		17-Apr-08		8:25:59		71		34.5

		7-Mar-08		10:07:10		65.6		46.5		7-Mar-08		10:06:20		66.81		37.5		7-Mar-08		10:07:53		71.6		33.5		17-Apr-08		10:25:59		74.01		35

		7-Mar-08		12:07:10		66.2		48		7-Mar-08		12:06:20		67.4		39.5		7-Mar-08		12:07:53		71		39.5		17-Apr-08		12:25:59		75.2		34.5

		7-Mar-08		14:07:10		66.2		43.5		7-Mar-08		14:06:20		68		39		7-Mar-08		14:07:53		71.6		38.5		17-Apr-08		14:25:59		75.2		34.5

		7-Mar-08		16:07:10		66.81		47.5		7-Mar-08		16:06:20		68		40		7-Mar-08		16:07:53		70.41		36.5		17-Apr-08		16:25:59		74.6		34.5

		7-Mar-08		18:07:10		66.2		48		7-Mar-08		18:06:20		68		36.5		7-Mar-08		18:07:53		70.41		35		17-Apr-08		18:25:59		74.01		34

		7-Mar-08		20:07:10		66.2		48		7-Mar-08		20:06:20		66.81		40.5		7-Mar-08		20:07:53		69.8		36		17-Apr-08		20:25:59		74.01		35

		7-Mar-08		22:07:10		65.6		48.5		7-Mar-08		22:06:20		66.81		39		7-Mar-08		22:07:53		70.41		38		17-Apr-08		22:25:59		73.4		35

		8-Mar-08		0:07:10		65.6		43		8-Mar-08		0:06:20		66.2		40.5		8-Mar-08		0:07:53		69.8		37		18-Apr-08		0:25:59		71.6		35

		8-Mar-08		2:07:10		65.6		48.5		8-Mar-08		2:06:20		65.01		41.5		8-Mar-08		2:07:53		69.2		37		18-Apr-08		2:25:59		70.41		36

		8-Mar-08		4:07:10		65.6		48		8-Mar-08		4:06:20		64.4		39.5		8-Mar-08		4:07:53		68		37		18-Apr-08		4:25:59		69.2		36

		8-Mar-08		6:07:10		65.6		48.5		8-Mar-08		6:06:20		63.8		38.5		8-Mar-08		6:07:53		67.4		36.5		18-Apr-08		6:25:59		69.8		36

		8-Mar-08		8:07:10		66.2		47.5		8-Mar-08		8:06:20		65.6		37		8-Mar-08		8:07:53		69.2		36		18-Apr-08		8:25:59		71.6		36

		8-Mar-08		10:07:10		66.2		42		8-Mar-08		10:06:20		67.4		39.5		8-Mar-08		10:07:53		71		38.5		18-Apr-08		10:25:59		74.01		37.5

		8-Mar-08		12:07:10		66.2		48		8-Mar-08		12:06:20		68		38.5		8-Mar-08		12:07:53		70.41		43		18-Apr-08		12:25:59		75.2		39

		8-Mar-08		14:07:10		66.2		47		8-Mar-08		14:06:20		67.4		38.5		8-Mar-08		14:07:53		71		36		18-Apr-08		14:25:59		75.2		38

		8-Mar-08		16:07:10		66.2		48		8-Mar-08		16:06:20		67.4		40		8-Mar-08		16:07:53		70.41		42		18-Apr-08		16:25:59		75.2		38

		8-Mar-08		18:07:10		66.2		49		8-Mar-08		18:06:20		67.4		44		8-Mar-08		18:07:53		70.41		42		18-Apr-08		18:25:59		74.6		37

		8-Mar-08		20:07:10		65.6		43.5		8-Mar-08		20:06:20		66.81		41.5		8-Mar-08		20:07:53		69.8		40		18-Apr-08		20:25:59		74.6		38

		8-Mar-08		22:07:10		65.6		48.5		8-Mar-08		22:06:20		66.2		45.5		8-Mar-08		22:07:53		70.41		40.5		18-Apr-08		22:25:59		73.4		37.5

		9-Mar-08		0:07:10		65.6		48.5		9-Mar-08		0:06:20		66.81		44.5		9-Mar-08		0:07:53		70.41		40		19-Apr-08		0:25:59		71.6		37.5

		9-Mar-08		2:07:10		65.6		47		9-Mar-08		2:06:20		66.2		43.5		9-Mar-08		2:07:53		69.8		39		19-Apr-08		2:25:59		71		38.5

		9-Mar-08		4:07:10		65.6		48		9-Mar-08		4:06:20		65.01		42.5		9-Mar-08		4:07:53		69.2		38.5		19-Apr-08		4:25:59		70.41		39.5

		9-Mar-08		6:07:10		65.6		42		9-Mar-08		6:06:20		64.4		42		9-Mar-08		6:07:53		68.61		38.5		19-Apr-08		6:25:59		71.6		39.5

		9-Mar-08		8:07:10		65.6		48		9-Mar-08		8:06:20		65.01		39		9-Mar-08		8:07:53		71		37		19-Apr-08		8:25:59		72.21		39

		9-Mar-08		10:07:10		66.2		48.5		9-Mar-08		10:06:20		66.81		43.5		9-Mar-08		10:07:53		71		34.5		19-Apr-08		10:25:59		73.4		40

		9-Mar-08		12:07:10		66.2		48.5		9-Mar-08		12:06:20		67.4		43		9-Mar-08		12:07:53		71.6		46		19-Apr-08		12:25:59		74.01		40.5

		9-Mar-08		14:07:10		66.2		47.5		9-Mar-08		14:06:20		68		35		9-Mar-08		14:07:53		71		43		19-Apr-08		14:25:59		75.2		41

		9-Mar-08		16:07:10		66.2		44		9-Mar-08		16:06:20		67.4		37.5		9-Mar-08		16:07:53		71		36.5		19-Apr-08		16:25:59		74.6		39.5

		9-Mar-08		18:07:10		66.2		47.5		9-Mar-08		18:06:20		67.4		31.5		9-Mar-08		18:07:53		69.8		36		19-Apr-08		18:25:59		74.01		38.5

		9-Mar-08		20:07:10		66.2		47.5		9-Mar-08		20:06:20		67.4		44.5		9-Mar-08		20:07:53		69.8		42		19-Apr-08		20:25:59		74.01		38.5

		9-Mar-08		22:07:10		65.6		48.5		9-Mar-08		22:06:20		66.2		47.5		9-Mar-08		22:07:53		71.6		40		19-Apr-08		22:25:59		72.8		37.5

		10-Mar-08		0:07:10		65.6		48.5		10-Mar-08		0:06:20		66.81		44.5		10-Mar-08		0:07:53		71		39.5		20-Apr-08		0:25:59		71		38

		10-Mar-08		2:07:10		65.6		48		10-Mar-08		2:06:20		66.2		44.5		10-Mar-08		2:07:53		70.41		39		20-Apr-08		2:25:59		69.8		38

		10-Mar-08		4:07:10		65.6		49		10-Mar-08		4:06:20		65.01		44		10-Mar-08		4:07:53		69.8		38.5		20-Apr-08		4:25:59		68.61		37.5

		10-Mar-08		6:07:10		65.6		49.5		10-Mar-08		6:06:20		64.4		42		10-Mar-08		6:07:53		68.61		38.5		20-Apr-08		6:25:59		68		37.5

		10-Mar-08		8:07:10		65.6		48		10-Mar-08		8:06:20		63.8		40.5		10-Mar-08		8:07:53		68		38		20-Apr-08		8:25:59		67.4		36.5

		10-Mar-08		10:07:10		65.6		48		10-Mar-08		10:06:20		66.2		41.5		10-Mar-08		10:07:53		69.2		39		20-Apr-08		10:25:59		68		37.5

		10-Mar-08		12:07:10		65.6		49		10-Mar-08		12:06:20		66.81		41		10-Mar-08		12:07:53		69.8		40		20-Apr-08		12:25:59		69.2		36.5

		10-Mar-08		14:07:10		66.2		47.5		10-Mar-08		14:06:20		68		37.5		10-Mar-08		14:07:53		70.41		41		20-Apr-08		14:25:59		70.41		33.5

		10-Mar-08		16:07:10		66.2		48		10-Mar-08		16:06:20		68		34.5		10-Mar-08		16:07:53		69.8		41.5		20-Apr-08		16:25:59		70.41		33

		10-Mar-08		18:07:10		66.2		48		10-Mar-08		18:06:20		68		33.5		10-Mar-08		18:07:53		70.41		39.5		20-Apr-08		18:25:59		70.41		32

		10-Mar-08		20:07:10		66.2		48		10-Mar-08		20:06:20		67.4		43		10-Mar-08		20:07:53		71		42		20-Apr-08		20:25:59		69.8		32

		10-Mar-08		22:07:10		65.6		49		10-Mar-08		22:06:20		66.2		45		10-Mar-08		22:07:53		71.6		40.5		20-Apr-08		22:25:59		68.61		33

		11-Mar-08		0:07:10		65.6		49		11-Mar-08		0:06:20		66.81		44.5		11-Mar-08		0:07:53		71		39.5		21-Apr-08		0:25:59		67.4		33.5

		11-Mar-08		2:07:10		65.6		49		11-Mar-08		2:06:20		66.2		45		11-Mar-08		2:07:53		70.41		39.5		21-Apr-08		2:25:59		66.81		34

		11-Mar-08		4:07:10		65.6		48.5		11-Mar-08		4:06:20		65.6		45		11-Mar-08		4:07:53		69.8		39		21-Apr-08		4:25:59		65.6		35

		11-Mar-08		6:07:10		65.6		48		11-Mar-08		6:06:20		65.01		45		11-Mar-08		6:07:53		71		39.5		21-Apr-08		6:25:59		65.01		35.5

		11-Mar-08		8:07:10		66.2		48		11-Mar-08		8:06:20		66.81		43		11-Mar-08		8:07:53		71.6		35.5		21-Apr-08		8:25:59		64.4		36.5

		11-Mar-08		10:07:10		66.81		47.5		11-Mar-08		10:06:20		67.4		43.5		11-Mar-08		10:07:53		71		37		21-Apr-08		10:25:59		65.6		37.5

		11-Mar-08		12:07:10		66.2		48		11-Mar-08		12:06:20		67.4		44		11-Mar-08		12:07:53		71		43		21-Apr-08		12:25:59		66.81		36

		11-Mar-08		14:07:10		66.81		52.5		11-Mar-08		14:06:20		68.61		52		11-Mar-08		14:07:53		70.41		48.5		21-Apr-08		14:25:59		68.61		36

		11-Mar-08		16:07:10		66.2		49.5		11-Mar-08		16:06:20		67.4		49		11-Mar-08		16:07:53		70.41		53		21-Apr-08		16:25:59		69.8		34.5

		11-Mar-08		18:07:10		66.2		49		11-Mar-08		18:06:20		68		45		11-Mar-08		18:07:53		71		42		21-Apr-08		18:25:59		69.8		33

		11-Mar-08		20:07:10		65.6		48.5		11-Mar-08		20:06:20		66.81		46		11-Mar-08		20:07:53		70.41		43		21-Apr-08		20:25:59		69.2		33

		11-Mar-08		22:07:10		65.6		48.5		11-Mar-08		22:06:20		67.4		45.5		11-Mar-08		22:07:53		71		42		21-Apr-08		22:25:59		68.61		34.5

		12-Mar-08		0:07:10		65.6		49		12-Mar-08		0:06:20		66.81		45.5		12-Mar-08		0:07:53		71.6		40.5		22-Apr-08		0:25:59		67.4		34.5

		12-Mar-08		2:07:10		65.6		49		12-Mar-08		2:06:20		66.81		45		12-Mar-08		2:07:53		70.41		40.5		22-Apr-08		2:25:59		66.2		35

		12-Mar-08		4:07:10		65.6		49		12-Mar-08		4:06:20		65.6		44.5		12-Mar-08		4:07:53		69.8		39.5		22-Apr-08		4:25:59		65.6		36

		12-Mar-08		6:07:10		65.6		49		12-Mar-08		6:06:20		65.01		44		12-Mar-08		6:07:53		70.41		39.5		22-Apr-08		6:25:59		66.81		34

		12-Mar-08		8:07:10		66.2		48		12-Mar-08		8:06:20		66.2		42.5		12-Mar-08		8:07:53		71		40.5		22-Apr-08		8:25:59		68		34.5

		12-Mar-08		10:07:10		66.2		49		12-Mar-08		10:06:20		66.81		50		12-Mar-08		10:07:53		70.41		45		22-Apr-08		10:25:59		72.21		36

		12-Mar-08		12:07:10		66.2		50		12-Mar-08		12:06:20		66.81		48		12-Mar-08		12:07:53		71.6		50		22-Apr-08		12:25:59		73.4		35.5

		12-Mar-08		14:07:10		66.2		49.5		12-Mar-08		14:06:20		68		50.5		12-Mar-08		14:07:53		71		41.5		22-Apr-08		14:25:59		73.4		35.5

		12-Mar-08		16:07:10		66.2		51.5		12-Mar-08		16:06:20		66.81		59.5		12-Mar-08		16:07:53		71		50.5		22-Apr-08		16:25:59		73.4		35.5

		12-Mar-08		18:07:10		66.2		51.5		12-Mar-08		18:06:20		67.4		48.5		12-Mar-08		18:07:53		70.41		50		22-Apr-08		18:25:59		72.8		35

		12-Mar-08		20:07:10		65.6		50		12-Mar-08		20:06:20		67.4		51.5		12-Mar-08		20:07:53		70.41		48		22-Apr-08		20:25:59		72.21		34.5

		12-Mar-08		22:07:10		65.6		49		12-Mar-08		22:06:20		67.4		49		12-Mar-08		22:07:53		70.41		44.5		22-Apr-08		22:25:59		71		34

		13-Mar-08		0:07:10		65.6		49		13-Mar-08		0:06:20		66.81		47.5		13-Mar-08		0:07:53		70.41		42		23-Apr-08		0:25:59		69.8		34

		13-Mar-08		2:07:10		65.6		49		13-Mar-08		2:06:20		65.6		46		13-Mar-08		2:07:53		70.41		41		23-Apr-08		2:25:59		68.61		34.5

		13-Mar-08		4:07:10		65.6		49.5		13-Mar-08		4:06:20		65.01		47		13-Mar-08		4:07:53		69.2		41		23-Apr-08		4:25:59		67.4		35

		13-Mar-08		6:07:10		65.6		49		13-Mar-08		6:06:20		65.6		48.5		13-Mar-08		6:07:53		70.41		42.5		23-Apr-08		6:25:59		68.61		34.5

		13-Mar-08		8:07:10		66.2		48		13-Mar-08		8:06:20		67.4		46.5		13-Mar-08		8:07:53		71		44		23-Apr-08		8:25:59		70.41		34.5

		13-Mar-08		10:07:10		66.2		48		13-Mar-08		10:06:20		66.81		46.5		13-Mar-08		10:07:53		71.6		41.5		23-Apr-08		10:25:59		71.6		35.5

		13-Mar-08		12:07:10		66.2		48.5		13-Mar-08		12:06:20		66.81		47.5		13-Mar-08		12:07:53		71		43		23-Apr-08		12:25:59		72.21		37.5

		13-Mar-08		14:07:10		66.81		49		13-Mar-08		14:06:20		67.4		46.5		13-Mar-08		14:07:53		71		46.5		23-Apr-08		14:25:59		72.8		39

		13-Mar-08		16:07:10		66.81		49.5		13-Mar-08		16:06:20		67.4		52		13-Mar-08		16:07:53		70.41		41.5		23-Apr-08		16:25:59		73.4		40.5

		13-Mar-08		18:07:10		66.2		49		13-Mar-08		18:06:20		66.81		49		13-Mar-08		18:07:53		71		44.5		23-Apr-08		18:25:59		73.4		40.5

		13-Mar-08		20:07:10		66.2		48.5		13-Mar-08		20:06:20		66.2		48		13-Mar-08		20:07:53		71		43.5		23-Apr-08		20:25:59		72.8		41.5

		13-Mar-08		22:07:10		66.2		49		13-Mar-08		22:06:20		67.4		46.5		13-Mar-08		22:07:53		72.21		41.5		23-Apr-08		22:25:59		71.6		41.5

		14-Mar-08		0:07:10		66.2		49.5		14-Mar-08		0:06:20		67.4		51		14-Mar-08		0:07:53		71.6		42		24-Apr-08		0:25:59		70.41		42

		14-Mar-08		2:07:10		65.6		50.5		14-Mar-08		2:06:20		67.4		52		14-Mar-08		2:07:53		71.6		43		24-Apr-08		2:25:59		69.2		42

		14-Mar-08		4:07:10		65.6		50.5		14-Mar-08		4:06:20		66.81		53		14-Mar-08		4:07:53		71.6		43.5		24-Apr-08		4:25:59		68.61		42.5

		14-Mar-08		6:07:10		66.2		50.5		14-Mar-08		6:06:20		67.4		53.5		14-Mar-08		6:07:53		71		40.5		24-Apr-08		6:25:59		69.2		42

		14-Mar-08		8:07:10		66.2		49.5		14-Mar-08		8:06:20		66.81		52		14-Mar-08		8:07:53		70.41		50		24-Apr-08		8:25:59		71		42

		14-Mar-08		10:07:10		66.2		51		14-Mar-08		10:06:20		67.4		52.5		14-Mar-08		10:07:53		71		51.5		24-Apr-08		10:25:59		72.8		43

		14-Mar-08		12:07:10		66.2		49.5		14-Mar-08		12:06:20		68		48		14-Mar-08		12:07:53		71		50.5		24-Apr-08		12:25:59		74.01		43

		14-Mar-08		14:07:10		66.81		48.5		14-Mar-08		14:06:20		68.61		47.5		14-Mar-08		14:07:53		71		52.5		24-Apr-08		14:25:59		74.01		40.5

		14-Mar-08		16:07:10		66.2		48		14-Mar-08		16:06:20		68		45.5		14-Mar-08		16:07:53		70.41		44		24-Apr-08		16:25:59		74.01		38.5

		14-Mar-08		18:07:10		65.6		48.5		14-Mar-08		18:06:20		66.81		46		14-Mar-08		18:07:53		70.41		43		24-Apr-08		18:25:59		72.8		36.5

		14-Mar-08		20:07:10		65.6		48.5		14-Mar-08		20:06:20		67.4		45		14-Mar-08		20:07:53		69.8		43		24-Apr-08		20:25:59		72.8		36.5

		14-Mar-08		22:07:10		65.6		48.5		14-Mar-08		22:06:20		67.4		45.5		14-Mar-08		22:07:53		71		41		24-Apr-08		22:25:59		71.6		35

		15-Mar-08		0:07:10		65.6		49		15-Mar-08		0:06:20		66.2		45		15-Mar-08		0:07:53		70.41		40.5		25-Apr-08		0:25:59		69.8		35

		15-Mar-08		2:07:10		65.6		49		15-Mar-08		2:06:20		65.6		44		15-Mar-08		2:07:53		69.8		39.5		25-Apr-08		2:25:59		68		35.5

		15-Mar-08		4:07:10		65.6		49		15-Mar-08		4:06:20		65.01		42.5		15-Mar-08		4:07:53		69.2		39		25-Apr-08		4:25:59		66.81		37

		15-Mar-08		6:07:10		66.2		48.5		15-Mar-08		6:06:20		65.6		44.5		15-Mar-08		6:07:53		69.2		42		25-Apr-08		6:25:59		68		36.5

		15-Mar-08		8:07:10		66.2		47.5		15-Mar-08		8:06:20		66.2		44		15-Mar-08		8:07:53		71		42		25-Apr-08		8:25:59		69.2		36.5

		15-Mar-08		10:07:10		66.81		48		15-Mar-08		10:06:20		67.4		46.5		15-Mar-08		10:07:53		71		47		25-Apr-08		10:25:59		72.8		38.5

		15-Mar-08		12:07:10		66.2		48		15-Mar-08		12:06:20		67.4		46.5		15-Mar-08		12:07:53		71		46.5		25-Apr-08		12:25:59		74.01		37

		15-Mar-08		14:07:10		66.2		48		15-Mar-08		14:06:20		67.4		41		15-Mar-08		14:07:53		71.6		44		25-Apr-08		14:25:59		74.6		36.5

		15-Mar-08		16:07:10		66.2		47.5		15-Mar-08		16:06:20		66.81		38		15-Mar-08		16:07:53		70.41		39.5		25-Apr-08		16:25:59		74.6		37.5

		15-Mar-08		18:07:10		65.6		48		15-Mar-08		18:06:20		66.81		40		15-Mar-08		18:07:53		69.8		38.5		25-Apr-08		18:25:59		74.01		35.5

		15-Mar-08		20:07:10		65.6		42.5		15-Mar-08		20:06:20		65.6		41		15-Mar-08		20:07:53		69.8		37.5		25-Apr-08		20:25:59		74.6		35.5

		15-Mar-08		22:07:10		65.6		49		15-Mar-08		22:06:20		65.01		41.5		15-Mar-08		22:07:53		69.2		37		25-Apr-08		22:25:59		74.01		35.5

		16-Mar-08		0:07:10		65.01		49		16-Mar-08		0:06:20		64.4		42		16-Mar-08		0:07:53		68.61		38		26-Apr-08		0:25:59		72.8		35

		16-Mar-08		2:07:10		65.01		50		16-Mar-08		2:06:20		63.8		43.5		16-Mar-08		2:07:53		68		38.5		26-Apr-08		2:25:59		71		36

		16-Mar-08		4:07:10		65.01		49		16-Mar-08		4:06:20		63.21		44		16-Mar-08		4:07:53		67.4		39		26-Apr-08		4:25:59		69.8		36.5

		16-Mar-08		6:07:10		65.01		49.5		16-Mar-08		6:06:20		63.21		43		16-Mar-08		6:07:53		68		39		26-Apr-08		6:25:59		70.41		37.5

		16-Mar-08		8:07:10		65.6		48		16-Mar-08		8:06:20		62		41.5		16-Mar-08		8:07:53		70.41		36.5		26-Apr-08		8:25:59		72.21		37

		16-Mar-08		10:07:10		65.6		49		16-Mar-08		10:06:20		64.4		44		16-Mar-08		10:07:53		71.6		38.5		26-Apr-08		10:25:59		74.01		38

		16-Mar-08		12:07:10		65.6		44		16-Mar-08		12:06:20		65.6		38		16-Mar-08		12:07:53		71		34		26-Apr-08		12:25:59		75.2		37.5

		16-Mar-08		14:07:10		65.6		38		16-Mar-08		14:06:20		66.2		34.5		16-Mar-08		14:07:53		70.41		33.5		26-Apr-08		14:25:59		73.4		34

		16-Mar-08		16:07:10		65.6		46		16-Mar-08		16:06:20		67.4		33		16-Mar-08		16:07:53		69.8		31.5		26-Apr-08		16:25:59		73.4		35.5

		16-Mar-08		18:07:10		65.6		41		16-Mar-08		18:06:20		66.2		36		16-Mar-08		18:07:53		69.2		34.5		26-Apr-08		18:25:59		73.4		37

		16-Mar-08		20:07:10		65.6		44		16-Mar-08		20:06:20		65.6		40		16-Mar-08		20:07:53		69.2		37		26-Apr-08		20:25:59		73.4		37

		16-Mar-08		22:07:10		65.6		48.5		16-Mar-08		22:06:20		65.6		37.5		16-Mar-08		22:07:53		68.61		36.5		26-Apr-08		22:25:59		72.8		36.5

		17-Mar-08		0:07:10		65.6		47.5		17-Mar-08		0:06:20		65.01		36		17-Mar-08		0:07:53		68		36		27-Apr-08		0:25:59		72.21		36.5

		17-Mar-08		2:07:10		65.6		47		17-Mar-08		2:06:20		64.4		34.5		17-Mar-08		2:07:53		67.4		35		27-Apr-08		2:25:59		71		36

		17-Mar-08		4:07:10		65.6		47.5		17-Mar-08		4:06:20		64.4		34		17-Mar-08		4:07:53		66.81		35		27-Apr-08		4:25:59		70.41		36.5

		17-Mar-08		6:07:10		65.01		38		17-Mar-08		6:06:20		64.4		34.5		17-Mar-08		6:07:53		66.2		35		27-Apr-08		6:25:59		69.8		36

		17-Mar-08		8:07:10		65.01		46.5		17-Mar-08		8:06:20		63.8		34.5		17-Mar-08		8:07:53		67.4		34.5		27-Apr-08		8:25:59		69.8		37.5

		17-Mar-08		10:07:10		65.6		38.5		17-Mar-08		10:06:20		65.01		34		17-Mar-08		10:07:53		68.61		33.5		27-Apr-08		10:25:59		71		40

		17-Mar-08		12:07:10		65.6		33.5		17-Mar-08		12:06:20		67.4		30		17-Mar-08		12:07:53		69.8		31.5		27-Apr-08		12:25:59		72.8		39.5

		17-Mar-08		14:07:10		65.6		42		17-Mar-08		14:06:20		66.81		23		17-Mar-08		14:07:53		69.8		30		27-Apr-08		14:25:59		74.01		38.5

		17-Mar-08		16:07:10		65.6		40		17-Mar-08		16:06:20		66.81		22		17-Mar-08		16:07:53		69.8		29		27-Apr-08		16:25:59		73.4		40.5

		17-Mar-08		18:07:10		65.6		36.5		17-Mar-08		18:06:20		66.2		31.5		17-Mar-08		18:07:53		69.8		31		27-Apr-08		18:25:59		73.4		40.5

		17-Mar-08		20:07:10		65.6		47.5		17-Mar-08		20:06:20		66.2		34.5		17-Mar-08		20:07:53		69.8		33		27-Apr-08		20:25:59		73.4		40.5

		17-Mar-08		22:07:10		65.6		47.5		17-Mar-08		22:06:20		66.81		35		17-Mar-08		22:07:53		70.41		34		27-Apr-08		22:25:59		73.4		38.5

		18-Mar-08		0:07:10		65.6		48		18-Mar-08		0:06:20		66.2		36		18-Mar-08		0:07:53		69.8		33.5		28-Apr-08		0:25:59		72.8		37.5

		18-Mar-08		2:07:10		65.6		39		18-Mar-08		2:06:20		65.01		37		18-Mar-08		2:07:53		68.61		34		28-Apr-08		2:25:59		72.21		39.5

		18-Mar-08		4:07:10		65.6		48		18-Mar-08		4:06:20		65.01		37.5		18-Mar-08		4:07:53		68		35		28-Apr-08		4:25:59		71.6		39.5

		18-Mar-08		6:07:10		66.2		47		18-Mar-08		6:06:20		65.01		37.5		18-Mar-08		6:07:53		69.2		34.5		28-Apr-08		6:25:59		70.41		39.5

		18-Mar-08		8:07:10		66.81		42		18-Mar-08		8:06:20		66.2		36.5		18-Mar-08		8:07:53		71.6		34.5		28-Apr-08		8:25:59		69.8		39.5

		18-Mar-08		10:07:10		66.2		38.5		18-Mar-08		10:06:20		67.4		35.5		18-Mar-08		10:07:53		71.6		39.5		28-Apr-08		10:25:59		71.6		41.5

		18-Mar-08		12:07:10		66.2		42		18-Mar-08		12:06:20		66.81		34.5		18-Mar-08		12:07:53		71.6		37		28-Apr-08		12:25:59		74.01		40

		18-Mar-08		14:07:10		66.81		46		18-Mar-08		14:06:20		66.2		39		18-Mar-08		14:07:53		71.6		34.5		28-Apr-08		14:25:59		74.01		39.5

		18-Mar-08		16:07:10		66.81		47.5		18-Mar-08		16:06:20		65.6		45		18-Mar-08		16:07:53		71.6		40		28-Apr-08		16:25:59		73.4		41.5

		18-Mar-08		18:07:10		66.81		46.5		18-Mar-08		18:06:20		65.6		45.5		18-Mar-08		18:07:53		70.41		37.5		28-Apr-08		18:25:59		73.4		41

		18-Mar-08		20:07:10		66.2		47		18-Mar-08		20:06:20		65.6		47		18-Mar-08		20:07:53		70.41		42.5		28-Apr-08		20:25:59		73.4		40.5

		18-Mar-08		22:07:10		66.2		47.5		18-Mar-08		22:06:20		65.01		47		18-Mar-08		22:07:53		71.6		40.5		28-Apr-08		22:25:59		73.4		39.5

		19-Mar-08		0:07:10		65.6		48		19-Mar-08		0:06:20		65.6		44.5		19-Mar-08		0:07:53		72.21		39		29-Apr-08		0:25:59		72.8		38.5

		19-Mar-08		2:07:10		65.6		48.5		19-Mar-08		2:06:20		64.4		49.5		19-Mar-08		2:07:53		71.6		39		29-Apr-08		2:25:59		71.6		38.5

		19-Mar-08		4:07:10		65.6		48		19-Mar-08		4:06:20		65.6		46.5		19-Mar-08		4:07:53		71		39		29-Apr-08		4:25:59		70.41		38.5

		19-Mar-08		6:07:10		66.2		47		19-Mar-08		6:06:20		65.6		45.5		19-Mar-08		6:07:53		71.6		39.5		29-Apr-08		6:25:59		70.41		38

		19-Mar-08		8:07:10		66.2		47		19-Mar-08		8:06:20		65.01		47		19-Mar-08		8:07:53		70.41		38		29-Apr-08		8:25:59		69.8		39.5

		19-Mar-08		10:07:10		66.2		47		19-Mar-08		10:06:20		66.2		47		19-Mar-08		10:07:53		70.41		37.5		29-Apr-08		10:25:59		72.8		40.5

		19-Mar-08		12:07:10		66.81		48.5		19-Mar-08		12:06:20		66.2		48		19-Mar-08		12:07:53		71.6		50.5		29-Apr-08		12:25:59		73.4		42.5

		19-Mar-08		14:07:10		66.81		49		19-Mar-08		14:06:20		66.2		51		19-Mar-08		14:07:53		71		41		29-Apr-08		14:25:59		73.4		43

		19-Mar-08		16:07:10		66.81		46.5		19-Mar-08		16:06:20		66.2		44		19-Mar-08		16:07:53		71.6		42.5		29-Apr-08		16:25:59		74.01		42.5

		19-Mar-08		18:07:10		66.2		47.5		19-Mar-08		18:06:20		66.2		45		19-Mar-08		18:07:53		70.41		40		29-Apr-08		18:25:59		74.01		41

		19-Mar-08		20:07:10		66.2		49		19-Mar-08		20:06:20		65.01		51.5		19-Mar-08		20:07:53		70.41		45		29-Apr-08		20:25:59		74.6		41

		19-Mar-08		22:07:10		65.6		48		19-Mar-08		22:06:20		65.6		52.5		19-Mar-08		22:07:53		71		44.5		29-Apr-08		22:25:59		74.01		40

		20-Mar-08		0:07:10		65.6		47		20-Mar-08		0:06:20		65.01		50.5		20-Mar-08		0:07:53		71		41.5		30-Apr-08		0:25:59		72.8		36.5

		20-Mar-08		2:07:10		65.6		48.5		20-Mar-08		2:06:20		65.6		47.5		20-Mar-08		2:07:53		71		40		30-Apr-08		2:25:59		71		36

		20-Mar-08		4:07:10		65.6		48.5		20-Mar-08		4:06:20		65.01		44.5		20-Mar-08		4:07:53		70.41		39		30-Apr-08		4:25:59		70.41		36

		20-Mar-08		6:07:10		65.6		41		20-Mar-08		6:06:20		64.4		43.5		20-Mar-08		6:07:53		70.41		38.5		30-Apr-08		6:25:59		70.41		36

		20-Mar-08		8:07:10		66.2		47		20-Mar-08		8:06:20		65.6		45		20-Mar-08		8:07:53		71.6		41		30-Apr-08		8:25:59		71		36

		20-Mar-08		10:07:10		66.2		45		20-Mar-08		10:06:20		65.6		49		20-Mar-08		10:07:53		71		45.5		30-Apr-08		10:25:59		72.8		36

		20-Mar-08		12:07:10		66.2		48		20-Mar-08		12:06:20		65.01		51.5		20-Mar-08		12:07:53		69.8		47		30-Apr-08		12:25:59		72.8		34.5

		20-Mar-08		14:07:10		66.81		47.5		20-Mar-08		14:06:20		65.6		53.5		20-Mar-08		14:07:53		71		51.5		30-Apr-08		14:25:59		73.4		33.5

		20-Mar-08		16:07:10		66.2		50		20-Mar-08		16:06:20		65.6		55.5		20-Mar-08		16:07:53		69.8		50.5		30-Apr-08		16:25:59		73.4		34

		20-Mar-08		18:07:10		66.2		48.5		20-Mar-08		18:06:20		65.6		56		20-Mar-08		18:07:53		69.8		48.5		30-Apr-08		18:25:59		72.8		32

		20-Mar-08		20:07:10		65.6		48.5		20-Mar-08		20:06:20		66.2		46		20-Mar-08		20:07:53		70.41		44		30-Apr-08		20:25:59		73.4		32

		20-Mar-08		22:07:10		65.6		48.5		20-Mar-08		22:06:20		65.6		47.5		20-Mar-08		22:07:53		71		41.5		30-Apr-08		22:25:59		72.21		31

		21-Mar-08		0:07:10		65.6		43		21-Mar-08		0:06:20		65.01		44		21-Mar-08		0:07:53		70.41		40		1-May-08		0:25:59		70.41		31.5

		21-Mar-08		2:07:10		65.6		49		21-Mar-08		2:06:20		65.01		41		21-Mar-08		2:07:53		69.8		38		1-May-08		2:25:59		69.2		31

		21-Mar-08		4:07:10		65.01		39.5		21-Mar-08		4:06:20		64.4		40		21-Mar-08		4:07:53		68.61		37.5		1-May-08		4:25:59		68		31

		21-Mar-08		6:07:10		65.6		48.5		21-Mar-08		6:06:20		64.4		39		21-Mar-08		6:07:53		69.2		37		1-May-08		6:25:59		70.41		30.5

		21-Mar-08		8:07:10		65.6		37.5		21-Mar-08		8:06:20		65.01		37.5		21-Mar-08		8:07:53		71		33		1-May-08		8:25:59		69.2		30

		21-Mar-08		10:07:10		66.2		47		21-Mar-08		10:06:20		66.2		39		21-Mar-08		10:07:53		71		40		1-May-08		10:25:59		71		30

		21-Mar-08		12:07:10		66.2		42.5		21-Mar-08		12:06:20		66.2		32		21-Mar-08		12:07:53		71		37		1-May-08		12:25:59		72.8		29

		21-Mar-08		14:07:10		66.2		46		21-Mar-08		14:06:20		66.81		30.5		21-Mar-08		14:07:53		70.41		31.5		1-May-08		14:25:59		73.4		28

		21-Mar-08		16:07:10		66.2		34.5		21-Mar-08		16:06:20		66.81		33		21-Mar-08		16:07:53		70.41		35.5		1-May-08		16:25:59		72.8		28

		21-Mar-08		18:07:10		66.2		46.5		21-Mar-08		18:06:20		66.2		36		21-Mar-08		18:07:53		70.41		33.5		1-May-08		18:25:59		73.4		29

		21-Mar-08		20:07:10		65.6		40		21-Mar-08		20:06:20		65.6		37		21-Mar-08		20:07:53		70.41		36.5		1-May-08		20:25:59		73.4		29.5

		21-Mar-08		22:07:10		65.6		39		21-Mar-08		22:06:20		65.01		37.5		21-Mar-08		22:07:53		70.41		35		1-May-08		22:25:59		72.8		29.5

		22-Mar-08		0:07:10		65.6		37		22-Mar-08		0:06:20		65.6		35		22-Mar-08		0:07:53		69.8		33.5		2-May-08		0:25:59		71.6		29.5

		22-Mar-08		2:07:10		65.01		36.5		22-Mar-08		2:06:20		65.6		35.5		22-Mar-08		2:07:53		69.2		33.5		2-May-08		2:25:59		70.41		30

		22-Mar-08		4:07:10		65.01		47		22-Mar-08		4:06:20		65.6		35		22-Mar-08		4:07:53		68.61		34		2-May-08		4:25:59		69.2		30

		22-Mar-08		6:07:10		65.6		46		22-Mar-08		6:06:20		65.6		34.5		22-Mar-08		6:07:53		69.2		33.5		2-May-08		6:25:59		71		30.5

		22-Mar-08		8:07:10		65.6		36		22-Mar-08		8:06:20		65.6		34.5		22-Mar-08		8:07:53		71		32.5		2-May-08		8:25:59		69.8		31.5

		22-Mar-08		10:07:10		66.2		41.5		22-Mar-08		10:06:20		65.6		37		22-Mar-08		10:07:53		70.41		34		2-May-08		10:25:59		72.21		32

		22-Mar-08		12:07:10		66.2		42		22-Mar-08		12:06:20		66.81		33.5		22-Mar-08		12:07:53		70.41		32.5		2-May-08		12:25:59		72.8		30.5

		22-Mar-08		14:07:10		66.81		45		22-Mar-08		14:06:20		66.2		33		22-Mar-08		14:07:53		71		33		2-May-08		14:25:59		73.4		28

		22-Mar-08		16:07:10		66.2		41.5		22-Mar-08		16:06:20		65.6		40		22-Mar-08		16:07:53		71		33		2-May-08		16:25:59		74.01		30

		22-Mar-08		18:07:10		66.2		47		22-Mar-08		18:06:20		65.01		40		22-Mar-08		18:07:53		70.41		34.5		2-May-08		18:25:59		72.8		31

		22-Mar-08		20:07:10		65.6		47		22-Mar-08		20:06:20		66.2		43		22-Mar-08		20:07:53		69.8		39.5		2-May-08		20:25:59		74.01		31.5

		22-Mar-08		22:07:10		65.6		47.5		22-Mar-08		22:06:20		65.01		42.5		22-Mar-08		22:07:53		70.41		38.5		2-May-08		22:25:59		74.01		30.5

		23-Mar-08		0:07:10		65.6		47.5		23-Mar-08		0:06:20		65.6		42		23-Mar-08		0:07:53		71		37		3-May-08		0:25:59		73.4		29.5

		23-Mar-08		2:07:10		65.6		40.5		23-Mar-08		2:06:20		65.01		40		23-Mar-08		2:07:53		70.41		36.5		3-May-08		2:25:59		72.21		30.5

		23-Mar-08		4:07:10		65.6		49		23-Mar-08		4:06:20		65.01		38.5		23-Mar-08		4:07:53		69.2		35		3-May-08		4:25:59		70.41		31.5

		23-Mar-08		6:07:10		65.01		38.5		23-Mar-08		6:06:20		65.6		38		23-Mar-08		6:07:53		69.8		35.5		3-May-08		6:25:59		70.41		32

		23-Mar-08		8:07:10		65.6		46		23-Mar-08		8:06:20		65.01		37.5		23-Mar-08		8:07:53		71		34.5		3-May-08		8:25:59		70.41		33.5

		23-Mar-08		10:07:10		65.6		41.5		23-Mar-08		10:06:20		66.2		40.5		23-Mar-08		10:07:53		70.41		34.5		3-May-08		10:25:59		72.8		34.5

		23-Mar-08		12:07:10		66.2		47		23-Mar-08		12:06:20		66.2		42.5		23-Mar-08		12:07:53		69.8		34.5		3-May-08		12:25:59		73.4		34

		23-Mar-08		14:07:10		66.2		42.5		23-Mar-08		14:06:20		65.6		43		23-Mar-08		14:07:53		70.41		43.5		3-May-08		14:25:59		73.4		35.5

		23-Mar-08		16:07:10		66.2		36		23-Mar-08		16:06:20		65.6		36		23-Mar-08		16:07:53		71		38.5		3-May-08		16:25:59		74.01		35

		23-Mar-08		18:07:10		66.2		43.5		23-Mar-08		18:06:20		66.2		42		23-Mar-08		18:07:53		70.41		40		3-May-08		18:25:59		73.4		36.5

		23-Mar-08		20:07:10		65.6		44		23-Mar-08		20:06:20		65.6		45.5		23-Mar-08		20:07:53		69.8		41.5		3-May-08		20:25:59		74.01		36.5

		23-Mar-08		22:07:10		65.6		48		23-Mar-08		22:06:20		65.01		46.5		23-Mar-08		22:07:53		71		39.5		3-May-08		22:25:59		74.01		35

		24-Mar-08		0:07:10		65.6		47.5		24-Mar-08		0:06:20		65.01		44.5		24-Mar-08		0:07:53		71		37.5		4-May-08		0:25:59		72.21		34.5

		24-Mar-08		2:07:10		65.6		43		24-Mar-08		2:06:20		65.6		41		24-Mar-08		2:07:53		69.8		36		4-May-08		2:25:59		70.41		35

		24-Mar-08		4:07:10		65.6		47.5		24-Mar-08		4:06:20		65.01		39.5		24-Mar-08		4:07:53		68.61		36		4-May-08		4:25:59		69.2		34.5

		24-Mar-08		6:07:10		65.01		47.5		24-Mar-08		6:06:20		64.4		38.5		24-Mar-08		6:07:53		68		35.5		4-May-08		6:25:59		69.2		34.5

		24-Mar-08		8:07:10		65.01		36		24-Mar-08		8:06:20		63.8		36.5		24-Mar-08		8:07:53		66.81		35		4-May-08		8:25:59		69.8		35

		24-Mar-08		10:07:10		65.6		47.5		24-Mar-08		10:06:20		65.6		39		24-Mar-08		10:07:53		69.8		35		4-May-08		10:25:59		71.6		37

		24-Mar-08		12:07:10		65.6		39.5		24-Mar-08		12:06:20		66.2		38		24-Mar-08		12:07:53		70.41		36.5		4-May-08		12:25:59		73.4		37

		24-Mar-08		14:07:10		66.2		43.5		24-Mar-08		14:06:20		65.6		39		24-Mar-08		14:07:53		69.8		39		4-May-08		14:25:59		74.6		38

		24-Mar-08		16:07:10		66.2		47.5		24-Mar-08		16:06:20		65.6		45.5		24-Mar-08		16:07:53		70.41		42		4-May-08		16:25:59		74.01		38

		24-Mar-08		18:07:10		66.2		45.5		24-Mar-08		18:06:20		66.2		50		24-Mar-08		18:07:53		69.8		45		4-May-08		18:25:59		73.4		40.5

		24-Mar-08		20:07:10		65.6		47.5		24-Mar-08		20:06:20		66.2		45.5		24-Mar-08		20:07:53		71		42.5		4-May-08		20:25:59		73.4		40

		24-Mar-08		22:07:10		65.6		43		24-Mar-08		22:06:20		65.6		45		24-Mar-08		22:07:53		71.6		39.5		4-May-08		22:25:59		72.8		39

		25-Mar-08		0:07:10		65.6		42.5		25-Mar-08		0:06:20		65.01		46		25-Mar-08		0:07:53		71		38.5		5-May-08		0:25:59		71.6		38.5

		25-Mar-08		2:07:10		65.6		41		25-Mar-08		2:06:20		65.6		42		25-Mar-08		2:07:53		69.8		37.5		5-May-08		2:25:59		71		38

		25-Mar-08		4:07:10		65.6		46		25-Mar-08		4:06:20		65.6		42.5		25-Mar-08		4:07:53		69.2		37		5-May-08		4:25:59		69.8		37.5

		25-Mar-08		6:07:10		65.6		39.5		25-Mar-08		6:06:20		65.6		41		25-Mar-08		6:07:53		69.8		37.5		5-May-08		6:25:59		68.61		37.5

		25-Mar-08		8:07:10		65.6		40		25-Mar-08		8:06:20		65.6		41.5		25-Mar-08		8:07:53		71.6		37		5-May-08		8:25:59		68.61		38

		25-Mar-08		10:07:10		66.2		44.5		25-Mar-08		10:06:20		66.2		49		25-Mar-08		10:07:53		70.41		44.5		5-May-08		10:25:59		69.8		40.5

		25-Mar-08		12:07:10		66.81		46.5		25-Mar-08		12:06:20		66.2		53.5		25-Mar-08		12:07:53		71.6		38.5		5-May-08		12:25:59		71.6		41.5

		25-Mar-08		14:07:10		66.81		47.5		25-Mar-08		14:06:20		66.2		59.5		25-Mar-08		14:07:53		71		46		5-May-08		14:25:59		72.8		41.5

		25-Mar-08		16:07:10		66.81		48.5		25-Mar-08		16:06:20		65.6		53.5		25-Mar-08		16:07:53		71		49		5-May-08		16:25:59		73.4		40.5

		25-Mar-08		18:07:10		66.2		47		25-Mar-08		18:06:20		65.6		57.5		25-Mar-08		18:07:53		70.41		50.5		5-May-08		18:25:59		73.4		39.5

		25-Mar-08		20:07:10		66.2		45.5		25-Mar-08		20:06:20		65.6		55		25-Mar-08		20:07:53		70.41		51		5-May-08		20:25:59		72.8		39

		25-Mar-08		22:07:10		65.6		45		25-Mar-08		22:06:20		65.6		51		25-Mar-08		22:07:53		70.41		46		5-May-08		22:25:59		72.21		38

		26-Mar-08		0:07:10		65.6		44		26-Mar-08		0:06:20		65.6		49		26-Mar-08		0:07:53		69.8		42.5		6-May-08		0:25:59		71.6		37.5

		26-Mar-08		2:07:10		65.6		43		26-Mar-08		2:06:20		65.6		47.5		26-Mar-08		2:07:53		69.8		40.5		6-May-08		2:25:59		70.41		38

		26-Mar-08		4:07:10		65.6		42		26-Mar-08		4:06:20		65.6		45.5		26-Mar-08		4:07:53		69.8		39		6-May-08		4:25:59		69.2		37.5

		26-Mar-08		6:07:10		65.6		43		26-Mar-08		6:06:20		64.4		49.5		26-Mar-08		6:07:53		70.41		40.5		6-May-08		6:25:59		69.8		37.5

		26-Mar-08		8:07:10		66.2		44		26-Mar-08		8:06:20		65.6		50.5		26-Mar-08		8:07:53		71.6		41.5		6-May-08		8:25:59		69.8		40

		26-Mar-08		10:07:10		66.2		45		26-Mar-08		10:06:20		65.01		53		26-Mar-08		10:07:53		71		45.5		6-May-08		10:25:59		72.21		41.5

		26-Mar-08		12:07:10		66.2		46		26-Mar-08		12:06:20		65.6		53.5		26-Mar-08		12:07:53		71		49		6-May-08		12:25:59		73.4		43.5

		26-Mar-08		14:07:10		66.81		45.5		26-Mar-08		14:06:20		65.6		53.5		26-Mar-08		14:07:53		71		48.5		6-May-08		14:25:59		73.4		43

		26-Mar-08		16:07:10		66.2		44		26-Mar-08		16:06:20		66.2		50.5		26-Mar-08		16:07:53		70.41		39.5		6-May-08		16:25:59		74.01		43

		26-Mar-08		18:07:10		65.6		43		26-Mar-08		18:06:20		66.2		45		26-Mar-08		18:07:53		70.41		48		6-May-08		18:25:59		74.01		40

		26-Mar-08		20:07:10		65.6		41		26-Mar-08		20:06:20		65.6		41.5		26-Mar-08		20:07:53		70.41		43.5		6-May-08		20:25:59		73.4		40

		26-Mar-08		22:07:10		65.6		40.5		26-Mar-08		22:06:20		64.4		44		26-Mar-08		22:07:53		72.21		37.5		6-May-08		22:25:59		72.21		39.5

		27-Mar-08		0:07:10		65.6		41		27-Mar-08		0:06:20		65.6		43		27-Mar-08		0:07:53		71.6		36.5		7-May-08		0:25:59		71.6		40

		27-Mar-08		2:07:10		65.01		39.5		27-Mar-08		2:06:20		64.4		42.5		27-Mar-08		2:07:53		70.41		36		7-May-08		2:25:59		71		40

		27-Mar-08		4:07:10		65.01		38		27-Mar-08		4:06:20		63.8		41.5		27-Mar-08		4:07:53		69.8		35		7-May-08		4:25:59		69.8		40

		27-Mar-08		6:07:10		65.01		37		27-Mar-08		6:06:20		63.8		40.5		27-Mar-08		6:07:53		70.41		35		7-May-08		6:25:59		71		40.5

		27-Mar-08		8:07:10		65.6		37		27-Mar-08		8:06:20		63.8		39		27-Mar-08		8:07:53		71.6		34.5		7-May-08		8:25:59		71.6		41.5

		27-Mar-08		10:07:10		65.6		40		27-Mar-08		10:06:20		66.2		41		27-Mar-08		10:07:53		71.6		35		7-May-08		10:25:59		73.4		41

		27-Mar-08		12:07:10		65.6		39		27-Mar-08		12:06:20		69.2		36.5		27-Mar-08		12:07:53		71		42		7-May-08		12:25:59		73.4		43

		27-Mar-08		14:07:10		66.2		40		27-Mar-08		14:06:20		69.2		37		27-Mar-08		14:07:53		71		35.5		7-May-08		14:25:59		73.4		45.5

		27-Mar-08		16:07:10		65.6		43		27-Mar-08		16:06:20		68.61		41.5		27-Mar-08		16:07:53		70.41		37		7-May-08		16:25:59		73.4		44.5

		27-Mar-08		18:07:10		65.6		41		27-Mar-08		18:06:20		68.61		38		27-Mar-08		18:07:53		70.41		42		7-May-08		18:25:59		73.4		43

		27-Mar-08		20:07:10		65.6		40		27-Mar-08		20:06:20		68		38.5		27-Mar-08		20:07:53		72.8		36		7-May-08		20:25:59		74.01		42

		27-Mar-08		22:07:10		65.6		37.5		27-Mar-08		22:06:20		66.81		36		27-Mar-08		22:07:53		74.6		32		7-May-08		22:25:59		74.01		37.5

		28-Mar-08		0:07:10		65.01		36.5		28-Mar-08		0:06:20		65.6		36.5		28-Mar-08		0:07:53		71.6		32.5		8-May-08		0:25:59		73.4		37

		28-Mar-08		2:07:10		65.01		35		28-Mar-08		2:06:20		64.4		35.5		28-Mar-08		2:07:53		69.8		32		8-May-08		2:25:59		71.6		37

		28-Mar-08		4:07:10		65.01		33.5		28-Mar-08		4:06:20		63.8		35		28-Mar-08		4:07:53		68.61		31.5		8-May-08		4:25:59		70.41		37.5

		28-Mar-08		6:07:10		65.01		33		28-Mar-08		6:06:20		63.21		35		28-Mar-08		6:07:53		69.2		32		8-May-08		6:25:59		73.4		35.5

		28-Mar-08		8:07:10		65.6		32		28-Mar-08		8:06:20		64.4		34		28-Mar-08		8:07:53		70.41		32		8-May-08		8:25:59		72.8		35.5

		28-Mar-08		10:07:10		65.6		30.5		28-Mar-08		10:06:20		66.2		31		28-Mar-08		10:07:53		71		33		8-May-08		10:25:59		72.8		37.5

		28-Mar-08		12:07:10		65.6		28		28-Mar-08		12:06:20		68.61		27		28-Mar-08		12:07:53		71		29.5		8-May-08		12:25:59		72.8		38.5

		28-Mar-08		14:07:10		66.2		28		28-Mar-08		14:06:20		69.2		25.5		28-Mar-08		14:07:53		70.41		32.5		8-May-08		14:25:59		73.4		39.5

		28-Mar-08		16:07:10		66.2		23.5		28-Mar-08		16:06:20		69.2		22		28-Mar-08		16:07:53		70.41		28.5		8-May-08		16:25:59		74.01		39.5

		28-Mar-08		18:07:10		65.6		24.5		28-Mar-08		18:06:20		69.2		21		28-Mar-08		18:07:53		71		26.5		8-May-08		18:25:59		73.4		39

		28-Mar-08		20:07:10		65.6		26		28-Mar-08		20:06:20		68.61		23.5		28-Mar-08		20:07:53		71.6		26.5		8-May-08		20:25:59		74.01		39.5

		28-Mar-08		22:07:10		65.01		35		28-Mar-08		22:06:20		67.4		34		28-Mar-08		22:07:53		74.6		28.5		8-May-08		22:25:59		74.01		37.5

		29-Mar-08		0:07:10		65.01		35		29-Mar-08		0:06:20		65.6		35.5		29-Mar-08		0:07:53		72.8		29.5		9-May-08		0:25:59		72.8		37

		29-Mar-08		2:07:10		65.01		36		29-Mar-08		2:06:20		65.01		37.5		29-Mar-08		2:07:53		71		30.5		9-May-08		2:25:59		71		36.5

		29-Mar-08		4:07:10		65.01		35.5		29-Mar-08		4:06:20		64.4		37.5		29-Mar-08		4:07:53		69.8		31		9-May-08		4:25:59		69.2		36.5

		29-Mar-08		6:07:10		65.6		34.5		29-Mar-08		6:06:20		64.4		37		29-Mar-08		6:07:53		70.41		33		9-May-08		6:25:59		72.8		35.5

		29-Mar-08		8:07:10		65.01		36.5		29-Mar-08		8:06:20		65.6		37.5		29-Mar-08		8:07:53		70.41		35		9-May-08		8:25:59		73.4		36.5

		29-Mar-08		10:07:10		65.6		32		29-Mar-08		10:06:20		68		32.5		29-Mar-08		10:07:53		70.41		35.5		9-May-08		10:25:59		73.4		38.5

		29-Mar-08		12:07:10		64.4		39		29-Mar-08		12:06:20		69.2		32		29-Mar-08		12:07:53		71		36.5		9-May-08		12:25:59		72.21		41

		29-Mar-08		14:07:10		66.81		38.5		29-Mar-08		14:06:20		68		38		29-Mar-08		14:07:53		71		44		9-May-08		14:25:59		72.21		41.5

		29-Mar-08		16:07:10		66.81		43		29-Mar-08		16:06:20		65.6		51		29-Mar-08		16:07:53		71		43		9-May-08		16:25:59		73.4		39.5

		29-Mar-08		18:07:10		66.81		44.5		29-Mar-08		18:06:20		64.4		55.5		29-Mar-08		18:07:53		72.21		42.5		9-May-08		18:25:59		72.8		39

		29-Mar-08		20:07:10		66.81		44.5		29-Mar-08		20:06:20		65.01		55		29-Mar-08		20:07:53		71		45.5		9-May-08		20:25:59		73.4		38.5

		29-Mar-08		22:07:10		66.81		45		29-Mar-08		22:06:20		64.4		57		29-Mar-08		22:07:53		70.41		44		9-May-08		22:25:59		72.8		37.5

		30-Mar-08		0:07:10		66.81		45		30-Mar-08		0:06:20		65.01		56		30-Mar-08		0:07:53		70.41		42.5		10-May-08		0:25:59		72.21		36

		30-Mar-08		2:07:10		66.81		44.5		30-Mar-08		2:06:20		65.01		54.5		30-Mar-08		2:07:53		69.8		43		10-May-08		2:25:59		72.21		35

		30-Mar-08		4:07:10		66.81		43.5		30-Mar-08		4:06:20		64.4		53.5		30-Mar-08		4:07:53		69.8		42		10-May-08		4:25:59		72.21		35

		30-Mar-08		6:07:10		66.81		41.5		30-Mar-08		6:06:20		65.01		50		30-Mar-08		6:07:53		69.8		41.5		10-May-08		6:25:59		72.21		34

		30-Mar-08		8:07:10		67.4		40.5		30-Mar-08		8:06:20		65.01		47.5		30-Mar-08		8:07:53		69.8		40		10-May-08		8:25:59		71		36

		30-Mar-08		10:07:10		67.4		39.5		30-Mar-08		10:06:20		64.4		47.5		30-Mar-08		10:07:53		69.8		39.5		10-May-08		10:25:59		73.4		36

		30-Mar-08		12:07:10		68		40.5		30-Mar-08		12:06:20		64.4		48		30-Mar-08		12:07:53		69.8		41		10-May-08		12:25:59		74.6		34.5

		30-Mar-08		14:07:10		67.4		42		30-Mar-08		14:06:20		65.01		51		30-Mar-08		14:07:53		70.41		37.5		10-May-08		14:25:59		75.2		33.5

		30-Mar-08		16:07:10		67.4		40.5		30-Mar-08		16:06:20		65.01		46.5		30-Mar-08		16:07:53		70.41		39		10-May-08		16:25:59		75.2		35.5

		30-Mar-08		18:07:10		67.4		39.5		30-Mar-08		18:06:20		65.01		45.5		30-Mar-08		18:07:53		69.8		43		10-May-08		18:25:59		75.2		35.5

		30-Mar-08		20:07:10		68		37		30-Mar-08		20:06:20		64.4		43		30-Mar-08		20:07:53		70.41		39.5		10-May-08		20:25:59		74.6		36

		30-Mar-08		22:07:10		68		33		30-Mar-08		22:06:20		64.4		37		30-Mar-08		22:07:53		71		35.5		10-May-08		22:25:59		74.6		34.5

		31-Mar-08		0:07:10		68		32		31-Mar-08		0:06:20		65.01		35		31-Mar-08		0:07:53		69.8		33		11-May-08		0:25:59		74.01		34

		31-Mar-08		2:07:10		67.4		32		31-Mar-08		2:06:20		64.4		35.5		31-Mar-08		2:07:53		69.8		32.5		11-May-08		2:25:59		72.21		34

		31-Mar-08		4:07:10		67.4		32.5		31-Mar-08		4:06:20		63.8		37		31-Mar-08		4:07:53		68.61		32.5		11-May-08		4:25:59		71.6		34

		31-Mar-08		6:07:10		68		32.5		31-Mar-08		6:06:20		63.21		38.5		31-Mar-08		6:07:53		68		33		11-May-08		6:25:59		72.21		34

		31-Mar-08		8:07:10		67.4		31		31-Mar-08		8:06:20		63.8		36		31-Mar-08		8:07:53		68		32.5		11-May-08		8:25:59		72.21		34.5

		31-Mar-08		10:07:10		67.4		28.5		31-Mar-08		10:06:20		64.4		32		31-Mar-08		10:07:53		69.2		31		11-May-08		10:25:59		72.8		35

		31-Mar-08		12:07:10		67.4		25.5		31-Mar-08		12:06:20		64.4		29.5		31-Mar-08		12:07:53		69.8		29.5		11-May-08		12:25:59		74.01		35

		31-Mar-08		14:07:10		68		23.5		31-Mar-08		14:06:20		65.01		25.5		31-Mar-08		14:07:53		69.8		27.5		11-May-08		14:25:59		75.81		35.5

		31-Mar-08		16:07:10		67.4		24		31-Mar-08		16:06:20		65.01		26		31-Mar-08		16:07:53		69.2		28		11-May-08		16:25:59		77		34.5

		31-Mar-08		18:07:10		67.4		26.5		31-Mar-08		18:06:20		65.01		29.5		31-Mar-08		18:07:53		69.8		28.5		11-May-08		18:25:59		78.2		35

		31-Mar-08		20:07:10		68		26.5		31-Mar-08		20:06:20		64.4		30		31-Mar-08		20:07:53		71		28.5		11-May-08		20:25:59		77.61		36

		31-Mar-08		22:07:10		67.4		27		31-Mar-08		22:06:20		64.4		30.5		31-Mar-08		22:07:53		70.41		27.5		11-May-08		22:25:59		75.81		37

		1-Apr-08		0:07:10		67.4		27.5		1-Apr-08		0:06:20		64.4		31.5		1-Apr-08		0:07:53		69.2		27.5		12-May-08		0:25:59		74.01		37.5

		1-Apr-08		2:07:10		67.4		28		1-Apr-08		2:06:20		63.8		32.5		1-Apr-08		2:07:53		68.61		28		12-May-08		2:25:59		72.8		38

		1-Apr-08		4:07:10		67.4		28		1-Apr-08		4:06:20		62.6		32.5		1-Apr-08		4:07:53		67.4		28.5		12-May-08		4:25:59		72.21		38

		1-Apr-08		6:07:10		67.4		28.5		1-Apr-08		6:06:20		62		34		1-Apr-08		6:07:53		66.81		29.5		12-May-08		6:25:59		72.21		37.5

		1-Apr-08		8:07:10		68		28.5		1-Apr-08		8:06:20		63.21		34		1-Apr-08		8:07:53		69.8		29.5		12-May-08		8:25:59		72.21		38.5

		1-Apr-08		10:07:10		67.4		30.5		1-Apr-08		10:06:20		65.01		34.5		1-Apr-08		10:07:53		71		31.5		12-May-08		10:25:59		71.6		40

		1-Apr-08		12:07:10		66.81		27		1-Apr-08		12:06:20		65.6		30		1-Apr-08		12:07:53		71		34		12-May-08		12:25:59		72.8		41

		1-Apr-08		14:07:10		66.81		30		1-Apr-08		14:06:20		66.2		31		1-Apr-08		14:07:53		71		35		12-May-08		14:25:59		74.01		36

		1-Apr-08		16:07:10		66.81		31		1-Apr-08		16:06:20		65.6		34		1-Apr-08		16:07:53		71		36.5		12-May-08		16:25:59		74.6		32

		1-Apr-08		18:07:10		66.81		29.5		1-Apr-08		18:06:20		65.01		32.5		1-Apr-08		18:07:53		71		33.5		12-May-08		18:25:59		76.4		31

		1-Apr-08		20:07:10		67.4		30.5		1-Apr-08		20:06:20		65.01		32.5		1-Apr-08		20:07:53		70.41		32		12-May-08		20:25:59		75.81		31.5

		1-Apr-08		22:07:10		67.4		29		1-Apr-08		22:06:20		64.4		32		1-Apr-08		22:07:53		70.41		32		12-May-08		22:25:59		74.01		31

		2-Apr-08		0:07:10		66.81		33		2-Apr-08		0:06:20		65.01		37		2-Apr-08		0:07:53		70.41		31		13-May-08		0:25:59		72.8		31

		2-Apr-08		2:07:10		66.81		34		2-Apr-08		2:06:20		64.4		38.5		2-Apr-08		2:07:53		70.41		31		13-May-08		2:25:59		71.6		31

		2-Apr-08		4:07:10		66.81		33		2-Apr-08		4:06:20		64.4		38		2-Apr-08		4:07:53		70.41		32		13-May-08		4:25:59		71.6		31

		2-Apr-08		6:07:10		66.81		31.5		2-Apr-08		6:06:20		65.01		35		2-Apr-08		6:07:53		71		32		13-May-08		6:25:59		71.6		30

		2-Apr-08		8:07:10		66.81		33.5		2-Apr-08		8:06:20		65.01		37.5		2-Apr-08		8:07:53		71.6		33.5		13-May-08		8:25:59		71.6		30

		2-Apr-08		10:07:10		66.81		33.5		2-Apr-08		10:06:20		66.2		35.5		2-Apr-08		10:07:53		70.41		35		13-May-08		10:25:59		74.01		29.5

		2-Apr-08		12:07:10		66.81		33		2-Apr-08		12:06:20		66.81		33		2-Apr-08		12:07:53		71		36		13-May-08		12:25:59		74.01		29.5

		2-Apr-08		14:07:10		66.81		39		2-Apr-08		14:06:20		67.4		42.5		2-Apr-08		14:07:53		71.6		34.5		13-May-08		14:25:59		75.2		29.5

		2-Apr-08		16:07:10		67.4		34		2-Apr-08		16:06:20		67.4		31.5		2-Apr-08		16:07:53		71.6		36.5		13-May-08		16:25:59		75.2		30

		2-Apr-08		18:07:10		66.81		35		2-Apr-08		18:06:20		66.2		36		2-Apr-08		18:07:53		71		32.5		13-May-08		18:25:59		75.2		30

		2-Apr-08		20:07:10		67.4		36.5		2-Apr-08		20:06:20		66.81		37		2-Apr-08		20:07:53		71		37		13-May-08		20:25:59		74.6		30.5

		2-Apr-08		22:07:10		66.81		37.5		2-Apr-08		22:06:20		65.6		41.5		2-Apr-08		22:07:53		75.2		33		13-May-08		22:25:59		74.01		29.5

		3-Apr-08		0:07:10		66.81		37.5		3-Apr-08		0:06:20		66.2		42		3-Apr-08		0:07:53		71.6		34		14-May-08		0:25:59		73.4		29.5

		3-Apr-08		2:07:10		66.81		36.5		3-Apr-08		2:06:20		65.6		40.5		3-Apr-08		2:07:53		70.41		34.5		14-May-08		2:25:59		72.21		30

		3-Apr-08		4:07:10		67.4		34.5		3-Apr-08		4:06:20		64.4		38.5		3-Apr-08		4:07:53		69.2		33.5		14-May-08		4:25:59		71.6		30.5

		3-Apr-08		6:07:10		67.4		35.5		3-Apr-08		6:06:20		64.4		38		3-Apr-08		6:07:53		69.2		33		14-May-08		6:25:59		72.21		31

		3-Apr-08		8:07:10		67.4		35.5		3-Apr-08		8:06:20		65.01		38.5		3-Apr-08		8:07:53		71		31		14-May-08		8:25:59		71.6		32.5

		3-Apr-08		10:07:10		65.01		39		3-Apr-08		10:06:20		66.2		41		3-Apr-08		10:07:53		71.6		34.5		14-May-08		10:25:59		74.6		33

		3-Apr-08		12:07:10		66.81		38		3-Apr-08		12:06:20		66.81		39		3-Apr-08		12:07:53		71		34.5		14-May-08		12:25:59		74.01		32

		3-Apr-08		14:07:10		66.81		40		3-Apr-08		14:06:20		67.4		41.5		3-Apr-08		14:07:53		71		38		14-May-08		14:25:59		74.01		30.5

		3-Apr-08		16:07:10		66.81		38		3-Apr-08		16:06:20		66.2		40		3-Apr-08		16:07:53		71.6		42.5		14-May-08		16:25:59		74.6		29

		3-Apr-08		18:07:10		66.81		35.5		3-Apr-08		18:06:20		66.81		36		3-Apr-08		18:07:53		71		32		14-May-08		18:25:59		74.01		29

		3-Apr-08		20:07:10		67.4		35.5		3-Apr-08		20:06:20		66.2		37.5		3-Apr-08		20:07:53		71		32.5		14-May-08		20:25:59		74.6		33

		3-Apr-08		22:07:10		67.4		34.5		3-Apr-08		22:06:20		65.6		37		3-Apr-08		22:07:53		72.21		34		14-May-08		22:25:59		75.2		33

		4-Apr-08		0:07:10		67.4		34.5		4-Apr-08		0:06:20		66.2		37.5		4-Apr-08		0:07:53		72.21		33.5		15-May-08		0:25:59		74.6		33.5

		4-Apr-08		2:07:10		66.81		34		4-Apr-08		2:06:20		65.6		36.5		4-Apr-08		2:07:53		70.41		32.5		15-May-08		2:25:59		74.01		34

		4-Apr-08		4:07:10		66.81		35		4-Apr-08		4:06:20		65.01		38		4-Apr-08		4:07:53		69.8		32		15-May-08		4:25:59		73.4		35

		4-Apr-08		6:07:10		66.81		37		4-Apr-08		6:06:20		65.6		40.5		4-Apr-08		6:07:53		69.8		34		15-May-08		6:25:59		73.4		36.5

		4-Apr-08		8:07:10		67.4		37.5		4-Apr-08		8:06:20		66.81		42		4-Apr-08		8:07:53		72.21		33.5		15-May-08		8:25:59		73.4		39

		4-Apr-08		10:07:10		68		38.5		4-Apr-08		10:06:20		66.81		42		4-Apr-08		10:07:53		71.6		36		15-May-08		10:25:59		74.6		40

		4-Apr-08		12:07:10		74.6		35		4-Apr-08		12:06:20		74.6		35.5		4-Apr-08		12:07:53		71.6		42.5		15-May-08		12:25:59		74.01		41.5

		4-Apr-08		14:07:10		66.81		38.5		4-Apr-08		14:06:20		67.4		38.5		4-Apr-08		14:07:53		71.6		45		15-May-08		14:25:59		74.01		38.5

		4-Apr-08		16:07:10		66.81		42		4-Apr-08		16:06:20		66.81		45		4-Apr-08		16:07:53		71		45		15-May-08		16:25:59		74.01		38.5

		4-Apr-08		18:07:10		66.81		40.5		4-Apr-08		18:06:20		66.81		43.5		4-Apr-08		18:07:53		71.6		44		15-May-08		18:25:59		73.4		38.5

		4-Apr-08		20:07:10		66.81		45.5		4-Apr-08		20:06:20		65.6		44		4-Apr-08		20:07:53		71.6		43		15-May-08		20:25:59		75.2		38.5

		4-Apr-08		22:07:10		66.81		45.5		4-Apr-08		22:06:20		66.2		43		4-Apr-08		22:07:53		71.6		35.5		15-May-08		22:25:59		76.4		36

		5-Apr-08		0:07:10		67.4		45		5-Apr-08		0:06:20		65.6		42		5-Apr-08		0:07:53		71		39.5		16-May-08		0:25:59		76.4		35.5

		5-Apr-08		2:07:10		66.81		46.5		5-Apr-08		2:06:20		65.01		43.5		5-Apr-08		2:07:53		70.41		37.5		16-May-08		2:25:59		75.81		35.5

		5-Apr-08		4:07:10		66.81		46.5		5-Apr-08		4:06:20		65.01		44.5		5-Apr-08		4:07:53		69.8		38		16-May-08		4:25:59		75.2		35.5

		5-Apr-08		6:07:10		66.81		46		5-Apr-08		6:06:20		65.01		43		5-Apr-08		6:07:53		70.41		39		16-May-08		6:25:59		75.2		35

		5-Apr-08		8:07:10		68		43.5		5-Apr-08		8:06:20		65.6		43.5		5-Apr-08		8:07:53		71		41		16-May-08		8:25:59		74.6		36.5

		5-Apr-08		10:07:10		67.4		47		5-Apr-08		10:06:20		67.4		40		5-Apr-08		10:07:53		70.41		39		16-May-08		10:25:59		74.01		38.5

		5-Apr-08		12:07:10		67.4		45.5		5-Apr-08		12:06:20		67.4		38.5		5-Apr-08		12:07:53		71		44		16-May-08		12:25:59		73.4		40.5

		5-Apr-08		14:07:10		66.81		47		5-Apr-08		14:06:20		68.61		40.5		5-Apr-08		14:07:53		74.6		35.5		16-May-08		14:25:59		72.8		40.5

		5-Apr-08		16:07:10		66.81		46		5-Apr-08		16:06:20		67.4		43		5-Apr-08		16:07:53		71.6		45.5		16-May-08		16:25:59		73.4		40.5

		5-Apr-08		18:07:10		66.81		46.5		5-Apr-08		18:06:20		66.81		40		5-Apr-08		18:07:53		73.4		40		16-May-08		18:25:59		74.01		40.5

		5-Apr-08		20:07:10		67.4		46.5		5-Apr-08		20:06:20		67.4		40.5		5-Apr-08		20:07:53		75.2		37		16-May-08		20:25:59		75.2		40.5

		5-Apr-08		22:07:10		66.81		46		5-Apr-08		22:06:20		67.4		36.5		5-Apr-08		22:07:53		73.4		36.5		16-May-08		22:25:59		77		40

		6-Apr-08		0:07:10		66.81		46		6-Apr-08		0:06:20		66.81		37		6-Apr-08		0:07:53		71		36		17-May-08		0:25:59		76.4		39

		6-Apr-08		2:07:10		66.81		46.5		6-Apr-08		2:06:20		65.6		37.5		6-Apr-08		2:07:53		69.8		35.5		17-May-08		2:25:59		75.2		39

		6-Apr-08		4:07:10		66.81		47		6-Apr-08		4:06:20		65.01		38		6-Apr-08		4:07:53		68.61		36		17-May-08		4:25:59		74.6		39

		6-Apr-08		6:07:10		67.4		46		6-Apr-08		6:06:20		65.01		37.5		6-Apr-08		6:07:53		67.4		36.5		17-May-08		6:25:59		74.6		40

		6-Apr-08		8:07:10		67.4		47		6-Apr-08		8:06:20		65.01		37.5		6-Apr-08		8:07:53		67.4		36.5		17-May-08		8:25:59		74.6		41.5

		6-Apr-08		10:07:10		67.4		45		6-Apr-08		10:06:20		66.81		37		6-Apr-08		10:07:53		69.2		36.5		17-May-08		10:25:59		74.01		43

		6-Apr-08		12:07:10		67.4		46		6-Apr-08		12:06:20		68		35.5		6-Apr-08		12:07:53		70.41		36.5		17-May-08		12:25:59		73.4		46.5

		6-Apr-08		14:07:10		67.4		46		6-Apr-08		14:06:20		68		37		6-Apr-08		14:07:53		70.41		39		17-May-08		14:25:59		74.01		45.5

		6-Apr-08		16:07:10		68		45.5		6-Apr-08		16:06:20		68		39		6-Apr-08		16:07:53		70.41		40.5		17-May-08		16:25:59		74.01		45

		6-Apr-08		18:07:10		67.4		46.5		6-Apr-08		18:06:20		67.4		38.5		6-Apr-08		18:07:53		71		40		17-May-08		18:25:59		73.4		42.5

		6-Apr-08		20:07:10		68		45.5		6-Apr-08		20:06:20		67.4		39.5		6-Apr-08		20:07:53		72.21		38		17-May-08		20:25:59		75.2		42.5

		6-Apr-08		22:07:10		67.4		43.5		6-Apr-08		22:06:20		67.4		39.5		6-Apr-08		22:07:53		71.6		37		17-May-08		22:25:59		75.81		40

		7-Apr-08		0:07:10		67.4		44		7-Apr-08		0:06:20		66.81		39		7-Apr-08		0:07:53		71		36.5		18-May-08		0:25:59		75.2		39.5

		7-Apr-08		2:07:10		68		46		7-Apr-08		2:06:20		66.2		37.5		7-Apr-08		2:07:53		69.8		36		18-May-08		2:25:59		74.6		40

		7-Apr-08		4:07:10		67.4		45		7-Apr-08		4:06:20		65.6		38		7-Apr-08		4:07:53		69.2		36.5		18-May-08		4:25:59		73.4		40

		7-Apr-08		6:07:10		67.4		45.5		7-Apr-08		6:06:20		65.6		38		7-Apr-08		6:07:53		68.61		37		18-May-08		6:25:59		73.4		39.5

		7-Apr-08		8:07:10		67.4		46.5		7-Apr-08		8:06:20		65.6		39		7-Apr-08		8:07:53		68		37		18-May-08		8:25:59		74.01		40.5

		7-Apr-08		10:07:10		67.4		46		7-Apr-08		10:06:20		66.81		40		7-Apr-08		10:07:53		69.8		37.5		18-May-08		10:25:59		75.81		41.5

		7-Apr-08		12:07:10		68		45		7-Apr-08		12:06:20		66.81		44		7-Apr-08		12:07:53		69.8		39		18-May-08		12:25:59		77.61		42

		7-Apr-08		14:07:10		67.4		45		7-Apr-08		14:06:20		67.4		36		7-Apr-08		14:07:53		71		37		18-May-08		14:25:59		79.41		43

		7-Apr-08		16:07:10		67.4		45.5		7-Apr-08		16:06:20		66.81		35.5		7-Apr-08		16:07:53		71.6		35.5		18-May-08		16:25:59		79.41		41.5

		7-Apr-08		18:07:10		67.4		45.5		7-Apr-08		18:06:20		67.4		33		7-Apr-08		18:07:53		72.21		34.5		18-May-08		18:25:59		78.2		41.5

		7-Apr-08		20:07:10		67.4		44.5		7-Apr-08		20:06:20		66.81		31.5		7-Apr-08		20:07:53		71.6		33		18-May-08		20:25:59		77.61		41

		7-Apr-08		22:07:10		68		46		7-Apr-08		22:06:20		67.4		32.5		7-Apr-08		22:07:53		71		33		18-May-08		22:25:59		76.4		40

		8-Apr-08		0:07:10		67.4		44.5		8-Apr-08		0:06:20		66.81		34		8-Apr-08		0:07:53		69.8		33		19-May-08		0:25:59		74.6		39.5

		8-Apr-08		2:07:10		67.4		46.5		8-Apr-08		2:06:20		66.2		35.5		8-Apr-08		2:07:53		69.2		34		19-May-08		2:25:59		73.4		39

		8-Apr-08		4:07:10		67.4		45.5		8-Apr-08		4:06:20		65.6		35.5		8-Apr-08		4:07:53		68		34.5		19-May-08		4:25:59		72.21		39

		8-Apr-08		6:07:10		67.4		46		8-Apr-08		6:06:20		65.01		35		8-Apr-08		6:07:53		68		35		19-May-08		6:25:59		72.21		39.5

		8-Apr-08		8:07:10		67.4		46.5		8-Apr-08		8:06:20		66.2		35		8-Apr-08		8:07:53		71.6		35		19-May-08		8:25:59		72.21		40

		8-Apr-08		10:07:10		67.4		45		8-Apr-08		10:06:20		68		31.5		8-Apr-08		10:07:53		71.6		33.5		19-May-08		10:25:59		72.8		41.5

		8-Apr-08		12:07:10		66.81		46.5		8-Apr-08		12:06:20		68		29.5		8-Apr-08		12:07:53		71.6		34.5		19-May-08		12:25:59		74.6		41.5

		8-Apr-08		14:07:10		66.81		47		8-Apr-08		14:06:20		67.4		28.5		8-Apr-08		14:07:53		71		34.5		19-May-08		14:25:59		75.81		42

		8-Apr-08		16:07:10		66.81		46.5		8-Apr-08		16:06:20		67.4		35		8-Apr-08		16:07:53		71		37		19-May-08		16:25:59		77		41.5

		8-Apr-08		18:07:10		66.81		46		8-Apr-08		18:06:20		66.81		33		8-Apr-08		18:07:53		71.6		35		19-May-08		18:25:59		77.61		40

		8-Apr-08		20:07:10		66.81		46.5		8-Apr-08		20:06:20		66.81		38.5		8-Apr-08		20:07:53		71		34.5		19-May-08		20:25:59		77		39.5

		8-Apr-08		22:07:10		67.4		47		8-Apr-08		22:06:20		66.2		34		8-Apr-08		22:07:53		71.6		37.5		19-May-08		22:25:59		74.6		39.5

		9-Apr-08		0:07:10		66.81		45.5		9-Apr-08		0:06:20		66.2		38		9-Apr-08		0:07:53		71		35.5		20-May-08		0:25:59		73.4		40

		9-Apr-08		2:07:10		66.81		48		9-Apr-08		2:06:20		66.2		35.5		9-Apr-08		2:07:53		70.41		35		20-May-08		2:25:59		72.21		40

		9-Apr-08		4:07:10		66.81		47.5		9-Apr-08		4:06:20		66.2		36		9-Apr-08		4:07:53		69.8		34.5		20-May-08		4:25:59		72.21		40

		9-Apr-08		6:07:10		66.81		44		9-Apr-08		6:06:20		66.2		37		9-Apr-08		6:07:53		69.8		35.5		20-May-08		6:25:59		72.21		40.5

		9-Apr-08		8:07:10		66.81		47.5		9-Apr-08		8:06:20		66.81		37		9-Apr-08		8:07:53		71		38		20-May-08		8:25:59		71.6		42

		9-Apr-08		10:07:10		66.81		46		9-Apr-08		10:06:20		67.4		34		9-Apr-08		10:07:53		71		34.5		20-May-08		10:25:59		73.4		42.5

		9-Apr-08		12:07:10		66.81		45		9-Apr-08		12:06:20		68		32		9-Apr-08		12:07:53		71		38.5		20-May-08		12:25:59		74.01		43.5

		9-Apr-08		14:07:10		66.81		45		9-Apr-08		14:06:20		68.61		29.5		9-Apr-08		14:07:53		70.41		38.5		20-May-08		14:25:59		74.01		44.5

		9-Apr-08		16:07:10		66.81		47		9-Apr-08		16:06:20		67.4		36		9-Apr-08		16:07:53		71		41.5		20-May-08		16:25:59		74.6		44

		9-Apr-08		18:07:10		66.81		46.5		9-Apr-08		18:06:20		68		34		9-Apr-08		18:07:53		71.6		39.5		20-May-08		18:25:59		74.01		43.5

		9-Apr-08		20:07:10		67.4		47		9-Apr-08		20:06:20		67.4		33.5		9-Apr-08		20:07:53		75.2		35		20-May-08		20:25:59		74.6		43

		9-Apr-08		22:07:10		66.81		47		9-Apr-08		22:06:20		66.81		34.5		9-Apr-08		22:07:53		72.8		34.5		20-May-08		22:25:59		74.01		41

		10-Apr-08		0:07:10		66.81		47.5		10-Apr-08		0:06:20		66.2		33.5		10-Apr-08		0:07:53		70.41		33.5		21-May-08		0:25:59		72.8		41

		10-Apr-08		2:07:10		66.81		47		10-Apr-08		2:06:20		65.6		34.5		10-Apr-08		2:07:53		69.8		33		21-May-08		2:25:59		72.21		41

		10-Apr-08		4:07:10		66.81		47		10-Apr-08		4:06:20		65.01		34.5		10-Apr-08		4:07:53		69.2		33.5		21-May-08		4:25:59		72.21		41

		10-Apr-08		6:07:10		67.4		46		10-Apr-08		6:06:20		65.6		34.5		10-Apr-08		6:07:53		68.61		34.5		21-May-08		6:25:59		72.21		40.5

		10-Apr-08		8:07:10		66.81		47		10-Apr-08		8:06:20		66.2		34.5		10-Apr-08		8:07:53		69.8		35		21-May-08		8:25:59		72.21		42

		10-Apr-08		10:07:10		66.81		47.5		10-Apr-08		10:06:20		68		34		10-Apr-08		10:07:53		70.41		38		21-May-08		10:25:59		73.4		42.5

		10-Apr-08		12:07:10		66.81		47		10-Apr-08		12:06:20		69.2		34		10-Apr-08		12:07:53		70.41		35		21-May-08		12:25:59		73.4		43

		10-Apr-08		14:07:10		66.81		47.5		10-Apr-08		14:06:20		69.8		36		10-Apr-08		14:07:53		71		42.5		21-May-08		14:25:59		74.01		44

		10-Apr-08		16:07:10		66.81		46.5		10-Apr-08		16:06:20		69.2		39.5		10-Apr-08		16:07:53		70.41		47		21-May-08		16:25:59		74.01		41

		10-Apr-08		18:07:10		66.81		47.5		10-Apr-08		18:06:20		68		32		10-Apr-08		18:07:53		69.8		35.5		21-May-08		18:25:59		74.01		35

		10-Apr-08		20:07:10		66.81		46.5		10-Apr-08		20:06:20		67.4		37		10-Apr-08		20:07:53		70.41		41.5		21-May-08		20:25:59		73.4		34.5

		10-Apr-08		22:07:10		66.81		47		10-Apr-08		22:06:20		67.4		37		10-Apr-08		22:07:53		71		37.5		21-May-08		22:25:59		74.01		35

		11-Apr-08		0:07:10		66.81		47.5		11-Apr-08		0:06:20		68		36.5		11-Apr-08		0:07:53		69.2		38		22-May-08		0:25:59		73.4		34.5

		11-Apr-08		2:07:10		66.81		46.5		11-Apr-08		2:06:20		66.81		36.5		11-Apr-08		2:07:53		69.8		36.5		22-May-08		2:25:59		72.21		34.5

		11-Apr-08		4:07:10		66.81		46.5		11-Apr-08		4:06:20		66.2		37.5		11-Apr-08		4:07:53		69.8		35.5		22-May-08		4:25:59		71.6		34

		11-Apr-08		6:07:10		66.81		46.5		11-Apr-08		6:06:20		65.6		37.5		11-Apr-08		6:07:53		69.2		36.5		22-May-08		6:25:59		72.21		32.5

		11-Apr-08		8:07:10		66.81		47.5		11-Apr-08		8:06:20		66.81		38		11-Apr-08		8:07:53		70.41		38.5		22-May-08		8:25:59		71.6		33.5

		11-Apr-08		10:07:10		66.81		48		11-Apr-08		10:06:20		68		36.5		11-Apr-08		10:07:53		70.41		36		22-May-08		10:25:59		73.4		34

		11-Apr-08		12:07:10		66.2		48.5		11-Apr-08		12:06:20		68.61		35		11-Apr-08		12:07:53		71		39.5		22-May-08		12:25:59		73.4		35

		11-Apr-08		14:07:10		66.81		48		11-Apr-08		14:06:20		68.61		34.5		11-Apr-08		14:07:53		70.41		45.5		22-May-08		14:25:59		74.01		35

		11-Apr-08		16:07:10		66.2		45.5		11-Apr-08		16:06:20		68.61		40		11-Apr-08		16:07:53		70.41		47.5		22-May-08		16:25:59		74.01		35

		11-Apr-08		18:07:10		66.81		48		11-Apr-08		18:06:20		68.61		37.5		11-Apr-08		18:07:53		71		45.5		22-May-08		18:25:59		74.01		34.5

		11-Apr-08		20:07:10		66.81		47.5		11-Apr-08		20:06:20		68.61		39.5		11-Apr-08		20:07:53		70.41		42		22-May-08		20:25:59		73.4		34.5

		11-Apr-08		22:07:10		66.81		47		11-Apr-08		22:06:20		67.4		42.5		11-Apr-08		22:07:53		70.41		43		22-May-08		22:25:59		72.8		33.5

		12-Apr-08		0:07:10		66.81		48		12-Apr-08		0:06:20		68		41.5		12-Apr-08		0:07:53		69.8		41.5		23-May-08		0:25:59		72.21		33

		12-Apr-08		2:07:10		66.81		47		12-Apr-08		2:06:20		66.81		42		12-Apr-08		2:07:53		69.8		39		23-May-08		2:25:59		71		32.5

		12-Apr-08		4:07:10		66.81		47.5		12-Apr-08		4:06:20		66.2		41		12-Apr-08		4:07:53		70.41		38.5		23-May-08		4:25:59		71.6		31.5

		12-Apr-08		6:07:10		66.81		47.5		12-Apr-08		6:06:20		66.2		40.5		12-Apr-08		6:07:53		70.41		38		23-May-08		6:25:59		71.6		30.5

		12-Apr-08		8:07:10		66.81		48.5		12-Apr-08		8:06:20		68		39.5		12-Apr-08		8:07:53		69.8		36		23-May-08		8:25:59		71		31.5

		12-Apr-08		10:07:10		66.81		47.5		12-Apr-08		10:06:20		68.61		43		12-Apr-08		10:07:53		70.41		43		23-May-08		10:25:59		73.4		31

		12-Apr-08		12:07:10		66.81		47		12-Apr-08		12:06:20		68		39		12-Apr-08		12:07:53		69.8		47.5		23-May-08		12:25:59		73.4		29.5

		12-Apr-08		14:07:10		67.4		46.5		12-Apr-08		14:06:20		68.61		33.5		12-Apr-08		14:07:53		70.41		40.5		23-May-08		14:25:59		74.01		29

		12-Apr-08		16:07:10		67.4		48		12-Apr-08		16:06:20		67.4		35		12-Apr-08		16:07:53		72.21		40		23-May-08		16:25:59		74.6		30

		12-Apr-08		18:07:10		67.4		45.5		12-Apr-08		18:06:20		67.4		34		12-Apr-08		18:07:53		68		45		23-May-08		18:25:59		74.01		31

		12-Apr-08		20:07:10		67.4		46.5		12-Apr-08		20:06:20		66.81		32.5		12-Apr-08		20:07:53		68		45		23-May-08		20:25:59		74.01		32

		12-Apr-08		22:07:10		67.4		46.5		12-Apr-08		22:06:20		66.2		38.5		12-Apr-08		22:07:53		68		44		23-May-08		22:25:59		74.6		31.5

		13-Apr-08		0:07:10		67.4		46		13-Apr-08		0:06:20		66.81		41		13-Apr-08		0:07:53		66.81		46		24-May-08		0:25:59		73.4		31.5

		13-Apr-08		2:07:10		67.4		46		13-Apr-08		2:06:20		65.6		42		13-Apr-08		2:07:53		66.81		45.5		24-May-08		2:25:59		72.21		32

		13-Apr-08		4:07:10		68		45.5		13-Apr-08		4:06:20		65.6		41		13-Apr-08		4:07:53		66.2		46.5		24-May-08		4:25:59		71.6		32

		13-Apr-08		6:07:10		68		46.5		13-Apr-08		6:06:20		66.81		40		13-Apr-08		6:07:53		66.2		47		24-May-08		6:25:59		72.21		31.5

		13-Apr-08		8:07:10		67.4		46.5		13-Apr-08		8:06:20		66.2		40.5		13-Apr-08		8:07:53		66.2		47.5		24-May-08		8:25:59		71.6		33

		13-Apr-08		10:07:10		68		47		13-Apr-08		10:06:20		66.81		42		13-Apr-08		10:07:53		66.81		47		24-May-08		10:25:59		74.01		33.5

		13-Apr-08		12:07:10		67.4		46		13-Apr-08		12:06:20		67.4		41.5		13-Apr-08		12:07:53		67.4		45.5		24-May-08		12:25:59		73.4		35

		13-Apr-08		14:07:10		67.4		46.5		13-Apr-08		14:06:20		67.4		43		13-Apr-08		14:07:53		67.4		46		24-May-08		14:25:59		74.01		35

		13-Apr-08		16:07:10		67.4		46		13-Apr-08		16:06:20		66.81		40		13-Apr-08		16:07:53		68		45.5		24-May-08		16:25:59		74.01		34.5

		13-Apr-08		18:07:10		67.4		46.5		13-Apr-08		18:06:20		66.81		38.5		13-Apr-08		18:07:53		67.4		45.5		24-May-08		18:25:59		74.01		34.5

		13-Apr-08		20:07:10		68		46		13-Apr-08		20:06:20		66.2		43.5		13-Apr-08		20:07:53		67.4		46		24-May-08		20:25:59		74.01		35.5

		13-Apr-08		22:07:10		67.4		47.5		13-Apr-08		22:06:20		66.2		53.5		13-Apr-08		22:07:53		67.4		46.5		24-May-08		22:25:59		74.01		35

		14-Apr-08		0:07:10		67.4		46		14-Apr-08		0:06:20		66.2		48.5		14-Apr-08		0:07:53		66.81		47		25-May-08		0:25:59		72.8		35.5

		14-Apr-08		2:07:10		67.4		46		14-Apr-08		2:06:20		66.2		46		14-Apr-08		2:07:53		66.81		47		25-May-08		2:25:59		72.21		36

		14-Apr-08		4:07:10		67.4		46		14-Apr-08		4:06:20		65.6		45.5		14-Apr-08		4:07:53		66.2		47.5		25-May-08		4:25:59		71.6		36.5

		14-Apr-08		6:07:10		68.61		46		14-Apr-08		6:06:20		65.6		44		14-Apr-08		6:07:53		66.2		48		25-May-08		6:25:59		71.6		37

		14-Apr-08		8:07:10		67.4		46		14-Apr-08		8:06:20		66.2		41.5		14-Apr-08		8:07:53		66.2		47		25-May-08		8:25:59		71.6		37.5

		14-Apr-08		10:07:10		68		46		14-Apr-08		10:06:20		66.2		43		14-Apr-08		10:07:53		66.2		48		25-May-08		10:25:59		71.6		38.5

		14-Apr-08		12:07:10		67.4		46		14-Apr-08		12:06:20		67.4		43		14-Apr-08		12:07:53		66.81		47		25-May-08		12:25:59		71.6		40

		14-Apr-08		14:07:10		67.4		48		14-Apr-08		14:06:20		67.4		45.5		14-Apr-08		14:07:53		67.4		48.5		25-May-08		14:25:59		71.6		40.5

		14-Apr-08		16:07:10		67.4		46		14-Apr-08		16:06:20		66.81		43		14-Apr-08		16:07:53		66.81		47		25-May-08		16:25:59		71.6		40

		14-Apr-08		18:07:10		67.4		47		14-Apr-08		18:06:20		66.81		46.5		14-Apr-08		18:07:53		66.81		48		25-May-08		18:25:59		71.6		41

		14-Apr-08		20:07:10		67.4		47		14-Apr-08		20:06:20		66.2		50		14-Apr-08		20:07:53		66.2		48		25-May-08		20:25:59		71.6		41

		14-Apr-08		22:07:10		68		45.5		14-Apr-08		22:06:20		66.2		46		14-Apr-08		22:07:53		66.2		48		25-May-08		22:25:59		71.6		41

		15-Apr-08		0:07:10		67.4		46		15-Apr-08		0:06:20		65.6		49		15-Apr-08		0:07:53		66.81		47		26-May-08		0:25:59		71.6		40

		15-Apr-08		2:07:10		67.4		47		15-Apr-08		2:06:20		66.2		46		15-Apr-08		2:07:53		66.81		47.5		26-May-08		2:25:59		71.6		38.5

		15-Apr-08		4:07:10		67.4		44		15-Apr-08		4:06:20		65.6		45		15-Apr-08		4:07:53		66.81		47.5		26-May-08		4:25:59		71.6		37.5

		15-Apr-08		6:07:10		68		46		15-Apr-08		6:06:20		65.01		45		15-Apr-08		6:07:53		66.2		48		26-May-08		6:25:59		71.6		37

		15-Apr-08		8:07:10		67.4		45.5		15-Apr-08		8:06:20		67.4		45		15-Apr-08		8:07:53		65.6		49.5		26-May-08		8:25:59		71.6		37.5

		15-Apr-08		10:07:10		67.4		47		15-Apr-08		10:06:20		69.2		44		15-Apr-08		10:07:53		65.01		49		26-May-08		10:25:59		71.6		39.5

		15-Apr-08		12:07:10		67.4		47		15-Apr-08		12:06:20		69.8		37.5		15-Apr-08		12:07:53		65.6		49		26-May-08		12:25:59		72.21		38.5

		15-Apr-08		14:07:10		67.4		41		15-Apr-08		14:06:20		71		33.5		15-Apr-08		14:07:53		66.2		47.5		26-May-08		14:25:59		72.8		38

		15-Apr-08		16:07:10		67.4		45.5		15-Apr-08		16:06:20		70.41		32.5		15-Apr-08		16:07:53		66.81		47		26-May-08		16:25:59		73.4		36.5

		15-Apr-08		18:07:10		67.4		45.5		15-Apr-08		18:06:20		69.2		31.5		15-Apr-08		18:07:53		68		45.5		26-May-08		18:25:59		74.01		36

		15-Apr-08		20:07:10		67.4		45		15-Apr-08		20:06:20		69.2		29		15-Apr-08		20:07:53		67.4		45		26-May-08		20:25:59		74.01		35.5

		15-Apr-08		22:07:10		68		45.5		15-Apr-08		22:06:20		68		31.5		15-Apr-08		22:07:53		67.4		45		26-May-08		22:25:59		72.21		37

		16-Apr-08		0:07:10		67.4		37		16-Apr-08		0:06:20		66.81		34.5		16-Apr-08		0:07:53		67.4		45.5		27-May-08		0:25:59		72.21		37.5

		16-Apr-08		2:07:10		67.4		46.5		16-Apr-08		2:06:20		65.6		33		16-Apr-08		2:07:53		68		44.5		27-May-08		2:25:59		71.6		37.5

		16-Apr-08		4:07:10		67.4		45		16-Apr-08		4:06:20		65.01		33		16-Apr-08		4:07:53		68		45		27-May-08		4:25:59		71.6		37.5

		16-Apr-08		6:07:10		67.4		45.5		16-Apr-08		6:06:20		65.01		33.5		16-Apr-08		6:07:53		68		44.5		27-May-08		6:25:59		72.21		37.5

		16-Apr-08		8:07:10		67.4		46		16-Apr-08		8:06:20		68		32.5		16-Apr-08		8:07:53		67.4		44		27-May-08		8:25:59		71		39

		16-Apr-08		10:07:10		69.2		34		16-Apr-08		10:06:20		70.41		30		16-Apr-08		10:07:53		66.2		47.5		27-May-08		10:25:59		71		39.5

		16-Apr-08		12:07:10		69.8		44		16-Apr-08		12:06:20		68.61		27.5		16-Apr-08		12:07:53		66.2		48		27-May-08		12:25:59		72.21		40.5

		16-Apr-08		14:07:10		70.41		43		16-Apr-08		14:06:20		69.8		26		16-Apr-08		14:07:53		66.2		49.5		27-May-08		14:25:59		72.8		40

		16-Apr-08		16:07:10		70.41		46		16-Apr-08		16:06:20		69.2		28		16-Apr-08		16:07:53		67.4		47		27-May-08		16:25:59		72.8		39.5

		16-Apr-08		18:07:10		70.41		45.5		16-Apr-08		18:06:20		68.61		31		16-Apr-08		18:07:53		68		48		27-May-08		18:25:59		72.8		41

		16-Apr-08		20:07:10		69.2		44.5		16-Apr-08		20:06:20		68		30		16-Apr-08		20:07:53		67.4		44.5		27-May-08		20:25:59		72.8		40.5

		16-Apr-08		22:07:10		69.2		44.5		16-Apr-08		22:06:20		68		30		16-Apr-08		22:07:53		68		45		27-May-08		22:25:59		72.21		39.5

		17-Apr-08		0:07:10		70.41		46		17-Apr-08		0:06:20		67.4		31.5		17-Apr-08		0:07:53		68		41		28-May-08		0:25:59		72.21		39.5

		17-Apr-08		2:07:10		70.41		43.5		17-Apr-08		2:06:20		66.2		33		17-Apr-08		2:07:53		68		48.5		28-May-08		2:25:59		72.21		40

		17-Apr-08		4:07:10		69.8		46		17-Apr-08		4:06:20		65.6		34		17-Apr-08		4:07:53		68		46.5		28-May-08		4:25:59		71.6		40

		17-Apr-08		6:07:10		69.8		46		17-Apr-08		6:06:20		65.6		34.5		17-Apr-08		6:07:53		68		47		28-May-08		6:25:59		72.21		40.5

		17-Apr-08		8:07:10		71		44.5		17-Apr-08		8:06:20		69.2		33		17-Apr-08		8:07:53		67.4		48		28-May-08		8:25:59		71.6		42.5

		17-Apr-08		10:07:10		70.41		44.5		17-Apr-08		10:06:20		70.41		31.5		17-Apr-08		10:07:53		66.81		45.5		28-May-08		10:25:59		73.4		42

		17-Apr-08		12:07:10		71		45.5		17-Apr-08		12:06:20		71		29		17-Apr-08		12:07:53		68		48.5		28-May-08		12:25:59		74.01		41

		17-Apr-08		14:07:10		71		45.5		17-Apr-08		14:06:20		69.2		29.5		17-Apr-08		14:07:53		67.4		49.5		28-May-08		14:25:59		74.01		41.5

		17-Apr-08		16:07:10		71		45.5		17-Apr-08		16:06:20		68.61		31.5		17-Apr-08		16:07:53		68		48		28-May-08		16:25:59		74.6		39.5

		17-Apr-08		18:07:10		71		46.5		17-Apr-08		18:06:20		70.41		31		17-Apr-08		18:07:53		68.61		48		28-May-08		18:25:59		75.2		38

		17-Apr-08		20:07:10		71		44.5		17-Apr-08		20:06:20		69.8		34.5		17-Apr-08		20:07:53		67.4		46.5		28-May-08		20:25:59		74.6		39.5

		17-Apr-08		22:07:10		69.8		42.5		17-Apr-08		22:06:20		69.8		36.5		17-Apr-08		22:07:53		67.4		46		28-May-08		22:25:59		74.01		38

		18-Apr-08		0:07:10		70.41		45.5		18-Apr-08		0:06:20		68.61		38		18-Apr-08		0:07:53		68		48.5		29-May-08		0:25:59		72.8		38

		18-Apr-08		2:07:10		70.41		42.5		18-Apr-08		2:06:20		67.4		39		18-Apr-08		2:07:53		68		47.5		29-May-08		2:25:59		72.21		38

		18-Apr-08		4:07:10		69.8		46.5		18-Apr-08		4:06:20		66.2		39.5		18-Apr-08		4:07:53		68		47.5		29-May-08		4:25:59		72.21		38.5

		18-Apr-08		6:07:10		69.8		46		18-Apr-08		6:06:20		65.6		40		18-Apr-08		6:07:53		68		42		29-May-08		6:25:59		72.8		38.5

		18-Apr-08		8:07:10		70.41		46.5		18-Apr-08		8:06:20		68.61		39		18-Apr-08		8:07:53		67.4		49		29-May-08		8:25:59		72.8		40

		18-Apr-08		10:07:10		70.41		46		18-Apr-08		10:06:20		71		37.5		18-Apr-08		10:07:53		67.4		47.5		29-May-08		10:25:59		74.01		39

		18-Apr-08		12:07:10		71		44		18-Apr-08		12:06:20		72.21		36.5		18-Apr-08		12:07:53		68		49		29-May-08		12:25:59		74.6		39.5

		18-Apr-08		14:07:10		70.41		44.5		18-Apr-08		14:06:20		71		34.5		18-Apr-08		14:07:53		66.81		49.5		29-May-08		14:25:59		75.2		39

		18-Apr-08		16:07:10		70.41		42.5		18-Apr-08		16:06:20		71		39		18-Apr-08		16:07:53		67.4		49		29-May-08		16:25:59		74.6		39

		18-Apr-08		18:07:10		70.41		45		18-Apr-08		18:06:20		70.41		38		18-Apr-08		18:07:53		68		47.5		29-May-08		18:25:59		74.6		38

		18-Apr-08		20:07:10		70.41		44.5		18-Apr-08		20:06:20		69.8		41		18-Apr-08		20:07:53		67.4		48.5		29-May-08		20:25:59		74.6		39.5

		18-Apr-08		22:07:10		70.41		45.5		18-Apr-08		22:06:20		69.2		41		18-Apr-08		22:07:53		68		48.5		29-May-08		22:25:59		74.6		38.5

		19-Apr-08		0:07:10		69.8		44.5		19-Apr-08		0:06:20		68		42.5		19-Apr-08		0:07:53		67.4		49		30-May-08		0:25:59		74.01		38.5

		19-Apr-08		2:07:10		69.8		45		19-Apr-08		2:06:20		67.4		45		19-Apr-08		2:07:53		67.4		49		30-May-08		2:25:59		72.8		38.5

		19-Apr-08		4:07:10		69.8		40		19-Apr-08		4:06:20		66.81		45		19-Apr-08		4:07:53		68		46.5		30-May-08		4:25:59		72.21		39

		19-Apr-08		6:07:10		69.8		45.5		19-Apr-08		6:06:20		66.81		45		19-Apr-08		6:07:53		68		49		30-May-08		6:25:59		72.21		39.5

		19-Apr-08		8:07:10		69.8		45		19-Apr-08		8:06:20		71		41		19-Apr-08		8:07:53		66.81		50		30-May-08		8:25:59		72.21		41.5

		19-Apr-08		10:07:10		69.8		45		19-Apr-08		10:06:20		71.6		40.5		19-Apr-08		10:07:53		66.81		50		30-May-08		10:25:59		74.6		41.5

		19-Apr-08		12:07:10		70.41		44.5		19-Apr-08		12:06:20		71.6		39		19-Apr-08		12:07:53		66.81		50		30-May-08		12:25:59		74.6		41.5

		19-Apr-08		14:07:10		70.41		42		19-Apr-08		14:06:20		72.8		41		19-Apr-08		14:07:53		66.81		48		30-May-08		14:25:59		74.6		41.5

		19-Apr-08		16:07:10		70.41		45		19-Apr-08		16:06:20		69.8		42.5		19-Apr-08		16:07:53		67.4		48		30-May-08		16:25:59		75.2		40.5

		19-Apr-08		18:07:10		69.8		45		19-Apr-08		18:06:20		69.8		43.5		19-Apr-08		18:07:53		67.4		49.5		30-May-08		18:25:59		74.6		39

		19-Apr-08		20:07:10		69.8		42		19-Apr-08		20:06:20		68.61		41		19-Apr-08		20:07:53		67.4		46		30-May-08		20:25:59		74.6		41

		19-Apr-08		22:07:10		69.8		44.5		19-Apr-08		22:06:20		68.61		39		19-Apr-08		22:07:53		67.4		49.5		30-May-08		22:25:59		74.6		39.5

		20-Apr-08		0:07:10		69.2		44		20-Apr-08		0:06:20		67.4		40		20-Apr-08		0:07:53		67.4		49.5		31-May-08		0:25:59		74.01		39

		20-Apr-08		2:07:10		69.2		44.5		20-Apr-08		2:06:20		66.2		40		20-Apr-08		2:07:53		67.4		48		31-May-08		2:25:59		72.8		39.5

		20-Apr-08		4:07:10		68.61		45.5		20-Apr-08		4:06:20		65.01		38.5		20-Apr-08		4:07:53		66.81		48.5		31-May-08		4:25:59		72.21		40

		20-Apr-08		6:07:10		68.61		46.5		20-Apr-08		6:06:20		65.01		36		20-Apr-08		6:07:53		67.4		48.5		31-May-08		6:25:59		71.6		41

		20-Apr-08		8:07:10		68.61		47		20-Apr-08		8:06:20		65.01		33.5		20-Apr-08		8:07:53		67.4		47.5		31-May-08		8:25:59		71.6		42

		20-Apr-08		10:07:10		68.61		46		20-Apr-08		10:06:20		67.4		30		20-Apr-08		10:07:53		68		47.5		31-May-08		10:25:59		73.4		42.5

		20-Apr-08		12:07:10		69.2		43.5		20-Apr-08		12:06:20		69.2		26		20-Apr-08		12:07:53		67.4		44.5		31-May-08		12:25:59		74.6		42

		20-Apr-08		14:07:10		69.2		43.5		20-Apr-08		14:06:20		69.2		23		20-Apr-08		14:07:53		66.81		36.5		31-May-08		14:25:59		75.2		43.5

		20-Apr-08		16:07:10		69.2		45		20-Apr-08		16:06:20		69.2		23.5		20-Apr-08		16:07:53		67.4		47.5		31-May-08		16:25:59		74.6		43

		20-Apr-08		18:07:10		69.2		44		20-Apr-08		18:06:20		69.8		23		20-Apr-08		18:07:53		67.4		44.5		31-May-08		18:25:59		74.6		44.5

		20-Apr-08		20:07:10		69.2		45.5		20-Apr-08		20:06:20		68		25.5		20-Apr-08		20:07:53		67.4		47		31-May-08		20:25:59		74.6		43

		20-Apr-08		22:07:10		68.61		45		20-Apr-08		22:06:20		66.81		27.5		20-Apr-08		22:07:53		67.4		47.5		31-May-08		22:25:59		74.01		41

		21-Apr-08		0:07:10		68.61		46.5		21-Apr-08		0:06:20		65.6		29		21-Apr-08		0:07:53		67.4		48.5		1-Jun-08		0:25:59		72.8		41

		21-Apr-08		2:07:10		68		44.5		21-Apr-08		2:06:20		65.01		30.5		21-Apr-08		2:07:53		66.81		37.5		1-Jun-08		2:25:59		72.21		40.5

		21-Apr-08		4:07:10		68		46.5		21-Apr-08		4:06:20		63.8		31.5		21-Apr-08		4:07:53		66.81		47.5		1-Jun-08		4:25:59		71.6		40.5

		21-Apr-08		6:07:10		68		47.5		21-Apr-08		6:06:20		63.21		33		21-Apr-08		6:07:53		67.4		47.5		1-Jun-08		6:25:59		72.21		40.5

		21-Apr-08		8:07:10		68		44		21-Apr-08		8:06:20		63.21		33		21-Apr-08		8:07:53		67.4		47.5		1-Jun-08		8:25:59		72.21		40.5

		21-Apr-08		10:07:10		68		47.5		21-Apr-08		10:06:20		65.01		29		21-Apr-08		10:07:53		67.4		47.5		1-Jun-08		10:25:59		72.21		40.5

		21-Apr-08		12:07:10		68		42.5		21-Apr-08		12:06:20		67.4		24.5		21-Apr-08		12:07:53		67.4		42		1-Jun-08		12:25:59		73.4		41

		21-Apr-08		14:07:10		68.61		45.5		21-Apr-08		14:06:20		69.2		27.5		21-Apr-08		14:07:53		67.4		48		1-Jun-08		14:25:59		74.6		41.5

		21-Apr-08		16:07:10		68.61		45		21-Apr-08		16:06:20		69.2		29.5		21-Apr-08		16:07:53		67.4		48		1-Jun-08		16:25:59		75.81		41

		21-Apr-08		18:07:10		68.61		45		21-Apr-08		18:06:20		69.2		27		21-Apr-08		18:07:53		66.81		46.5		1-Jun-08		18:25:59		77		39.5

		21-Apr-08		20:07:10		69.2		45		21-Apr-08		20:06:20		68		30		21-Apr-08		20:07:53		67.4		48		1-Jun-08		20:25:59		76.4		39.5

		21-Apr-08		22:07:10		68.61		46.5		21-Apr-08		22:06:20		66.2		32		21-Apr-08		22:07:53		67.4		48.5		1-Jun-08		22:25:59		74.6		39

		22-Apr-08		0:07:10		68.61		45		22-Apr-08		0:06:20		65.01		30		22-Apr-08		0:07:53		67.4		48		2-Jun-08		0:25:59		72.8		39

		22-Apr-08		2:07:10		68		47		22-Apr-08		2:06:20		64.4		32		22-Apr-08		2:07:53		67.4		48		2-Jun-08		2:25:59		72.21		38.5

		22-Apr-08		4:07:10		67.4		47		22-Apr-08		4:06:20		63.8		32.5		22-Apr-08		4:07:53		66.81		41		2-Jun-08		4:25:59		72.21		38

		22-Apr-08		6:07:10		68		46.5		22-Apr-08		6:06:20		63.21		34		22-Apr-08		6:07:53		67.4		48		2-Jun-08		6:25:59		71.6		37.5

		22-Apr-08		8:07:10		68.61		47		22-Apr-08		8:06:20		66.81		33.5		22-Apr-08		8:07:53		66.81		49		2-Jun-08		8:25:59		71.6		38

		22-Apr-08		10:07:10		69.2		44.5		22-Apr-08		10:06:20		71		29.5		22-Apr-08		10:07:53		66.2		49.5		2-Jun-08		10:25:59		72.21		39

		22-Apr-08		12:07:10		69.8		44		22-Apr-08		12:06:20		71		27.5		22-Apr-08		12:07:53		66.81		48		2-Jun-08		12:25:59		73.4		38.5

		22-Apr-08		14:07:10		69.8		46		22-Apr-08		14:06:20		71		31		22-Apr-08		14:07:53		66.2		49.5		2-Jun-08		14:25:59		75.2		38

		22-Apr-08		16:07:10		69.2		44.5		22-Apr-08		16:06:20		69.8		32.5		22-Apr-08		16:07:53		67.4		47.5		2-Jun-08		16:25:59		75.81		38

		22-Apr-08		18:07:10		69.2		45		22-Apr-08		18:06:20		69.8		32		22-Apr-08		18:07:53		68		46.5		2-Jun-08		18:25:59		76.4		37

		22-Apr-08		20:07:10		69.8		45		22-Apr-08		20:06:20		69.2		31.5		22-Apr-08		20:07:53		68		46.5		2-Jun-08		20:25:59		75.81		37

		22-Apr-08		22:07:10		69.8		43.5		22-Apr-08		22:06:20		68		32		22-Apr-08		22:07:53		68		47		2-Jun-08		22:25:59		74.01		37.5

		23-Apr-08		0:07:10		69.2		45		23-Apr-08		0:06:20		66.81		32		23-Apr-08		0:07:53		67.4		47.5		3-Jun-08		0:25:59		72.21		37

		23-Apr-08		2:07:10		68.61		45		23-Apr-08		2:06:20		65.6		33		23-Apr-08		2:07:53		67.4		47		3-Jun-08		2:25:59		72.21		36.5

		23-Apr-08		4:07:10		68.61		46.5		23-Apr-08		4:06:20		65.01		34.5		23-Apr-08		4:07:53		67.4		47.5		3-Jun-08		4:25:59		71.6		36

		23-Apr-08		6:07:10		68.61		43.5		23-Apr-08		6:06:20		64.4		35.5		23-Apr-08		6:07:53		67.4		47.5		3-Jun-08		6:25:59		72.21		35.5

		23-Apr-08		8:07:10		69.2		42.5		23-Apr-08		8:06:20		66.81		35.5		23-Apr-08		8:07:53		67.4		48		3-Jun-08		8:25:59		71.6		37.5

		23-Apr-08		10:07:10		69.8		46		23-Apr-08		10:06:20		70.41		32.5		23-Apr-08		10:07:53		67.4		48		3-Jun-08		10:25:59		74.01		38

		23-Apr-08		12:07:10		69.2		45.5		23-Apr-08		12:06:20		71		35.5		23-Apr-08		12:07:53		66.81		49.5		3-Jun-08		12:25:59		74.01		39

		23-Apr-08		14:07:10		69.8		45		23-Apr-08		14:06:20		71.6		41		23-Apr-08		14:07:53		66.2		50.5		3-Jun-08		14:25:59		74.6		39.5

		23-Apr-08		16:07:10		70.41		47		23-Apr-08		16:06:20		69.8		49		23-Apr-08		16:07:53		67.4		50.5		3-Jun-08		16:25:59		74.6		39

		23-Apr-08		18:07:10		70.41		44.5		23-Apr-08		18:06:20		69.2		47.5		23-Apr-08		18:07:53		68		50		3-Jun-08		18:25:59		74.6		38.5

		23-Apr-08		20:07:10		70.41		46		23-Apr-08		20:06:20		69.8		49.5		23-Apr-08		20:07:53		68		50		3-Jun-08		20:25:59		74.6		34.5

		23-Apr-08		22:07:10		70.41		46.5		23-Apr-08		22:06:20		69.2		48.5		23-Apr-08		22:07:53		68		50		3-Jun-08		22:25:59		74.6		31.5

		24-Apr-08		0:07:10		70.41		47		24-Apr-08		0:06:20		68		47		24-Apr-08		0:07:53		68		49.5		4-Jun-08		0:25:59		73.4		32.5

		24-Apr-08		2:07:10		69.8		44.5		24-Apr-08		2:06:20		66.81		47.5		24-Apr-08		2:07:53		68		49.5		4-Jun-08		2:25:59		72.8		33.5

		24-Apr-08		4:07:10		69.8		46.5		24-Apr-08		4:06:20		66.2		46		24-Apr-08		4:07:53		68		48.5		4-Jun-08		4:25:59		72.21		34

		24-Apr-08		6:07:10		69.8		46.5		24-Apr-08		6:06:20		65.6		44.5		24-Apr-08		6:07:53		68		49		4-Jun-08		6:25:59		72.21		33.5

		24-Apr-08		8:07:10		70.41		47		24-Apr-08		8:06:20		68		44		24-Apr-08		8:07:53		67.4		50		4-Jun-08		8:25:59		72.21		37

		24-Apr-08		10:07:10		70.41		46		24-Apr-08		10:06:20		70.41		46		24-Apr-08		10:07:53		68		49.5		4-Jun-08		10:25:59		74.01		41.5

		24-Apr-08		12:07:10		70.41		46.5		24-Apr-08		12:06:20		69.8		44.5		24-Apr-08		12:07:53		68		50		4-Jun-08		12:25:59		74.01		44

		24-Apr-08		14:07:10		70.41		46		24-Apr-08		14:06:20		71		36		24-Apr-08		14:07:53		68		49		4-Jun-08		14:25:59		74.01		44.5

		24-Apr-08		16:07:10		70.41		44.5		24-Apr-08		16:06:20		69.8		32		24-Apr-08		16:07:53		68		48		4-Jun-08		16:25:59		73.4		42

		24-Apr-08		18:07:10		69.8		44		24-Apr-08		18:06:20		70.41		31		24-Apr-08		18:07:53		68		45		4-Jun-08		18:25:59		73.4		39

		24-Apr-08		20:07:10		70.41		46		24-Apr-08		20:06:20		69.8		30.5		24-Apr-08		20:07:53		69.2		46.5		4-Jun-08		20:25:59		74.6		39.5

		24-Apr-08		22:07:10		70.41		46		24-Apr-08		22:06:20		68		33		24-Apr-08		22:07:53		68		48.5		4-Jun-08		22:25:59		74.6		38

		25-Apr-08		0:07:10		69.8		45		25-Apr-08		0:06:20		66.2		34		25-Apr-08		0:07:53		68		48.5		5-Jun-08		0:25:59		74.01		37.5

		25-Apr-08		2:07:10		69.2		46		25-Apr-08		2:06:20		65.01		35.5		25-Apr-08		2:07:53		68.61		46		5-Jun-08		2:25:59		72.8		36.5

		25-Apr-08		4:07:10		69.2		45		25-Apr-08		4:06:20		63.8		36		25-Apr-08		4:07:53		68		47.5		5-Jun-08		4:25:59		72.21		36

		25-Apr-08		6:07:10		69.8		45		25-Apr-08		6:06:20		63.21		36		25-Apr-08		6:07:53		68.61		47.5		5-Jun-08		6:25:59		72.21		35.5

		25-Apr-08		8:07:10		69.8		46		25-Apr-08		8:06:20		66.81		35.5		25-Apr-08		8:07:53		68.61		47.5		5-Jun-08		8:25:59		72.21		35.5

		25-Apr-08		10:07:10		69.8		45		25-Apr-08		10:06:20		70.41		32.5		25-Apr-08		10:07:53		67.4		49.5		5-Jun-08		10:25:59		74.01		35.5

		25-Apr-08		12:07:10		70.41		42.5		25-Apr-08		12:06:20		71		28.5		25-Apr-08		12:07:53		68.61		48		5-Jun-08		12:25:59		73.4		35

		25-Apr-08		14:07:10		70.41		45.5		25-Apr-08		14:06:20		71		28		25-Apr-08		14:07:53		68		47.5		5-Jun-08		14:25:59		73.4		34

		25-Apr-08		16:07:10		70.41		46		25-Apr-08		16:06:20		71.6		32.5		25-Apr-08		16:07:53		68.61		48.5		5-Jun-08		16:25:59		74.01		34.5

		25-Apr-08		18:07:10		70.41		45.5		25-Apr-08		18:06:20		70.41		31		25-Apr-08		18:07:53		68		40.5		5-Jun-08		18:25:59		73.4		35

		25-Apr-08		20:07:10		70.41		41.5		25-Apr-08		20:06:20		71		32.5		25-Apr-08		20:07:53		68		48		5-Jun-08		20:25:59		74.01		35.5

		25-Apr-08		22:07:10		69.8		45		25-Apr-08		22:06:20		70.41		35.5		25-Apr-08		22:07:53		68		46		5-Jun-08		22:25:59		74.6		34

		26-Apr-08		0:07:10		70.41		46		26-Apr-08		0:06:20		69.2		36.5		26-Apr-08		0:07:53		68		49		6-Jun-08		0:25:59		74.01		34.5

		26-Apr-08		2:07:10		69.8		45.5		26-Apr-08		2:06:20		67.4		38.5		26-Apr-08		2:07:53		68.61		48		6-Jun-08		2:25:59		72.21		35

		26-Apr-08		4:07:10		69.8		44.5		26-Apr-08		4:06:20		66.2		39		26-Apr-08		4:07:53		68		48		6-Jun-08		4:25:59		71.6		35

		26-Apr-08		6:07:10		69.8		46		26-Apr-08		6:06:20		65.6		38.5		26-Apr-08		6:07:53		68.61		48		6-Jun-08		6:25:59		71.6		35

		26-Apr-08		8:07:10		70.41		46.5		26-Apr-08		8:06:20		68.61		37.5		26-Apr-08		8:07:53		68.61		48.5		6-Jun-08		8:25:59		72.21		37

		26-Apr-08		10:07:10		70.41		45.5		26-Apr-08		10:06:20		71		35.5		26-Apr-08		10:07:53		68		46.5		6-Jun-08		10:25:59		73.4		37.5

		26-Apr-08		12:07:10		71		46.5		26-Apr-08		12:06:20		71		32.5		26-Apr-08		12:07:53		68.61		49		6-Jun-08		12:25:59		73.4		35.5

		26-Apr-08		14:07:10		71		32		26-Apr-08		14:06:20		69.2		31		26-Apr-08		14:07:53		67.4		36		6-Jun-08		14:25:59		74.01		37.5

		26-Apr-08		16:07:10		71		35		26-Apr-08		16:06:20		68.61		36		26-Apr-08		16:07:53		67.4		39.5		6-Jun-08		16:25:59		74.01		38.5

		26-Apr-08		18:07:10		71		39.5		26-Apr-08		18:06:20		69.2		39.5		26-Apr-08		18:07:53		68.61		42.5		6-Jun-08		18:25:59		73.4		38.5

		26-Apr-08		20:07:10		70.41		38		26-Apr-08		20:06:20		69.2		41		26-Apr-08		20:07:53		68.61		41		6-Jun-08		20:25:59		74.01		41

		26-Apr-08		22:07:10		69.8		38		26-Apr-08		22:06:20		68		42		26-Apr-08		22:07:53		68.61		40.5		6-Jun-08		22:25:59		74.6		39

		27-Apr-08		0:07:10		69.8		36.5		27-Apr-08		0:06:20		68		39.5		27-Apr-08		0:07:53		68.61		39.5		7-Jun-08		0:25:59		74.01		38.5

		27-Apr-08		2:07:10		70.41		36.5		27-Apr-08		2:06:20		68		39.5		27-Apr-08		2:07:53		68.61		39.5		7-Jun-08		2:25:59		72.8		39

		27-Apr-08		4:07:10		70.41		37.5		27-Apr-08		4:06:20		66.81		42.5		27-Apr-08		4:07:53		68.61		39.5		7-Jun-08		4:25:59		71.6		38.5

		27-Apr-08		6:07:10		69.8		36		27-Apr-08		6:06:20		67.4		40.5		27-Apr-08		6:07:53		68		39		7-Jun-08		6:25:59		72.21		37.5

		27-Apr-08		8:07:10		69.8		37.5		27-Apr-08		8:06:20		68		42		27-Apr-08		8:07:53		68.61		40.5		7-Jun-08		8:25:59		72.21		38

		27-Apr-08		10:07:10		70.41		40		27-Apr-08		10:06:20		69.2		43		27-Apr-08		10:07:53		68.61		42.5		7-Jun-08		10:25:59		73.4		37.5

		27-Apr-08		12:07:10		71		40		27-Apr-08		12:06:20		69.2		42.5		27-Apr-08		12:07:53		68		44		7-Jun-08		12:25:59		73.4		36

		27-Apr-08		14:07:10		71		40		27-Apr-08		14:06:20		69.2		40.5		27-Apr-08		14:07:53		69.2		42.5		7-Jun-08		14:25:59		73.4		34

		27-Apr-08		16:07:10		71		43		27-Apr-08		16:06:20		69.2		47		27-Apr-08		16:07:53		69.2		46		7-Jun-08		16:25:59		73.4		33.5

		27-Apr-08		18:07:10		71		42.5		27-Apr-08		18:06:20		69.2		43.5		27-Apr-08		18:07:53		69.2		44		7-Jun-08		18:25:59		73.4		34

		27-Apr-08		20:07:10		71.6		38		27-Apr-08		20:06:20		68		43.5		27-Apr-08		20:07:53		68.61		42.5		7-Jun-08		20:25:59		74.01		35

		27-Apr-08		22:07:10		71		37.5		27-Apr-08		22:06:20		68		42.5		27-Apr-08		22:07:53		68.61		41		7-Jun-08		22:25:59		74.01		33.5

		28-Apr-08		0:07:10		70.41		38.5		28-Apr-08		0:06:20		68		40		28-Apr-08		0:07:53		68.61		40		8-Jun-08		0:25:59		73.4		33

		28-Apr-08		2:07:10		69.8		39.5		28-Apr-08		2:06:20		68		45		28-Apr-08		2:07:53		68.61		42		8-Jun-08		2:25:59		72.21		33

		28-Apr-08		4:07:10		69.2		39.5		28-Apr-08		4:06:20		67.4		47.5		28-Apr-08		4:07:53		68		41.5		8-Jun-08		4:25:59		71.6		33

		28-Apr-08		6:07:10		69.2		39.5		28-Apr-08		6:06:20		67.4		45		28-Apr-08		6:07:53		68		41.5		8-Jun-08		6:25:59		71.6		33

		28-Apr-08		8:07:10		70.41		40		28-Apr-08		8:06:20		68		47		28-Apr-08		8:07:53		68.61		42.5		8-Jun-08		8:25:59		71.6		33

		28-Apr-08		10:07:10		70.41		40.5		28-Apr-08		10:06:20		68		47.5		28-Apr-08		10:07:53		68.61		43		8-Jun-08		10:25:59		72.21		34

		28-Apr-08		12:07:10		71		40		28-Apr-08		12:06:20		68.61		44		28-Apr-08		12:07:53		69.2		43		8-Jun-08		12:25:59		74.6		33

		28-Apr-08		14:07:10		71		43		28-Apr-08		14:06:20		69.2		43		28-Apr-08		14:07:53		69.2		45.5		8-Jun-08		14:25:59		75.81		31.5

		28-Apr-08		16:07:10		71		44		28-Apr-08		16:06:20		68.61		52		28-Apr-08		16:07:53		69.2		47		8-Jun-08		16:25:59		77		30.5

		28-Apr-08		18:07:10		71		41.5		28-Apr-08		18:06:20		69.2		46		28-Apr-08		18:07:53		68.61		45		8-Jun-08		18:25:59		77		31.5

		28-Apr-08		20:07:10		71		39		28-Apr-08		20:06:20		68.61		45		28-Apr-08		20:07:53		68.61		43		8-Jun-08		20:25:59		77		33.5

		28-Apr-08		22:07:10		71		38.5		28-Apr-08		22:06:20		68.61		43.5		28-Apr-08		22:07:53		68.61		41.5		8-Jun-08		22:25:59		75.81		34.5

		29-Apr-08		0:07:10		69.2		38.5		29-Apr-08		0:06:20		68		45		29-Apr-08		0:07:53		68		41		9-Jun-08		0:25:59		74.6		34

		29-Apr-08		2:07:10		69.8		38		29-Apr-08		2:06:20		67.4		44.5		29-Apr-08		2:07:53		68.61		40.5		9-Jun-08		2:25:59		74.01		34.5

		29-Apr-08		4:07:10		69.8		37.5		29-Apr-08		4:06:20		66.81		44		29-Apr-08		4:07:53		68.61		40		9-Jun-08		4:25:59		72.8		35

		29-Apr-08		6:07:10		69.2		36.5		29-Apr-08		6:06:20		66.2		44		29-Apr-08		6:07:53		68.61		39		9-Jun-08		6:25:59		72.21		35.5

		29-Apr-08		8:07:10		69.8		38.5		29-Apr-08		8:06:20		68		44.5		29-Apr-08		8:07:53		68		41		9-Jun-08		8:25:59		72.21		36.5

		29-Apr-08		10:07:10		70.41		39.5		29-Apr-08		10:06:20		69.8		45		29-Apr-08		10:07:53		68		43		9-Jun-08		10:25:59		74.01		37

		29-Apr-08		12:07:10		71		42		29-Apr-08		12:06:20		70.41		48.5		29-Apr-08		12:07:53		69.2		44.5		9-Jun-08		12:25:59		76.4		36

		29-Apr-08		14:07:10		71		42.5		29-Apr-08		14:06:20		70.41		48		29-Apr-08		14:07:53		68.61		46.5		9-Jun-08		14:25:59		77.61		35

		29-Apr-08		16:07:10		71		43		29-Apr-08		16:06:20		69.8		49		29-Apr-08		16:07:53		68.61		47		9-Jun-08		16:25:59		78.8		34.5

		29-Apr-08		18:07:10		71.6		41.5		29-Apr-08		18:06:20		69.2		48.5		29-Apr-08		18:07:53		68.61		45.5		9-Jun-08		18:25:59		78.2		35.5

		29-Apr-08		20:07:10		71		40		29-Apr-08		20:06:20		69.2		46.5		29-Apr-08		20:07:53		68.61		43.5		9-Jun-08		20:25:59		78.2		35.5

		29-Apr-08		22:07:10		71		39		29-Apr-08		22:06:20		69.2		47.5		29-Apr-08		22:07:53		68.61		42.5		9-Jun-08		22:25:59		76.4		35.5

		30-Apr-08		0:07:10		69.2		33		30-Apr-08		0:06:20		68		34		30-Apr-08		0:07:53		68		35.5		10-Jun-08		0:25:59		74.6		35.5

		30-Apr-08		2:07:10		69.2		35.5		30-Apr-08		2:06:20		68.61		37.5		30-Apr-08		2:07:53		68.61		37.5		10-Jun-08		2:25:59		73.4		36

		30-Apr-08		4:07:10		69.8		35		30-Apr-08		4:06:20		67.4		38.5		30-Apr-08		4:07:53		68.61		37		10-Jun-08		4:25:59		72.8		36

		30-Apr-08		6:07:10		70.41		35		30-Apr-08		6:06:20		69.2		39		30-Apr-08		6:07:53		68.61		38		10-Jun-08		6:25:59		72.21		37

		30-Apr-08		8:07:10		70.41		34		30-Apr-08		8:06:20		69.8		34		30-Apr-08		8:07:53		68		36.5		10-Jun-08		8:25:59		72.8		39

		30-Apr-08		10:07:10		69.2		34		30-Apr-08		10:06:20		69.8		35		30-Apr-08		10:07:53		67.4		37.5		10-Jun-08		10:25:59		73.4		38.5

		30-Apr-08		12:07:10		69.8		32.5		30-Apr-08		12:06:20		69.8		35		30-Apr-08		12:07:53		68		36		10-Jun-08		12:25:59		72.8		39

		30-Apr-08		14:07:10		69.8		33.5		30-Apr-08		14:06:20		69.2		34		30-Apr-08		14:07:53		68.61		36		10-Jun-08		14:25:59		72.8		39

		30-Apr-08		16:07:10		69.8		34		30-Apr-08		16:06:20		69.2		35		30-Apr-08		16:07:53		68.61		36.5		10-Jun-08		16:25:59		72.21		40

		30-Apr-08		18:07:10		69.8		31		30-Apr-08		18:06:20		69.2		32		30-Apr-08		18:07:53		68		33.5		10-Jun-08		18:25:59		72.8		42.5

		30-Apr-08		20:07:10		68.61		31.5		30-Apr-08		20:06:20		68.61		31.5		30-Apr-08		20:07:53		68		33.5		10-Jun-08		20:25:59		74.6		43

		30-Apr-08		22:07:10		69.2		31		30-Apr-08		22:06:20		68.61		32.5		30-Apr-08		22:07:53		68.61		33.5		10-Jun-08		22:25:59		76.4		40.5

		1-May-08		0:07:10		68.61		31.5		1-May-08		0:06:20		67.4		34		1-May-08		0:07:53		68		34		11-Jun-08		0:25:59		75.81		40.5

		1-May-08		2:07:10		68.61		30.5		1-May-08		2:06:20		66.2		33		1-May-08		2:07:53		68		32.5		11-Jun-08		2:25:59		75.2		39

		1-May-08		4:07:10		68		29.5		1-May-08		4:06:20		65.6		32		1-May-08		4:07:53		68		31		11-Jun-08		4:25:59		74.01		38

		1-May-08		6:07:10		68.61		29		1-May-08		6:06:20		65.6		31.5		1-May-08		6:07:53		68		30.5		11-Jun-08		6:25:59		72.8		37.5

		1-May-08		8:07:10		69.2		28		1-May-08		8:06:20		69.2		30		1-May-08		8:07:53		68.61		30.5		11-Jun-08		8:25:59		72.21		37

		1-May-08		10:07:10		69.8		26		1-May-08		10:06:20		70.41		27.5		1-May-08		10:07:53		68.61		29		11-Jun-08		10:25:59		72.8		33

		1-May-08		12:07:10		69.8		24		1-May-08		12:06:20		70.41		24.5		1-May-08		12:07:53		68.61		27		11-Jun-08		12:25:59		72.8		30.5

		1-May-08		14:07:10		70.41		25		1-May-08		14:06:20		71		26		1-May-08		14:07:53		69.8		27		11-Jun-08		14:25:59		74.01		30.5

		1-May-08		16:07:10		71		25.5		1-May-08		16:06:20		69.8		27.5		1-May-08		16:07:53		69.2		27.5		11-Jun-08		16:25:59		74.01		30.5

		1-May-08		18:07:10		70.41		29		1-May-08		18:06:20		70.41		29.5		1-May-08		18:07:53		69.8		30		11-Jun-08		18:25:59		73.4		32

		1-May-08		20:07:10		69.2		29.5		1-May-08		20:06:20		69.2		30		1-May-08		20:07:53		69.2		31		11-Jun-08		20:25:59		74.6		32.5

		1-May-08		22:07:10		69.2		30.5		1-May-08		22:06:20		69.8		30.5		1-May-08		22:07:53		69.2		32		11-Jun-08		22:25:59		75.2		32

		2-May-08		0:07:10		69.8		30.5		2-May-08		0:06:20		68		33		2-May-08		0:07:53		69.2		32.5		12-Jun-08		0:25:59		74.6		32

		2-May-08		2:07:10		69.8		30.5		2-May-08		2:06:20		67.4		33.5		2-May-08		2:07:53		69.2		32		12-Jun-08		2:25:59		73.4		32.5

		2-May-08		4:07:10		69.2		30.5		2-May-08		4:06:20		66.81		34		2-May-08		4:07:53		69.2		31.5		12-Jun-08		4:25:59		72.21		32.5

		2-May-08		6:07:10		69.2		30		2-May-08		6:06:20		66.81		34		2-May-08		6:07:53		69.2		32		12-Jun-08		6:25:59		71.6		32.5

		2-May-08		8:07:10		69.8		30.5		2-May-08		8:06:20		69.2		33		2-May-08		8:07:53		69.8		32		12-Jun-08		8:25:59		72.21		34.5

		2-May-08		10:07:10		69.8		30		2-May-08		10:06:20		69.8		31.5		2-May-08		10:07:53		69.8		31.5		12-Jun-08		10:25:59		73.4		34.5

		2-May-08		12:07:10		70.41		27		2-May-08		12:06:20		69.8		28		2-May-08		12:07:53		70.41		29.5		12-Jun-08		12:25:59		73.4		32.5

		2-May-08		14:07:10		71		23.5		2-May-08		14:06:20		71		25.5		2-May-08		14:07:53		69.8		26		12-Jun-08		14:25:59		72.8		29

		2-May-08		16:07:10		70.41		29.5		2-May-08		16:06:20		69.8		31		2-May-08		16:07:53		69.2		31		12-Jun-08		16:25:59		73.4		27.5

		2-May-08		18:07:10		70.41		30.5		2-May-08		18:06:20		70.41		31.5		2-May-08		18:07:53		69.8		32		12-Jun-08		18:25:59		73.4		29

		2-May-08		20:07:10		71		34		2-May-08		20:06:20		70.41		34		2-May-08		20:07:53		69.8		34		12-Jun-08		20:25:59		74.6		31.5

		2-May-08		22:07:10		70.41		29		2-May-08		22:06:20		70.41		30		2-May-08		22:07:53		70.41		31		12-Jun-08		22:25:59		75.2		32.5

		3-May-08		0:07:10		69.2		30		3-May-08		0:06:20		69.2		31		3-May-08		0:07:53		69.8		31.5		13-Jun-08		0:25:59		74.6		33

		3-May-08		2:07:10		70.41		33		3-May-08		2:06:20		68.61		36		3-May-08		2:07:53		69.8		34		13-Jun-08		2:25:59		73.4		33.5

		3-May-08		4:07:10		70.41		32.5		3-May-08		4:06:20		67.4		36		3-May-08		4:07:53		69.8		33.5		13-Jun-08		4:25:59		72.8		34

		3-May-08		6:07:10		70.41		32		3-May-08		6:06:20		66.81		36.5		3-May-08		6:07:53		69.8		33.5		13-Jun-08		6:25:59		71.6		35

		3-May-08		8:07:10		70.41		33.5		3-May-08		8:06:20		69.8		35.5		3-May-08		8:07:53		69.2		35		13-Jun-08		8:25:59		72.21		37

		3-May-08		10:07:10		70.41		34		3-May-08		10:06:20		70.41		35.5		3-May-08		10:07:53		69.8		35.5		13-Jun-08		10:25:59		72.21		37

		3-May-08		12:07:10		71		33.5		3-May-08		12:06:20		71		34		3-May-08		12:07:53		69.8		34.5		13-Jun-08		12:25:59		72.21		30.5

		3-May-08		14:07:10		71		36.5		3-May-08		14:06:20		71.6		35		3-May-08		14:07:53		69.8		36.5		13-Jun-08		14:25:59		73.4		27.5

		3-May-08		16:07:10		71		34		3-May-08		16:06:20		70.41		35.5		3-May-08		16:07:53		69.8		36.5		13-Jun-08		16:25:59		73.4		30.5

		3-May-08		18:07:10		71		37.5		3-May-08		18:06:20		71		40		3-May-08		18:07:53		69.8		39		13-Jun-08		18:25:59		73.4		28.5

		3-May-08		20:07:10		71		36.5		3-May-08		20:06:20		70.41		40		3-May-08		20:07:53		69.8		38		13-Jun-08		20:25:59		74.6		29

		3-May-08		22:07:10		71		35.5		3-May-08		22:06:20		69.8		39		3-May-08		22:07:53		69.8		37		13-Jun-08		22:25:59		75.81		29.5

		4-May-08		0:07:10		71		35		4-May-08		0:06:20		68		40		4-May-08		0:07:53		69.2		37		14-Jun-08		0:25:59		75.2		30.5

		4-May-08		2:07:10		70.41		35		4-May-08		2:06:20		66.81		41		4-May-08		2:07:53		69.8		36.5		14-Jun-08		2:25:59		74.01		31.5

		4-May-08		4:07:10		70.41		34.5		4-May-08		4:06:20		66.2		41		4-May-08		4:07:53		69.2		35.5		14-Jun-08		4:25:59		72.8		32

		4-May-08		6:07:10		69.8		33.5		4-May-08		6:06:20		65.6		40		4-May-08		6:07:53		69.8		35		14-Jun-08		6:25:59		72.21		33.5

		4-May-08		8:07:10		70.41		35.5		4-May-08		8:06:20		66.81		41.5		4-May-08		8:07:53		70.41		36		14-Jun-08		8:25:59		72.21		35.5

		4-May-08		10:07:10		70.41		36		4-May-08		10:06:20		69.8		39		4-May-08		10:07:53		70.41		37.5		14-Jun-08		10:25:59		72.8		37

		4-May-08		12:07:10		71		37		4-May-08		12:06:20		71		39.5		4-May-08		12:07:53		70.41		39		14-Jun-08		12:25:59		72.8		39.5

		4-May-08		14:07:10		71		39.5		4-May-08		14:06:20		70.41		45.5		4-May-08		14:07:53		68.61		42.5		14-Jun-08		14:25:59		73.4		38

		4-May-08		16:07:10		71		39.5		4-May-08		16:06:20		70.41		44.5		4-May-08		16:07:53		68.61		43.5		14-Jun-08		16:25:59		72.8		38.5

		4-May-08		18:07:10		71		40		4-May-08		18:06:20		69.8		48		4-May-08		18:07:53		69.2		43		14-Jun-08		18:25:59		73.4		38.5

		4-May-08		20:07:10		71		38.5		4-May-08		20:06:20		69.2		47		4-May-08		20:07:53		68.61		42		14-Jun-08		20:25:59		74.01		37

		4-May-08		22:07:10		71		38		4-May-08		22:06:20		69.8		44		4-May-08		22:07:53		68.61		40.5		14-Jun-08		22:25:59		74.01		37.5

		5-May-08		0:07:10		71		37.5		5-May-08		0:06:20		68.61		44		5-May-08		0:07:53		70.41		39.5		15-Jun-08		0:25:59		72.8		37

		5-May-08		2:07:10		71		37		5-May-08		2:06:20		68		44.5		5-May-08		2:07:53		70.41		38.5		15-Jun-08		2:25:59		72.21		37.5

		5-May-08		4:07:10		70.41		36.5		5-May-08		4:06:20		66.81		44.5		5-May-08		4:07:53		69.8		37.5		15-Jun-08		4:25:59		71.6		37.5

		5-May-08		6:07:10		69.8		35		5-May-08		6:06:20		66.2		43		5-May-08		6:07:53		69.8		37		15-Jun-08		6:25:59		71.6		37.5

		5-May-08		8:07:10		69.8		37		5-May-08		8:06:20		66.2		44.5		5-May-08		8:07:53		69.8		37.5		15-Jun-08		8:25:59		72.21		38

		5-May-08		10:07:10		69.8		38		5-May-08		10:06:20		68.61		44		5-May-08		10:07:53		69.8		39		15-Jun-08		10:25:59		72.21		39

		5-May-08		12:07:10		70.41		40		5-May-08		12:06:20		70.41		45		5-May-08		12:07:53		71		40.5		15-Jun-08		12:25:59		73.4		40

		5-May-08		14:07:10		71		40		5-May-08		14:06:20		71		44.5		5-May-08		14:07:53		71		41.5		15-Jun-08		14:25:59		74.6		41

		5-May-08		16:07:10		71		38		5-May-08		16:06:20		69.8		42		5-May-08		16:07:53		70.41		40		15-Jun-08		16:25:59		75.2		41.5

		5-May-08		18:07:10		71		37.5		5-May-08		18:06:20		70.41		41.5		5-May-08		18:07:53		70.41		39		15-Jun-08		18:25:59		75.81		41

		5-May-08		20:07:10		71		37		5-May-08		20:06:20		70.41		41.5		5-May-08		20:07:53		69.8		38.5		15-Jun-08		20:25:59		75.2		40

		5-May-08		22:07:10		70.41		37		5-May-08		22:06:20		69.8		41		5-May-08		22:07:53		69.8		38.5		15-Jun-08		22:25:59		74.01		39.5

		6-May-08		0:07:10		71		36.5		6-May-08		0:06:20		69.2		42		6-May-08		0:07:53		70.41		38		16-Jun-08		0:25:59		72.8		39

		6-May-08		2:07:10		71		36.5		6-May-08		2:06:20		67.4		43		6-May-08		2:07:53		70.41		37.5		16-Jun-08		2:25:59		72.21		39

		6-May-08		4:07:10		70.41		36		6-May-08		4:06:20		66.81		43		6-May-08		4:07:53		69.8		37		16-Jun-08		4:25:59		71.6		39

		6-May-08		6:07:10		69.8		35.5		6-May-08		6:06:20		65.6		43		6-May-08		6:07:53		69.2		37		16-Jun-08		6:25:59		71		39

		6-May-08		8:07:10		70.41		38		6-May-08		8:06:20		68		43.5		6-May-08		8:07:53		68.61		42		16-Jun-08		8:25:59		70.41		39.5

		6-May-08		10:07:10		70.41		39		6-May-08		10:06:20		71		44		6-May-08		10:07:53		67.4		41.5		16-Jun-08		10:25:59		70.41		40.5

		6-May-08		12:07:10		70.41		40.5		6-May-08		12:06:20		71.6		45		6-May-08		12:07:53		67.4		44		16-Jun-08		12:25:59		72.21		41.5

		6-May-08		14:07:10		71		40.5		6-May-08		14:06:20		71		44.5		6-May-08		14:07:53		67.4		44.5		16-Jun-08		14:25:59		73.4		42.5

		6-May-08		16:07:10		71		40		6-May-08		16:06:20		70.41		46.5		6-May-08		16:07:53		68.61		43.5		16-Jun-08		16:25:59		74.6		41

		6-May-08		18:07:10		70.41		39		6-May-08		18:06:20		69.2		45.5		6-May-08		18:07:53		68.61		41		16-Jun-08		18:25:59		75.2		40

		6-May-08		20:07:10		70.41		39.5		6-May-08		20:06:20		68.61		45		6-May-08		20:07:53		68.61		41.5		16-Jun-08		20:25:59		75.2		39

		6-May-08		22:07:10		70.41		38		6-May-08		22:06:20		69.2		44		6-May-08		22:07:53		68.61		41		16-Jun-08		22:25:59		74.01		38.5

		7-May-08		0:07:10		70.41		38.5		7-May-08		0:06:20		68.61		45		7-May-08		0:07:53		68.61		41		17-Jun-08		0:25:59		72.21		38

		7-May-08		2:07:10		70.41		38.5		7-May-08		2:06:20		68		46.5		7-May-08		2:07:53		68		41.5		17-Jun-08		2:25:59		71		37.5

		7-May-08		4:07:10		69.8		38		7-May-08		4:06:20		67.4		47		7-May-08		4:07:53		68.61		40.5		17-Jun-08		4:25:59		70.41		38.5

		7-May-08		6:07:10		70.41		39		7-May-08		6:06:20		66.81		47.5		7-May-08		6:07:53		68		42		17-Jun-08		6:25:59		70.41		39.5

		7-May-08		8:07:10		70.41		39		7-May-08		8:06:20		69.8		45		7-May-08		8:07:53		68.61		41.5		17-Jun-08		8:25:59		70.41		41.5

		7-May-08		10:07:10		71		38.5		7-May-08		10:06:20		70.41		45		7-May-08		10:07:53		68		42		17-Jun-08		10:25:59		71.6		42.5

		7-May-08		12:07:10		71		40.5		7-May-08		12:06:20		70.41		47		7-May-08		12:07:53		68		43.5		17-Jun-08		12:25:59		73.4		42.5

		7-May-08		14:07:10		71		43.5		7-May-08		14:06:20		69.8		51		7-May-08		14:07:53		68.61		46.5		17-Jun-08		14:25:59		74.01		43.5

		7-May-08		16:07:10		71		43		7-May-08		16:06:20		70.41		56		7-May-08		16:07:53		68.61		46.5		17-Jun-08		16:25:59		74.6		41

		7-May-08		18:07:10		70.41		43.5		7-May-08		18:06:20		71		50		7-May-08		18:07:53		68		46.5		17-Jun-08		18:25:59		74.01		40

		7-May-08		20:07:10		71		36.5		7-May-08		20:06:20		70.41		39		7-May-08		20:07:53		68		41		17-Jun-08		20:25:59		74.01		39.5

		7-May-08		22:07:10		71		34.5		7-May-08		22:06:20		69.8		36		7-May-08		22:07:53		68		38		17-Jun-08		22:25:59		74.01		38.5

		8-May-08		0:07:10		69.8		37		8-May-08		0:06:20		69.8		40.5		8-May-08		0:07:53		68		40		18-Jun-08		0:25:59		72.8		38

		8-May-08		2:07:10		70.41		37		8-May-08		2:06:20		68.61		41		8-May-08		2:07:53		69.2		39		18-Jun-08		2:25:59		71.6		37.5

		8-May-08		4:07:10		70.41		36		8-May-08		4:06:20		68		41.5		8-May-08		4:07:53		69.8		37.5		18-Jun-08		4:25:59		70.41		38.5

		8-May-08		6:07:10		71		34.5		8-May-08		6:06:20		68		39.5		8-May-08		6:07:53		68.61		38		18-Jun-08		6:25:59		70.41		39.5

		8-May-08		8:07:10		71		34.5		8-May-08		8:06:20		69.8		37		8-May-08		8:07:53		68.61		38		18-Jun-08		8:25:59		70.41		41.5

		8-May-08		10:07:10		70.41		36		8-May-08		10:06:20		70.41		38.5		8-May-08		10:07:53		68.61		38		18-Jun-08		10:25:59		72.8		42

		8-May-08		12:07:10		70.41		37		8-May-08		12:06:20		71		38.5		8-May-08		12:07:53		67.4		40.5		18-Jun-08		12:25:59		72.8		41.5

		8-May-08		14:07:10		70.41		39		8-May-08		14:06:20		71		41		8-May-08		14:07:53		67.4		43		18-Jun-08		14:25:59		72.8		42.5

		8-May-08		16:07:10		71		38.5		8-May-08		16:06:20		70.41		43		8-May-08		16:07:53		68		41.5		18-Jun-08		16:25:59		73.4		43

		8-May-08		18:07:10		71		39		8-May-08		18:06:20		71		41.5		8-May-08		18:07:53		68.61		42		18-Jun-08		18:25:59		74.01		34.5

		8-May-08		20:07:10		71		38		8-May-08		20:06:20		70.41		43.5		8-May-08		20:07:53		68		41.5		18-Jun-08		20:25:59		74.6		32

		8-May-08		22:07:10		70.41		37		8-May-08		22:06:20		69.8		41		8-May-08		22:07:53		68		40		18-Jun-08		22:25:59		74.6		30.5

		9-May-08		0:07:10		70.41		37		9-May-08		0:06:20		68.61		41.5		9-May-08		0:07:53		68		40		19-Jun-08		0:25:59		74.01		30.5

		9-May-08		2:07:10		70.41		36.5		9-May-08		2:06:20		67.4		42		9-May-08		2:07:53		68.61		39		19-Jun-08		2:25:59		73.4		31.5

		9-May-08		4:07:10		69.8		35.5		9-May-08		4:06:20		66.81		42.5		9-May-08		4:07:53		69.2		38		19-Jun-08		4:25:59		72.21		33

		9-May-08		6:07:10		71		35.5		9-May-08		6:06:20		66.81		41.5		9-May-08		6:07:53		69.2		37.5		19-Jun-08		6:25:59		71		33.5

		9-May-08		8:07:10		71		37		9-May-08		8:06:20		69.8		42		9-May-08		8:07:53		69.2		39		19-Jun-08		8:25:59		71		35.5

		9-May-08		10:07:10		70.41		38		9-May-08		10:06:20		71		40.5		9-May-08		10:07:53		68.61		40		19-Jun-08		10:25:59		72.8		35.5

		9-May-08		12:07:10		70.41		40		9-May-08		12:06:20		71.6		43		9-May-08		12:07:53		69.2		41.5		19-Jun-08		12:25:59		73.4		33.5

		9-May-08		14:07:10		70.41		39		9-May-08		14:06:20		69.8		45.5		9-May-08		14:07:53		68		42.5		19-Jun-08		14:25:59		72.21		35.5

		9-May-08		16:07:10		70.41		38		9-May-08		16:06:20		69.2		43		9-May-08		16:07:53		67.4		42.5		19-Jun-08		16:25:59		72.21		33.5

		9-May-08		18:07:10		70.41		38.5		9-May-08		18:06:20		68.61		42.5		9-May-08		18:07:53		68.61		41.5		19-Jun-08		18:25:59		74.01		28.5

		9-May-08		20:07:10		70.41		37		9-May-08		20:06:20		68.61		42		9-May-08		20:07:53		68		40		19-Jun-08		20:25:59		74.6		29

		9-May-08		22:07:10		69.8		36.5		9-May-08		22:06:20		68		41.5		9-May-08		22:07:53		68.61		39		19-Jun-08		22:25:59		75.2		27.5

		10-May-08		0:07:10		69.8		35.5		10-May-08		0:06:20		68		40.5		10-May-08		0:07:53		68		39		20-Jun-08		0:25:59		74.6		30

		10-May-08		2:07:10		69.8		34.5		10-May-08		2:06:20		66.81		40.5		10-May-08		2:07:53		68		37.5		20-Jun-08		2:25:59		73.4		31

		10-May-08		4:07:10		69.8		34		10-May-08		4:06:20		66.2		40.5		10-May-08		4:07:53		68.61		37		20-Jun-08		4:25:59		72.8		31.5

		10-May-08		6:07:10		70.41		33.5		10-May-08		6:06:20		65.6		39.5		10-May-08		6:07:53		68.61		35.5		20-Jun-08		6:25:59		71.6		32.5

		10-May-08		8:07:10		70.41		35.5		10-May-08		8:06:20		68		41.5		10-May-08		8:07:53		67.4		38.5		20-Jun-08		8:25:59		72.21		35

		10-May-08		10:07:10		69.8		34		10-May-08		10:06:20		70.41		35		10-May-08		10:07:53		68		37.5		20-Jun-08		10:25:59		73.4		36.5

		10-May-08		12:07:10		71		33.5		10-May-08		12:06:20		71		34.5		10-May-08		12:07:53		68.61		36.5		20-Jun-08		12:25:59		72.8		35

		10-May-08		14:07:10		71.6		32		10-May-08		14:06:20		70.41		34.5		10-May-08		14:07:53		68		35.5		20-Jun-08		14:25:59		72.8		33.5

		10-May-08		16:07:10		71.6		35		10-May-08		16:06:20		69.8		38.5		10-May-08		16:07:53		67.4		40.5		20-Jun-08		16:25:59		72.8		34

		10-May-08		18:07:10		71.6		36		10-May-08		18:06:20		69.2		39.5		10-May-08		18:07:53		67.4		41.5		20-Jun-08		18:25:59		72.8		31

		10-May-08		20:07:10		71		35.5		10-May-08		20:06:20		68.61		40.5		10-May-08		20:07:53		68		39.5		20-Jun-08		20:25:59		74.6		31.5

		10-May-08		22:07:10		70.41		35.5		10-May-08		22:06:20		68.61		39.5		10-May-08		22:07:53		68		38.5		20-Jun-08		22:25:59		75.81		30.5

		11-May-08		0:07:10		70.41		35.5		11-May-08		0:06:20		68.61		39.5		11-May-08		0:07:53		68		38.5		21-Jun-08		0:25:59		75.2		31.5

		11-May-08		2:07:10		70.41		35		11-May-08		2:06:20		67.4		40		11-May-08		2:07:53		68		38		21-Jun-08		2:25:59		74.01		32

		11-May-08		4:07:10		69.8		34		11-May-08		4:06:20		66.81		40.5		11-May-08		4:07:53		68.61		37		21-Jun-08		4:25:59		73.4		32.5

		11-May-08		6:07:10		70.41		34.5		11-May-08		6:06:20		68		39		11-May-08		6:07:53		68.61		36.5		21-Jun-08		6:25:59		72.21		34

		11-May-08		8:07:10		70.41		35.5		11-May-08		8:06:20		69.8		39		11-May-08		8:07:53		68		38.5		21-Jun-08		8:25:59		72.8		35.5

		11-May-08		10:07:10		70.41		35		11-May-08		10:06:20		69.8		36.5		11-May-08		10:07:53		68.61		37.5		21-Jun-08		10:25:59		72.8		35.5

		11-May-08		12:07:10		71		35.5		11-May-08		12:06:20		70.41		38		11-May-08		12:07:53		68.61		39		21-Jun-08		12:25:59		72.8		33.5

		11-May-08		14:07:10		71.6		38		11-May-08		14:06:20		69.2		41		11-May-08		14:07:53		68.61		41.5		21-Jun-08		14:25:59		72.8		32

		11-May-08		16:07:10		71.6		37.5		11-May-08		16:06:20		68.61		40		11-May-08		16:07:53		68.61		40.5		21-Jun-08		16:25:59		73.4		30

		11-May-08		18:07:10		71.6		38.5		11-May-08		18:06:20		69.2		44		11-May-08		18:07:53		68.61		42.5		21-Jun-08		18:25:59		71.6		27

		11-May-08		20:07:10		71.6		39		11-May-08		20:06:20		69.2		50		11-May-08		20:07:53		68.61		43.5		21-Jun-08		20:25:59		74.01		26.5

		11-May-08		22:07:10		71		38.5		11-May-08		22:06:20		68.61		46.5		11-May-08		22:07:53		69.2		41.5		21-Jun-08		22:25:59		75.81		25.5

		12-May-08		0:07:10		69.8		38.5		12-May-08		0:06:20		68.61		47.5		12-May-08		0:07:53		69.2		41		22-Jun-08		0:25:59		75.81		27.5

		12-May-08		2:07:10		70.41		39		12-May-08		2:06:20		68.61		47.5		12-May-08		2:07:53		69.8		41		22-Jun-08		2:25:59		75.2		29

		12-May-08		4:07:10		70.41		38		12-May-08		4:06:20		68		47		12-May-08		4:07:53		69.8		40		22-Jun-08		4:25:59		74.01		29.5

		12-May-08		6:07:10		71		38		12-May-08		6:06:20		67.4		47		12-May-08		6:07:53		69.8		40		22-Jun-08		6:25:59		74.6		30

		12-May-08		8:07:10		71		38.5		12-May-08		8:06:20		67.4		47.5		12-May-08		8:07:53		69.8		40.5		22-Jun-08		8:25:59		75.2		30.5

		12-May-08		10:07:10		70.41		39		12-May-08		10:06:20		68.61		45		12-May-08		10:07:53		69.8		40.5		22-Jun-08		10:25:59		77		31

		12-May-08		12:07:10		70.41		40		12-May-08		12:06:20		69.2		44.5		12-May-08		12:07:53		69.8		41.5		22-Jun-08		12:25:59		78.2		29.5

		12-May-08		14:07:10		71		33		12-May-08		14:06:20		69.2		32		12-May-08		14:07:53		69.8		34.5		22-Jun-08		14:25:59		79.41		28.5

		12-May-08		16:07:10		71		29.5		12-May-08		16:06:20		69.8		29.5		12-May-08		16:07:53		69.8		31		22-Jun-08		16:25:59		79.41		27

		12-May-08		18:07:10		71.6		31.5		12-May-08		18:06:20		69.8		33		12-May-08		18:07:53		69.8		33		22-Jun-08		18:25:59		78.8		25

		12-May-08		20:07:10		71.6		30.5		12-May-08		20:06:20		69.2		33		12-May-08		20:07:53		69.8		33		22-Jun-08		20:25:59		78.8		25

		12-May-08		22:07:10		70.41		30.5		12-May-08		22:06:20		68		33		12-May-08		22:07:53		69.8		32.5		22-Jun-08		22:25:59		77.61		27

		13-May-08		0:07:10		68.61		31		13-May-08		0:06:20		68.61		32.5		13-May-08		0:07:53		68.61		32.5		23-Jun-08		0:25:59		76.4		29

		13-May-08		2:07:10		68		32		13-May-08		2:06:20		68		33		13-May-08		2:07:53		68		33		23-Jun-08		2:25:59		75.2		31

		13-May-08		4:07:10		68		31.5		13-May-08		4:06:20		68.61		32		13-May-08		4:07:53		68		32.5		23-Jun-08		4:25:59		74.01		32

		13-May-08		6:07:10		68		30.5		13-May-08		6:06:20		68.61		31		13-May-08		6:07:53		68		32		23-Jun-08		6:25:59		73.4		32.5

		13-May-08		8:07:10		68.61		29		13-May-08		8:06:20		69.2		31		13-May-08		8:07:53		68.61		31.5		23-Jun-08		8:25:59		72.8		34

		13-May-08		10:07:10		69.8		28		13-May-08		10:06:20		70.41		29.5		13-May-08		10:07:53		68.61		30.5		23-Jun-08		10:25:59		74.01		35.5

		13-May-08		12:07:10		71		27.5		13-May-08		12:06:20		71.6		29		13-May-08		12:07:53		68.61		30.5		23-Jun-08		12:25:59		75.2		35.5

		13-May-08		14:07:10		71.6		28.5		13-May-08		14:06:20		71		30		13-May-08		14:07:53		68.61		31.5		23-Jun-08		14:25:59		76.4		36

		13-May-08		16:07:10		71.6		29.5		13-May-08		16:06:20		69.2		32.5		13-May-08		16:07:53		68.61		33		23-Jun-08		16:25:59		77		36

		13-May-08		18:07:10		71.6		30.5		13-May-08		18:06:20		70.41		33		13-May-08		18:07:53		68.61		34.5		23-Jun-08		18:25:59		77.61		35.5

		13-May-08		20:07:10		71		30		13-May-08		20:06:20		69.8		31.5		13-May-08		20:07:53		68		33.5		23-Jun-08		20:25:59		77.61		34.5

		13-May-08		22:07:10		70.41		30.5		13-May-08		22:06:20		70.41		31.5		13-May-08		22:07:53		68.61		33		23-Jun-08		22:25:59		75.81		34.5

		14-May-08		0:07:10		69.2		31		14-May-08		0:06:20		69.8		32		14-May-08		0:07:53		68		33.5		24-Jun-08		0:25:59		74.6		34.5

		14-May-08		2:07:10		68		32.5		14-May-08		2:06:20		69.2		33.5		14-May-08		2:07:53		68		34.5		24-Jun-08		2:25:59		73.4		34.5

		14-May-08		4:07:10		68		33		14-May-08		4:06:20		69.2		34		14-May-08		4:07:53		68		34.5		24-Jun-08		4:25:59		72.21		34.5

		14-May-08		6:07:10		68.61		33		14-May-08		6:06:20		69.2		34		14-May-08		6:07:53		68		35		24-Jun-08		6:25:59		71		36.5

		14-May-08		8:07:10		69.2		34		14-May-08		8:06:20		70.41		36.5		14-May-08		8:07:53		68		36		24-Jun-08		8:25:59		71		39

		14-May-08		10:07:10		71		34		14-May-08		10:06:20		71		36		14-May-08		10:07:53		67.4		38		24-Jun-08		10:25:59		72.21		40.5

		14-May-08		12:07:10		71.6		28.5		14-May-08		12:06:20		70.41		31.5		14-May-08		12:07:53		68		33		24-Jun-08		12:25:59		72.21		41.5

		14-May-08		14:07:10		71.6		29.5		14-May-08		14:06:20		70.41		32		14-May-08		14:07:53		68		34		24-Jun-08		14:25:59		73.4		39.5

		14-May-08		16:07:10		71.6		26.5		14-May-08		16:06:20		71		28		14-May-08		16:07:53		68		30		24-Jun-08		16:25:59		74.01		39

		14-May-08		18:07:10		71.6		27.5		14-May-08		18:06:20		71		28		14-May-08		18:07:53		68		30.5		24-Jun-08		18:25:59		74.01		38.5

		14-May-08		20:07:10		71.6		35		14-May-08		20:06:20		70.41		39.5		14-May-08		20:07:53		68		39.5		24-Jun-08		20:25:59		74.01		39.5

		14-May-08		22:07:10		71		36		14-May-08		22:06:20		69.8		41		14-May-08		22:07:53		68		40		24-Jun-08		22:25:59		75.2		37

		15-May-08		0:07:10		70.41		36.5		15-May-08		0:06:20		69.8		41		15-May-08		0:07:53		68.61		39.5		25-Jun-08		0:25:59		73.4		37

		15-May-08		2:07:10		69.8		37		15-May-08		2:06:20		69.2		42		15-May-08		2:07:53		68.61		39.5		25-Jun-08		2:25:59		72.21		37

		15-May-08		4:07:10		69.8		38		15-May-08		4:06:20		69.8		42.5		15-May-08		4:07:53		69.2		40.5		25-Jun-08		4:25:59		71		37

		15-May-08		6:07:10		70.41		39		15-May-08		6:06:20		69.8		42.5		15-May-08		6:07:53		68.61		41		25-Jun-08		6:25:59		70.41		38

		15-May-08		8:07:10		71		40		15-May-08		8:06:20		70.41		48.5		15-May-08		8:07:53		68		43.5		25-Jun-08		8:25:59		70.41		40.5

		15-May-08		10:07:10		71.6		40.5		15-May-08		10:06:20		71		46		15-May-08		10:07:53		67.4		46.5		25-Jun-08		10:25:59		72.8		41.5

		15-May-08		12:07:10		71.6		40.5		15-May-08		12:06:20		70.41		46.5		15-May-08		12:07:53		68		46.5		25-Jun-08		12:25:59		73.4		41

		15-May-08		14:07:10		71.6		38		15-May-08		14:06:20		69.8		41		15-May-08		14:07:53		68		43		25-Jun-08		14:25:59		72.8		42

		15-May-08		16:07:10		71.6		37.5		15-May-08		16:06:20		69.8		40.5		15-May-08		16:07:53		68		42.5		25-Jun-08		16:25:59		72.8		41.5

		15-May-08		18:07:10		71.6		39		15-May-08		18:06:20		68.61		42.5		15-May-08		18:07:53		69.2		43		25-Jun-08		18:25:59		74.01		39.5

		15-May-08		20:07:10		71.6		39		15-May-08		20:06:20		68.61		44		15-May-08		20:07:53		68.61		43.5		25-Jun-08		20:25:59		74.01		41

		15-May-08		22:07:10		71.6		37.5		15-May-08		22:06:20		68		44		15-May-08		22:07:53		68.61		42		25-Jun-08		22:25:59		74.6		38.5

		16-May-08		0:07:10		72.21		37		16-May-08		0:06:20		68		42.5		16-May-08		0:07:53		68.61		41.5		26-Jun-08		0:25:59		74.01		37.5

		16-May-08		2:07:10		71.6		37		16-May-08		2:06:20		68		43		16-May-08		2:07:53		69.2		40.5		26-Jun-08		2:25:59		72.8		37.5

		16-May-08		4:07:10		71.6		36.5		16-May-08		4:06:20		68		43		16-May-08		4:07:53		69.2		40.5		26-Jun-08		4:25:59		71.6		38

		16-May-08		6:07:10		71.6		36		16-May-08		6:06:20		68.61		42		16-May-08		6:07:53		69.2		39.5		26-Jun-08		6:25:59		71		38.5

		16-May-08		8:07:10		72.21		36.5		16-May-08		8:06:20		69.8		42		16-May-08		8:07:53		68.61		41		26-Jun-08		8:25:59		71		40.5

		16-May-08		10:07:10		71.6		38		16-May-08		10:06:20		69.2		43		16-May-08		10:07:53		68		43		26-Jun-08		10:25:59		73.4		40.5

		16-May-08		12:07:10		71.6		39.5		16-May-08		12:06:20		70.41		43.5		16-May-08		12:07:53		68		44		26-Jun-08		12:25:59		72.21		43

		16-May-08		14:07:10		71.6		39		16-May-08		14:06:20		70.41		43		16-May-08		14:07:53		68		44		26-Jun-08		14:25:59		72.21		44

		16-May-08		16:07:10		71.6		40		16-May-08		16:06:20		69.2		46		16-May-08		16:07:53		68.61		45		26-Jun-08		16:25:59		72.21		43.5

		16-May-08		18:07:10		71.6		40.5		16-May-08		18:06:20		69.2		45		16-May-08		18:07:53		68.61		45		26-Jun-08		18:25:59		71.6		43

		16-May-08		20:07:10		71.6		42		16-May-08		20:06:20		69.2		48.5		16-May-08		20:07:53		69.2		46.5		26-Jun-08		20:25:59		72.8		40.5

		16-May-08		22:07:10		72.21		41		16-May-08		22:06:20		68.61		54.5		16-May-08		22:07:53		68		46.5		26-Jun-08		22:25:59		73.4		40.5

		17-May-08		0:07:10		72.21		39.5		17-May-08		0:06:20		68.61		50		17-May-08		0:07:53		68.61		44.5		27-Jun-08		0:25:59		72.8		39.5

		17-May-08		2:07:10		72.21		39		17-May-08		2:06:20		68.61		47		17-May-08		2:07:53		68.61		43.5		27-Jun-08		2:25:59		71.6		39

		17-May-08		4:07:10		71.6		39		17-May-08		4:06:20		68		51		17-May-08		4:07:53		68.61		43		27-Jun-08		4:25:59		71		39

		17-May-08		6:07:10		71.6		39		17-May-08		6:06:20		68.61		53		17-May-08		6:07:53		69.2		43		27-Jun-08		6:25:59		70.41		39.5

		17-May-08		8:07:10		72.21		40		17-May-08		8:06:20		69.8		55.5		17-May-08		8:07:53		68		45.5		27-Jun-08		8:25:59		70.41		41

		17-May-08		10:07:10		72.21		40.5		17-May-08		10:06:20		69.8		53.5		17-May-08		10:07:53		68		46		27-Jun-08		10:25:59		72.8		42.5

		17-May-08		12:07:10		71		44.5		17-May-08		12:06:20		69.8		50		17-May-08		12:07:53		68.61		49.5		27-Jun-08		12:25:59		72.21		43

		17-May-08		14:07:10		71.6		45		17-May-08		14:06:20		70.41		52.5		17-May-08		14:07:53		68		51		27-Jun-08		14:25:59		72.21		44.5

		17-May-08		16:07:10		71.6		44.5		17-May-08		16:06:20		69.8		51		17-May-08		16:07:53		68.61		49.5		27-Jun-08		16:25:59		72.8		44

		17-May-08		18:07:10		71.6		41.5		17-May-08		18:06:20		69.2		45.5		17-May-08		18:07:53		68.61		45.5		27-Jun-08		18:25:59		72.8		41

		17-May-08		20:07:10		71.6		41.5		17-May-08		20:06:20		68.61		49		17-May-08		20:07:53		68.61		46		27-Jun-08		20:25:59		73.4		41.5

		17-May-08		22:07:10		72.21		39.5		17-May-08		22:06:20		69.2		48		17-May-08		22:07:53		68		44.5		27-Jun-08		22:25:59		74.01		40

		18-May-08		0:07:10		72.21		39		18-May-08		0:06:20		68		50.5		18-May-08		0:07:53		68.61		43.5		28-Jun-08		0:25:59		73.4		39.5

		18-May-08		2:07:10		71.6		40		18-May-08		2:06:20		68		52		18-May-08		2:07:53		68.61		43.5		28-Jun-08		2:25:59		72.21		39.5

		18-May-08		4:07:10		71		40		18-May-08		4:06:20		68		52.5		18-May-08		4:07:53		69.2		43		28-Jun-08		4:25:59		71.6		39.5

		18-May-08		6:07:10		70.41		39.5		18-May-08		6:06:20		68		50.5		18-May-08		6:07:53		69.2		42		28-Jun-08		6:25:59		71		40

		18-May-08		8:07:10		71		40.5		18-May-08		8:06:20		68.61		53.5		18-May-08		8:07:53		68.61		44		28-Jun-08		8:25:59		71		42

		18-May-08		10:07:10		71.6		42.5		18-May-08		10:06:20		69.2		56.5		18-May-08		10:07:53		68.61		46.5		28-Jun-08		10:25:59		73.4		43

		18-May-08		12:07:10		71.6		44.5		18-May-08		12:06:20		69.2		53.5		18-May-08		12:07:53		68.61		49.5		28-Jun-08		12:25:59		72.8		44

		18-May-08		14:07:10		72.21		48.5		18-May-08		14:06:20		69.2		58.5		18-May-08		14:07:53		68.61		54		28-Jun-08		14:25:59		72.21		45

		18-May-08		16:07:10		72.21		45		18-May-08		16:06:20		68.61		63.5		18-May-08		16:07:53		68.61		51.5		28-Jun-08		16:25:59		72.8		45.5

		18-May-08		18:07:10		72.21		43		18-May-08		18:06:20		68.61		60.5		18-May-08		18:07:53		68.61		49.5		28-Jun-08		18:25:59		72.8		43.5

		18-May-08		20:07:10		72.21		40.5		18-May-08		20:06:20		68.61		52.5		18-May-08		20:07:53		68		46		28-Jun-08		20:25:59		72.8		43.5

		18-May-08		22:07:10		72.21		39		18-May-08		22:06:20		68		51.5		18-May-08		22:07:53		68.61		43.5		28-Jun-08		22:25:59		72.8		42.5

		19-May-08		0:07:10		71		39		19-May-08		0:06:20		68		49.5		19-May-08		0:07:53		69.2		42		29-Jun-08		0:25:59		72.21		42.5

		19-May-08		2:07:10		70.41		39.5		19-May-08		2:06:20		68		49		19-May-08		2:07:53		69.2		42		29-Jun-08		2:25:59		71.6		42.5

		19-May-08		4:07:10		70.41		39		19-May-08		4:06:20		67.4		48		19-May-08		4:07:53		69.2		41.5		29-Jun-08		4:25:59		71		43

		19-May-08		6:07:10		71		39		19-May-08		6:06:20		67.4		49		19-May-08		6:07:53		69.2		41.5		29-Jun-08		6:25:59		71		43.5

		19-May-08		8:07:10		71		39.5		19-May-08		8:06:20		68		49		19-May-08		8:07:53		69.2		42		29-Jun-08		8:25:59		71		44

		19-May-08		10:07:10		70.41		40.5		19-May-08		10:06:20		68		48.5		19-May-08		10:07:53		69.2		43		29-Jun-08		10:25:59		71.6		44.5

		19-May-08		12:07:10		71		41.5		19-May-08		12:06:20		68.61		51		19-May-08		12:07:53		69.2		44.5		29-Jun-08		12:25:59		72.21		45.5

		19-May-08		14:07:10		71.6		41.5		19-May-08		14:06:20		68		54.5		19-May-08		14:07:53		69.8		45		29-Jun-08		14:25:59		74.01		45.5

		19-May-08		16:07:10		72.21		42		19-May-08		16:06:20		68.61		51.5		19-May-08		16:07:53		69.2		46		29-Jun-08		16:25:59		75.2		44.5

		19-May-08		18:07:10		72.21		40		19-May-08		18:06:20		68		55		19-May-08		18:07:53		69.2		44.5		29-Jun-08		18:25:59		75.81		43.5

		19-May-08		20:07:10		72.21		39		19-May-08		20:06:20		68.61		50.5		19-May-08		20:07:53		69.2		43		29-Jun-08		20:25:59		75.2		43

		19-May-08		22:07:10		71		39		19-May-08		22:06:20		67.4		52.5		19-May-08		22:07:53		69.2		42		29-Jun-08		22:25:59		74.01		42.5

		20-May-08		0:07:10		71		39.5		20-May-08		0:06:20		67.4		51		20-May-08		0:07:53		69.2		42		30-Jun-08		0:25:59		72.21		42.5

		20-May-08		2:07:10		71		39.5		20-May-08		2:06:20		68		50		20-May-08		2:07:53		69.2		42		30-Jun-08		2:25:59		71.6		42.5

		20-May-08		4:07:10		70.41		39.5		20-May-08		4:06:20		67.4		49.5		20-May-08		4:07:53		69.2		41.5		30-Jun-08		4:25:59		71		42.5

		20-May-08		6:07:10		71		39.5		20-May-08		6:06:20		68		49.5		20-May-08		6:07:53		69.2		41.5		30-Jun-08		6:25:59		70.41		43

		20-May-08		8:07:10		71		39		20-May-08		8:06:20		68.61		50.5		20-May-08		8:07:53		68.61		44		30-Jun-08		8:25:59		70.41		43.5

		20-May-08		10:07:10		71		39		20-May-08		10:06:20		71		44.5		20-May-08		10:07:53		68.61		43		30-Jun-08		10:25:59		70.41		44

		20-May-08		12:07:10		71		41		20-May-08		12:06:20		71		49.5		20-May-08		12:07:53		68		45		30-Jun-08		12:25:59		72.21		44.5

		20-May-08		14:07:10		71		43		20-May-08		14:06:20		71		55.5		20-May-08		14:07:53		68		48		30-Jun-08		14:25:59		73.4		44.5

		20-May-08		16:07:10		71.6		42		20-May-08		16:06:20		70.41		49.5		20-May-08		16:07:53		68.61		46.5		30-Jun-08		16:25:59		74.6		44.5

		20-May-08		18:07:10		71.6		41		20-May-08		18:06:20		69.8		51		20-May-08		18:07:53		69.2		44.5		30-Jun-08		18:25:59		75.2		43

		20-May-08		20:07:10		71		39		20-May-08		20:06:20		69.8		48.5		20-May-08		20:07:53		69.2		42.5		30-Jun-08		20:25:59		75.2		42.5

		20-May-08		22:07:10		71		39.5		20-May-08		22:06:20		69.8		48		20-May-08		22:07:53		69.8		41.5		30-Jun-08		22:25:59		73.4		42

		21-May-08		0:07:10		70.41		40		21-May-08		0:06:20		69.2		48.5		21-May-08		0:07:53		69.2		42		1-Jul-08		0:25:59		72.21		42

		21-May-08		2:07:10		70.41		40		21-May-08		2:06:20		68.61		48.5		21-May-08		2:07:53		69.8		42		1-Jul-08		2:25:59		71.6		42

		21-May-08		4:07:10		71		39.5		21-May-08		4:06:20		68.61		48		21-May-08		4:07:53		69.2		41.5		1-Jul-08		4:25:59		71		42

		21-May-08		6:07:10		71		39.5		21-May-08		6:06:20		68		48.5		21-May-08		6:07:53		69.8		41		1-Jul-08		6:25:59		71		43

		21-May-08		8:07:10		71		39.5		21-May-08		8:06:20		70.41		48.5		21-May-08		8:07:53		68.61		42		1-Jul-08		8:25:59		70.41		45

		21-May-08		10:07:10		71		40		21-May-08		10:06:20		71		47		21-May-08		10:07:53		68		43		1-Jul-08		10:25:59		72.21		45

		21-May-08		12:07:10		71		41		21-May-08		12:06:20		71		51		21-May-08		12:07:53		68.61		44.5		1-Jul-08		12:25:59		72.21		45

		21-May-08		14:07:10		71		44		21-May-08		14:06:20		71.6		54		21-May-08		14:07:53		68		48.5		1-Jul-08		14:25:59		72.8		46.5

		21-May-08		16:07:10		71		39.5		21-May-08		16:06:20		71		45		21-May-08		16:07:53		69.2		43.5		1-Jul-08		16:25:59		72.8		46.5

		21-May-08		18:07:10		71.6		32		21-May-08		18:06:20		71		34		21-May-08		18:07:53		69.2		36.5		1-Jul-08		18:25:59		72.8		44.5

		21-May-08		20:07:10		71		30		21-May-08		20:06:20		70.41		30		21-May-08		20:07:53		69.8		31.5		1-Jul-08		20:25:59		74.01		42

		21-May-08		22:07:10		70.41		36		21-May-08		22:06:20		70.41		39		21-May-08		22:07:53		69.8		38		1-Jul-08		22:25:59		74.01		43.5

		22-May-08		0:07:10		69.2		35		22-May-08		0:06:20		69.2		37.5		22-May-08		0:07:53		68.61		37		2-Jul-08		0:25:59		73.4		43

		22-May-08		2:07:10		68.61		34.5		22-May-08		2:06:20		69.2		35.5		22-May-08		2:07:53		68.61		36.5		2-Jul-08		2:25:59		72.21		43

		22-May-08		4:07:10		68.61		34		22-May-08		4:06:20		69.2		35		22-May-08		4:07:53		68.61		35		2-Jul-08		4:25:59		72.21		43.5

		22-May-08		6:07:10		69.8		32.5		22-May-08		6:06:20		69.2		34.5		22-May-08		6:07:53		69.2		34.5		2-Jul-08		6:25:59		71.6		44.5

		22-May-08		8:07:10		69.8		32.5		22-May-08		8:06:20		71		34.5		22-May-08		8:07:53		68.61		35		2-Jul-08		8:25:59		71		46.5

		22-May-08		10:07:10		70.41		33.5		22-May-08		10:06:20		71.6		34		22-May-08		10:07:53		68.61		35.5		2-Jul-08		10:25:59		72.21		47.5

		22-May-08		12:07:10		71		33.5		22-May-08		12:06:20		70.41		35.5		22-May-08		12:07:53		69.2		36		2-Jul-08		12:25:59		72.21		46.5

		22-May-08		14:07:10		71		34.5		22-May-08		14:06:20		69.8		37		22-May-08		14:07:53		68.61		38		2-Jul-08		14:25:59		72.21		47.5

		22-May-08		16:07:10		71		35		22-May-08		16:06:20		69.2		38		22-May-08		16:07:53		68.61		38.5		2-Jul-08		16:25:59		72.8		45.5

		22-May-08		18:07:10		71		35		22-May-08		18:06:20		68.61		37.5		22-May-08		18:07:53		68		38		2-Jul-08		18:25:59		72.8		44.5

		22-May-08		20:07:10		70.41		34.5		22-May-08		20:06:20		68.61		37		22-May-08		20:07:53		68		37		2-Jul-08		20:25:59		73.4		42.5

		22-May-08		22:07:10		69.2		33.5		22-May-08		22:06:20		68		36.5		22-May-08		22:07:53		68.61		36		2-Jul-08		22:25:59		74.01		43

		23-May-08		0:07:10		68.61		33.5		23-May-08		0:06:20		68		36		23-May-08		0:07:53		68		35.5		3-Jul-08		0:25:59		72.8		42.5

		23-May-08		2:07:10		68		32.5		23-May-08		2:06:20		68		34.5		23-May-08		2:07:53		68		34.5		3-Jul-08		2:25:59		71.6		42

		23-May-08		4:07:10		68.61		31		23-May-08		4:06:20		68		32.5		23-May-08		4:07:53		68.61		33		3-Jul-08		4:25:59		71		42.5

		23-May-08		6:07:10		69.8		30		23-May-08		6:06:20		68		32		23-May-08		6:07:53		69.2		32		3-Jul-08		6:25:59		70.41		43

		23-May-08		8:07:10		69.8		30		23-May-08		8:06:20		68.61		33		23-May-08		8:07:53		69.2		32		3-Jul-08		8:25:59		71		44.5

		23-May-08		10:07:10		70.41		30		23-May-08		10:06:20		68.61		32.5		23-May-08		10:07:53		68		32		3-Jul-08		10:25:59		72.21		45

		23-May-08		12:07:10		71		25		23-May-08		12:06:20		69.2		27.5		23-May-08		12:07:53		68		28.5		3-Jul-08		12:25:59		71.6		46.5

		23-May-08		14:07:10		71		28.5		23-May-08		14:06:20		68.61		30		23-May-08		14:07:53		67.4		31		3-Jul-08		14:25:59		72.21		46

		23-May-08		16:07:10		71		29.5		23-May-08		16:06:20		68		33		23-May-08		16:07:53		68.61		32.5		3-Jul-08		16:25:59		72.21		45.5

		23-May-08		18:07:10		71		32		23-May-08		18:06:20		68.61		34.5		23-May-08		18:07:53		68.61		35		3-Jul-08		18:25:59		73.4		44

		23-May-08		20:07:10		71		33.5		23-May-08		20:06:20		69.2		36		23-May-08		20:07:53		68.61		36		3-Jul-08		20:25:59		74.01		42

		23-May-08		22:07:10		70.41		33		23-May-08		22:06:20		68.61		37		23-May-08		22:07:53		68.61		36		3-Jul-08		22:25:59		74.6		42

		24-May-08		0:07:10		69.2		33.5		24-May-08		0:06:20		68		37		24-May-08		0:07:53		68.61		36		4-Jul-08		0:25:59		73.4		41.5

		24-May-08		2:07:10		68.61		33.5		24-May-08		2:06:20		68		37		24-May-08		2:07:53		68		36		4-Jul-08		2:25:59		72.21		41.5

		24-May-08		4:07:10		69.2		33		24-May-08		4:06:20		67.4		37		24-May-08		4:07:53		68.61		35		4-Jul-08		4:25:59		71.6		41.5

		24-May-08		6:07:10		70.41		32.5		24-May-08		6:06:20		68		36		24-May-08		6:07:53		69.2		34.5		4-Jul-08		6:25:59		71		42

		24-May-08		8:07:10		70.41		32.5		24-May-08		8:06:20		67.4		38.5		24-May-08		8:07:53		68.61		35.5		4-Jul-08		8:25:59		71		44.5

		24-May-08		10:07:10		70.41		34		24-May-08		10:06:20		70.41		36		24-May-08		10:07:53		68.61		36.5		4-Jul-08		10:25:59		71.6		45

		24-May-08		12:07:10		71		35		24-May-08		12:06:20		71		36		24-May-08		12:07:53		69.2		36.5		4-Jul-08		12:25:59		72.21		48.5

		24-May-08		14:07:10		71		34		24-May-08		14:06:20		71		37		24-May-08		14:07:53		68		37.5		4-Jul-08		14:25:59		73.4		50

		24-May-08		16:07:10		71		34.5		24-May-08		16:06:20		69.8		37		24-May-08		16:07:53		69.2		37		4-Jul-08		16:25:59		72.8		49

		24-May-08		18:07:10		70.41		35.5		24-May-08		18:06:20		70.41		39		24-May-08		18:07:53		69.2		38		4-Jul-08		18:25:59		73.4		48.5

		24-May-08		20:07:10		70.41		36.5		24-May-08		20:06:20		69.8		41		24-May-08		20:07:53		68.61		39		4-Jul-08		20:25:59		74.01		46

		24-May-08		22:07:10		71		36.5		24-May-08		22:06:20		69.2		42.5		24-May-08		22:07:53		68.61		39.5		4-Jul-08		22:25:59		74.01		47

		25-May-08		0:07:10		70.41		37		25-May-08		0:06:20		69.2		42.5		25-May-08		0:07:53		69.2		39.5		5-Jul-08		0:25:59		73.4		46.5

		25-May-08		2:07:10		70.41		37		25-May-08		2:06:20		68.61		42.5		25-May-08		2:07:53		69.2		39		5-Jul-08		2:25:59		72.21		46

		25-May-08		4:07:10		70.41		37.5		25-May-08		4:06:20		68.61		43		25-May-08		4:07:53		69.2		39		5-Jul-08		4:25:59		71.6		45.5

		25-May-08		6:07:10		70.41		37.5		25-May-08		6:06:20		68.61		45		25-May-08		6:07:53		69.2		39.5		5-Jul-08		6:25:59		71		46.5

		25-May-08		8:07:10		70.41		38		25-May-08		8:06:20		68.61		45		25-May-08		8:07:53		69.2		39.5		5-Jul-08		8:25:59		71		48

		25-May-08		10:07:10		70.41		39.5		25-May-08		10:06:20		68.61		48		25-May-08		10:07:53		69.2		41.5		5-Jul-08		10:25:59		72.21		48

		25-May-08		12:07:10		70.41		40		25-May-08		12:06:20		69.2		50		25-May-08		12:07:53		69.8		42		5-Jul-08		12:25:59		72.21		48.5

		25-May-08		14:07:10		69.8		37.5		25-May-08		14:06:20		68.61		46		25-May-08		14:07:53		69.8		40		5-Jul-08		14:25:59		73.4		48

		25-May-08		16:07:10		69.8		38.5		25-May-08		16:06:20		68.61		44.5		25-May-08		16:07:53		69.2		39.5		5-Jul-08		16:25:59		73.4		47.5

		25-May-08		18:07:10		69.8		39.5		25-May-08		18:06:20		69.2		48.5		25-May-08		18:07:53		69.8		41		5-Jul-08		18:25:59		73.4		46.5

		25-May-08		20:07:10		70.41		40		25-May-08		20:06:20		69.2		50		25-May-08		20:07:53		69.2		41.5		5-Jul-08		20:25:59		72.8		45.5

		25-May-08		22:07:10		70.41		40		25-May-08		22:06:20		68.61		48		25-May-08		22:07:53		69.2		41		5-Jul-08		22:25:59		72.8		47

		26-May-08		0:07:10		70.41		39		26-May-08		0:06:20		68		47		26-May-08		0:07:53		69.2		40.5		6-Jul-08		0:25:59		72.21		46

		26-May-08		2:07:10		70.41		37.5		26-May-08		2:06:20		67.4		45		26-May-08		2:07:53		69.2		39		6-Jul-08		2:25:59		72.21		45.5

		26-May-08		4:07:10		70.41		36.5		26-May-08		4:06:20		66.81		44		26-May-08		4:07:53		69.2		38		6-Jul-08		4:25:59		71		45.5

		26-May-08		6:07:10		70.41		36.5		26-May-08		6:06:20		66.81		44.5		26-May-08		6:07:53		69.8		38		6-Jul-08		6:25:59		71		45

		26-May-08		8:07:10		70.41		38.5		26-May-08		8:06:20		67.4		45.5		26-May-08		8:07:53		69.8		39		6-Jul-08		8:25:59		70.41		45.5

		26-May-08		10:07:10		69.8		37		26-May-08		10:06:20		69.2		43		26-May-08		10:07:53		69.2		39.5		6-Jul-08		10:25:59		71.6		47.5

		26-May-08		12:07:10		69.8		37		26-May-08		12:06:20		69.2		40.5		26-May-08		12:07:53		69.2		38.5		6-Jul-08		12:25:59		73.4		48.5

		26-May-08		14:07:10		70.41		37		26-May-08		14:06:20		69.2		40		26-May-08		14:07:53		69.8		38.5		6-Jul-08		14:25:59		75.2		49

		26-May-08		16:07:10		70.41		36		26-May-08		16:06:20		69.2		39		26-May-08		16:07:53		69.2		38		6-Jul-08		16:25:59		77		47.5

		26-May-08		18:07:10		70.41		35.5		26-May-08		18:06:20		68.61		38.5		26-May-08		18:07:53		69.2		37		6-Jul-08		18:25:59		77.61		45.5

		26-May-08		20:07:10		70.41		36		26-May-08		20:06:20		69.2		38.5		26-May-08		20:07:53		69.8		37.5		6-Jul-08		20:25:59		78.2		45

		26-May-08		22:07:10		69.8		37.5		26-May-08		22:06:20		69.2		44		26-May-08		22:07:53		69.2		39.5		6-Jul-08		22:25:59		77		45.5

		27-May-08		0:07:10		70.41		38		27-May-08		0:06:20		68.61		44.5		27-May-08		0:07:53		69.8		39.5		7-Jul-08		0:25:59		75.81		45.5

		27-May-08		2:07:10		70.41		37.5		27-May-08		2:06:20		68		45		27-May-08		2:07:53		69.8		39		7-Jul-08		2:25:59		74.6		44.5

		27-May-08		4:07:10		70.41		37.5		27-May-08		4:06:20		67.4		45.5		27-May-08		4:07:53		69.8		39		7-Jul-08		4:25:59		74.01		44.5

		27-May-08		6:07:10		70.41		37		27-May-08		6:06:20		67.4		45		27-May-08		6:07:53		69.2		38.5		7-Jul-08		6:25:59		72.8		44

		27-May-08		8:07:10		70.41		38		27-May-08		8:06:20		68		45		27-May-08		8:07:53		69.2		39.5		7-Jul-08		8:25:59		72.21		44.5

		27-May-08		10:07:10		69.8		37.5		27-May-08		10:06:20		69.2		42.5		27-May-08		10:07:53		69.2		39		7-Jul-08		10:25:59		73.4		46.5

		27-May-08		12:07:10		70.41		39		27-May-08		12:06:20		69.2		45		27-May-08		12:07:53		69.2		40		7-Jul-08		12:25:59		74.6		48

		27-May-08		14:07:10		70.41		38.5		27-May-08		14:06:20		68.61		45		27-May-08		14:07:53		69.2		40.5		7-Jul-08		14:25:59		76.4		49

		27-May-08		16:07:10		70.41		39		27-May-08		16:06:20		69.2		45.5		27-May-08		16:07:53		69.2		40.5		7-Jul-08		16:25:59		77.61		47.5

		27-May-08		18:07:10		70.41		39		27-May-08		18:06:20		69.2		46		27-May-08		18:07:53		69.2		40.5		7-Jul-08		18:25:59		78.2		46

		27-May-08		20:07:10		70.41		38.5		27-May-08		20:06:20		69.2		46		27-May-08		20:07:53		69.8		40		7-Jul-08		20:25:59		78.2		44.5

		27-May-08		22:07:10		70.41		39		27-May-08		22:06:20		69.2		45		27-May-08		22:07:53		69.8		40		7-Jul-08		22:25:59		76.4		43.5

		28-May-08		0:07:10		70.41		38.5		28-May-08		0:06:20		69.2		46		28-May-08		0:07:53		69.8		40		8-Jul-08		0:25:59		75.2		42.5

		28-May-08		2:07:10		70.41		39		28-May-08		2:06:20		69.2		46.5		28-May-08		2:07:53		69.2		40.5		8-Jul-08		2:25:59		74.01		42.5

		28-May-08		4:07:10		70.41		39		28-May-08		4:06:20		68.61		47		28-May-08		4:07:53		69.8		40.5		8-Jul-08		4:25:59		72.8		42

		28-May-08		6:07:10		70.41		39.5		28-May-08		6:06:20		69.2		47.5		28-May-08		6:07:53		69.2		41		8-Jul-08		6:25:59		72.21		41.5

		28-May-08		8:07:10		70.41		39		28-May-08		8:06:20		69.2		50		28-May-08		8:07:53		69.2		41.5		8-Jul-08		8:25:59		71.6		46

		28-May-08		10:07:10		71		38.5		28-May-08		10:06:20		69.8		45		28-May-08		10:07:53		68.61		41		8-Jul-08		10:25:59		72.8		47

		28-May-08		12:07:10		71		38.5		28-May-08		12:06:20		69.8		44		28-May-08		12:07:53		69.2		41.5		8-Jul-08		12:25:59		72.8		49

		28-May-08		14:07:10		71		39		28-May-08		14:06:20		69.2		43.5		28-May-08		14:07:53		68.61		42.5		8-Jul-08		14:25:59		72.8		49

		28-May-08		16:07:10		71		38		28-May-08		16:06:20		69.8		45.5		28-May-08		16:07:53		68.61		41.5		8-Jul-08		16:25:59		73.4		48.5

		28-May-08		18:07:10		71		37.5		28-May-08		18:06:20		71		41.5		28-May-08		18:07:53		69.2		40.5		8-Jul-08		18:25:59		73.4		47

		28-May-08		20:07:10		71		37.5		28-May-08		20:06:20		70.41		42.5		28-May-08		20:07:53		69.2		40		8-Jul-08		20:25:59		74.6		45.5

		28-May-08		22:07:10		70.41		37.5		28-May-08		22:06:20		71		41.5		28-May-08		22:07:53		69.2		39		8-Jul-08		22:25:59		75.2		45

		29-May-08		0:07:10		70.41		37.5		29-May-08		0:06:20		69.8		43		29-May-08		0:07:53		69.2		39.5		9-Jul-08		0:25:59		75.2		44

		29-May-08		2:07:10		70.41		38		29-May-08		2:06:20		69.2		44		29-May-08		2:07:53		69.8		39.5		9-Jul-08		2:25:59		74.6		44

		29-May-08		4:07:10		70.41		38		29-May-08		4:06:20		68.61		45		29-May-08		4:07:53		69.8		39.5		9-Jul-08		4:25:59		74.01		43.5

		29-May-08		6:07:10		70.41		38.5		29-May-08		6:06:20		68.61		45.5		29-May-08		6:07:53		69.8		40		9-Jul-08		6:25:59		73.4		42

		29-May-08		8:07:10		71		38.5		29-May-08		8:06:20		69.8		46.5		29-May-08		8:07:53		69.2		40.5		9-Jul-08		8:25:59		72.21		45.5

		29-May-08		10:07:10		71		36.5		29-May-08		10:06:20		69.2		41.5		29-May-08		10:07:53		68.61		39.5		9-Jul-08		10:25:59		72.8		50

		29-May-08		12:07:10		71		37.5		29-May-08		12:06:20		69.8		43		29-May-08		12:07:53		69.2		40		9-Jul-08		12:25:59		72.8		50.5

		29-May-08		14:07:10		71		37.5		29-May-08		14:06:20		69.2		41.5		29-May-08		14:07:53		68.61		40.5		9-Jul-08		14:25:59		72.21		49.5

		29-May-08		16:07:10		71		37		29-May-08		16:06:20		69.8		41		29-May-08		16:07:53		68.61		40.5		9-Jul-08		16:25:59		72.8		48.5

		29-May-08		18:07:10		71		38		29-May-08		18:06:20		70.41		42.5		29-May-08		18:07:53		68.61		41		9-Jul-08		18:25:59		73.4		47.5

		29-May-08		20:07:10		71		38		29-May-08		20:06:20		70.41		44.5		29-May-08		20:07:53		69.2		40.5		9-Jul-08		20:25:59		74.01		45

		29-May-08		22:07:10		71		38		29-May-08		22:06:20		70.41		43.5		29-May-08		22:07:53		69.8		40		9-Jul-08		22:25:59		75.81		44

		30-May-08		0:07:10		69.8		38.5		30-May-08		0:06:20		69.2		47		30-May-08		0:07:53		67.4		42.5		10-Jul-08		0:25:59		75.2		44

		30-May-08		2:07:10		70.41		39		30-May-08		2:06:20		68.61		46.5		30-May-08		2:07:53		69.2		41		10-Jul-08		2:25:59		74.6		44

		30-May-08		4:07:10		71		39		30-May-08		4:06:20		68.61		47.5		30-May-08		4:07:53		69.8		40.5		10-Jul-08		4:25:59		74.01		44.5

		30-May-08		6:07:10		71		38.5		30-May-08		6:06:20		68		47.5		30-May-08		6:07:53		69.8		40.5		10-Jul-08		6:25:59		73.4		43

		30-May-08		8:07:10		70.41		39.5		30-May-08		8:06:20		70.41		48.5		30-May-08		8:07:53		68.61		42		10-Jul-08		8:25:59		73.4		46

		30-May-08		10:07:10		71		39		30-May-08		10:06:20		71		44.5		30-May-08		10:07:53		68.61		41.5		10-Jul-08		10:25:59		74.01		47.5

		30-May-08		12:07:10		71.6		39		30-May-08		12:06:20		69.2		49		30-May-08		12:07:53		69.2		41.5		10-Jul-08		12:25:59		72.8		49.5

		30-May-08		14:07:10		71		39.5		30-May-08		14:06:20		69.2		45.5		30-May-08		14:07:53		69.2		42.5		10-Jul-08		14:25:59		72.21		51

		30-May-08		16:07:10		71		39.5		30-May-08		16:06:20		69.2		49		30-May-08		16:07:53		68		44		10-Jul-08		16:25:59		72.8		50.5

		30-May-08		18:07:10		71		39		30-May-08		18:06:20		69.2		47.5		30-May-08		18:07:53		68.61		42		10-Jul-08		18:25:59		73.4		49

		30-May-08		20:07:10		71		38.5		30-May-08		20:06:20		69.2		44		30-May-08		20:07:53		69.2		41		10-Jul-08		20:25:59		74.6		46

		30-May-08		22:07:10		70.41		38.5		30-May-08		22:06:20		68.61		45		30-May-08		22:07:53		69.2		41		10-Jul-08		22:25:59		75.81		47

		31-May-08		0:07:10		71		39.5		31-May-08		0:06:20		68		49.5		31-May-08		0:07:53		69.2		42		11-Jul-08		0:25:59		75.81		46

		31-May-08		2:07:10		70.41		39		31-May-08		2:06:20		68		49.5		31-May-08		2:07:53		69.2		41		11-Jul-08		2:25:59		74.6		46.5

		31-May-08		4:07:10		70.41		39		31-May-08		4:06:20		68		49		31-May-08		4:07:53		69.8		40.5		11-Jul-08		4:25:59		74.01		46.5

		31-May-08		6:07:10		70.41		39		31-May-08		6:06:20		68		51.5		31-May-08		6:07:53		68.61		41.5		11-Jul-08		6:25:59		73.4		44.5

		31-May-08		8:07:10		71		39		31-May-08		8:06:20		68		45.5		31-May-08		8:07:53		68		42.5		11-Jul-08		8:25:59		72.21		47.5

		31-May-08		10:07:10		70.41		39.5		31-May-08		10:06:20		69.2		51		31-May-08		10:07:53		68		42.5		11-Jul-08		10:25:59		73.4		50.5

		31-May-08		12:07:10		71		40		31-May-08		12:06:20		69.2		49		31-May-08		12:07:53		68		44		11-Jul-08		12:25:59		72.8		51

		31-May-08		14:07:10		71		42		31-May-08		14:06:20		69.2		48		31-May-08		14:07:53		68.61		45.5		11-Jul-08		14:25:59		72.8		51.5

		31-May-08		16:07:10		71		40.5		31-May-08		16:06:20		69.2		51		31-May-08		16:07:53		68.61		45		11-Jul-08		16:25:59		72.8		49

		31-May-08		18:07:10		71		40.5		31-May-08		18:06:20		68.61		52.5		31-May-08		18:07:53		68		45		11-Jul-08		18:25:59		73.4		47.5

		31-May-08		20:07:10		71		39.5		31-May-08		20:06:20		68.61		52		31-May-08		20:07:53		68.61		43		11-Jul-08		20:25:59		74.01		46.5

		31-May-08		22:07:10		70.41		39		31-May-08		22:06:20		69.2		48		31-May-08		22:07:53		69.8		41		11-Jul-08		22:25:59		75.2		45

		1-Jun-08		0:07:10		70.41		39.5		1-Jun-08		0:06:20		68.61		47.5		1-Jun-08		0:07:53		68.61		41.5		12-Jul-08		0:25:59		74.6		43.5

		1-Jun-08		2:07:10		70.41		39		1-Jun-08		2:06:20		68.61		47.5		1-Jun-08		2:07:53		69.2		41		12-Jul-08		2:25:59		73.4		44

		1-Jun-08		4:07:10		70.41		39		1-Jun-08		4:06:20		68.61		47.5		1-Jun-08		4:07:53		69.2		41.5		12-Jul-08		4:25:59		72.21		44.5

		1-Jun-08		6:07:10		70.41		39		1-Jun-08		6:06:20		67.4		50.5		1-Jun-08		6:07:53		69.8		41		12-Jul-08		6:25:59		72.21		44

		1-Jun-08		8:07:10		70.41		39.5		1-Jun-08		8:06:20		67.4		51		1-Jun-08		8:07:53		69.2		41.5		12-Jul-08		8:25:59		71.6		46.5

		1-Jun-08		10:07:10		70.41		39.5		1-Jun-08		10:06:20		67.4		50		1-Jun-08		10:07:53		69.8		41		12-Jul-08		10:25:59		72.8		48

		1-Jun-08		12:07:10		70.41		39.5		1-Jun-08		12:06:20		67.4		50.5		1-Jun-08		12:07:53		69.2		42		12-Jul-08		12:25:59		74.6		46.5

		1-Jun-08		14:07:10		71		41		1-Jun-08		14:06:20		68.61		52		1-Jun-08		14:07:53		69.2		43.5		12-Jul-08		14:25:59		74.6		46.5

		1-Jun-08		16:07:10		71		40		1-Jun-08		16:06:20		69.2		50		1-Jun-08		16:07:53		69.2		43.5		12-Jul-08		16:25:59		75.81		45

		1-Jun-08		18:07:10		71.6		39.5		1-Jun-08		18:06:20		69.2		47.5		1-Jun-08		18:07:53		69.2		43		12-Jul-08		18:25:59		75.2		44.5

		1-Jun-08		20:07:10		71.6		38.5		1-Jun-08		20:06:20		68.61		47		1-Jun-08		20:07:53		69.2		42		12-Jul-08		20:25:59		75.81		41.5

		1-Jun-08		22:07:10		70.41		38.5		1-Jun-08		22:06:20		68		47.5		1-Jun-08		22:07:53		68.61		41		12-Jul-08		22:25:59		76.4		43

		2-Jun-08		0:07:10		70.41		38.5		2-Jun-08		0:06:20		68.61		46		2-Jun-08		0:07:53		68.61		41		13-Jul-08		0:25:59		76.4		43

		2-Jun-08		2:07:10		70.41		38		2-Jun-08		2:06:20		68		46		2-Jun-08		2:07:53		68.61		40.5		13-Jul-08		2:25:59		75.81		44

		2-Jun-08		4:07:10		70.41		37		2-Jun-08		4:06:20		67.4		45		2-Jun-08		4:07:53		68.61		39.5		13-Jul-08		4:25:59		75.81		44

		2-Jun-08		6:07:10		69.8		36		2-Jun-08		6:06:20		66.2		44		2-Jun-08		6:07:53		68.61		38.5		13-Jul-08		6:25:59		75.81		44.5

		2-Jun-08		8:07:10		70.41		38		2-Jun-08		8:06:20		66.81		46		2-Jun-08		8:07:53		69.2		40		13-Jul-08		8:25:59		75.81		44.5

		2-Jun-08		10:07:10		69.8		37		2-Jun-08		10:06:20		68.61		40.5		2-Jun-08		10:07:53		68.61		39.5		13-Jul-08		10:25:59		75.81		44.5

		2-Jun-08		12:07:10		70.41		38		2-Jun-08		12:06:20		69.2		41		2-Jun-08		12:07:53		69.2		39.5		13-Jul-08		12:25:59		76.4		44

		2-Jun-08		14:07:10		71		39		2-Jun-08		14:06:20		69.8		42		2-Jun-08		14:07:53		69.2		41.5		13-Jul-08		14:25:59		77.61		44.5

		2-Jun-08		16:07:10		71		38.5		2-Jun-08		16:06:20		69.2		45.5		2-Jun-08		16:07:53		65.01		46		13-Jul-08		16:25:59		78.8		43.5

		2-Jun-08		18:07:10		71		38.5		2-Jun-08		18:06:20		68.61		45		2-Jun-08		18:07:53		67.4		43		13-Jul-08		18:25:59		78.8		43

		2-Jun-08		20:07:10		71		37.5		2-Jun-08		20:06:20		67.4		47		2-Jun-08		20:07:53		66.81		43.5		13-Jul-08		20:25:59		78.8		43.5

		2-Jun-08		22:07:10		69.8		37		2-Jun-08		22:06:20		68		45		2-Jun-08		22:07:53		67.4		42		13-Jul-08		22:25:59		77.61		42.5

		3-Jun-08		0:07:10		69.8		37		3-Jun-08		0:06:20		67.4		44		3-Jun-08		0:07:53		67.4		41		14-Jul-08		0:25:59		77		42.5

		3-Jun-08		2:07:10		70.41		36.5		3-Jun-08		2:06:20		66.81		43.5		3-Jun-08		2:07:53		66.81		40.5		14-Jul-08		2:25:59		76.4		42.5

		3-Jun-08		4:07:10		69.8		35		3-Jun-08		4:06:20		66.2		43		3-Jun-08		4:07:53		67.4		39.5		14-Jul-08		4:25:59		75.81		42.5

		3-Jun-08		6:07:10		70.41		35.5		3-Jun-08		6:06:20		66.2		42.5		3-Jun-08		6:07:53		67.4		38.5		14-Jul-08		6:25:59		75.2		42

		3-Jun-08		8:07:10		70.41		37		3-Jun-08		8:06:20		68		42		3-Jun-08		8:07:53		68.61		39.5		14-Jul-08		8:25:59		74.6		42.5

		3-Jun-08		10:07:10		71		37		3-Jun-08		10:06:20		68		44.5		3-Jun-08		10:07:53		67.4		41.5		14-Jul-08		10:25:59		75.2		42.5

		3-Jun-08		12:07:10		71		37.5		3-Jun-08		12:06:20		71		41		3-Jun-08		12:07:53		68		41.5		14-Jul-08		12:25:59		76.4		43

		3-Jun-08		14:07:10		71		39.5		3-Jun-08		14:06:20		70.41		45.5		3-Jun-08		14:07:53		66.81		45		14-Jul-08		14:25:59		77		43.5

		3-Jun-08		16:07:10		71		39.5		3-Jun-08		16:06:20		69.2		44.5		3-Jun-08		16:07:53		67.4		44.5		14-Jul-08		16:25:59		78.2		43.5

		3-Jun-08		18:07:10		71		39.5		3-Jun-08		18:06:20		69.2		45		3-Jun-08		18:07:53		67.4		44.5		14-Jul-08		18:25:59		78.8		43

		3-Jun-08		20:07:10		71		30.5		3-Jun-08		20:06:20		69.2		31.5		3-Jun-08		20:07:53		67.4		34.5		14-Jul-08		20:25:59		78.8		42.5

		3-Jun-08		22:07:10		70.41		27		3-Jun-08		22:06:20		68.61		29.5		3-Jun-08		22:07:53		68		31		14-Jul-08		22:25:59		77.61		41.5

		4-Jun-08		0:07:10		69.2		34		4-Jun-08		0:06:20		68.61		37		4-Jun-08		0:07:53		68		37		15-Jul-08		0:25:59		77		41

		4-Jun-08		2:07:10		69.2		35.5		4-Jun-08		2:06:20		68		40		4-Jun-08		2:07:53		68		38		15-Jul-08		2:25:59		76.4		41

		4-Jun-08		4:07:10		68.61		35		4-Jun-08		4:06:20		67.4		39.5		4-Jun-08		4:07:53		68		37.5		15-Jul-08		4:25:59		75.81		41.5

		4-Jun-08		6:07:10		69.8		34.5		4-Jun-08		6:06:20		68		39		4-Jun-08		6:07:53		68.61		37		15-Jul-08		6:25:59		75.2		41

		4-Jun-08		8:07:10		69.8		38.5		4-Jun-08		8:06:20		68		46		4-Jun-08		8:07:53		68		40.5		15-Jul-08		8:25:59		74.01		43.5

		4-Jun-08		10:07:10		70.41		41		4-Jun-08		10:06:20		69.8		53		4-Jun-08		10:07:53		68		45		15-Jul-08		10:25:59		74.6		45

		4-Jun-08		12:07:10		71		42.5		4-Jun-08		12:06:20		69.8		50		4-Jun-08		12:07:53		68		46.5		15-Jul-08		12:25:59		75.2		44.5

		4-Jun-08		14:07:10		70.41		41.5		4-Jun-08		14:06:20		69.2		53		4-Jun-08		14:07:53		66.81		47		15-Jul-08		14:25:59		75.81		45

		4-Jun-08		16:07:10		70.41		40		4-Jun-08		16:06:20		70.41		44.5		4-Jun-08		16:07:53		67.4		44.5		15-Jul-08		16:25:59		75.81		44

		4-Jun-08		18:07:10		71		38		4-Jun-08		18:06:20		70.41		38.5		4-Jun-08		18:07:53		67.4		42		15-Jul-08		18:25:59		76.4		42.5

		4-Jun-08		20:07:10		71		38		4-Jun-08		20:06:20		70.41		42		4-Jun-08		20:07:53		67.4		43		15-Jul-08		20:25:59		77		39.5

		4-Jun-08		22:07:10		71		37.5		4-Jun-08		22:06:20		69.8		43		4-Jun-08		22:07:53		67.4		42.5		15-Jul-08		22:25:59		77		41

		5-Jun-08		0:07:10		70.41		38		5-Jun-08		0:06:20		69.2		44		5-Jun-08		0:07:53		68		41.5		16-Jul-08		0:25:59		76.4		41.5

		5-Jun-08		2:07:10		69.8		36		5-Jun-08		2:06:20		69.8		38.5		5-Jun-08		2:07:53		68.61		39		16-Jul-08		2:25:59		75.81		41.5

		5-Jun-08		4:07:10		68.61		36		5-Jun-08		4:06:20		69.2		38.5		5-Jun-08		4:07:53		68		38.5		16-Jul-08		4:25:59		75.81		42

		5-Jun-08		6:07:10		68.61		36		5-Jun-08		6:06:20		68.61		38.5		5-Jun-08		6:07:53		68		38		16-Jul-08		6:25:59		75.2		41

		5-Jun-08		8:07:10		69.2		35		5-Jun-08		8:06:20		69.2		39.5		5-Jun-08		8:07:53		68		38		16-Jul-08		8:25:59		74.6		43.5

		5-Jun-08		10:07:10		70.41		35		5-Jun-08		10:06:20		71		36.5		5-Jun-08		10:07:53		68		38.5		16-Jul-08		10:25:59		75.2		44.5

		5-Jun-08		12:07:10		70.41		34.5		5-Jun-08		12:06:20		69.8		35		5-Jun-08		12:07:53		68.61		37		16-Jul-08		12:25:59		75.2		43.5

		5-Jun-08		14:07:10		70.41		32		5-Jun-08		14:06:20		69.2		34.5		5-Jun-08		14:07:53		68.61		35		16-Jul-08		14:25:59		75.81		45

		5-Jun-08		16:07:10		70.41		34.5		5-Jun-08		16:06:20		70.41		36.5		5-Jun-08		16:07:53		68.61		37.5		16-Jul-08		16:25:59		75.2		43.5

		5-Jun-08		18:07:10		71		35		5-Jun-08		18:06:20		69.8		36		5-Jun-08		18:07:53		68.61		37.5

		5-Jun-08		20:07:10		71		35.5		5-Jun-08		20:06:20		69.2		38.5		5-Jun-08		20:07:53		69.2		38

		5-Jun-08		22:07:10		71		35		5-Jun-08		22:06:20		68.61		39		5-Jun-08		22:07:53		69.2		37.5

		6-Jun-08		0:07:10		69.8		35.5		6-Jun-08		0:06:20		68		41		6-Jun-08		0:07:53		68.61		38.5

		6-Jun-08		2:07:10		69.2		36		6-Jun-08		2:06:20		67.4		41		6-Jun-08		2:07:53		68.61		38

		6-Jun-08		4:07:10		69.2		36		6-Jun-08		4:06:20		67.4		41.5		6-Jun-08		4:07:53		68.61		38.5

		6-Jun-08		6:07:10		69.2		36		6-Jun-08		6:06:20		67.4		41.5		6-Jun-08		6:07:53		68		38.5

		6-Jun-08		8:07:10		69.8		36.5		6-Jun-08		8:06:20		68		42		6-Jun-08		8:07:53		68.61		39.5

		6-Jun-08		10:07:10		70.41		36		6-Jun-08		10:06:20		68		42		6-Jun-08		10:07:53		68		40

		6-Jun-08		12:07:10		70.41		33		6-Jun-08		12:06:20		69.8		36		6-Jun-08		12:07:53		68		37.5

		6-Jun-08		14:07:10		70.41		38.5		6-Jun-08		14:06:20		69.2		40.5		6-Jun-08		14:07:53		67.4		42

		6-Jun-08		16:07:10		70.41		39.5		6-Jun-08		16:06:20		69.8		43		6-Jun-08		16:07:53		68		43

		6-Jun-08		18:07:10		71		38.5		6-Jun-08		18:06:20		69.2		44.5		6-Jun-08		18:07:53		68		42.5

		6-Jun-08		20:07:10		71		39.5		6-Jun-08		20:06:20		69.2		47		6-Jun-08		20:07:53		68.61		43

		6-Jun-08		22:07:10		71		39		6-Jun-08		22:06:20		68.61		51.5		6-Jun-08		22:07:53		68.61		43

		7-Jun-08		0:07:10		70.41		38.5		7-Jun-08		0:06:20		68.61		45		7-Jun-08		0:07:53		69.2		41

		7-Jun-08		2:07:10		69.8		38		7-Jun-08		2:06:20		68		48.5		7-Jun-08		2:07:53		69.2		40.5

		7-Jun-08		4:07:10		69.2		38		7-Jun-08		4:06:20		67.4		45.5		7-Jun-08		4:07:53		68.61		40

		7-Jun-08		6:07:10		69.2		37.5		7-Jun-08		6:06:20		67.4		43.5		7-Jun-08		6:07:53		68.61		39.5

		7-Jun-08		8:07:10		69.8		37.5		7-Jun-08		8:06:20		68.61		44		7-Jun-08		8:07:53		68.61		39.5

		7-Jun-08		10:07:10		70.41		36		7-Jun-08		10:06:20		68.61		40		7-Jun-08		10:07:53		68		39.5

		7-Jun-08		12:07:10		70.41		34.5		7-Jun-08		12:06:20		70.41		36.5		7-Jun-08		12:07:53		69.2		37

		7-Jun-08		14:07:10		70.41		31.5		7-Jun-08		14:06:20		69.8		32.5		7-Jun-08		14:07:53		68.61		33.5

		7-Jun-08		16:07:10		71		32		7-Jun-08		16:06:20		68.61		34.5		7-Jun-08		16:07:53		68		35

		7-Jun-08		18:07:10		70.41		34.5		7-Jun-08		18:06:20		68.61		36.5		7-Jun-08		18:07:53		68.61		36.5

		7-Jun-08		20:07:10		71		34.5		7-Jun-08		20:06:20		69.2		38		7-Jun-08		20:07:53		69.2		37

		7-Jun-08		22:07:10		70.41		34		7-Jun-08		22:06:20		68.61		38		7-Jun-08		22:07:53		68.61		36.5

		8-Jun-08		0:07:10		69.8		34		8-Jun-08		0:06:20		68		38		8-Jun-08		0:07:53		68.61		36.5

		8-Jun-08		2:07:10		69.2		34		8-Jun-08		2:06:20		68		37.5		8-Jun-08		2:07:53		68.61		36

		8-Jun-08		4:07:10		69.2		34		8-Jun-08		4:06:20		68		37		8-Jun-08		4:07:53		68.61		35.5

		8-Jun-08		6:07:10		69.8		33		8-Jun-08		6:06:20		67.4		37		8-Jun-08		6:07:53		68.61		35.5

		8-Jun-08		8:07:10		69.8		33.5		8-Jun-08		8:06:20		68		36.5		8-Jun-08		8:07:53		68.61		35.5

		8-Jun-08		10:07:10		70.41		34.5		8-Jun-08		10:06:20		68		37		8-Jun-08		10:07:53		69.2		35.5

		8-Jun-08		12:07:10		71		33		8-Jun-08		12:06:20		68.61		34.5		8-Jun-08		12:07:53		69.2		35

		8-Jun-08		14:07:10		71		30.5		8-Jun-08		14:06:20		68.61		32		8-Jun-08		14:07:53		69.2		33

		8-Jun-08		16:07:10		71.6		31		8-Jun-08		16:06:20		69.2		33.5		8-Jun-08		16:07:53		68.61		34.5

		8-Jun-08		18:07:10		71.6		34.5		8-Jun-08		18:06:20		68.61		37.5		8-Jun-08		18:07:53		68.61		38

		8-Jun-08		20:07:10		71.6		36.5		8-Jun-08		20:06:20		68.61		45		8-Jun-08		20:07:53		68.61		40.5

		8-Jun-08		22:07:10		71		37		8-Jun-08		22:06:20		68.61		44		8-Jun-08		22:07:53		68.61		40

		9-Jun-08		0:07:10		71		36		9-Jun-08		0:06:20		68.61		40.5		9-Jun-08		0:07:53		69.2		38.5

		9-Jun-08		2:07:10		70.41		36.5		9-Jun-08		2:06:20		68		43		9-Jun-08		2:07:53		69.2		38

		9-Jun-08		4:07:10		69.8		36.5		9-Jun-08		4:06:20		68		43		9-Jun-08		4:07:53		69.2		38.5

		9-Jun-08		6:07:10		69.2		37		9-Jun-08		6:06:20		67.4		43.5		9-Jun-08		6:07:53		69.2		39

		9-Jun-08		8:07:10		69.8		38		9-Jun-08		8:06:20		67.4		45		9-Jun-08		8:07:53		69.2		39

		9-Jun-08		10:07:10		70.41		38.5		9-Jun-08		10:06:20		68.61		43.5		9-Jun-08		10:07:53		69.2		40

		9-Jun-08		12:07:10		71		38		9-Jun-08		12:06:20		68.61		42.5		9-Jun-08		12:07:53		69.8		40.5

		9-Jun-08		14:07:10		71		38		9-Jun-08		14:06:20		68.61		41.5		9-Jun-08		14:07:53		69.2		40.5

		9-Jun-08		16:07:10		72.21		38.5		9-Jun-08		16:06:20		68.61		44.5		9-Jun-08		16:07:53		69.8		42

		9-Jun-08		18:07:10		71.6		39		9-Jun-08		18:06:20		68.61		46.5		9-Jun-08		18:07:53		69.2		43

		9-Jun-08		20:07:10		71.6		38		9-Jun-08		20:06:20		68		48		9-Jun-08		20:07:53		69.2		41.5

		9-Jun-08		22:07:10		71		37.5		9-Jun-08		22:06:20		68		47		9-Jun-08		22:07:53		69.2		40

		10-Jun-08		0:07:10		70.41		37.5		10-Jun-08		0:06:20		68		45.5		10-Jun-08		0:07:53		69.2		39.5

		10-Jun-08		2:07:10		69.8		37		10-Jun-08		2:06:20		67.4		46		10-Jun-08		2:07:53		69.2		39.5

		10-Jun-08		4:07:10		69.8		38		10-Jun-08		4:06:20		68		47		10-Jun-08		4:07:53		69.2		39.5

		10-Jun-08		6:07:10		69.8		38		10-Jun-08		6:06:20		68		44.5		10-Jun-08		6:07:53		69.8		39.5

		10-Jun-08		8:07:10		71		38.5		10-Jun-08		8:06:20		68.61		48		10-Jun-08		8:07:53		69.2		41

		10-Jun-08		10:07:10		71		37.5		10-Jun-08		10:06:20		69.2		43		10-Jun-08		10:07:53		69.2		40.5

		10-Jun-08		12:07:10		71		38		10-Jun-08		12:06:20		70.41		40		10-Jun-08		12:07:53		69.2		40.5

		10-Jun-08		14:07:10		71		37.5		10-Jun-08		14:06:20		71.6		37.5		10-Jun-08		14:07:53		68.61		39.5

		10-Jun-08		16:07:10		70.41		40		10-Jun-08		16:06:20		70.41		41		10-Jun-08		16:07:53		68.61		42

		10-Jun-08		18:07:10		70.41		44		10-Jun-08		18:06:20		71.6		47.5		10-Jun-08		18:07:53		69.2		46.5

		10-Jun-08		20:07:10		71		42		10-Jun-08		20:06:20		71		47		10-Jun-08		20:07:53		68.61		46

		10-Jun-08		22:07:10		71.6		41		10-Jun-08		22:06:20		71		51		10-Jun-08		22:07:53		69.2		44.5

		11-Jun-08		0:07:10		71.6		40.5		11-Jun-08		0:06:20		71		47.5		11-Jun-08		0:07:53		68.61		45

		11-Jun-08		2:07:10		71.6		36.5		11-Jun-08		2:06:20		71		40.5		11-Jun-08		2:07:53		69.2		40

		11-Jun-08		4:07:10		71		37.5		11-Jun-08		4:06:20		69.8		44		11-Jun-08		4:07:53		69.2		40.5

		11-Jun-08		6:07:10		70.41		36.5		11-Jun-08		6:06:20		69.8		41		11-Jun-08		6:07:53		69.2		39

		11-Jun-08		8:07:10		71		35.5		11-Jun-08		8:06:20		70.41		39		11-Jun-08		8:07:53		68		39

		11-Jun-08		10:07:10		71		27.5		11-Jun-08		10:06:20		70.41		29.5		11-Jun-08		10:07:53		67.4		31.5

		11-Jun-08		12:07:10		71		24		11-Jun-08		12:06:20		69.8		24.5		11-Jun-08		12:07:53		68.61		27

		11-Jun-08		14:07:10		71.6		27.5		11-Jun-08		14:06:20		70.41		30.5		11-Jun-08		14:07:53		68		31.5

		11-Jun-08		16:07:10		71		28.5		11-Jun-08		16:06:20		69.8		30		11-Jun-08		16:07:53		68.61		31.5

		11-Jun-08		18:07:10		71		31.5		11-Jun-08		18:06:20		69.8		33		11-Jun-08		18:07:53		68.61		34

		11-Jun-08		20:07:10		71		33.5		11-Jun-08		20:06:20		69.8		35		11-Jun-08		20:07:53		68.61		36

		11-Jun-08		22:07:10		71.6		33.5		11-Jun-08		22:06:20		69.2		37		11-Jun-08		22:07:53		68.61		37

		12-Jun-08		0:07:10		70.41		34		12-Jun-08		0:06:20		69.2		36.5		12-Jun-08		0:07:53		68.61		36.5

		12-Jun-08		2:07:10		69.8		33.5		12-Jun-08		2:06:20		68.61		36.5		12-Jun-08		2:07:53		68.61		36

		12-Jun-08		4:07:10		69.2		34		12-Jun-08		4:06:20		68.61		37		12-Jun-08		4:07:53		68.61		36

		12-Jun-08		6:07:10		68.61		34.5		12-Jun-08		6:06:20		68		37		12-Jun-08		6:07:53		68		36.5

		12-Jun-08		8:07:10		69.8		34.5		12-Jun-08		8:06:20		69.2		37.5		12-Jun-08		8:07:53		68.61		36.5

		12-Jun-08		10:07:10		71		34		12-Jun-08		10:06:20		71		36		12-Jun-08		10:07:53		68.61		37

		12-Jun-08		12:07:10		71		29.5		12-Jun-08		12:06:20		71.6		30		12-Jun-08		12:07:53		69.8		32

		12-Jun-08		14:07:10		71		24.5		12-Jun-08		14:06:20		72.8		26		12-Jun-08		14:07:53		69.8		28.5

		12-Jun-08		16:07:10		71		26.5		12-Jun-08		16:06:20		71.6		20.5		12-Jun-08		16:07:53		69.2		28

		12-Jun-08		18:07:10		70.41		27.5		12-Jun-08		18:06:20		71		27.5		12-Jun-08		18:07:53		69.2		29.5

		12-Jun-08		20:07:10		70.41		35.5		12-Jun-08		20:06:20		71		38.5		12-Jun-08		20:07:53		69.2		38

		12-Jun-08		22:07:10		71		35.5		12-Jun-08		22:06:20		70.41		40		12-Jun-08		22:07:53		69.2		38

		13-Jun-08		0:07:10		70.41		36		13-Jun-08		0:06:20		70.41		39.5		13-Jun-08		0:07:53		69.2		37.5

		13-Jun-08		2:07:10		69.8		36		13-Jun-08		2:06:20		69.8		39.5		13-Jun-08		2:07:53		69.2		37.5

		13-Jun-08		4:07:10		69.8		36.5		13-Jun-08		4:06:20		69.8		40.5		13-Jun-08		4:07:53		69.2		38

		13-Jun-08		6:07:10		69.2		36.5		13-Jun-08		6:06:20		69.8		39.5		13-Jun-08		6:07:53		69.2		37.5

		13-Jun-08		8:07:10		70.41		37		13-Jun-08		8:06:20		70.41		39.5		13-Jun-08		8:07:53		69.2		39

		13-Jun-08		10:07:10		71		36.5		13-Jun-08		10:06:20		70.41		38.5		13-Jun-08		10:07:53		69.2		38.5

		13-Jun-08		12:07:10		71		24		13-Jun-08		12:06:20		71.6		25		13-Jun-08		12:07:53		69.8		28

		13-Jun-08		14:07:10		71		22.5		13-Jun-08		14:06:20		71.6		23.5		13-Jun-08		14:07:53		69.2		25

		13-Jun-08		16:07:10		70.41		29		13-Jun-08		16:06:20		72.21		30		13-Jun-08		16:07:53		69.8		31.5

		13-Jun-08		18:07:10		71		26.5		13-Jun-08		18:06:20		71		27		13-Jun-08		18:07:53		69.8		29

		13-Jun-08		20:07:10		71		29		13-Jun-08		20:06:20		71.6		27.5		13-Jun-08		20:07:53		68.61		29.5

		13-Jun-08		22:07:10		71.6		32.5		13-Jun-08		22:06:20		71		33.5		13-Jun-08		22:07:53		69.2		34.5

		14-Jun-08		0:07:10		71		33		14-Jun-08		0:06:20		70.41		35.5		14-Jun-08		0:07:53		69.2		35.5

		14-Jun-08		2:07:10		70.41		34.5		14-Jun-08		2:06:20		70.41		37		14-Jun-08		2:07:53		69.2		36

		14-Jun-08		4:07:10		69.8		34.5		14-Jun-08		4:06:20		69.8		38.5		14-Jun-08		4:07:53		69.2		36.5

		14-Jun-08		6:07:10		69.8		35.5		14-Jun-08		6:06:20		69.8		38.5		14-Jun-08		6:07:53		68.61		37

		14-Jun-08		8:07:10		70.41		36		14-Jun-08		8:06:20		71		38.5		14-Jun-08		8:07:53		69.2		38

		14-Jun-08		10:07:10		71		36.5		14-Jun-08		10:06:20		71		39.5		14-Jun-08		10:07:53		68.61		39.5

		14-Jun-08		12:07:10		70.41		39		14-Jun-08		12:06:20		71.6		42		14-Jun-08		12:07:53		69.2		41.5

		14-Jun-08		14:07:10		71		37.5		14-Jun-08		14:06:20		72.8		37		14-Jun-08		14:07:53		69.2		39.5

		14-Jun-08		16:07:10		70.41		39		14-Jun-08		16:06:20		71		41		14-Jun-08		16:07:53		69.8		41

		14-Jun-08		18:07:10		70.41		39		14-Jun-08		18:06:20		71		42.5		14-Jun-08		18:07:53		68.61		42

		14-Jun-08		20:07:10		70.41		38		14-Jun-08		20:06:20		70.41		45		14-Jun-08		20:07:53		68.61		41.5

		14-Jun-08		22:07:10		70.41		38		14-Jun-08		22:06:20		71		45		14-Jun-08		22:07:53		68.61		40.5

		15-Jun-08		0:07:10		70.41		38.5		15-Jun-08		0:06:20		69.8		43.5		15-Jun-08		0:07:53		68.61		40.5

		15-Jun-08		2:07:10		70.41		38		15-Jun-08		2:06:20		69.8		44		15-Jun-08		2:07:53		68.61		40.5

		15-Jun-08		4:07:10		69.8		37.5		15-Jun-08		4:06:20		69.2		44		15-Jun-08		4:07:53		68.61		40

		15-Jun-08		6:07:10		69.8		38		15-Jun-08		6:06:20		69.2		45		15-Jun-08		6:07:53		68.61		40.5

		15-Jun-08		8:07:10		70.41		39		15-Jun-08		8:06:20		69.2		45.5		15-Jun-08		8:07:53		68.61		41

		15-Jun-08		10:07:10		70.41		39		15-Jun-08		10:06:20		69.8		45		15-Jun-08		10:07:53		68.61		41

		15-Jun-08		12:07:10		70.41		40		15-Jun-08		12:06:20		70.41		46.5		15-Jun-08		12:07:53		69.2		42

		15-Jun-08		14:07:10		71		41.5		15-Jun-08		14:06:20		71		47.5		15-Jun-08		14:07:53		69.2		44

		15-Jun-08		16:07:10		71		41.5		15-Jun-08		16:06:20		70.41		51.5		15-Jun-08		16:07:53		69.2		44.5

		15-Jun-08		18:07:10		71		40.5		15-Jun-08		18:06:20		70.41		50		15-Jun-08		18:07:53		69.2		43.5

		15-Jun-08		20:07:10		71		38.5		15-Jun-08		20:06:20		69.8		47		15-Jun-08		20:07:53		69.2		41.5

		15-Jun-08		22:07:10		71		38.5		15-Jun-08		22:06:20		70.41		45.5		15-Jun-08		22:07:53		69.2		41

		16-Jun-08		0:07:10		70.41		38.5		16-Jun-08		0:06:20		69.8		44.5		16-Jun-08		0:07:53		69.2		40.5

		16-Jun-08		2:07:10		70.41		38		16-Jun-08		2:06:20		69.2		44.5		16-Jun-08		2:07:53		69.2		40

		16-Jun-08		4:07:10		70.41		38		16-Jun-08		4:06:20		68.61		45		16-Jun-08		4:07:53		69.2		40

		16-Jun-08		6:07:10		69.8		37.5		16-Jun-08		6:06:20		68.61		44.5		16-Jun-08		6:07:53		69.2		39.5

		16-Jun-08		8:07:10		69.8		38		16-Jun-08		8:06:20		68.61		44.5		16-Jun-08		8:07:53		69.2		40

		16-Jun-08		10:07:10		69.8		38.5		16-Jun-08		10:06:20		69.8		44.5		16-Jun-08		10:07:53		69.2		40

		16-Jun-08		12:07:10		70.41		40.5		16-Jun-08		12:06:20		69.8		47		16-Jun-08		12:07:53		69.2		41.5

		16-Jun-08		14:07:10		70.41		42		16-Jun-08		14:06:20		70.41		49.5		16-Jun-08		14:07:53		69.2		43.5

		16-Jun-08		16:07:10		71		40.5		16-Jun-08		16:06:20		71		46		16-Jun-08		16:07:53		69.2		43

		16-Jun-08		18:07:10		71		39.5		16-Jun-08		18:06:20		71		43.5		16-Jun-08		18:07:53		69.2		42.5

		16-Jun-08		20:07:10		71		38		16-Jun-08		20:06:20		70.41		44.5		16-Jun-08		20:07:53		69.2		41

		16-Jun-08		22:07:10		70.41		38		16-Jun-08		22:06:20		70.41		43		16-Jun-08		22:07:53		69.2		40

		17-Jun-08		0:07:10		70.41		37.5		17-Jun-08		0:06:20		69.8		42		17-Jun-08		0:07:53		69.2		39.5

		17-Jun-08		2:07:10		69.8		36.5		17-Jun-08		2:06:20		68.61		43		17-Jun-08		2:07:53		69.2		39

		17-Jun-08		4:07:10		69.8		38		17-Jun-08		4:06:20		68		45.5		17-Jun-08		4:07:53		69.2		40

		17-Jun-08		6:07:10		69.8		38		17-Jun-08		6:06:20		68		45.5		17-Jun-08		6:07:53		69.2		40

		17-Jun-08		8:07:10		70.41		38.5		17-Jun-08		8:06:20		70.41		45		17-Jun-08		8:07:53		68.61		41

		17-Jun-08		10:07:10		70.41		39		17-Jun-08		10:06:20		71		44		17-Jun-08		10:07:53		68.61		41

		17-Jun-08		12:07:10		71		39.5		17-Jun-08		12:06:20		69.8		45.5		17-Jun-08		12:07:53		69.2		42

		17-Jun-08		14:07:10		71		41.5		17-Jun-08		14:06:20		70.41		48.5		17-Jun-08		14:07:53		68		45

		17-Jun-08		16:07:10		71		40		17-Jun-08		16:06:20		70.41		45		17-Jun-08		16:07:53		69.2		43.5

		17-Jun-08		18:07:10		71		39.5		17-Jun-08		18:06:20		70.41		46		17-Jun-08		18:07:53		69.8		41.5

		17-Jun-08		20:07:10		70.41		38.5		17-Jun-08		20:06:20		69.8		44.5		17-Jun-08		20:07:53		69.8		40

		17-Jun-08		22:07:10		70.41		38		17-Jun-08		22:06:20		69.8		43		17-Jun-08		22:07:53		69.8		39.5

		18-Jun-08		0:07:10		70.41		37.5		18-Jun-08		0:06:20		69.2		43		18-Jun-08		0:07:53		69.8		39

		18-Jun-08		2:07:10		70.41		37.5		18-Jun-08		2:06:20		68		43.5		18-Jun-08		2:07:53		69.8		38.5

		18-Jun-08		4:07:10		70.41		38		18-Jun-08		4:06:20		67.4		46		18-Jun-08		4:07:53		69.8		39

		18-Jun-08		6:07:10		70.41		38		18-Jun-08		6:06:20		66.81		46.5		18-Jun-08		6:07:53		69.8		39

		18-Jun-08		8:07:10		70.41		39		18-Jun-08		8:06:20		70.41		43.5		18-Jun-08		8:07:53		69.2		40.5

		18-Jun-08		10:07:10		71		38.5		18-Jun-08		10:06:20		70.41		44.5		18-Jun-08		10:07:53		68.61		41

		18-Jun-08		12:07:10		71		39		18-Jun-08		12:06:20		69.8		44.5		18-Jun-08		12:07:53		69.8		41

		18-Jun-08		14:07:10		71		42		18-Jun-08		14:06:20		69.8		46.5		18-Jun-08		14:07:53		69.2		44.5

		18-Jun-08		16:07:10		71		43.5		18-Jun-08		16:06:20		69.8		51.5		18-Jun-08		16:07:53		69.2		46

		18-Jun-08		18:07:10		71		29		18-Jun-08		18:06:20		69.2		31		18-Jun-08		18:07:53		69.2		32

		18-Jun-08		20:07:10		71		28		18-Jun-08		20:06:20		68.61		29		18-Jun-08		20:07:53		69.2		30

		18-Jun-08		22:07:10		71		29.5		18-Jun-08		22:06:20		68.61		31		18-Jun-08		22:07:53		69.2		31.5

		19-Jun-08		0:07:10		70.41		29		19-Jun-08		0:06:20		68.61		31.5		19-Jun-08		0:07:53		69.2		31

		19-Jun-08		2:07:10		69.8		34		19-Jun-08		2:06:20		68		37		19-Jun-08		2:07:53		69.2		35.5

		19-Jun-08		4:07:10		69.2		35		19-Jun-08		4:06:20		67.4		39.5		19-Jun-08		4:07:53		68.61		36.5

		19-Jun-08		6:07:10		69.8		34		19-Jun-08		6:06:20		67.4		39		19-Jun-08		6:07:53		69.2		35.5

		19-Jun-08		8:07:10		69.8		35.5		19-Jun-08		8:06:20		68		41.5		19-Jun-08		8:07:53		69.2		37.5

		19-Jun-08		10:07:10		71		33.5		19-Jun-08		10:06:20		70.41		36.5		19-Jun-08		10:07:53		69.2		36.5

		19-Jun-08		12:07:10		71		31		19-Jun-08		12:06:20		70.41		33		19-Jun-08		12:07:53		69.8		33

		19-Jun-08		14:07:10		70.41		34.5		19-Jun-08		14:06:20		71		36		19-Jun-08		14:07:53		69.8		36

		19-Jun-08		16:07:10		70.41		31		19-Jun-08		16:06:20		69.2		32.5		19-Jun-08		16:07:53		69.8		32.5

		19-Jun-08		18:07:10		71		25		19-Jun-08		18:06:20		69.2		26		19-Jun-08		18:07:53		69.2		27

		19-Jun-08		20:07:10		71		26		19-Jun-08		20:06:20		69.2		27		19-Jun-08		20:07:53		69.2		27.5

		19-Jun-08		22:07:10		71		30.5		19-Jun-08		22:06:20		68.61		31.5		19-Jun-08		22:07:53		69.2		31.5

		20-Jun-08		0:07:10		71		33		20-Jun-08		0:06:20		68		37		20-Jun-08		0:07:53		68.61		35.5

		20-Jun-08		2:07:10		70.41		33.5		20-Jun-08		2:06:20		68		37.5		20-Jun-08		2:07:53		68.61		35.5

		20-Jun-08		4:07:10		69.8		33.5		20-Jun-08		4:06:20		68		38		20-Jun-08		4:07:53		68.61		36

		20-Jun-08		6:07:10		69.2		34.5		20-Jun-08		6:06:20		67.4		39		20-Jun-08		6:07:53		68		36.5

		20-Jun-08		8:07:10		69.8		35.5		20-Jun-08		8:06:20		68.61		39		20-Jun-08		8:07:53		68.61		37.5

		20-Jun-08		10:07:10		71		35.5		20-Jun-08		10:06:20		70.41		38		20-Jun-08		10:07:53		68.61		38

		20-Jun-08		12:07:10		70.41		34		20-Jun-08		12:06:20		72.21		34.5		20-Jun-08		12:07:53		68.61		36.5

		20-Jun-08		14:07:10		70.41		31		20-Jun-08		14:06:20		69.8		32		20-Jun-08		14:07:53		68		33.5

		20-Jun-08		16:07:10		70.41		32.5		20-Jun-08		16:06:20		71		34.5		20-Jun-08		16:07:53		68.61		35.5

		20-Jun-08		18:07:10		70.41		29		20-Jun-08		18:06:20		69.2		30		20-Jun-08		18:07:53		68.61		31

		20-Jun-08		20:07:10		71		31.5		20-Jun-08		20:06:20		68		34.5		20-Jun-08		20:07:53		68.61		34.5

		20-Jun-08		22:07:10		71		32.5		20-Jun-08		22:06:20		68		36		20-Jun-08		22:07:53		68.61		35

		21-Jun-08		0:07:10		71		34.5		21-Jun-08		0:06:20		68.61		38.5		21-Jun-08		0:07:53		68.61		37

		21-Jun-08		2:07:10		70.41		35		21-Jun-08		2:06:20		67.4		41		21-Jun-08		2:07:53		68.61		37

		21-Jun-08		4:07:10		70.41		36		21-Jun-08		4:06:20		67.4		41		21-Jun-08		4:07:53		69.2		37.5

		21-Jun-08		6:07:10		69.8		36		21-Jun-08		6:06:20		68		43		21-Jun-08		6:07:53		68.61		38.5

		21-Jun-08		8:07:10		71		36		21-Jun-08		8:06:20		68.61		43		21-Jun-08		8:07:53		68.61		39

		21-Jun-08		10:07:10		71		35		21-Jun-08		10:06:20		69.2		37		21-Jun-08		10:07:53		69.2		37

		21-Jun-08		12:07:10		70.41		30.5		21-Jun-08		12:06:20		71		31.5		21-Jun-08		12:07:53		69.2		33

		21-Jun-08		14:07:10		71		30		21-Jun-08		14:06:20		70.41		30.5		21-Jun-08		14:07:53		69.2		31.5

		21-Jun-08		16:07:10		71		26.5		21-Jun-08		16:06:20		71.6		26.5		21-Jun-08		16:07:53		68.61		29

		21-Jun-08		18:07:10		70.41		23		21-Jun-08		18:06:20		70.41		24		21-Jun-08		18:07:53		69.2		26

		21-Jun-08		20:07:10		71		22.5		21-Jun-08		20:06:20		71		22.5		21-Jun-08		20:07:53		69.2		24.5

		21-Jun-08		22:07:10		71		27.5		21-Jun-08		22:06:20		70.41		29		21-Jun-08		22:07:53		69.2		30

		22-Jun-08		0:07:10		71		31		22-Jun-08		0:06:20		70.41		34		22-Jun-08		0:07:53		68.61		34.5

		22-Jun-08		2:07:10		71		31.5		22-Jun-08		2:06:20		69.8		35		22-Jun-08		2:07:53		68.61		35.5

		22-Jun-08		4:07:10		71		32.5		22-Jun-08		4:06:20		69.8		34.5		22-Jun-08		4:07:53		68.61		35.5

		22-Jun-08		6:07:10		70.41		33		22-Jun-08		6:06:20		69.2		35.5		22-Jun-08		6:07:53		68.61		35.5

		22-Jun-08		8:07:10		71		33.5		22-Jun-08		8:06:20		69.2		36.5		22-Jun-08		8:07:53		69.8		35.5

		22-Jun-08		10:07:10		71		34.5		22-Jun-08		10:06:20		70.41		37		22-Jun-08		10:07:53		69.8		37

		22-Jun-08		12:07:10		71.6		32		22-Jun-08		12:06:20		71		34.5		22-Jun-08		12:07:53		69.2		36

		22-Jun-08		14:07:10		71.6		29.5		22-Jun-08		14:06:20		71		32.5		22-Jun-08		14:07:53		69.8		33.5

		22-Jun-08		16:07:10		72.21		26		22-Jun-08		16:06:20		70.41		29		22-Jun-08		16:07:53		69.2		30.5

		22-Jun-08		18:07:10		72.21		22.5		22-Jun-08		18:06:20		70.41		25.5		22-Jun-08		18:07:53		69.2		26.5

		22-Jun-08		20:07:10		72.21		30.5		22-Jun-08		20:06:20		70.41		31.5		22-Jun-08		20:07:53		69.8		31.5

		22-Jun-08		22:07:10		71.6		31		22-Jun-08		22:06:20		70.41		34.5		22-Jun-08		22:07:53		69.2		34

		23-Jun-08		0:07:10		71		34.5		23-Jun-08		0:06:20		69.2		39		23-Jun-08		0:07:53		69.2		36.5

		23-Jun-08		2:07:10		70.41		35.5		23-Jun-08		2:06:20		69.8		41.5		23-Jun-08		2:07:53		69.2		38

		23-Jun-08		4:07:10		70.41		36		23-Jun-08		4:06:20		69.2		42		23-Jun-08		4:07:53		69.8		38

		23-Jun-08		6:07:10		70.41		35.5		23-Jun-08		6:06:20		68.61		42		23-Jun-08		6:07:53		69.8		37.5

		23-Jun-08		8:07:10		70.41		37		23-Jun-08		8:06:20		69.2		44		23-Jun-08		8:07:53		69.8		38.5

		23-Jun-08		10:07:10		71		38		23-Jun-08		10:06:20		69.2		45		23-Jun-08		10:07:53		69.8		39.5

		23-Jun-08		12:07:10		71		38.5		23-Jun-08		12:06:20		69.8		42.5		23-Jun-08		12:07:53		69.8		39.5

		23-Jun-08		14:07:10		71		39		23-Jun-08		14:06:20		70.41		44.5		23-Jun-08		14:07:53		69.8		41

		23-Jun-08		16:07:10		71.6		39.5		23-Jun-08		16:06:20		69.8		46.5		23-Jun-08		16:07:53		69.8		42

		23-Jun-08		18:07:10		71.6		38		23-Jun-08		18:06:20		70.41		42.5		23-Jun-08		18:07:53		69.2		41

		23-Jun-08		20:07:10		71.6		37		23-Jun-08		20:06:20		69.8		43		23-Jun-08		20:07:53		69.8		39.5

		23-Jun-08		22:07:10		71		36		23-Jun-08		22:06:20		69.2		42.5		23-Jun-08		22:07:53		69.8		38.5

		24-Jun-08		0:07:10		69.8		36.5		24-Jun-08		0:06:20		69.2		42		24-Jun-08		0:07:53		69.2		38.5

		24-Jun-08		2:07:10		70.41		36.5		24-Jun-08		2:06:20		68.61		42		24-Jun-08		2:07:53		69.8		38

		24-Jun-08		4:07:10		70.41		36		24-Jun-08		4:06:20		68		42.5		24-Jun-08		4:07:53		69.8		37.5

		24-Jun-08		6:07:10		70.41		37.5		24-Jun-08		6:06:20		67.4		45.5		24-Jun-08		6:07:53		69.8		38.5

		24-Jun-08		8:07:10		70.41		38.5		24-Jun-08		8:06:20		69.8		44.5		24-Jun-08		8:07:53		69.8		40

		24-Jun-08		10:07:10		70.41		38		24-Jun-08		10:06:20		71		44		24-Jun-08		10:07:53		69.2		40.5

		24-Jun-08		12:07:10		70.41		39.5		24-Jun-08		12:06:20		71.6		42.5		24-Jun-08		12:07:53		69.8		41

		24-Jun-08		14:07:10		70.41		38.5		24-Jun-08		14:06:20		71		42.5		24-Jun-08		14:07:53		68		42.5

		24-Jun-08		16:07:10		71		39		24-Jun-08		16:06:20		69.2		47		24-Jun-08		16:07:53		68		42.5

		24-Jun-08		18:07:10		71		38.5		24-Jun-08		18:06:20		69.2		45.5		24-Jun-08		18:07:53		69.2		41.5

		24-Jun-08		20:07:10		70.41		38.5		24-Jun-08		20:06:20		68.61		47		24-Jun-08		20:07:53		69.2		40.5

		24-Jun-08		22:07:10		70.41		38		24-Jun-08		22:06:20		68.61		44		24-Jun-08		22:07:53		69.2		39.5

		25-Jun-08		0:07:10		70.41		38.5		25-Jun-08		0:06:20		68		43.5		25-Jun-08		0:07:53		69.2		40

		25-Jun-08		2:07:10		70.41		37.5		25-Jun-08		2:06:20		67.4		46.5		25-Jun-08		2:07:53		69.8		39

		25-Jun-08		4:07:10		70.41		37.5		25-Jun-08		4:06:20		67.4		45		25-Jun-08		4:07:53		69.8		39

		25-Jun-08		6:07:10		70.41		37		25-Jun-08		6:06:20		66.81		45		25-Jun-08		6:07:53		69.8		38.5

		25-Jun-08		8:07:10		69.8		38.5		25-Jun-08		8:06:20		68		44		25-Jun-08		8:07:53		68.61		40.5

		25-Jun-08		10:07:10		70.41		39		25-Jun-08		10:06:20		69.8		46.5		25-Jun-08		10:07:53		68.61		42

		25-Jun-08		12:07:10		70.41		40.5		25-Jun-08		12:06:20		69.8		44		25-Jun-08		12:07:53		68		43.5

		25-Jun-08		14:07:10		70.41		42		25-Jun-08		14:06:20		69.8		47		25-Jun-08		14:07:53		67.4		46.5

		25-Jun-08		16:07:10		70.41		41.5		25-Jun-08		16:06:20		69.8		50		25-Jun-08		16:07:53		68.61		45

		25-Jun-08		18:07:10		71		39.5		25-Jun-08		18:06:20		69.2		48		25-Jun-08		18:07:53		68.61		43.5

		25-Jun-08		20:07:10		71		38.5		25-Jun-08		20:06:20		69.2		44		25-Jun-08		20:07:53		69.2		42

		25-Jun-08		22:07:10		71		38		25-Jun-08		22:06:20		69.8		43.5		25-Jun-08		22:07:53		69.2		40.5

		26-Jun-08		0:07:10		70.41		38		26-Jun-08		0:06:20		68.61		46		26-Jun-08		0:07:53		69.2		40

		26-Jun-08		2:07:10		69.8		38		26-Jun-08		2:06:20		68.61		44.5		26-Jun-08		2:07:53		68.61		39.5

		26-Jun-08		4:07:10		70.41		38		26-Jun-08		4:06:20		68.61		44		26-Jun-08		4:07:53		69.2		39.5

		26-Jun-08		6:07:10		70.41		37.5		26-Jun-08		6:06:20		68		44.5		26-Jun-08		6:07:53		69.8		39

		26-Jun-08		8:07:10		70.41		39		26-Jun-08		8:06:20		69.2		44		26-Jun-08		8:07:53		68		41.5

		26-Jun-08		10:07:10		70.41		39		26-Jun-08		10:06:20		69.2		45		26-Jun-08		10:07:53		68.61		41.5

		26-Jun-08		12:07:10		70.41		40.5		26-Jun-08		12:06:20		71		43.5		26-Jun-08		12:07:53		68.61		43

		26-Jun-08		14:07:10		70.41		42.5		26-Jun-08		14:06:20		70.41		47.5		26-Jun-08		14:07:53		68		46

		26-Jun-08		16:07:10		70.41		42.5		26-Jun-08		16:06:20		68.61		49.5		26-Jun-08		16:07:53		68.61		45.5

		26-Jun-08		18:07:10		70.41		41.5		26-Jun-08		18:06:20		69.2		47		26-Jun-08		18:07:53		69.2		43.5

		26-Jun-08		20:07:10		70.41		40		26-Jun-08		20:06:20		69.2		47.5		26-Jun-08		20:07:53		69.2		42

		26-Jun-08		22:07:10		70.41		39		26-Jun-08		22:06:20		69.2		46.5		26-Jun-08		22:07:53		69.2		41

		27-Jun-08		0:07:10		69.8		38		27-Jun-08		0:06:20		68		47.5		27-Jun-08		0:07:53		68.61		40.5

		27-Jun-08		2:07:10		69.8		38		27-Jun-08		2:06:20		67.4		46		27-Jun-08		2:07:53		69.2		40

		27-Jun-08		4:07:10		70.41		38		27-Jun-08		4:06:20		68		45		27-Jun-08		4:07:53		69.8		39

		27-Jun-08		6:07:10		69.8		37.5		27-Jun-08		6:06:20		67.4		45		27-Jun-08		6:07:53		69.8		39

		27-Jun-08		8:07:10		70.41		39		27-Jun-08		8:06:20		68.61		49.5		27-Jun-08		8:07:53		69.2		40.5

		27-Jun-08		10:07:10		70.41		39.5		27-Jun-08		10:06:20		69.8		44.5		27-Jun-08		10:07:53		68.61		42

		27-Jun-08		12:07:10		70.41		41		27-Jun-08		12:06:20		70.41		50.5		27-Jun-08		12:07:53		69.2		43

		27-Jun-08		14:07:10		70.41		43		27-Jun-08		14:06:20		71		48.5		27-Jun-08		14:07:53		68		46

		27-Jun-08		16:07:10		70.41		42.5		27-Jun-08		16:06:20		70.41		48.5		27-Jun-08		16:07:53		68		46

		27-Jun-08		18:07:10		70.41		40		27-Jun-08		18:06:20		70.41		44		27-Jun-08		18:07:53		68.61		43

		27-Jun-08		20:07:10		70.41		39		27-Jun-08		20:06:20		70.41		44.5		27-Jun-08		20:07:53		68.61		42

		27-Jun-08		22:07:10		70.41		38.5		27-Jun-08		22:06:20		70.41		45		27-Jun-08		22:07:53		69.2		41

		28-Jun-08		0:07:10		69.8		38.5		28-Jun-08		0:06:20		69.2		46		28-Jun-08		0:07:53		68.61		41

		28-Jun-08		2:07:10		69.8		38.5		28-Jun-08		2:06:20		69.2		45		28-Jun-08		2:07:53		68.61		40.5

		28-Jun-08		4:07:10		69.2		38.5		28-Jun-08		4:06:20		69.2		44.5		28-Jun-08		4:07:53		68.61		40

		28-Jun-08		6:07:10		69.2		39.5		28-Jun-08		6:06:20		69.2		45.5		28-Jun-08		6:07:53		68.61		40.5

		28-Jun-08		8:07:10		69.8		39.5		28-Jun-08		8:06:20		70.41		44		28-Jun-08		8:07:53		68.61		41.5

		28-Jun-08		10:07:10		71		40.5		28-Jun-08		10:06:20		71		50.5		28-Jun-08		10:07:53		68.61		43

		28-Jun-08		12:07:10		70.41		42.5		28-Jun-08		12:06:20		71.6		48		28-Jun-08		12:07:53		69.8		44

		28-Jun-08		14:07:10		70.41		43.5		28-Jun-08		14:06:20		71.6		53.5		28-Jun-08		14:07:53		68.61		46

		28-Jun-08		16:07:10		70.41		44		28-Jun-08		16:06:20		71		50		28-Jun-08		16:07:53		69.2		46.5

		28-Jun-08		18:07:10		71		40.5		28-Jun-08		18:06:20		70.41		51		28-Jun-08		18:07:53		69.2		43.5

		28-Jun-08		20:07:10		71		39.5		28-Jun-08		20:06:20		70.41		49.5		28-Jun-08		20:07:53		69.2		42

		28-Jun-08		22:07:10		70.41		39.5		28-Jun-08		22:06:20		69.8		49		28-Jun-08		22:07:53		69.8		41

		29-Jun-08		0:07:10		69.8		39.5		29-Jun-08		0:06:20		69.8		49.5		29-Jun-08		0:07:53		69.2		41.5

		29-Jun-08		2:07:10		69.8		40		29-Jun-08		2:06:20		69.2		49		29-Jun-08		2:07:53		69.2		41.5

		29-Jun-08		4:07:10		69.8		40		29-Jun-08		4:06:20		69.2		50		29-Jun-08		4:07:53		69.8		41.5

		29-Jun-08		6:07:10		69.8		40		29-Jun-08		6:06:20		69.2		50.5		29-Jun-08		6:07:53		69.8		41

		29-Jun-08		8:07:10		69.8		40		29-Jun-08		8:06:20		69.8		50.5		29-Jun-08		8:07:53		69.8		41.5

		29-Jun-08		10:07:10		70.41		40.5		29-Jun-08		10:06:20		69.2		47		29-Jun-08		10:07:53		69.8		41.5

		29-Jun-08		12:07:10		70.41		41.5		29-Jun-08		12:06:20		69.2		53.5		29-Jun-08		12:07:53		69.8		42.5

		29-Jun-08		14:07:10		70.41		42.5		29-Jun-08		14:06:20		69.8		48		29-Jun-08		14:07:53		70.41		44

		29-Jun-08		16:07:10		71		43		29-Jun-08		16:06:20		69.8		52.5		29-Jun-08		16:07:53		70.41		44.5

		29-Jun-08		18:07:10		71		42		29-Jun-08		18:06:20		70.41		53		29-Jun-08		18:07:53		70.41		44

		29-Jun-08		20:07:10		71		40		29-Jun-08		20:06:20		69.2		52		29-Jun-08		20:07:53		69.8		42

		29-Jun-08		22:07:10		70.41		39.5		29-Jun-08		22:06:20		69.2		50		29-Jun-08		22:07:53		69.8		41

		30-Jun-08		0:07:10		69.2		40		30-Jun-08		0:06:20		69.2		48.5		30-Jun-08		0:07:53		69.2		41

		30-Jun-08		2:07:10		69.2		40		30-Jun-08		2:06:20		69.2		48.5		30-Jun-08		2:07:53		69.8		41

		30-Jun-08		4:07:10		69.2		40		30-Jun-08		4:06:20		69.2		49		30-Jun-08		4:07:53		69.2		41

		30-Jun-08		6:07:10		69.2		40		30-Jun-08		6:06:20		69.2		49		30-Jun-08		6:07:53		69.2		41

		30-Jun-08		8:07:10		69.2		40		30-Jun-08		8:06:20		69.2		49		30-Jun-08		8:07:53		69.8		41

		30-Jun-08		10:07:10		69.2		40		30-Jun-08		10:06:20		69.8		47.5		30-Jun-08		10:07:53		69.8		41

		30-Jun-08		12:07:10		70.41		41.5		30-Jun-08		12:06:20		69.8		49.5		30-Jun-08		12:07:53		70.41		42

		30-Jun-08		14:07:10		70.41		43		30-Jun-08		14:06:20		70.41		48		30-Jun-08		14:07:53		70.41		43.5

		30-Jun-08		16:07:10		71		43		30-Jun-08		16:06:20		70.41		50.5		30-Jun-08		16:07:53		70.41		44.5

		30-Jun-08		18:07:10		71		41.5		30-Jun-08		18:06:20		69.8		50		30-Jun-08		18:07:53		70.41		43.5

		30-Jun-08		20:07:10		71		40		30-Jun-08		20:06:20		69.8		50		30-Jun-08		20:07:53		70.41		42

		30-Jun-08		22:07:10		69.8		39.5		30-Jun-08		22:06:20		69.8		48.5		30-Jun-08		22:07:53		69.8		40.5

		1-Jul-08		0:07:10		69.8		40		1-Jul-08		0:06:20		69.2		48.5		1-Jul-08		0:07:53		69.2		41

		1-Jul-08		2:07:10		69.2		40		1-Jul-08		2:06:20		69.2		48.5		1-Jul-08		2:07:53		69.2		41

		1-Jul-08		4:07:10		69.8		40.5		1-Jul-08		4:06:20		68.61		49		1-Jul-08		4:07:53		69.8		41

		1-Jul-08		6:07:10		69.8		40		1-Jul-08		6:06:20		68.61		49.5		1-Jul-08		6:07:53		69.8		41

		1-Jul-08		8:07:10		70.41		40.5		1-Jul-08		8:06:20		71		48.5		1-Jul-08		8:07:53		69.8		41

		1-Jul-08		10:07:10		70.41		40		1-Jul-08		10:06:20		71		47.5		1-Jul-08		10:07:53		69.8		41.5

		1-Jul-08		12:07:10		70.41		42		1-Jul-08		12:06:20		70.41		46		1-Jul-08		12:07:53		70.41		43.5

		1-Jul-08		14:07:10		71		44		1-Jul-08		14:06:20		70.41		48		1-Jul-08		14:07:53		69.8		45

		1-Jul-08		16:07:10		70.41		44.5		1-Jul-08		16:06:20		70.41		57.5		1-Jul-08		16:07:53		69.2		47

		1-Jul-08		18:07:10		71		43		1-Jul-08		18:06:20		70.41		53		1-Jul-08		18:07:53		69.2		45.5

		1-Jul-08		20:07:10		71		41		1-Jul-08		20:06:20		70.41		53.5		1-Jul-08		20:07:53		69.2		44

		1-Jul-08		22:07:10		71		40		1-Jul-08		22:06:20		69.8		52		1-Jul-08		22:07:53		69.8		42

		2-Jul-08		0:07:10		70.41		40		2-Jul-08		0:06:20		69.2		52		2-Jul-08		0:07:53		69.2		41.5

		2-Jul-08		2:07:10		69.8		40		2-Jul-08		2:06:20		69.2		52		2-Jul-08		2:07:53		69.2		42

		2-Jul-08		4:07:10		69.8		40		2-Jul-08		4:06:20		69.8		51.5		2-Jul-08		4:07:53		69.8		41.5

		2-Jul-08		6:07:10		69.8		40.5		2-Jul-08		6:06:20		69.2		53		2-Jul-08		6:07:53		69.2		42

		2-Jul-08		8:07:10		70.41		41		2-Jul-08		8:06:20		70.41		49		2-Jul-08		8:07:53		69.2		42.5

		2-Jul-08		10:07:10		70.41		40.5		2-Jul-08		10:06:20		69.8		46.5		2-Jul-08		10:07:53		69.8		42

		2-Jul-08		12:07:10		71		42.5		2-Jul-08		12:06:20		70.41		54		2-Jul-08		12:07:53		69.8		43.5

		2-Jul-08		14:07:10		70.41		44.5		2-Jul-08		14:06:20		70.41		50.5		2-Jul-08		14:07:53		69.2		46.5

		2-Jul-08		16:07:10		71		44.5		2-Jul-08		16:06:20		70.41		57.5		2-Jul-08		16:07:53		69.2		47

		2-Jul-08		18:07:10		71		43		2-Jul-08		18:06:20		69.8		49		2-Jul-08		18:07:53		69.8		45

		2-Jul-08		20:07:10		71		41		2-Jul-08		20:06:20		69.8		52		2-Jul-08		20:07:53		69.8		43

		2-Jul-08		22:07:10		70.41		40		2-Jul-08		22:06:20		69.8		49.5		2-Jul-08		22:07:53		69.8		41.5

		3-Jul-08		0:07:10		69.2		40		3-Jul-08		0:06:20		69.8		49		3-Jul-08		0:07:53		69.2		41.5

		3-Jul-08		2:07:10		70.41		40		3-Jul-08		2:06:20		69.2		48		3-Jul-08		2:07:53		69.8		41

		3-Jul-08		4:07:10		70.41		40		3-Jul-08		4:06:20		68.61		49		3-Jul-08		4:07:53		69.8		41

		3-Jul-08		6:07:10		69.8		40		3-Jul-08		6:06:20		68		49.5		3-Jul-08		6:07:53		69.8		41

		3-Jul-08		8:07:10		70.41		40.5		3-Jul-08		8:06:20		69.8		49		3-Jul-08		8:07:53		69.8		41.5

		3-Jul-08		10:07:10		70.41		41		3-Jul-08		10:06:20		70.41		45		3-Jul-08		10:07:53		69.8		41.5

		3-Jul-08		12:07:10		70.41		43		3-Jul-08		12:06:20		71		45.5		3-Jul-08		12:07:53		69.8		43.5

		3-Jul-08		14:07:10		70.41		44.5		3-Jul-08		14:06:20		71		47		3-Jul-08		14:07:53		69.2		46

		3-Jul-08		16:07:10		70.41		44		3-Jul-08		16:06:20		69.8		53		3-Jul-08		16:07:53		69.2		46

		3-Jul-08		18:07:10		70.41		43		3-Jul-08		18:06:20		70.41		49		3-Jul-08		18:07:53		69.8		44.5

		3-Jul-08		20:07:10		70.41		41.5		3-Jul-08		20:06:20		70.41		51.5		3-Jul-08		20:07:53		69.8		43.5

		3-Jul-08		22:07:10		71		40		3-Jul-08		22:06:20		69.2		51		3-Jul-08		22:07:53		69.8		42

		4-Jul-08		0:07:10		69.8		39.5		4-Jul-08		0:06:20		69.2		49.5		4-Jul-08		0:07:53		69.2		41.5

		4-Jul-08		2:07:10		69.2		40.5		4-Jul-08		2:06:20		69.2		47.5		4-Jul-08		2:07:53		69.2		41.5

		4-Jul-08		4:07:10		69.8		40		4-Jul-08		4:06:20		68.61		48		4-Jul-08		4:07:53		69.2		41.5

		4-Jul-08		6:07:10		69.8		39.5		4-Jul-08		6:06:20		69.8		44		4-Jul-08		6:07:53		69.2		41.5

		4-Jul-08		8:07:10		69.8		40		4-Jul-08		8:06:20		69.8		50.5		4-Jul-08		8:07:53		69.2		41.5

		4-Jul-08		10:07:10		71		42		4-Jul-08		10:06:20		69.8		50.5		4-Jul-08		10:07:53		69.2		43

		4-Jul-08		12:07:10		70.41		47		4-Jul-08		12:06:20		71.6		55		4-Jul-08		12:07:53		69.2		48

		4-Jul-08		14:07:10		71		47.5		4-Jul-08		14:06:20		71		55		4-Jul-08		14:07:53		69.2		50

		4-Jul-08		16:07:10		71		48		4-Jul-08		16:06:20		71.6		57		4-Jul-08		16:07:53		69.2		50

		4-Jul-08		18:07:10		71.6		46		4-Jul-08		18:06:20		71.6		54		4-Jul-08		18:07:53		69.2		49.5

		4-Jul-08		20:07:10		71.6		43.5		4-Jul-08		20:06:20		71.6		59		4-Jul-08		20:07:53		69.2		46.5

		4-Jul-08		22:07:10		71		41.5		4-Jul-08		22:06:20		69.8		56.5		4-Jul-08		22:07:53		69.2		45

		5-Jul-08		0:07:10		70.41		42		5-Jul-08		0:06:20		69.8		56.5		5-Jul-08		0:07:53		68.61		44.5

		5-Jul-08		2:07:10		69.8		41		5-Jul-08		2:06:20		69.8		54.5		5-Jul-08		2:07:53		69.2		43.5

		5-Jul-08		4:07:10		69.8		41		5-Jul-08		4:06:20		69.2		53		5-Jul-08		4:07:53		69.2		42.5

		5-Jul-08		6:07:10		69.2		41.5		5-Jul-08		6:06:20		68.61		54.5		5-Jul-08		6:07:53		68.61		43

		5-Jul-08		8:07:10		69.8		42		5-Jul-08		8:06:20		69.2		55		5-Jul-08		8:07:53		69.2		44

		5-Jul-08		10:07:10		71		43		5-Jul-08		10:06:20		69.8		51.5		5-Jul-08		10:07:53		69.2		45

		5-Jul-08		12:07:10		71		45		5-Jul-08		12:06:20		69.8		53.5		5-Jul-08		12:07:53		69.2		47.5

		5-Jul-08		14:07:10		71.6		45.5		5-Jul-08		14:06:20		70.41		55		5-Jul-08		14:07:53		69.2		48.5

		5-Jul-08		16:07:10		71.6		46		5-Jul-08		16:06:20		70.41		55.5		5-Jul-08		16:07:53		69.2		49.5

		5-Jul-08		18:07:10		71.6		45		5-Jul-08		18:06:20		70.41		59.5		5-Jul-08		18:07:53		68.61		48.5

		5-Jul-08		20:07:10		71		42.5		5-Jul-08		20:06:20		69.8		58		5-Jul-08		20:07:53		69.2		46

		5-Jul-08		22:07:10		71		41.5		5-Jul-08		22:06:20		69.2		57.5		5-Jul-08		22:07:53		69.2		45

		6-Jul-08		0:07:10		70.41		41		6-Jul-08		0:06:20		69.2		56		6-Jul-08		0:07:53		69.2		43.5

		6-Jul-08		2:07:10		69.8		40.5		6-Jul-08		2:06:20		68.61		54.5		6-Jul-08		2:07:53		68.61		43

		6-Jul-08		4:07:10		69.8		40.5		6-Jul-08		4:06:20		69.2		52.5		6-Jul-08		4:07:53		68.61		42.5

		6-Jul-08		6:07:10		69.2		41.5		6-Jul-08		6:06:20		69.2		51.5		6-Jul-08		6:07:53		68.61		42.5

		6-Jul-08		8:07:10		69.8		41.5		6-Jul-08		8:06:20		69.2		53		6-Jul-08		8:07:53		68.61		43.5

		6-Jul-08		10:07:10		71		43		6-Jul-08		10:06:20		69.8		55.5		6-Jul-08		10:07:53		69.2		45

		6-Jul-08		12:07:10		71		47		6-Jul-08		12:06:20		70.41		58.5		6-Jul-08		12:07:53		69.2		49

		6-Jul-08		14:07:10		71.6		49		6-Jul-08		14:06:20		70.41		57.5		6-Jul-08		14:07:53		69.2		52

		6-Jul-08		16:07:10		72.21		46		6-Jul-08		16:06:20		70.41		54		6-Jul-08		16:07:53		69.2		51

		6-Jul-08		18:07:10		72.21		47		6-Jul-08		18:06:20		69.8		61		6-Jul-08		18:07:53		69.2		51

		6-Jul-08		20:07:10		72.21		45		6-Jul-08		20:06:20		70.41		54.5		6-Jul-08		20:07:53		69.2		50

		6-Jul-08		22:07:10		72.21		43		6-Jul-08		22:06:20		69.8		62		6-Jul-08		22:07:53		68.61		48

		7-Jul-08		0:07:10		71.6		41.5		7-Jul-08		0:06:20		69.8		57		7-Jul-08		0:07:53		69.2		45

		7-Jul-08		2:07:10		71		41		7-Jul-08		2:06:20		69.8		52		7-Jul-08		2:07:53		69.2		44.5

		7-Jul-08		4:07:10		70.41		41		7-Jul-08		4:06:20		69.2		54		7-Jul-08		4:07:53		69.2		43.5

		7-Jul-08		6:07:10		69.8		40.5		7-Jul-08		6:06:20		69.2		52.5		7-Jul-08		6:07:53		68.61		43

		7-Jul-08		8:07:10		70.41		41.5		7-Jul-08		8:06:20		69.2		53.5		7-Jul-08		8:07:53		69.2		43.5

		7-Jul-08		10:07:10		71		44		7-Jul-08		10:06:20		69.2		58		7-Jul-08		10:07:53		69.2		46

		7-Jul-08		12:07:10		71.6		47.5		7-Jul-08		12:06:20		69.8		62		7-Jul-08		12:07:53		69.2		50

		7-Jul-08		14:07:10		71.6		50.5		7-Jul-08		14:06:20		70.41		59.5		7-Jul-08		14:07:53		69.2		54

		7-Jul-08		16:07:10		72.21		48.5		7-Jul-08		16:06:20		69.8		62		7-Jul-08		16:07:53		69.8		52.5

		7-Jul-08		18:07:10		72.21		46.5		7-Jul-08		18:06:20		70.41		59.5		7-Jul-08		18:07:53		69.2		52

		7-Jul-08		20:07:10		72.21		42.5		7-Jul-08		20:06:20		69.8		55		7-Jul-08		20:07:53		68.61		47.5

		7-Jul-08		22:07:10		72.21		40.5		7-Jul-08		22:06:20		69.8		50		7-Jul-08		22:07:53		69.2		44.5

		8-Jul-08		0:07:10		71		40		8-Jul-08		0:06:20		69.2		52		8-Jul-08		0:07:53		69.2		43.5

		8-Jul-08		2:07:10		70.41		40.5		8-Jul-08		2:06:20		69.2		51		8-Jul-08		2:07:53		69.2		42.5

		8-Jul-08		4:07:10		69.8		40.5		8-Jul-08		4:06:20		68.61		51.5		8-Jul-08		4:07:53		68.61		42.5

		8-Jul-08		6:07:10		69.2		40.5		8-Jul-08		6:06:20		69.2		51.5		8-Jul-08		6:07:53		68.61		42.5

		8-Jul-08		8:07:10		70.41		41.5		8-Jul-08		8:06:20		69.8		53.5		8-Jul-08		8:07:53		68.61		44

		8-Jul-08		10:07:10		71.6		44		8-Jul-08		10:06:20		69.8		50.5		8-Jul-08		10:07:53		68.61		47.5

		8-Jul-08		12:07:10		71		49		8-Jul-08		12:06:20		69.8		54		8-Jul-08		12:07:53		69.2		51

		8-Jul-08		14:07:10		71		49.5		8-Jul-08		14:06:20		70.41		55.5		8-Jul-08		14:07:53		69.2		53.5

		8-Jul-08		16:07:10		71		50		8-Jul-08		16:06:20		70.41		58.5		8-Jul-08		16:07:53		68.61		53.5

		8-Jul-08		18:07:10		71		49		8-Jul-08		18:06:20		70.41		55.5		8-Jul-08		18:07:53		68.61		52.5

		8-Jul-08		20:07:10		71		45		8-Jul-08		20:06:20		71		57.5		8-Jul-08		20:07:53		68		50

		8-Jul-08		22:07:10		71.6		43		8-Jul-08		22:06:20		70.41		53		8-Jul-08		22:07:53		68.61		47.5

		9-Jul-08		0:07:10		71.6		42		9-Jul-08		0:06:20		70.41		52		9-Jul-08		0:07:53		69.2		46

		9-Jul-08		2:07:10		71		41.5		9-Jul-08		2:06:20		69.8		50		9-Jul-08		2:07:53		69.2		44.5

		9-Jul-08		4:07:10		71		41.5		9-Jul-08		4:06:20		69.2		53.5		9-Jul-08		4:07:53		69.2		44

		9-Jul-08		6:07:10		70.41		41		9-Jul-08		6:06:20		69.2		52.5		9-Jul-08		6:07:53		69.2		43.5

		9-Jul-08		8:07:10		71		42.5		9-Jul-08		8:06:20		70.41		56.5		9-Jul-08		8:07:53		68.61		45

		9-Jul-08		10:07:10		71		45.5		9-Jul-08		10:06:20		71		53		9-Jul-08		10:07:53		69.2		48.5

		9-Jul-08		12:07:10		71		49		9-Jul-08		12:06:20		71.6		51		9-Jul-08		12:07:53		69.8		50.5

		9-Jul-08		14:07:10		70.41		47.5		9-Jul-08		14:06:20		71.6		51		9-Jul-08		14:07:53		68.61		51

		9-Jul-08		16:07:10		70.41		49		9-Jul-08		16:06:20		71.6		52.5		9-Jul-08		16:07:53		69.8		50

		9-Jul-08		18:07:10		70.41		48.5		9-Jul-08		18:06:20		70.41		53		9-Jul-08		18:07:53		69.8		50

		9-Jul-08		20:07:10		71		44		9-Jul-08		20:06:20		71		53		9-Jul-08		20:07:53		69.2		47.5

		9-Jul-08		22:07:10		71.6		43		9-Jul-08		22:06:20		70.41		54		9-Jul-08		22:07:53		69.8		46

		10-Jul-08		0:07:10		71.6		42		10-Jul-08		0:06:20		69.8		54.5		10-Jul-08		0:07:53		69.2		45

		10-Jul-08		2:07:10		71.6		41.5		10-Jul-08		2:06:20		69.8		54		10-Jul-08		2:07:53		69.8		44

		10-Jul-08		4:07:10		71		42		10-Jul-08		4:06:20		69.2		58		10-Jul-08		4:07:53		69.8		44

		10-Jul-08		6:07:10		71		41.5		10-Jul-08		6:06:20		69.8		55.5		10-Jul-08		6:07:53		69.8		43.5

		10-Jul-08		8:07:10		71		42.5		10-Jul-08		8:06:20		69.8		58.5		10-Jul-08		8:07:53		69.8		45

		10-Jul-08		10:07:10		71		44.5		10-Jul-08		10:06:20		69.8		58.5		10-Jul-08		10:07:53		68		48.5

		10-Jul-08		12:07:10		70.41		49		10-Jul-08		12:06:20		69.8		56.5		10-Jul-08		12:07:53		69.2		50.5

		10-Jul-08		14:07:10		70.41		52.5		10-Jul-08		14:06:20		71.6		54		10-Jul-08		14:07:53		69.2		54.5

		10-Jul-08		16:07:10		70.41		51		10-Jul-08		16:06:20		71.6		60		10-Jul-08		16:07:53		68.61		54

		10-Jul-08		18:07:10		70.41		49.5		10-Jul-08		18:06:20		70.41		63		10-Jul-08		18:07:53		69.8		51

		10-Jul-08		20:07:10		71		46		10-Jul-08		20:06:20		70.41		58.5		10-Jul-08		20:07:53		69.8		48.5

		10-Jul-08		22:07:10		71.6		43.5		10-Jul-08		22:06:20		70.41		57		10-Jul-08		22:07:53		69.8		47

		11-Jul-08		0:07:10		71.6		42.5		11-Jul-08		0:06:20		69.8		61		11-Jul-08		0:07:53		69.2		46.5

		11-Jul-08		2:07:10		71.6		42.5		11-Jul-08		2:06:20		69.8		53.5		11-Jul-08		2:07:53		69.8		45.5

		11-Jul-08		4:07:10		71		42		11-Jul-08		4:06:20		69.8		53.5		11-Jul-08		4:07:53		69.2		44.5

		11-Jul-08		6:07:10		71		41.5		11-Jul-08		6:06:20		69.8		57		11-Jul-08		6:07:53		69.2		44.5

		11-Jul-08		8:07:10		71		42.5		11-Jul-08		8:06:20		71.6		49		11-Jul-08		8:07:53		69.8		45

		11-Jul-08		10:07:10		71		45.5		11-Jul-08		10:06:20		72.21		56.5		11-Jul-08		10:07:53		68.61		48

		11-Jul-08		12:07:10		71		48.5		11-Jul-08		12:06:20		69.8		63		11-Jul-08		12:07:53		69.2		50.5

		11-Jul-08		14:07:10		71		49.5		11-Jul-08		14:06:20		70.41		55.5		11-Jul-08		14:07:53		69.2		52.5

		11-Jul-08		16:07:10		71		47		11-Jul-08		16:06:20		69.8		63.5		11-Jul-08		16:07:53		69.2		49.5

		11-Jul-08		18:07:10		71		45		11-Jul-08		18:06:20		70.41		54		11-Jul-08		18:07:53		69.2		47.5

		11-Jul-08		20:07:10		71		42.5		11-Jul-08		20:06:20		70.41		53		11-Jul-08		20:07:53		69.2		45.5

		11-Jul-08		22:07:10		71		40.5		11-Jul-08		22:06:20		70.41		52.5		11-Jul-08		22:07:53		69.8		43.5

		12-Jul-08		0:07:10		70.41		41		12-Jul-08		0:06:20		69.2		53		12-Jul-08		0:07:53		69.2		43

		12-Jul-08		2:07:10		70.41		41		12-Jul-08		2:06:20		69.2		52.5		12-Jul-08		2:07:53		69.8		42.5

		12-Jul-08		4:07:10		69.8		40.5		12-Jul-08		4:06:20		69.2		52.5		12-Jul-08		4:07:53		69.2		42.5

		12-Jul-08		6:07:10		69.8		40.5		12-Jul-08		6:06:20		69.2		52.5		12-Jul-08		6:07:53		69.2		42.5

		12-Jul-08		8:07:10		70.41		41.5		12-Jul-08		8:06:20		69.2		55		12-Jul-08		8:07:53		69.2		43

		12-Jul-08		10:07:10		71		42.5		12-Jul-08		10:06:20		69.2		57.5		12-Jul-08		10:07:53		69.2		44.5

		12-Jul-08		12:07:10		71		45.5		12-Jul-08		12:06:20		68.61		53.5		12-Jul-08		12:07:53		69.8		46.5

		12-Jul-08		14:07:10		70.41		45.5		12-Jul-08		14:06:20		69.2		52.5		12-Jul-08		14:07:53		69.8		47.5

		12-Jul-08		16:07:10		70.41		45.5		12-Jul-08		16:06:20		69.2		63.5		12-Jul-08		16:07:53		69.8		47.5

		12-Jul-08		18:07:10		70.41		44.5		12-Jul-08		18:06:20		69.8		54		12-Jul-08		18:07:53		70.41		46.5

		12-Jul-08		20:07:10		71		42.5		12-Jul-08		20:06:20		70.41		54		12-Jul-08		20:07:53		70.41		45

		12-Jul-08		22:07:10		71		42.5		12-Jul-08		22:06:20		69.8		59.5		12-Jul-08		22:07:53		70.41		44.5

		13-Jul-08		0:07:10		71		42.5		13-Jul-08		0:06:20		69.8		60		13-Jul-08		0:07:53		69.8		44

		13-Jul-08		2:07:10		71		42.5		13-Jul-08		2:06:20		69.2		60.5		13-Jul-08		2:07:53		70.41		44.5

		13-Jul-08		4:07:10		71		42.5		13-Jul-08		4:06:20		69.2		60		13-Jul-08		4:07:53		70.41		44.5

		13-Jul-08		6:07:10		71		42.5		13-Jul-08		6:06:20		69.2		61		13-Jul-08		6:07:53		70.41		44.5

		13-Jul-08		8:07:10		71		42.5		13-Jul-08		8:06:20		68.61		59		13-Jul-08		8:07:53		69.8		44

		13-Jul-08		10:07:10		71		43		13-Jul-08		10:06:20		69.2		59.5		13-Jul-08		10:07:53		70.41		44.5

		13-Jul-08		12:07:10		71		45		13-Jul-08		12:06:20		69.2		59		13-Jul-08		12:07:53		69.8		46

		13-Jul-08		14:07:10		71		45		13-Jul-08		14:06:20		70.41		54		13-Jul-08		14:07:53		69.8		47

		13-Jul-08		16:07:10		71.6		44.5		13-Jul-08		16:06:20		69.8		55.5		13-Jul-08		16:07:53		69.8		47

		13-Jul-08		18:07:10		71.6		44		13-Jul-08		18:06:20		69.2		58.5		13-Jul-08		18:07:53		69.2		47

		13-Jul-08		20:07:10		71.6		43		13-Jul-08		20:06:20		69.2		57.5		13-Jul-08		20:07:53		69.8		46.5

		13-Jul-08		22:07:10		71		42.5		13-Jul-08		22:06:20		69.2		60.5		13-Jul-08		22:07:53		70.41		45.5

		14-Jul-08		0:07:10		71		42.5		14-Jul-08		0:06:20		69.2		58		14-Jul-08		0:07:53		70.41		44.5

		14-Jul-08		2:07:10		70.41		42		14-Jul-08		2:06:20		69.2		52		14-Jul-08		2:07:53		70.41		43.5

		14-Jul-08		4:07:10		70.41		42		14-Jul-08		4:06:20		69.2		57.5		14-Jul-08		4:07:53		69.8		43

		14-Jul-08		6:07:10		69.8		41		14-Jul-08		6:06:20		69.2		55.5		14-Jul-08		6:07:53		69.8		42.5

		14-Jul-08		8:07:10		69.8		42		14-Jul-08		8:06:20		69.2		56.5		14-Jul-08		8:07:53		69.8		43

		14-Jul-08		10:07:10		70.41		44		14-Jul-08		10:06:20		69.2		53.5		14-Jul-08		10:07:53		70.41		44.5

		14-Jul-08		12:07:10		70.41		47		14-Jul-08		12:06:20		69.8		62		14-Jul-08		12:07:53		70.41		47

		14-Jul-08		14:07:10		71		47		14-Jul-08		14:06:20		69.8		59.5		14-Jul-08		14:07:53		70.41		48

		14-Jul-08		16:07:10		71		47		14-Jul-08		16:06:20		69.8		60.5		14-Jul-08		16:07:53		70.41		48.5

		14-Jul-08		18:07:10		71		45		14-Jul-08		18:06:20		70.41		57		14-Jul-08		18:07:53		70.41		47

		14-Jul-08		20:07:10		71		43.5		14-Jul-08		20:06:20		69.8		59.5		14-Jul-08		20:07:53		70.41		46

		14-Jul-08		22:07:10		71		42.5		14-Jul-08		22:06:20		69.2		59.5		14-Jul-08		22:07:53		70.41		44.5

		15-Jul-08		0:07:10		70.41		42		15-Jul-08		0:06:20		69.2		57		15-Jul-08		0:07:53		70.41		43.5

		15-Jul-08		2:07:10		70.41		42		15-Jul-08		2:06:20		68.61		56		15-Jul-08		2:07:53		70.41		43.5

		15-Jul-08		4:07:10		69.8		41.5		15-Jul-08		4:06:20		68.61		59		15-Jul-08		4:07:53		69.8		43

		15-Jul-08		6:07:10		69.8		42		15-Jul-08		6:06:20		69.2		56.5		15-Jul-08		6:07:53		69.8		43

		15-Jul-08		8:07:10		70.41		42		15-Jul-08		8:06:20		68		53.5		15-Jul-08		8:07:53		69.8		43.5

		15-Jul-08		10:07:10		71		42		15-Jul-08		10:06:20		69.2		54.5		15-Jul-08		10:07:53		69.8		44

		15-Jul-08		12:07:10		71		44.5		15-Jul-08		12:06:20		69.2		60		15-Jul-08		12:07:53		69.8		45

		15-Jul-08		14:07:10		71		46.5		15-Jul-08		14:06:20		69.2		62		15-Jul-08		14:07:53		69.2		48.5

		15-Jul-08		16:07:10		70.41		45.5		15-Jul-08		16:06:20		69.2		57.5		15-Jul-08		16:07:53		69.8		47.5

		15-Jul-08		18:07:10		70.41		44.5		15-Jul-08		18:06:20		69.8		54.5		15-Jul-08		18:07:53		69.8		46

		15-Jul-08		20:07:10		71		42.5		15-Jul-08		20:06:20		70.41		53.5		15-Jul-08		20:07:53		69.8		44.5

		15-Jul-08		22:07:10		71		41.5		15-Jul-08		22:06:20		69.2		54.5		15-Jul-08		22:07:53		69.8		43.5

		16-Jul-08		0:07:10		70.41		41.5		16-Jul-08		0:06:20		69.2		57		16-Jul-08		0:07:53		69.2		43

		16-Jul-08		2:07:10		69.8		41.5		16-Jul-08		2:06:20		69.8		55.5		16-Jul-08		2:07:53		69.2		43.5

		16-Jul-08		4:07:10		69.8		41.5		16-Jul-08		4:06:20		68.61		56.5		16-Jul-08		4:07:53		69.2		43

		16-Jul-08		6:07:10		69.8		41		16-Jul-08		6:06:20		69.2		56		16-Jul-08		6:07:53		69.2		43

		16-Jul-08		8:07:10		70.41		41.5		16-Jul-08		8:06:20		68.61		58.5		16-Jul-08		8:07:53		69.2		43

		16-Jul-08		10:07:10		70.41		42		16-Jul-08		10:06:20		69.8		55		16-Jul-08		10:07:53		68.61		44.5

		16-Jul-08		12:07:10		71		42.5		16-Jul-08		12:06:20		69.8		51		16-Jul-08		12:07:53		69.2		44.5

		16-Jul-08		14:07:10		71		44.5		16-Jul-08		14:06:20		69.8		51		16-Jul-08		14:07:53		68.61		47.5

		16-Jul-08		16:07:10		71		45		16-Jul-08		16:06:20		70.41		57		16-Jul-08		16:07:53		68.61		48

		automated instrument that measured temp-humidity is no longer in use.  Temp and humidity data and charts are generated in "CER Pressure" tab. JH 1-29-09





		



CER 1 Temperature(°F)

CER 2 Temperature(°F)

CER 3 Temperature(°F)

Date

Temperature (Deg. F)

Figure 9.  CER Temperature



		



CER 1 Humidity(%)

CER 3 Humidity(%)

QA Humidity(%)

CER 2 Humidity(%)

Date

Humidity (%)

Figure 10.  CER Relative Humidity



		






_1294743785.xls
Chart1

		39330		39330		38807		38807		38807		38807		38807

		39355		39355		38807		38807		38807		38807		38807

		39386		39386		38811		38811		38811		38811		38811

		39416		39416		38811		38811		38811		38811		38811

		39447		39447		38812		38812		38812		38812		38812

		39478		39478		38812		38812		38812		38812		38812

		39507		39507		38813		38813		38813		38813		38813

		39538		39538		38813		38813		38813		38813		38813

		39568		39568		38814		38814		38814		38814		38814

		39599		39599		38814		38814		38814		38814		38814

		39629		39629		38817		38817		38817		38817		38817

		39660		39660		38817		38817		38817		38817		38817

		39690		39690		38818		38818		38818		38818		38818

		39721		39721		38818		38818		38818		38818		38818

						38819		38819		38819		38819		38819

						38819		38819		38819		38819		38819

						38820		38820		38820		38820		38820

						38820		38820		38820		38820		38820

						38824		38824		38824		38824		38824

						38824		38824		38824		38824		38824

						38825		38825		38825		38825		38825

						38825		38825		38825		38825		38825

						38826		38826		38826		38826		38826

						38826		38826		38826		38826		38826

						38827		38827		38827		38827		38827

						38827		38827		38827		38827		38827

						38828		38828		38828		38828		38828

						38828		38828		38828		38828		38828

						38832		38832		38832		38832		38832

						38832		38832		38832		38832		38832

						38833		38833		38833		38833		38833

						38833		38833		38833		38833		38833

						38834		38834		38834		38834		38834

						38834		38834		38834		38834		38834

						38835		38835		38835		38835		38835

						38835		38835		38835		38835		38835

						38923		38923		38923		38923		38923

						38923		38923		38923		38923		38923

						38924		38924		38924		38924		38924

						38924		38924		38924		38924		38924

						38925		38925		38925		38925		38925

						38925		38925		38925		38925		38925

						38926		38926		38926		38926		38926

						38926		38926		38926		38926		38926

						38927		38927		38927		38927		38927

						38927		38927		38927		38927		38927

						38928		38928		38928		38928		38928

						38928		38928		38928		38928		38928

						38929		38929		38929		38929		38929

						38929		38929		38929		38929		38929

						38930		38930		38930		38930		38930

						38930		38930		38930		38930		38930

						38931		38931		38931		38931		38931

						38931		38931		38931		38931		38931

						38932		38932		38932		38932		38932

						38932		38932		38932		38932		38932

						38933		38933		38933		38933		38933

						38933		38933		38933		38933		38933

						38936		38936		38936		38936		38936

						38936		38936		38936		38936		38936

						38937		38937		38937		38937		38937

						38937		38937		38937		38937		38937

						38939		38939		38939		38939		38939

						38939		38939		38939		38939		38939

						38943		38943		38943		38943		38943

						38944		38944		38944		38944		38944

						38945		38945		38945		38945		38945

						38945		38945		38945		38945		38945

						38946		38946		38946		38946		38946

						38946		38946		38946		38946		38946

						38947		38947		38947		38947		38947

						38947		38947		38947		38947		38947

						38950		38950		38950		38950		38950

						38951		38951		38951		38951		38951

						38951		38951		38951		38951		38951

						38952		38952		38952		38952		38952

						38952		38952		38952		38952		38952

						38953		38953		38953		38953		38953

						38953		38953		38953		38953		38953

						38954		38954		38954		38954		38954

						38954		38954		38954		38954		38954

						38957		38957		38957		38957		38957

						38957		38957		38957		38957		38957

						38959		38959		38959		38959		38959

						38959		38959		38959		38959		38959

						38960		38960		38960		38960		38960

						38960		38960		38960		38960		38960

						38961		38961		38961		38961		38961

						38961		38961		38961		38961		38961

						38965		38965		38965		38965		38965

						38965		38965		38965		38965		38965

						38966		38966		38966		38966		38966

						38966		38966		38966		38966		38966

						38967		38967		38967		38967		38967

						38967		38967		38967		38967		38967

						38968		38968		38968		38968		38968

						38968		38968		38968		38968		38968

						38971		38971		38971		38971		38971

						38971		38971		38971		38971		38971

						38972		38972		38972		38972		38972

						38972		38972		38972		38972		38972

						38973		38973		38973		38973		38973

						38973		38973		38973		38973		38973

						38974		38974		38974		38974		38974

						38974		38974		38974		38974		38974

						38975		38975		38975		38975		38975

						38975		38975		38975		38975		38975

						38978		38978		38978		38978		38978

						38978		38978		38978		38978		38978

						38979		38979		38979		38979		38979

						38979		38979		38979		38979		38979

						38980		38980		38980		38980		38980

						38980		38980		38980		38980		38980

						38981		38981		38981		38981		38981

						38981		38981		38981		38981		38981

						38983		38983		38983		38983		38983

						38983		38983		38983		38983		38983

						38985		38985		38985		38985		38985

						38985		38985		38985		38985		38985

						38992		38992		38992		38992		38992

						38992		38992		38992		38992		38992

						38993		38993		38993		38993		38993

						38993		38993		38993		38993		38993

						38994		38994		38994		38994		38994

						38996		38996		38996		38996		38996

						38999		38999		38999		38999		38999

						38999		38999		38999		38999		38999

						39000		39000		39000		39000		39000

						39000		39000		39000		39000		39000

						39001		39001		39001		39001		39001

						39001		39001		39001		39001		39001

						39002		39002		39002		39002		39002

						39002		39002		39002		39002		39002

						39003		39003		39003		39003		39003

						39003		39003		39003		39003		39003

						39006		39006		39006		39006		39006

						39006		39006		39006		39006		39006

						39007		39007		39007		39007		39007

						39007		39007		39007		39007		39007

						39008		39008		39008		39008		39008

						39008		39008		39008		39008		39008

						39009		39009		39009		39009		39009

						39009		39009		39009		39009		39009

						39010		39010		39010		39010		39010

						39010		39010		39010		39010		39010

						39013		39013		39013		39013		39013

						39013		39013		39013		39013		39013

						39014		39014		39014		39014		39014

						39014		39014		39014		39014		39014

						39016		39016		39016		39016		39016

						39016		39016		39016		39016		39016

						39020		39020		39020		39020		39020

						39020		39020		39020		39020		39020

						39021		39021		39021		39021		39021

						39021		39021		39021		39021		39021

						39022		39022		39022		39022		39022

						39022		39022		39022		39022		39022

						39023		39023		39023		39023		39023

						39023		39023		39023		39023		39023

						39024		39024		39024		39024		39024

						39024		39024		39024		39024		39024

						39027		39027		39027		39027		39027

						39027		39027		39027		39027		39027

						39028		39028		39028		39028		39028

						39028		39028		39028		39028		39028

						39029		39029		39029		39029		39029

						39029		39029		39029		39029		39029

						39030		39030		39030		39030		39030

						39030		39030		39030		39030		39030

						39031		39031		39031		39031		39031

						39031		39031		39031		39031		39031

						39034		39034		39034		39034		39034

						39034		39034		39034		39034		39034

						39035		39035		39035		39035		39035

						39035		39035		39035		39035		39035

						39036		39036		39036		39036		39036

						39036		39036		39036		39036		39036

						39037		39037		39037		39037		39037

						39038		39038		39038		39038		39038

						39038		39038		39038		39038		39038

						39041		39041		39041		39041		39041

						39041		39041		39041		39041		39041

						39042		39042		39042		39042		39042

						39042		39042		39042		39042		39042

						39043		39043		39043		39043		39043

						39043		39043		39043		39043		39043

						39048		39048		39048		39048		39048

						39048		39048		39048		39048		39048

						39049		39049		39049		39049		39049

						39049		39049		39049		39049		39049

						39050		39050		39050		39050		39050

						39050		39050		39050		39050		39050

						39051		39051		39051		39051		39051

						39051		39051		39051		39051		39051

						39052		39052		39052		39052		39052

						39052		39052		39052		39052		39052

						39055		39055		39055		39055		39055

						39055		39055		39055		39055		39055

						39056		39056		39056		39056		39056

						39056		39056		39056		39056		39056

						39057		39057		39057		39057		39057

						39057		39057		39057		39057		39057

						39058		39058		39058		39058		39058

						39058		39058		39058		39058		39058

						39059		39059		39059		39059		39059

						39059		39059		39059		39059		39059

						39062		39062		39062		39062		39062

						39062		39062		39062		39062		39062

						39063		39063		39063		39063		39063

						39063		39063		39063		39063		39063

						39064		39064		39064		39064		39064

						39064		39064		39064		39064		39064

						39065		39065		39065		39065		39065

						39069		39069		39069		39069		39069

						39069		39069		39069		39069		39069

						39070		39070		39070		39070		39070

						39070		39070		39070		39070		39070

						39071		39071		39071		39071		39071

						39071		39071		39071		39071		39071

						39072		39072		39072		39072		39072

						39072		39072		39072		39072		39072

						39073		39073		39073		39073		39073

						39078		39078		39078		39078		39078

						39079		39079		39079		39079		39079

						39079		39079		39079		39079		39079

						39080		39080		39080		39080		39080

						39080		39080		39080		39080		39080

						39084		39084		39084		39084		39084

						39084		39084		39084		39084		39084

						39085		39085		39085		39085		39085

						39085		39085		39085		39085		39085

						39086		39086		39086		39086		39086

						39086		39086		39086		39086		39086

						39087		39087		39087		39087		39087

						39087		39087		39087		39087		39087

						39090		39090		39090		39090		39090

						39090		39090		39090		39090		39090

						39091		39091		39091		39091		39091

						39091		39091		39091		39091		39091

						39092		39092		39092		39092		39092

						39092		39092		39092		39092		39092

						39093		39093		39093		39093		39093

						39093		39093		39093		39093		39093

						39094		39094		39094		39094		39094

						39094		39094		39094		39094		39094

						39097		39097		39097		39097		39097

						39097		39097		39097		39097		39097

						39098		39098		39098		39098		39098

						39098		39098		39098		39098		39098

						39099		39099		39099		39099		39099

						39099		39099		39099		39099		39099

						39100		39100		39100		39100		39100

						39100		39100		39100		39100		39100

						39101		39101		39101		39101		39101

						39101		39101		39101		39101		39101

						39104		39104		39104		39104		39104

						39104		39104		39104		39104		39104

						39105		39105		39105		39105		39105

						39105		39105		39105		39105		39105

						39106		39106		39106		39106		39106

						39106		39106		39106		39106		39106

						39107		39107		39107		39107		39107

						39107		39107		39107		39107		39107

						39108		39108		39108		39108		39108

						39108		39108		39108		39108		39108

						39111		39111		39111		39111		39111

						39111		39111		39111		39111		39111

						39112		39112		39112		39112		39112

						39112		39112		39112		39112		39112

						39113		39113		39113		39113		39113

						39113		39113		39113		39113		39113

						39114		39114		39114		39114		39114

						39114		39114		39114		39114		39114

						39115		39115		39115		39115		39115

						39115		39115		39115		39115		39115

						39118		39118		39118		39118		39118

						39118		39118		39118		39118		39118

						39119		39119		39119		39119		39119

						39119		39119		39119		39119		39119

						39120		39120		39120		39120		39120

						39120		39120		39120		39120		39120

						39121		39121		39121		39121		39121

						39121		39121		39121		39121		39121

						39122		39122		39122		39122		39122

						39122		39122		39122		39122		39122

						39125		39125		39125		39125		39125

						39125		39125		39125		39125		39125

						39126		39126		39126		39126		39126

						39126		39126		39126		39126		39126

						39127		39127		39127		39127		39127

						39127		39127		39127		39127		39127

						39128		39128		39128		39128		39128

						39129		39129		39129		39129		39129

						39133		39133		39133		39133		39133

						39133		39133		39133		39133		39133

						39134		39134		39134		39134		39134

						39134		39134		39134		39134		39134

						39135		39135		39135		39135		39135

						39135		39135		39135		39135		39135

						39136		39136		39136		39136		39136

						39136		39136		39136		39136		39136

						39139		39139		39139		39139		39139

						39139		39139		39139		39139		39139

						39140		39140		39140		39140		39140

						39140		39140		39140		39140		39140

						39141		39141		39141		39141		39141

						39142		39142		39142		39142		39142

						39143		39143		39143		39143		39143

						39146		39146		39146		39146		39146

						39147		39147		39147		39147		39147

						39148		39148		39148		39148		39148

						39149		39149		39149		39149		39149

						39150		39150		39150		39150		39150

						39153		39153		39153		39153		39153

						39154		39154		39154		39154		39154

						39155		39155		39155		39155		39155

						39156		39156		39156		39156		39156

						39157		39157		39157		39157		39157

						39160		39160		39160		39160		39160

						39161		39161		39161		39161		39161

						39162		39162		39162		39162		39162

						39163		39163		39163		39163		39163

						39164		39164		39164		39164		39164

						39167		39167		39167		39167		39167

						39168		39168		39168		39168		39168

						39169		39169		39169		39169		39169

						39170		39170		39170		39170		39170

						39171		39171		39171		39171		39171

						39174		39174		39174		39174		39174

						39175		39175		39175		39175		39175

						39176		39176		39176		39176		39176

						39177		39177		39177		39177		39177

						39178		39178		39178		39178		39178

						39181		39181		39181		39181		39181

						39182		39182		39182		39182		39182

						39183		39183		39183		39183		39183

						39184		39184		39184		39184		39184

						39185		39185		39185		39185		39185

						39188		39188		39188		39188		39188

						39189		39189		39189		39189		39189

						39190		39190		39190		39190		39190

						39191		39191		39191		39191		39191

						39195		39195		39195		39195		39195

						39196		39196		39196		39196		39196

						39197		39197		39197		39197		39197

						39198		39198		39198		39198		39198

						39199		39199		39199		39199		39199

						39202		39202		39202		39202		39202

						39203		39203		39203		39203		39203

						39204		39204		39204		39204		39204

						39205		39205		39205		39205		39205

						39206		39206		39206		39206		39206

						39209		39209		39209		39209		39209

						39210		39210		39210		39210		39210

						39211		39211		39211		39211		39211

						39212		39212		39212		39212		39212

						39213		39213		39213		39213		39213

						39216		39216		39216		39216		39216

						39217		39217		39217		39217		39217

						39218		39218		39218		39218		39218

						39219		39219		39219		39219		39219

						39220		39220		39220		39220		39220

						39223		39223		39223		39223		39223

						39224		39224		39224		39224		39224

						39225		39225		39225		39225		39225

						39226		39226		39226		39226		39226

						39226		39226		39226		39226		39226

						39231		39231		39231		39231		39231

						39232		39232		39232		39232		39232

						39233		39233		39233		39233		39233

						39234		39234		39234		39234		39234

						39237		39237		39237		39237		39237

						39238		39238		39238		39238		39238

						39239		39239		39239		39239		39239

						39240		39240		39240		39240		39240

						39241		39241		39241		39241		39241

						39242		39242		39242		39242		39242

						39244		39244		39244		39244		39244

						39245		39245		39245		39245		39245

						39246		39246		39246		39246		39246

						39247		39247		39247		39247		39247

						39248		39248		39248		39248		39248

						39251		39251		39251		39251		39251

						39252		39252		39252		39252		39252

						39253		39253		39253		39253		39253

						39254		39254		39254		39254		39254

						39258		39258		39258		39258		39258

						39259		39259		39259		39259		39259

						39260		39260		39260		39260		39260

						39261		39261		39261		39261		39261

						39262		39262		39262		39262		39262

						39265		39265		39265		39265		39265

						39266		39266		39266		39266		39266

						39268		39268		39268		39268		39268

						39269		39269		39269		39269		39269

						39272		39272		39272		39272		39272

						39273		39273		39273		39273		39273

						39274		39274		39274		39274		39274

						39275		39275		39275		39275		39275

						39276		39276		39276		39276		39276

						39279		39279		39279		39279		39279

						39280		39280		39280		39280		39280

						39281		39281		39281		39281		39281

						39282		39282		39282		39282		39282

						39283		39283		39283		39283		39283

						39286		39286		39286		39286		39286

						39287		39287		39287		39287		39287

						39288		39288		39288		39288		39288

						39289		39289		39289		39289		39289

						39291		39291		39291		39291		39291

						39293		39293		39293		39293		39293

						39294		39294		39294		39294		39294

						39295		39295		39295		39295		39295

						39296		39296		39296		39296		39296

						39297		39297		39297		39297		39297

						39298		39298		39298		39298		39298

						39300		39300		39300		39300		39300

						39301		39301		39301		39301		39301

						39302		39302		39302		39302		39302

						39303		39303		39303		39303		39303

						39304		39304		39304		39304		39304

						39307		39307		39307		39307		39307

						39308		39308		39308		39308		39308

						39309		39309		39309		39309		39309

						39310		39310		39310		39310		39310

						39311		39311		39311		39311		39311

						39314		39314		39314		39314		39314

						39315		39315		39315		39315		39315

						39316		39316		39316		39316		39316

						39317		39317		39317		39317		39317

						39318		39318		39318		39318		39318

						39321		39321		39321		39321		39321

						39322		39322		39322		39322		39322

						39323		39323		39323		39323		39323

						39324		39324		39324		39324		39324

						39325		39325		39325		39325		39325

						39329		39329		39329		39329		39329

						39330		39330		39330		39330		39330

						39331		39331		39331		39331		39331

						39332		39332		39332		39332		39332

						39333		39333		39333		39333		39333

						39335		39335		39335		39335		39335

						39336		39336		39336		39336		39336

						39337		39337		39337		39337		39337

						39338		39338		39338		39338		39338

						39339		39339		39339		39339		39339

						39340		39340		39340		39340		39340

						39342		39342		39342		39342		39342

						39343		39343		39343		39343		39343

						39344		39344		39344		39344		39344

						39345		39345		39345		39345		39345

						39346		39346		39346		39346		39346

						39349		39349		39349		39349		39349

						39350		39350		39350		39350		39350

						39351		39351		39351		39351		39351

						39352		39352		39352		39352		39352

						39353		39353		39353		39353		39353

						39356		39356		39356		39356		39356

						39357		39357		39357		39357		39357

						39358		39358		39358		39358		39358

						39359		39359		39359		39359		39359

						39360		39360		39360		39360		39360

						39363		39363		39363		39363		39363

						39364		39364		39364		39364		39364

						39365		39365		39365		39365		39365

						39366		39366		39366		39366		39366

						39367		39367		39367		39367		39367

						39368		39368		39368		39368		39368

						39370		39370		39370		39370		39370

						39371		39371		39371		39371		39371

						39372		39372		39372		39372		39372

						39373		39373		39373		39373		39373

						39374		39374		39374		39374		39374

						39377		39377		39377		39377		39377

						39378		39378		39378		39378		39378

						39379		39379		39379		39379		39379

						39380		39380		39380		39380		39380

						39381		39381		39381		39381		39381

						39384		39384		39384		39384		39384

						39385		39385		39385		39385		39385

						39386		39386		39386		39386		39386

						39387		39387		39387		39387		39387

						39388		39388		39388		39388		39388

						39391		39391		39391		39391		39391

						39392		39392		39392		39392		39392

						39393		39393		39393		39393		39393

						39394		39394		39394		39394		39394

						39395		39395		39395		39395		39395

						39398		39398		39398		39398		39398

						39399		39399		39399		39399		39399

						39400		39400		39400		39400		39400

						39401		39401		39401		39401		39401

						39402		39402		39402		39402		39402

						39405		39405		39405		39405		39405

						39406		39406		39406		39406		39406

						39407		39407		39407		39407		39407

						39412		39412		39412		39412		39412

						39413		39413		39413		39413		39413

						39414		39414		39414		39414		39414

						39415		39415		39415		39415		39415

						39416		39416		39416		39416		39416

						39419		39419		39419		39419		39419

						39420		39420		39420		39420		39420

						39421		39421		39421		39421		39421

						39422		39422		39422		39422		39422

						39423		39423		39423		39423		39423

						39426		39426		39426		39426		39426

						39427		39427		39427		39427		39427

						39428		39428		39428		39428		39428

						39429		39429		39429		39429		39429

						39430		39430		39430		39430		39430

						39433		39433		39433		39433		39433

						39434		39434		39434		39434		39434

						39435		39435		39435		39435		39435

						39436		39436		39436		39436		39436

						39437		39437		39437		39437		39437

						39442		39442		39442		39442		39442

						39443		39443		39443		39443		39443

						39444		39444		39444		39444		39444

						39447		39447		39447		39447		39447

						39492		39492		39492		39492		39492

						39493		39493		39493		39493		39493

						39497		39497		39497		39497		39497

						39498		39498		39498		39498		39498

						39499		39499		39499		39499		39499

						39500		39500		39500		39500		39500

						39503		39503		39503		39503		39503

						39504		39504		39504		39504		39504

						39505		39505		39505		39505		39505

						39506		39506		39506		39506		39506

						39507		39507		39507		39507		39507

						39510		39510		39510		39510		39510

						39511		39511		39511		39511		39511

						39512		39512		39512		39512		39512

						39513		39513		39513		39513		39513

						39514		39514		39514		39514		39514

						39517		39517		39517		39517		39517

						39518		39518		39518		39518		39518

						39519		39519		39519		39519		39519

						39521		39521		39521		39521		39521

						39524		39524		39524		39524		39524

						39525		39525		39525		39525		39525

						39526		39526		39526		39526		39526

						39527		39527		39527		39527		39527

						39528		39528		39528		39528		39528

						39531		39531		39531		39531		39531

						39532		39532		39532		39532		39532

						39533		39533		39533		39533		39533

						39534		39534		39534		39534		39534

						39535		39535		39535		39535		39535

						39538		39538		39538		39538		39538

						39539		39539		39539		39539		39539

						39540		39540		39540		39540		39540

						39541		39541		39541		39541		39541

						39542		39542		39542		39542		39542

						39543		39543		39543		39543		39543

						39545		39545		39545		39545		39545

						39546		39546		39546		39546		39546

						39547		39547		39547		39547		39547

						39548		39548		39548		39548		39548

						39549		39549		39549		39549		39549

						39552		39552		39552		39552		39552

						39553		39553		39553		39553		39553

						39554		39554		39554		39554		39554

						39555		39555		39555		39555		39555

						39556		39556		39556		39556		39556

						39557		39557		39557		39557		39557

						39559		39559		39559		39559		39559

						39560		39560		39560		39560		39560

						39561		39561		39561		39561		39561

						39562		39562		39562		39562		39562

						39563		39563		39563		39563		39563

						39566		39566		39566		39566		39566

						39567		39567		39567		39567		39567

						39568		39568		39568		39568		39568

						39569		39569		39569		39569		39569

						39570		39570		39570		39570		39570

						39571		39571		39571		39571		39571

						39573		39573		39573		39573		39573

						39574		39574		39574		39574		39574

						39575		39575		39575		39575		39575

						39576		39576		39576		39576		39576

						39577		39577		39577		39577		39577

						39578		39578		39578		39578		39578

						39580		39580		39580		39580		39580

						39581		39581		39581		39581		39581

						39582		39582		39582		39582		39582

						39583		39583		39583		39583		39583

						39584		39584		39584		39584		39584

						39587		39587		39587		39587		39587

						39588		39588		39588		39588		39588

						39589		39589		39589		39589		39589

						39590		39590		39590		39590		39590

						39591		39591		39591		39591		39591

						39595		39595		39595		39595		39595

						39596		39596		39596		39596		39596

						39597		39597		39597		39597		39597

						39598		39598		39598		39598		39598

						39601		39601		39601		39601		39601

						39602		39602		39602		39602		39602

						39603		39603		39603		39603		39603

						39604		39604		39604		39604		39604

						39605		39605		39605		39605		39605

						39608		39608		39608		39608		39608

						39609		39609		39609		39609		39609

						39610		39610		39610		39610		39610

						39611		39611		39611		39611		39611

						39612		39612		39612		39612		39612

						39615		39615		39615		39615		39615

						39616		39616		39616		39616		39616

						39617		39617		39617		39617		39617

						39618		39618		39618		39618		39618

						39619		39619		39619		39619		39619

						39620		39620		39620		39620		39620

						39622		39622		39622		39622		39622

						39623		39623		39623		39623		39623

						39624		39624		39624		39624		39624

						39625		39625		39625		39625		39625

						39626		39626		39626		39626		39626

						39629		39629		39629		39629		39629

						39630		39630		39630		39630		39630

						39631		39631		39631		39631		39631

						39632		39632		39632		39632		39632

						39636		39636		39636		39636		39636

						39637		39637		39637		39637		39637

						39638		39638		39638		39638		39638

						39639		39639		39639		39639		39639

						39640		39640		39640		39640		39640

						39641		39641		39641		39641		39641

						39643		39643		39643		39643		39643

						39644		39644		39644		39644		39644

						39645		39645		39645		39645		39645

						39646		39646		39646		39646		39646

						39647		39647		39647		39647		39647

						39648		39648		39648		39648		39648

						39650		39650		39650		39650		39650

						39651		39651		39651		39651		39651

						39652		39652		39652		39652		39652

						39653		39653		39653		39653		39653

						39654		39654		39654		39654		39654

						39655		39655		39655		39655		39655

						39657		39657		39657		39657		39657

						39658		39658		39658		39658		39658

						39659		39659		39659		39659		39659

						39660		39660		39660		39660		39660

						39661		39661		39661		39661		39661

						39662		39662		39662		39662		39662

						39664		39664		39664		39664		39664

						39665		39665		39665		39665		39665

						39666		39666		39666		39666		39666

						39667		39667		39667		39667		39667

						39668		39668		39668		39668		39668

						39669		39669		39669		39669		39669

						39671		39671		39671		39671		39671

						39672		39672		39672		39672		39672

						39673		39673		39673		39673		39673

						39674		39674		39674		39674		39674

						39675		39675		39675		39675		39675

						39676		39676		39676		39676		39676

						39678		39678		39678		39678		39678

						39679		39679		39679		39679		39679

						39680		39680		39680		39680		39680

						39681		39681		39681		39681		39681

						39682		39682		39682		39682		39682

						39683		39683		39683		39683		39683

						39685		39685		39685		39685		39685

						39686		39686		39686		39686		39686

						39687		39687		39687		39687		39687

						39688		39688		39688		39688		39688

						39689		39689		39689		39689		39689

						39693		39693		39693		39693		39693

						39694		39694		39694		39694		39694

						39695		39695		39695		39695		39695

						39696		39696		39696		39696		39696

						39697		39697		39697		39697		39697

						39699		39699		39699		39699		39699

						39700		39700		39700		39700		39700

						39701		39701		39701		39701		39701

						39702		39702		39702		39702		39702

						39703		39703		39703		39703		39703

						39704		39704		39704		39704		39704

						39706		39706		39706		39706		39706

						39707		39707		39707		39707		39707

						39708		39708		39708		39708		39708

						39709		39709		39709		39709		39709

						39710		39710		39710		39710		39710

						39711		39711		39711		39711		39711

						39713		39713		39713		39713		39713

						39714		39714		39714		39714		39714

						39715		39715		39715		39715		39715

						39716		39716		39716		39716		39716

						39717		39717		39717		39717		39717

						39718		39718		39718		39718		39718

						39720		39720		39720		39720		39720

						39721		39721		39721		39721		39721



Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)

R&D Bio-Safety Cabinet South (left axis)

Date

Diff. Pressure (Water Column In.)

Mfg Bio-Safety Cabinet South CFM

Figure 7.  CER2 Bio-Safety Cabinet Differential Pressure Daily Run Chart

0.25

0.1

0.25

0.1

0.25

0.1

0.25

0.1

0.25

0.1

0.25

0.1

0.25

0.1

0.25

0.1

0.25

0.1

0.25

0.1

0.25

0.1

0.2

0.15

0.2

0.15

0.2

0.15

0.61

0.4

0.61

0.41

0.6

0.41

0.6

0.41

0.61

0.41

0.61

0.41

0.61

0.41

0.61

0.41

0.6

0.42

0.6

0.4

0.6

0.41

0.61

0.41

0.65

0.4

0.61

0.41

0.6

0.4

0.6

0.4

0.62

0.4

0.62

0.42

0.62

0.42

0.6

0.4

0.62

0.42

0.62

0.42

0.62

0.42

0.61

0.42

0.62

0.42

0.62

0.42

0.62

0.42

0.62

0.42

0.62

0.42

0.62

0.42

0.62

0.42

0.61

0.41

0.62

0.42

0.61

0.41

0.62

0.42

0.62

0.42

0.62

0.42

0.64

0.44

0.62

0.42

0.62

0.42

0.62

0.42

0.62

0.42

0.62

0.42

0.62

0.42

0.62

0.42

0.62

0.42

0.62

0.4

0.62

0.41

0.62

0.42

0.62

0.42

0.62

0.42

0.62

0.42

0.62

0.4

0.62

0.42

0.62

0.42

0.62

0.42

0.66

0.44

0.64

0.42

0.64

0.42

0.66

0.44

0.66

0.44

0.66

0.44

0.64

0.44

0.64

0.44

0.64

0.44

0.64

0.42

0.64

0.44

0.64

0.42

0.64

0.44

0.64

0.44

0.66

0.42

0.6

0.42

0.66

0.42

0.66

0.42

0.64

0.42

0.66

0.4

0.66

0.42

0.64

0.42

0.66

0.42

0.64

0.42

0.62

0.44

0.64

0.44

0.64

0.44

0.292

0.485

61

1180

0.309

0.28

0.414

61

1172

0.31

0.293

0.426

60

1184

0.309

0.26

0.41

63

1184

0.309

0.29

0.441

62

1164

0.305

0.281

0.419

62

1184

0.307

0.288

0.421

63

1184

0.311

0.281

0.413

64

1192

0.312

0.288

0.413

62

1184

0.311

0.283

0.457

62

1172

0.31

0.256

0.409

63

1184

0.311

0.285

0.435

63

1204

0.311

0.261

0.438

63

1184

0.311

0.291

0.445

63

1184

0.311

0.281

0.458

61

1184

0.311

0.282

0.455

63

1192

0.322

0.264

0.428

64

1184

0.321

0.285

0.438

63

1204

0.322

0.261

0.422

62

1188

0.312

0.261

0.451

63

1184

0.321

0.26

0.439

63

1196

0.32

0.279

0.422

63

1196

0.32

0.273

0.419

64

1192

0.321

0.262

0.431

64

1192

0.321

0.277

0.439

63

1196

0.322

0.238

0.418

63

1184

0.321

0.264

0.445

63

1192

0.319

0.276

0.447

63

1204

0.321

0.28

0.46

63

1204

0.32

0.26

0.44

63

1192

0.32

0.3

0.48

63

1204

0.32

0.28

0.46

61

1192

0.32

0.28

0.44

63

1204

0.32

0.28

0.44

64

1192

0.32

0.26

0.44

63

1196

0.32

0.26

0.44

63

1196

0.32

0.26

0.46

65

1204

0.32

0.28

0.44

61

1192

0.32

0.28

0.44

63

1196

0.32

0.28

0.44

61

1204

0.32

0.28

0.44

61

1192

0.32

0.28

0.46

61

1196

0.32

0.28

0.44

62

1196

0.32

0.28

0.48

62

1196

0.32

0.28

0.48

62

1196

0.32

0.28

0.48

62

1196

0.32

0.28

0.48

62

1196

0.32

0.28

0.46

64

1196

0.32

0.28

0.46

64

1196

0.32

0.28

0.48

63

1196

0.32

0.28

0.46

63

1196

0.32

0.26

0.44

63

1204

0.32

0.26

0.44

63

1204

0.32

0.28

0.44

60

1184

0.32

0.28

0.46

60

1192

0.32

0.28

0.46

60

1196

0.32

0.28

0.46

60

1210

0.32

0.28

0.46

60

1210

0.32

0.28

0.44

60

1192

0.32

0.28

0.44

60

1184

0.32

0.28

0.44

62

1196

0.32

0.28

0.44

60

1196

0.32

0.3

0.46

62

1204

0.32

0.3

0.46

62

1204

0.32

0.26

0.42

60

1196

0.32

0.26

0.46

61

1192

0.32

0.3

0.46

60

1184

0.32

0.3

0.46

60

1196

0.32

0.3

0.44

60

1184

0.32

0.28

0.44

60

1204

0.32

0.28

0.44

62

1196

0.32

0.28

0.46

60

1196

0.32

0.28

0.42

61

1176

0.32

0.28

0.46

61

1172

0.32

0.28

0.44

61

1196

0.32

0.28

0.44

61

1204

0.32

0.26

0.44

61

1200

0.32

0.28

0.48

61

1196

0.32

0.28

0.44

60

1200

0.28

0.28

0.42

61

1196

0.32

0.28

0.44

61

1188

0.32

0.3

0.44

61

1192

0.32

0.28

0.44

61

1188

0.32

0.32

0.48

61

1188

0.32

0.3

0.44

55

1172

0.32

0.3

0.48

55

1196

0.32

0.3

0.48

55

1196

0.32

0.26

0.44

55

1208

0.32

0.3

0.46

55

1204

0.32

0.28

0.44

55

1216

0.32

0.3

0.44

55

1196

0.32

0.28

0.46

55

1196

0.32

0.28

0.46

55

1196

0.32

0.26

0.46

55

32

0.32

0.28

0.44

57

32

0.32

0.28

0.42

60

32

0.32

0.28

0.44

60

32

0.32

0.28

0.44

60

32

0.32

0.32

0.44

60

32

0.32

0.3

0.44

60

32

0.32

0.28

0.44

60

32

0.32

0.3

0.46

60

32

0.32

0.32

0.48

57

32

0.32

0.28

0.44

57

32

0.32

0.28

0.42

60

32

0.32

0.28

0.42

0.32

0.32

0.48

55

1104

0.32

0.3

0.48

55

1104

0.32

0.3

0.48

61

1200

0.32

0.28

0.42

61

1200

0.32

0.28

0.42

61

1200

0.32

0.28

0.44

61

1200

0.32

0.3

0.48

61

1200

0.32

0.28

0.4

61

1200

0.32

0.24

0.42

61

1200

0.32

0.28

0.44

61

1200

0.32

0.26

0.46

61

1200

0.32

0.24

0.42

61

1200

0.32

0.28

0.46

61

1200

0.32

0.3

0.46

61

1200

0.32

0.3

0.44

0.32

0.3

0.48

0.32

0.3

0.48

0.32

0.28

0.44

0.32

0.28

0.48

0.34

0.28

0.48

0.32

0.32

0.48

0.32

0.26

0.44

0.32

0.28

0.44

0.32

0.28

0.44

0.32

0.28

0.46

0.3

0.26

0.42

0.32

0.26

0.42

0.32

0.26

0.42

0.32

0.28

0.44

0.32

0.26

0.42

0.32

0.28

0.48

0.32

0.24

0.44

0.32

0.26

0.46

0.32

0.26

0.44

0.32

0.26

0.44

0.32

0.26

0.44

0.3

0.28

0.44

0.3

0.24

0.42

0.32

0.28

0.44

0.32

0.26

0.44

0.32

0.26

0.44

0.32

0.24

0.42

0.32

0.24

0.44

0.32

0.28

0.46

0.32

0.26

0.42

0.32

0.28

0.48

0.32

0.3

0.44

0.32

0.24

0.42

0.3

0.26

0.46

0.32

0.26

0.42

0.32

0.26

0.42

0.32

0.24

0.44

0.32

0.26

0.44

0.32

0.26

0.42

0.32

0.28

0.48

0.32

0.24

0.44

0.32

0.26

0.44

0.32

0.24

0.44

0.32



Airstrip Count

		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148

		39206		39206		39206		39148		39148

		39230		39230		39230		39167		39167

		39267		39267		39267		39206		39206

		39297		39297		39297		39230		39230

		39349		39349		39349		39267		39267

		39392		39392		39392		39297		39297

		39427		39427		39427		39349		39349

		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713



CER 1

CER 2

CER3

Alert Level

Action Level

Date

Average CER Count

Figure 1.  Average Airstrip Count

3.625

6

29

10

15

5.375

7.5

28

10

15

13.125

13.25

28.75

10

15

13.25

11

27.75

10

15

4.25

5.25

24.5

10

15

4

1.75

11.75

10

15

4.25

9.25

10

15

19.5

5.5

22.5

10

15

5.75

4.25

13

10

15

3.25

1

4.75

10

15

11.625

8

18.25

10

15

3.875

1.75

10.5

10

15

4.125

2

10

35

45

1.125

0.5

3.5

35

45

3

1.25

6.5

35

45

3.25

0.75

5.25

35

45

2

0.75

2.75

35

45

6.375

1.75

8.25

35

45

13.5

1.25

10.25

35

45

2.6666666667

2.6666666667

11.25

35

45

6.2

4

3.75

35

45

6.2666666667

2

3.75

35

45

7.6666666667

3

7.5

35

45

9.4

2.8888888889

9

35

45

8.4

3.4444444444

6.5

35

45

6.5333333333

2.3333333333

8.5

35

45



Contact Plate Count

		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148

		39206		39206		39206		39148		39148

		39230		39230		39230		39167		39167

		39267		39267		39267		39206		39206

		39297		39297		39297		39230		39230

		39349		39349		39349		39267		39267

		39392		39392		39392		39297		39297

		39427		39427		39427		39392		39392

		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

Alert Level

Action Level

Date

Contact Plate Count

Figure 2. Average Contact Plate Count

1.4285714286

0.25

2.5

10

15

3.7142857143

2.75

4

10

15

1.1428571429

1.75

0.8333333333

10

15

2.4285714286

3

2.5

10

15

2.4285714286

0.75

3.1666666667

10

15

5.5714285714

3.25

5

10

15

5.2857142857

5.2

10

15

2.7142857143

1.5

2

10

15

1.1428571429

0

2

10

15

3.1428571429

1

3.25

10

15

3.4285714286

3.25

2.25

10

15

1.5714285714

0.75

1.5

10

15

1.7142857143

1

2.25

6

7

0.5714285714

0.5

2.25

6

7

1.5714285714

0.5

3

6

7

2

0.75

2.5

6

7

0.7142857143

0.25

1.75

6

7

3.4285714286

1.25

3.25

6

7

4

1

3.75

6

7

1.5333333333

1

3

6

7

2

1

2.25

6

7

1.7333333333

0.6666666667

1.5

6

7

0.9333333333

0.4444444444

1.5

6

7

0.9333333333

0.7777777778

2.5

6

7

1.1333333333

0.6666666667

1.75

6

7

0.9333333333

0.6666666667

1.5

6

7



0.5micron Count

		38776		38776		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126		39126		39126

		39148		39167		39167		39148		39148		39148		39148

		39148		39206		39206		39148		39148		39148		39148

		39167		39230		39230		39167		39167		39167		39167

		39206		39267		39267		39206		39206		39206		39206

		39230		39297		39297		39230		39230		39297		39297

		39267		39349		39349		39267		39267		39349		39349

		39297		39392		39392		39297		39297		39392		39392

		39392		39427		39427		39392		39392		39427		39427

		39545		39545		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

CER 1,3 Alert Level

CER 1,3 Action Level

CER 2 Alert Level

CER 2 Action Level

Date

0.5um/cu ft Count

Figure 3.  Average 0.5mm/cu ft Count

194

383

3263.8

5000

10000

5000

10000

339.5

338.3333333333

1210.4

5000

10000

5000

10000

362.75

719.3333333333

2800.4

5000

10000

5000

10000

688.125

416.3333333333

1999.6

5000

10000

5000

10000

618.75

336.6666666667

2033

5000

10000

5000

10000

692.625

1000

1857.4

5000

10000

5000

10000

401.375

1423.2

5000

10000

5000

10000

523.125

842

2313.2

5000

10000

5000

10000

273

292.3333333333

624.4

5000

10000

5000

10000

588.875

620

1580.4

5000

10000

5000

10000

714

474.6666666667

1255.6

5000

10000

5000

10000

755.625

587.3333333333

1139.8

5000

10000

5000

10000

772.875

643

1484

3800

4500

1250

1500

244

896.6666666667

1571.2

3800

4500

1250

1500

551.75

704.3333333333

2714

3800

4500

1250

1500

678.625

553

1781.8

3800

4500

1250

1500

369.625

300

731.6

3800

4500

1250

1500

664

478

1178.6

3800

4500

1250

1500

835.625

525

1260.6

3800

4500

1250

1500

699

83.7777777778

1354.8

3800

4500

1250

1500

635

204.4444444444

620.8

3800

4500

1250

1500

606

181.3333333333

750.8

3800

4500

1250

1500

606

109.5555555556

474.6

3800

4500

1250

1500

612.0666666667

156.7777777778

659.8

3800

4500

1250

1500

285.1333333333

190.5555555556

945.2

3800

4500

1250

1500

474

216.3333333333

768.6

3800

4500

1250

1500



5.0micron Count

		38776		38776		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148		39148		39148

		39206		39206		39206		39148		39148		39148		39148

		39230		39230		39230		39167		39167		39167		39167

		39267		39267		39267		39206		39206		39267		39267

		39297		39297		39297		39230		39230		39297		39297

		39349		39349		39349		39267		39267		39349		39349

		39392		39392		39392		39297		39297		39392		39392

		39427		39427		39427		39392		39392		39427		39427

		39545		39545		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

CER 1,3 Alert Level

CER 1,3 Action Level

CER 2 Alert Level

CER 2 Action Level

Date

5.0um/cu ft Count

Figure 4.  Average 5.0mm/cu ft Count

14.125

48.6666666667

226.8

30

50

30

50

33.625

49.3333333333

104.4

30

50

30

50

36.25

49

211.4

30

50

30

50

126.75

76.6666666667

305.2

30

50

30

50

67.875

37.3333333333

344.6

30

50

30

50

71.75

72.3333333333

166.4

30

50

30

50

43.5

235

30

50

30

50

65.125

37.3333333333

219.4

30

50

30

50

33.125

31.3333333333

50.6

30

50

30

50

47.75

50.6666666667

99.4

30

50

30

50

43.875

32.3333333333

79.2

30

50

30

50

47.125

44.3333333333

92.8

30

50

30

50

49

43.3333333333

92.2

410

500

90

105

30.75

75.6666666667

129.2

410

500

90

105

78.875

89

258.4

410

500

90

105

60

44

147

410

500

90

105

28.375

22.6666666667

53

410

500

90

105

26.125

20.3333333333

58

410

500

90

105

45.125

24.3333333333

80.8

410

500

90

105

37.3333333333

10

69.2

410

500

90

105

34.6

12.5555555556

33.2

410

500

90

105

29

9.3333333333

34

410

500

90

105

29

7.1111111111

33

410

500

90

105

30.0666666667

8.8888888889

27.6

410

500

78

83

18.7333333333

11.5555555556

43.4

410

500

78

83

24.3333333333

9.8888888889

37.6

410

500

78

83



CER 1

				AIRSTRIPS:																																																																																																		CONTACT PLATES:																																																																																																		PARTICLE COUNTS

				A						B						C						D						E						F						G						H						I						J						K						L						M						N						O						Average								A						B						C						D						E						F						G						H						I						J						K						L						M						N						O						Average								A				B				C				D				E				F				G				H				I				J				K				L				M				N				O				Average

		Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 1		Date		Alert Level		Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 1		Date		Alert Level		Action Level		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		CER 1 0.5um/ cu ft		Date		CER 1,3 Alert Level		CER 1,3 Action Level		CER 1 5.0um/cu ft		Date		CER 1,3 Alert Level		CER 1,3 Action Level

		2/28/06		2		0		2		4		0		4		5		0		5		4		0		4		8		0		8		0		0		0		3		0		3		3		0		3																																												4		2/28/06		10		15		0		0		0		0		0		0		1		0		1		0		0		0		2		0		2		0		0		0		3		0		3		4		0		4						0						0						0						0						0						0						0		1		2/28/06		10		15		207		8		291		16		133		12		278		21		134		13		25		5		262		22		222		16																														194		02/28/06		5000		10000		14		2/28/06		30		50

		3/30/06		4		0		4		4		0		4		7		0		7		6		0		6		10		0		10		2		0		2		6		0		6		4		0		4																																												5		3/30/06		10		15		1		0		1		3		0		3		6		0		6		3		0		3		2		0		2		5		0		5		3		0		3		3		0		3						0						0						0						0						0						0						0		4		3/30/06		10		15		310		48		483		69		134		18		263		24		444		31		679		40		199		8		204		31																														340		03/30/06		5000		10000		34		3/30/06		30		50

		4/28/06		4		0		4		12		0		12		12		0		12		15		0		15		17		0		17		6		4		10		12		0		12		23		0		23																																												13		4/28/06		10		15		0		0		0		2		0		2		2		0		2		0		0		0		0		0		0		0		0		0		4		0		4		0		0		0						0						0						0						0						0						0						0		1		4/28/06		10		15		487		81		221		21		261		19		390		32		480		60		287		23		321		19		455		35																														363		04/28/06		5000		10000		36		4/28/06		30		50

		5/30/06		6		0		6		10		0		10		12		0		12		17		0		17		19		0		19		9		0		9		12		0		12		21		0		21																																												13		5/30/06		10		15		1		0		1		4		0		4		3		0		3		0		0		0		1		0		1		0		0		0		7		0		7		1		0		1						0						0						0						0						0						0						0		2		5/30/06		10		15		678		124		1084		137		214		36		113		21		1478		449		220		32		1009		120		709		95																														688		05/30/06		5000		10000		127		5/30/06		30		50

		7/7/06		4		0		4		2		0		2		6		0		6		4		0		4		8		0		8		1		0		1		4		0		4		5		0		5																																												4		7/7/06		10		15		1		0		1		2		0		2		1		0		1		2		0		2		2		0		2		1		0		1		4		0		4		4		0		4						0						0						0						0						0						0						0		2		7/7/06		10		15		631		86		779		72		1234		81		282		38		464		75		694		93		564		65		302		33																														619		07/07/06		5000		10000		68		7/7/06		30		50

		9/5/06		4		0		4		4		0		4		6		0		6		5		0		5		2		0		2		2		0		2		4		0		4		5		0		5																																												4		9/5/06		10		15		4		0		4		6		0		6		4		0		4		3		0		3		6		0		6		5		0		5		5		0		5		6		0		6						0						0						0						0						0						0						0		6		9/5/06		10		15		1056		113		622		73		227		35		828		84		603		57		875		95		545		56		785		61																														693		09/05/06		5000		10000		72		9/5/06		30		50

		10/5/06		5		0		5		4		0		4		4		0		4		5		0		5		6		0		6		4		0		4		3		0		3		3		0		3																																												4		10/5/06		10		15		5		0		5		6		0		6		4		0		4		4		0		4		5		0		5		3		0		3		6		0		6		4		0		4						0						0						0						0						0						0						0		5		10/5/06		10		15		122		14		263		18		352		48		540		69		361		38		421		63		389		41		763		57																														401		10/05/06		5000		10000		44		10/5/06		30		50

		11/14/06		11		0		11		27		0		27		10		0		10		24		0		24		26		0		26		32		0		32		12		0		12		14		0		14																																												20		11/14/06		10		15		1		0		1		1		0		1		0		0		0		0		0		0		5		0		5		1		0		1		2		0		2		9		0		9						0						0						0						0						0						0						0		3		11/14/06		10		15		596		71		455		67		641		77		585		62		991		81		357		52		62		60		498		51																														523		11/14/06		5000		10000		65		11/14/06		30		50

		12/20/06		2		0		2		1		0		1		5		0		5		1		0		1		13		0		13		7		0		7		13		0		13		4		0		4																																												6		12/20/06		10		15		1		0		1		2		0		2		0		0		0		1		0		1		3		0		3		1		0		1		0		0		0		0		0		0						0						0						0						0						0						0						0		1		12/20/06		10		15		367		35		390		46		168		18		321		30		343		32		191		14		90		25		314		65																														273		12/20/06		5000		10000		33		12/20/06		30		50

		1/16/07		3		0		3		2		0		2		4		0		4		6		0		6		2		0		2		2		0		2		3		0		3		4		0		4																																												3		1/16/07		10		15		2		0		2		2		0		2		1		0		1		3		0		3		4		0		4		2		0		2		4		0		4		4		0		4						0						0						0						0						0						0						0		3		1/16/07		10		15		361		21		449		56		304		35		265		31		761		42		804		62		901		64		866		71																														589		01/16/07		5000		10000		48		1/16/07		30		50

		2/13/07		11		0		11		5		0		5		10		0		10		6		0		6		24		0		24		6		0		6		10		0		10		21		0		21																																												12		2/13/07		10		15		1		0		1		8		0		8		3		0		3		2		0		2		0		0		0		4		0		4		2		0		2		4		0		4						0						0						0						0						0						0						0		3		2/13/07		10		15		611		41		862		50		841		42		942		61		744		40		622		33		402		24		688		60																														714		02/13/07		5000		10000		44		2/13/07		30		50

		3/26/07		3		0		3		4		0		4		4		0		4		6		0		6		2		0		2		4		0		4		6		0		6		2		0		2																																												4		3/7/07		10		15		1		0		1		1		0		1		2		0		2		0		0		0		1		0		1		2		0		2		2		0		2		2		0		2						0						0						0						0						0						0						0		2		3/7/07		10		15		721		51		640		42		871		48		901		52		844		48		408		36		799		49		861		51																														756		03/07/07		5000		10000		47		3/7/07		30		50

		5/4/07		4		0		4		4		0		4		3		0		3		4		0		4		6		0		6		2		0		2		6		0		6		4		0		4																																												4		3/7/07		35		45		2		0		2		1		0		1		2		0		2		1		0		1		0		0		0		1		0		1		2		0		2		3		0		3						0						0						0						0						0						0						0		2		3/7/07		6		7		641		41		722		52		699		47		944		61		872		45		698		41		662		37		945		68																														773		03/07/07		3800		4500		49		3/7/07		410		500

		5/28/07		1		0		1		1		0		1		2		0		2		0		0		0		2		0		2		1		0		1		1		0		1		1		0		1																																												1		3/26/07		35		45		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1						0						0						0						0						0						0						0		1		3/26/07		6		7		161		17		200		21		251		36		275		28		320		53		101		15		460		55		184		21																														244		03/26/07		3800		4500		31		3/26/07		410		500

		7/4/07		2		0		2		3		0		3		3		0		3		3		0		3		2		0		2		4		0		4		4		0		4		3		0		3																																												3		5/4/07		35		45		2		0		2		2		0		2		1		0		1		0		0		0		1		0		1		1		0		1		2		0		2		2		0		2						0						0						0						0						0						0						0		2		5/4/07		6		7		346		64		339		37		537		77		301		55		492		86		292		31		896		120		1211		161																														552		05/04/07		3800		4500		79		5/4/07		410		500

		8/3/07		4		0		4		2		0		2		3		0		3		2		0		2		2		0		2		4		0		4		4		0		4		5		0		5																																												3		5/28/07		35		45		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		3		0		3		3		0		3		2		0		2						0						0						0						0						0						0						0		2		5/28/07		6		7		221		20		107		19		647		49		587		37		744		87		907		78		1241		101		975		89																														679		05/28/07		3800		4500		60		5/28/07		410		500

		9/24/07		2		0		2		1		0		1		1		0		1		2		0		2		3		0		3		3		0		3		2		0		2		2		0		2																																												2		7/4/07		35		45		0		0		0		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		2		0		2		2		0		2						0						0						0						0						0						0						0		1		7/4/07		6		7		310		27		488		31		210		20		401		29		121		18		404		31		601		41		422		30																														370		07/04/07		3800		4500		28		7/4/07		410		500

		11/6/07		6		0		6		4		0		4		4		0		4		4		0		4		8		0		8		7		0		7		8		0		8		10		0		10																																												6		8/3/07		35		45		2		0		2		2		0		2		3		0		3		1		0		1		3		0		3		5		0		5		4		0		4		4		0		4						0						0						0						0						0						0						0		3		8/3/07		6		7		523		33		678		25		498		14		671		22		687		23		721		33		856		34		678		25																														664		08/03/07		3800		4500		26		8/3/07		410		500

		12/11/07		10		0		10		9		0		9		11		0		11		12		0		12		12		0		12		15		0		15		21		0		21		18		0		18																																												14		9/24/07		35		45		2		0		2		1		0		1		3		0		3		4		0		4		4		0		4		4		0		4		3		0		3		7		0		7						0						0						0						0						0						0						0		4		11/6/07		6		7		678		36		761		31		734		34		891		44		851		33		781		33		1011		81		978		69																														836		11/06/07		3800		4500		45		11/6/07		410		500

		4/7/08		6		0		6		5		0		5		7		0		7		6		0		6		0		0		0		0		0		0		2		0		2		4		0		4		4		0		4		3		0		3		2		0		2		0		0		0		0		0		0		0		0		0		1		0		1		3		4/7/08		35		45		2		0		2		1		0		1		3		0		3		3		0		3		2		0		2		1		0		1		1		0		1		0		0		0		2		0		2		0		0		0		2		0		2		1		0		1		1		0		1		2		0		2		2		0		2		2		4/7/08		6		7		989		45		1045		58		1349		61		1305		60		689		46		430		30		1027		60		899		42		621		24		318		19		501		24		313		33		295		13		303		21		401		24		699		04/07/08		3800		4500		37		4/7/08		410		500

		5/7/08		9		0		9		8		0		8		7		0		7		8		0		8		3		0		3		3		0		3		3		0		3		7		0		7		7		0		7		4		0		4		8		0		8		4		0		4		8		0		8		9		0		9		5		0		5		6		5/7/08		35		45		3		0		3		2		0		2		2		0		2		2		0		2		3		0		3		3		0		3		2		0		2		1		0		1		1		0		1		1		0		1		2		0		2		2		0		2		2		0		2		2		0		2		2		0		2		2		5/7/08		6		7		782		44		671		39		724		41		454		22		576		33		430		30		671		32		572		28		781		37		671		32		677		33		476		41		672		31		781		43		587		33		635		05/07/08		3800		4500		35		5/7/08		410		500

		6/3/08		8		0		8		8		0		8		4		0		4		5		0		5		6		0		6		6		0		6		5		0		5		5		0		5		5		0		5		4		0		4		7		0		7		8		0		8		8		0		8		9		0		9		6		0		6		6		6/3/08		35		45		3		0		3		1		0		1		1		0		1		2		0		2		1		0		1		3		0		3		1		0		1		2		0		2		2		0		2		0		0		0		2		0		2		1		0		1		2		0		2		2		0		2		3		0		3		2		6/3/08		6		7		621		33		393		22		891		31		671		25		1192		44		671		19		781		22		245		19		1325		44		601		41		418		31		351		29		301		21		290		23		339		31		606		06/03/08		3800		4500		29		6/3/08		410		500

		7/1/08		9		0		9		9		0		9		7		0		7		9		0		9		8		0		8		5		0		5		8		0		8		8		0		8		8		0		8		6		0		6		11		0		11		6		0		6		9		0		9		9		0		9		3		0		3		8		7/1/08		35		45		1		0		1		2		0		2		0		0		0		1		0		1		1		0		1		1		0		1		0		0		0		0		0		0		2		0		2		1		0		1		1		0		1		2		0		2		0		0		0		1		0		1		1		0		1		1		7/1/08		6		7		621		33		393		22		891		31		671		25		1192		44		671		19		781		22		245		19		1325		44		601		41		418		31		351		29		301		21		290		23		339		31		606		07/01/08		3800		4500		29		7/1/08		410		500

		7/21/08		11		0		11		11		0		11		5		0		5		5		0		5		12		0		12		11		0		11		12		0		12		6		0		6		6		0		6		9		0		9		14		0		14		15		0		15		11		0		11		6		0		6		7		0		7		9		7/21/08		35		45		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		7/21/08		6		7		232		23		452		26		337		27		671		33		476		27		501		28		488		28		782		37		561		27		442		28		891		38		590		29		876		31		991		42		891		27		612		07/21/08		3800		4500		30		7/21/08		410		500

		9/4/08		10		0		10		9		0		9		6		0		6		7		0		7		7		0		7		9		0		9		6		0		6		9		0		9		11		0		11		12		0		12		10		0		10		9		0		9		6		0		6		6		0		6		9		0		9		8		9/4/08		35		45		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		9/4/08		6		7		219		19		140		14		275		16		101		9		244		16		301		21		189		19		181		17		176		17		215		21		414		24		409		21		357		21		454		19		602		27		285		09/04/08		3800		4500		19		9/4/08		410		500

		9/22/08		5		0		5		5		0		5		9		0		9		5		0		5		5		0		5		9		0		9		11		0		11		4		0		4		11		0		11		5		0		5		5		0		5		6		0		6		6		0		6		8		0		8		4		0		4		7		9/22/08		35		45		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		0		0		0		2		0		2		1		0		1		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		9/22/08		6		7		332		21		254		19		354		21		548		31		369		22		584		26		651		22		448		26		296		19		489		29		336		21		754		32		565		26		665		29		465		21		474		09/22/08		3800		4500		24		9/22/08		410		500

		11/6/08		3		0		3		3		0		3		5		0		5		4		0		4		4		0		4		3		0		3		4		0		4		4		0		4		4		0		4		5		0		5		5		0		5		3		0		3		3		0		3		3		0		3		4		0		4		4		11/6/08		35		45		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		1		0		1		0		11/6/08		6		7		721		31		867		39		253		12		458		22		357		20		445		28		432		22		685		31		591		28		241		9		219		8		473		19		501		21		765		33		801		36		521		11/06/08		3800		4500		24		11/6/08		410		500

		12/1/08		2		0		2		0		0		0		0		0		0		2		0		2		2		0		2		3		0		3		0		0		0		1		0		1		4		0		4		3		0		3		2		0		2		1		0		1		0		0		0		2		0		2		3		0		3		2		12/1/08		35		45		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		1		12/1/08		6		7		110		9		89		9		122		13		25		6		59		8		131		18		40		7		274		19		157		12		88		6		150		9		114		8		517		32		180		15		234		21		153		12/01/08		3800		4500		13		12/1/08		410		500

		12/16/08		3		0		3		2		0		2		3		0		3		2		0		2		2		0		2		3		0		3		4		0		4		3		0		3		5		0		5		4		0		4		4		0		4		3		0		3		3		0		3		3		0		3		3		0		3		3		12/16/08		35		45		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		1		0		1		1		12/16/08		6		7		291		18		178		11		271		19		189		14		177		14		276		18		198		11		187		14		278		17		91		7		87		6		287		16		376		21		301		17		227		19		228		12/16/08		3800		4500		15		12/16/08		410		500



&L&"Arial Narrow,Bold"&14CER 1&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER 2

										AIRSTRIPS:																																																												CONTACT PLATES:																																																						PARTICLE COUNTS

				A						B						C						D						E						F						G						H						I						Average						A						B						C						D						E						F						G						H						I						Average						A				B				C				D				E				F				G				H				I				Average

		Sample Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 2		Alert Level		Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 2		Total Alert Level		Total Action Level		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		CER 2 0.5um/cu ft		Date		CER 2 Alert Level		CER 2 Action Level		CER 2 5.0um/cu ft		Date		CER 2 Alert Level		CER 2 Action Level

		2/28/06								6		0		6		0		0		0		9		0		9		9		0		9																										6		10		15								0		0		0		0		0		0		1		0		1		0		0		0																										0		10		15		297		39		288		43		0		0		564		64																						383		2/28/06		5000		10000		49		02/28/06		30		50

		3/30/06								9		0		9		1		0		1		8		0		8		12		0		12																										8		10		15								2		0		2		0		0		0		6		0		6		3		0		3																										3		10		15		460		68		264		39		0		0		291		41																						338		3/30/06		5000		10000		49		03/30/06		30		50

		4/28/06								29		0		29		0		0		0		22		0		22		2		0		2																										13		10		15								2		0		2		2		0		2		0		0		0		3		0		3																										2		10		15		1084		67		543		41		0		0		531		39																						719		4/28/06		5000		10000		49		04/28/06		30		50

		5/30/06								21		0		21		0		0		0		19		0		19		4		0		4																										11		10		15								4		0		4		2		0		2		1		0		1		5		0		5																										3		10		15		435		87		354		66		0		0		460		77																						416		5/30/06		5000		10000		77		05/30/06		30		50

		7/7/06								5		0		5		0		0		0		8		0		8		8		0		8																										5		10		15								0		0		0		0		0		0		2		0		2		1		0		1																										1		10		15		232		33		299		39		0		0		479		40																						337		7/7/06		5000		10000		37		07/07/06		30		50

		9/5/06								3		0		3		0		0		0		2		0		2		2		0		2																										2		10		15								4		0		4		0		0		0		4		0		4		5		0		5																										3		10		15		1289		79		289		30		0		0		1422		108																						1000		9/5/06		5000		10000		72		09/05/06		30		50

		10/5/06																																																																																																																																																																10/5/06		5000		10000				10/05/06		30		50

		11/14/06								16		0		16		0		0		0		4		0		4		2		0		2																										6		10		15								1		0		1		0		0		0		4		0		4		1		0		1																										2		10		15		961		41		877		40		0		0		688		31																						842		11/14/06		5000		10000		37		11/14/06		30		50

		12/20/06								5		0		5		4		0		4		6		0		6		2		0		2																										4		10		15								0		0		0		0		0		0		0		0		0		0		0		0																										0		10		15		463		36		141		17		0		0		273		41																						292		12/20/06		5000		10000		31		12/20/06		30		50

		1/16/07								2		0		2		0		0		0		1		0		1		1		0		1																										1		10		15								1		0		1		0		0		0		1		0		1		2		0		2																										1		10		15		781		62		451		32		0		0		628		58																						620		1/16/07		5000		10000		51		01/16/07		30		50

		2/13/07								12		0		12		0		0		0		10		0		10		10		0		10																										8		10		15								4		0		4		0		0		0		4		0		4		4		1		5																										3		10		15		640		31		285		44		0		0		499		22																						475		2/13/07		5000		10000		32		02/13/07		30		50

		3/26/07								2		0		2		0		0		0		2		0		2		3		0		3																										2		35		45								1		0		1		0		0		0		1		0		1		1		0		1																										1		6		7		490		40		684		51		0		0		588		42																						587		3/7/07		5000		10000		44		03/07/07		30		50

		5/4/07								2		0		2		0		0		0		3		0		3		3		0		3																										2		35		45								1		0		1		0		0		0		1		0		1		2		0		2																										1		6		7		640		41		585		37		0		0		704		52																						643		3/7/07		1250		1500		43		03/07/07		90		105

		5/28/07								0		0		0		0		0		0		1		0		1		1		0		1																										1		35		45								1		0		1		0		0		0		0		0		0		1		0		1																										1		6		7		1104		101		944		81		0		0		642		45																						897		3/26/07		1250		1500		76		03/26/07		90		105

		7/4/07								1		0		1		0		0		0		2		0		2		2		0		2																										1		35		45								0		0		0		0		0		0		1		0		1		1		0		1																										1		6		7		10		0		962		123		0		0		1141		132																						704		5/4/07		1250		1500		89		07/04/07		90		105

		8/3/07								0		0		0		0		0		0		1		0		1		2		0		2																										1		35		45								1		0		1		0		0		0		1		0		1		1		0		1																										1		6		7		0		0		784		61		0		0		875		71																						553		8/3/07		1250		1500		44		08/03/07		90		105

		9/24/07								1		0		1		0		0		0		1		0		1		1		0		1																										1		35		45								0		0		0		0		0		0		0		0		0		1		0		1																										0		6		7		0		0		199		19		0		0		701		49																						300		9/24/07		1250		1500		23		09/24/07		90		105

		11/6/07								1		0		1		0		0		0		3		0		3		3		0		3																										2		35		45								1		0		1		0		0		0		2		0		2		2		0		2																										1		6		7		4		0		563		22		0		0		867		39																						478		11/6/07		1250		1500		20		11/06/07		90		105

		12/11/07								0		0		0		0		0		0		2		0		2		3		0		3																										1		35		45								0		0		0		0		0		0		3		0		3		1		0		1																										1		6		7		2		0		672		36		0		0		901		37																						525		12/11/07		1250		1500		24		12/11/07		90		105

		4/7/08		0		0		0		4		0		4		7		0		7		0		0		0		4		0		4		0		0		0		6		0		6		3		0		3		0		0		0		3		35		45		0		0		0		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		2		0		2		2		0		2		0		0		0		1		6		7		0		0		162		23		208		25		0		0		93		19		0		0		90		6		201		17		0		0		84		4/7/08		1250		1500		10		04/07/08		90		105

		5/7/08		0		0		0		3		0		3		9		0		9		0		0		0		8		0		8		0		0		0		8		0		8		8		0		8		0		0		0		4		35		45		0		0		0		2		0		2		3		0		3		0		0		0		2		0		2		0		0		0		1		0		1		1		0		1		0		0		0		1		6		7		0		0		401		24		489		25		0		0		281		22		0		0		187		18		482		24		0		0		204		5/7/08		1250		1500		13		05/07/08		90		105

		6/3/08		0		0		0		3		0		3		3		0		3		0		0		0		5		0		5		0		0		0		5		0		5		2		0		2		0		0		0		2		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		0		1		0		0		0		1		6		7		0		0		267		10		498		22		0		0		268		22		0		0		301		19		298		11		0		0		181		6/3/08		1250		1500		9		06/03/08		90		105

		7/1/08		0		0		0		8		0		8		0		0		0		8		0		8		6		0		6		0		0		0		3		0		3		2		0		2		0		0		0		3		35		45		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		0		6		7		0		0		403		22		0		0		153		11		287		19		1		0		21		1		121		11		0		0		110		7/1/08		1250		1500		7		07/01/08		90		105

		7/21/08		0		0		0		6		0		6		0		0		0		7		0		7		7		0		7		0		0		0		4		0		4		2		0		2		0		0		0		3		35		45		0		0		0		2		0		2		0		0		0		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		0		0		0		1		6		7		0		0		376		19		0		0		298		17		337		21		0		0		109		8		291		15		0		0		157		7/21/08		1250		1500		9		07/21/08		78		83

		9/4/08		0		0		0		7		0		7		9		0		9		0		0		0		4		0		4		0		0		0		4		0		4		4		0		4		3		0		3		3		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		6		7		0		0		210		19		175		11		0		0		361		18		0		0		101		7		162		9		706		40		191		9/4/08		1250		1500		12		09/04/08		78		83

		9/22/08		0		0		0		5		0		5		4		0		4		0		0		0		4		0		4		0		0		0		2		0		2		4		0		4		2		0		2		2		35		45		0		0		0		2		0		2		0		0		0		0		0		0		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		1		6		7		0		0		332		21		296		15		0		0		194		9		0		0		265		11		295		11		565		22		216		9/22/08		1250		1500		10		09/22/08		78		83

		11/6/08		0		0		0		2		0		2		3		0		3		0		0		0		2		0		2		0		0		0		3		0		3		3		0		3		2		0		2		2		35		45		0		0		0		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		6		7		0		0		776		22		409		19		0		0		292		8		0		0		301		16		228		11		220		9		247		11/6/08		1250		1500		9		11/06/08		78		83

		12/1/08		0		0		0		3		0		3		2		0		2		0		0		0		3		0		3		0		0		0		2		0		2		0		0		0		1		0		1		1		35		45		0		0		0		1		0		1		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		6		7		0		0		290		12		203		11		0		0		221		12		0		0		313		21		19		3		148		10		133		12/1/08		1250		1500		8		12/01/08		78		83

		12/16/08		0		0		0		4		0		4		3		0		3		0		0		0		3		0		3		0		0		0		3		0		3		0		0		0		1		0		1		2		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		6		7		0		0		199		9		289		16		0		0		167		7		0		0		267		17		89		6		177		11		132		12/16/08		1250		1500		7		12/16/08		78		83



&L&"Arial Narrow,Bold"&14CER 2&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER 3

				AIRSTRIPS:																														CONTACT PLATES:																																				PARTICLE COUNTS

				A						B						D						E						Average						A						B						C						D						E						Average						A				B				C				D				E				Average

		Sample Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER3		Total Alert Level		Total Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 3		Total Alert Level		Total Action Level		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		CER 3 0.5um/cu ft		0.5um/cu ft Alert Level		0.5um/cu ft Action Level		CER 3 5.0um/cu ft		5.0um/cu ft Alert Level		5.0um/cu ft Action Level

		2/28/06		29		1		30		21		0		21		28		0		28		37		0		37		29		10		15		3		0		3		3		0		3		3		0		3		2		0		2		4		0		4		3		10		15		4411		344		3943		271		3664		229		3068		212		1233		78		3264		5000		10000		227		30		50

		3/30/06		32		1		33		26		0		26		21		0		21		32		0		32		28		10		15		5		0		5		4		0		4		6		0		6		4		0		4		5		0		5		4		10		15		1261		119		979		81		1461		101		1721		120		630		101		1210		5000		10000		104		30		50

		4/28/06		29		2		31		32		0		32		23		0		23		29		0		29		29		10		15		2		0		2		3		0		3		0		0		0		0		0		0		0		0		0		1		10		15		4536		307		3293		245		2424		222		2637		211		1112		72		2800		5000		10000		211		30		50

		5/30/06		31		0		31		29		0		29		21		1		22		29		0		29		28		10		15		4		0		4		5		0		5		2		0		2		1		0		1		3		0		3		3		10		15		1914		327		2122		327		2561		413		1572		207		1829		252		2000		5000		10000		305		30		50

		7/7/06		26		0		26		19		0		19		22		0		22		31		0		31		25		10		15		4		0		4		5		0		5		3		0		3		2		0		2		5		0		5		3		10		15		2150		382		2668		423		2561		401		2022		399		764		118		2033		5000		10000		345		30		50

		9/5/06		10		0		10		12		0		12		11		0		11		14		0		14		12		10		15		6		0		6		4		0		4		4		0		4		6		0		6		5		0		5		5		10		15		2286		180		2142		171		1829		162		1749		171		1281		148		1857		5000		10000		166		30		50

		10/5/06		9		0		9		10		0		10		10		0		10		8		0		8		9		10		15		7		0		7		5		0		5		6		0		6		4		0		4		4		0		4		5		10		15		1679		346		793		137		1841		241		1429		248		1374		203		1423		5000		10000		235		30		50

		11/14/06		19		2		21		26		0		26		26		0		26		17		0		17		23		10		15		2		0		2		1		0		1		0		0		0		1		0		1		6		0		6		2		10		15		2241		243		2301		231		1974		198		2475		224		2575		201		2313		5000		10000		219		30		50

		12/20/06		10		0		10		13		0		13		13		0		13		16		0		16		13		10		15		5		0		5		1		0		1		0		0		0		3		0		3		1		0		1		2		10		15		406		33		727		46		923		94		604		41		462		39		624		5000		10000		51		30		50

		1/16/07		4		0		4		5		0		5		7		0		7		3		0		3		5		10		15		3		0		3		2		0		2		3		0		3		4		0		4		4		0		4		3		10		15		485		41		1785		101		1986		128		1785		109		1861		118		1580		5000		10000		99		30		50

		2/13/07		12		0		12		22		0		22		18		0		18		21		0		21		18		10		15		2		0		2		4		0		4		2		0		2		1		0		1		2		0		2		2		10		15		1261		87		1641		98		901		62		988		61		1487		88		1256		5000		10000		79		30		50

		3/26/07		11		0		11		12		0		12		10		0		10		9		0		9		11		35		45		2		0		2		1		0		1		2		0		2		1		0		1		2		0		2		2		6		7		1421		109		1221		101		866		71		949		82		1242		101		1140		3800		4500		93		410		500

		5/4/07		10		0		10		10		0		10		9		0		9		11		0		11		10		35		45		2		0		2		3		0		3		1		0		1		2		0		2		2		0		2		2		6		7		1741		110		1444		91		1235		81		1479		87		1521		92		1484		3800		4500		92		410		500

		5/28/07		6		0		6		4		0		4		2		0		2		2		0		2		4		35		45		4		0		4		2		0		2		1		0		1		1		0		1		2		0		2		2		6		7		1421		102		1387		100		1842		169		1785		154		1421		121		1571		3800		4500		129		410		500

		7/4/07		7		0		7		6		0		6		6		0		6		7		0		7		7		35		45		4		0		4		3		0		3		2		0		2		1		0		1		4		0		4		3		6		7		3950		375		2745		292		1658		177		2431		201		2786		247		2714		3800		4500		258		410		500

		8/3/07		6		0		6		6		0		6		4		0		4		5		0		5		5		35		45		3		0		3		3		0		3		2		0		2		2		0		2		2		0		2		3		6		7		1672		145		1897		152		1866		149		1987		151		1487		138		1782		3800		4500		147		410		500

		9/24/07		4		0		4		3		0		3		2		0		2		2		0		2		3		35		45		2		0		2		2		0		2		2		0		2		1		0		1		2		0		2		2		6		7		781		61		1011		72		689		49		768		52		409		31		732		3800		4500		53		410		500

		11/6/07		7		0		7		9		0		9		8		0		8		9		0		9		8		35		45		3		0		3		3		0		3		5		0		5		1		0		1		6		0		6		3		6		7		1276		78		1454		65		1109		55		987		45		1067		47		1179		3800		4500		58		410		500

		12/11/07		9		0		9		12		0		12		9		0		9		11		0		11		10		35		45		2		0		2		4		0		4		4		0		4		5		0		5		4		0		4		4		6		7		1853		101		1321		99		901		45		1241		87		987		72		1261		3800		4500		81		410		500

		4/7/08		8		0		8		15		0		15		12		0		12		10		0		10		11		35		45		2		0		2		3		0		3		2		0		2		3		0		3		4		0		4		3		6		7		1047		69		1642		79		1421		67		1677		71		987		60		1355		3800		4500		69		410		500

		5/7/08		3		0		3		4		0		4		4		0		4		4		0		4		4		35		45		4		0		4		3		0		3		4		0		4		1		0		1		1		0		1		2		6		7		561		31		761		44		660		39		451		21		671		31		621		3800		4500		33		410		500

		6/3/08		3		0		3		4		0		4		4		0		4		4		0		4		4		35		45		2		0		2		2		0		2		2		0		2		1		0		1		1		0		1		2		6		7		409		26		391		33		782		34		891		33		1281		44		751		3800		4500		34		410		500

		7/1/08		7		0		7		7		0		7		8		0		8		8		0		8		8		35		45		2		0		2		2		0		2		1		0		1		1		0		1		1		0		1		2		6		7		1121		81		677		42		339		22		125		11		111		9		475		3800		4500		33		410		500

		7/21/08		9		0		9		8		0		8		8		0		8		11		0		11		9		35		45		3		0		3		3		0		3		2		0		2		2		0		2		2		0		2		3		6		7		891		41		781		33		789		31		499		21		339		12		660		3800		4500		28		410		500

		9/4/08		6		0		6		9		0		9		4		0		4		7		0		7		7		35		45		2		0		2		2		0		2		1		0		1		2		0		2		1		0		1		2		6		7		793		37		1044		44		977		39		1011		57		901		40		945		3800		4500		43		410		500

		9/22/08		9		0		9		9		0		9		9		0		9		7		0		7		9		35		45		1		0		1		2		0		2		2		0		2		2		0		2		1		0		1		2		6		7		984		44		564		31		965		33		698		41		632		39		769		3800		4500		38		410		500

		11/6/08		6		0		6		6		0		6		4		0		4		3		0		3		5		35		45		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		1		6		7		1198		81		901		67		789		43		761		41		904		61		911		3800		4500		59		410		500

		12/1/08		7		0		7		7		0		7		6		0		6		7		0		7		7		35		45		2		0		2		1		0		1		2		0		2		1		0		1		1		0		1		1		6		7		1198		81		901		67		789		43		761		41		904		61		911		3800		4500		59		410		500

		12/16/08		8		0		8		8		0		8		6		0		6		9		0		9		8		35		45		1		0		1		2		0		2		1		0		1		1		0		1		1		0		1		1		6		7		892		41		1098		69		892		34		901		44		1167		72		990		3800		4500		52		410		500



&L&"Arial Narrow,Bold"&14CER 3&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER Pressure

		Daily				Monthly				Daily				Monthly				Daily																		Monthly																		Daily								Monthly								Specs

		Date		CER1		Month		CER1		Date		CER Change Room		Month		CER Change Room		Date		CER2		Temp (F)		Relative Humidity (%)		R&D Bio-Safety Cabinet North (left axis)		R&D Bio-Safety Cabinet South (left axis)		Mfg Bio-Safety Cabinet North (left axis)		Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)		Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)		Month		CER 2		Temp (F)		Relative Humidity (%)		R&D Bio-Safety Cabinet North (left axis)		R&D Bio-Safety Cabinet South (left axis)		Mfg Bio-Safety Cabinet North (left axis)		Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)		Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)		Date		CER3		Temp (ºF)		Humidity (%RH)		Month		CER 3		Temp (ºF)		Humidity (%RH)		Date		CER Alert Level		CER Action Level		Bio-Safety Cabinet Alert Level (left axis)		Bio-Safety Cabinet Action  Level (left axis)		Mfg Bio-Safety Cabinet South Alert Level (right axis)		Mfg Bio-Safety Cabinet South Alarm Level (right axis)

		4/24/06		0.05		April-06		0.045		3/31/06		0.05		March-06		0.055		3/31/06		0.09																March-06		0.090																6/19/06		0.05						June-06		0.051						4/30/06		0.05		0.03

		4/24/06		0.05		May-06		0.022		3/31/06		0.06		April-06		0.053		3/31/06		0.09																April-06		0.089																6/19/06		0.06						July-06		0.061						5/31/06		0.05		0.03

		4/25/06		0.05		June-06		0.013		4/4/06		0.05		May-06		0.050		4/4/06		0.09																July-06		0.076																6/28/06		0.03						August-06		0.055						6/30/06		0.05		0.03

		4/25/06		0.04		July-06		0.041		4/4/06		0.05		June-06		0.046		4/4/06		0.09																August-06		0.068																6/28/06		0.06						September-06		0.052						7/31/06		0.05		0.03

		4/26/06		0.06		August-06		0.033		4/5/06		0.05		July-06		0.048		4/5/06		0.09																September-06		0.062																6/29/06		0.03						October-06		0.051						8/31/06		0.05		0.03

		4/26/06		0.04		September-06		0.027		4/5/06		0.06		August-06		0.050		4/5/06		0.09																October-06		0.034																6/29/06		0.06						November-06		0.053						9/30/06		0.05		0.03

		4/27/06		0.04		October-06		0.033		4/6/06		0.05		September-06		0.048		4/6/06		0.09																November-06		0.020																6/30/06		0.06						December-06		0.051						10/31/06		0.05		0.03

		4/27/06		0.045		November-06		0.028		4/6/06		0.06		October-06		0.053		4/6/06		0.09																December-06		0.012																6/30/06		0.06						February-07		0.040						11/30/06		0.05		0.03

		4/28/06		0.05		December-06		0.030		4/7/06		0.055		November-06		0.035		4/7/06		0.09																January-07		0.011																7/5/06		0.03						March-07		0.037						12/31/06		0.05		0.03

		4/28/06		0.04		January-07		0.030		4/7/06		0.05		December-06		0.031		4/7/06		0.09																February-07		0.013																7/5/06		0.03						April-07		0.038						1/31/07		0.05		0.03

		4/29/06		0.035		February-07		0.038		4/10/06		0.055		January-07		0.031		4/10/06		0.095																March-07		0.031																7/6/06		0.06						May-07		0.038						1/28/07		0.05		0.03

		4/29/06		0.035		March-07		0.037		4/10/06		0.055		February-07		0.035		4/10/06		0.09																April-07		0.033																7/6/06		0.06						June-07		0.040						3/7/07		0.05		0.03

		5/1/06		0.025		April-07		0.031		4/11/06		0.055		March-07		0.036		4/11/06		0.095																May-07		0.044																7/7/06		0.06						July-07		0.057						3/7/07		0.03		0.005

		5/1/06		0.03		May-07		0.027		4/11/06		0.055		April-07		0.035		4/11/06		0.095																June-07		0.048																7/7/06		0.06						August-07		0.053						4/30/07		0.03		0.005

		5/2/06		0.025		June-07		0.027		4/12/06		0.055		May-07		0.032		4/12/06		0.09																July-07		0.050																7/10/06		0.06						September-07		0.050						5/16/07		0.03		0.005

		5/2/06		0.03		July-07		0.035		4/12/06		0.055		June-07		0.028		4/12/06		0.09																August-07		0.042																7/10/06		0.06						October-07		0.049						5/16/07		0.015		0.005

		5/3/06		0.015		August-07		0.032		4/13/06		0.055		July-07		0.030		4/13/06		0.09																September-07		0.046						0.610		0.408								7/11/06		0.06						November-07		0.047						5/31/07		0.015		0.005

		5/4/06		0.03		September-07		0.030		4/13/06		0.055		August-07		0.032		4/13/06		0.095																October-07		0.041						0.620		0.420								7/11/06		0.06						December-07		0.043						6/30/07		0.015		0.005

		5/5/06		0.03		October-07		0.030		4/17/06		0.06		September-07		0.029		4/17/06		0.095																November-07		0.035						0.632		0.424								7/12/06		0.06						January-08		0.040						7/31/07		0.015		0.005

		5/5/06		0.03		November-07		0.065		4/17/06		0.055		October-07		0.027		4/17/06		0.09																December-07		0.030						0.643		0.426								7/12/06		0.06						February-08		0.040						8/31/07		0.015		0.005

		5/6/06		0.03		December-07		0.077		4/18/06		0.055		November-07		0.044		4/18/06		0.095																January-08																		7/13/06		0.06						March-08		0.040						9/5/07		0.015		0.005		0.25		0.1

		5/6/06		0.025		January-08		0.088		4/18/06		0.06		December-07		0.043		4/18/06		0.09																February-08		0.049		69.778		46.100		0.281		0.309		0.428		62.091		1180.364		7/13/06		0.06						April-08		0.048		70.864		42.636		9/30/07		0.015		0.005		0.25		0.1

		5/7/06		0.03		February-08		0.035		4/19/06		0.045		January-08		0.032		4/19/06		0.085																March-08		0.063		70.000		39.750		0.272		0.318		0.441		63.000		1193.000		7/14/06		0.06						May-08		0.040		72.696		37.435		10/31/07		0.015		0.005		0.25		0.1

		5/8/06		0.03		March-08		0.041		4/19/06		0.05		February-08		0.035		4/19/06		0.09																April-08		0.053		71.045		41.000		0.276		0.320		0.454		62.333		1196.333		7/14/06		0.06						June-08		0.025		72.136		33.909		11/30/07		0.015		0.005		0.25		0.1

		5/8/06		0.03		April-08		0.043		4/20/06		0.055		March-08		0.039		4/20/06		0.079																May-08		0.043		72.304		35.913		0.282		0.320		0.449		60.652		1194.957		7/17/06		0.06						July-08		0.059		71.920		39.400		12/31/07		0.015		0.005		0.25		0.1

		5/9/06		0.025		May-08		0.041		4/20/06		0.05		April-08		0.040		4/20/06		0.08																June-08		0.043		71.826		33.522		0.288		0.318		0.447		57.913		790.783		7/17/06		0.06						August-08		0.057		71.600		40.040		1/31/08		0.015		0.005		0.25		0.1

		5/9/06		0.025		June-08		0.039		4/24/06		0.06		May-08		0.040		4/21/06		0.085																July-08		0.077		71.800		38.360		0.285		0.320		0.447		59.789		882.526		7/18/06		0.06						September-08		0.059		71.240		38.000		2/29/08		0.015		0.005		0.25		0.1

		5/10/06		0.025		July-08		0.027		4/24/06		0.06		June-08		0.037		4/21/06		0.085																August-08		0.061		71.440		38.480		0.272		0.318		0.448		0.000		0.000		7/18/06		0.06														3/31/08		0.015		0.005		0.25		0.1

		5/10/06		0.025		August-08		0.031		4/25/06		0.06		July-08		0.040		4/25/06		0.086																September-08		0.059		70.640		38.280		0.259		0.319		0.439		0.000		0.000		7/19/06		0.06														4/30/08		0.015		0.005		0.25		0.1

		5/11/06		0.015		September-08		0.030		4/25/06		0.06		August-08		0.041		4/25/06		0.085																																		7/19/06		0.06														5/31/08		0.015		0.005		0.25		0.1

		5/11/06		0.025						4/26/06		0.05		September-08		0.041		4/26/06		0.085																																		7/20/06		0.07														6/30/08		0.015		0.005		0.25		0.1

		5/12/06		0.025						4/26/06		0.02						4/26/06		0.087																																		7/20/06		0.07														7/31/08		0.015		0.005		0.2		0.15

		5/12/06		0.02						4/27/06		0.06						4/27/06		0.085																																		7/21/06		0.07														8/30/08		0.015		0.005		0.2		0.15

		5/15/06		0.02						4/27/06		0.055						4/27/06		0.085																																		7/21/06		0.07														9/30/08		0.015		0.005		0.2		0.15

		5/15/06		0.025						4/28/06		0.04						4/28/06		0.09																																		7/22/06		0.07

		5/16/06		0.01						4/28/06		0.055						4/28/06		0.08																																		7/22/06		0.07

		5/16/06		0.01						4/29/06		0.05						7/25/06		0.085																																		7/24/06		0.07

		5/17/06		0.01						4/29/06		0.05						7/25/06		0.085																																		7/24/06		0.07

		5/17/06		0.025						5/1/06		0.05						7/26/06		0.085																																		7/25/06		0.06

		5/18/06		0.02						5/1/06		0.055						7/26/06		0.075																																		7/25/06		0.06

		5/18/06		0.02						5/2/06		0.05						7/27/06		0.08																																		7/26/06		0.06

		5/19/06		0.03						5/2/06		0.055						7/27/06		0.08																																		7/26/06		0.06

		5/19/06		0.02						5/3/06		0.05						7/28/06		0.075																																		7/27/06		0.06

		5/20/06		0.01						5/4/06		0.045						7/28/06		0.079																																		7/27/06		0.06

		5/20/06		0.02						5/5/06		0.055						7/29/06		0.069																																		8/1/06		0.06

		5/22/06		0.015						5/5/06		0.05						7/29/06		0.07																																		8/1/06		0.06

		5/22/06		0.015						5/6/06		0.065						7/30/06		0.069																																		8/2/06		0.06

		5/23/06		0.015						5/6/06		0.055						7/30/06		0.069																																		8/2/06		0.06

		5/23/06		0.015						5/7/06		0.05						7/31/06		0.075																																		8/3/06		0.06

		5/24/06		0.015						5/8/06		0.05						7/31/06		0.073																																		8/3/06		0.06

		5/24/06		0.015						5/8/06		0.05						8/1/06		0.07																																		8/4/06		0.06

		5/25/06		0.015						5/9/06		0.05						8/1/06		0.075																																		8/4/06		0.06

		5/25/06		0.03						5/9/06		0.055						8/2/06		0.07																																		8/7/06		0.055

		5/30/06		0.015						5/10/06		0.045						8/2/06		0.07																																		8/7/06		0.06

		5/30/06		0.02						5/10/06		0.04						8/3/06		0.07																																		8/8/06		0.06

		6/1/06		0.01						5/11/06		0.045						8/3/06		0.074																																		8/8/06		0.06

		6/1/06		0.01						5/11/06		0.055						8/4/06		0.074																																		8/9/06		0.06

		6/2/06		0.015						5/12/06		0.05						8/4/06		0.074																																		8/9/06		0.06

		6/5/06		0.01						5/12/06		0.06						8/7/06		0.073																																		8/10/06		0.055

		6/5/06		0.013						5/15/06		0.045						8/7/06		0.073																																		8/10/06		0.055

		6/6/06		0.01						5/15/06		0.055						8/8/06		0.073																																		8/11/06		0.055

		6/6/06		0.01						5/16/06		0.05						8/8/06		0.073																																		8/11/06		0.055

		6/7/06		0.01						5/16/06		0.055						8/10/06		0.074																																		8/14/06		0.055

		6/7/06		0.01						5/17/06		0.04						8/10/06		0.071																																		8/14/06		0.055

		6/8/06		0.01						5/17/06		0.045						8/14/06		0.07																																		8/15/06		0.055

		6/8/06		0.01						5/18/06		0.05						8/15/06		0.069																																		8/15/06		0.055

		6/9/06		0.01						5/18/06		0.055						8/16/06		0.069																																		8/16/06		0.055

		6/9/06		0.01						5/19/06		0.04						8/16/06		0.07																																		8/16/06		0.055

		6/12/06		0.03						5/19/06		0.045						8/17/06		0.069																																		8/17/06		0.055

		6/12/06		0.01						5/20/06		0.04						8/17/06		0.069																																		8/17/06		0.06

		6/13/06		0.03						5/20/06		0.043						8/18/06		0.07																																		8/18/06		0.05

		6/13/06		0.01						5/22/06		0.05						8/18/06		0.068																																		8/18/06		0.065

		6/16/06		0.01						5/22/06		0.05						8/21/06		0.065																																		8/19/06		0.05

		6/16/06		0.01						5/23/06		0.05						8/22/06		0.06																																		8/19/06		0.055

		7/6/06		0.05						5/23/06		0.05						8/22/06		0.065																																		8/21/06		0.055

		7/6/06		0.04						5/24/06		0.045						8/23/06		0.065																																		8/21/06		0.05

		7/7/06		0.04						5/24/06		0.05						8/23/06		0.068																																		8/22/06		0.05

		7/8/06		0.04						5/25/06		0.05						8/24/06		0.065																																		8/22/06		0.056

		7/10/06		0.05						5/25/06		0.05						8/24/06		0.055																																		8/23/06		0.055

		7/11/06		0.04						5/30/06		0.045						8/25/06		0.065																																		8/23/06		0.055

		7/12/06		0.05						5/30/06		0.05						8/25/06		0.065																																		8/24/06		0.05

		7/13/06		0.05						6/1/06		0.045						8/28/06		0.065																																		8/24/06		0.05

		7/17/06		0.06						6/1/06		0.05						8/28/06		0.065																																		8/25/06		0.05

		7/18/06		0.04						6/2/06		0.04						8/30/06		0.065																																		8/25/06		0.055

		7/19/06		0.04						6/5/06		0.05						8/30/06		0.063																																		8/26/06		0.05

		7/20/06		0.04						6/5/06		0.055						8/31/06		0.065																																		8/26/06		0.05

		7/21/06		0.033						6/6/06		0.055						8/31/06		0.065																																		8/28/06		0.05

		7/22/06		0.04						6/6/06		0.05						9/1/06		0.06																																		8/28/06		0.05

		7/23/06		0.04						6/7/06		0.055						9/1/06		0.065																																		8/29/06		0.05

		7/24/06		0.04						6/7/06		0.05						9/5/06		0.065																																		8/29/06		0.05

		7/25/06		0.04						6/8/06		0.05						9/5/06		0.065																																		8/30/06		0.05

		7/26/06		0.035						6/8/06		0.05						9/6/06		0.055																																		8/30/06		0.05

		7/26/06		0.04						6/9/06		0.045						9/6/06		0.065																																		8/31/06		0.05

		7/27/06		0.03						6/9/06		0.05						9/7/06		0.055																																		8/31/06		0.05

		7/27/06		0.04						6/12/06		0.01						9/7/06		0.063																																		9/1/06		0.055

		7/28/06		0.04						6/12/06		0.05						9/8/06		0.06																																		9/6/06		0.05

		7/31/06		0.03						6/13/06		0.01						9/8/06		0.063																																		9/6/06		0.05

		8/1/06		0.035						6/13/06		0.05						9/11/06		0.06																																		9/7/06		0.05

		8/2/06		0.03						6/14/06		0.05						9/11/06		0.065																																		9/7/06		0.05

		8/3/06		0.03						6/14/06		0.055						9/12/06		0.06																																		9/8/06		0.05

		8/4/06		0.03						6/15/06		0.055						9/12/06		0.065																																		9/8/06		0.05

		8/7/06		0.03						6/15/06		0.06						9/13/06		0.06																																		9/11/06		0.05

		8/8/06		0.03						6/16/06		0.05						9/13/06		0.065																																		9/11/06		0.05

		8/10/06		0.03						6/16/06		0.04						9/14/06		0.06																																		9/12/06		0.05

		8/10/06		0.05						6/17/06		0.045						9/14/06		0.065																																		9/12/06		0.06

		8/11/06		0.03						6/17/06		0.05						9/15/06		0.06																																		9/13/06		0.05

		8/11/06		0.05						6/19/06		0.05						9/15/06		0.065																																		9/13/06		0.055

		8/14/06		0.03						6/19/06		0.05						9/18/06		0.06																																		9/14/06		0.05

		8/15/06		0.03						6/20/06		0.05						9/18/06		0.063																																		9/14/06		0.04

		8/16/06		0.05						6/20/06		0.05						9/19/06		0.065																																		9/15/06		0.05

		8/16/06		0.03						6/21/06		0.04						9/19/06		0.055																																		9/15/06		0.05

		8/17/06		0.035						6/21/06		0.05						9/20/06		0.065																																		9/18/06		0.055

		8/17/06		0.03						6/22/06		0.04						9/20/06		0.06																																		9/18/06		0.06

		8/18/06		0.03						6/22/06		0.045						9/21/06		0.065																																		9/19/06		0.05

		8/18/06		0.03						6/26/06		0.04						9/21/06		0.062																																		9/19/06		0.055

		8/19/06		0.035						6/27/06		0.04						9/23/06		0.065																																		9/20/06		0.05

		8/19/06		0.03						6/28/06		0.04						9/23/06		0.062																																		9/20/06		0.05

		8/20/06		0.035						6/29/06		0.04						9/25/06		0.059																																		9/21/06		0.055

		8/21/06		0.03						7/5/06		0.04						9/25/06		0.06																																		9/21/06		0.055

		8/21/06		0.03						7/6/06		0.04						10/2/06		0.06																																		9/22/06		0.05

		8/22/06		0.025						7/7/06		0.05						10/2/06		0.05																																		9/22/06		0.055

		8/22/06		0.035						7/8/06		0.05						10/3/06		0.048																																		9/23/06		0.06

		8/23/06		0.035						7/10/06		0.03						10/3/06		0.042																																		9/23/06		0.06

		8/23/06		0.035						7/11/06		0.05						10/4/06		0.048																																		9/25/06		0.05

		8/24/06		0.035						7/12/06		0.04						10/6/06		0.038																																		9/25/06		0.055

		8/24/06		0.035						7/13/06		0.0425						10/9/06		0.055																																		9/26/06		0.05

		8/25/06		0.035						7/17/06		0.04						10/9/06		0.036																																		9/26/06		0.05

		8/25/06		0.035						7/18/06		0.05						10/10/06		0.037																																		9/27/06		0.05

		8/26/06		0.03						7/19/06		0.05						10/10/06		0.032																																		9/27/06		0.05

		8/26/06		0.035						7/20/06		0.05						10/11/06		0.032																																		9/28/06		0.05

		8/28/06		0.03						7/21/06		0.055						10/11/06		0.032																																		9/28/06		0.05

		8/28/06		0.03						7/22/06		0.055						10/12/06		0.033																																		9/29/06		0.05

		8/29/06		0.03						7/23/06		0.055						10/12/06		0.03																																		9/29/06		0.05

		8/29/06		0.03						7/24/06		0.055						10/13/06		0.031																																		10/2/06		0.055

		8/30/06		0.03						7/25/06		0.05						10/13/06		0.03																																		10/2/06		0.06

		8/30/06		0.035						7/26/06		0.055						10/16/06		0.033																																		10/3/06		0.05

		8/31/06		0.03						7/26/06		0.05						10/16/06		0.032																																		10/3/06		0.05

		8/31/06		0.03						7/27/06		0.05						10/17/06		0.032																																		10/4/06		0.055

		9/1/06		0.03						7/27/06		0.05						10/17/06		0.03																																		10/4/06		0.05

		9/5/06		0.03						7/28/06		0.05						10/18/06		0.033																																		10/5/06		0.05

		9/5/06		0.03						7/31/06		0.05						10/18/06		0.03																																		10/5/06		0.05

		9/6/06		0.02						8/1/06		0.05						10/19/06		0.025																																		10/9/06		0.05

		9/7/06		0.02						8/2/06		0.05						10/19/06		0.03																																		10/9/06		0.05

		9/8/06		0.03						8/3/06		0.05						10/20/06		0.03																																		10/10/06		0.05

		9/11/06		0.03						8/4/06		0.05						10/20/06		0.035																																		10/10/06		0.05

		9/11/06		0.03						8/7/06		0.05						10/23/06		0.032																																		10/11/06		0.05

		9/12/06		0.03						8/8/06		0.05						10/23/06		0.026																																		10/11/06		0.05

		9/12/06		0.03						8/11/06		0.03						10/24/06		0.029																																		10/12/06		0.05

		9/13/06		0.025						8/11/06		0.05						10/24/06		0.029																																		10/12/06		0.05

		9/13/06		0.03						8/14/06		0.05						10/26/06		0.03																																		10/13/06		0.05

		9/14/06		0.03						8/15/06		0.035						10/26/06		0.03																																		10/13/06		0.05

		9/15/06		0.03						8/16/06		0.05						10/30/06		0.025																																		10/14/06		0.05

		9/18/06		0.03						8/17/06		0.05						10/30/06		0.023																																		10/14/06		0.05

		9/19/06		0.03						8/17/06		0.05						10/31/06		0.025																																		10/16/06		0.05

		9/19/06		0.03						8/18/06		0.05						10/31/06		0.015																																		10/16/06		0.05

		9/20/06		0.03						8/18/06		0.05						11/1/06		0.026																																		10/17/06		0.05

		9/20/06		0.03						8/19/06		0.05						11/1/06		0.022																																		10/17/06		0.05

		9/21/06		0.02						8/19/06		0.05						11/2/06		0.025																																		10/18/06		0.05

		9/21/06		0.02						8/20/06		0.05						11/2/06		0.015																																		10/18/06		0.05

		9/22/06		0.02						8/21/06		0.05						11/3/06		0.025																																		10/19/06		0.05

		9/22/06		0.02						8/21/06		0.05						11/3/06		0.015																																		10/19/06		0.05

		9/23/06		0.02						8/22/06		0.045						11/6/06		0.025																																		10/20/06		0.05

		9/23/06		0.03						8/22/06		0.05						11/6/06		0.023																																		10/20/06		0.05

		9/25/06		0.02						8/23/06		0.05						11/7/06		0.02																																		10/23/06		0.05

		9/25/06		0.02						8/23/06		0.055						11/7/06		0.018																																		10/23/06		0.055

		9/26/06		0.02						8/24/06		0.05						11/8/06		0.04																																		10/24/06		0.05

		9/26/06		0.02						8/24/06		0.055						11/8/06		0.018																																		10/24/06		0.05

		9/27/06		0.02						8/25/06		0.05						11/9/06		0.02																																		10/25/06		0.05

		9/27/06		0.05						8/25/06		0.055						11/9/06		0.019																																		10/25/06		0.05

		9/28/06		0.03						8/26/06		0.05						11/10/06		0.02																																		10/26/06		0.05

		9/28/06		0.03						8/26/06		0.05						11/10/06		0.015																																		10/26/06		0.05

		9/29/06		0.02						8/28/06		0.05						11/13/06		0.02																																		10/27/06		0.05

		9/29/06		0.03						8/28/06		0.055						11/13/06		0.02																																		10/27/06		0.05

		10/2/06		0.04						8/29/06		0.05						11/14/06		0.02																																		10/28/06		0.05

		10/3/06		0.03						8/29/06		0.05						11/14/06		0.02																																		10/28/06		0.05

		10/3/06		0.03						8/30/06		0.05						11/15/06		0.02																																		10/30/06		0.05

		10/4/06		0.03						8/30/06		0.05						11/15/06		0.02																																		10/30/06		0.05

		10/4/06		0.03						8/31/06		0.05						11/16/06		0.02																																		10/31/06		0.05

		10/5/06		0.04						8/31/06		0.055						11/17/06		0.02																																		10/31/06		0.05

		10/5/06		0.03						9/1/06		0.05						11/17/06		0.018																																		11/1/06		0.05

		10/6/06		0.02						9/5/06		0.045						11/20/06		0.02																																		11/1/06		0.05

		10/7/06		0.05						9/5/06		0.05						11/20/06		0.015																																		11/2/06		0.05

		10/7/06		0.05						9/6/06		0.045						11/21/06		0.02																																		11/2/06		0.055

		10/9/06		0.04						9/7/06		0.05						11/21/06		0.012																																		11/3/06		0.045

		10/9/06		0.04						9/8/06		0.05						11/22/06		0.02																																		11/3/06		0.05

		10/10/06		0.02						9/11/06		0.05						11/22/06		0.02																																		11/6/06		0.05

		10/10/06		0.02						9/11/06		0.05						11/27/06		0.02																																		11/6/06		0.05

		10/11/06		0.03						9/12/06		0.05						11/27/06		0.04																																		11/7/06		0.05

		10/11/06		0.04						9/12/06		0.05						11/28/06		0.02																																		11/7/06		0.055

		10/12/06		0.035						9/13/06		0.05						11/28/06		0.01																																		11/8/06		0.05

		10/12/06		0.035						9/13/06		0.05						11/29/06		0.02																																		11/8/06		0.06

		10/13/06		0.04						9/14/06		0.05						11/29/06		0.015																																		11/9/06		0.05

		10/13/06		0.04						9/15/06		0.05						11/30/06		0.02																																		11/9/06		0.05

		10/14/06		0.04						9/18/06		0.05						11/30/06		0.015																																		11/10/06		0.05

		10/14/06		0.035						9/19/06		0.05						12/1/06		0.01																																		11/10/06		0.05

		10/16/06		0.04						9/19/06		0.05						12/1/06		0.012																																		11/13/06		0.05

		10/16/06		0.035						9/20/06		0.05						12/4/06		0.01																																		11/13/06		0.06

		10/17/06		0.03						9/20/06		0.05						12/4/06		0.015																																		11/14/06		0.06

		10/17/06		0.04						9/21/06		0.05						12/5/06		0.01																																		11/14/06		0.05

		10/18/06		0.03						9/21/06		0.05						12/5/06		0.015																																		11/15/06		0.055

		10/18/06		0.03						9/22/06		0.05						12/6/06		0.01																																		11/15/06		0.05

		10/19/06		0.025						9/22/06		0.05						12/6/06		0.01																																		11/16/06		0.055

		10/19/06		0.02						9/23/06		0.05						12/7/06		0.02																																		11/16/06		0.055

		10/20/06		0.035						9/23/06		0.05						12/7/06		0.01																																		11/17/06		0.05

		10/20/06		0.05						9/25/06		0.05						12/8/06		0.01																																		11/17/06		0.055

		10/21/06		0.04						9/25/06		0.05						12/8/06		0.01																																		11/18/06		0.05

		10/21/06		0.03						9/26/06		0.05						12/11/06		0.01																																		11/18/06		0.065

		10/23/06		0.035						9/26/06		0.05						12/11/06		0.015																																		11/20/06		0.05

		10/23/06		0.04						9/27/06		0.05						12/12/06		0.01																																		11/20/06		0.06

		10/24/06		0.02						9/27/06		0.02						12/12/06		0.015																																		11/21/06		0.05

		10/24/06		0.02						9/28/06		0.03						12/13/06		0.01																																		11/21/06		0.06

		10/25/06		0.035						9/28/06		0.03						12/13/06		0.015																																		11/22/06		0.05

		10/25/06		0.035						9/29/06		0.05						12/14/06		0.02																																		11/22/06		0.05

		10/26/06		0.025						9/29/06		0.05						12/18/06		0.01																																		11/27/06		0.05

		10/26/06		0.045						10/2/06		0.04						12/18/06		0.01																																		11/27/06		0.05

		10/27/06		0.03						10/3/06		0.05						12/19/06		0.01																																		11/28/06		0.055

		10/27/06		0.03						10/3/06		0.05						12/19/06		0.009																																		11/28/06		0.06

		10/28/06		0.03						10/4/06		0.05						12/20/06		0.01																																		11/29/06		0.05

		10/28/06		0.025						10/4/06		0.05						12/20/06		0.01																																		11/29/06		0.055

		10/30/06		0.035						10/5/06		0.04						12/21/06		0.01																																		11/30/06		0.05

		10/30/06		0.035						10/5/06		0.04						12/21/06		0.008																																		11/30/06		0.05

		10/31/06		0.03						10/6/06		0.03						12/22/06		0.01																																		12/1/06		0.05

		11/1/06		0.025						10/7/06		0.03						12/27/06		0.03																																		12/1/06		0.065

		11/2/06		0.035						10/7/06		0.03						12/28/06		0.01																																		12/2/06		0.05

		11/2/06		0.03						10/9/06		0.03						12/28/06		0.01																																		12/2/06		0.065

		11/3/06		0.02						10/9/06		0.03						12/29/06		0.01																																		12/4/06		0.045

		11/6/06		0.015						10/10/06		0.05						12/29/06		0.01																																		12/4/06		0.05

		11/7/06		0.02						10/10/06		0.05						1/2/07		0.01																																		12/5/06		0.045

		11/8/06		0.025						10/11/06		0.03						1/2/07		0.01																																		12/5/06		0.05

		11/9/06		0.03						10/11/06		0.04						1/3/07		0.01																																		12/6/06		0.05

		11/10/06		0.025						10/12/06		0.035						1/3/07		0.01																																		12/6/06		0.05

		11/11/06		0.035						10/12/06		0.035						1/4/07		0.01																																		12/7/06		0.05

		11/13/06		0.035						10/13/06		0.03						1/4/07		0.01																																		12/7/06		0.05

		11/13/06		0.02						10/13/06		0.04						1/5/07		0.01																																		12/8/06		0.05

		11/14/06		0.02						10/14/06		0.03						1/5/07		0.01																																		12/8/06		0.05

		11/14/06		0.02						10/14/06		0.035						1/8/07		0.01																																		12/9/06		0.05

		11/15/06		0.03						10/16/06		0.04						1/8/07		0.01																																		12/9/06		0.05

		11/15/06		0.035						10/16/06		0.04						1/9/07		0.01																																		12/11/06		0.05

		11/16/06		0.035						10/17/06		0.04						1/9/07		0.01																																		12/11/06		0.05

		11/17/06		0.03						10/17/06		0.04						1/10/07		0.01																																		12/12/06		0.05

		11/17/06		0.035						10/18/06		0.04						1/10/07		0.01																																		12/12/06		0.05

		11/18/06		0.03						10/18/06		0.04						1/11/07		0.02																																		12/13/06		0.055

		11/18/06		0.03						10/19/06		0.04						1/11/07		0.01																																		12/13/06		0.055

		11/20/06		0.045						10/19/06		0.04						1/12/07		0.01																																		12/14/06		0.04

		11/21/06		0.035						10/20/06		0.04						1/12/07		0.01																																		12/14/06		0.05

		11/22/06		0.025						10/20/06		0.04						1/15/07		0.02																																		12/15/06		0.05

		11/22/06		0.035						10/21/06		0.03						1/15/07		0.01																																		12/15/06		0.05

		11/27/06		0.03						10/21/06		0.04						1/16/07		0.01																																		2/28/07		0.04

		11/27/06		0.035						10/23/06		0.035						1/16/07		0.015																																		2/28/07		0.04

		11/28/06		0.015						10/23/06		0.04						1/17/07		0.01																																		3/1/07		0.04

		11/29/06		0.015						10/24/06		0.035						1/17/07		0.01																																		3/2/07		0.04

		11/30/06		0.025						10/24/06		0.035						1/18/07		0.01																																		3/3/07		0.04

		12/1/06		0.025						10/25/06		0.03						1/18/07		0.01																																		3/5/07		0.04

		12/2/06		0.025						10/25/06		0.045						1/19/07		0.01																																		3/6/07		0.04

		12/4/06		0.025						10/26/06		0.045						1/19/07		0.01																																		3/7/07		0.04

		12/5/06		0.03						10/26/06		0.04						1/22/07		0.01																																		3/8/07		0.04

		12/6/06		0.03						10/27/06		0.035						1/22/07		0.02																																		3/9/07		0.04

		12/6/06		0.03						10/27/06		0.03						1/23/07		0.01																																		3/12/07		0.045

		12/7/06		0.03						10/28/06		0.03						1/23/07		0.01																																		3/13/07		0.04

		12/7/06		0.035						10/28/06		0.05						1/24/07		0.01																																		3/14/07		0.04

		12/8/06		0.03						10/30/06		0.035						1/24/07		0.005																																		3/15/07		0.03

		12/8/06		0.03						10/30/06		0.035						1/25/07		0.01																																		3/16/07		0.04

		12/9/06		0.03						10/31/06		0.035						1/25/07		0.01																																		3/17/07		0.04

		12/11/06		0.03						11/1/06		0.035						1/26/07		0.01																																		3/19/07		0.03

		12/11/06		0.03						11/2/06		0.035						1/26/07		0.01																																		3/20/07		0.04

		12/12/06		0.03						11/2/06		0.04						1/29/07		0.01																																		3/21/07		0.04

		12/12/06		0.035						11/3/06		0.035						1/29/07		0.01																																		3/22/07		0.03

		12/13/06		0.03						11/6/06		0.05						1/30/07		0.01																																		3/23/07		0.03

		12/13/06		0.03						11/7/06		0.035						1/30/07		0.01																																		3/26/07		0.04

		12/14/06		0.03						11/8/06		0.04						1/31/07		0.01																																		3/27/07		0.03

		12/14/06		0.03						11/9/06		0.035						1/31/07		0.01																																		3/28/07		0.04

		12/15/06		0.03						11/10/06		0.045						2/1/07		0.01																																		3/29/07		0.03

		12/15/06		0.03						11/11/06		0.04						2/1/07		0.005																																		3/30/07		0.04

		12/18/06		0.03						11/13/06		0.04						2/2/07		0.01																																		3/31/07		0.03

		12/18/06		0.03						11/13/06		0.05						2/2/07		0.005																																		4/2/07		0.03

		12/19/06		0.03						11/14/06		0.04						2/5/07		0.01																																		4/3/07		0.045

		12/19/06		0.03						11/14/06		0.04						2/5/07		0.005																																		4/4/07		0.04

		12/20/06		0.03						11/15/06		0.03						2/6/07		0.01																																		4/5/07		0.04

		12/21/06		0.03						11/15/06		0.03						2/6/07		0.005																																		4/6/07		0.04

		12/21/06		0.03						11/16/06		0.03						2/7/07		0.01																																		4/9/07		0.04

		12/22/06		0.02						11/17/06		0.03						2/7/07		0.005																																		4/10/07		0.03

		12/22/06		0.035						11/17/06		0.035						2/8/07		0.01																																		4/11/07		0.04

		12/27/06		0.03						11/18/06		0.03						2/8/07		0.015																																		4/12/07		0.04

		12/27/06		0.03						11/18/06		0.03						2/9/07		0.01																																		4/13/07		0.035

		12/28/06		0.03						11/20/06		0.015						2/9/07		0.018																																		4/16/07		0.035

		12/28/06		0.03						11/21/06		0.03						2/12/07		0.01																																		4/17/07		0.04

		12/29/06		0.03						11/22/06		0.035						2/12/07		0.012																																		4/18/07		0.035

		12/29/06		0.035						11/22/06		0.035						2/13/07		0.01																																		4/19/07		0.04

		1/2/07		0.03						11/27/06		0.035						2/13/07		0.02																																		4/20/07		0.04

		1/2/07		0.03						11/27/06		0.03						2/14/07		0.02																																		4/23/07		0.03

		1/3/07		0.03						11/28/06		0.035						2/14/07		0.015																																		4/24/07		0.04

		1/3/07		0.03						11/29/06		0.035						2/15/07		0.02																																		4/25/07		0.035

		1/4/07		0.03						11/30/06		0.035						2/16/07		0.01																																		4/26/07		0.035

		1/5/07		0.03						12/1/06		0.03						2/20/07		0.015																																		4/27/07		0.035

		1/5/07		0.03						12/2/06		0.03						2/20/07		0.015																																		4/28/07		0.045

		1/8/07		0.03						12/4/06		0.03						2/21/07		0.02																																		4/30/07		0.04

		1/8/07		0.03						12/5/06		0.03						2/21/07		0.015																																		5/1/07		0.04

		1/9/07		0.03						12/6/06		0.03						2/22/07		0.02																																		5/2/07		0.04

		1/9/07		0.03						12/6/06		0.035						2/22/07		0.018																																		5/3/07		0.04

		1/10/07		0.03						12/7/06		0.03						2/23/07		0.02																																		5/4/07		0.04

		1/10/07		0.03						12/7/06		0.03						2/23/07		0.016																																		5/5/07		0.04

		1/11/07		0.03						12/8/06		0.03						2/26/07		0.015																																		5/7/07		0.035

		1/11/07		0.03						12/8/06		0.035						2/26/07		0.014																																		5/8/07		0.04

		1/12/07		0.03						12/9/06		0.03						2/27/07		0.015																																		5/9/07		0.045

		1/13/07		0.03						12/11/06		0.03						2/27/07		0.014																																		5/10/07		0.04

		1/13/07		0.03						12/11/06		0.03						2/28/07		0.01																																		5/11/07		0.035

		1/15/07		0.03						12/12/06		0.03						3/1/07		0.015																																		5/14/07		0.03

		1/15/07		0.03						12/12/06		0.03						3/2/07		0.015																																		5/15/07		0.035

		1/16/07		0.03						12/13/06		0.03						3/5/07		0.01																																		5/16/07		0.045

		1/16/07		0.025						12/13/06		0.03						3/6/07		0.01																																		5/17/07		0.035

		1/17/07		0.02						12/14/06		0.03						3/7/07		0.04																																		5/18/07		0.04

		1/18/07		0.02						12/14/06		0.035						3/8/07		0.04																																		5/19/07		0.04

		1/19/07		0.03						12/15/06		0.03						3/9/07		0.04																																		5/21/07		0.04

		1/19/07		0.03						12/15/06		0.035						3/12/07		0.04																																		5/22/07		0.04

		1/20/07		0.03						12/18/06		0.03						3/13/07		0.04																																		5/23/07		0.045

		1/22/07		0.03						12/18/06		0.03						3/14/07		0.04																																		5/24/07		0.04

		1/23/07		0.03						12/19/06		0.03						3/15/07		0.035																																		5/29/07		0.03

		1/24/07		0.03						12/19/06		0.03						3/16/07		0.04																																		5/30/07		0.03

		1/24/07		0.03						12/20/06		0.03						3/19/07		0.035																																		5/31/07		0.035

		1/25/07		0.03						12/21/06		0.03						3/20/07		0.035																																		6/1/07		0.035

		1/25/07		0.03						12/21/06		0.035						3/21/07		0.035																																		6/2/07		0.05

		1/26/07		0.03						12/22/06		0.03						3/22/07		0.032																																		6/4/07		0.035

		1/26/07		0.035						12/22/06		0.03						3/23/07		0.03																																		6/5/07		0.04

		1/29/07		0.03						12/27/06		0.03						3/26/07		0.03																																		6/6/07		0.04

		1/29/07		0.035						12/27/06		0.03						3/27/07		0.03																																		6/7/07		0.04

		1/30/07		0.035						12/28/06		0.03						3/28/07		0.035																																		6/8/07		0.045

		1/30/07		0.035						12/28/06		0.035						3/29/07		0.035																																		6/9/07		0.04

		1/31/07		0.03						12/29/06		0.03						3/30/07		0.03																																		6/11/07		0.04

		1/31/07		0.035						12/29/06		0.035						4/2/07		0.03																																		6/12/07		0.04

		2/1/07		0.03						1/2/07		0.03						4/3/07		0.025																																		6/13/07		0.04

		2/1/07		0.03						1/2/07		0.03						4/4/07		0.03																																		6/14/07		0.035

		2/2/07		0.03						1/3/07		0.03						4/5/07		0.025																																		6/15/07		0.045

		2/2/07		0.03						1/3/07		0.03						4/6/07		0.03																																		6/16/07		0.05

		2/3/07		0.03						1/4/07		0.03						4/9/07		0.025																																		6/19/07		0.04

		2/3/07		0.035						1/5/07		0.03						4/10/07		0.03																																		6/20/07		0.04

		2/5/07		0.03						1/5/07		0.03						4/11/07		0.03																																		6/21/07		0.035

		2/5/07		0.03						1/8/07		0.03						4/12/07		0.03																																		6/22/07		0.04

		2/6/07		0.03						1/8/07		0.03						4/13/07		0.028																																		6/23/07		0.04

		2/6/07		0.03						1/9/07		0.03						4/16/07		0.032																																		6/25/07		0.04

		2/7/07		0.05						1/9/07		0.03						4/17/07		0.03																																		6/26/07		0.04

		2/7/07		0.04						1/10/07		0.03						4/18/07		0.025																																		6/27/07		0.04

		2/8/07		0.04						1/10/07		0.035						4/19/07		0.025																																		6/28/07		0.04

		2/8/07		0.03						1/11/07		0.03						4/23/07		0.04																																		6/29/07		0.04

		2/10/07		0.03						1/11/07		0.03						4/24/07		0.044																																		7/2/07		0.04

		2/10/07		0.05						1/12/07		0.03						4/25/07		0.049																																		7/3/07		0.045

		2/12/07		0.03						1/13/07		0.03						4/26/07		0.049																																		7/5/07		0.05

		2/13/07		0.035						1/13/07		0.03						4/27/07		0.045																																		7/6/07		0.05

		2/13/07		0.04						1/15/07		0.03						4/30/07		0.045																																		7/9/07		0.045

		2/14/07		0.04						1/15/07		0.03						5/1/07		0.042																																		7/10/07		0.07

		2/14/07		0.04						1/16/07		0.03						5/2/07		0.045																																		7/11/07		0.045

		2/15/07		0.05						1/16/07		0.03						5/3/07		0.042																																		7/12/07		0.055

		2/15/07		0.04						1/17/07		0.03						5/4/07		0.045																																		7/13/07		0.05

		2/16/07		0.04						1/18/07		0.03						5/7/07		0.045																																		7/14/07		0.05

		2/16/07		0.04						1/19/07		0.035						5/8/07		0.045																																		7/16/07		0.055

		2/20/07		0.05						1/19/07		0.03						5/9/07		0.045																																		7/17/07		0.05

		2/20/07		0.05						1/20/07		0.03						5/10/07		0.045																																		7/18/07		0.075

		2/21/07		0.04						1/22/07		0.03						5/11/07		0.045																																		7/19/07		0.07

		2/21/07		0.055						1/23/07		0.03						5/14/07		0.046																																		7/20/07		0.07

		2/22/07		0.04						1/24/07		0.03						5/15/07		0.05																																		7/23/07		0.07

		2/22/07		0.05						1/24/07		0.03						5/16/07		0.055																																		7/24/07		0.07

		2/23/07		0.03						1/25/07		0.03						5/17/07		0.045																																		7/25/07		0.065

		2/23/07		0.05						1/25/07		0.03						5/18/07		0.04																																		7/26/07		0.055

		2/26/07		0.05						1/26/07		0.03						5/21/07		0.044																																		7/27/07		0.06

		2/26/07		0.04						1/26/07		0.035						5/22/07		0.045																																		7/28/07		0.065

		2/27/07		0.03						1/29/07		0.035						5/23/07		0.045																																		7/30/07		0.05

		2/27/07		0.04						1/29/07		0.035						5/24/07		0.04																																		7/31/07		0.06

		2/28/07		0.03						1/30/07		0.03						5/24/07		0.04																																		8/1/07		0.06

		2/28/07		0.03						1/30/07		0.03						5/29/07		0.025																																		8/2/07		0.06

		3/1/07		0.04						1/31/07		0.03						5/30/07		0.045																																		8/3/07		0.06

		3/2/07		0.04						1/31/07		0.035						5/31/07		0.05																																		8/6/07		0.06

		3/5/07		0.04						2/1/07		0.035						6/1/07		0.051																																		8/7/07		0.06

		3/6/07		0.04						2/1/07		0.03						6/4/07		0.044																																		8/8/07		0.05

		3/7/07		0.04						2/2/07		0.03						6/5/07		0.047																																		8/9/07		0.05

		3/8/07		0.04						2/2/07		0.03						6/6/07		0.046																																		8/10/07		0.05

		3/9/07		0.04						2/3/07		0.03						6/7/07		0.05																																		8/11/07		0.05

		3/12/07		0.04						2/3/07		0.03						6/8/07		0.048																																		8/13/07		0.06

		3/13/07		0.03						2/5/07		0.03						6/9/07		0.049																																		8/14/07		0.05

		3/14/07		0.03						2/5/07		0.03						6/11/07		0.049																																		8/15/07		0.05

		3/15/07		0.04						2/6/07		0.03						6/12/07		0.05																																		8/16/07		0.055

		3/16/07		0.04						2/6/07		0.035						6/13/07		0.045																																		8/17/07		0.055

		3/19/07		0.03						2/7/07		0.03						6/14/07		0.048																																		8/20/07		0.05

		3/20/07		0.04						2/7/07		0.03						6/15/07		0.045																																		8/21/07		0.05

		3/21/07		0.035						2/8/07		0.03						6/18/07		0.045																																		8/22/07		0.05

		3/22/07		0.04						2/8/07		0.03						6/19/07		0.045																																		8/23/07		0.05

		3/23/07		0.04						2/10/07		0.03						6/20/07		0.045																																		8/24/07		0.05

		3/26/07		0.035						2/10/07		0.04						6/21/07		0.045																																		8/27/07		0.05

		3/27/07		0.04						2/12/07		0.03						6/25/07		0.042																																		8/28/07		0.05

		3/28/07		0.035						2/13/07		0.035						6/26/07		0.045																																		8/29/07		0.05

		3/29/07		0.035						2/13/07		0.05						6/27/07		0.04																																		8/30/07		0.05

		3/30/07		0.03						2/14/07		0.04						6/28/07		0.063																																		8/31/07		0.05

		3/31/07		0.035						2/14/07		0.04						6/29/07		0.061																																		9/4/07		0.05

		4/2/07		0.04						2/15/07		0.05						7/2/07		0.06																																		9/5/07		0.05

		4/3/07		0.035						2/15/07		0.04						7/3/07		0.062																																		9/6/07		0.05

		4/4/07		0.035						2/16/07		0.04						7/5/07		0.06																																		9/7/07		0.055

		4/5/07		0.035						2/16/07		0.04						7/6/07		0.058																																		9/10/07		0.045

		4/6/07		0.035						2/20/07		0.05						7/9/07		0.06																																		9/11/07		0.05

		4/9/07		0.035						2/20/07		0.05						7/10/07		0.06																																		9/12/07		0.05

		4/10/07		0.03						2/21/07		0.04						7/11/07		0.055																																		9/13/07		0.045

		4/11/07		0.03						2/21/07		0.035						7/12/07		0.056																																		9/14/07		0.05

		4/12/07		0.03						2/22/07		0.04						7/13/07		0.056																																		9/17/07		0.05

		4/13/07		0.03						2/22/07		0.04						7/16/07		0.055																																		9/18/07		0.045

		4/14/07		0.03						2/23/07		0.03						7/17/07		0.05																																		9/19/07		0.05

		4/16/07		0.03						2/23/07		0.04						7/18/07		0.045																																		9/20/07		0.05

		4/17/07		0.03						2/26/07		0.03						7/19/07		0.045																																		9/21/07		0.05

		4/18/07		0.025						2/26/07		0.035						7/20/07		0.04																																		9/22/07		0.05

		4/19/07		0.03						2/27/07		0.03						7/23/07		0.04																																		9/24/07		0.05

		4/20/07		0.035						2/27/07		0.03						7/24/07		0.04																																		9/25/07		0.05

		4/21/07		0.035						2/28/07		0.03						7/25/07		0.04																																		9/26/07		0.05

		4/23/07		0.025						3/1/07		0.03						7/26/07		0.04																																		9/27/07		0.05

		4/24/07		0.02						3/2/07		0.03						7/28/07		0.04																																		9/28/07		0.05

		4/25/07		0.03						3/5/07		0.03						7/30/07		0.044																																		10/1/07		0.05

		4/26/07		0.04						3/6/07		0.03						7/31/07		0.044																																		10/2/07		0.06

		4/27/07		0.025						3/7/07		0.04						8/1/07		0.04																																		10/3/07		0.05

		4/30/07		0.025						3/8/07		0.04						8/2/07		0.04																																		10/4/07		0.05

		5/1/07		0.03						3/9/07		0.04						8/3/07		0.04																																		10/5/07		0.045

		5/2/07		0.02						3/12/07		0.04						8/4/07		0.042																																		10/8/07		0.05

		5/3/07		0.02						3/13/07		0.04						8/6/07		0.04																																		10/9/07		0.05

		5/4/07		0.02						3/14/07		0.03						8/7/07		0.04																																		10/10/07		0.05

		5/5/07		0.02						3/15/07		0.035						8/8/07		0.034																																		10/11/07		0.05

		5/7/07		0.02						3/16/07		0.035						8/9/07		0.032																																		10/12/07		0.05

		5/8/07		0.025						3/19/07		0.035						8/10/07		0.043																																		10/15/07		0.05

		5/9/07		0.03						3/20/07		0.04						8/13/07		0.045																																		10/16/07		0.045

		5/10/07		0.025						3/21/07		0.04						8/14/07		0.045																																		10/17/07		0.05

		5/11/07		0.005						3/22/07		0.04						8/15/07		0.043																																		10/18/07		0.05

		5/14/07		0.035						3/23/07		0.035						8/16/07		0.04																																		10/19/07		0.045

		5/15/07		0.035						3/26/07		0.035						8/17/07		0.04																																		10/22/07		0.05

		5/16/07		0.03						3/27/07		0.04						8/20/07		0.04																																		10/23/07		0.05

		5/17/07		0.03						3/28/07		0.04						8/21/07		0.03																																		10/24/07		0.045

		5/18/07		0.03						3/29/07		0.035						8/22/07		0.04																																		10/25/07		0.045

		5/19/07		0.03						3/30/07		0.03						8/23/07		0.04																																		10/26/07		0.05

		5/21/07		0.025						3/31/07		0.035						8/24/07		0.04																																		10/29/07		0.05

		5/22/07		0.025						4/2/07		0.035						8/27/07		0.045																																		10/30/07		0.045

		5/23/07		0.025						4/3/07		0.035						8/28/07		0.04																																		10/31/07		0.05

		5/24/07		0.02						4/4/07		0.04						8/29/07		0.055																																		11/1/07		0.045

		5/25/07		0.025						4/5/07		0.04						8/30/07		0.055																																		11/2/07		0.05

		5/29/07		0.025						4/6/07		0.04						8/31/07		0.05																																		11/5/07		0.05

		5/30/07		0.048						4/9/07		0.035						9/4/07		0.05																																		11/6/07		0.045

		5/31/07		0.04						4/10/07		0.035						9/5/07		0.04						0.61		0.4																										11/7/07		0.05

		6/1/07		0.025						4/11/07		0.04						9/6/07		0.05						0.61		0.41																										11/8/07		0.05

		6/2/07		0.03						4/12/07		0.035						9/7/07		0.045						0.6		0.41																										11/9/07		0.05

		6/4/07		0.03						4/13/07		0.035						9/8/07		0.04						0.6		0.41																										11/12/07		0.045

		6/5/07		0.0175						4/14/07		0.03						9/10/07		0.055						0.61		0.41																										11/13/07		0.05

		6/6/07		0.03						4/16/07		0.035						9/11/07		0.05						0.61		0.41																										11/14/07		0.045

		6/7/07		0.04						4/17/07		0.035						9/12/07		0.05						0.61		0.41																										11/15/07		0.045

		6/8/07		0.025						4/18/07		0.04						9/13/07		0.05						0.61		0.41																										11/16/07		0.045

		6/9/07		0.02						4/19/07		0.035						9/14/07		0.05						0.6		0.42																										11/19/07		0.045

		6/11/07		0.04						4/20/07		0.04						9/15/07		0.05						0.6		0.4																										11/20/07		0.045

		6/12/07		0.02						4/21/07		0.035						9/17/07		0.054						0.6		0.41																										11/21/07		0.045

		6/13/07		0.03						4/23/07		0.035						9/18/07		0.054						0.61		0.41																										11/26/07		0.045

		6/14/07		0.025						4/24/07		0.02						9/19/07		0.045						0.65		0.4																										11/27/07		0.045

		6/15/07		0.02						4/25/07		0.04						9/20/07		0.045						0.61		0.41																										11/28/07		0.045

		6/18/07		0.025						4/26/07		0.035						9/21/07		0.04						0.6		0.4																										11/29/07		0.045

		6/19/07		0.02						4/27/07		0.04						9/24/07		0.035						0.6		0.4																										11/30/07		0.045

		6/20/07		0.03						4/30/07		0.025						9/25/07		0.04						0.62		0.4																										12/1/07		0.045

		6/21/07		0.016						5/1/07		0.03						9/26/07		0.04						0.62		0.42																										12/3/07		0.045

		6/22/07		0.025						5/2/07		0.03						9/27/07		0.04						0.62		0.42																										12/4/07		0.045

		6/25/07		0.02						5/3/07		0.03						9/28/07		0.05						0.6		0.4																										12/5/07		0.045

		6/26/07		0.025						5/4/07		0.035						10/1/07		0.04						0.62		0.42																										12/6/07		0.045

		6/27/07		0.03						5/5/07		0.035						10/2/07		0.045						0.62		0.42																										12/7/07		0.045

		6/28/07		0.045						5/7/07		0.04						10/3/07		0.045						0.62		0.42																										12/8/07		0.045

		6/29/07		0.025						5/8/07		0.045						10/4/07		0.05						0.61		0.42																										12/10/07		0.045

		7/2/07		0.04						5/9/07		0.03						10/5/07		0.05						0.62		0.42																										12/11/07		0.04

		7/3/07		0.04						5/10/07		0.04						10/8/07		0.05						0.62		0.42																										12/12/07		0.04

		7/5/07		0.04						5/11/07		0.03						10/9/07		0.04						0.62		0.42																										12/13/07		0.04

		7/6/07		0.04						5/14/07		0.03						10/10/07		0.04						0.62		0.42																										12/14/07		0.04

		7/9/07		0.04						5/15/07		0.03						10/11/07		0.05						0.62		0.42																										12/17/07		0.04

		7/10/07		0.03						5/16/07		0.03						10/12/07		0.045						0.62		0.42																										12/18/07		0.045

		7/11/07		0.035						5/17/07		0.03						10/13/07		0.04						0.62		0.42																										12/19/07		0.04

		7/12/07		0.035						5/18/07		0.03						10/15/07		0.04						0.61		0.41																										12/20/07		0.04

		7/13/07		0.03						5/19/07		0.03						10/16/07		0.04						0.62		0.42																										12/26/07		0.04

		7/16/07		0.03						5/21/07		0.03						10/17/07		0.04						0.61		0.41																										12/27/07		0.04

		7/17/07		0.035						5/22/07		0.03						10/18/07		0.04						0.62		0.42																										12/28/07		0.04

		7/18/07		0.03						5/23/07		0.03						10/19/07		0.04						0.62		0.42																										12/31/07		0.05

		7/19/07		0.03						5/24/07		0.03						10/22/07		0.045						0.62		0.42																										1/2/08		0.04

		7/20/07		0.03						5/25/07		0.03						10/23/07		0.05						0.64		0.44																										1/3/08		0.04

		7/23/07		0.04						5/29/07		0.035						10/24/07		0.045						0.62		0.42																										1/4/08		0.04

		7/24/07		0.035						5/30/07		0.02						10/25/07		0.03						0.62		0.42																										1/7/08		0.04

		7/25/07		0.035						5/31/07		0.03						10/26/07		0.035						0.62		0.42																										1/8/08		0.04

		7/26/07		0.04						6/1/07		0.03						10/29/07		0.03						0.62		0.42																										1/9/08		0.04

		7/27/07		0.04						6/2/07		0.03						10/30/07		0.025						0.62		0.42																										1/10/08		0.04

		7/30/07		0.035						6/4/07		0.03						10/31/07		0.03						0.62		0.42																										1/11/08		0.04

		7/31/07		0.035						6/5/07		0.04						11/1/07		0.035						0.62		0.42																										1/14/08		0.04

		8/1/07		0.03						6/6/07		0.025						11/2/07		0.035						0.62		0.42																										1/15/08		0.04

		8/2/07		0.035						6/7/07		0.03						11/5/07		0.025						0.62		0.4																										1/16/08		0.04

		8/3/07		0.04						6/8/07		0.03						11/6/07		0.04						0.62		0.41																										1/17/08		0.04

		8/4/07		0.03						6/9/07		0.025						11/7/07		0.02						0.62		0.42																										1/18/08		0.04

		8/6/07		0.03						6/11/07		0.03						11/8/07		0.03						0.62		0.42																										1/21/08		0.04

		8/7/07		0.035						6/12/07		0.02						11/9/07		0.02						0.62		0.42																										1/22/08		0.04

		8/8/07		0.03						6/13/07		0.03						11/12/07		0.035						0.62		0.42																										1/23/08		0.04

		8/9/07		0.03						6/14/07		0.025						11/13/07		0.04						0.62		0.4																										1/24/08		0.04

		8/10/07		0.04						6/15/07		0.025						11/14/07		0.04						0.62		0.42																										1/25/08		0.045

		8/13/07		0.03						6/18/07		0.03						11/15/07		0.04						0.62		0.42																										1/28/08		0.04

		8/14/07		0.03						6/19/07		0.025						11/16/07		0.035						0.62		0.42																										1/29/08		0.04

		8/15/07		0.03						6/20/07		0.03						11/19/07		0.045						0.66		0.44																										1/30/08		0.04

		8/17/07		0.03						6/21/07		0.03						11/20/07		0.04						0.64		0.42																										1/31/08		0.04

		8/20/07		0.03						6/22/07		0.02						11/21/07		0.04						0.64		0.42																										2/1/08		0.04

		8/21/07		0.03						6/25/07		0.02						11/26/07		0.04						0.66		0.44																										2/4/08		0.04

		8/22/07		0.03						6/26/07		0.02						11/27/07		0.042						0.66		0.44																										2/5/08		0.04

		8/23/07		0.03						6/27/07		0.03						11/28/07		0.04						0.66		0.44																										2/6/08		0.04

		8/24/07		0.03						6/28/07		0.03						11/29/07		0.03						0.64		0.44																										2/7/08		0.04

		8/25/07		0.02						6/29/07		0.04						11/30/07		0.03						0.64		0.44																										2/8/08		0.04

		8/27/07		0.04						7/2/07		0.03						12/3/07		0.04						0.64		0.44																										2/11/08		0.04

		8/28/07		0.035						7/3/07		0.025						12/4/07		0.03						0.64		0.42																										2/12/08		0.04

		8/29/07		0.04						7/5/07		0.03						12/5/07		0.03						0.64		0.44																										2/13/08		0.04

		8/30/07		0.03						7/6/07		0.025						12/6/07		0.03						0.64		0.42																										2/14/08		0.04

		8/31/07		0.03						7/9/07		0.025						12/7/07		0.03						0.64		0.44																										2/15/08		0.04

		9/4/07		0.03						7/10/07		0.03						12/10/07		0.03						0.64		0.44																										2/16/08		0.04

		9/5/07		0.03						7/11/07		0.035						12/11/07		0.03						0.66		0.42																										2/19/08		0.04

		9/6/07		0.035						7/12/07		0.035						12/12/07		0.03						0.6		0.42																										2/20/08		0.045

		9/7/07		0.02						7/13/07		0.03						12/13/07		0.045						0.66		0.42																										2/21/08		0.04

		9/8/07		0.04						7/16/07		0.03						12/14/07		0.03						0.66		0.42																										2/22/08		0.04

		9/10/07		0.025						7/17/07		0.03						12/17/07		0.03						0.64		0.42																										2/25/08		0.04

		9/11/07		0.035						7/18/07		0.025						12/18/07		0.03						0.66		0.4																										2/26/08		0.04

		9/12/07		0.035						7/19/07		0.025						12/19/07		0.02						0.66		0.42																										2/27/08		0.04

		9/13/07		0.03						7/20/07		0.035						12/20/07		0.03						0.64		0.42																										2/28/08		0.04

		9/14/07		0.03						7/23/07		0.03						12/21/07		0.04						0.66		0.42																										2/29/08		0.04

		9/17/07		0.03						7/24/07		0.025						12/26/07		0.03						0.64		0.42																										3/1/08		0.04

		9/18/07		0.025						7/25/07		0.035						12/27/07		0.025						0.62		0.44																										3/2/08		0.04

		9/19/07		0.04						7/26/07		0.03						12/28/07		0.025						0.64		0.44																										3/3/08		0.04

		9/20/07		0.04						7/27/07		0.03						12/31/07		0.02						0.64		0.44																										3/4/08		0.04

		9/21/07		0.03						7/30/07		0.035																																										3/5/08		0.04

		9/24/07		0.025						7/31/07		0.04						2/14/08		0.04						0.292		0.309		0.485		61		1180																				3/6/08		0.04

		9/25/07		0.035						8/1/07		0.03						2/15/08		0.037		69		50		0.28		0.31		0.414		61		1172																				3/7/08		0.04

		9/26/07		0.025						8/2/07		0.035						2/19/08		0.035		69		48		0.293		0.309		0.426		60		1184																				3/8/08		0.04

		9/27/07		0.02						8/3/07		0.03						2/20/08		0.03		70		46		0.26		0.309		0.41		63		1184																				3/10/08		0.04

		9/28/07		0.02						8/4/07		0.03						2/21/08		0.032		70		46		0.29		0.305		0.441		62		1164																				3/11/08		0.04

		9/29/07		0.02						8/6/07		0.03						2/22/08		0.031		70		45		0.281		0.307		0.419		62		1184																				3/12/08		0.04

		10/1/07		0.015						8/7/07		0.025						2/25/08		0.069		70		46		0.288		0.311		0.421		63		1184																				3/13/08		0.04

		10/2/07		0.035						8/8/07		0.03						2/26/08		0.068		70		44		0.281		0.312		0.413		64		1192																				3/14/08		0.04

		10/3/07		0.03						8/9/07		0.045						2/27/08		0.067		70		45		0.288		0.311		0.413		62		1184																				3/15/08		0.04

		10/4/07		0.04						8/10/07		0.04						2/28/08		0.063		70		46		0.283		0.31		0.457		62		1172																				3/17/08		0.04

		10/5/07		0.025						8/13/07		0.04						2/29/08		0.064		70		45		0.256		0.311		0.409		63		1184																				3/18/08		0.04

		10/8/07		0.03						8/14/07		0.04						3/3/08		0.07		70		33		0.285		0.311		0.435		63		1204																				3/19/08		0.04

		10/9/07		0.03						8/15/07		0.04						3/4/08		0.07		70		44		0.261		0.311		0.438		63		1184																				3/20/08		0.04

		10/10/07		0.03						8/17/07		0.04						3/5/08		0.069		70		44		0.291		0.311		0.445		63		1184																				3/21/08		0.04

		10/11/07		0.03						8/20/07		0.03						3/6/08		0.068		70		44		0.281		0.311		0.458		61		1184																				3/22/08		0.04

		10/12/07		0.02						8/21/07		0.03						3/7/08		0.067		70		44		0.282		0.322		0.455		63		1192																				3/24/08		0.04

		10/15/07		0.03						8/22/07		0.035						3/10/08		0.069		70		46		0.264		0.321		0.428		64		1184																				3/25/08		0.04

		10/16/07		0.02						8/23/07		0.03						3/11/08		0.071		70		43		0.285		0.322		0.438		63		1204																				3/26/08		0.045

		10/17/07		0.04						8/24/07		0.035						3/12/08		0.056		70		44		0.261		0.312		0.422		62		1188																				3/27/08		0.04		70		25

		10/18/07		0.04						8/25/07		0.02						3/14/08		0.067		70		43		0.261		0.321		0.451		63		1184																				3/28/08		0.04		70		41

		10/19/07		0.025						8/27/07		0.025						3/17/08		0.069		70		45		0.26		0.32		0.439		63		1196																				3/31/08		0.04		70		28

		10/22/07		0.03						8/28/07		0.025						3/18/08		0.062		70		47		0.279		0.32		0.422		63		1196																				4/1/08		0.04		70		29

		10/23/07		0.03						8/29/07		0.03						3/19/08		0.053		70		44		0.273		0.321		0.419		64		1192																				4/2/08		0.055		70		36

		10/24/07		0.04						8/30/07		0.03						3/20/08		0.064		70		33		0.262		0.321		0.431		64		1192																				4/3/08		0.04		69		40

		10/25/07		0.035						8/31/07		0.03						3/21/08		0.063		70		35		0.277		0.322		0.439		63		1196																				4/4/08		0.045		70		44

		10/26/07		0.045						9/4/07		0.03						3/24/08		0.052		70		42		0.238		0.321		0.418		63		1184																				4/5/08		0.04		70		41

		10/29/07		0.02						9/5/07		0.03						3/25/08		0.057		70		38		0.264		0.319		0.445		63		1192																				4/7/08		0.05		70		44

		10/30/07		0.02						9/6/07		0.03						3/26/08		0.056		70		35		0.276		0.321		0.447		63		1204																				4/8/08		0.05		70		44

		10/31/07		0.02						9/7/07		0.03						3/27/08		0.07		70		24		0.28		0.32		0.46		63		1204																				4/9/08		0.05		70		44

		11/1/07		0.03						9/8/07		0.03						3/28/08		0.05		70		40		0.26		0.32		0.44		63		1192																				4/10/08		0.05		70		44

		11/2/07		0.025						9/10/07		0.02						3/31/08		0.06		70		27		0.3		0.32		0.48		63		1204																				4/11/08		0.05		70		46

		11/5/07		0.03						9/11/07		0.02						4/1/08		0.06		70		28		0.28		0.32		0.46		61		1192																				4/14/08		0.05		72		41

		11/6/07		0.025						9/12/07		0.03						4/2/08		0.06		70		30		0.28		0.32		0.44		63		1204																				4/15/08		0.05		74		42

		11/7/07		0.025						9/13/07		0.02						4/3/08		0.06		70		38		0.28		0.32		0.44		64		1192																				4/16/08		0.05		70		45

		11/8/07		0.085						9/14/07		0.035						4/4/08		0.05		70		44		0.26		0.32		0.44		63		1196																				4/17/08		0.045		72		46

		11/9/07		0.08						9/17/07		0.03						4/5/08		0.05		70		40		0.26		0.32		0.44		63		1196																				4/18/08		0.04		70		48

		11/12/07		0.075						9/18/07		0.03						4/7/08		0.055		70		44		0.26		0.32		0.46		65		1204																				4/19/08		0.05		69		48

		11/13/07		0.08						9/19/07		0.04						4/8/08		0.055		70		44		0.28		0.32		0.44		61		1192																				4/21/08		0.05		73		47

		11/14/07		0.075						9/20/07		0.04						4/9/08		0.055		70		46		0.28		0.32		0.44		63		1196																				4/22/08		0.045		77		46

		11/15/07		0.075						9/21/07		0.03						4/10/08		0.05		70		45		0.28		0.32		0.44		61		1204																				4/23/08		0.05		71		45

		11/16/07		0.07						9/24/07		0.025						4/11/08		0.05		70		42		0.28		0.32		0.44		61		1192																				4/24/08		0.045		73		46

		11/19/07		0.075						9/25/07		0.025						4/14/08		0.05		70		43		0.28		0.32		0.46		61		1196																				4/25/08		0.04		70		46

		11/20/07		0.07						9/26/07		0.03						4/15/08		0.05		73		41		0.28		0.32		0.44		62		1196																				4/30/08		0.06		69		26

		11/21/07		0.075						9/27/07		0.03						4/16/08		0.05		72		43		0.28		0.32		0.48		62		1196																				5/1/08		0.04		75		42

		11/26/07		0.08						9/28/07		0.03						4/17/08		0.05		72		44		0.28		0.32		0.48		62		1196																				5/2/08		0.04		72		35

		11/27/07		0.08						9/29/07		0.025						4/18/08		0.05		72		45		0.28		0.32		0.48		62		1196																				5/3/08		0.04		78		34

		11/28/07		0.08						10/1/07		0.03						4/19/08		0.06		72		44		0.28		0.32		0.48		62		1196																				5/5/08		0.04		71		40

		11/29/07		0.075						10/2/07		0.025						4/21/08		0.055		71		45		0.28		0.32		0.46		64		1196																				5/6/08		0.045		75		40

		11/30/07		0.08						10/3/07		0.03						4/22/08		0.05		72		43		0.28		0.32		0.46		64		1196																				5/7/08		0.05		72		36

		12/3/07		0.07						10/4/07		0.03						4/23/08		0.05		73		42		0.28		0.32		0.48		63		1196																				5/8/08		0.045		72		38

		12/4/07		0.08						10/5/07		0.02						4/24/08		0.055		73		45		0.28		0.32		0.46		63		1196																				5/9/08		0.04		74		34

		12/5/07		0.07						10/8/07		0.03						4/25/08		0.05		73		41		0.26		0.32		0.44		63		1204																				5/10/08		0.045		72		34

		12/6/07		0.08						10/9/07		0.02						4/28/08								0.26		0.32		0.44		63		1204																				5/12/08		0.055		69		28

		12/7/07		0.075						10/10/07		0.025						4/29/08								0.28		0.32		0.44		60		1184																				5/13/08		0.04		75		31

		12/10/07		0.075						10/11/07		0.03						4/30/08		0.06		70		25		0.28		0.32		0.46		60		1192																				5/14/08		0.05		71		38

		12/11/07		0.075						10/12/07		0.02						5/1/08		0.055		73		39		0.28		0.32		0.46		60		1196																				5/15/08		0.04		72		42

		12/12/07		0.075						10/15/07		0.025						5/2/08		0.045		72		34		0.28		0.32		0.46		60		1210																				5/16/08		0.04		71		48

		12/13/07		0.075						10/16/07		0.025						5/3/08		0.05		73		38		0.28		0.32		0.46		60		1210																				5/19/08		0.04		75		42

		12/14/07		0.075						10/17/07		0.03						5/5/08		0.04		72		38		0.28		0.32		0.44		60		1192																				5/20/08		0.04		73		44

		12/17/07		0.08						10/18/07		0.025						5/6/08		0.04		73		42		0.28		0.32		0.44		60		1184																				5/21/08		0.04		71		36

		12/18/07		0.075						10/19/07		0.025						5/7/08		0.04		73		37		0.28		0.32		0.44		62		1196																				5/22/08		0.04		73		30

		12/19/07		0.08						10/22/07		0.025						5/8/08		0.04		73		35		0.28		0.32		0.44		60		1196																				5/23/08		0.04		71		36

		12/20/07		0.08						10/23/07		0.02						5/9/08		0.04		72		34		0.3		0.32		0.46		62		1204																				5/27/08		0.02		73		37

		12/21/07		0.08						10/24/07		0.035						5/10/08		0.04		72		32		0.3		0.32		0.46		62		1204																				5/28/08		0.03		71		39

		12/26/07		0.08						10/25/07		0.025						5/12/08		0.055		68		28		0.26		0.32		0.42		60		1196																				5/29/08		0.03		74		39

		12/27/07		0.08						10/26/07		0.035						5/13/08		0.04		73		31		0.26		0.32		0.46		61		1192																				5/30/08		0.04		72		38

		12/28/07		0.075						10/29/07		0.025						5/14/08		0.045		73		25		0.3		0.32		0.46		60		1184																				5/31/08		0.025		72		39

		12/31/07		0.08						10/30/07		0.03						5/15/08		0.035		73		39		0.3		0.32		0.46		60		1196																				6/2/08		0.025		74		27

		1/2/08		0.09						10/31/07		0.03						5/16/08		0.035		73		45		0.3		0.32		0.44		60		1184																				6/3/08		0.02		71		34

		1/3/08		0.075						11/1/07		0.04						5/19/08		0.045		72		41		0.28		0.32		0.44		60		1204																				6/4/08		0.025		69		33

		1/4/08		0.09						11/2/07		0.03						5/20/08		0.045		73		42		0.28		0.32		0.44		62		1196																				6/5/08		0.025		71		39

		1/7/08		0.125						11/5/07		0.025						5/21/08		0.045		70		35		0.28		0.32		0.46		60		1196																				6/6/08		0.025		71		32

		1/8/08		0.08						11/6/07		0.03						5/22/08		0.045		72		30		0.28		0.32		0.42		61		1176																				6/9/08		0.03		72		43

		1/9/08		0.08						11/7/07		0.035						5/23/08		0.045		73		34		0.28		0.32		0.46		61		1172																				6/10/08		0.03		73		33

		1/10/08		0.08						11/8/07		0.05						5/27/08		0.035		73		36		0.28		0.32		0.44		61		1196																				6/11/08		0.025		70		33

		1/11/08		0.08						11/9/07		0.05						5/28/08		0.04		72		37		0.28		0.32		0.44		61		1204																				6/12/08		0.025		71		35

		1/14/08		0.09						11/12/07		0.03						5/29/08		0.04		73		37		0.26		0.32		0.44		61		1200																				6/13/08		0.025		75		32

		1/15/08		0.085						11/13/07		0.05						5/30/08		0.04		72		37		0.28		0.32		0.48		61		1196																				6/16/08		0.025		72		37

		1/16/08		0.09						11/14/07		0.05						6/2/08		0.04		71		30		0.28		0.28		0.44		60		1200																				6/17/08		0.03		72		26

		1/17/08		0.08						11/15/07		0.05						6/3/08		0.035		72		35		0.28		0.32		0.42		61		1196																				6/18/08		0.025		73		33

		1/18/08		0.09						11/16/07		0.05						6/4/08		0.035		70		33		0.28		0.32		0.44		61		1188																				6/19/08		0.025		71		29

		1/21/08		0.04						11/19/07		0.05						6/5/08		0.035		71		37		0.3		0.32		0.44		61		1192																				6/20/08		0.02		73		33

		1/22/08		0.11						11/20/07		0.05						6/6/08		0.035		71		31		0.28		0.32		0.44		61		1188																				6/21/08		0.025		74		27

		1/23/08		0.09						11/21/07		0.05						6/9/08		0.04		72		40		0.32		0.32		0.48		61		1188																				6/23/08		0.02		72		37

		1/24/08		0.09						11/26/07		0.05						6/10/08		0.04		72		31		0.3		0.32		0.44		55		1172																				6/24/08		0.025		73		35

		1/25/08		0.095						11/27/07		0.05						6/11/08		0.04		70		34		0.3		0.32		0.48		55		1196																				6/25/08		0.03		72		36

		1/28/08		0.09						11/28/07		0.05						6/12/08		0.04		72		31		0.3		0.32		0.48		55		1196																				6/26/08		0.03		74		35

		1/29/08		0.09						11/29/07		0.045						6/13/08		0.05		71		36		0.26		0.32		0.44		55		1208																				6/27/08		0.02		71		39

		1/30/08		0.1						11/30/07		0.05						6/16/08		0.05		73		34		0.3		0.32		0.46		55		1204																				6/30/08		0.02		73		38

		1/31/08		0.105						12/3/07		0.05						6/17/08		0.05		73		24		0.28		0.32		0.44		55		1216																				7/1/08		0.055		73		39

		2/1/08		0.09						12/4/07		0.05						6/18/08		0.05		73		31		0.3		0.32		0.44		55		1196																				7/2/08		0.055		73		38

		2/4/08		0.03						12/5/07		0.045						6/19/08		0.05		71		30		0.28		0.32		0.46		55		1196																				7/3/08		0.065		71		39

		2/5/08		0.04						12/6/07		0.05						6/20/08		0.05		73		28		0.28		0.32		0.46		55		1196																				7/7/08		0.055		75		38

		2/6/08		0.025						12/7/07		0.045						6/21/08		0.045		72		30		0.26		0.32		0.46		55		32																				7/8/08		0.05		72		40

		2/7/08		0.02						12/10/07		0.05						6/23/08		0.05		73		39		0.28		0.32		0.44		57		32																				7/9/08		0.06		73		39

		2/8/08		0.04						12/11/07		0.045						6/24/08		0.05		72		34		0.28		0.32		0.42		60		32																				7/10/08		0.06		74		39

		2/9/08		0.05						12/12/07		0.045						6/25/08		0.04		73		36		0.28		0.32		0.44		60		32																				7/11/08		0.06		71		40

		2/11/08		0.02						12/13/07		0.045						6/26/08		0.04		72		34		0.28		0.32		0.44		60		32																				7/12/08		0.06		73		42

		2/12/08		0.035						12/14/07		0.045						6/27/08		0.04		71		38		0.32		0.32		0.44		60		32																				7/14/08		0.06		72		41

		2/13/08		0.025						12/17/07		0.045						6/30/08		0.04		73		37		0.3		0.32		0.44		60		32																				7/15/08		0.06		71		41

		2/14/08		0.025						12/18/07		0.04						7/1/08		0.035		71		38		0.28		0.32		0.44		60		32																				7/16/08		0.065		72		40

		2/15/08		0.03						12/19/07		0.04						7/2/08		0.07		72		38		0.3		0.32		0.46		60		32																				7/17/08		0.05		71		41

		2/19/08		0.03						12/20/07		0.03						7/3/08		0.08		72		38		0.32		0.32		0.48		57		32																				7/18/08		0.065		72		40

		2/20/08		0.05						12/21/07		0.04						7/7/08		0.06		73		40		0.28		0.32		0.44		57		32																				7/19/08		0.06		72		39

		2/21/08		0.03						12/26/07		0.04						7/8/08		0.06		72		38		0.28		0.32		0.42		60		32																				7/21/08		0.06		71		40

		2/22/08		0.03						12/27/07		0.04						7/9/08		0.06		73		39		0.28		0.32		0.42																								7/22/08		0.05		74		36

		2/23/08		0.035						12/28/07		0.04						7/10/08		0.07		72		40		0.32		0.32		0.48		55		1104																				7/23/08		0.07		72		39

		2/24/08		0.035						12/31/07		0.04						7/11/08		0.065		71		39		0.3		0.32		0.48		55		1104																				7/24/08		0.05		72		37

		2/25/08		0.03						1/2/08		0.04						7/12/08		0.08		73		40																														7/25/08		0.06		71		38

		2/26/08		0.035						1/3/08		0.04						7/14/08		0.08		72		40		0.3		0.32		0.48		61		1200																				7/26/08		0.07		71		38

		2/27/08		0.03						1/4/08		0.04						7/15/08		0.09		71		40		0.28		0.32		0.42		61		1200																				7/28/08		0.06		70		41

		2/28/08		0.03						1/7/08		0.025						7/16/08		0.09		72		39		0.28		0.32		0.42		61		1200																				7/29/08		0.06		70		41

		2/29/08		0.03						1/8/08		0.03						7/17/08		0.08		72		39		0.28		0.32		0.44		61		1200																				7/30/08		0.06		71		39

		3/1/08		0.035						1/9/08		0.03						7/18/08		0.09		72		38		0.3		0.32		0.48		61		1200																				7/31/08		0.065		71		40

		3/3/08		0.03						1/10/08		0.03						7/19/08		0.09		73		37																														8/1/08		0.06		73		36

		3/4/08		0.035						1/11/08		0.03						7/21/08		0.09		72		38		0.28		0.32		0.4		61		1200																				8/2/08		0.06		71		40

		3/5/08		0.043						1/14/08		0.025						7/22/08		0.08		73		37		0.24		0.32		0.42		61		1200																				8/4/08		0.06		72		40

		3/6/08		0.043						1/15/08		0.03						7/23/08		0.09		71		38		0.28		0.32		0.44		61		1200																				8/5/08		0.06		73		39

		3/7/08		0.043						1/16/08		0.03						7/24/08		0.09		72		36		0.26		0.32		0.46		61		1200																				8/6/08		0.06		71		41

		3/10/08		0.043						1/17/08		0.03						7/25/08		0.09		72		36		0.24		0.32		0.42		61		1200																				8/7/08		0.06		72		39

		3/11/08		0.042						1/18/08		0.025						7/26/08		0.09		71		37		0.28		0.32		0.46		61		1200																				8/8/08		0.05		72		40

		3/12/08		0.039						1/21/08		0.035						7/28/08		0.09		71		38		0.3		0.32		0.46		61		1200																				8/9/08		0.055		71		40

		3/13/08		0.03						1/22/08		0.03						7/29/08		0.06		70		40		0.3		0.32		0.44																								8/11/08		0.06		71		39

		3/14/08		0.041						1/23/08		0.035						7/30/08		0.07		71		38		0.3		0.32		0.48																								8/12/08		0.065		71		41

		3/17/08		0.047						1/24/08		0.03						7/31/08		0.075		71		38																														8/13/08		0.055		71		41

		3/18/08		0.048						1/25/08		0.035						8/1/08		0.07		72		37		0.3		0.32		0.48																								8/14/08		0.05		71		41

		3/19/08		0.047						1/28/08		0.035						8/2/08		0.07		72		38																														8/15/08		0.05		72		39

		3/20/08		0.042						1/29/08		0.035						8/4/08		0.07		73		37		0.28		0.32		0.44																								8/16/08		0.06		72		40

		3/21/08		0.043						1/30/08		0.025						8/5/08		0.06		73		37		0.28		0.34		0.48																								8/18/08		0.06		72		41

		3/22/08		0.045						1/31/08		0.03						8/6/08		0.07		71		38		0.28		0.32		0.48																								8/19/08		0.06		72		41

		3/24/08		0.043						2/1/08		0.03						8/7/08		0.06		71		38		0.32		0.32		0.48																								8/20/08		0.06		71		40

		3/25/08		0.045						2/4/08		0.035						8/8/08		0.06		72		38		0.26		0.32		0.44																								8/21/08		0.05		73		44

		3/26/08		0.043						2/5/08		0.025						8/9/08		0.06		71		40																														8/22/08		0.05		72		40

		3/27/08		0.04						2/6/08		0.035						8/11/08		0.07		71		38		0.28		0.32		0.44																								8/23/08		0.05		72		41

		3/28/08		0.04						2/7/08		0.025						8/12/08		0.07		71		40		0.28		0.32		0.44																								8/25/08		0.06		71		40

		3/31/08		0.045						2/8/08		0.02						8/13/08		0.065		71		40		0.28		0.3		0.46																								8/26/08		0.06		70		39

		4/1/08		0.045						2/9/08		0.02						8/14/08		0.05		71		39		0.26		0.32		0.42																								8/27/08		0.05		71		40

		4/2/08		0.045						2/14/08		0.035						8/15/08		0.06		71		38		0.26		0.32		0.42																								8/28/08		0.055		71		40

		4/3/08		0.04						2/15/08		0.033						8/16/08		0.06		71		40																														8/29/08		0.055		72		39

		4/4/08		0.045						2/19/08		0.036						8/18/08		0.065		71		41		0.26		0.32		0.42																								9/2/08		0.055		69		32

		4/5/08		0.045						2/20/08		0.037						8/19/08		0.06		72		40		0.28		0.32		0.44																								9/3/08		0.055		72		39

		4/7/08		0.045						2/21/08		0.037						8/20/08		0.06		71		31		0.26		0.32		0.42																								9/4/08		0.055		70		38

		4/8/08		0.04						2/22/08		0.034						8/21/08		0.05		73		42		0.28		0.32		0.48																								9/5/08		0.06		71		36

		4/9/08		0.04						2/25/08		0.044						8/22/08		0.06		71		38		0.24		0.32		0.44																								9/6/08		0.06		71		39

		4/10/08		0.04						2/26/08		0.043						8/23/08		0.06		72		40																														9/8/08		0.06		74		38

		4/11/08		0.045						2/27/08		0.043						8/25/08		0.06		71		40		0.26		0.32		0.46																								9/9/08		0.06		72		40

		4/14/08		0.045						2/28/08		0.044						8/26/08		0.06		70		38		0.26		0.32		0.44																								9/10/08		0.06		72		40

		4/15/08		0.04						2/29/08		0.046						8/27/08		0.05		71		38		0.26		0.32		0.44																								9/11/08		0.06		71		41

		4/16/08		0.04						3/3/08		0.045						8/28/08		0.05		71		38		0.26		0.3		0.44																								9/12/08		0.06		70		40

		4/17/08		0.04						3/4/08		0.044						8/29/08		0.065		72		38		0.28		0.3		0.44																								9/13/08		0.06		70		41

		4/18/08		0.04						3/5/08		0.039						9/2/08		0.06		69		31		0.24		0.32		0.42																								9/15/08		0.06		70		40

		4/19/08		0.05						3/6/08		0.039						9/3/08		0.06		72		40		0.28		0.32		0.44																								9/16/08		0.06		71		40

		4/21/08		0.05						3/7/08		0.038						9/4/08		0.06		70		37		0.26		0.32		0.44																								9/17/08		0.06		70		30

		4/22/08		0.045						3/10/08		0.037						9/5/08		0.06		70		36		0.26		0.32		0.44																								9/18/08		0.06		71		37

		4/23/08		0.04						3/11/08		0.04						9/6/08		0.06		70		38																														9/19/08		0.06		72		43

		4/24/08		0.04						3/12/08		0.036						9/8/08		0.06		72		41		0.24		0.32		0.42																								9/20/08		0.06		72		42

		4/25/08		0.04						3/14/08		0.039						9/9/08		0.06		71		40		0.24		0.32		0.44																								9/22/08		0.06		71		39

		4/30/08		0.04						3/17/08		0.038						9/10/08		0.06		70		41		0.28		0.32		0.46																								9/23/08		0.065		72		37

		5/1/08		0.04						3/18/08		0.038						9/11/08		0.06		70		41		0.26		0.32		0.42																								9/24/08		0.055		70		33

		5/2/08		0.04						3/19/08		0.037						9/12/08		0.06		70		40		0.28		0.32		0.48																								9/25/08		0.06		72		32

		5/3/08		0.045						3/20/08		0.039						9/13/08		0.06		70		40																														9/26/08		0.06		72		43

		5/5/08		0.04						3/21/08		0.038						9/15/08		0.06		69		41		0.3		0.32		0.44																								9/27/08		0.06		70		37

		5/6/08		0.04						3/24/08		0.038						9/16/08		0.06		69		41		0.24		0.3		0.42																								9/29/08		0.06		71		40

		5/7/08		0.045						3/25/08		0.038						9/17/08		0.07		69		38		0.26		0.32		0.46																								9/30/08		0.06		75		33

		5/8/08		0.04						3/26/08		0.039						9/18/08		0.06		70		38		0.26		0.32		0.42

		5/9/08		0.04						3/27/08		0.045						9/19/08		0.06		73		42		0.26		0.32		0.42

		5/10/08		0.04						3/28/08		0.04						9/20/08		0.05		73		41

		5/12/08		0.04						3/31/08		0.04						9/22/08		0.06		71		38		0.24		0.32		0.44

		5/13/08		0.04						4/1/08		0.04						9/23/08		0.065		71		37		0.26		0.32		0.44

		5/14/08		0.04						4/2/08		0.04						9/24/08		0.055		71		32		0.26		0.32		0.42

		5/15/08		0.04						4/3/08		0.035						9/25/08		0.06		71		32		0.28		0.32		0.48

		5/16/08		0.04						4/4/08		0.04						9/26/08		0.055		73		41		0.24		0.32		0.44

		5/19/08		0.04						4/5/08		0.035						9/27/08		0.06		71		35

		5/20/08		0.04						4/7/08		0.04						9/29/08		0.06		70		40		0.26		0.32		0.44

		5/21/08		0.04						4/8/08		0.04						9/30/08		0.05		71		36		0.24		0.32		0.44

		5/22/08		0.04						4/9/08		0.035						10/1/08								0.24		0.32		0.44

		5/23/08		0.04						4/10/08		0.04						10/2/08								0.24		0.32		0.44

		5/27/08		0.04						4/11/08		0.04

		5/28/08		0.04						4/14/08		0.04

		5/29/08		0.05						4/15/08		0.04

		5/30/08		0.04						4/16/08		0.04

		5/31/08		0.045						4/17/08		0.04

		6/2/08		0.04						4/18/08		0.035

		6/3/08		0.04						4/19/08		0.05

		6/4/08		0.04						4/21/08		0.05

		6/5/08		0.04						4/22/08		0.04

		6/6/08		0.04						4/23/08		0.04

		6/9/08		0.04						4/24/08		0.04

		6/10/08		0.04						4/25/08		0.04

		6/11/08		0.04						4/30/08		0.04

		6/12/08		0.04						5/1/08		0.04

		6/13/08		0.04						5/2/08		0.04

		6/16/08		0.04						5/3/08		0.04

		6/17/08		0.04						5/5/08		0.04

		6/18/08		0.04						5/6/08		0.04

		6/19/08		0.04						5/7/08		0.04

		6/20/08		0.04						5/8/08		0.04

		6/21/08		0.035						5/9/08		0.04

		6/23/08		0.035						5/10/08		0.04

		6/24/08		0.04						5/12/08		0.04

		6/25/08		0.035						5/13/08		0.04

		6/26/08		0.035						5/14/08		0.04

		6/27/08		0.035						5/15/08		0.04

		6/30/08		0.035						5/16/08		0.04

		7/1/08		0.03						5/19/08		0.04

		7/2/08		0.03						5/20/08		0.04

		7/3/08		0.035						5/21/08		0.04

		7/7/08		0.03						5/22/08		0.04

		7/8/08		0.03						5/23/08		0.04

		7/9/08		0.035						5/27/08		0.04

		7/10/08		0.035						5/28/08		0.04

		7/11/08		0.035						5/29/08		0.04

		7/12/08		0.03						5/30/08		0.04

		7/14/08		0.025						6/2/08		0.04

		7/15/08		0.03						6/3/08		0.035

		7/16/08		0.03						6/4/08		0.035

		7/17/08		0.03						6/5/08		0.035

		7/18/08		0.04						6/6/08		0.035

		7/19/08		0.03						6/9/08		0.035

		7/21/08		0.03						6/10/08		0.035

		7/22/08		0.03						6/11/08		0.035

		7/23/08		0.02						6/12/08		0.035

		7/24/08		0.025						6/13/08		0.04

		7/25/08		0.01						6/16/08		0.035

		7/26/08		0.01						6/17/08		0.045

		7/28/08		0.01						6/18/08		0.045

		7/29/08		0.03						6/19/08		0.045

		7/30/08		0.01						6/20/08		0.035

		7/31/08		0.015						6/21/08		0.035

		8/1/08		0.025						6/23/08		0.035

		8/2/08		0.03						6/24/08		0.045

		8/4/08		0.03						6/25/08		0.035

		8/5/08		0.03						6/26/08		0.035

		8/6/08		0.04						6/27/08		0.035

		8/7/08		0.035						6/30/08		0.035

		8/8/08		0.03						7/1/08		0.04

		8/9/08		0.03						7/2/08		0.04

		8/11/08		0.035						7/3/08		0.04

		8/12/08		0.035						7/7/08		0.04

		8/13/08		0.035						7/8/08		0.04

		8/14/08		0.03						7/9/08		0.04

		8/15/08		0.03						7/10/08		0.04

		8/16/08		0.03						7/11/08		0.04

		8/18/08		0.03						7/12/08		0.04

		8/19/08		0.04						7/14/08		0.04

		8/20/08		0.03						7/15/08		0.04

		8/21/08		0.03						7/16/08		0.04

		8/22/08		0.03						7/17/08		0.04

		8/23/08		0.03						7/18/08		0.04

		8/25/08		0.03						7/19/08		0.04

		8/26/08		0.03						7/21/08		0.04

		8/27/08		0.03						7/22/08		0.04

		8/28/08		0.03						7/23/08		0.04

		8/29/08		0.03						7/24/08		0.04

		9/2/08		0.03						7/25/08		0.04

		9/3/08		0.03						7/26/08		0.04

		9/4/08		0.03						7/28/08		0.04

		9/5/08		0.03						7/29/08		0.04

		9/6/08		0.03						7/30/08		0.04

		9/8/08		0.03						7/31/08		0.04

		9/9/08		0.03						8/1/08		0.045

		9/10/08		0.03						8/2/08		0.04

		9/11/08		0.03						8/4/08		0.04

		9/12/08		0.03						8/5/08		0.04

		9/13/08		0.03						8/6/08		0.05

		9/15/08		0.035						8/7/08		0.04

		9/16/08		0.03						8/8/08		0.04

		9/17/08		0.03						8/9/08		0.04

		9/18/08		0.03						8/11/08		0.04

		9/19/08		0.03						8/12/08		0.04

		9/20/08		0.03						8/13/08		0.04

		9/22/08		0.03						8/14/08		0.04

		9/23/08		0.03						8/15/08		0.04

		9/24/08		0.025						8/16/08		0.04

		9/25/08		0.03						8/18/08		0.04

		9/26/08		0.03						8/19/08		0.04

		9/27/08		0.03						8/20/08		0.04

		9/29/08		0.03						8/21/08		0.04

		9/30/08		0.03						8/22/08		0.04

		10/1/08		0.03						8/23/08		0.04

		10/2/08		0.03						8/25/08		0.04

		10/3/08		0.03						8/26/08		0.04

		10/4/08		0.03						8/27/08		0.04

		10/6/08		0.03						8/28/08		0.04

		10/7/08		0.04						8/29/08		0.04

		10/8/08		0.03						9/2/08		0.04

		10/9/08		0.03						9/3/08		0.04

		10/10/08		0.03						9/4/08		0.04

		10/11/08		0.03						9/5/08		0.04

		10/13/08		0.03						9/6/08		0.04

		10/14/08		0.03						9/8/08		0.04

		10/15/08		0.03						9/9/08		0.04

		10/16/08		0.04						9/10/08		0.04

		10/17/08		0.03						9/11/08		0.04

		10/18/08		0.03						9/12/08		0.04

		10/20/08		0.03						9/13/08		0.04

		10/21/08		0.03						9/15/08		0.04

		10/22/08		0.03						9/16/08		0.04

		10/23/08		0.03						9/17/08		0.04

		10/24/08		0.03						9/18/08		0.04

		10/25/08		0.03						9/19/08		0.04

		10/27/08		0.03						9/20/08		0.04

		10/28/08		0.03						9/22/08		0.04

		10/29/08		0.03						9/23/08		0.045

		10/30/08		0.03						9/24/08		0.045

		10/31/08		0.03						9/25/08		0.045

		11/3/08		0.03						9/26/08		0.04

		11/4/08		0.03						9/27/08		0.04

		11/5/08		0.03						9/29/08		0.04

		11/6/08		0.04						9/30/08		0.04

		11/7/08		0.035						10/1/08		0.04

		11/8/08		0.04						10/2/08		0.04

		11/10/08		0.04						10/3/08		0.04

		11/11/08		0.04						10/4/08		0.04

		11/12/08		0.04						10/6/08		0.04

		11/13/08		0.04						10/7/08		0.05

		11/14/08		0.04						10/8/08		0.045

		11/15/08		0.035						10/9/08		0.04

		11/17/08		0.04						10/10/08		0.04

		11/18/08		0.05						10/11/08		0.04

		11/19/08		0.04						10/13/08		0.045

		11/20/08		0.04						10/14/08		0.04

		11/21/08		0.035						10/15/08		0.045

		11/22/08		0.03						10/16/08		0.04

		11/24/08		0.03						10/17/08		0.04

		11/25/08		0.03						10/18/08		0.04

		11/26/08		0.03						10/20/08		0.04

		12/1/08		0.03						10/21/08		0.04

		12/2/08		0.04						10/22/08		0.04

		12/3/08		0.03						10/23/08		0.04

		12/4/08		0.03						10/24/08		0.04

		12/5/08		0.03						10/25/08		0.04

		12/6/08		0.03						10/27/08		0.04

		12/8/08		0.03						10/28/08		0.04

		12/9/08		0.04						10/29/08		0.04

		12/10/08		0.03						10/30/08		0.04

		12/11/08		0.03						10/31/08		0.04

		12/12/08		0.035						11/3/08		0.04

		12/13/08		0.03						11/4/08		0.04

		12/15/08		0.04						11/5/08		0.05

		12/16/08		0.03						11/6/08		0.04

		12/17/08		0.03						11/7/08		0.04

		12/18/08		0.03						11/8/08		0.045

		12/19/08		0.04						11/10/08		0.04

		1/12/09		0.035						11/11/08		0.04

		1/13/09		0.02						11/12/08		0.04

		1/14/09		0.035						11/13/08		0.04

										11/14/08		0.04

										11/15/08		0.04

										11/17/08		0.04

										11/18/08		0.04

										11/19/08		0.04

										11/20/08		0.045

										11/21/08		0.045

										11/22/08		0.04

										11/24/08		0.04

										11/25/08		0.04

										11/26/08		0.04

										12/1/08		0.04





CER Pressure

		



Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)

R&D Bio-Safety Cabinet South (left axis)

Date

Diff. Pressure (Water Column In.)

Mfg Bio-Safety Cabinet South CFM

Figure 7.  CER2 Bio-Safety Cabinet Differential Pressure Daily Run Chart



Conf-Rel

		



Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

R&D Bio-Safety Cabinet South (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)

Date

Diff. Pressure (Water Column In.)

Mfg Bio-Safety Cabinet (cfm)

Figure 8.  Bio-Safety Cabinet Differential Pressure - Monthly Average



Temp-Humid

		



CER1

CER Change Room

CER2

CER3

CER Alert Level

CER Action Level

Date

Diff. Pressure (Water Column In.)

Figure 5.  CER Differential Pressure Daily Run Chart



Sheet1

		



CER1

CER Change Room

CER 2

CER 3

CER Alert Level

CER Action Level

Date

Diff. Pressure (Water Column In.)

Figure 6.  CER Differential Pressure - Monthly Average



		TO:		DCN 0273 File

		FROM:		Andy Pearson

		DATE:		3/3/07

		RE:		Confidence and Reliability Levels for CER Monitoring

		The table below shows 95/95, and 95/99 confidence/reliability levels for  CER and Change Room

		monitoring carried out from Feb 06 to Feb 07.

		Recommended action and alert levels correspond to worst case 95/95 (alert) and 95/99 (action) values.

						95/95 Limit		Recommended Alert Level		95/99 Limit		95/99 Limit		Recommended Action Level

		Airstrips (utl)		CER1		17		35		21		21		45

				CER2		15				20		20

				CER3		34				43		43

		Contact Plates (utl)		CER1		5		6		6		6		7

				CER2		4				5		5

				CER3		6				7		7

		0.5um Particle Counts (utl)		CER1		1092		3800		1324		1324		4500

				CER3		3797				4549		4549

				CER2		1232		1250		1495		1495		1500

		5.0um Particle Counts (utl)		CER1		159		410		200		200		500

				CER3		410				497		497

				CER2		91		90		107		107		105

		Pressure Differential (ltl)		CER1		0.011		0.030		0.003		0.003		0.005

				CER1/2 Chg Rm		0.021				0.013		0.013

				CER2		-0.021				-0.045		-0.045

				CER3		0.040				0.035		0.035

		Andy Pearson

		Sr.Quality Engineer





		CER2								CER1								CER3								QA

		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 2 Temperature(°F)		CER 2 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 1 Temperature(°F)		CER 1 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 3 Temperature(°F)		CER 3 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		QA Temperature(°F)		QA Humidity(%)

		29-Aug-07		16:07:10		75.81		46.5		29-Aug-07		16:06:20		76.4		48		29-Aug-07		16:07:53		75.81		74		9-Oct-07		16:25:59		78.2		33

		29-Aug-07		18:07:10		74.01		40.5		29-Aug-07		18:06:20		70.41		41.5		29-Aug-07		18:07:53		74.6		41.5		9-Oct-07		18:25:59		75.81		35.5

		29-Aug-07		20:07:10		74.6		40.5		29-Aug-07		20:06:20		71.6		43.5		29-Aug-07		20:07:53		73.4		43		9-Oct-07		20:25:59		75.2		34.5

		29-Aug-07		22:07:10		75.81		40.5		29-Aug-07		22:06:20		71.6		46.5		29-Aug-07		22:07:53		74.6		42		9-Oct-07		22:25:59		74.6		35

		30-Aug-07		0:07:10		75.81		40.5		30-Aug-07		0:06:20		71.6		47.5		30-Aug-07		0:07:53		75.2		41.5		10-Oct-07		0:25:59		73.4		36

		30-Aug-07		2:07:10		75.81		41		30-Aug-07		2:06:20		71		49		30-Aug-07		2:07:53		75.81		41.5		10-Oct-07		2:25:59		72.8		37

		30-Aug-07		4:07:10		75.2		42.5		30-Aug-07		4:06:20		71		51		30-Aug-07		4:07:53		75.2		41.5		10-Oct-07		4:25:59		72.21		38

		30-Aug-07		6:07:10		75.81		41		30-Aug-07		6:06:20		71.6		46.5		30-Aug-07		6:07:53		75.2		42		10-Oct-07		6:25:59		72.21		39

		30-Aug-07		8:07:10		75.81		45.5		30-Aug-07		8:06:20		72.21		55.5		30-Aug-07		8:07:53		75.2		44		10-Oct-07		8:25:59		71.6		41.5

		30-Aug-07		10:07:10		74.6		43.5		30-Aug-07		10:06:20		72.21		41.5		30-Aug-07		10:07:53		74.6		45		10-Oct-07		10:25:59		72.8		42.5

		30-Aug-07		12:07:10		74.6		43.5		30-Aug-07		12:06:20		71.6		46		30-Aug-07		12:07:53		72.8		45.5		10-Oct-07		12:25:59		74.01		42.5

		30-Aug-07		14:07:10		74.6		43		30-Aug-07		14:06:20		72.21		43		30-Aug-07		14:07:53		72.21		44.5		10-Oct-07		14:25:59		75.2		43

		30-Aug-07		16:07:10		75.2		43.5		30-Aug-07		16:06:20		72.21		43.5		30-Aug-07		16:07:53		72.8		44.5		10-Oct-07		16:25:59		75.2		42

		30-Aug-07		18:07:10		75.2		45		30-Aug-07		18:06:20		70.41		49.5		30-Aug-07		18:07:53		71.6		46		10-Oct-07		18:25:59		75.2		41

		30-Aug-07		20:07:10		75.2		45.5		30-Aug-07		20:06:20		71.6		52		30-Aug-07		20:07:53		75.81		45		10-Oct-07		20:25:59		74.01		42.5

		30-Aug-07		22:07:10		76.4		45		30-Aug-07		22:06:20		71		53.5		30-Aug-07		22:07:53		75.2		45		10-Oct-07		22:25:59		73.4		43.5

		31-Aug-07		0:07:10		76.4		44.5		31-Aug-07		0:06:20		71		53.5		31-Aug-07		0:07:53		75.2		44.5		11-Oct-07		0:25:59		72.8		44.5

		31-Aug-07		2:07:10		75.81		44.5		31-Aug-07		2:06:20		71.6		53		31-Aug-07		2:07:53		75.2		45.5		11-Oct-07		2:25:59		72.21		45

		31-Aug-07		4:07:10		75.81		45		31-Aug-07		4:06:20		71.6		53		31-Aug-07		4:07:53		72.8		41.5		11-Oct-07		4:25:59		71.6		45.5

		31-Aug-07		6:07:10		75.81		45.5		31-Aug-07		6:06:20		72.21		54		31-Aug-07		6:07:53		71		54.5		11-Oct-07		6:25:59		72.21		45

		31-Aug-07		8:07:10		75.2		44		31-Aug-07		8:06:20		72.21		43.5		31-Aug-07		8:07:53		71.6		50.5		11-Oct-07		8:25:59		71.6		46.5

		31-Aug-07		10:07:10		74.6		45.5		31-Aug-07		10:06:20		72.21		49.5		31-Aug-07		10:07:53		72.21		44.5		11-Oct-07		10:25:59		72.8		48.5

		31-Aug-07		12:07:10		74.6		49.5		31-Aug-07		12:06:20		71.6		60.5		31-Aug-07		12:07:53		72.21		45		11-Oct-07		12:25:59		74.6		44.5

		31-Aug-07		14:07:10		74.6		45.5		31-Aug-07		14:06:20		71.6		44		31-Aug-07		14:07:53		72.8		47		11-Oct-07		14:25:59		75.81		42.5

		31-Aug-07		16:07:10		74.6		48		31-Aug-07		16:06:20		71.6		56.5		31-Aug-07		16:07:53		72.8		43.5		11-Oct-07		16:25:59		76.4		42.5

		31-Aug-07		18:07:10		75.2		46.5		31-Aug-07		18:06:20		70.41		54.5		31-Aug-07		18:07:53		71		50		11-Oct-07		18:25:59		76.4		41

		31-Aug-07		20:07:10		75.2		46		31-Aug-07		20:06:20		71.6		53		31-Aug-07		20:07:53		74.6		50		11-Oct-07		20:25:59		74.6		41.5

		31-Aug-07		22:07:10		76.4		44		31-Aug-07		22:06:20		71.6		48.5		31-Aug-07		22:07:53		75.2		47		11-Oct-07		22:25:59		74.6		41

		1-Sep-07		0:07:10		76.4		42.5		1-Sep-07		0:06:20		71.6		46.5		1-Sep-07		0:07:53		75.2		45.5		12-Oct-07		0:25:59		73.4		41

		1-Sep-07		2:07:10		76.4		44		1-Sep-07		2:06:20		71.6		53		1-Sep-07		2:07:53		74.6		45.5		12-Oct-07		2:25:59		71.6		41

		1-Sep-07		4:07:10		76.4		44		1-Sep-07		4:06:20		71.6		53		1-Sep-07		4:07:53		72.8		50		12-Oct-07		4:25:59		71		41.5

		1-Sep-07		6:07:10		76.4		45		1-Sep-07		6:06:20		73.4		56.5		1-Sep-07		6:07:53		71.6		45		12-Oct-07		6:25:59		70.41		41.5

		1-Sep-07		8:07:10		75.2		42.5		1-Sep-07		8:06:20		72.21		41		1-Sep-07		8:07:53		71.6		53		12-Oct-07		8:25:59		69.8		41.5

		1-Sep-07		10:07:10		74.6		43.5		1-Sep-07		10:06:20		71.6		42		1-Sep-07		10:07:53		72.21		43.5		12-Oct-07		10:25:59		71.6		44.5

		1-Sep-07		12:07:10		74.6		51.5		1-Sep-07		12:06:20		70.41		64		1-Sep-07		12:07:53		71.6		45.5		12-Oct-07		12:25:59		74.6		43.5

		1-Sep-07		14:07:10		74.6		52		1-Sep-07		14:06:20		70.41		64.5		1-Sep-07		14:07:53		71		50.5		12-Oct-07		14:25:59		75.2		42.5

		1-Sep-07		16:07:10		74.6		46.5		1-Sep-07		16:06:20		70.41		52.5		1-Sep-07		16:07:53		71		57.5		12-Oct-07		16:25:59		75.2		42.5

		1-Sep-07		18:07:10		74.6		45.5		1-Sep-07		18:06:20		70.41		50.5		1-Sep-07		18:07:53		71		58.5		12-Oct-07		18:25:59		74.6		40

		1-Sep-07		20:07:10		74.6		49.5		1-Sep-07		20:06:20		71		56		1-Sep-07		20:07:53		71		55.5		12-Oct-07		20:25:59		74.01		40.5

		1-Sep-07		22:07:10		75.2		47		1-Sep-07		22:06:20		71		56		1-Sep-07		22:07:53		72.21		50.5		12-Oct-07		22:25:59		74.01		40

		2-Sep-07		0:07:10		75.2		45		2-Sep-07		0:06:20		71.6		52.5		2-Sep-07		0:07:53		72.21		50		13-Oct-07		0:25:59		72.8		40.5

		2-Sep-07		2:07:10		75.2		44.5		2-Sep-07		2:06:20		71		51		2-Sep-07		2:07:53		71.6		50		13-Oct-07		2:25:59		71.6		41

		2-Sep-07		4:07:10		74.6		44		2-Sep-07		4:06:20		70.41		51.5		2-Sep-07		4:07:53		70.41		49.5		13-Oct-07		4:25:59		71		42.5

		2-Sep-07		6:07:10		74.01		41.5		2-Sep-07		6:06:20		71		45.5		2-Sep-07		6:07:53		69.2		48.5		13-Oct-07		6:25:59		71.6		43

		2-Sep-07		8:07:10		73.4		44		2-Sep-07		8:06:20		69.8		51		2-Sep-07		8:07:53		69.2		51		13-Oct-07		8:25:59		71		46

		2-Sep-07		10:07:10		74.01		48.5		2-Sep-07		10:06:20		70.41		57.5		2-Sep-07		10:07:53		71		48.5		13-Oct-07		10:25:59		72.21		47.5

		2-Sep-07		12:07:10		74.6		49.5		2-Sep-07		12:06:20		70.41		59.5		2-Sep-07		12:07:53		71		53		13-Oct-07		12:25:59		72.8		47

		2-Sep-07		14:07:10		75.81		49.5		2-Sep-07		14:06:20		70.41		60.5		2-Sep-07		14:07:53		71		60		13-Oct-07		14:25:59		72.21		47.5

		2-Sep-07		16:07:10		76.4		43.5		2-Sep-07		16:06:20		70.41		47.5		2-Sep-07		16:07:53		71		46.5		13-Oct-07		16:25:59		74.01		47

		2-Sep-07		18:07:10		76.4		46.5		2-Sep-07		18:06:20		69.8		55.5		2-Sep-07		18:07:53		71		58		13-Oct-07		18:25:59		74.6		44.5

		2-Sep-07		20:07:10		77		44		2-Sep-07		20:06:20		71		52.5		2-Sep-07		20:07:53		74.01		47		13-Oct-07		20:25:59		72.8		45.5

		2-Sep-07		22:07:10		77		41.5		2-Sep-07		22:06:20		71.6		51		2-Sep-07		22:07:53		74.6		44.5		13-Oct-07		22:25:59		71.6		45

		3-Sep-07		0:07:10		76.4		41		3-Sep-07		0:06:20		71		50.5		3-Sep-07		0:07:53		74.01		44.5		14-Oct-07		0:25:59		71		45

		3-Sep-07		2:07:10		75.81		40		3-Sep-07		2:06:20		71		44		3-Sep-07		2:07:53		72.21		45.5		14-Oct-07		2:25:59		69.8		43.5

		3-Sep-07		4:07:10		75.2		39		3-Sep-07		4:06:20		71		41.5		3-Sep-07		4:07:53		71		46.5		14-Oct-07		4:25:59		69.2		43

		3-Sep-07		6:07:10		75.2		40		3-Sep-07		6:06:20		71.6		46		3-Sep-07		6:07:53		69.2		47.5		14-Oct-07		6:25:59		69.2		42.5

		3-Sep-07		8:07:10		74.01		42		3-Sep-07		8:06:20		69.8		49		3-Sep-07		8:07:53		68.61		49.5		14-Oct-07		8:25:59		69.2		41

		3-Sep-07		10:07:10		74.01		43		3-Sep-07		10:06:20		70.41		48		3-Sep-07		10:07:53		70.41		52		14-Oct-07		10:25:59		71		44

		3-Sep-07		12:07:10		74.6		41.5		3-Sep-07		12:06:20		70.41		43.5		3-Sep-07		12:07:53		71		43.5		14-Oct-07		12:25:59		72.21		45

		3-Sep-07		14:07:10		75.2		43		3-Sep-07		14:06:20		70.41		47		3-Sep-07		14:07:53		71.6		52		14-Oct-07		14:25:59		74.01		44.5

		3-Sep-07		16:07:10		75.81		44.5		3-Sep-07		16:06:20		69.8		49.5		3-Sep-07		16:07:53		71.6		52		14-Oct-07		16:25:59		75.2		44.5

		3-Sep-07		18:07:10		76.4		40.5		3-Sep-07		18:06:20		70.41		47		3-Sep-07		18:07:53		71		45		14-Oct-07		18:25:59		75.81		44

		3-Sep-07		20:07:10		77.61		40		3-Sep-07		20:06:20		71.6		45.5		3-Sep-07		20:07:53		75.81		42		14-Oct-07		20:25:59		74.6		44.5

		3-Sep-07		22:07:10		77		41		3-Sep-07		22:06:20		71.6		50.5		3-Sep-07		22:07:53		74.6		43.5		14-Oct-07		22:25:59		73.4		45

		4-Sep-07		0:07:10		76.4		40.5		4-Sep-07		0:06:20		71		50		4-Sep-07		0:07:53		74.6		43.5		15-Oct-07		0:25:59		72.8		45.5

		4-Sep-07		2:07:10		75.81		40		4-Sep-07		2:06:20		71		49.5		4-Sep-07		2:07:53		72.8		44		15-Oct-07		2:25:59		72.21		46

		4-Sep-07		4:07:10		75.81		39.5		4-Sep-07		4:06:20		71.6		47		4-Sep-07		4:07:53		71.6		45		15-Oct-07		4:25:59		71.6		46

		4-Sep-07		6:07:10		74.6		40		4-Sep-07		6:06:20		71		47.5		4-Sep-07		6:07:53		69.8		46.5		15-Oct-07		6:25:59		71		46.5

		4-Sep-07		8:07:10		74.01		39.5		4-Sep-07		8:06:20		70.41		42		4-Sep-07		8:07:53		69.8		48.5		15-Oct-07		8:25:59		70.41		47

		4-Sep-07		10:07:10		74.01		45.5		4-Sep-07		10:06:20		69.8		53.5		4-Sep-07		10:07:53		71		52		15-Oct-07		10:25:59		69.8		47.5

		4-Sep-07		12:07:10		74.01		48		4-Sep-07		12:06:20		69.8		55		4-Sep-07		12:07:53		71		45.5		15-Oct-07		12:25:59		70.41		48.5

		4-Sep-07		14:07:10		74.01		49		4-Sep-07		14:06:20		70.41		52		4-Sep-07		14:07:53		71		58.5		15-Oct-07		14:25:59		71.6		49

		4-Sep-07		16:07:10		74.6		47.5		4-Sep-07		16:06:20		70.41		50		4-Sep-07		16:07:53		71		49		15-Oct-07		16:25:59		73.4		48

		4-Sep-07		18:07:10		74.6		47.5		4-Sep-07		18:06:20		70.41		50		4-Sep-07		18:07:53		71		49.5		15-Oct-07		18:25:59		74.6		45.5

		4-Sep-07		20:07:10		75.2		50		4-Sep-07		20:06:20		71		58.5		4-Sep-07		20:07:53		71.6		55.5		15-Oct-07		20:25:59		72.8		46

		4-Sep-07		22:07:10		75.81		47.5		4-Sep-07		22:06:20		71.6		56		4-Sep-07		22:07:53		74.01		50		15-Oct-07		22:25:59		71.6		46

		5-Sep-07		0:07:10		75.81		46.5		5-Sep-07		0:06:20		71		56.5		5-Sep-07		0:07:53		74.01		49.5		16-Oct-07		0:25:59		71		46

		5-Sep-07		2:07:10		75.81		44.5		5-Sep-07		2:06:20		71		47.5		5-Sep-07		2:07:53		72.8		50.5		16-Oct-07		2:25:59		70.41		46.5

		5-Sep-07		4:07:10		75.2		45.5		5-Sep-07		4:06:20		71		55		5-Sep-07		4:07:53		71.6		49		16-Oct-07		4:25:59		69.8		46

		5-Sep-07		6:07:10		75.2		47		5-Sep-07		6:06:20		71.6		55		5-Sep-07		6:07:53		70.41		48		16-Oct-07		6:25:59		70.41		46.5

		5-Sep-07		8:07:10		75.2		45		5-Sep-07		8:06:20		72.21		45.5		5-Sep-07		8:07:53		71		53		16-Oct-07		8:25:59		69.8		47.5

		5-Sep-07		10:07:10		74.6		51.5		5-Sep-07		10:06:20		72.21		55		5-Sep-07		10:07:53		72.8		46.5		16-Oct-07		10:25:59		71		49.5

		5-Sep-07		12:07:10		74.01		50.5		5-Sep-07		12:06:20		71		56		5-Sep-07		12:07:53		72.21		57.5		16-Oct-07		12:25:59		72.21		52

		5-Sep-07		14:07:10		74.01		48		5-Sep-07		14:06:20		71.6		54.5		5-Sep-07		14:07:53		72.21		54		16-Oct-07		14:25:59		73.4		52.5

		5-Sep-07		16:07:10		74.01		49		5-Sep-07		16:06:20		71		54		5-Sep-07		16:07:53		72.21		51		16-Oct-07		16:25:59		75.2		47.5

		5-Sep-07		18:07:10		74.6		49		5-Sep-07		18:06:20		70.41		60		5-Sep-07		18:07:53		71.6		48.5		16-Oct-07		18:25:59		75.81		47.5

		5-Sep-07		20:07:10		74.6		48		5-Sep-07		20:06:20		71.6		55		5-Sep-07		20:07:53		71		58		16-Oct-07		20:25:59		74.01		48.5

		5-Sep-07		22:07:10		75.81		46.5		5-Sep-07		22:06:20		71		55.5		5-Sep-07		22:07:53		75.2		47		16-Oct-07		22:25:59		73.4		49

		6-Sep-07		0:07:10		75.81		43.5		6-Sep-07		0:06:20		71.6		50.5		6-Sep-07		0:07:53		74.6		47		17-Oct-07		0:25:59		72.21		49

		6-Sep-07		2:07:10		75.2		44.5		6-Sep-07		2:06:20		71		52.5		6-Sep-07		2:07:53		73.4		47		17-Oct-07		2:25:59		71		48

		6-Sep-07		4:07:10		75.2		43.5		6-Sep-07		4:06:20		71.6		51		6-Sep-07		4:07:53		72.21		48.5		17-Oct-07		4:25:59		70.41		47.5

		6-Sep-07		6:07:10		75.2		42.5		6-Sep-07		6:06:20		71.6		48.5		6-Sep-07		6:07:53		71		50.5		17-Oct-07		6:25:59		69.8		46

		6-Sep-07		8:07:10		75.2		45.5		6-Sep-07		8:06:20		72.21		52		6-Sep-07		8:07:53		71.6		48.5		17-Oct-07		8:25:59		69.2		46.5

		6-Sep-07		10:07:10		75.2		43.5		6-Sep-07		10:06:20		72.21		46		6-Sep-07		10:07:53		72.21		49.5		17-Oct-07		10:25:59		70.41		49

		6-Sep-07		12:07:10		74.6		41.5		6-Sep-07		12:06:20		71.6		42.5		6-Sep-07		12:07:53		72.21		52		17-Oct-07		12:25:59		71.6		51.5

		6-Sep-07		14:07:10		74.01		40		6-Sep-07		14:06:20		71.6		40.5		6-Sep-07		14:07:53		72.21		42		17-Oct-07		14:25:59		72.21		53

		6-Sep-07		16:07:10		74.6		40		6-Sep-07		16:06:20		71.6		43		6-Sep-07		16:07:53		72.21		40		17-Oct-07		16:25:59		72.8		54

		6-Sep-07		18:07:10		74.6		38		6-Sep-07		18:06:20		69.8		42		6-Sep-07		18:07:53		72.21		37.5		17-Oct-07		18:25:59		74.01		50.5

		6-Sep-07		20:07:10		75.2		38		6-Sep-07		20:06:20		71.6		43		6-Sep-07		20:07:53		75.2		39.5		17-Oct-07		20:25:59		72.21		48.5

		6-Sep-07		22:07:10		75.81		38.5		6-Sep-07		22:06:20		71.6		45.5		6-Sep-07		22:07:53		75.2		39.5		17-Oct-07		22:25:59		71		48

		7-Sep-07		0:07:10		75.81		39		7-Sep-07		0:06:20		71.6		46.5		7-Sep-07		0:07:53		75.2		39.5		18-Oct-07		0:25:59		70.41		47

		7-Sep-07		2:07:10		75.81		39		7-Sep-07		2:06:20		71.6		46		7-Sep-07		2:07:53		74.01		41		18-Oct-07		2:25:59		69.2		45.5

		7-Sep-07		4:07:10		75.2		39		7-Sep-07		4:06:20		71		46		7-Sep-07		4:07:53		72.21		37		18-Oct-07		4:25:59		68.61		45

		7-Sep-07		6:07:10		75.81		38		7-Sep-07		6:06:20		71.6		44		7-Sep-07		6:07:53		71		45.5		18-Oct-07		6:25:59		69.2		46

		7-Sep-07		8:07:10		75.81		41		7-Sep-07		8:06:20		71.6		50		7-Sep-07		8:07:53		71.6		39.5		18-Oct-07		8:25:59		69.2		47

		7-Sep-07		10:07:10		75.2		38.5		7-Sep-07		10:06:20		71.6		40.5		7-Sep-07		10:07:53		72.21		40		18-Oct-07		10:25:59		70.41		50

		7-Sep-07		12:07:10		74.6		40		7-Sep-07		12:06:20		71		42.5		7-Sep-07		12:07:53		72.21		51.5		18-Oct-07		12:25:59		72.8		48.5

		7-Sep-07		14:07:10		74.6		43		7-Sep-07		14:06:20		71.6		42		7-Sep-07		14:07:53		71.6		42.5		18-Oct-07		14:25:59		74.6		45

		7-Sep-07		16:07:10		75.81		46		7-Sep-07		16:06:20		71		61		7-Sep-07		16:07:53		71.6		44.5		18-Oct-07		16:25:59		75.81		43

		7-Sep-07		18:07:10		75.2		45.5		7-Sep-07		18:06:20		71		48		7-Sep-07		18:07:53		71		53.5		18-Oct-07		18:25:59		75.81		43

		7-Sep-07		20:07:10		75.81		49		7-Sep-07		20:06:20		71.6		57		7-Sep-07		20:07:53		71.6		55		18-Oct-07		20:25:59		74.6		43.5

		7-Sep-07		22:07:10		75.81		48.5		7-Sep-07		22:06:20		71.6		58		7-Sep-07		22:07:53		72.8		52		18-Oct-07		22:25:59		73.4		44

		8-Sep-07		0:07:10		75.2		47.5		8-Sep-07		0:06:20		71		56.5		8-Sep-07		0:07:53		72.8		51		19-Oct-07		0:25:59		72.21		44.5

		8-Sep-07		2:07:10		75.2		47		8-Sep-07		2:06:20		71.6		55		8-Sep-07		2:07:53		72.21		51.5		19-Oct-07		2:25:59		71		44.5

		8-Sep-07		4:07:10		75.2		47		8-Sep-07		4:06:20		71		55.5		8-Sep-07		4:07:53		71.6		51		19-Oct-07		4:25:59		70.41		45

		8-Sep-07		6:07:10		75.81		47		8-Sep-07		6:06:20		71.6		54.5		8-Sep-07		6:07:53		71		55		19-Oct-07		6:25:59		70.41		45.5

		8-Sep-07		8:07:10		75.2		47.5		8-Sep-07		8:06:20		72.21		56		8-Sep-07		8:07:53		71.6		57		19-Oct-07		8:25:59		70.41		46.5

		8-Sep-07		10:07:10		74.6		44.5		8-Sep-07		10:06:20		72.21		45		8-Sep-07		10:07:53		72.21		46.5		19-Oct-07		10:25:59		71.6		47.5

		8-Sep-07		12:07:10		74.6		50.5		8-Sep-07		12:06:20		71		57		8-Sep-07		12:07:53		72.21		45		19-Oct-07		12:25:59		73.4		46

		8-Sep-07		14:07:10		74.01		46		8-Sep-07		14:06:20		72.21		46		8-Sep-07		14:07:53		71.6		46.5		19-Oct-07		14:25:59		75.2		45.5

		8-Sep-07		16:07:10		74.01		53		8-Sep-07		16:06:20		71		67		8-Sep-07		16:07:53		71.6		50.5		19-Oct-07		16:25:59		74.6		49

		8-Sep-07		18:07:10		74.01		53		8-Sep-07		18:06:20		70.41		63		8-Sep-07		18:07:53		71		53.5		19-Oct-07		18:25:59		74.6		50.5

		8-Sep-07		20:07:10		74.6		51		8-Sep-07		20:06:20		71		58		8-Sep-07		20:07:53		70.41		57		19-Oct-07		20:25:59		74.01		51.5

		8-Sep-07		22:07:10		74.6		48		8-Sep-07		22:06:20		71		55		8-Sep-07		22:07:53		70.41		54		19-Oct-07		22:25:59		74.01		51

		9-Sep-07		0:07:10		74.6		45		9-Sep-07		0:06:20		71		46		9-Sep-07		0:07:53		69.8		53		20-Oct-07		0:25:59		73.4		51.5

		9-Sep-07		2:07:10		74.01		45.5		9-Sep-07		2:06:20		71		52.5		9-Sep-07		2:07:53		69.2		52.5		20-Oct-07		2:25:59		72.8		52.5

		9-Sep-07		4:07:10		74.01		46.5		9-Sep-07		4:06:20		71		53.5		9-Sep-07		4:07:53		69.2		55		20-Oct-07		4:25:59		72.8		53

		9-Sep-07		6:07:10		74.01		48.5		9-Sep-07		6:06:20		71.6		56		9-Sep-07		6:07:53		68.61		56		20-Oct-07		6:25:59		72.8		54

		9-Sep-07		8:07:10		74.01		46		9-Sep-07		8:06:20		71		50		9-Sep-07		8:07:53		68.61		57		20-Oct-07		8:25:59		72.8		56.5

		9-Sep-07		10:07:10		73.4		50.5		9-Sep-07		10:06:20		70.41		57.5		9-Sep-07		10:07:53		68.61		58		20-Oct-07		10:25:59		74.01		57.5

		9-Sep-07		12:07:10		73.4		51.5		9-Sep-07		12:06:20		70.41		56.5		9-Sep-07		12:07:53		69.8		57.5		20-Oct-07		12:25:59		75.2		57.5

		9-Sep-07		14:07:10		73.4		55		9-Sep-07		14:06:20		70.41		63.5		9-Sep-07		14:07:53		70.41		54.5		20-Oct-07		14:25:59		75.81		57

		9-Sep-07		16:07:10		74.6		54		9-Sep-07		16:06:20		70.41		64.5		9-Sep-07		16:07:53		71		51		20-Oct-07		16:25:59		75.81		57

		9-Sep-07		18:07:10		75.2		50		9-Sep-07		18:06:20		70.41		55		9-Sep-07		18:07:53		70.41		60		20-Oct-07		18:25:59		75.81		56

		9-Sep-07		20:07:10		75.2		44.5		9-Sep-07		20:06:20		71.6		47		9-Sep-07		20:07:53		70.41		55		20-Oct-07		20:25:59		74.01		54.5

		9-Sep-07		22:07:10		74.6		47		9-Sep-07		22:06:20		71		54.5		9-Sep-07		22:07:53		69.8		54		20-Oct-07		22:25:59		72.8		53

		10-Sep-07		0:07:10		74.6		46		10-Sep-07		0:06:20		71		52.5		10-Sep-07		0:07:53		69.2		53.5		21-Oct-07		0:25:59		71.6		51

		10-Sep-07		2:07:10		74.6		45.5		10-Sep-07		2:06:20		71.6		51		10-Sep-07		2:07:53		68.61		53.5		21-Oct-07		2:25:59		71		50

		10-Sep-07		4:07:10		74.01		45		10-Sep-07		4:06:20		71.6		50		10-Sep-07		4:07:53		68.61		54		21-Oct-07		4:25:59		70.41		49.5

		10-Sep-07		6:07:10		74.01		45		10-Sep-07		6:06:20		71		51		10-Sep-07		6:07:53		68		54.5		21-Oct-07		6:25:59		69.8		47.5

		10-Sep-07		8:07:10		72.8		44.5		10-Sep-07		8:06:20		69.8		50.5		10-Sep-07		8:07:53		67.4		54.5		21-Oct-07		8:25:59		69.2		45.5

		10-Sep-07		10:07:10		72.8		45.5		10-Sep-07		10:06:20		69.8		46.5		10-Sep-07		10:07:53		67.4		55		21-Oct-07		10:25:59		69.2		48

		10-Sep-07		12:07:10		72.8		46		10-Sep-07		12:06:20		70.41		49.5		10-Sep-07		12:07:53		68.61		56		21-Oct-07		12:25:59		70.41		45.5

		10-Sep-07		14:07:10		73.4		49		10-Sep-07		14:06:20		70.41		56.5		10-Sep-07		14:07:53		69.8		59.5		21-Oct-07		14:25:59		71		42

		10-Sep-07		16:07:10		74.01		53.5		10-Sep-07		16:06:20		70.41		62.5		10-Sep-07		16:07:53		70.41		49		21-Oct-07		16:25:59		72.21		39

		10-Sep-07		18:07:10		74.6		52.5		10-Sep-07		18:06:20		70.41		63		10-Sep-07		18:07:53		71		56		21-Oct-07		18:25:59		73.4		36.5

		10-Sep-07		20:07:10		75.2		49		10-Sep-07		20:06:20		71.6		55.5		10-Sep-07		20:07:53		71.6		54.5		21-Oct-07		20:25:59		72.21		38

		10-Sep-07		22:07:10		74.6		48		10-Sep-07		22:06:20		71		56		10-Sep-07		22:07:53		70.41		54		21-Oct-07		22:25:59		71		40

		11-Sep-07		0:07:10		74.6		47		11-Sep-07		0:06:20		71		54.5		11-Sep-07		0:07:53		69.8		53.5		22-Oct-07		0:25:59		69.8		39.5

		11-Sep-07		2:07:10		74.01		45.5		11-Sep-07		2:06:20		71		52		11-Sep-07		2:07:53		68.61		53.5		22-Oct-07		2:25:59		69.2		39.5

		11-Sep-07		4:07:10		74.01		44.5		11-Sep-07		4:06:20		71.6		48.5		11-Sep-07		4:07:53		68		53.5		22-Oct-07		4:25:59		69.2		39

		11-Sep-07		6:07:10		74.01		43		11-Sep-07		6:06:20		71		48		11-Sep-07		6:07:53		68.61		52		22-Oct-07		6:25:59		68.61		38.5

		11-Sep-07		8:07:10		74.01		43.5		11-Sep-07		8:06:20		70.41		45		11-Sep-07		8:07:53		71.6		51.5		22-Oct-07		8:25:59		68		37.5

		11-Sep-07		10:07:10		74.6		46.5		11-Sep-07		10:06:20		71		45.5		11-Sep-07		10:07:53		71.6		48		22-Oct-07		10:25:59		68		37.5

		11-Sep-07		12:07:10		74.01		52.5		11-Sep-07		12:06:20		71		63		11-Sep-07		12:07:53		72.21		46		22-Oct-07		12:25:59		69.2		36

		11-Sep-07		14:07:10		74.6		46.5		11-Sep-07		14:06:20		71.6		45		11-Sep-07		14:07:53		71.6		45		22-Oct-07		14:25:59		72.21		33

		11-Sep-07		16:07:10		75.2		48.5		11-Sep-07		16:06:20		70.41		52		11-Sep-07		16:07:53		71		63		22-Oct-07		16:25:59		72.8		33

		11-Sep-07		18:07:10		74.6		49.5		11-Sep-07		18:06:20		70.41		54		11-Sep-07		18:07:53		71		60.5		22-Oct-07		18:25:59		72.8		32.5

		11-Sep-07		20:07:10		75.2		50.5		11-Sep-07		20:06:20		71		58.5		11-Sep-07		20:07:53		70.41		57.5		22-Oct-07		20:25:59		72.8		31.5

		11-Sep-07		22:07:10		75.2		45.5		11-Sep-07		22:06:20		71.6		51.5		11-Sep-07		22:07:53		72.21		52		22-Oct-07		22:25:59		72.21		35

		12-Sep-07		0:07:10		74.6		46.5		12-Sep-07		0:06:20		71.6		53		12-Sep-07		0:07:53		71.6		51		23-Oct-07		0:25:59		71.6		36

		12-Sep-07		2:07:10		74.6		45.5		12-Sep-07		2:06:20		71.6		51.5		12-Sep-07		2:07:53		71		51		23-Oct-07		2:25:59		70.41		37

		12-Sep-07		4:07:10		74.01		46.5		12-Sep-07		4:06:20		70.41		53.5		12-Sep-07		4:07:53		70.41		52		23-Oct-07		4:25:59		69.8		36.5

		12-Sep-07		6:07:10		74.6		46.5		12-Sep-07		6:06:20		71		53		12-Sep-07		6:07:53		70.41		50		23-Oct-07		6:25:59		69.8		36.5

		12-Sep-07		8:07:10		74.01		45.5		12-Sep-07		8:06:20		71.6		44.5		12-Sep-07		8:07:53		71		48.5		23-Oct-07		8:25:59		68.61		37.5

		12-Sep-07		10:07:10		74.01		47.5		12-Sep-07		10:06:20		72.21		55		12-Sep-07		10:07:53		71.6		56		23-Oct-07		10:25:59		71.6		39

		12-Sep-07		12:07:10		74.6		47		12-Sep-07		12:06:20		71.6		53		12-Sep-07		12:07:53		72.21		52		23-Oct-07		12:25:59		74.6		37.5

		12-Sep-07		14:07:10		74.01		46		12-Sep-07		14:06:20		71.6		43		12-Sep-07		14:07:53		71.6		54		23-Oct-07		14:25:59		75.2		37

		12-Sep-07		16:07:10		74.6		49		12-Sep-07		16:06:20		71		53		12-Sep-07		16:07:53		71.6		46.5		23-Oct-07		16:25:59		75.81		36.5

		12-Sep-07		18:07:10		74.6		53		12-Sep-07		18:06:20		70.41		65		12-Sep-07		18:07:53		71		62.5		23-Oct-07		18:25:59		75.81		35.5

		12-Sep-07		20:07:10		74.6		52		12-Sep-07		20:06:20		71		60.5		12-Sep-07		20:07:53		71		54.5		23-Oct-07		20:25:59		74.6		36

		12-Sep-07		22:07:10		74.6		49		12-Sep-07		22:06:20		71.6		56.5		12-Sep-07		22:07:53		72.8		52.5		23-Oct-07		22:25:59		74.01		37.5

		13-Sep-07		0:07:10		75.2		49		13-Sep-07		0:06:20		71.6		56.5		13-Sep-07		0:07:53		72.8		53		24-Oct-07		0:25:59		73.4		38.5

		13-Sep-07		2:07:10		75.2		48.5		13-Sep-07		2:06:20		71		57		13-Sep-07		2:07:53		72.21		53		24-Oct-07		2:25:59		72.21		39

		13-Sep-07		4:07:10		74.6		48.5		13-Sep-07		4:06:20		70.41		58.5		13-Sep-07		4:07:53		71.6		56		24-Oct-07		4:25:59		71		39.5

		13-Sep-07		6:07:10		75.2		49		13-Sep-07		6:06:20		71		58		13-Sep-07		6:07:53		70.41		50.5		24-Oct-07		6:25:59		71		39

		13-Sep-07		8:07:10		74.6		50		13-Sep-07		8:06:20		71		52.5		13-Sep-07		8:07:53		71		56		24-Oct-07		8:25:59		69.8		39.5

		13-Sep-07		10:07:10		74.01		45.5		13-Sep-07		10:06:20		71.6		44.5		13-Sep-07		10:07:53		71.6		57		24-Oct-07		10:25:59		72.21		42.5

		13-Sep-07		12:07:10		74.6		48		13-Sep-07		12:06:20		71.6		52.5		13-Sep-07		12:07:53		71.6		48		24-Oct-07		12:25:59		75.2		41

		13-Sep-07		14:07:10		74.6		45.5		13-Sep-07		14:06:20		71.6		44		13-Sep-07		14:07:53		70.41		61.5		24-Oct-07		14:25:59		75.81		40.5

		13-Sep-07		16:07:10		74.6		52.5		13-Sep-07		16:06:20		70.41		58		13-Sep-07		16:07:53		71		61.5		24-Oct-07		16:25:59		76.4		40.5

		13-Sep-07		18:07:10		75.2		47		13-Sep-07		18:06:20		70.41		51		13-Sep-07		18:07:53		70.41		59.5		24-Oct-07		18:25:59		75.81		42.5

		13-Sep-07		20:07:10		75.2		48		13-Sep-07		20:06:20		71.6		55.5		13-Sep-07		20:07:53		71.6		55		24-Oct-07		20:25:59		75.2		45

		13-Sep-07		22:07:10		74.6		47.5		13-Sep-07		22:06:20		71		54.5		13-Sep-07		22:07:53		71.6		52.5		24-Oct-07		22:25:59		75.81		44.5

		14-Sep-07		0:07:10		74.6		46.5		14-Sep-07		0:06:20		71.6		53		14-Sep-07		0:07:53		71.6		51.5		25-Oct-07		0:25:59		74.6		43

		14-Sep-07		2:07:10		74.6		46.5		14-Sep-07		2:06:20		71		51.5		14-Sep-07		2:07:53		71.6		51.5		25-Oct-07		2:25:59		73.4		43

		14-Sep-07		4:07:10		74.6		44.5		14-Sep-07		4:06:20		71.6		50		14-Sep-07		4:07:53		71		45		25-Oct-07		4:25:59		72.21		43

		14-Sep-07		6:07:10		74.6		43.5		14-Sep-07		6:06:20		71		49.5		14-Sep-07		6:07:53		71		51		25-Oct-07		6:25:59		71.6		43

		14-Sep-07		8:07:10		74.01		46		14-Sep-07		8:06:20		71.6		54		14-Sep-07		8:07:53		71		53		25-Oct-07		8:25:59		71		42.5

		14-Sep-07		10:07:10		74.6		46.5		14-Sep-07		10:06:20		71.6		55.5		14-Sep-07		10:07:53		72.21		47.5		25-Oct-07		10:25:59		73.4		44

		14-Sep-07		12:07:10		74.01		47.5		14-Sep-07		12:06:20		70.41		53		14-Sep-07		12:07:53		72.21		43		25-Oct-07		12:25:59		75.2		44

		14-Sep-07		14:07:10		74.6		49		14-Sep-07		14:06:20		71.6		56		14-Sep-07		14:07:53		71.6		48		25-Oct-07		14:25:59		75.81		43

		14-Sep-07		16:07:10		75.2		46.5		14-Sep-07		16:06:20		71		53		14-Sep-07		16:07:53		71.6		58.5		25-Oct-07		16:25:59		75.81		41

		14-Sep-07		18:07:10		75.2		50.5		14-Sep-07		18:06:20		71		64.5		14-Sep-07		18:07:53		71		62		25-Oct-07		18:25:59		75.81		44.5

		14-Sep-07		20:07:10		75.2		50		14-Sep-07		20:06:20		71.6		59		14-Sep-07		20:07:53		72.8		55.5		25-Oct-07		20:25:59		75.2		43.5

		14-Sep-07		22:07:10		75.2		50.5		14-Sep-07		22:06:20		71.6		59.5		14-Sep-07		22:07:53		74.01		52.5		25-Oct-07		22:25:59		74.6		42.5

		15-Sep-07		0:07:10		75.2		48.5		15-Sep-07		0:06:20		71		51.5		15-Sep-07		0:07:53		73.4		52		26-Oct-07		0:25:59		73.4		42.5

		15-Sep-07		2:07:10		74.6		48		15-Sep-07		2:06:20		71.6		56		15-Sep-07		2:07:53		73.4		52		26-Oct-07		2:25:59		72.21		43

		15-Sep-07		4:07:10		74.6		48.5		15-Sep-07		4:06:20		71.6		55.5		15-Sep-07		4:07:53		72.21		54.5		26-Oct-07		4:25:59		71		42.5

		15-Sep-07		6:07:10		75.2		49.5		15-Sep-07		6:06:20		71.6		58.5		15-Sep-07		6:07:53		71		51		26-Oct-07		6:25:59		70.41		41.5

		15-Sep-07		8:07:10		75.2		46		15-Sep-07		8:06:20		72.21		49		15-Sep-07		8:07:53		71.6		56		26-Oct-07		8:25:59		69.2		41

		15-Sep-07		10:07:10		74.6		50		15-Sep-07		10:06:20		71.6		57.5		15-Sep-07		10:07:53		71.6		50		26-Oct-07		10:25:59		71		44.5

		15-Sep-07		12:07:10		74.01		51		15-Sep-07		12:06:20		71		51		15-Sep-07		12:07:53		72.21		49.5		26-Oct-07		12:25:59		74.6		43.5

		15-Sep-07		14:07:10		74.6		46.5		15-Sep-07		14:06:20		71.6		47.5		15-Sep-07		14:07:53		71.6		54		26-Oct-07		14:25:59		75.81		43.5

		15-Sep-07		16:07:10		74.6		45.5		15-Sep-07		16:06:20		69.2		50.5		15-Sep-07		16:07:53		71.6		53		26-Oct-07		16:25:59		76.4		43.5

		15-Sep-07		18:07:10		73.4		46		15-Sep-07		18:06:20		68		50		15-Sep-07		18:07:53		71		48.5		26-Oct-07		18:25:59		75.81		44

		15-Sep-07		20:07:10		74.6		45		15-Sep-07		20:06:20		71		52		15-Sep-07		20:07:53		71		50.5		26-Oct-07		20:25:59		74.6		43

		15-Sep-07		22:07:10		75.2		44.5		15-Sep-07		22:06:20		71.6		52		15-Sep-07		22:07:53		72.8		48		26-Oct-07		22:25:59		73.4		42.5

		16-Sep-07		0:07:10		75.2		44		16-Sep-07		0:06:20		71		51.5		16-Sep-07		0:07:53		72.8		48		27-Oct-07		0:25:59		72.21		43

		16-Sep-07		2:07:10		75.2		43		16-Sep-07		2:06:20		71.6		49.5		16-Sep-07		2:07:53		72.21		47.5		27-Oct-07		2:25:59		71		44

		16-Sep-07		4:07:10		74.6		44		16-Sep-07		4:06:20		71		51		16-Sep-07		4:07:53		71		48.5		27-Oct-07		4:25:59		70.41		44.5

		16-Sep-07		6:07:10		74.01		43		16-Sep-07		6:06:20		69.8		44		16-Sep-07		6:07:53		71		49		27-Oct-07		6:25:59		70.41		45.5

		16-Sep-07		8:07:10		73.4		44		16-Sep-07		8:06:20		68.61		54		16-Sep-07		8:07:53		70.41		48		27-Oct-07		8:25:59		70.41		46

		16-Sep-07		10:07:10		73.4		45.5		16-Sep-07		10:06:20		68.61		57		16-Sep-07		10:07:53		69.8		52.5		27-Oct-07		10:25:59		72.21		45.5

		16-Sep-07		12:07:10		72.8		46		16-Sep-07		12:06:20		68.61		47.5		16-Sep-07		12:07:53		70.41		56		27-Oct-07		12:25:59		74.6		44

		16-Sep-07		14:07:10		73.4		44.5		16-Sep-07		14:06:20		68.61		47		16-Sep-07		14:07:53		71		51		27-Oct-07		14:25:59		75.2		42.5

		16-Sep-07		16:07:10		74.6		45		16-Sep-07		16:06:20		68.61		52		16-Sep-07		16:07:53		71		50.5		27-Oct-07		16:25:59		75.2		43.5

		16-Sep-07		18:07:10		74.6		46		16-Sep-07		18:06:20		68.61		59		16-Sep-07		18:07:53		70.41		53		27-Oct-07		18:25:59		74.6		44

		16-Sep-07		20:07:10		75.81		45		16-Sep-07		20:06:20		71		54		16-Sep-07		20:07:53		71.6		51.5		27-Oct-07		20:25:59		72.21		43.5

		16-Sep-07		22:07:10		75.2		44.5		16-Sep-07		22:06:20		71		52.5		16-Sep-07		22:07:53		72.21		49.5		27-Oct-07		22:25:59		71.6		44

		17-Sep-07		0:07:10		75.2		43		17-Sep-07		0:06:20		71		51.5		17-Sep-07		0:07:53		71.6		49		28-Oct-07		0:25:59		70.41		43.5

		17-Sep-07		2:07:10		74.6		42.5		17-Sep-07		2:06:20		70.41		49.5		17-Sep-07		2:07:53		70.41		48.5		28-Oct-07		2:25:59		69.2		42.5

		17-Sep-07		4:07:10		74.01		41.5		17-Sep-07		4:06:20		70.41		47		17-Sep-07		4:07:53		69.8		48		28-Oct-07		4:25:59		68.61		42

		17-Sep-07		6:07:10		73.4		41.5		17-Sep-07		6:06:20		69.8		42		17-Sep-07		6:07:53		69.2		49		28-Oct-07		6:25:59		68.61		41.5

		17-Sep-07		8:07:10		72.21		44.5		17-Sep-07		8:06:20		68		52.5		17-Sep-07		8:07:53		69.2		50		28-Oct-07		8:25:59		68		42

		17-Sep-07		10:07:10		72.8		47.5		17-Sep-07		10:06:20		68.61		57.5		17-Sep-07		10:07:53		70.41		49.5		28-Oct-07		10:25:59		67.4		44.5

		17-Sep-07		12:07:10		72.8		50.5		17-Sep-07		12:06:20		68.61		61		17-Sep-07		12:07:53		71		49.5		28-Oct-07		12:25:59		68.61		45.5

		17-Sep-07		14:07:10		74.01		45.5		17-Sep-07		14:06:20		69.2		52		17-Sep-07		14:07:53		71		57		28-Oct-07		14:25:59		69.8		46

		17-Sep-07		16:07:10		74.6		49.5		17-Sep-07		16:06:20		68.61		58		17-Sep-07		16:07:53		71		51.5		28-Oct-07		16:25:59		71.6		47

		17-Sep-07		18:07:10		74.6		48.5		17-Sep-07		18:06:20		68.61		61.5		17-Sep-07		18:07:53		71		50		28-Oct-07		18:25:59		71.6		45

		17-Sep-07		20:07:10		75.81		46		17-Sep-07		20:06:20		71		55		17-Sep-07		20:07:53		74.01		48		28-Oct-07		20:25:59		70.41		45

		17-Sep-07		22:07:10		75.81		44		17-Sep-07		22:06:20		71.6		52		17-Sep-07		22:07:53		74.6		46.5		28-Oct-07		22:25:59		69.8		44.5

		18-Sep-07		0:07:10		75.2		42.5		18-Sep-07		0:06:20		71		50		18-Sep-07		0:07:53		73.4		45.5		29-Oct-07		0:25:59		69.2		44

		18-Sep-07		2:07:10		75.2		41.5		18-Sep-07		2:06:20		71.6		48		18-Sep-07		2:07:53		72.21		45.5		29-Oct-07		2:25:59		68.61		44

		18-Sep-07		4:07:10		74.6		40.5		18-Sep-07		4:06:20		71		46.5		18-Sep-07		4:07:53		71		45.5		29-Oct-07		4:25:59		68.61		44

		18-Sep-07		6:07:10		74.6		39.5		18-Sep-07		6:06:20		69.8		45		18-Sep-07		6:07:53		70.41		45.5		29-Oct-07		6:25:59		68		43.5

		18-Sep-07		8:07:10		72.8		40		18-Sep-07		8:06:20		69.2		39.5		18-Sep-07		8:07:53		71		44.5		29-Oct-07		8:25:59		67.4		43

		18-Sep-07		10:07:10		73.4		42.5		18-Sep-07		10:06:20		70.41		46.5		18-Sep-07		10:07:53		71.6		42.5		29-Oct-07		10:25:59		68.61		45.5

		18-Sep-07		12:07:10		73.4		44.5		18-Sep-07		12:06:20		69.8		51		18-Sep-07		12:07:53		72.21		43.5		29-Oct-07		12:25:59		70.41		46.5

		18-Sep-07		14:07:10		73.4		42.5		18-Sep-07		14:06:20		69.8		42		18-Sep-07		14:07:53		71.6		43.5		29-Oct-07		14:25:59		72.21		47.5

		18-Sep-07		16:07:10		74.01		47.5		18-Sep-07		16:06:20		69.2		61		18-Sep-07		16:07:53		71		49.5		29-Oct-07		16:25:59		74.6		47.5

		18-Sep-07		18:07:10		74.01		43.5		18-Sep-07		18:06:20		69.2		49.5		18-Sep-07		18:07:53		71		43		29-Oct-07		18:25:59		75.2		47

		18-Sep-07		20:07:10		74.6		44		18-Sep-07		20:06:20		71.6		50		18-Sep-07		20:07:53		71.6		51.5		29-Oct-07		20:25:59		74.01		46

		18-Sep-07		22:07:10		75.2		42.5		18-Sep-07		22:06:20		71.6		50.5		18-Sep-07		22:07:53		73.4		46		29-Oct-07		22:25:59		72.8		46

		19-Sep-07		0:07:10		75.2		42.5		19-Sep-07		0:06:20		71		49.5		19-Sep-07		0:07:53		73.4		44.5		30-Oct-07		0:25:59		71.6		46

		19-Sep-07		2:07:10		74.6		41		19-Sep-07		2:06:20		71		48		19-Sep-07		2:07:53		72.8		44		30-Oct-07		2:25:59		71		46

		19-Sep-07		4:07:10		74.6		40		19-Sep-07		4:06:20		71		46		19-Sep-07		4:07:53		71		44		30-Oct-07		4:25:59		69.8		45.5

		19-Sep-07		6:07:10		74.01		38.5		19-Sep-07		6:06:20		70.41		41.5		19-Sep-07		6:07:53		70.41		43.5		30-Oct-07		6:25:59		69.8		46

		19-Sep-07		8:07:10		72.8		41		19-Sep-07		8:06:20		69.8		48		19-Sep-07		8:07:53		71		42.5		30-Oct-07		8:25:59		69.2		48

		19-Sep-07		10:07:10		72.8		43.5		19-Sep-07		10:06:20		70.41		51.5		19-Sep-07		10:07:53		71.6		45.5		30-Oct-07		10:25:59		71		48

		19-Sep-07		12:07:10		73.4		45.5		19-Sep-07		12:06:20		70.41		56		19-Sep-07		12:07:53		72.21		53		30-Oct-07		12:25:59		72.8		49

		19-Sep-07		14:07:10		74.6		43.5		19-Sep-07		14:06:20		72.21		49		19-Sep-07		14:07:53		71.6		41		30-Oct-07		14:25:59		74.6		48

		19-Sep-07		16:07:10		73.4		42.5		19-Sep-07		16:06:20		68.61		45		19-Sep-07		16:07:53		72.21		48		30-Oct-07		16:25:59		75.2		47.5

		19-Sep-07		18:07:10		73.4		42		19-Sep-07		18:06:20		68.61		43		19-Sep-07		18:07:53		71		50		30-Oct-07		18:25:59		75.2		45

		19-Sep-07		20:07:10		74.6		42		19-Sep-07		20:06:20		70.41		49		19-Sep-07		20:07:53		71		47.5		30-Oct-07		20:25:59		72.8		45.5

		19-Sep-07		22:07:10		74.6		39.5		19-Sep-07		22:06:20		70.41		46.5		19-Sep-07		22:07:53		72.21		42.5		30-Oct-07		22:25:59		71.6		46.5

		20-Sep-07		0:07:10		74.6		38		20-Sep-07		0:06:20		70.41		44		20-Sep-07		0:07:53		71.6		41		31-Oct-07		0:25:59		71		46.5

		20-Sep-07		2:07:10		74.01		37		20-Sep-07		2:06:20		70.41		42		20-Sep-07		2:07:53		71		40.5		31-Oct-07		2:25:59		70.41		47.5

		20-Sep-07		4:07:10		73.4		36		20-Sep-07		4:06:20		70.41		41		20-Sep-07		4:07:53		69.8		40.5		31-Oct-07		4:25:59		70.41		48

		20-Sep-07		6:07:10		72.8		36		20-Sep-07		6:06:20		69.8		40		20-Sep-07		6:07:53		69.8		40		31-Oct-07		6:25:59		70.41		48.5

		20-Sep-07		8:07:10		72.8		37.5		20-Sep-07		8:06:20		69.8		44		20-Sep-07		8:07:53		71		39.5		31-Oct-07		8:25:59		69.8		48

		20-Sep-07		10:07:10		73.4		37.5		20-Sep-07		10:06:20		70.41		45.5		20-Sep-07		10:07:53		71.6		35.5		31-Oct-07		10:25:59		71.6		48

		20-Sep-07		12:07:10		73.4		36		20-Sep-07		12:06:20		69.2		35.5		20-Sep-07		12:07:53		72.21		34.5		31-Oct-07		12:25:59		72.21		47.5

		20-Sep-07		14:07:10		73.4		34		20-Sep-07		14:06:20		69.8		36		20-Sep-07		14:07:53		71.6		39.5		31-Oct-07		14:25:59		73.4		46.5

		20-Sep-07		16:07:10		73.4		34		20-Sep-07		16:06:20		68.61		37.5		20-Sep-07		16:07:53		71		33		31-Oct-07		16:25:59		74.6		46

		20-Sep-07		18:07:10		74.01		34.5		20-Sep-07		18:06:20		68		41.5		20-Sep-07		18:07:53		70.41		38.5		31-Oct-07		18:25:59		75.2		44.5

		20-Sep-07		20:07:10		74.6		36		20-Sep-07		20:06:20		69.8		41		20-Sep-07		20:07:53		72.8		37.5		31-Oct-07		20:25:59		72.8		44.5

		20-Sep-07		22:07:10		74.6		34		20-Sep-07		22:06:20		70.41		39.5		20-Sep-07		22:07:53		72.21		36.5		31-Oct-07		22:25:59		72.21		45.5

		21-Sep-07		0:07:10		74.01		34.5		21-Sep-07		0:06:20		69.8		40.5		21-Sep-07		0:07:53		71.6		37.5		1-Nov-07		0:25:59		70.41		46

		21-Sep-07		2:07:10		74.01		33.5		21-Sep-07		2:06:20		70.41		36		21-Sep-07		2:07:53		71		37		1-Nov-07		2:25:59		69.8		47

		21-Sep-07		4:07:10		73.4		33		21-Sep-07		4:06:20		70.41		38		21-Sep-07		4:07:53		69.8		37		1-Nov-07		4:25:59		69.8		48

		21-Sep-07		6:07:10		73.4		34.5		21-Sep-07		6:06:20		69.8		39.5		21-Sep-07		6:07:53		69.8		39		1-Nov-07		6:25:59		69.8		48.5

		21-Sep-07		8:07:10		72.8		37.5		21-Sep-07		8:06:20		69.8		44.5		21-Sep-07		8:07:53		71		39		1-Nov-07		8:25:59		69.8		48.5

		21-Sep-07		10:07:10		72.8		38.5		21-Sep-07		10:06:20		69.8		41.5		21-Sep-07		10:07:53		71.6		42		1-Nov-07		10:25:59		72.21		48

		21-Sep-07		12:07:10		74.6		37		21-Sep-07		12:06:20		73.4		36		21-Sep-07		12:07:53		71.6		36.5		1-Nov-07		12:25:59		72.8		48.5

		21-Sep-07		14:07:10		74.6		38.5		21-Sep-07		14:06:20		71.6		45		21-Sep-07		14:07:53		71		41.5		1-Nov-07		14:25:59		73.4		48.5

		21-Sep-07		16:07:10		74.6		38		21-Sep-07		16:06:20		70.41		45.5		21-Sep-07		16:07:53		71		41		1-Nov-07		16:25:59		74.01		49.5

		21-Sep-07		18:07:10		74.6		37.5		21-Sep-07		18:06:20		70.41		44		21-Sep-07		18:07:53		71		40.5		1-Nov-07		18:25:59		74.01		48

		21-Sep-07		20:07:10		75.81		35		21-Sep-07		20:06:20		72.21		39		21-Sep-07		20:07:53		71.6		39		1-Nov-07		20:25:59		72.21		48

		21-Sep-07		22:07:10		75.81		33.5		21-Sep-07		22:06:20		72.8		37.5		21-Sep-07		22:07:53		71		38		1-Nov-07		22:25:59		71.6		49

		22-Sep-07		0:07:10		75.2		33		22-Sep-07		0:06:20		72.21		37		22-Sep-07		0:07:53		70.41		38.5		2-Nov-07		0:25:59		71		49

		22-Sep-07		2:07:10		74.6		32.5		22-Sep-07		2:06:20		71.6		36.5		22-Sep-07		2:07:53		68.61		38.5		2-Nov-07		2:25:59		70.41		49.5

		22-Sep-07		4:07:10		73.4		33		22-Sep-07		4:06:20		70.41		37.5		22-Sep-07		4:07:53		68		39.5		2-Nov-07		4:25:59		69.8		49

		22-Sep-07		6:07:10		72.8		33.5		22-Sep-07		6:06:20		69.8		37.5		22-Sep-07		6:07:53		67.4		40.5		2-Nov-07		6:25:59		69.8		48

		22-Sep-07		8:07:10		72.8		33.5		22-Sep-07		8:06:20		71.6		37.5		22-Sep-07		8:07:53		69.2		40		2-Nov-07		8:25:59		71.6		46.5

		22-Sep-07		10:07:10		73.4		36		22-Sep-07		10:06:20		72.21		39		22-Sep-07		10:07:53		71.6		43.5		2-Nov-07		10:25:59		71.6		48

		22-Sep-07		12:07:10		73.4		36.5		22-Sep-07		12:06:20		71.6		40.5		22-Sep-07		12:07:53		71.6		44.5		2-Nov-07		12:25:59		73.4		48

		22-Sep-07		14:07:10		74.01		38		22-Sep-07		14:06:20		71		40.5		22-Sep-07		14:07:53		72.21		43		2-Nov-07		14:25:59		75.2		48

		22-Sep-07		16:07:10		74.6		40.5		22-Sep-07		16:06:20		70.41		47		22-Sep-07		16:07:53		71.6		47		2-Nov-07		16:25:59		75.2		49.5

		22-Sep-07		18:07:10		74.6		38.5		22-Sep-07		18:06:20		70.41		45		22-Sep-07		18:07:53		71		38.5		2-Nov-07		18:25:59		75.2		50

		22-Sep-07		20:07:10		75.2		37.5		22-Sep-07		20:06:20		72.21		42		22-Sep-07		20:07:53		70.41		44		2-Nov-07		20:25:59		74.6		46

		22-Sep-07		22:07:10		75.81		37.5		22-Sep-07		22:06:20		72.8		42.5		22-Sep-07		22:07:53		71.6		43		2-Nov-07		22:25:59		73.4		45.5

		23-Sep-07		0:07:10		75.81		38.5		23-Sep-07		0:06:20		73.4		43.5		23-Sep-07		0:07:53		71.6		44.5		3-Nov-07		0:25:59		71.6		45

		23-Sep-07		2:07:10		75.2		40		23-Sep-07		2:06:20		72.21		46.5		23-Sep-07		2:07:53		71		46.5		3-Nov-07		2:25:59		69.8		44

		23-Sep-07		4:07:10		75.2		41		23-Sep-07		4:06:20		72.8		46		23-Sep-07		4:07:53		71		47.5		3-Nov-07		4:25:59		69.2		43

		23-Sep-07		6:07:10		74.6		42		23-Sep-07		6:06:20		71.6		44		23-Sep-07		6:07:53		71.6		48		3-Nov-07		6:25:59		69.2		42

		23-Sep-07		8:07:10		74.01		44.5		23-Sep-07		8:06:20		69.8		52		23-Sep-07		8:07:53		71		43.5		3-Nov-07		8:25:59		71.6		39.5

		23-Sep-07		10:07:10		73.4		44.5		23-Sep-07		10:06:20		70.41		50.5		23-Sep-07		10:07:53		71.6		56		3-Nov-07		10:25:59		71.6		42.5

		23-Sep-07		12:07:10		74.01		44.5		23-Sep-07		12:06:20		70.41		48		23-Sep-07		12:07:53		71		49		3-Nov-07		12:25:59		75.2		42.5

		23-Sep-07		14:07:10		73.4		48.5		23-Sep-07		14:06:20		70.41		56.5		23-Sep-07		14:07:53		71		54		3-Nov-07		14:25:59		76.4		42.5

		23-Sep-07		16:07:10		74.01		50.5		23-Sep-07		16:06:20		70.41		60		23-Sep-07		16:07:53		70.41		51		3-Nov-07		16:25:59		75.81		42

		23-Sep-07		18:07:10		73.4		50.5		23-Sep-07		18:06:20		70.41		59		23-Sep-07		18:07:53		69.8		56.5		3-Nov-07		18:25:59		75.81		43.5

		23-Sep-07		20:07:10		74.6		49.5		23-Sep-07		20:06:20		72.21		55		23-Sep-07		20:07:53		69.8		56		3-Nov-07		20:25:59		74.6		43

		23-Sep-07		22:07:10		74.6		48		23-Sep-07		22:06:20		72.21		52.5		23-Sep-07		22:07:53		70.41		55.5		3-Nov-07		22:25:59		73.4		43.5

		24-Sep-07		0:07:10		74.6		47.5		24-Sep-07		0:06:20		72.21		52		24-Sep-07		0:07:53		69.8		54.5		4-Nov-07		0:25:59		71.6		43

		24-Sep-07		2:07:10		74.6		47.5		24-Sep-07		2:06:20		72.21		52		24-Sep-07		2:07:53		69.8		55		4-Nov-07		2:25:59		70.41		42

		24-Sep-07		4:07:10		74.6		47		24-Sep-07		4:06:20		72.21		51.5		24-Sep-07		4:07:53		69.8		54.5		4-Nov-07		4:25:59		69.2		41

		24-Sep-07		6:07:10		74.01		46.5		24-Sep-07		6:06:20		71.6		46		24-Sep-07		6:07:53		69.8		54.5		4-Nov-07		6:25:59		68.61		40

		24-Sep-07		8:07:10		73.4		49		24-Sep-07		8:06:20		70.41		56		24-Sep-07		8:07:53		69.2		55		4-Nov-07		8:25:59		67.4		38.5

		24-Sep-07		10:07:10		72.8		50.5		24-Sep-07		10:06:20		69.8		56.5		24-Sep-07		10:07:53		69.8		55.5		4-Nov-07		10:25:59		68		40.5

		24-Sep-07		12:07:10		72.8		51		24-Sep-07		12:06:20		69.2		55.5		24-Sep-07		12:07:53		69.8		56		4-Nov-07		12:25:59		69.2		42.5

		24-Sep-07		14:07:10		73.4		50		24-Sep-07		14:06:20		69.8		56.5		24-Sep-07		14:07:53		70.41		51.5		4-Nov-07		14:25:59		71		43

		24-Sep-07		16:07:10		74.01		46		24-Sep-07		16:06:20		69.8		44		24-Sep-07		16:07:53		70.41		48		4-Nov-07		16:25:59		72.21		43

		24-Sep-07		18:07:10		74.01		45		24-Sep-07		18:06:20		69.8		51		24-Sep-07		18:07:53		71		46.5		4-Nov-07		18:25:59		72.8		41.5

		24-Sep-07		20:07:10		75.2		40		24-Sep-07		20:06:20		72.8		39.5		24-Sep-07		20:07:53		72.21		45		4-Nov-07		20:25:59		71.6		39

		24-Sep-07		22:07:10		75.81		40		24-Sep-07		22:06:20		73.4		43.5		24-Sep-07		22:07:53		71.6		45.5		4-Nov-07		22:25:59		70.41		39.5

		25-Sep-07		0:07:10		74.6		39		25-Sep-07		0:06:20		72.21		43		25-Sep-07		0:07:53		70.41		45		5-Nov-07		0:25:59		69.8		40

		25-Sep-07		2:07:10		74.01		37.5		25-Sep-07		2:06:20		71.6		41		25-Sep-07		2:07:53		69.2		44		5-Nov-07		2:25:59		68.61		40

		25-Sep-07		4:07:10		73.4		37		25-Sep-07		4:06:20		71		40		25-Sep-07		4:07:53		68		43		5-Nov-07		4:25:59		68		39

		25-Sep-07		6:07:10		72.8		36.5		25-Sep-07		6:06:20		69.8		38.5		25-Sep-07		6:07:53		68.61		42		5-Nov-07		6:25:59		67.4		38.5

		25-Sep-07		8:07:10		72.8		37		25-Sep-07		8:06:20		71		41		25-Sep-07		8:07:53		69.2		41		5-Nov-07		8:25:59		66.2		37.5

		25-Sep-07		10:07:10		74.01		38		25-Sep-07		10:06:20		72.21		40		25-Sep-07		10:07:53		71		48		5-Nov-07		10:25:59		67.4		39.5

		25-Sep-07		12:07:10		74.6		39		25-Sep-07		12:06:20		71.6		43		25-Sep-07		12:07:53		71.6		43		5-Nov-07		12:25:59		69.2		40.5

		25-Sep-07		14:07:10		74.01		34.5		25-Sep-07		14:06:20		71.6		37.5		25-Sep-07		14:07:53		71.6		35		5-Nov-07		14:25:59		71		41.5

		25-Sep-07		16:07:10		74.6		36.5		25-Sep-07		16:06:20		70.41		40.5		25-Sep-07		16:07:53		72.21		39		5-Nov-07		16:25:59		72.21		41.5

		25-Sep-07		18:07:10		74.01		33.5		25-Sep-07		18:06:20		70.41		36		25-Sep-07		18:07:53		71.6		37		5-Nov-07		18:25:59		72.8		41

		25-Sep-07		20:07:10		75.81		36.5		25-Sep-07		20:06:20		72.8		40.5		25-Sep-07		20:07:53		71		42.5		5-Nov-07		20:25:59		71.6		42.5

		25-Sep-07		22:07:10		75.81		36		25-Sep-07		22:06:20		72.8		40		25-Sep-07		22:07:53		72.8		40		5-Nov-07		22:25:59		71		43

		26-Sep-07		0:07:10		75.81		35		26-Sep-07		0:06:20		72.8		39		26-Sep-07		0:07:53		71.6		40		6-Nov-07		0:25:59		69.8		42

		26-Sep-07		2:07:10		75.2		34.5		26-Sep-07		2:06:20		72.21		39		26-Sep-07		2:07:53		69.8		40		6-Nov-07		2:25:59		69.2		41.5

		26-Sep-07		4:07:10		74.01		34		26-Sep-07		4:06:20		71		38		26-Sep-07		4:07:53		68.61		40		6-Nov-07		4:25:59		68		40.5

		26-Sep-07		6:07:10		72.8		33.5		26-Sep-07		6:06:20		70.41		36		26-Sep-07		6:07:53		68.61		39.5		6-Nov-07		6:25:59		68		39.5

		26-Sep-07		8:07:10		73.4		33		26-Sep-07		8:06:20		71.6		36.5		26-Sep-07		8:07:53		70.41		37.5		6-Nov-07		8:25:59		69.8		37

		26-Sep-07		10:07:10		74.01		37		26-Sep-07		10:06:20		71.6		38.5		26-Sep-07		10:07:53		71.6		34.5		6-Nov-07		10:25:59		71		39.5

		26-Sep-07		12:07:10		74.6		34.5		26-Sep-07		12:06:20		71.6		36		26-Sep-07		12:07:53		71.6		35.5		6-Nov-07		12:25:59		73.4		39.5

		26-Sep-07		14:07:10		74.6		33		26-Sep-07		14:06:20		71.6		35.5		26-Sep-07		14:07:53		71.6		34		6-Nov-07		14:25:59		75.2		39.5

		26-Sep-07		16:07:10		75.2		32.5		26-Sep-07		16:06:20		71		35.5		26-Sep-07		16:07:53		71.6		34.5		6-Nov-07		16:25:59		75.81		42.5

		26-Sep-07		18:07:10		74.6		31		26-Sep-07		18:06:20		69.8		34.5		26-Sep-07		18:07:53		71		34.5		6-Nov-07		18:25:59		75.2		41.5

		26-Sep-07		20:07:10		75.81		32		26-Sep-07		20:06:20		72.8		35.5		26-Sep-07		20:07:53		71		33.5		6-Nov-07		20:25:59		72.8		41

		26-Sep-07		22:07:10		76.4		31		26-Sep-07		22:06:20		72.8		35.5		26-Sep-07		22:07:53		73.4		34.5		6-Nov-07		22:25:59		71.6		42

		27-Sep-07		0:07:10		76.4		31		27-Sep-07		0:06:20		72.8		35.5		27-Sep-07		0:07:53		72.8		34.5		7-Nov-07		0:25:59		71		43

		27-Sep-07		2:07:10		75.81		30.5		27-Sep-07		2:06:20		72.21		35		27-Sep-07		2:07:53		71.6		34.5		7-Nov-07		2:25:59		69.8		43

		27-Sep-07		4:07:10		75.2		30		27-Sep-07		4:06:20		72.21		34		27-Sep-07		4:07:53		70.41		35		7-Nov-07		4:25:59		69.2		43.5

		27-Sep-07		6:07:10		75.2		30.5		27-Sep-07		6:06:20		72.21		33		27-Sep-07		6:07:53		70.41		35.5		7-Nov-07		6:25:59		69.2		44

		27-Sep-07		8:07:10		74.6		31.5		27-Sep-07		8:06:20		71.6		35		27-Sep-07		8:07:53		71.6		33		7-Nov-07		8:25:59		71		43

		27-Sep-07		10:07:10		74.6		32		27-Sep-07		10:06:20		72.21		37.5		27-Sep-07		10:07:53		71.6		36.5		7-Nov-07		10:25:59		71.6		42.5

		27-Sep-07		12:07:10		74.6		34		27-Sep-07		12:06:20		71.6		37		27-Sep-07		12:07:53		72.21		39		7-Nov-07		12:25:59		72.8		42

		27-Sep-07		14:07:10		74.6		34		27-Sep-07		14:06:20		71		35.5		27-Sep-07		14:07:53		72.21		34		7-Nov-07		14:25:59		74.01		42.5

		27-Sep-07		16:07:10		75.2		33		27-Sep-07		16:06:20		70.41		37.5		27-Sep-07		16:07:53		71.6		34.5		7-Nov-07		16:25:59		74.6		44

		27-Sep-07		18:07:10		75.2		32.5		27-Sep-07		18:06:20		71		36		27-Sep-07		18:07:53		71.6		35.5		7-Nov-07		18:25:59		74.6		43

		27-Sep-07		20:07:10		76.4		30.5		27-Sep-07		20:06:20		72.8		33.5		27-Sep-07		20:07:53		74.6		31.5		7-Nov-07		20:25:59		72.21		42.5

		27-Sep-07		22:07:10		76.4		30.5		27-Sep-07		22:06:20		72.8		34.5		27-Sep-07		22:07:53		75.2		32		7-Nov-07		22:25:59		71.6		42

		28-Sep-07		0:07:10		76.4		30		28-Sep-07		0:06:20		72.8		34.5		28-Sep-07		0:07:53		74.6		32.5		8-Nov-07		0:25:59		69.8		42.5

		28-Sep-07		2:07:10		75.81		29.5		28-Sep-07		2:06:20		72.8		33		28-Sep-07		2:07:53		72.8		33		8-Nov-07		2:25:59		69.2		43

		28-Sep-07		4:07:10		75.2		30		28-Sep-07		4:06:20		72.8		34		28-Sep-07		4:07:53		71.6		34		8-Nov-07		4:25:59		68.61		42.5

		28-Sep-07		6:07:10		75.2		30.5		28-Sep-07		6:06:20		72.8		32.5		28-Sep-07		6:07:53		70.41		35		8-Nov-07		6:25:59		68.61		43

		28-Sep-07		8:07:10		74.6		31.5		28-Sep-07		8:06:20		71		37		28-Sep-07		8:07:53		71.6		31.5		8-Nov-07		8:25:59		71.6		40.5

		28-Sep-07		10:07:10		74.6		32.5		28-Sep-07		10:06:20		71.6		39		28-Sep-07		10:07:53		71.6		38.5		8-Nov-07		10:25:59		71		41.5

		28-Sep-07		12:07:10		74.6		33		28-Sep-07		12:06:20		71.6		36.5		28-Sep-07		12:07:53		72.21		34.5		8-Nov-07		12:25:59		72.8		43.5

		28-Sep-07		14:07:10		74.01		36		28-Sep-07		14:06:20		71		36		28-Sep-07		14:07:53		71.6		40		8-Nov-07		14:25:59		74.01		42.5

		28-Sep-07		16:07:10		75.2		37.5		28-Sep-07		16:06:20		71		44		28-Sep-07		16:07:53		71.6		41.5		8-Nov-07		16:25:59		75.2		43.5

		28-Sep-07		18:07:10		74.6		39		28-Sep-07		18:06:20		70.41		46.5		28-Sep-07		18:07:53		71		45		8-Nov-07		18:25:59		74.01		43

		28-Sep-07		20:07:10		75.81		37		28-Sep-07		20:06:20		72.8		42		28-Sep-07		20:07:53		71.6		42		8-Nov-07		20:25:59		72.21		43.5

		28-Sep-07		22:07:10		75.81		36.5		28-Sep-07		22:06:20		72.8		42		28-Sep-07		22:07:53		72.21		41		8-Nov-07		22:25:59		72.21		45.5

		29-Sep-07		0:07:10		75.2		36.5		29-Sep-07		0:06:20		72.21		42		29-Sep-07		0:07:53		71.6		42		9-Nov-07		0:25:59		71		44.5

		29-Sep-07		2:07:10		75.2		37		29-Sep-07		2:06:20		72.8		42		29-Sep-07		2:07:53		71		42.5		9-Nov-07		2:25:59		69.8		44.5

		29-Sep-07		4:07:10		75.2		37		29-Sep-07		4:06:20		72.8		41		29-Sep-07		4:07:53		71		42.5		9-Nov-07		4:25:59		69.2		45

		29-Sep-07		6:07:10		75.2		35		29-Sep-07		6:06:20		72.8		35		29-Sep-07		6:07:53		69.8		45.5		9-Nov-07		6:25:59		69.2		46.5

		29-Sep-07		8:07:10		74.6		39		29-Sep-07		8:06:20		71.6		42		29-Sep-07		8:07:53		71		45.5		9-Nov-07		8:25:59		71		45

		29-Sep-07		10:07:10		74.01		40.5		29-Sep-07		10:06:20		71		42		29-Sep-07		10:07:53		71.6		46		9-Nov-07		10:25:59		71		46

		29-Sep-07		12:07:10		74.6		39		29-Sep-07		12:06:20		71.6		38.5		29-Sep-07		12:07:53		71.6		48.5		9-Nov-07		12:25:59		72.21		47

		29-Sep-07		14:07:10		74.01		45		29-Sep-07		14:06:20		71.6		54		29-Sep-07		14:07:53		71.6		47		9-Nov-07		14:25:59		74.01		44.5

		29-Sep-07		16:07:10		74.6		42		29-Sep-07		16:06:20		71.6		48.5		29-Sep-07		16:07:53		71.6		52		9-Nov-07		16:25:59		74.01		44.5

		29-Sep-07		18:07:10		74.6		43.5		29-Sep-07		18:06:20		70.41		53		29-Sep-07		18:07:53		71		52		9-Nov-07		18:25:59		74.01		43.5

		29-Sep-07		20:07:10		75.2		36		29-Sep-07		20:06:20		72.21		38		29-Sep-07		20:07:53		70.41		42		9-Nov-07		20:25:59		73.4		43

		29-Sep-07		22:07:10		75.2		32.5		29-Sep-07		22:06:20		72.8		35		29-Sep-07		22:07:53		71		36.5		9-Nov-07		22:25:59		72.21		45

		30-Sep-07		0:07:10		75.2		31		30-Sep-07		0:06:20		73.4		33.5		30-Sep-07		0:07:53		70.41		35.5		10-Nov-07		0:25:59		71		45

		30-Sep-07		2:07:10		74.6		30.5		30-Sep-07		2:06:20		72.8		32.5		30-Sep-07		2:07:53		69.8		34.5		10-Nov-07		2:25:59		69.8		45.5

		30-Sep-07		4:07:10		74.01		30		30-Sep-07		4:06:20		71.6		32.5		30-Sep-07		4:07:53		68.61		34.5		10-Nov-07		4:25:59		69.2		46

		30-Sep-07		6:07:10		73.4		29.5		30-Sep-07		6:06:20		72.21		32.5		30-Sep-07		6:07:53		68		34.5		10-Nov-07		6:25:59		69.2		45.5

		30-Sep-07		8:07:10		72.21		30.5		30-Sep-07		8:06:20		71		34		30-Sep-07		8:07:53		68		34.5		10-Nov-07		8:25:59		71		42.5

		30-Sep-07		10:07:10		72.8		31		30-Sep-07		10:06:20		71.6		34.5		30-Sep-07		10:07:53		70.41		34.5		10-Nov-07		10:25:59		73.4		43

		30-Sep-07		12:07:10		73.4		31		30-Sep-07		12:06:20		71		33.5		30-Sep-07		12:07:53		70.41		32		10-Nov-07		12:25:59		74.01		43

		30-Sep-07		14:07:10		73.4		29		30-Sep-07		14:06:20		70.41		31.5		30-Sep-07		14:07:53		71		31		10-Nov-07		14:25:59		74.6		42

		30-Sep-07		16:07:10		74.01		30		30-Sep-07		16:06:20		69.8		34.5		30-Sep-07		16:07:53		71		31		10-Nov-07		16:25:59		75.2		43

		30-Sep-07		18:07:10		74.01		29		30-Sep-07		18:06:20		69.8		32.5		30-Sep-07		18:07:53		71		31		10-Nov-07		18:25:59		74.6		44

		30-Sep-07		20:07:10		75.2		28		30-Sep-07		20:06:20		72.21		31		30-Sep-07		20:07:53		71.6		32		10-Nov-07		20:25:59		72.8		44.5

		30-Sep-07		22:07:10		75.81		27.5		30-Sep-07		22:06:20		72.8		31		30-Sep-07		22:07:53		71.6		31.5		10-Nov-07		22:25:59		72.21		45.5

		1-Oct-07		0:07:10		75.2		27		1-Oct-07		0:06:20		72.8		30		1-Oct-07		0:07:53		70.41		32		11-Nov-07		0:25:59		70.41		44

		1-Oct-07		2:07:10		74.01		27.5		1-Oct-07		2:06:20		71.6		30.5		1-Oct-07		2:07:53		68.61		32		11-Nov-07		2:25:59		69.2		43

		1-Oct-07		4:07:10		72.8		27.5		1-Oct-07		4:06:20		70.41		30.5		1-Oct-07		4:07:53		68		32.5		11-Nov-07		4:25:59		68.61		43

		1-Oct-07		6:07:10		72.21		27.5		1-Oct-07		6:06:20		69.8		30		1-Oct-07		6:07:53		66.2		33		11-Nov-07		6:25:59		68		43.5

		1-Oct-07		8:07:10		71		28.5		1-Oct-07		8:06:20		68.61		31.5		1-Oct-07		8:07:53		68		32		11-Nov-07		8:25:59		68		44.5

		1-Oct-07		10:07:10		71.6		30		1-Oct-07		10:06:20		69.8		31.5		1-Oct-07		10:07:53		68.61		33.5		11-Nov-07		10:25:59		69.2		46.5

		1-Oct-07		12:07:10		72.21		30		1-Oct-07		12:06:20		70.41		32		1-Oct-07		12:07:53		70.41		33.5		11-Nov-07		12:25:59		69.2		49

		1-Oct-07		14:07:10		73.4		28.5		1-Oct-07		14:06:20		69.8		30		1-Oct-07		14:07:53		70.41		31.5		11-Nov-07		14:25:59		69.8		50.5

		1-Oct-07		16:07:10		73.4		27		1-Oct-07		16:06:20		69.8		29.5		1-Oct-07		16:07:53		70.41		30.5		11-Nov-07		16:25:59		69.8		52

		1-Oct-07		18:07:10		74.01		30		1-Oct-07		18:06:20		69.8		35.5		1-Oct-07		18:07:53		71		32		11-Nov-07		18:25:59		69.8		53

		1-Oct-07		20:07:10		75.81		33		1-Oct-07		20:06:20		72.8		38		1-Oct-07		20:07:53		72.21		37.5		11-Nov-07		20:25:59		69.2		54

		1-Oct-07		22:07:10		75.2		35.5		1-Oct-07		22:06:20		72.21		41		1-Oct-07		22:07:53		72.21		39.5		11-Nov-07		22:25:59		69.2		55

		2-Oct-07		0:07:10		75.2		35.5		2-Oct-07		0:06:20		72.8		41		2-Oct-07		0:07:53		71.6		41		12-Nov-07		0:25:59		69.2		55.5

		2-Oct-07		2:07:10		75.2		36.5		2-Oct-07		2:06:20		72.8		41		2-Oct-07		2:07:53		71		42.5		12-Nov-07		2:25:59		69.2		55.5

		2-Oct-07		4:07:10		75.2		40		2-Oct-07		4:06:20		72.8		46		2-Oct-07		4:07:53		71		46.5		12-Nov-07		4:25:59		69.2		54

		2-Oct-07		6:07:10		75.2		39		2-Oct-07		6:06:20		72.8		41		2-Oct-07		6:07:53		70.41		53.5		12-Nov-07		6:25:59		68.61		50.5

		2-Oct-07		8:07:10		74.6		44.5		2-Oct-07		8:06:20		71.6		46.5		2-Oct-07		8:07:53		71		51.5		12-Nov-07		8:25:59		68		47.5

		2-Oct-07		10:07:10		74.6		40.5		2-Oct-07		10:06:20		71.6		44.5		2-Oct-07		10:07:53		72.21		41		12-Nov-07		10:25:59		68		47.5

		2-Oct-07		12:07:10		74.6		44.5		2-Oct-07		12:06:20		71		47.5		2-Oct-07		12:07:53		72.21		51.5		12-Nov-07		12:25:59		69.2		46

		2-Oct-07		14:07:10		74.6		42		2-Oct-07		14:06:20		71.6		51		2-Oct-07		14:07:53		71.6		50		12-Nov-07		14:25:59		70.41		44

		2-Oct-07		16:07:10		75.2		38.5		2-Oct-07		16:06:20		71.6		46		2-Oct-07		16:07:53		71		46		12-Nov-07		16:25:59		71		42.5

		2-Oct-07		18:07:10		74.6		34		2-Oct-07		18:06:20		71		39.5		2-Oct-07		18:07:53		71		36		12-Nov-07		18:25:59		71		42.5

		2-Oct-07		20:07:10		75.81		37		2-Oct-07		20:06:20		72.8		41.5		2-Oct-07		20:07:53		70.41		44.5		12-Nov-07		20:25:59		69.8		42.5

		2-Oct-07		22:07:10		76.4		36.5		2-Oct-07		22:06:20		72.8		41.5		2-Oct-07		22:07:53		72.8		41		12-Nov-07		22:25:59		68.61		43

		3-Oct-07		0:07:10		75.81		35.5		3-Oct-07		0:06:20		72.8		40		3-Oct-07		0:07:53		72.21		40		13-Nov-07		0:25:59		68		42.5

		3-Oct-07		2:07:10		75.81		34.5		3-Oct-07		2:06:20		72.8		38		3-Oct-07		2:07:53		71		39.5		13-Nov-07		2:25:59		67.4		42.5

		3-Oct-07		4:07:10		74.6		34.5		3-Oct-07		4:06:20		71.6		38.5		3-Oct-07		4:07:53		69.8		39.5		13-Nov-07		4:25:59		67.4		42

		3-Oct-07		6:07:10		74.01		34.5		3-Oct-07		6:06:20		71.6		37.5		3-Oct-07		6:07:53		69.8		40		13-Nov-07		6:25:59		67.4		42.5

		3-Oct-07		8:07:10		73.4		36.5		3-Oct-07		8:06:20		71.6		42		3-Oct-07		8:07:53		71.6		39.5		13-Nov-07		8:25:59		71		40.5

		3-Oct-07		10:07:10		74.6		39		3-Oct-07		10:06:20		71.6		45		3-Oct-07		10:07:53		71.6		43.5		13-Nov-07		10:25:59		71		41

		3-Oct-07		12:07:10		74.6		38.5		3-Oct-07		12:06:20		71.6		37.5		3-Oct-07		12:07:53		72.21		43		13-Nov-07		12:25:59		74.6		39.5

		3-Oct-07		14:07:10		74.6		39		3-Oct-07		14:06:20		71.6		38		3-Oct-07		14:07:53		72.21		42		13-Nov-07		14:25:59		74.6		38.5

		3-Oct-07		16:07:10		74.6		37		3-Oct-07		16:06:20		71		41.5		3-Oct-07		16:07:53		71		42.5		13-Nov-07		16:25:59		75.2		37.5

		3-Oct-07		18:07:10		74.6		38.5		3-Oct-07		18:06:20		69.8		47.5		3-Oct-07		18:07:53		71		38		13-Nov-07		18:25:59		75.2		35.5

		3-Oct-07		20:07:10		75.81		37.5		3-Oct-07		20:06:20		72.8		43		3-Oct-07		20:07:53		71		44		13-Nov-07		20:25:59		73.4		38.5

		3-Oct-07		22:07:10		76.4		36.5		3-Oct-07		22:06:20		72.8		40		3-Oct-07		22:07:53		71.6		41.5		13-Nov-07		22:25:59		72.21		41

		4-Oct-07		0:07:10		75.81		35		4-Oct-07		0:06:20		72.8		39.5		4-Oct-07		0:07:53		71.6		40.5		14-Nov-07		0:25:59		71.6		43

		4-Oct-07		2:07:10		75.2		34.5		4-Oct-07		2:06:20		72.21		38.5		4-Oct-07		2:07:53		70.41		40.5		14-Nov-07		2:25:59		70.41		44.5

		4-Oct-07		4:07:10		74.01		34		4-Oct-07		4:06:20		71		38.5		4-Oct-07		4:07:53		69.2		40		14-Nov-07		4:25:59		69.8		45

		4-Oct-07		6:07:10		74.01		33.5		4-Oct-07		6:06:20		70.41		37		4-Oct-07		6:07:53		68.61		39.5		14-Nov-07		6:25:59		69.8		47

		4-Oct-07		8:07:10		74.01		34.5		4-Oct-07		8:06:20		71.6		39		4-Oct-07		8:07:53		70.41		38		14-Nov-07		8:25:59		73.4		46

		4-Oct-07		10:07:10		74.6		36		4-Oct-07		10:06:20		72.21		41		4-Oct-07		10:07:53		71.6		35.5		14-Nov-07		10:25:59		74.6		47

		4-Oct-07		12:07:10		76.4		36		4-Oct-07		12:06:20		72.21		41.5		4-Oct-07		12:07:53		71.6		45.5		14-Nov-07		12:25:59		74.6		48.5

		4-Oct-07		14:07:10		75.81		35		4-Oct-07		14:06:20		72.21		36		4-Oct-07		14:07:53		72.21		35.5		14-Nov-07		14:25:59		75.2		49.5

		4-Oct-07		16:07:10		76.4		38.5		4-Oct-07		16:06:20		71		41.5		4-Oct-07		16:07:53		71		49		14-Nov-07		16:25:59		75.2		49.5

		4-Oct-07		18:07:10		76.4		33.5		4-Oct-07		18:06:20		70.41		40		4-Oct-07		18:07:53		70.41		41		14-Nov-07		18:25:59		75.2		49.5

		4-Oct-07		20:07:10		76.4		34		4-Oct-07		20:06:20		72.8		38.5		4-Oct-07		20:07:53		72.8		37.5		14-Nov-07		20:25:59		74.6		49

		4-Oct-07		22:07:10		76.4		31.5		4-Oct-07		22:06:20		72.8		35.5		4-Oct-07		22:07:53		72.8		35		14-Nov-07		22:25:59		74.01		52

		5-Oct-07		0:07:10		75.81		30.5		5-Oct-07		0:06:20		72.8		34.5		5-Oct-07		0:07:53		72.21		34.5		15-Nov-07		0:25:59		72.8		50.5

		5-Oct-07		2:07:10		75.2		29		5-Oct-07		2:06:20		72.8		32.5		5-Oct-07		2:07:53		71		33.5		15-Nov-07		2:25:59		71.6		51

		5-Oct-07		4:07:10		74.6		28.5		5-Oct-07		4:06:20		72.8		31		5-Oct-07		4:07:53		69.8		32.5		15-Nov-07		4:25:59		71		50

		5-Oct-07		6:07:10		74.6		29		5-Oct-07		6:06:20		72.21		31.5		5-Oct-07		6:07:53		69.8		33.5		15-Nov-07		6:25:59		69.8		49

		5-Oct-07		8:07:10		74.01		30.5		5-Oct-07		8:06:20		71.6		33.5		5-Oct-07		8:07:53		71		34		15-Nov-07		8:25:59		72.8		44.5

		5-Oct-07		10:07:10		74.6		31.5		5-Oct-07		10:06:20		72.21		36.5		5-Oct-07		10:07:53		71.6		32.5		15-Nov-07		10:25:59		74.6		47

		5-Oct-07		12:07:10		75.2		32		5-Oct-07		12:06:20		71.6		34		5-Oct-07		12:07:53		71.6		33		15-Nov-07		12:25:59		74.6		48.5

		5-Oct-07		14:07:10		75.2		33		5-Oct-07		14:06:20		72.21		39.5		5-Oct-07		14:07:53		71.6		38.5		15-Nov-07		14:25:59		75.2		48

		5-Oct-07		16:07:10		75.81		32		5-Oct-07		16:06:20		70.41		39.5		5-Oct-07		16:07:53		71		35.5		15-Nov-07		16:25:59		75.2		49

		5-Oct-07		18:07:10		75.2		30		5-Oct-07		18:06:20		69.8		35		5-Oct-07		18:07:53		70.41		34.5		15-Nov-07		18:25:59		74.6		50

		5-Oct-07		20:07:10		75.81		29.5		5-Oct-07		20:06:20		72.21		33.5		5-Oct-07		20:07:53		70.41		34.5		15-Nov-07		20:25:59		74.01		50

		5-Oct-07		22:07:10		75.2		29.5		5-Oct-07		22:06:20		72.21		33.5		5-Oct-07		22:07:53		69.8		34.5		15-Nov-07		22:25:59		74.01		49.5

		6-Oct-07		0:07:10		75.2		29.5		6-Oct-07		0:06:20		72.21		33.5		6-Oct-07		0:07:53		69.2		35		16-Nov-07		0:25:59		72.21		49.5

		6-Oct-07		2:07:10		74.01		30		6-Oct-07		2:06:20		71.6		33.5		6-Oct-07		2:07:53		68		35.5		16-Nov-07		2:25:59		71		48.5

		6-Oct-07		4:07:10		72.8		29.5		6-Oct-07		4:06:20		70.41		33		6-Oct-07		4:07:53		66.81		36		16-Nov-07		4:25:59		69.8		48

		6-Oct-07		6:07:10		72.8		29		6-Oct-07		6:06:20		72.21		30		6-Oct-07		6:07:53		68		34.5		16-Nov-07		6:25:59		69.8		47

		6-Oct-07		8:07:10		72.8		29.5		6-Oct-07		8:06:20		71.6		34.5		6-Oct-07		8:07:53		69.2		33		16-Nov-07		8:25:59		72.8		42.5

		6-Oct-07		10:07:10		73.4		30.5		6-Oct-07		10:06:20		71.6		33.5		6-Oct-07		10:07:53		71.6		31		16-Nov-07		10:25:59		74.01		44

		6-Oct-07		12:07:10		74.01		30.5		6-Oct-07		12:06:20		70.41		36		6-Oct-07		12:07:53		71.6		34.5		16-Nov-07		12:25:59		74.6		47

		6-Oct-07		14:07:10		75.2		28		6-Oct-07		14:06:20		69.2		32.5		6-Oct-07		14:07:53		71		30.5		16-Nov-07		14:25:59		74.6		49.5

		6-Oct-07		16:07:10		75.2		27		6-Oct-07		16:06:20		69.2		31.5		6-Oct-07		16:07:53		70.41		31.5		16-Nov-07		16:25:59		75.81		49.5

		6-Oct-07		18:07:10		75.81		27.5		6-Oct-07		18:06:20		69.2		33		6-Oct-07		18:07:53		71		30		16-Nov-07		18:25:59		75.81		49.5

		6-Oct-07		20:07:10		76.4		27.5		6-Oct-07		20:06:20		72.21		31.5		6-Oct-07		20:07:53		70.41		33.5		16-Nov-07		20:25:59		74.01		50

		6-Oct-07		22:07:10		75.81		27		6-Oct-07		22:06:20		73.4		31.5		6-Oct-07		22:07:53		70.41		33		16-Nov-07		22:25:59		73.4		51.5

		7-Oct-07		0:07:10		75.2		27		7-Oct-07		0:06:20		72.8		30.5		7-Oct-07		0:07:53		69.8		32.5		17-Nov-07		0:25:59		72.21		51

		7-Oct-07		2:07:10		74.6		27		7-Oct-07		2:06:20		72.21		31		7-Oct-07		2:07:53		68.61		33		17-Nov-07		2:25:59		71		51.5

		7-Oct-07		4:07:10		74.01		28		7-Oct-07		4:06:20		71.6		31.5		7-Oct-07		4:07:53		68		34		17-Nov-07		4:25:59		70.41		51.5

		7-Oct-07		6:07:10		72.8		28.5		7-Oct-07		6:06:20		71		32		7-Oct-07		6:07:53		66.81		35		17-Nov-07		6:25:59		70.41		52

		7-Oct-07		8:07:10		72.21		29		7-Oct-07		8:06:20		69.2		32.5		7-Oct-07		8:07:53		67.4		34		17-Nov-07		8:25:59		71		50.5

		7-Oct-07		10:07:10		71.6		31		7-Oct-07		10:06:20		68.61		34.5		7-Oct-07		10:07:53		68.61		35		17-Nov-07		10:25:59		71.6		50.5

		7-Oct-07		12:07:10		72.21		29		7-Oct-07		12:06:20		68.61		31		7-Oct-07		12:07:53		70.41		31.5		17-Nov-07		12:25:59		72.8		50

		7-Oct-07		14:07:10		72.8		26.5		7-Oct-07		14:06:20		69.2		28.5		7-Oct-07		14:07:53		70.41		29		17-Nov-07		14:25:59		75.2		49.5

		7-Oct-07		16:07:10		73.4		27		7-Oct-07		16:06:20		69.2		31		7-Oct-07		16:07:53		70.41		30.5		17-Nov-07		16:25:59		75.2		48

		7-Oct-07		18:07:10		74.01		26		7-Oct-07		18:06:20		69.8		29.5		7-Oct-07		18:07:53		71		29		17-Nov-07		18:25:59		74.6		49

		7-Oct-07		20:07:10		75.2		25		7-Oct-07		20:06:20		72.21		28.5		7-Oct-07		20:07:53		71		29		17-Nov-07		20:25:59		72.8		48.5

		7-Oct-07		22:07:10		75.2		26.5		7-Oct-07		22:06:20		72.8		31		7-Oct-07		22:07:53		70.41		31.5		17-Nov-07		22:25:59		72.21		49

		8-Oct-07		0:07:10		74.6		26.5		8-Oct-07		0:06:20		72.21		30.5		8-Oct-07		0:07:53		69.2		31.5		18-Nov-07		0:25:59		71		52

		8-Oct-07		2:07:10		73.4		25.5		8-Oct-07		2:06:20		71		29		8-Oct-07		2:07:53		68		31		18-Nov-07		2:25:59		70.41		51

		8-Oct-07		4:07:10		72.8		26		8-Oct-07		4:06:20		69.8		29		8-Oct-07		4:07:53		66.81		31.5		18-Nov-07		4:25:59		69.8		50.5

		8-Oct-07		6:07:10		71.6		26		8-Oct-07		6:06:20		69.2		29.5		8-Oct-07		6:07:53		65.6		32		18-Nov-07		6:25:59		69.2		51

		8-Oct-07		8:07:10		71		27		8-Oct-07		8:06:20		68.61		30		8-Oct-07		8:07:53		67.4		31		18-Nov-07		8:25:59		68.61		50.5

		8-Oct-07		10:07:10		71.6		28.5		8-Oct-07		10:06:20		68.61		32		8-Oct-07		10:07:53		68		32.5		18-Nov-07		10:25:59		68.61		51

		8-Oct-07		12:07:10		72.21		29.5		8-Oct-07		12:06:20		69.2		33		8-Oct-07		12:07:53		69.8		33		18-Nov-07		12:25:59		69.2		51.5

		8-Oct-07		14:07:10		72.8		31		8-Oct-07		14:06:20		69.2		34.5		8-Oct-07		14:07:53		70.41		34.5		18-Nov-07		14:25:59		69.8		52

		8-Oct-07		16:07:10		73.4		30.5		8-Oct-07		16:06:20		69.2		35.5		8-Oct-07		16:07:53		70.41		35.5		18-Nov-07		16:25:59		71.6		54

		8-Oct-07		18:07:10		74.01		31.5		8-Oct-07		18:06:20		69.2		35		8-Oct-07		18:07:53		71		34		18-Nov-07		18:25:59		72.21		54

		8-Oct-07		20:07:10		75.2		33.5		8-Oct-07		20:06:20		72.21		36		8-Oct-07		20:07:53		71.6		38.5		18-Nov-07		20:25:59		71		53

		8-Oct-07		22:07:10		75.2		34.5		8-Oct-07		22:06:20		72.21		39.5		8-Oct-07		22:07:53		71		40		18-Nov-07		22:25:59		69.8		53

		9-Oct-07		0:07:10		74.6		34		9-Oct-07		0:06:20		72.21		38.5		9-Oct-07		0:07:53		69.8		40		19-Nov-07		0:25:59		69.2		53

		9-Oct-07		2:07:10		74.01		33.5		9-Oct-07		2:06:20		71.6		37.5		9-Oct-07		2:07:53		68.61		40		19-Nov-07		2:25:59		69.2		53

		9-Oct-07		4:07:10		73.4		33		9-Oct-07		4:06:20		71		36.5		9-Oct-07		4:07:53		67.4		39.5		19-Nov-07		4:25:59		68.61		53

		9-Oct-07		6:07:10		73.4		32.5		9-Oct-07		6:06:20		69.8		36		9-Oct-07		6:07:53		68.61		37.5		19-Nov-07		6:25:59		68.61		53

		9-Oct-07		8:07:10		72.8		33.5		9-Oct-07		8:06:20		69.8		38.5		9-Oct-07		8:07:53		70.41		36		19-Nov-07		8:25:59		68		53

		9-Oct-07		10:07:10		73.4		37.5		9-Oct-07		10:06:20		71		45		9-Oct-07		10:07:53		71.6		37		19-Nov-07		10:25:59		68.61		53

		9-Oct-07		12:07:10		74.6		35.5		9-Oct-07		12:06:20		71		41		9-Oct-07		12:07:53		71.6		42		19-Nov-07		12:25:59		68.61		55

		9-Oct-07		14:07:10		74.6		36		9-Oct-07		14:06:20		71		41		9-Oct-07		14:07:53		71.6		38.5		19-Nov-07		14:25:59		69.8		56

		9-Oct-07		16:07:10		75.2		34		9-Oct-07		16:06:20		69.8		42		9-Oct-07		16:07:53		71.6		37		19-Nov-07		16:25:59		71		57.5

		9-Oct-07		18:07:10		74.01		36.5		9-Oct-07		18:06:20		69.2		44.5		9-Oct-07		18:07:53		71		41.5		19-Nov-07		18:25:59		71.6		56.5

		9-Oct-07		20:07:10		75.81		32		9-Oct-07		20:06:20		72.8		35.5		9-Oct-07		20:07:53		71		37.5		19-Nov-07		20:25:59		71		55

		9-Oct-07		22:07:10		76.4		33.5		9-Oct-07		22:06:20		73.4		38.5		9-Oct-07		22:07:53		71.6		39		19-Nov-07		22:25:59		70.41		54.5

		10-Oct-07		0:07:10		75.81		34.5		10-Oct-07		0:06:20		72.8		39.5		10-Oct-07		0:07:53		70.41		41		20-Nov-07		0:25:59		69.2		53.5

		10-Oct-07		2:07:10		75.2		35.5		10-Oct-07		2:06:20		72.21		40.5		10-Oct-07		2:07:53		69.8		42		20-Nov-07		2:25:59		68.61		52.5

		10-Oct-07		4:07:10		74.6		36		10-Oct-07		4:06:20		72.21		40.5		10-Oct-07		4:07:53		69.2		43		20-Nov-07		4:25:59		68		53

		10-Oct-07		6:07:10		74.6		37.5		10-Oct-07		6:06:20		71		44.5		10-Oct-07		6:07:53		69.2		45		20-Nov-07		6:25:59		68.61		54.5

		10-Oct-07		8:07:10		74.01		39		10-Oct-07		8:06:20		71		38.5		10-Oct-07		8:07:53		71.6		44		20-Nov-07		8:25:59		71.6		54

		10-Oct-07		10:07:10		74.01		43		10-Oct-07		10:06:20		69.8		48.5		10-Oct-07		10:07:53		71		44		20-Nov-07		10:25:59		74.01		55

		10-Oct-07		12:07:10		74.6		42.5		10-Oct-07		12:06:20		70.41		48.5		10-Oct-07		12:07:53		71.6		43		20-Nov-07		12:25:59		74.01		53.5

		10-Oct-07		14:07:10		74.6		44.5		10-Oct-07		14:06:20		71		50.5		10-Oct-07		14:07:53		71		51.5		20-Nov-07		14:25:59		73.4		48.5

		10-Oct-07		16:07:10		74.6		42		10-Oct-07		16:06:20		69.8		57		10-Oct-07		16:07:53		70.41		49		20-Nov-07		16:25:59		74.01		45

		10-Oct-07		18:07:10		74.01		41		10-Oct-07		18:06:20		69.8		51		10-Oct-07		18:07:53		70.41		48		20-Nov-07		18:25:59		74.01		43

		10-Oct-07		20:07:10		75.2		41		10-Oct-07		20:06:20		72.21		47		10-Oct-07		20:07:53		69.8		50		20-Nov-07		20:25:59		72.21		43

		10-Oct-07		22:07:10		75.2		43		10-Oct-07		22:06:20		72.21		50.5		10-Oct-07		22:07:53		69.8		50		20-Nov-07		22:25:59		71		44.5

		11-Oct-07		0:07:10		74.6		44		11-Oct-07		0:06:20		72.21		51		11-Oct-07		0:07:53		69.8		51		21-Nov-07		0:25:59		69.8		44

		11-Oct-07		2:07:10		74.6		44		11-Oct-07		2:06:20		71.6		50.5		11-Oct-07		2:07:53		69.2		51		21-Nov-07		2:25:59		68.61		43

		11-Oct-07		4:07:10		74.01		44		11-Oct-07		4:06:20		71.6		49.5		11-Oct-07		4:07:53		69.2		51.5		21-Nov-07		4:25:59		68		42.5

		11-Oct-07		6:07:10		74.01		44		11-Oct-07		6:06:20		71		50.5		11-Oct-07		6:07:53		69.2		51		21-Nov-07		6:25:59		68		41

		11-Oct-07		8:07:10		73.4		44.5		11-Oct-07		8:06:20		70.41		45		11-Oct-07		8:07:53		71		49		21-Nov-07		8:25:59		71.6		37

		11-Oct-07		10:07:10		73.4		43		11-Oct-07		10:06:20		71.6		45		11-Oct-07		10:07:53		71		48		21-Nov-07		10:25:59		71.6		38

		11-Oct-07		12:07:10		74.01		46		11-Oct-07		12:06:20		70.41		51		11-Oct-07		12:07:53		71.6		49		21-Nov-07		12:25:59		72.21		38.5

		11-Oct-07		14:07:10		74.6		41.5		11-Oct-07		14:06:20		71		41		11-Oct-07		14:07:53		71		49.5		21-Nov-07		14:25:59		72.8		37.5

		11-Oct-07		16:07:10		75.2		46.5		11-Oct-07		16:06:20		69.2		59.5		11-Oct-07		16:07:53		70.41		53		21-Nov-07		16:25:59		73.4		37

		11-Oct-07		18:07:10		74.6		39.5		11-Oct-07		18:06:20		69.8		45		11-Oct-07		18:07:53		70.41		47		21-Nov-07		18:25:59		73.4		38

		11-Oct-07		20:07:10		75.2		40		11-Oct-07		20:06:20		72.21		45		11-Oct-07		20:07:53		70.41		46		21-Nov-07		20:25:59		71.6		38

		11-Oct-07		22:07:10		74.6		39.5		11-Oct-07		22:06:20		72.21		44		11-Oct-07		22:07:53		69.8		45.5		21-Nov-07		22:25:59		69.8		38.5

		12-Oct-07		0:07:10		74.01		38.5		12-Oct-07		0:06:20		72.21		42.5		12-Oct-07		0:07:53		68.61		45		22-Nov-07		0:25:59		68.61		38.5

		12-Oct-07		2:07:10		73.4		38		12-Oct-07		2:06:20		71.6		42		12-Oct-07		2:07:53		67.4		45.5		22-Nov-07		2:25:59		67.4		37.5

		12-Oct-07		4:07:10		72.21		38.5		12-Oct-07		4:06:20		71		42.5		12-Oct-07		4:07:53		66.81		46.5		22-Nov-07		4:25:59		66.81		36.5

		12-Oct-07		6:07:10		72.21		38		12-Oct-07		6:06:20		70.41		41.5		12-Oct-07		6:07:53		68.61		44		22-Nov-07		6:25:59		67.4		35

		12-Oct-07		8:07:10		72.21		38		12-Oct-07		8:06:20		70.41		43.5		12-Oct-07		8:07:53		69.8		42		22-Nov-07		8:25:59		70.41		32.5

		12-Oct-07		10:07:10		72.8		43.5		12-Oct-07		10:06:20		71		51.5		12-Oct-07		10:07:53		71.6		40		22-Nov-07		10:25:59		71.6		33.5

		12-Oct-07		12:07:10		73.4		40.5		12-Oct-07		12:06:20		70.41		45.5		12-Oct-07		12:07:53		71.6		49		22-Nov-07		12:25:59		72.21		35

		12-Oct-07		14:07:10		73.4		43.5		12-Oct-07		14:06:20		69.8		41		12-Oct-07		14:07:53		71		44.5		22-Nov-07		14:25:59		73.4		34

		12-Oct-07		16:07:10		74.01		45		12-Oct-07		16:06:20		69.2		56.5		12-Oct-07		16:07:53		71		46.5		22-Nov-07		16:25:59		72.8		32.5

		12-Oct-07		18:07:10		74.01		39.5		12-Oct-07		18:06:20		69.8		46.5		12-Oct-07		18:07:53		70.41		44.5		22-Nov-07		18:25:59		72.8		34.5

		12-Oct-07		20:07:10		74.6		38.5		12-Oct-07		20:06:20		72.21		42		12-Oct-07		20:07:53		70.41		44		22-Nov-07		20:25:59		71		34

		12-Oct-07		22:07:10		75.2		37		12-Oct-07		22:06:20		72.8		40.5		12-Oct-07		22:07:53		69.8		43.5		22-Nov-07		22:25:59		69.2		35

		13-Oct-07		0:07:10		74.6		36.5		13-Oct-07		0:06:20		72.21		40		13-Oct-07		0:07:53		68.61		44		23-Nov-07		0:25:59		68		35

		13-Oct-07		2:07:10		74.01		38		13-Oct-07		2:06:20		72.21		42		13-Oct-07		2:07:53		68		46		23-Nov-07		2:25:59		66.81		34.5

		13-Oct-07		4:07:10		74.01		39.5		13-Oct-07		4:06:20		72.21		44		13-Oct-07		4:07:53		67.4		48.5		23-Nov-07		4:25:59		66.2		34

		13-Oct-07		6:07:10		73.4		40		13-Oct-07		6:06:20		71		46		13-Oct-07		6:07:53		68.61		48		23-Nov-07		6:25:59		66.81		32.5

		13-Oct-07		8:07:10		72.8		44		13-Oct-07		8:06:20		71		45		13-Oct-07		8:07:53		70.41		48.5		23-Nov-07		8:25:59		69.2		30.5

		13-Oct-07		10:07:10		72.8		44		13-Oct-07		10:06:20		71		43		13-Oct-07		10:07:53		71		50		23-Nov-07		10:25:59		71.6		31

		13-Oct-07		12:07:10		73.4		44		13-Oct-07		12:06:20		70.41		54.5		13-Oct-07		12:07:53		71.6		52		23-Nov-07		12:25:59		70.41		33

		13-Oct-07		14:07:10		73.4		46.5		13-Oct-07		14:06:20		70.41		51		13-Oct-07		14:07:53		71		50		23-Nov-07		14:25:59		71		33.5

		13-Oct-07		16:07:10		72.8		49.5		13-Oct-07		16:06:20		69.2		61		13-Oct-07		16:07:53		71		53		23-Nov-07		16:25:59		71		32.5

		13-Oct-07		18:07:10		72.8		44		13-Oct-07		18:06:20		69.8		50		13-Oct-07		18:07:53		70.41		50.5		23-Nov-07		18:25:59		71		34

		13-Oct-07		20:07:10		73.4		43.5		13-Oct-07		20:06:20		71		48		13-Oct-07		20:07:53		69.8		48.5		23-Nov-07		20:25:59		70.41		34.5

		13-Oct-07		22:07:10		73.4		42.5		13-Oct-07		22:06:20		71.6		46.5		13-Oct-07		22:07:53		68.61		49		23-Nov-07		22:25:59		68.61		34.5

		14-Oct-07		0:07:10		72.21		41.5		14-Oct-07		0:06:20		71		45		14-Oct-07		0:07:53		67.4		49		24-Nov-07		0:25:59		67.4		34.5

		14-Oct-07		2:07:10		71.6		40.5		14-Oct-07		2:06:20		69.8		43.5		14-Oct-07		2:07:53		66.2		48		24-Nov-07		2:25:59		66.81		34

		14-Oct-07		4:07:10		71		40		14-Oct-07		4:06:20		69.2		42.5		14-Oct-07		4:07:53		65.6		47.5		24-Nov-07		4:25:59		66.2		33.5

		14-Oct-07		6:07:10		70.41		39		14-Oct-07		6:06:20		68.61		41		14-Oct-07		6:07:53		65.6		46		24-Nov-07		6:25:59		66.81		32.5

		14-Oct-07		8:07:10		71		37.5		14-Oct-07		8:06:20		68.61		40.5		14-Oct-07		8:07:53		67.4		41.5		24-Nov-07		8:25:59		68.61		29.5

		14-Oct-07		10:07:10		71.6		43.5		14-Oct-07		10:06:20		68.61		49		14-Oct-07		10:07:53		68.61		48.5		24-Nov-07		10:25:59		70.41		25.5

		14-Oct-07		12:07:10		72.21		46		14-Oct-07		12:06:20		68.61		49.5		14-Oct-07		12:07:53		69.8		49.5		24-Nov-07		12:25:59		69.8		24

		14-Oct-07		14:07:10		72.8		47		14-Oct-07		14:06:20		69.2		54		14-Oct-07		14:07:53		70.41		50		24-Nov-07		14:25:59		70.41		23

		14-Oct-07		16:07:10		72.8		45.5		14-Oct-07		16:06:20		69.2		45.5		14-Oct-07		16:07:53		70.41		45.5		24-Nov-07		16:25:59		71.6		22.5

		14-Oct-07		18:07:10		73.4		46		14-Oct-07		18:06:20		69.2		53.5		14-Oct-07		18:07:53		70.41		52.5		24-Nov-07		18:25:59		71		22.5

		14-Oct-07		20:07:10		74.6		44.5		14-Oct-07		20:06:20		71.6		49		14-Oct-07		20:07:53		69.8		50.5		24-Nov-07		20:25:59		69.8		24.5

		14-Oct-07		22:07:10		74.01		43		14-Oct-07		22:06:20		72.21		47		14-Oct-07		22:07:53		69.2		50		24-Nov-07		22:25:59		68.61		27

		15-Oct-07		0:07:10		74.01		43		15-Oct-07		0:06:20		72.21		47		15-Oct-07		0:07:53		68.61		51.5		25-Nov-07		0:25:59		67.4		28

		15-Oct-07		2:07:10		74.01		43.5		15-Oct-07		2:06:20		72.21		47		15-Oct-07		2:07:53		68		52		25-Nov-07		2:25:59		66.81		28.5

		15-Oct-07		4:07:10		73.4		43.5		15-Oct-07		4:06:20		71.6		47		15-Oct-07		4:07:53		67.4		52		25-Nov-07		4:25:59		66.2		28.5

		15-Oct-07		6:07:10		72.8		43.5		15-Oct-07		6:06:20		71		43		15-Oct-07		6:07:53		66.81		52.5		25-Nov-07		6:25:59		65.6		28.5

		15-Oct-07		8:07:10		71.6		45		15-Oct-07		8:06:20		69.2		50		15-Oct-07		8:07:53		68.61		49.5		25-Nov-07		8:25:59		65.6		28

		15-Oct-07		10:07:10		71		46.5		15-Oct-07		10:06:20		68.61		52		15-Oct-07		10:07:53		68		52		25-Nov-07		10:25:59		65.6		29

		15-Oct-07		12:07:10		71		46		15-Oct-07		12:06:20		69.2		52		15-Oct-07		12:07:53		68		53		25-Nov-07		12:25:59		66.2		30.5

		15-Oct-07		14:07:10		71.6		48		15-Oct-07		14:06:20		69.2		45		15-Oct-07		14:07:53		69.2		53		25-Nov-07		14:25:59		68		30

		15-Oct-07		16:07:10		72.21		49.5		15-Oct-07		16:06:20		69.2		49.5		15-Oct-07		16:07:53		69.8		53.5		25-Nov-07		16:25:59		68		30.5

		15-Oct-07		18:07:10		72.8		48		15-Oct-07		18:06:20		69.2		54.5		15-Oct-07		18:07:53		69.8		53.5		25-Nov-07		18:25:59		68		31.5

		15-Oct-07		20:07:10		74.01		44		15-Oct-07		20:06:20		71.6		48		15-Oct-07		20:07:53		69.8		50		25-Nov-07		20:25:59		67.4		32

		15-Oct-07		22:07:10		73.4		42.5		15-Oct-07		22:06:20		71.6		45.5		15-Oct-07		22:07:53		68		50		25-Nov-07		22:25:59		66.81		33

		16-Oct-07		0:07:10		72.8		42		16-Oct-07		0:06:20		71		45.5		16-Oct-07		0:07:53		66.81		50.5		26-Nov-07		0:25:59		66.81		33.5

		16-Oct-07		2:07:10		72.21		42		16-Oct-07		2:06:20		71		45.5		16-Oct-07		2:07:53		66.2		51		26-Nov-07		2:25:59		66.2		33.5

		16-Oct-07		4:07:10		72.21		42.5		16-Oct-07		4:06:20		70.41		46		16-Oct-07		4:07:53		65.6		51.5		26-Nov-07		4:25:59		66.2		34

		16-Oct-07		6:07:10		72.21		43		16-Oct-07		6:06:20		70.41		46.5		16-Oct-07		6:07:53		68.61		48.5		26-Nov-07		6:25:59		66.2		34

		16-Oct-07		8:07:10		72.21		45.5		16-Oct-07		8:06:20		70.41		51.5		16-Oct-07		8:07:53		68.61		49.5		26-Nov-07		8:25:59		65.6		34.5

		16-Oct-07		10:07:10		72.8		45.5		16-Oct-07		10:06:20		71.6		54.5		16-Oct-07		10:07:53		71		49.5		26-Nov-07		10:25:59		65.6		35.5

		16-Oct-07		12:07:10		72.8		48.5		16-Oct-07		12:06:20		69.8		44.5		16-Oct-07		12:07:53		71.6		53		26-Nov-07		12:25:59		66.2		36.5

		16-Oct-07		14:07:10		72.8		53		16-Oct-07		14:06:20		71		54		16-Oct-07		14:07:53		71		57.5		26-Nov-07		14:25:59		66.2		35.5

		16-Oct-07		16:07:10		74.01		48.5		16-Oct-07		16:06:20		69.8		59.5		16-Oct-07		16:07:53		70.41		55.5		26-Nov-07		16:25:59		66.81		35

		16-Oct-07		18:07:10		73.4		47.5		16-Oct-07		18:06:20		70.41		57.5		16-Oct-07		18:07:53		69.8		54.5		26-Nov-07		18:25:59		67.4		35.5

		16-Oct-07		20:07:10		74.6		48		16-Oct-07		20:06:20		72.21		53		16-Oct-07		20:07:53		70.41		54.5		26-Nov-07		20:25:59		66.81		36

		16-Oct-07		22:07:10		74.6		47		16-Oct-07		22:06:20		72.21		51		16-Oct-07		22:07:53		69.8		54		26-Nov-07		22:25:59		66.2		35.5

		17-Oct-07		0:07:10		74.01		45		17-Oct-07		0:06:20		72.8		48.5		17-Oct-07		0:07:53		69.2		52.5		27-Nov-07		0:25:59		65.6		35.5

		17-Oct-07		2:07:10		73.4		43		17-Oct-07		2:06:20		71.6		45.5		17-Oct-07		2:07:53		68		51		27-Nov-07		2:25:59		65.6		34.5

		17-Oct-07		4:07:10		72.8		42.5		17-Oct-07		4:06:20		71		45		17-Oct-07		4:07:53		66.81		50.5		27-Nov-07		4:25:59		65.01		34

		17-Oct-07		6:07:10		72.8		43		17-Oct-07		6:06:20		70.41		44.5		17-Oct-07		6:07:53		68		49		27-Nov-07		6:25:59		66.2		32.5

		17-Oct-07		8:07:10		71.6		43.5		17-Oct-07		8:06:20		69.8		48		17-Oct-07		8:07:53		69.8		46		27-Nov-07		8:25:59		68.61		30.5

		17-Oct-07		10:07:10		72.8		43.5		17-Oct-07		10:06:20		71		52.5		17-Oct-07		10:07:53		71		46		27-Nov-07		10:25:59		70.41		32.5

		17-Oct-07		12:07:10		73.4		46		17-Oct-07		12:06:20		71		55.5		17-Oct-07		12:07:53		71.6		46		27-Nov-07		12:25:59		72.21		33.5

		17-Oct-07		14:07:10		73.4		47		17-Oct-07		14:06:20		71		41		17-Oct-07		14:07:53		71		52.5		27-Nov-07		14:25:59		72.8		34.5

		17-Oct-07		16:07:10		72.8		53		17-Oct-07		16:06:20		69.2		55.5		17-Oct-07		16:07:53		70.41		60.5		27-Nov-07		16:25:59		73.4		35.5

		17-Oct-07		18:07:10		72.8		52		17-Oct-07		18:06:20		69.2		60		17-Oct-07		18:07:53		69.8		55.5		27-Nov-07		18:25:59		72.8		37

		17-Oct-07		20:07:10		72.8		46.5		17-Oct-07		20:06:20		71		49.5		17-Oct-07		20:07:53		69.8		51.5		27-Nov-07		20:25:59		71		37

		17-Oct-07		22:07:10		72.21		44		17-Oct-07		22:06:20		71		46.5		17-Oct-07		22:07:53		68		49.5		27-Nov-07		22:25:59		69.8		36.5

		18-Oct-07		0:07:10		71		42		18-Oct-07		0:06:20		69.8		44		18-Oct-07		0:07:53		66.81		48.5		28-Nov-07		0:25:59		68.61		36.5

		18-Oct-07		2:07:10		70.41		41		18-Oct-07		2:06:20		69.2		43		18-Oct-07		2:07:53		66.2		47.5		28-Nov-07		2:25:59		67.4		36.5

		18-Oct-07		4:07:10		70.41		41.5		18-Oct-07		4:06:20		69.2		44		18-Oct-07		4:07:53		66.2		48.5		28-Nov-07		4:25:59		66.81		36.5

		18-Oct-07		6:07:10		71		43.5		18-Oct-07		6:06:20		69.8		46		18-Oct-07		6:07:53		68		48		28-Nov-07		6:25:59		67.4		36

		18-Oct-07		8:07:10		71.6		44.5		18-Oct-07		8:06:20		71		49.5		18-Oct-07		8:07:53		69.8		46		28-Nov-07		8:25:59		69.8		35

		18-Oct-07		10:07:10		74.01		45.5		18-Oct-07		10:06:20		74.01		41.5		18-Oct-07		10:07:53		71		51.5		28-Nov-07		10:25:59		73.4		36

		18-Oct-07		12:07:10		74.6		44		18-Oct-07		12:06:20		73.4		46.5		18-Oct-07		12:07:53		71.6		50.5		28-Nov-07		12:25:59		72.8		38.5

		18-Oct-07		14:07:10		75.2		41.5		18-Oct-07		14:06:20		74.6		37.5		18-Oct-07		14:07:53		71.6		45		28-Nov-07		14:25:59		73.4		35

		18-Oct-07		16:07:10		75.2		41		18-Oct-07		16:06:20		72.21		41.5		18-Oct-07		16:07:53		70.41		47		28-Nov-07		16:25:59		74.01		34

		18-Oct-07		18:07:10		74.6		41.5		18-Oct-07		18:06:20		71.6		42.5		18-Oct-07		18:07:53		70.41		48.5		28-Nov-07		18:25:59		74.01		35.5

		18-Oct-07		20:07:10		74.6		41		18-Oct-07		20:06:20		72.8		44		18-Oct-07		20:07:53		69.8		47		28-Nov-07		20:25:59		72.21		37

		18-Oct-07		22:07:10		73.4		40.5		18-Oct-07		22:06:20		72.21		43		18-Oct-07		22:07:53		68.61		47.5		28-Nov-07		22:25:59		71		37

		19-Oct-07		0:07:10		72.8		41		19-Oct-07		0:06:20		72.21		43.5		19-Oct-07		0:07:53		67.4		48.5		29-Nov-07		0:25:59		69.8		37

		19-Oct-07		2:07:10		72.21		41.5		19-Oct-07		2:06:20		71		43.5		19-Oct-07		2:07:53		66.81		49.5		29-Nov-07		2:25:59		68.61		37

		19-Oct-07		4:07:10		71.6		42.5		19-Oct-07		4:06:20		71		44.5		19-Oct-07		4:07:53		66.2		52		29-Nov-07		4:25:59		67.4		36.5

		19-Oct-07		6:07:10		71.6		43		19-Oct-07		6:06:20		71		45.5		19-Oct-07		6:07:53		68		49		29-Nov-07		6:25:59		67.4		34.5

		19-Oct-07		8:07:10		72.21		44		19-Oct-07		8:06:20		72.21		47		19-Oct-07		8:07:53		69.2		48		29-Nov-07		8:25:59		69.8		32

		19-Oct-07		10:07:10		72.8		43.5		19-Oct-07		10:06:20		72.21		40		19-Oct-07		10:07:53		71		49.5		29-Nov-07		10:25:59		72.21		33

		19-Oct-07		12:07:10		74.01		44.5		19-Oct-07		12:06:20		72.21		49.5		19-Oct-07		12:07:53		71.6		51		29-Nov-07		12:25:59		72.21		33

		19-Oct-07		14:07:10		75.2		47		19-Oct-07		14:06:20		72.8		47		19-Oct-07		14:07:53		71		54		29-Nov-07		14:25:59		73.4		32.5

		19-Oct-07		16:07:10		74.6		47		19-Oct-07		16:06:20		71.6		45.5		19-Oct-07		16:07:53		71		48		29-Nov-07		16:25:59		73.4		32

		19-Oct-07		18:07:10		74.6		51.5		19-Oct-07		18:06:20		71		56.5		19-Oct-07		18:07:53		70.41		58.5		29-Nov-07		18:25:59		72.8		30.5

		19-Oct-07		20:07:10		74.6		51.5		19-Oct-07		20:06:20		72.8		57		19-Oct-07		20:07:53		70.41		58		29-Nov-07		20:25:59		71		32

		19-Oct-07		22:07:10		74.01		52.5		19-Oct-07		22:06:20		73.4		56		19-Oct-07		22:07:53		70.41		59		29-Nov-07		22:25:59		69.8		32.5

		20-Oct-07		0:07:10		74.01		53		20-Oct-07		0:06:20		72.8		57.5		20-Oct-07		0:07:53		70.41		60.5		30-Nov-07		0:25:59		69.2		33

		20-Oct-07		2:07:10		73.4		55.5		20-Oct-07		2:06:20		72.8		59		20-Oct-07		2:07:53		69.8		61.5		30-Nov-07		2:25:59		68		32.5

		20-Oct-07		4:07:10		73.4		56		20-Oct-07		4:06:20		72.8		59.5		20-Oct-07		4:07:53		69.8		62		30-Nov-07		4:25:59		67.4		32.5

		20-Oct-07		6:07:10		74.01		56		20-Oct-07		6:06:20		72.8		59		20-Oct-07		6:07:53		70.41		65		30-Nov-07		6:25:59		67.4		31.5

		20-Oct-07		8:07:10		73.4		52.5		20-Oct-07		8:06:20		71		55		20-Oct-07		8:07:53		71		63.5		30-Nov-07		8:25:59		69.2		29.5

		20-Oct-07		10:07:10		73.4		54.5		20-Oct-07		10:06:20		71		54		20-Oct-07		10:07:53		71.6		63.5		30-Nov-07		10:25:59		72.21		31.5

		20-Oct-07		12:07:10		74.6		53		20-Oct-07		12:06:20		71		59.5		20-Oct-07		12:07:53		71.6		58		30-Nov-07		12:25:59		71.6		33

		20-Oct-07		14:07:10		75.2		54.5		20-Oct-07		14:06:20		71		48.5		20-Oct-07		14:07:53		71		62		30-Nov-07		14:25:59		74.01		31.5

		20-Oct-07		16:07:10		74.6		56.5		20-Oct-07		16:06:20		69.8		67		20-Oct-07		16:07:53		70.41		70		30-Nov-07		16:25:59		74.6		30.5

		20-Oct-07		18:07:10		73.4		57.5		20-Oct-07		18:06:20		69.2		61		20-Oct-07		18:07:53		70.41		59.5		30-Nov-07		18:25:59		74.01		29

		20-Oct-07		20:07:10		74.6		53.5		20-Oct-07		20:06:20		72.21		58		20-Oct-07		20:07:53		69.8		61.5		30-Nov-07		20:25:59		72.8		27.5

		20-Oct-07		22:07:10		74.01		49		20-Oct-07		22:06:20		72.21		51.5		20-Oct-07		22:07:53		69.2		56.5		30-Nov-07		22:25:59		71		30

		21-Oct-07		0:07:10		73.4		45		21-Oct-07		0:06:20		71.6		46.5		21-Oct-07		0:07:53		68		53		1-Dec-07		0:25:59		69.2		31

		21-Oct-07		2:07:10		72.21		44.5		21-Oct-07		2:06:20		71		47		21-Oct-07		2:07:53		66.81		53.5		1-Dec-07		2:25:59		68		31

		21-Oct-07		4:07:10		71.6		45		21-Oct-07		4:06:20		71		47		21-Oct-07		4:07:53		66.2		54		1-Dec-07		4:25:59		67.4		31

		21-Oct-07		6:07:10		71		43		21-Oct-07		6:06:20		70.41		45		21-Oct-07		6:07:53		65.6		52		1-Dec-07		6:25:59		68		29.5

		21-Oct-07		8:07:10		70.41		42		21-Oct-07		8:06:20		68.61		44		21-Oct-07		8:07:53		68		46		1-Dec-07		8:25:59		71		28

		21-Oct-07		10:07:10		70.41		45		21-Oct-07		10:06:20		69.2		50		21-Oct-07		10:07:53		67.4		52		1-Dec-07		10:25:59		72.8		28

		21-Oct-07		12:07:10		71		41.5		21-Oct-07		12:06:20		68.61		42.5		21-Oct-07		12:07:53		69.2		45		1-Dec-07		12:25:59		74.01		26.5

		21-Oct-07		14:07:10		71		37.5		21-Oct-07		14:06:20		69.2		37		21-Oct-07		14:07:53		69.2		40.5		1-Dec-07		14:25:59		74.01		27

		21-Oct-07		16:07:10		71		36		21-Oct-07		16:06:20		68.61		38		21-Oct-07		16:07:53		69.2		38		1-Dec-07		16:25:59		74.6		26

		21-Oct-07		18:07:10		71.6		35		21-Oct-07		18:06:20		68.61		37		21-Oct-07		18:07:53		69.8		37		1-Dec-07		18:25:59		75.2		26.5

		21-Oct-07		20:07:10		72.21		35.5		21-Oct-07		20:06:20		70.41		38		21-Oct-07		20:07:53		68.61		40		1-Dec-07		20:25:59		74.01		25

		21-Oct-07		22:07:10		72.21		36		21-Oct-07		22:06:20		71		38		21-Oct-07		22:07:53		67.4		42		1-Dec-07		22:25:59		70.41		27

		22-Oct-07		0:07:10		71.6		36		22-Oct-07		0:06:20		70.41		38		22-Oct-07		0:07:53		66.2		42.5		2-Dec-07		0:25:59		68.61		28

		22-Oct-07		2:07:10		71		35.5		22-Oct-07		2:06:20		69.8		37.5		22-Oct-07		2:07:53		65.01		43		2-Dec-07		2:25:59		67.4		27.5

		22-Oct-07		4:07:10		70.41		35.5		22-Oct-07		4:06:20		69.8		37		22-Oct-07		4:07:53		64.4		43		2-Dec-07		4:25:59		66.2		27.5

		22-Oct-07		6:07:10		69.8		34.5		22-Oct-07		6:06:20		69.2		36.5		22-Oct-07		6:07:53		63.8		42.5		2-Dec-07		6:25:59		66.2		27

		22-Oct-07		8:07:10		69.2		34.5		22-Oct-07		8:06:20		68.61		36.5		22-Oct-07		8:07:53		68		37.5		2-Dec-07		8:25:59		66.2		26

		22-Oct-07		10:07:10		69.8		33.5		22-Oct-07		10:06:20		68.61		35		22-Oct-07		10:07:53		67.4		37.5		2-Dec-07		10:25:59		66.2		26.5

		22-Oct-07		12:07:10		69.8		33		22-Oct-07		12:06:20		68.61		34		22-Oct-07		12:07:53		68.61		35.5		2-Dec-07		12:25:59		66.81		29

		22-Oct-07		14:07:10		71		31		22-Oct-07		14:06:20		68.61		32		22-Oct-07		14:07:53		69.8		34		2-Dec-07		14:25:59		67.4		29.5

		22-Oct-07		16:07:10		72.21		30.5		22-Oct-07		16:06:20		68.61		31		22-Oct-07		16:07:53		70.41		33.5		2-Dec-07		16:25:59		68		30

		22-Oct-07		18:07:10		72.21		30.5		22-Oct-07		18:06:20		69.2		32.5		22-Oct-07		18:07:53		70.41		33.5		2-Dec-07		18:25:59		67.4		30

		22-Oct-07		20:07:10		74.01		28		22-Oct-07		20:06:20		72.21		29.5		22-Oct-07		20:07:53		71.6		31		2-Dec-07		20:25:59		66.81		31

		22-Oct-07		22:07:10		74.01		32		22-Oct-07		22:06:20		72.8		35		22-Oct-07		22:07:53		71		36.5		2-Dec-07		22:25:59		66.2		31

		23-Oct-07		0:07:10		73.4		33		23-Oct-07		0:06:20		72.21		36		23-Oct-07		0:07:53		69.2		38		3-Dec-07		0:25:59		66.2		30.5

		23-Oct-07		2:07:10		72.8		33.5		23-Oct-07		2:06:20		71.6		36.5		23-Oct-07		2:07:53		68.61		39		3-Dec-07		2:25:59		66.2		31

		23-Oct-07		4:07:10		72.21		34		23-Oct-07		4:06:20		71		36.5		23-Oct-07		4:07:53		66.81		40		3-Dec-07		4:25:59		66.2		32.5

		23-Oct-07		6:07:10		71.6		34.5		23-Oct-07		6:06:20		69.8		36.5		23-Oct-07		6:07:53		68		39.5		3-Dec-07		6:25:59		66.2		34.5

		23-Oct-07		8:07:10		71.6		35.5		23-Oct-07		8:06:20		69.8		38.5		23-Oct-07		8:07:53		69.2		38		3-Dec-07		8:25:59		66.2		35.5

		23-Oct-07		10:07:10		72.21		37.5		23-Oct-07		10:06:20		70.41		43.5		23-Oct-07		10:07:53		70.41		42		3-Dec-07		10:25:59		66.81		35.5

		23-Oct-07		12:07:10		72.8		35		23-Oct-07		12:06:20		70.41		36.5		23-Oct-07		12:07:53		71.6		34.5		3-Dec-07		12:25:59		67.4		36.5

		23-Oct-07		14:07:10		74.6		38.5		23-Oct-07		14:06:20		69.8		45		23-Oct-07		14:07:53		71.6		41		3-Dec-07		14:25:59		67.4		37.5

		23-Oct-07		16:07:10		75.81		35		23-Oct-07		16:06:20		71		41.5		23-Oct-07		16:07:53		71.6		42.5		3-Dec-07		16:25:59		68		39

		23-Oct-07		18:07:10		75.2		34		23-Oct-07		18:06:20		71.6		36		23-Oct-07		18:07:53		71		36		3-Dec-07		18:25:59		68		39.5

		23-Oct-07		20:07:10		75.81		34.5		23-Oct-07		20:06:20		72.8		38		23-Oct-07		20:07:53		70.41		40.5		3-Dec-07		20:25:59		68		40

		23-Oct-07		22:07:10		75.2		36		23-Oct-07		22:06:20		72.21		40		23-Oct-07		22:07:53		71.6		40.5		3-Dec-07		22:25:59		68		42

		24-Oct-07		0:07:10		74.6		36.5		24-Oct-07		0:06:20		72.21		40.5		24-Oct-07		0:07:53		71		42		4-Dec-07		0:25:59		68		42

		24-Oct-07		2:07:10		74.01		36.5		24-Oct-07		2:06:20		72.21		40		24-Oct-07		2:07:53		69.2		42.5		4-Dec-07		2:25:59		68		41.5

		24-Oct-07		4:07:10		73.4		36.5		24-Oct-07		4:06:20		72.21		39		24-Oct-07		4:07:53		68.61		42.5		4-Dec-07		4:25:59		67.4		41.5

		24-Oct-07		6:07:10		73.4		35.5		24-Oct-07		6:06:20		72.21		38		24-Oct-07		6:07:53		68		42.5		4-Dec-07		6:25:59		68.61		41

		24-Oct-07		8:07:10		73.4		36		24-Oct-07		8:06:20		71.6		40		24-Oct-07		8:07:53		69.8		40		4-Dec-07		8:25:59		72.8		37

		24-Oct-07		10:07:10		75.2		39		24-Oct-07		10:06:20		72.21		40.5		24-Oct-07		10:07:53		71.6		46.5		4-Dec-07		10:25:59		74.6		38

		24-Oct-07		12:07:10		75.81		39.5		24-Oct-07		12:06:20		72.21		38		24-Oct-07		12:07:53		71.6		49		4-Dec-07		12:25:59		75.2		36

		24-Oct-07		14:07:10		75.81		39		24-Oct-07		14:06:20		72.8		46.5		24-Oct-07		14:07:53		71.6		49		4-Dec-07		14:25:59		74.6		37

		24-Oct-07		16:07:10		76.4		40		24-Oct-07		16:06:20		71.6		50		24-Oct-07		16:07:53		71.6		45		4-Dec-07		16:25:59		74.6		38

		24-Oct-07		18:07:10		74.6		41		24-Oct-07		18:06:20		69.8		42		24-Oct-07		18:07:53		71		53.5		4-Dec-07		18:25:59		74.6		39

		24-Oct-07		20:07:10		75.81		43.5		24-Oct-07		20:06:20		73.4		48.5		24-Oct-07		20:07:53		70.41		55.5		4-Dec-07		20:25:59		74.01		39.5

		24-Oct-07		22:07:10		75.81		43.5		24-Oct-07		22:06:20		72.8		48		24-Oct-07		22:07:53		72.8		48		4-Dec-07		22:25:59		72.8		41

		25-Oct-07		0:07:10		75.2		41.5		25-Oct-07		0:06:20		72.8		45.5		25-Oct-07		0:07:53		72.21		46		5-Dec-07		0:25:59		71.6		44.5

		25-Oct-07		2:07:10		74.6		40		25-Oct-07		2:06:20		72.8		43.5		25-Oct-07		2:07:53		71.6		45		5-Dec-07		2:25:59		70.41		45

		25-Oct-07		4:07:10		74.01		39		25-Oct-07		4:06:20		72.8		41.5		25-Oct-07		4:07:53		69.8		44		5-Dec-07		4:25:59		69.8		45.5

		25-Oct-07		6:07:10		73.4		39		25-Oct-07		6:06:20		71.6		42		25-Oct-07		6:07:53		69.2		45		5-Dec-07		6:25:59		70.41		50

		25-Oct-07		8:07:10		72.8		39.5		25-Oct-07		8:06:20		71		45.5		25-Oct-07		8:07:53		71		42.5		5-Dec-07		8:25:59		74.6		47

		25-Oct-07		10:07:10		72.8		43.5		25-Oct-07		10:06:20		70.41		52.5		25-Oct-07		10:07:53		71.6		49.5		5-Dec-07		10:25:59		75.81		48

		25-Oct-07		12:07:10		73.4		43.5		25-Oct-07		12:06:20		70.41		52		25-Oct-07		12:07:53		71.6		44		5-Dec-07		12:25:59		75.2		50

		25-Oct-07		14:07:10		74.01		42		25-Oct-07		14:06:20		71		39.5		25-Oct-07		14:07:53		71.6		47		5-Dec-07		14:25:59		74.6		51.5

		25-Oct-07		16:07:10		74.6		46		25-Oct-07		16:06:20		69.8		54		25-Oct-07		16:07:53		71.6		50.5		5-Dec-07		16:25:59		74.6		50

		25-Oct-07		18:07:10		74.6		47		25-Oct-07		18:06:20		69.2		56.5		25-Oct-07		18:07:53		71		48.5		5-Dec-07		18:25:59		74.6		49.5

		25-Oct-07		20:07:10		75.81		42		25-Oct-07		20:06:20		72.8		46.5		25-Oct-07		20:07:53		72.8		46.5		5-Dec-07		20:25:59		74.6		48.5

		25-Oct-07		22:07:10		75.2		40.5		25-Oct-07		22:06:20		72.8		43.5		25-Oct-07		22:07:53		72.8		44.5		5-Dec-07		22:25:59		72.8		50

		26-Oct-07		0:07:10		74.6		39.5		26-Oct-07		0:06:20		72.8		43.5		26-Oct-07		0:07:53		71.6		44		6-Dec-07		0:25:59		72.21		51.5

		26-Oct-07		2:07:10		74.01		39		26-Oct-07		2:06:20		72.21		42		26-Oct-07		2:07:53		69.8		44		6-Dec-07		2:25:59		71		51.5

		26-Oct-07		4:07:10		72.8		38		26-Oct-07		4:06:20		71		40.5		26-Oct-07		4:07:53		68.61		43.5		6-Dec-07		4:25:59		70.41		52

		26-Oct-07		6:07:10		72.8		37.5		26-Oct-07		6:06:20		70.41		39.5		26-Oct-07		6:07:53		68		43.5		6-Dec-07		6:25:59		70.41		52

		26-Oct-07		8:07:10		72.21		38		26-Oct-07		8:06:20		69.8		42.5		26-Oct-07		8:07:53		69.2		40.5		6-Dec-07		8:25:59		74.6		46.5

		26-Oct-07		10:07:10		72.8		38.5		26-Oct-07		10:06:20		71		40		26-Oct-07		10:07:53		71		47.5		6-Dec-07		10:25:59		75.81		45

		26-Oct-07		12:07:10		73.4		44.5		26-Oct-07		12:06:20		70.41		50.5		26-Oct-07		12:07:53		71.6		44.5		6-Dec-07		12:25:59		75.2		47

		26-Oct-07		14:07:10		74.6		40		26-Oct-07		14:06:20		71		39.5		26-Oct-07		14:07:53		71.6		48.5		6-Dec-07		14:25:59		74.6		49

		26-Oct-07		16:07:10		74.6		47		26-Oct-07		16:06:20		69.8		58.5		26-Oct-07		16:07:53		71		56		6-Dec-07		16:25:59		74.6		47

		26-Oct-07		18:07:10		74.01		47.5		26-Oct-07		18:06:20		69.2		56		26-Oct-07		18:07:53		70.41		52.5		6-Dec-07		18:25:59		74.6		40.5

		26-Oct-07		20:07:10		74.6		41.5		26-Oct-07		20:06:20		71		47.5		26-Oct-07		20:07:53		71		47.5		6-Dec-07		20:25:59		74.01		39.5

		26-Oct-07		22:07:10		74.01		40.5		26-Oct-07		22:06:20		71		40.5		26-Oct-07		22:07:53		70.41		45.5		6-Dec-07		22:25:59		72.21		42

		27-Oct-07		0:07:10		73.4		40.5		27-Oct-07		0:06:20		71.6		44.5		27-Oct-07		0:07:53		69.2		46		7-Dec-07		0:25:59		71		44

		27-Oct-07		2:07:10		72.8		41.5		27-Oct-07		2:06:20		70.41		46.5		27-Oct-07		2:07:53		68		48		7-Dec-07		2:25:59		70.41		43.5

		27-Oct-07		4:07:10		72.21		42		27-Oct-07		4:06:20		70.41		46		27-Oct-07		4:07:53		68		48.5		7-Dec-07		4:25:59		70.41		44

		27-Oct-07		6:07:10		72.8		42		27-Oct-07		6:06:20		71		45.5		27-Oct-07		6:07:53		68		49		7-Dec-07		6:25:59		70.41		44.5

		27-Oct-07		8:07:10		72.21		41		27-Oct-07		8:06:20		71		45.5		27-Oct-07		8:07:53		71		46.5		7-Dec-07		8:25:59		74.6		41

		27-Oct-07		10:07:10		72.8		45		27-Oct-07		10:06:20		71		45.5		27-Oct-07		10:07:53		71		37.5		7-Dec-07		10:25:59		74.6		42

		27-Oct-07		12:07:10		73.4		45		27-Oct-07		12:06:20		70.41		53.5		27-Oct-07		12:07:53		71		52.5		7-Dec-07		12:25:59		72.8		45.5

		27-Oct-07		14:07:10		73.4		42.5		27-Oct-07		14:06:20		71		47.5		27-Oct-07		14:07:53		71		51		7-Dec-07		14:25:59		72.8		46.5

		27-Oct-07		16:07:10		73.4		46		27-Oct-07		16:06:20		68.61		46		27-Oct-07		16:07:53		71		46.5		7-Dec-07		16:25:59		72.8		47.5

		27-Oct-07		18:07:10		73.4		44.5		27-Oct-07		18:06:20		68		46.5		27-Oct-07		18:07:53		69.8		49.5		7-Dec-07		18:25:59		72.8		46

		27-Oct-07		20:07:10		72.8		42		27-Oct-07		20:06:20		69.2		47.5		27-Oct-07		20:07:53		69.8		46.5		7-Dec-07		20:25:59		72.21		46

		27-Oct-07		22:07:10		72.21		41.5		27-Oct-07		22:06:20		69.2		46		27-Oct-07		22:07:53		68.61		46		7-Dec-07		22:25:59		69.8		47.5

		28-Oct-07		0:07:10		71.6		40		28-Oct-07		0:06:20		68.61		44.5		28-Oct-07		0:07:53		67.4		45		8-Dec-07		0:25:59		68.61		48

		28-Oct-07		2:07:10		71		39		28-Oct-07		2:06:20		68.61		43		28-Oct-07		2:07:53		66.2		45		8-Dec-07		2:25:59		68		47

		28-Oct-07		4:07:10		70.41		38.5		28-Oct-07		4:06:20		68.61		41.5		28-Oct-07		4:07:53		65.01		45.5		8-Dec-07		4:25:59		67.4		46.5

		28-Oct-07		6:07:10		69.8		38		28-Oct-07		6:06:20		68		41.5		28-Oct-07		6:07:53		63.8		46		8-Dec-07		6:25:59		68		45.5

		28-Oct-07		8:07:10		69.2		39.5		28-Oct-07		8:06:20		68		43.5		28-Oct-07		8:07:53		66.81		43.5		8-Dec-07		8:25:59		71.6		40

		28-Oct-07		10:07:10		69.2		42		28-Oct-07		10:06:20		68		47		28-Oct-07		10:07:53		66.81		46.5		8-Dec-07		10:25:59		72.21		39.5

		28-Oct-07		12:07:10		69.2		44.5		28-Oct-07		12:06:20		67.4		50		28-Oct-07		12:07:53		67.4		48		8-Dec-07		12:25:59		71.6		40

		28-Oct-07		14:07:10		69.8		47		28-Oct-07		14:06:20		67.4		53		28-Oct-07		14:07:53		68.61		50		8-Dec-07		14:25:59		72.21		39.5

		28-Oct-07		16:07:10		70.41		49.5		28-Oct-07		16:06:20		67.4		49		28-Oct-07		16:07:53		69.2		52		8-Dec-07		16:25:59		72.21		38

		28-Oct-07		18:07:10		71		43		28-Oct-07		18:06:20		68		46.5		28-Oct-07		18:07:53		69.2		47.5		8-Dec-07		18:25:59		71.6		37.5

		28-Oct-07		20:07:10		71		43.5		28-Oct-07		20:06:20		68.61		47		28-Oct-07		20:07:53		68.61		47		8-Dec-07		20:25:59		70.41		36.5

		28-Oct-07		22:07:10		71		41		28-Oct-07		22:06:20		69.2		44.5		28-Oct-07		22:07:53		67.4		46.5		8-Dec-07		22:25:59		69.8		36.5

		29-Oct-07		0:07:10		70.41		41.5		29-Oct-07		0:06:20		68.61		44.5		29-Oct-07		0:07:53		66.2		47		9-Dec-07		0:25:59		68		37

		29-Oct-07		2:07:10		70.41		41.5		29-Oct-07		2:06:20		68.61		44.5		29-Oct-07		2:07:53		65.6		48		9-Dec-07		2:25:59		66.81		37

		29-Oct-07		4:07:10		69.8		40.5		29-Oct-07		4:06:20		68		44		29-Oct-07		4:07:53		65.01		48		9-Dec-07		4:25:59		66.2		36.5

		29-Oct-07		6:07:10		69.8		40.5		29-Oct-07		6:06:20		68		43.5		29-Oct-07		6:07:53		64.4		48		9-Dec-07		6:25:59		66.2		36

		29-Oct-07		8:07:10		69.2		40		29-Oct-07		8:06:20		68		43		29-Oct-07		8:07:53		67.4		43.5		9-Dec-07		8:25:59		66.2		35.5

		29-Oct-07		10:07:10		69.2		43.5		29-Oct-07		10:06:20		68		49.5		29-Oct-07		10:07:53		67.4		48		9-Dec-07		10:25:59		66.2		34

		29-Oct-07		12:07:10		69.8		47.5		29-Oct-07		12:06:20		68		53.5		29-Oct-07		12:07:53		69.2		50		9-Dec-07		12:25:59		66.2		34

		29-Oct-07		14:07:10		71		48.5		29-Oct-07		14:06:20		68		48.5		29-Oct-07		14:07:53		69.8		54.5		9-Dec-07		14:25:59		66.81		33.5

		29-Oct-07		16:07:10		71.6		48.5		29-Oct-07		16:06:20		68.61		55		29-Oct-07		16:07:53		70.41		45.5		9-Dec-07		16:25:59		66.81		33

		29-Oct-07		18:07:10		72.21		50.5		29-Oct-07		18:06:20		68.61		62.5		29-Oct-07		18:07:53		70.41		55.5		9-Dec-07		18:25:59		66.81		31

		29-Oct-07		20:07:10		72.8		48.5		29-Oct-07		20:06:20		69.2		46		29-Oct-07		20:07:53		71.6		50		9-Dec-07		20:25:59		65.6		30.5

		29-Oct-07		22:07:10		72.21		46		29-Oct-07		22:06:20		69.2		51.5		29-Oct-07		22:07:53		70.41		48.5		9-Dec-07		22:25:59		65.01		31.5

		30-Oct-07		0:07:10		71.6		45		30-Oct-07		0:06:20		68.61		50.5		30-Oct-07		0:07:53		69.2		48		10-Dec-07		0:25:59		64.4		31

		30-Oct-07		2:07:10		71.6		44.5		30-Oct-07		2:06:20		68.61		46.5		30-Oct-07		2:07:53		68.61		48.5		10-Dec-07		2:25:59		63.8		31

		30-Oct-07		4:07:10		71		43.5		30-Oct-07		4:06:20		69.2		48		30-Oct-07		4:07:53		67.4		49		10-Dec-07		4:25:59		63.21		31

		30-Oct-07		6:07:10		71.6		43.5		30-Oct-07		6:06:20		69.2		46.5		30-Oct-07		6:07:53		68		49		10-Dec-07		6:25:59		62.6		31

		30-Oct-07		8:07:10		71		46		30-Oct-07		8:06:20		68.61		44.5		30-Oct-07		8:07:53		69.2		47.5		10-Dec-07		8:25:59		63.21		31

		30-Oct-07		10:07:10		72.21		46		30-Oct-07		10:06:20		69.2		55.5		30-Oct-07		10:07:53		71.6		47.5		10-Dec-07		10:25:59		64.4		31

		30-Oct-07		12:07:10		72.21		49		30-Oct-07		12:06:20		69.8		56		30-Oct-07		12:07:53		71		49		10-Dec-07		12:25:59		65.6		31.5

		30-Oct-07		14:07:10		73.4		47		30-Oct-07		14:06:20		70.41		53.5		30-Oct-07		14:07:53		71		55		10-Dec-07		14:25:59		66.2		32

		30-Oct-07		16:07:10		73.4		48.5		30-Oct-07		16:06:20		68.61		61.5		30-Oct-07		16:07:53		70.41		54		10-Dec-07		16:25:59		66.81		32.5

		30-Oct-07		18:07:10		72.8		45		30-Oct-07		18:06:20		69.2		54.5		30-Oct-07		18:07:53		70.41		51.5		10-Dec-07		18:25:59		66.81		33

		30-Oct-07		20:07:10		72.21		46		30-Oct-07		20:06:20		68.61		53		30-Oct-07		20:07:53		69.8		48.5		10-Dec-07		20:25:59		66.2		34

		30-Oct-07		22:07:10		71.6		45.5		30-Oct-07		22:06:20		68.61		51.5		30-Oct-07		22:07:53		69.2		49		10-Dec-07		22:25:59		65.01		35

		31-Oct-07		0:07:10		71.6		45		31-Oct-07		0:06:20		69.2		50		31-Oct-07		0:07:53		68.61		49.5		11-Dec-07		0:25:59		64.4		36.5

		31-Oct-07		2:07:10		71		46.5		31-Oct-07		2:06:20		68.61		52		31-Oct-07		2:07:53		68		51		11-Dec-07		2:25:59		63.21		36.5

		31-Oct-07		4:07:10		71		47		31-Oct-07		4:06:20		68.61		52		31-Oct-07		4:07:53		67.4		52.5		11-Dec-07		4:25:59		63.21		36

		31-Oct-07		6:07:10		71.6		47		31-Oct-07		6:06:20		68.61		52		31-Oct-07		6:07:53		72.21		48		11-Dec-07		6:25:59		64.4		34.5

		31-Oct-07		8:07:10		71.6		47.5		31-Oct-07		8:06:20		69.8		48.5		31-Oct-07		8:07:53		71		43.5		11-Dec-07		8:25:59		66.81		31.5

		31-Oct-07		10:07:10		72.21		48		31-Oct-07		10:06:20		69.8		51.5		31-Oct-07		10:07:53		71.6		49.5		11-Dec-07		10:25:59		69.8		31.5

		31-Oct-07		12:07:10		72.8		46.5		31-Oct-07		12:06:20		69.2		45.5		31-Oct-07		12:07:53		72.21		48		11-Dec-07		12:25:59		74.01		32

		31-Oct-07		14:07:10		72.8		46.5		31-Oct-07		14:06:20		70.41		45.5		31-Oct-07		14:07:53		71		52		11-Dec-07		14:25:59		71.6		33.5

		31-Oct-07		16:07:10		73.4		47		31-Oct-07		16:06:20		68		51		31-Oct-07		16:07:53		71		45.5		11-Dec-07		16:25:59		71.6		34.5

		31-Oct-07		18:07:10		72.8		47		31-Oct-07		18:06:20		68.61		48		31-Oct-07		18:07:53		70.41		51.5		11-Dec-07		18:25:59		71.6		33.5

		31-Oct-07		20:07:10		72.21		45		31-Oct-07		20:06:20		68.61		51.5		31-Oct-07		20:07:53		69.8		48		11-Dec-07		20:25:59		69.8		33.5

		31-Oct-07		22:07:10		72.21		44.5		31-Oct-07		22:06:20		69.2		49.5		31-Oct-07		22:07:53		68.61		49.5		11-Dec-07		22:25:59		67.4		33

		1-Nov-07		0:07:10		71.6		44.5		1-Nov-07		0:06:20		69.2		49.5		1-Nov-07		0:07:53		67.4		50		12-Dec-07		0:25:59		66.2		33.5

		1-Nov-07		2:07:10		71.6		45.5		1-Nov-07		2:06:20		69.2		50		1-Nov-07		2:07:53		66.81		51.5		12-Dec-07		2:25:59		65.01		31

		1-Nov-07		4:07:10		71		46.5		1-Nov-07		4:06:20		68.61		52		1-Nov-07		4:07:53		66.81		53		12-Dec-07		4:25:59		63.8		29

		1-Nov-07		6:07:10		71.6		47.5		1-Nov-07		6:06:20		69.2		53.5		1-Nov-07		6:07:53		68.61		51		12-Dec-07		6:25:59		65.6		24

		1-Nov-07		8:07:10		72.21		44.5		1-Nov-07		8:06:20		69.8		53.5		1-Nov-07		8:07:53		70.41		49		12-Dec-07		8:25:59		69.8		21.5

		1-Nov-07		10:07:10		72.21		47		1-Nov-07		10:06:20		68.61		51.5		1-Nov-07		10:07:53		71		48.5		12-Dec-07		10:25:59		72.21		23

		1-Nov-07		12:07:10		72.8		45.5		1-Nov-07		12:06:20		69.8		44		1-Nov-07		12:07:53		71.6		45.5		12-Dec-07		12:25:59		71.6		22

		1-Nov-07		14:07:10		72.8		46.5		1-Nov-07		14:06:20		68.61		47.5		1-Nov-07		14:07:53		71		51		12-Dec-07		14:25:59		72.21		21

		1-Nov-07		16:07:10		72.8		51.5		1-Nov-07		16:06:20		68.61		60.5		1-Nov-07		16:07:53		70.41		55.5		12-Dec-07		16:25:59		72.21		20.5

		1-Nov-07		18:07:10		72.8		50		1-Nov-07		18:06:20		68.61		59		1-Nov-07		18:07:53		69.8		54.5		12-Dec-07		18:25:59		71.6		23

		1-Nov-07		20:07:10		72.21		47.5		1-Nov-07		20:06:20		68.61		53.5		1-Nov-07		20:07:53		69.8		50.5		12-Dec-07		20:25:59		69.8		24

		1-Nov-07		22:07:10		71.6		47.5		1-Nov-07		22:06:20		69.2		52		1-Nov-07		22:07:53		69.2		51		12-Dec-07		22:25:59		68.61		25.5

		2-Nov-07		0:07:10		71		48		2-Nov-07		0:06:20		68.61		52.5		2-Nov-07		0:07:53		68.61		51.5		13-Dec-07		0:25:59		66.2		26.5

		2-Nov-07		2:07:10		71		48		2-Nov-07		2:06:20		68.61		52.5		2-Nov-07		2:07:53		68		52.5		13-Dec-07		2:25:59		64.4		27

		2-Nov-07		4:07:10		70.41		47.5		2-Nov-07		4:06:20		68.61		52		2-Nov-07		4:07:53		67.4		52.5		13-Dec-07		4:25:59		63.21		27.5

		2-Nov-07		6:07:10		71		46		2-Nov-07		6:06:20		69.2		49		2-Nov-07		6:07:53		68		51.5		13-Dec-07		6:25:59		64.4		28

		2-Nov-07		8:07:10		72.21		46.5		2-Nov-07		8:06:20		68.61		54.5		2-Nov-07		8:07:53		69.8		48		13-Dec-07		8:25:59		68		27.5

		2-Nov-07		10:07:10		73.4		46		2-Nov-07		10:06:20		69.2		53		2-Nov-07		10:07:53		71.6		46.5		13-Dec-07		10:25:59		70.41		28.5

		2-Nov-07		12:07:10		74.01		47		2-Nov-07		12:06:20		69.8		56.5		2-Nov-07		12:07:53		71.6		47.5		13-Dec-07		12:25:59		71.6		29

		2-Nov-07		14:07:10		74.01		44		2-Nov-07		14:06:20		71		48.5		2-Nov-07		14:07:53		71		44		13-Dec-07		14:25:59		71.6		26

		2-Nov-07		16:07:10		74.01		52.5		2-Nov-07		16:06:20		69.2		58		2-Nov-07		16:07:53		71		56.5		13-Dec-07		16:25:59		71.6		25.5

		2-Nov-07		18:07:10		74.01		49.5		2-Nov-07		18:06:20		69.2		49.5		2-Nov-07		18:07:53		70.41		50		13-Dec-07		18:25:59		71.6		26

		2-Nov-07		20:07:10		73.4		46.5		2-Nov-07		20:06:20		69.2		51.5		2-Nov-07		20:07:53		70.41		51		13-Dec-07		20:25:59		71		27.5

		2-Nov-07		22:07:10		72.8		42		2-Nov-07		22:06:20		69.8		47.5		2-Nov-07		22:07:53		69.8		47		13-Dec-07		22:25:59		68		28.5

		3-Nov-07		0:07:10		71.6		42		3-Nov-07		0:06:20		69.2		46		3-Nov-07		0:07:53		68		46.5		14-Dec-07		0:25:59		66.2		29.5

		3-Nov-07		2:07:10		71		40.5		3-Nov-07		2:06:20		69.2		43.5		3-Nov-07		2:07:53		66.81		46.5		14-Dec-07		2:25:59		64.4		29.5

		3-Nov-07		4:07:10		70.41		40		3-Nov-07		4:06:20		68		42.5		3-Nov-07		4:07:53		66.81		45		14-Dec-07		4:25:59		63.8		30

		3-Nov-07		6:07:10		70.41		38		3-Nov-07		6:06:20		67.4		40.5		3-Nov-07		6:07:53		67.4		42.5		14-Dec-07		6:25:59		65.01		29

		3-Nov-07		8:07:10		72.8		36.5		3-Nov-07		8:06:20		69.2		42		3-Nov-07		8:07:53		68.61		39		14-Dec-07		8:25:59		66.81		27

		3-Nov-07		10:07:10		74.01		39.5		3-Nov-07		10:06:20		71.6		46		3-Nov-07		10:07:53		70.41		47		14-Dec-07		10:25:59		70.41		28.5

		3-Nov-07		12:07:10		74.6		40		3-Nov-07		12:06:20		71.6		46.5		3-Nov-07		12:07:53		71.6		45.5		14-Dec-07		12:25:59		72.21		28.5

		3-Nov-07		14:07:10		74.6		42		3-Nov-07		14:06:20		70.41		50		3-Nov-07		14:07:53		71		52		14-Dec-07		14:25:59		72.21		29.5

		3-Nov-07		16:07:10		74.01		42.5		3-Nov-07		16:06:20		69.8		50.5		3-Nov-07		16:07:53		71		49.5		14-Dec-07		16:25:59		72.21		30.5

		3-Nov-07		18:07:10		74.01		47.5		3-Nov-07		18:06:20		69.2		59.5		3-Nov-07		18:07:53		71		47		14-Dec-07		18:25:59		72.8		31.5

		3-Nov-07		20:07:10		74.6		42		3-Nov-07		20:06:20		71		47.5		3-Nov-07		20:07:53		70.41		48.5		14-Dec-07		20:25:59		71		31.5

		3-Nov-07		22:07:10		74.01		40.5		3-Nov-07		22:06:20		71		45		3-Nov-07		22:07:53		69.8		45.5		14-Dec-07		22:25:59		68.61		31

		4-Nov-07		0:07:10		72.8		38.5		4-Nov-07		0:06:20		69.8		42		4-Nov-07		0:07:53		68		44.5		15-Dec-07		0:25:59		66.2		31.5

		4-Nov-07		2:07:10		71.6		37.5		4-Nov-07		2:06:20		69.8		40		4-Nov-07		2:07:53		66.81		44		15-Dec-07		2:25:59		64.4		31.5

		4-Nov-07		4:07:10		71		36.5		4-Nov-07		4:06:20		69.2		39		4-Nov-07		4:07:53		65.01		43.5		15-Dec-07		4:25:59		63.21		31

		4-Nov-07		6:07:10		69.8		35.5		4-Nov-07		6:06:20		68.61		38		4-Nov-07		6:07:53		63.8		43.5		15-Dec-07		6:25:59		64.4		30

		4-Nov-07		8:07:10		69.2		35		4-Nov-07		8:06:20		67.4		38		4-Nov-07		8:07:53		66.81		39		15-Dec-07		8:25:59		66.81		28.5

		4-Nov-07		10:07:10		69.8		37.5		4-Nov-07		10:06:20		68.61		40.5		4-Nov-07		10:07:53		67.4		41		15-Dec-07		10:25:59		69.2		30

		4-Nov-07		12:07:10		70.41		40.5		4-Nov-07		12:06:20		68.61		43		4-Nov-07		12:07:53		68.61		43.5		15-Dec-07		12:25:59		72.21		31

		4-Nov-07		14:07:10		71		41		4-Nov-07		14:06:20		69.2		39.5		4-Nov-07		14:07:53		70.41		41		15-Dec-07		14:25:59		71.6		32

		4-Nov-07		16:07:10		72.21		42.5		4-Nov-07		16:06:20		69.2		41.5		4-Nov-07		16:07:53		70.41		46.5		15-Dec-07		16:25:59		72.21		31.5

		4-Nov-07		18:07:10		72.8		38.5		4-Nov-07		18:06:20		69.2		41		4-Nov-07		18:07:53		69.8		44		15-Dec-07		18:25:59		71.6		34

		4-Nov-07		20:07:10		72.8		36		4-Nov-07		20:06:20		70.41		39		4-Nov-07		20:07:53		70.41		40		15-Dec-07		20:25:59		71		34.5

		4-Nov-07		22:07:10		72.8		35.5		4-Nov-07		22:06:20		70.41		39		4-Nov-07		22:07:53		69.2		40		15-Dec-07		22:25:59		68.61		34

		5-Nov-07		0:07:10		72.21		36.5		5-Nov-07		0:06:20		70.41		40		5-Nov-07		0:07:53		67.4		42		16-Dec-07		0:25:59		67.4		35

		5-Nov-07		2:07:10		71.6		36		5-Nov-07		2:06:20		70.41		38.5		5-Nov-07		2:07:53		65.6		42		16-Dec-07		2:25:59		66.81		35

		5-Nov-07		4:07:10		70.41		35.5		5-Nov-07		4:06:20		69.2		37.5		5-Nov-07		4:07:53		64.4		42.5		16-Dec-07		4:25:59		66.2		35.5

		5-Nov-07		6:07:10		69.8		34.5		5-Nov-07		6:06:20		68.61		37		5-Nov-07		6:07:53		64.4		41.5		16-Dec-07		6:25:59		66.2		35.5

		5-Nov-07		8:07:10		69.2		34		5-Nov-07		8:06:20		67.4		37		5-Nov-07		8:07:53		66.81		37.5		16-Dec-07		8:25:59		65.6		35.5

		5-Nov-07		10:07:10		69.2		37		5-Nov-07		10:06:20		68		40		5-Nov-07		10:07:53		67.4		40.5		16-Dec-07		10:25:59		65.6		36

		5-Nov-07		12:07:10		69.8		39		5-Nov-07		12:06:20		68.61		39		5-Nov-07		12:07:53		68		42		16-Dec-07		12:25:59		66.2		37.5

		5-Nov-07		14:07:10		71		40.5		5-Nov-07		14:06:20		68.61		43		5-Nov-07		14:07:53		69.8		42.5		16-Dec-07		14:25:59		66.2		38.5

		5-Nov-07		16:07:10		71.6		41.5		5-Nov-07		16:06:20		69.2		40.5		5-Nov-07		16:07:53		69.8		45		16-Dec-07		16:25:59		66.2		40

		5-Nov-07		18:07:10		72.21		40.5		5-Nov-07		18:06:20		68.61		45		5-Nov-07		18:07:53		70.41		43.5		16-Dec-07		18:25:59		65.6		41.5

		5-Nov-07		20:07:10		72.8		40		5-Nov-07		20:06:20		71		43		5-Nov-07		20:07:53		70.41		44.5		16-Dec-07		20:25:59		65.01		42

		5-Nov-07		22:07:10		72.21		40.5		5-Nov-07		22:06:20		70.41		44.5		5-Nov-07		22:07:53		69.2		44.5		16-Dec-07		22:25:59		65.01		42

		6-Nov-07		0:07:10		71.6		39		6-Nov-07		0:06:20		70.41		41.5		6-Nov-07		0:07:53		67.4		44		17-Dec-07		0:25:59		64.4		42.5

		6-Nov-07		2:07:10		71		38		6-Nov-07		2:06:20		69.8		40		6-Nov-07		2:07:53		66.2		44		17-Dec-07		2:25:59		63.8		43.5

		6-Nov-07		4:07:10		69.8		36		6-Nov-07		4:06:20		68.61		38		6-Nov-07		4:07:53		65.01		42.5		17-Dec-07		4:25:59		63.8		43.5

		6-Nov-07		6:07:10		69.2		35		6-Nov-07		6:06:20		67.4		37		6-Nov-07		6:07:53		67.4		38		17-Dec-07		6:25:59		63.21		43

		6-Nov-07		8:07:10		71.6		33.5		6-Nov-07		8:06:20		68		36		6-Nov-07		8:07:53		68		37		17-Dec-07		8:25:59		64.4		44

		6-Nov-07		10:07:10		72.8		35.5		6-Nov-07		10:06:20		70.41		42.5		6-Nov-07		10:07:53		70.41		35.5		17-Dec-07		10:25:59		65.6		43.5

		6-Nov-07		12:07:10		74.01		38.5		6-Nov-07		12:06:20		70.41		47.5		6-Nov-07		12:07:53		70.41		46.5		17-Dec-07		12:25:59		66.2		43.5

		6-Nov-07		14:07:10		74.01		37		6-Nov-07		14:06:20		71		39		6-Nov-07		14:07:53		70.41		49.5		17-Dec-07		14:25:59		66.2		42

		6-Nov-07		16:07:10		74.6		44		6-Nov-07		16:06:20		70.41		48.5		6-Nov-07		16:07:53		71		49		17-Dec-07		16:25:59		66.81		41.5

		6-Nov-07		18:07:10		74.6		41.5		6-Nov-07		18:06:20		69.2		43		6-Nov-07		18:07:53		70.41		46.5		17-Dec-07		18:25:59		66.81		41.5

		6-Nov-07		20:07:10		73.4		39.5		6-Nov-07		20:06:20		70.41		44.5		6-Nov-07		20:07:53		69.8		44.5		17-Dec-07		20:25:59		65.6		41.5

		6-Nov-07		22:07:10		72.8		40		6-Nov-07		22:06:20		70.41		44		6-Nov-07		22:07:53		68		46		17-Dec-07		22:25:59		65.01		43.5

		7-Nov-07		0:07:10		72.21		40.5		7-Nov-07		0:06:20		70.41		44.5		7-Nov-07		0:07:53		67.4		47		18-Dec-07		0:25:59		64.4		44.5

		7-Nov-07		2:07:10		71.6		41		7-Nov-07		2:06:20		70.41		44		7-Nov-07		2:07:53		66.2		48		18-Dec-07		2:25:59		63.8		45

		7-Nov-07		4:07:10		71		41		7-Nov-07		4:06:20		69.8		43.5		7-Nov-07		4:07:53		65.6		48.5		18-Dec-07		4:25:59		63.8		44

		7-Nov-07		6:07:10		70.41		41.5		7-Nov-07		6:06:20		69.8		43.5		7-Nov-07		6:07:53		67.4		45		18-Dec-07		6:25:59		65.6		46

		7-Nov-07		8:07:10		71.6		41.5		7-Nov-07		8:06:20		68.61		45		7-Nov-07		8:07:53		70.41		43.5		18-Dec-07		8:25:59		68		45

		7-Nov-07		10:07:10		72.8		41		7-Nov-07		10:06:20		70.41		47.5		7-Nov-07		10:07:53		71		44		18-Dec-07		10:25:59		71		45

		7-Nov-07		12:07:10		72.8		40		7-Nov-07		12:06:20		71		38.5		7-Nov-07		12:07:53		70.41		45.5		18-Dec-07		12:25:59		71.6		44

		7-Nov-07		14:07:10		73.4		42.5		7-Nov-07		14:06:20		71		50.5		7-Nov-07		14:07:53		70.41		45.5		18-Dec-07		14:25:59		71.6		45.5

		7-Nov-07		16:07:10		74.01		46		7-Nov-07		16:06:20		70.41		46		7-Nov-07		16:07:53		71		53		18-Dec-07		16:25:59		71.6		45

		7-Nov-07		18:07:10		74.01		43.5		7-Nov-07		18:06:20		69.2		51.5		7-Nov-07		18:07:53		69.8		50		18-Dec-07		18:25:59		72.21		44

		7-Nov-07		20:07:10		72.8		40.5		7-Nov-07		20:06:20		70.41		44		7-Nov-07		20:07:53		69.2		45.5		18-Dec-07		20:25:59		70.41		43

		7-Nov-07		22:07:10		72.21		39		7-Nov-07		22:06:20		70.41		41		7-Nov-07		22:07:53		68		44		18-Dec-07		22:25:59		68.61		44

		8-Nov-07		0:07:10		71.6		40		8-Nov-07		0:06:20		70.41		42.5		8-Nov-07		0:07:53		66.81		46.5		19-Dec-07		0:25:59		67.4		45

		8-Nov-07		2:07:10		71		40.5		8-Nov-07		2:06:20		70.41		42		8-Nov-07		2:07:53		65.6		47.5		19-Dec-07		2:25:59		66.2		46

		8-Nov-07		4:07:10		70.41		39.5		8-Nov-07		4:06:20		69.8		40.5		8-Nov-07		4:07:53		65.01		47		19-Dec-07		4:25:59		65.01		46.5

		8-Nov-07		6:07:10		69.8		39.5		8-Nov-07		6:06:20		69.8		40		8-Nov-07		6:07:53		67.4		43		19-Dec-07		6:25:59		65.6		49

		8-Nov-07		8:07:10		71.6		38.5		8-Nov-07		8:06:20		68.61		42.5		8-Nov-07		8:07:53		69.2		41.5		19-Dec-07		8:25:59		69.2		46.5

		8-Nov-07		10:07:10		71		40		8-Nov-07		10:06:20		67.4		47		8-Nov-07		10:07:53		71		41		19-Dec-07		10:25:59		71.6		47

		8-Nov-07		12:07:10		72.21		43		8-Nov-07		12:06:20		70.41		46.5		8-Nov-07		12:07:53		70.41		47		19-Dec-07		12:25:59		72.21		46.5

		8-Nov-07		14:07:10		71.6		41		8-Nov-07		14:06:20		68		43		8-Nov-07		14:07:53		71.6		45.5		19-Dec-07		14:25:59		72.21		49.5

		8-Nov-07		16:07:10		74.01		43.5		8-Nov-07		16:06:20		71.6		43		8-Nov-07		16:07:53		70.41		53		19-Dec-07		16:25:59		72.8		46.5

		8-Nov-07		18:07:10		73.4		43		8-Nov-07		18:06:20		71		47.5		8-Nov-07		18:07:53		69.8		48		19-Dec-07		18:25:59		72.21		44.5

		8-Nov-07		20:07:10		71.6		43		8-Nov-07		20:06:20		69.2		46.5		8-Nov-07		20:07:53		69.8		47		19-Dec-07		20:25:59		71.6		42

		8-Nov-07		22:07:10		71.6		44		8-Nov-07		22:06:20		68.61		48		8-Nov-07		22:07:53		68.61		48		19-Dec-07		22:25:59		69.2		43

		9-Nov-07		0:07:10		71		43		9-Nov-07		0:06:20		68.61		46.5		9-Nov-07		0:07:53		68		47		20-Dec-07		0:25:59		68		42.5

		9-Nov-07		2:07:10		70.41		44		9-Nov-07		2:06:20		68.61		47.5		9-Nov-07		2:07:53		67.4		48.5		20-Dec-07		2:25:59		67.4		42.5

		9-Nov-07		4:07:10		70.41		44.5		9-Nov-07		4:06:20		68.61		47.5		9-Nov-07		4:07:53		66.81		49.5		20-Dec-07		4:25:59		66.81		42.5

		9-Nov-07		6:07:10		69.8		44		9-Nov-07		6:06:20		68.61		46.5		9-Nov-07		6:07:53		68		47		20-Dec-07		6:25:59		67.4		42.5

		9-Nov-07		8:07:10		71.6		43		9-Nov-07		8:06:20		69.8		46		9-Nov-07		8:07:53		70.41		47		20-Dec-07		8:25:59		69.8		41.5

		9-Nov-07		10:07:10		71.6		44.5		9-Nov-07		10:06:20		71		48		9-Nov-07		10:07:53		71.6		47.5		20-Dec-07		10:25:59		71.6		41.5

		9-Nov-07		12:07:10		72.21		45		9-Nov-07		12:06:20		71		49		9-Nov-07		12:07:53		70.41		48		20-Dec-07		12:25:59		72.8		41

		9-Nov-07		14:07:10		74.01		42.5		9-Nov-07		14:06:20		71.6		44.5		9-Nov-07		14:07:53		71		49.5		20-Dec-07		14:25:59		72.8		42.5

		9-Nov-07		16:07:10		74.01		44		9-Nov-07		16:06:20		71.6		49		9-Nov-07		16:07:53		69.8		49.5		20-Dec-07		16:25:59		72.8		43.5

		9-Nov-07		18:07:10		72.8		42.5		9-Nov-07		18:06:20		70.41		46.5		9-Nov-07		18:07:53		69.8		50		20-Dec-07		18:25:59		72.8		43

		9-Nov-07		20:07:10		72.8		42.5		9-Nov-07		20:06:20		69.8		46		9-Nov-07		20:07:53		69.2		47		20-Dec-07		20:25:59		71.6		43

		9-Nov-07		22:07:10		71.6		43.5		9-Nov-07		22:06:20		69.2		47		9-Nov-07		22:07:53		69.2		47.5		20-Dec-07		22:25:59		70.41		45

		10-Nov-07		0:07:10		71		44.5		10-Nov-07		0:06:20		69.2		48.5		10-Nov-07		0:07:53		68.61		48.5		21-Dec-07		0:25:59		69.2		45.5

		10-Nov-07		2:07:10		71		45		10-Nov-07		2:06:20		68.61		49.5		10-Nov-07		2:07:53		68		49.5		21-Dec-07		2:25:59		68.61		46.5

		10-Nov-07		4:07:10		70.41		45		10-Nov-07		4:06:20		68.61		48		10-Nov-07		4:07:53		67.4		49.5		21-Dec-07		4:25:59		68.61		46.5

		10-Nov-07		6:07:10		69.8		42		10-Nov-07		6:06:20		68.61		45		10-Nov-07		6:07:53		66.81		47		21-Dec-07		6:25:59		68.61		46

		10-Nov-07		8:07:10		72.21		40		10-Nov-07		8:06:20		68.61		44		10-Nov-07		8:07:53		69.8		44		21-Dec-07		8:25:59		70.41		41

		10-Nov-07		10:07:10		74.01		39.5		10-Nov-07		10:06:20		71		42		10-Nov-07		10:07:53		70.41		47		21-Dec-07		10:25:59		72.8		40.5

		10-Nov-07		12:07:10		73.4		41		10-Nov-07		12:06:20		71		48.5		10-Nov-07		12:07:53		70.41		47		21-Dec-07		12:25:59		72.21		38.5

		10-Nov-07		14:07:10		73.4		40		10-Nov-07		14:06:20		71.6		41		10-Nov-07		14:07:53		71		51		21-Dec-07		14:25:59		72.8		37

		10-Nov-07		16:07:10		74.01		44		10-Nov-07		16:06:20		71		50		10-Nov-07		16:07:53		70.41		41.5		21-Dec-07		16:25:59		72.21		35.5

		10-Nov-07		18:07:10		73.4		44.5		10-Nov-07		18:06:20		69.8		51		10-Nov-07		18:07:53		70.41		52.5		21-Dec-07		18:25:59		71.6		34.5

		10-Nov-07		20:07:10		72.8		44		10-Nov-07		20:06:20		69.2		48.5		10-Nov-07		20:07:53		69.8		48.5		21-Dec-07		20:25:59		69.8		34.5

		10-Nov-07		22:07:10		71.6		42.5		10-Nov-07		22:06:20		68.61		46.5		10-Nov-07		22:07:53		69.2		46.5		21-Dec-07		22:25:59		68.61		35

		11-Nov-07		0:07:10		71		41		11-Nov-07		0:06:20		68.61		44.5		11-Nov-07		0:07:53		68		45		22-Dec-07		0:25:59		68		35

		11-Nov-07		2:07:10		70.41		40		11-Nov-07		2:06:20		68		43		11-Nov-07		2:07:53		66.2		45		22-Dec-07		2:25:59		67.4		34.5

		11-Nov-07		4:07:10		69.8		40		11-Nov-07		4:06:20		68		44		11-Nov-07		4:07:53		65.6		46.5		22-Dec-07		4:25:59		66.2		34

		11-Nov-07		6:07:10		69.8		41		11-Nov-07		6:06:20		68		45.5		11-Nov-07		6:07:53		65.01		48		22-Dec-07		6:25:59		66.81		33

		11-Nov-07		8:07:10		69.8		43		11-Nov-07		8:06:20		68		47.5		11-Nov-07		8:07:53		67.4		47		22-Dec-07		8:25:59		69.2		30.5

		11-Nov-07		10:07:10		69.8		46		11-Nov-07		10:06:20		68		51		11-Nov-07		10:07:53		68		48.5		22-Dec-07		10:25:59		70.41		31

		11-Nov-07		12:07:10		69.8		50		11-Nov-07		12:06:20		68		55		11-Nov-07		12:07:53		67.4		53.5		22-Dec-07		12:25:59		71		30

		11-Nov-07		14:07:10		70.41		52.5		11-Nov-07		14:06:20		68.61		57.5		11-Nov-07		14:07:53		68		54.5		22-Dec-07		14:25:59		70.41		30

		11-Nov-07		16:07:10		70.41		53.5		11-Nov-07		16:06:20		68.61		58.5		11-Nov-07		16:07:53		68		55.5		22-Dec-07		16:25:59		71.6		29.5

		11-Nov-07		18:07:10		70.41		54.5		11-Nov-07		18:06:20		68.61		59		11-Nov-07		18:07:53		68.61		56.5		22-Dec-07		18:25:59		70.41		30

		11-Nov-07		20:07:10		70.41		54.5		11-Nov-07		20:06:20		68.61		59		11-Nov-07		20:07:53		68.61		56		22-Dec-07		20:25:59		69.2		30.5

		11-Nov-07		22:07:10		70.41		55		11-Nov-07		22:06:20		68.61		59.5		11-Nov-07		22:07:53		68		56.5		22-Dec-07		22:25:59		66.81		31.5

		12-Nov-07		0:07:10		70.41		55		12-Nov-07		0:06:20		68.61		59		12-Nov-07		0:07:53		68		57		23-Dec-07		0:25:59		64.4		32

		12-Nov-07		2:07:10		70.41		55		12-Nov-07		2:06:20		68.61		59		12-Nov-07		2:07:53		68		57.5		23-Dec-07		2:25:59		63.21		32.5

		12-Nov-07		4:07:10		69.8		50.5		12-Nov-07		4:06:20		68.61		52		12-Nov-07		4:07:53		67.4		55.5		23-Dec-07		4:25:59		62.6		31.5

		12-Nov-07		6:07:10		69.8		45.5		12-Nov-07		6:06:20		68.61		46		12-Nov-07		6:07:53		66.2		51.5		23-Dec-07		6:25:59		62		31

		12-Nov-07		8:07:10		69.2		43.5		12-Nov-07		8:06:20		68		45.5		12-Nov-07		8:07:53		67.4		47		23-Dec-07		8:25:59		62.6		31

		12-Nov-07		10:07:10		69.2		44		12-Nov-07		10:06:20		68.61		46		12-Nov-07		10:07:53		68		47		23-Dec-07		10:25:59		62.6		32

		12-Nov-07		12:07:10		70.41		43		12-Nov-07		12:06:20		69.2		43.5		12-Nov-07		12:07:53		68		46.5		23-Dec-07		12:25:59		62.6		33.5

		12-Nov-07		14:07:10		71		39.5		12-Nov-07		14:06:20		69.2		39		12-Nov-07		14:07:53		69.2		43		23-Dec-07		14:25:59		65.01		35

		12-Nov-07		16:07:10		71		38.5		12-Nov-07		16:06:20		69.2		38.5		12-Nov-07		16:07:53		69.8		42.5		23-Dec-07		16:25:59		65.01		34

		12-Nov-07		18:07:10		71.6		39		12-Nov-07		18:06:20		69.8		38.5		12-Nov-07		18:07:53		69.8		42.5		23-Dec-07		18:25:59		64.4		34

		12-Nov-07		20:07:10		71		39.5		12-Nov-07		20:06:20		68.61		42		12-Nov-07		20:07:53		69.2		43		23-Dec-07		20:25:59		63.21		35.5

		12-Nov-07		22:07:10		70.41		39		12-Nov-07		22:06:20		68.61		41.5		12-Nov-07		22:07:53		67.4		43		23-Dec-07		22:25:59		62.6		35.5

		13-Nov-07		0:07:10		69.8		38.5		13-Nov-07		0:06:20		68		41		13-Nov-07		0:07:53		65.6		43.5		24-Dec-07		0:25:59		62.6		36

		13-Nov-07		2:07:10		69.2		38		13-Nov-07		2:06:20		68		40.5		13-Nov-07		2:07:53		64.4		44.5		24-Dec-07		2:25:59		62		36

		13-Nov-07		4:07:10		69.2		38		13-Nov-07		4:06:20		68		40.5		13-Nov-07		4:07:53		63.8		45		24-Dec-07		4:25:59		62		36

		13-Nov-07		6:07:10		68.61		39		13-Nov-07		6:06:20		68		41.5		13-Nov-07		6:07:53		66.81		43		24-Dec-07		6:25:59		62		36

		13-Nov-07		8:07:10		71.6		38		13-Nov-07		8:06:20		69.2		41		13-Nov-07		8:07:53		69.2		41.5		24-Dec-07		8:25:59		62		36

		13-Nov-07		10:07:10		72.8		38		13-Nov-07		10:06:20		70.41		42.5		13-Nov-07		10:07:53		71		41		24-Dec-07		10:25:59		62		36.5

		13-Nov-07		12:07:10		75.2		37.5		13-Nov-07		12:06:20		71		40		13-Nov-07		12:07:53		70.41		42.5		24-Dec-07		12:25:59		62		38

		13-Nov-07		14:07:10		74.6		35		13-Nov-07		14:06:20		71.6		38.5		13-Nov-07		14:07:53		71.6		42		24-Dec-07		14:25:59		63.21		41.5

		13-Nov-07		16:07:10		74.01		34.5		13-Nov-07		16:06:20		71.6		37.5		13-Nov-07		16:07:53		70.41		41		24-Dec-07		16:25:59		64.4		42.5

		13-Nov-07		18:07:10		74.01		32		13-Nov-07		18:06:20		69.8		31.5		13-Nov-07		18:07:53		70.41		38		24-Dec-07		18:25:59		65.6		43

		13-Nov-07		20:07:10		73.4		37		13-Nov-07		20:06:20		69.8		42		13-Nov-07		20:07:53		70.41		42		24-Dec-07		20:25:59		65.01		45.5

		13-Nov-07		22:07:10		72.8		40		13-Nov-07		22:06:20		69.8		45		13-Nov-07		22:07:53		69.8		44		24-Dec-07		22:25:59		64.4		44.5

		14-Nov-07		0:07:10		72.21		42		14-Nov-07		0:06:20		69.2		47.5		14-Nov-07		0:07:53		69.8		45		25-Dec-07		0:25:59		63.8		45

		14-Nov-07		2:07:10		72.21		43		14-Nov-07		2:06:20		69.8		48		14-Nov-07		2:07:53		69.2		47.5		25-Dec-07		2:25:59		63.8		45

		14-Nov-07		4:07:10		71.6		44.5		14-Nov-07		4:06:20		69.2		50		14-Nov-07		4:07:53		68.61		48.5		25-Dec-07		4:25:59		63.21		44.5

		14-Nov-07		6:07:10		71		46		14-Nov-07		6:06:20		69.2		51.5		14-Nov-07		6:07:53		68.61		50		25-Dec-07		6:25:59		64.4		44

		14-Nov-07		8:07:10		73.4		45		14-Nov-07		8:06:20		69.8		51.5		14-Nov-07		8:07:53		70.41		44		25-Dec-07		8:25:59		66.81		40.5

		14-Nov-07		10:07:10		74.01		46		14-Nov-07		10:06:20		71.6		54.5		14-Nov-07		10:07:53		70.41		53		25-Dec-07		10:25:59		69.2		36.5

		14-Nov-07		12:07:10		74.01		47.5		14-Nov-07		12:06:20		72.21		54		14-Nov-07		12:07:53		70.41		47		25-Dec-07		12:25:59		70.41		34.5

		14-Nov-07		14:07:10		74.01		48		14-Nov-07		14:06:20		72.21		45		14-Nov-07		14:07:53		70.41		47		25-Dec-07		14:25:59		71		33

		14-Nov-07		16:07:10		74.6		49.5		14-Nov-07		16:06:20		71.6		44.5		14-Nov-07		16:07:53		71		59.5		25-Dec-07		16:25:59		70.41		33.5

		14-Nov-07		18:07:10		74.6		49.5		14-Nov-07		18:06:20		71		49		14-Nov-07		18:07:53		71		53.5		25-Dec-07		18:25:59		68.61		33.5

		14-Nov-07		20:07:10		74.01		49		14-Nov-07		20:06:20		70.41		52.5		14-Nov-07		20:07:53		70.41		57.5		25-Dec-07		20:25:59		66.81		35

		14-Nov-07		22:07:10		73.4		52		14-Nov-07		22:06:20		69.8		61		14-Nov-07		22:07:53		71		55.5		25-Dec-07		22:25:59		64.4		35.5

		15-Nov-07		0:07:10		72.8		52		15-Nov-07		0:06:20		69.8		57		15-Nov-07		0:07:53		71		54		26-Dec-07		0:25:59		63.21		35

		15-Nov-07		2:07:10		72.21		50.5		15-Nov-07		2:06:20		69.8		56		15-Nov-07		2:07:53		70.41		53.5		26-Dec-07		2:25:59		62.6		34

		15-Nov-07		4:07:10		71.6		47		15-Nov-07		4:06:20		68.61		50.5		15-Nov-07		4:07:53		69.8		50.5		26-Dec-07		4:25:59		62		33.5

		15-Nov-07		6:07:10		71		45.5		15-Nov-07		6:06:20		68.61		49		15-Nov-07		6:07:53		68.61		49.5		26-Dec-07		6:25:59		62		33

		15-Nov-07		8:07:10		72.21		43.5		15-Nov-07		8:06:20		69.2		47		15-Nov-07		8:07:53		70.41		47.5		26-Dec-07		8:25:59		62.6		32.5

		15-Nov-07		10:07:10		74.01		44.5		15-Nov-07		10:06:20		71.6		56		15-Nov-07		10:07:53		71		46.5		26-Dec-07		10:25:59		62		32.5

		15-Nov-07		12:07:10		74.01		46.5		15-Nov-07		12:06:20		71.6		54		15-Nov-07		12:07:53		71.6		50.5		26-Dec-07		12:25:59		62		33.5

		15-Nov-07		14:07:10		74.01		47.5		15-Nov-07		14:06:20		71.6		56		15-Nov-07		14:07:53		71		52		26-Dec-07		14:25:59		62.6		34.5

		15-Nov-07		16:07:10		74.6		50		15-Nov-07		16:06:20		71.6		45.5		15-Nov-07		16:07:53		70.41		56		26-Dec-07		16:25:59		63.8		35.5

		15-Nov-07		18:07:10		74.01		51		15-Nov-07		18:06:20		70.41		51		15-Nov-07		18:07:53		70.41		56		26-Dec-07		18:25:59		63.8		37

		15-Nov-07		20:07:10		73.4		50		15-Nov-07		20:06:20		69.8		56.5		15-Nov-07		20:07:53		71		55.5		26-Dec-07		20:25:59		63.21		38

		15-Nov-07		22:07:10		73.4		48.5		15-Nov-07		22:06:20		69.8		54.5		15-Nov-07		22:07:53		71.6		51.5		26-Dec-07		22:25:59		62.6		37.5

		16-Nov-07		0:07:10		72.8		46.5		16-Nov-07		0:06:20		69.8		51		16-Nov-07		0:07:53		71		50		27-Dec-07		0:25:59		62		38.5

		16-Nov-07		2:07:10		71.6		45.5		16-Nov-07		2:06:20		68.61		49.5		16-Nov-07		2:07:53		69.2		49		27-Dec-07		2:25:59		62		39

		16-Nov-07		4:07:10		71		45.5		16-Nov-07		4:06:20		68.61		49.5		16-Nov-07		4:07:53		68.61		49.5		27-Dec-07		4:25:59		62		38

		16-Nov-07		6:07:10		70.41		44		16-Nov-07		6:06:20		68.61		47.5		16-Nov-07		6:07:53		67.4		49		27-Dec-07		6:25:59		62		37.5

		16-Nov-07		8:07:10		71.6		42.5		16-Nov-07		8:06:20		68.61		46		16-Nov-07		8:07:53		70.41		46		27-Dec-07		8:25:59		63.21		36.5

		16-Nov-07		10:07:10		72.8		44.5		16-Nov-07		10:06:20		71		49.5		16-Nov-07		10:07:53		72.21		47		27-Dec-07		10:25:59		67.4		35

		16-Nov-07		12:07:10		73.4		45		16-Nov-07		12:06:20		71.6		50.5		16-Nov-07		12:07:53		71		47		27-Dec-07		12:25:59		72.21		30.5

		16-Nov-07		14:07:10		74.01		46.5		16-Nov-07		14:06:20		71.6		53.5		16-Nov-07		14:07:53		71.6		51.5		27-Dec-07		14:25:59		71		28

		16-Nov-07		16:07:10		74.01		50		16-Nov-07		16:06:20		71.6		52		16-Nov-07		16:07:53		71		60.5		27-Dec-07		16:25:59		71		26

		16-Nov-07		18:07:10		74.01		49.5		16-Nov-07		18:06:20		70.41		62		16-Nov-07		18:07:53		70.41		53.5		27-Dec-07		18:25:59		70.41		26

		16-Nov-07		20:07:10		73.4		51		16-Nov-07		20:06:20		69.8		57.5		16-Nov-07		20:07:53		70.41		57		27-Dec-07		20:25:59		69.2		26.5

		16-Nov-07		22:07:10		72.8		51		16-Nov-07		22:06:20		69.8		56.5		16-Nov-07		22:07:53		70.41		55.5		27-Dec-07		22:25:59		66.2		31.5

		17-Nov-07		0:07:10		72.21		50.5		17-Nov-07		0:06:20		69.8		56		17-Nov-07		0:07:53		70.41		54		28-Dec-07		0:25:59		63.8		29.5

		17-Nov-07		2:07:10		71.6		50.5		17-Nov-07		2:06:20		69.2		56		17-Nov-07		2:07:53		69.8		53.5		28-Dec-07		2:25:59		62.6		29.5

		17-Nov-07		4:07:10		71.6		50.5		17-Nov-07		4:06:20		69.2		55.5		17-Nov-07		4:07:53		69.2		54		28-Dec-07		4:25:59		62.6		29.5

		17-Nov-07		6:07:10		71		49.5		17-Nov-07		6:06:20		68		54		17-Nov-07		6:07:53		68.61		53.5		28-Dec-07		6:25:59		62.6		29

		17-Nov-07		8:07:10		71.6		49.5		17-Nov-07		8:06:20		68		55		17-Nov-07		8:07:53		71		53		28-Dec-07		8:25:59		65.01		28.5

		17-Nov-07		10:07:10		72.21		47.5		17-Nov-07		10:06:20		71		51.5		17-Nov-07		10:07:53		71		49.5		28-Dec-07		10:25:59		68.61		28

		17-Nov-07		12:07:10		73.4		47.5		17-Nov-07		12:06:20		72.21		55		17-Nov-07		12:07:53		71.6		55.5		28-Dec-07		12:25:59		71.6		27

		17-Nov-07		14:07:10		74.01		49.5		17-Nov-07		14:06:20		71		46		17-Nov-07		14:07:53		71		57.5		28-Dec-07		14:25:59		71		28.5

		17-Nov-07		16:07:10		74.6		50		17-Nov-07		16:06:20		71.6		48		17-Nov-07		16:07:53		70.41		58		28-Dec-07		16:25:59		71		28.5

		17-Nov-07		18:07:10		74.6		48.5		17-Nov-07		18:06:20		69.8		55		17-Nov-07		18:07:53		70.41		50		28-Dec-07		18:25:59		72.21		29.5

		17-Nov-07		20:07:10		72.8		47.5		17-Nov-07		20:06:20		69.8		52		17-Nov-07		20:07:53		69.8		52		28-Dec-07		20:25:59		71		32

		17-Nov-07		22:07:10		71.6		48		17-Nov-07		22:06:20		69.2		53.5		17-Nov-07		22:07:53		69.2		51.5		28-Dec-07		22:25:59		68		34.5

		18-Nov-07		0:07:10		71.6		49.5		18-Nov-07		0:06:20		68.61		54		18-Nov-07		0:07:53		69.2		53		29-Dec-07		0:25:59		65.6		35

		18-Nov-07		2:07:10		71		49		18-Nov-07		2:06:20		68		54.5		18-Nov-07		2:07:53		68		53		29-Dec-07		2:25:59		64.4		36

		18-Nov-07		4:07:10		70.41		50		18-Nov-07		4:06:20		68		55		18-Nov-07		4:07:53		67.4		53.5		29-Dec-07		4:25:59		63.21		37

		18-Nov-07		6:07:10		69.8		49.5		18-Nov-07		6:06:20		67.4		54.5		18-Nov-07		6:07:53		66.81		54		29-Dec-07		6:25:59		64.4		37.5

		18-Nov-07		8:07:10		69.8		49.5		18-Nov-07		8:06:20		67.4		54.5		18-Nov-07		8:07:53		67.4		53		29-Dec-07		8:25:59		66.81		36.5

		18-Nov-07		10:07:10		69.2		49.5		18-Nov-07		10:06:20		67.4		54.5		18-Nov-07		10:07:53		67.4		53		29-Dec-07		10:25:59		69.8		36

		18-Nov-07		12:07:10		69.8		51.5		18-Nov-07		12:06:20		67.4		56.5		18-Nov-07		12:07:53		67.4		55.5		29-Dec-07		12:25:59		72.8		34

		18-Nov-07		14:07:10		70.41		52		18-Nov-07		14:06:20		68.61		55.5		18-Nov-07		14:07:53		68		55.5		29-Dec-07		14:25:59		72.8		34

		18-Nov-07		16:07:10		71		53.5		18-Nov-07		16:06:20		69.2		53.5		18-Nov-07		16:07:53		69.8		58		29-Dec-07		16:25:59		73.4		33

		18-Nov-07		18:07:10		71.6		55		18-Nov-07		18:06:20		69.2		56		18-Nov-07		18:07:53		69.8		58.5		29-Dec-07		18:25:59		72.21		33.5

		18-Nov-07		20:07:10		71		52		18-Nov-07		20:06:20		69.2		55.5		18-Nov-07		20:07:53		69.8		54.5		29-Dec-07		20:25:59		71		34

		18-Nov-07		22:07:10		70.41		52		18-Nov-07		22:06:20		68.61		56		18-Nov-07		22:07:53		68.61		55		29-Dec-07		22:25:59		67.4		36

		19-Nov-07		0:07:10		70.41		52		19-Nov-07		0:06:20		68		56		19-Nov-07		0:07:53		68.61		54.5		30-Dec-07		0:25:59		65.01		37.5

		19-Nov-07		2:07:10		69.8		51		19-Nov-07		2:06:20		67.4		56		19-Nov-07		2:07:53		68		55		30-Dec-07		2:25:59		63.8		38

		19-Nov-07		4:07:10		69.8		51		19-Nov-07		4:06:20		67.4		56.5		19-Nov-07		4:07:53		67.4		55.5		30-Dec-07		4:25:59		63.21		39

		19-Nov-07		6:07:10		69.8		51		19-Nov-07		6:06:20		67.4		55.5		19-Nov-07		6:07:53		66.81		56		30-Dec-07		6:25:59		62.6		39.5

		19-Nov-07		8:07:10		69.2		51		19-Nov-07		8:06:20		67.4		55.5		19-Nov-07		8:07:53		67.4		54		30-Dec-07		8:25:59		62.6		40.5

		19-Nov-07		10:07:10		69.2		52		19-Nov-07		10:06:20		67.4		56.5		19-Nov-07		10:07:53		67.4		55.5		30-Dec-07		10:25:59		63.21		42.5

		19-Nov-07		12:07:10		69.8		54.5		19-Nov-07		12:06:20		68		60		19-Nov-07		12:07:53		67.4		58		30-Dec-07		12:25:59		63.21		43.5

		19-Nov-07		14:07:10		70.41		56.5		19-Nov-07		14:06:20		68.61		60		19-Nov-07		14:07:53		68.61		59.5		30-Dec-07		14:25:59		63.8		44.5

		19-Nov-07		16:07:10		71		59		19-Nov-07		16:06:20		69.2		65		19-Nov-07		16:07:53		69.2		61.5		30-Dec-07		16:25:59		63.21		45

		19-Nov-07		18:07:10		71		55		19-Nov-07		18:06:20		69.8		54		19-Nov-07		18:07:53		69.8		59		30-Dec-07		18:25:59		63.21		46

		19-Nov-07		20:07:10		71.6		53		19-Nov-07		20:06:20		69.8		55		19-Nov-07		20:07:53		69.8		56		30-Dec-07		20:25:59		62.6		46.5

		19-Nov-07		22:07:10		71		52		19-Nov-07		22:06:20		69.2		54.5		19-Nov-07		22:07:53		69.2		54.5		30-Dec-07		22:25:59		62.6		47

		20-Nov-07		0:07:10		70.41		50		20-Nov-07		0:06:20		68		53.5		20-Nov-07		0:07:53		68.61		53		31-Dec-07		0:25:59		62.6		47.5

		20-Nov-07		2:07:10		69.8		48.5		20-Nov-07		2:06:20		68		52.5		20-Nov-07		2:07:53		67.4		52.5		31-Dec-07		2:25:59		62.6		48

		20-Nov-07		4:07:10		69.2		50		20-Nov-07		4:06:20		67.4		54.5		20-Nov-07		4:07:53		66.81		54		31-Dec-07		4:25:59		62.6		48.5

		20-Nov-07		6:07:10		69.2		52.5		20-Nov-07		6:06:20		67.4		58		20-Nov-07		6:07:53		67.4		54.5		31-Dec-07		6:25:59		62		48

		20-Nov-07		8:07:10		71		54.5		20-Nov-07		8:06:20		68.61		60		20-Nov-07		8:07:53		69.8		56.5		31-Dec-07		8:25:59		63.21		46

		20-Nov-07		10:07:10		72.8		56		20-Nov-07		10:06:20		70.41		58		20-Nov-07		10:07:53		71		50		31-Dec-07		10:25:59		63.8		44

		20-Nov-07		12:07:10		74.6		50.5		20-Nov-07		12:06:20		71		58.5		20-Nov-07		12:07:53		71.6		58		31-Dec-07		12:25:59		65.01		42.5

		20-Nov-07		14:07:10		74.6		45.5		20-Nov-07		14:06:20		71.6		52		20-Nov-07		14:07:53		71		52		31-Dec-07		14:25:59		65.6		41.5

		20-Nov-07		16:07:10		74.01		41		20-Nov-07		16:06:20		72.21		44		20-Nov-07		16:07:53		70.41		51.5		31-Dec-07		16:25:59		65.6		40.5

		20-Nov-07		18:07:10		73.4		40.5		20-Nov-07		18:06:20		69.8		42.5		20-Nov-07		18:07:53		70.41		48		31-Dec-07		18:25:59		65.6		39

		20-Nov-07		20:07:10		72.8		40		20-Nov-07		20:06:20		69.8		42		20-Nov-07		20:07:53		69.2		45.5		31-Dec-07		20:25:59		64.4		38.5

		20-Nov-07		22:07:10		71.6		39.5		20-Nov-07		22:06:20		68.61		42.5		20-Nov-07		22:07:53		68.61		44		31-Dec-07		22:25:59		62.6		38.5

		21-Nov-07		0:07:10		71		39		21-Nov-07		0:06:20		68.61		40.5		21-Nov-07		0:07:53		68		43		1-Jan-08		0:25:59		62.6		37

		21-Nov-07		2:07:10		70.41		38.5		21-Nov-07		2:06:20		68		40.5		21-Nov-07		2:07:53		66.2		43.5		1-Jan-08		2:25:59		62		36

		21-Nov-07		4:07:10		69.8		37		21-Nov-07		4:06:20		68		39.5		21-Nov-07		4:07:53		65.01		43.5		1-Jan-08		4:25:59		62		35

		21-Nov-07		6:07:10		69.2		36.5		21-Nov-07		6:06:20		68		38.5		21-Nov-07		6:07:53		67.4		39.5		1-Jan-08		6:25:59		62.6		33.5

		21-Nov-07		8:07:10		71		35.5		21-Nov-07		8:06:20		68		37		21-Nov-07		8:07:53		68.61		38		1-Jan-08		8:25:59		65.01		32.5

		21-Nov-07		10:07:10		71.6		35.5		21-Nov-07		10:06:20		69.8		34.5		21-Nov-07		10:07:53		71.6		37		1-Jan-08		10:25:59		68		31

		21-Nov-07		12:07:10		72.8		33.5		21-Nov-07		12:06:20		70.41		34.5		21-Nov-07		12:07:53		70.41		38.5		1-Jan-08		12:25:59		72.21		30.5

		21-Nov-07		14:07:10		73.4		33.5		21-Nov-07		14:06:20		71		35		21-Nov-07		14:07:53		71.6		34.5		1-Jan-08		14:25:59		71.6		31.5

		21-Nov-07		16:07:10		74.6		33.5		21-Nov-07		16:06:20		71		36		21-Nov-07		16:07:53		71		37.5		1-Jan-08		16:25:59		72.21		30.5

		21-Nov-07		18:07:10		74.01		35		21-Nov-07		18:06:20		69.8		37.5		21-Nov-07		18:07:53		70.41		38.5		1-Jan-08		18:25:59		71		31.5

		21-Nov-07		20:07:10		72.8		34		21-Nov-07		20:06:20		69.2		36		21-Nov-07		20:07:53		70.41		38		1-Jan-08		20:25:59		70.41		31.5

		21-Nov-07		22:07:10		71		34		21-Nov-07		22:06:20		68.61		36.5		21-Nov-07		22:07:53		68		37.5		1-Jan-08		22:25:59		66.2		32.5

		22-Nov-07		0:07:10		70.41		33.5		22-Nov-07		0:06:20		68		35.5		22-Nov-07		0:07:53		65.6		38		2-Jan-08		0:25:59		63.8		33

		22-Nov-07		2:07:10		69.8		32		22-Nov-07		2:06:20		68		34		22-Nov-07		2:07:53		64.4		38		2-Jan-08		2:25:59		62.6		33

		22-Nov-07		4:07:10		69.2		31		22-Nov-07		4:06:20		67.4		33		22-Nov-07		4:07:53		63.21		37.5		2-Jan-08		4:25:59		62		32.5

		22-Nov-07		6:07:10		68.61		31		22-Nov-07		6:06:20		68		32.5		22-Nov-07		6:07:53		66.81		33.5		2-Jan-08		6:25:59		62.6		31.5

		22-Nov-07		8:07:10		70.41		30.5		22-Nov-07		8:06:20		69.8		31.5		22-Nov-07		8:07:53		69.2		32		2-Jan-08		8:25:59		63.8		31

		22-Nov-07		10:07:10		71.6		31.5		22-Nov-07		10:06:20		70.41		33.5		22-Nov-07		10:07:53		71.6		33		2-Jan-08		10:25:59		64.4		31

		22-Nov-07		12:07:10		72.21		32.5		22-Nov-07		12:06:20		71		34		22-Nov-07		12:07:53		70.41		35.5		2-Jan-08		12:25:59		66.81		32.5

		22-Nov-07		14:07:10		73.4		31.5		22-Nov-07		14:06:20		71		32.5		22-Nov-07		14:07:53		71.6		33.5		2-Jan-08		14:25:59		68.61		34

		22-Nov-07		16:07:10		73.4		29		22-Nov-07		16:06:20		69.8		29		22-Nov-07		16:07:53		71.6		33		2-Jan-08		16:25:59		70.41		34.5

		22-Nov-07		18:07:10		74.01		31.5		22-Nov-07		18:06:20		69.8		34		22-Nov-07		18:07:53		70.41		36		2-Jan-08		18:25:59		71		33.5

		22-Nov-07		20:07:10		71.6		31		22-Nov-07		20:06:20		68.61		33		22-Nov-07		20:07:53		69.8		34.5		2-Jan-08		20:25:59		70.41		33

		22-Nov-07		22:07:10		70.41		31.5		22-Nov-07		22:06:20		66.81		34.5		22-Nov-07		22:07:53		66.81		35.5		2-Jan-08		22:25:59		66.2		34.5

		23-Nov-07		0:07:10		69.2		31.5		23-Nov-07		0:06:20		66.2		35		23-Nov-07		0:07:53		64.4		37		3-Jan-08		0:25:59		64.4		35.5

		23-Nov-07		2:07:10		68.61		31		23-Nov-07		2:06:20		66.2		34		23-Nov-07		2:07:53		63.21		37		3-Jan-08		2:25:59		62.6		35.5

		23-Nov-07		4:07:10		68		31		23-Nov-07		4:06:20		66.2		33.5		23-Nov-07		4:07:53		62		36.5		3-Jan-08		4:25:59		62		36

		23-Nov-07		6:07:10		67.4		30		23-Nov-07		6:06:20		66.2		31.5		23-Nov-07		6:07:53		66.2		32.5		3-Jan-08		6:25:59		63.8		36

		23-Nov-07		8:07:10		69.2		28.5		23-Nov-07		8:06:20		67.4		30		23-Nov-07		8:07:53		67.4		31		3-Jan-08		8:25:59		65.01		34.5

		23-Nov-07		10:07:10		69.8		30		23-Nov-07		10:06:20		68		33		23-Nov-07		10:07:53		68		32.5		3-Jan-08		10:25:59		67.4		35

		23-Nov-07		12:07:10		70.41		31.5		23-Nov-07		12:06:20		68.61		33		23-Nov-07		12:07:53		68.61		33.5		3-Jan-08		12:25:59		72.8		33.5

		23-Nov-07		14:07:10		71		31		23-Nov-07		14:06:20		69.2		32		23-Nov-07		14:07:53		69.2		34		3-Jan-08		14:25:59		73.4		33

		23-Nov-07		16:07:10		71.6		29.5		23-Nov-07		16:06:20		69.2		29		23-Nov-07		16:07:53		69.8		32.5		3-Jan-08		16:25:59		72.8		34

		23-Nov-07		18:07:10		71.6		31.5		23-Nov-07		18:06:20		69.8		31.5		23-Nov-07		18:07:53		69.8		34		3-Jan-08		18:25:59		72.8		34.5

		23-Nov-07		20:07:10		71.6		32		23-Nov-07		20:06:20		68.61		35		23-Nov-07		20:07:53		68.61		36		3-Jan-08		20:25:59		71.6		35

		23-Nov-07		22:07:10		69.8		32		23-Nov-07		22:06:20		67.4		35.5		23-Nov-07		22:07:53		66.81		36		3-Jan-08		22:25:59		68		36

		24-Nov-07		0:07:10		68.61		32		24-Nov-07		0:06:20		66.2		35.5		24-Nov-07		0:07:53		65.01		36.5		4-Jan-08		0:25:59		65.6		36.5

		24-Nov-07		2:07:10		68		31.5		24-Nov-07		2:06:20		66.2		33.5		24-Nov-07		2:07:53		63.8		36.5		4-Jan-08		2:25:59		64.4		38

		24-Nov-07		4:07:10		67.4		30.5		24-Nov-07		4:06:20		66.2		31.5		24-Nov-07		4:07:53		62.6		35.5		4-Jan-08		4:25:59		63.8		39

		24-Nov-07		6:07:10		67.4		30.5		24-Nov-07		6:06:20		66.2		32.5		24-Nov-07		6:07:53		66.81		32		4-Jan-08		6:25:59		65.01		41

		24-Nov-07		8:07:10		69.2		27		24-Nov-07		8:06:20		68		28		24-Nov-07		8:07:53		68		30		4-Jan-08		8:25:59		68.61		40

		24-Nov-07		10:07:10		70.41		23.5		24-Nov-07		10:06:20		69.2		22		24-Nov-07		10:07:53		68		26		4-Jan-08		10:25:59		71.6		41

		24-Nov-07		12:07:10		71		20.5		24-Nov-07		12:06:20		69.2		18.5		24-Nov-07		12:07:53		68.61		24		4-Jan-08		12:25:59		74.01		40.5

		24-Nov-07		14:07:10		71		19		24-Nov-07		14:06:20		69.2		16		24-Nov-07		14:07:53		69.2		23		4-Jan-08		14:25:59		73.4		42.5

		24-Nov-07		16:07:10		71.6		18.5		24-Nov-07		16:06:20		69.2		16.5		24-Nov-07		16:07:53		69.8		22		4-Jan-08		16:25:59		74.01		41.5

		24-Nov-07		18:07:10		71.6		18.5		24-Nov-07		18:06:20		69.2		17		24-Nov-07		18:07:53		70.41		22		4-Jan-08		18:25:59		73.4		42

		24-Nov-07		20:07:10		71.6		21		24-Nov-07		20:06:20		69.2		22		24-Nov-07		20:07:53		69.2		24.5		4-Jan-08		20:25:59		72.8		43

		24-Nov-07		22:07:10		69.8		24.5		24-Nov-07		22:06:20		67.4		28		24-Nov-07		22:07:53		67.4		28		4-Jan-08		22:25:59		69.8		44

		25-Nov-07		0:07:10		69.2		25.5		25-Nov-07		0:06:20		66.81		29		25-Nov-07		0:07:53		65.6		29.5		5-Jan-08		0:25:59		68		45

		25-Nov-07		2:07:10		68		25.5		25-Nov-07		2:06:20		66.2		28.5		25-Nov-07		2:07:53		63.8		30.5		5-Jan-08		2:25:59		67.4		45.5

		25-Nov-07		4:07:10		67.4		26		25-Nov-07		4:06:20		66.2		28.5		25-Nov-07		4:07:53		62.6		30.5		5-Jan-08		4:25:59		66.81		46

		25-Nov-07		6:07:10		66.81		25.5		25-Nov-07		6:06:20		66.2		28		25-Nov-07		6:07:53		62		31		5-Jan-08		6:25:59		67.4		49

		25-Nov-07		8:07:10		67.4		24.5		25-Nov-07		8:06:20		67.4		26		25-Nov-07		8:07:53		66.81		26.5		5-Jan-08		8:25:59		71.6		48.5

		25-Nov-07		10:07:10		68		26.5		25-Nov-07		10:06:20		68		29		25-Nov-07		10:07:53		67.4		28		5-Jan-08		10:25:59		73.4		48.5

		25-Nov-07		12:07:10		68.61		27.5		25-Nov-07		12:06:20		68		29		25-Nov-07		12:07:53		67.4		30		5-Jan-08		12:25:59		72.8		48.5

		25-Nov-07		14:07:10		69.2		26		25-Nov-07		14:06:20		69.2		26		25-Nov-07		14:07:53		68		29		5-Jan-08		14:25:59		72.21		46

		25-Nov-07		16:07:10		69.8		27.5		25-Nov-07		16:06:20		69.2		28.5		25-Nov-07		16:07:53		68.61		30.5		5-Jan-08		16:25:59		72.8		44.5

		25-Nov-07		18:07:10		70.41		29.5		25-Nov-07		18:06:20		69.2		30.5		25-Nov-07		18:07:53		68.61		31.5		5-Jan-08		18:25:59		73.4		42

		25-Nov-07		20:07:10		69.2		29.5		25-Nov-07		20:06:20		68		32		25-Nov-07		20:07:53		67.4		32.5		5-Jan-08		20:25:59		72.21		41.5

		25-Nov-07		22:07:10		68.61		32		25-Nov-07		22:06:20		66.81		35.5		25-Nov-07		22:07:53		66.2		35		5-Jan-08		22:25:59		68.61		43.5

		26-Nov-07		0:07:10		68		32		26-Nov-07		0:06:20		66.2		35.5		26-Nov-07		0:07:53		65.01		36		6-Jan-08		0:25:59		67.4		44

		26-Nov-07		2:07:10		68		32.5		26-Nov-07		2:06:20		66.2		35.5		26-Nov-07		2:07:53		63.8		37		6-Jan-08		2:25:59		66.2		43.5

		26-Nov-07		4:07:10		67.4		32.5		26-Nov-07		4:06:20		66.2		35.5		26-Nov-07		4:07:53		63.21		37.5		6-Jan-08		4:25:59		65.6		43.5

		26-Nov-07		6:07:10		67.4		33		26-Nov-07		6:06:20		66.2		35.5		26-Nov-07		6:07:53		62.6		38		6-Jan-08		6:25:59		65.01		43.5

		26-Nov-07		8:07:10		68		32.5		26-Nov-07		8:06:20		67.4		34.5		26-Nov-07		8:07:53		67.4		34		6-Jan-08		8:25:59		64.4		43.5

		26-Nov-07		10:07:10		68		34		26-Nov-07		10:06:20		67.4		36.5		26-Nov-07		10:07:53		67.4		36		6-Jan-08		10:25:59		64.4		44.5

		26-Nov-07		12:07:10		68.61		34.5		26-Nov-07		12:06:20		67.4		37		26-Nov-07		12:07:53		68		35.5		6-Jan-08		12:25:59		64.4		45.5

		26-Nov-07		14:07:10		68.61		32		26-Nov-07		14:06:20		68		32		26-Nov-07		14:07:53		68		34		6-Jan-08		14:25:59		64.4		47

		26-Nov-07		16:07:10		69.2		32		26-Nov-07		16:06:20		68.61		33		26-Nov-07		16:07:53		67.4		34.5		6-Jan-08		16:25:59		65.01		47.5

		26-Nov-07		18:07:10		69.2		33		26-Nov-07		18:06:20		68		35		26-Nov-07		18:07:53		68		35.5		6-Jan-08		18:25:59		64.4		47.5

		26-Nov-07		20:07:10		68.61		34		26-Nov-07		20:06:20		67.4		36.5		26-Nov-07		20:07:53		66.81		36.5		6-Jan-08		20:25:59		64.4		47.5

		26-Nov-07		22:07:10		68		33.5		26-Nov-07		22:06:20		66.2		36		26-Nov-07		22:07:53		64.4		37.5		6-Jan-08		22:25:59		64.4		46.5

		27-Nov-07		0:07:10		67.4		33		27-Nov-07		0:06:20		66.2		36		27-Nov-07		0:07:53		63.8		38		7-Jan-08		0:25:59		64.4		46

		27-Nov-07		2:07:10		66.81		32		27-Nov-07		2:06:20		66.2		34		27-Nov-07		2:07:53		62.6		36.5		7-Jan-08		2:25:59		63.8		45

		27-Nov-07		4:07:10		66.81		31.5		27-Nov-07		4:06:20		65.6		32.5		27-Nov-07		4:07:53		62		36.5		7-Jan-08		4:25:59		63.8		44.5

		27-Nov-07		6:07:10		66.81		30.5		27-Nov-07		6:06:20		65.6		32		27-Nov-07		6:07:53		66.81		32		7-Jan-08		6:25:59		63.21		43.5

		27-Nov-07		8:07:10		69.2		28.5		27-Nov-07		8:06:20		67.4		30.5		27-Nov-07		8:07:53		68.61		30.5		7-Jan-08		8:25:59		63.21		43

		27-Nov-07		10:07:10		69.8		31		27-Nov-07		10:06:20		69.8		32.5		27-Nov-07		10:07:53		69.2		32		7-Jan-08		10:25:59		63.8		42

		27-Nov-07		12:07:10		71		32.5		27-Nov-07		12:06:20		71.6		34		27-Nov-07		12:07:53		71		33.5		7-Jan-08		12:25:59		63.8		43

		27-Nov-07		14:07:10		71.6		34		27-Nov-07		14:06:20		71		35.5		27-Nov-07		14:07:53		71		34.5		7-Jan-08		14:25:59		65.01		44.5

		27-Nov-07		16:07:10		72.21		34		27-Nov-07		16:06:20		71.6		37.5		27-Nov-07		16:07:53		70.41		38		7-Jan-08		16:25:59		65.01		44.5

		27-Nov-07		18:07:10		72.21		36.5		27-Nov-07		18:06:20		69.8		39.5		27-Nov-07		18:07:53		69.8		39		7-Jan-08		18:25:59		65.6		44

		27-Nov-07		20:07:10		71.6		36.5		27-Nov-07		20:06:20		68.61		40		27-Nov-07		20:07:53		69.2		39.5		7-Jan-08		20:25:59		64.4		44.5

		27-Nov-07		22:07:10		69.8		35		27-Nov-07		22:06:20		67.4		38.5		27-Nov-07		22:07:53		67.4		38.5		7-Jan-08		22:25:59		63.8		45

		28-Nov-07		0:07:10		69.2		35		28-Nov-07		0:06:20		66.81		38.5		28-Nov-07		0:07:53		66.2		38.5		8-Jan-08		0:25:59		63.8		45.5

		28-Nov-07		2:07:10		68		34.5		28-Nov-07		2:06:20		66.2		38		28-Nov-07		2:07:53		65.01		39		8-Jan-08		2:25:59		63.8		45.5

		28-Nov-07		4:07:10		68		34		28-Nov-07		4:06:20		66.2		37		28-Nov-07		4:07:53		63.8		39		8-Jan-08		4:25:59		63.8		46

		28-Nov-07		6:07:10		67.4		34.5		28-Nov-07		6:06:20		66.2		37.5		28-Nov-07		6:07:53		67.4		35.5		8-Jan-08		6:25:59		65.01		45

		28-Nov-07		8:07:10		69.8		34		28-Nov-07		8:06:20		68		36.5		28-Nov-07		8:07:53		69.2		36.5		8-Jan-08		8:25:59		67.4		40.5

		28-Nov-07		10:07:10		71		34.5		28-Nov-07		10:06:20		70.41		36.5		28-Nov-07		10:07:53		71.6		36		8-Jan-08		10:25:59		69.8		39

		28-Nov-07		12:07:10		72.21		39		28-Nov-07		12:06:20		71		43.5		28-Nov-07		12:07:53		71		41		8-Jan-08		12:25:59		73.4		39

		28-Nov-07		14:07:10		72.8		34		28-Nov-07		14:06:20		71		34		28-Nov-07		14:07:53		71		39		8-Jan-08		14:25:59		72.8		37

		28-Nov-07		16:07:10		72.8		33.5		28-Nov-07		16:06:20		71.6		34.5		28-Nov-07		16:07:53		71		37.5		8-Jan-08		16:25:59		72.21		36

		28-Nov-07		18:07:10		72.8		35		28-Nov-07		18:06:20		70.41		37.5		28-Nov-07		18:07:53		71		37.5		8-Jan-08		18:25:59		72.21		35.5

		28-Nov-07		20:07:10		72.8		35		28-Nov-07		20:06:20		69.8		37.5		28-Nov-07		20:07:53		70.41		38.5		8-Jan-08		20:25:59		71.6		34.5

		28-Nov-07		22:07:10		71.6		35		28-Nov-07		22:06:20		68.61		38		28-Nov-07		22:07:53		69.2		38		8-Jan-08		22:25:59		68		37.5

		29-Nov-07		0:07:10		70.41		35.5		29-Nov-07		0:06:20		67.4		38.5		29-Nov-07		0:07:53		68		38		9-Jan-08		0:25:59		66.81		38

		29-Nov-07		2:07:10		69.2		34		29-Nov-07		2:06:20		66.81		37		29-Nov-07		2:07:53		66.2		38		9-Jan-08		2:25:59		65.6		39

		29-Nov-07		4:07:10		68.61		33		29-Nov-07		4:06:20		66.81		35.5		29-Nov-07		4:07:53		65.01		37.5		9-Jan-08		4:25:59		65.01		39.5

		29-Nov-07		6:07:10		68.61		32		29-Nov-07		6:06:20		66.2		33.5		29-Nov-07		6:07:53		66.81		34.5		9-Jan-08		6:25:59		65.6		39.5

		29-Nov-07		8:07:10		70.41		30.5		29-Nov-07		8:06:20		68		32		29-Nov-07		8:07:53		68		33.5		9-Jan-08		8:25:59		68.61		38

		29-Nov-07		10:07:10		71.6		32.5		29-Nov-07		10:06:20		71		34.5		29-Nov-07		10:07:53		70.41		34		9-Jan-08		10:25:59		71		40

		29-Nov-07		12:07:10		72.8		31		29-Nov-07		12:06:20		71.6		32.5		29-Nov-07		12:07:53		71		33		9-Jan-08		12:25:59		73.4		39

		29-Nov-07		14:07:10		72.8		31		29-Nov-07		14:06:20		71.6		32.5		29-Nov-07		14:07:53		71.6		31		9-Jan-08		14:25:59		74.01		40

		29-Nov-07		16:07:10		72.8		30.5		29-Nov-07		16:06:20		71.6		31.5		29-Nov-07		16:07:53		71		35		9-Jan-08		16:25:59		74.6		41

		29-Nov-07		18:07:10		72.8		28		29-Nov-07		18:06:20		69.2		29		29-Nov-07		18:07:53		71		32		9-Jan-08		18:25:59		75.2		41.5

		29-Nov-07		20:07:10		72.21		30		29-Nov-07		20:06:20		69.2		31		29-Nov-07		20:07:53		69.8		32.5		9-Jan-08		20:25:59		73.4		41.5

		29-Nov-07		22:07:10		70.41		31		29-Nov-07		22:06:20		67.4		34		29-Nov-07		22:07:53		68		34		9-Jan-08		22:25:59		69.8		42.5

		30-Nov-07		0:07:10		69.2		31		30-Nov-07		0:06:20		66.81		34		30-Nov-07		0:07:53		66.2		34.5		10-Jan-08		0:25:59		68		44

		30-Nov-07		2:07:10		68.61		30.5		30-Nov-07		2:06:20		66.2		33.5		30-Nov-07		2:07:53		65.01		35		10-Jan-08		2:25:59		66.81		44.5

		30-Nov-07		4:07:10		68		30		30-Nov-07		4:06:20		65.6		33		30-Nov-07		4:07:53		63.21		35		10-Jan-08		4:25:59		66.2		45

		30-Nov-07		6:07:10		67.4		30		30-Nov-07		6:06:20		66.2		32		30-Nov-07		6:07:53		67.4		31		10-Jan-08		6:25:59		68		45

		30-Nov-07		8:07:10		69.8		28		30-Nov-07		8:06:20		68.61		30.5		30-Nov-07		8:07:53		68		31		10-Jan-08		8:25:59		71.6		41.5

		30-Nov-07		10:07:10		71		30		30-Nov-07		10:06:20		70.41		33		30-Nov-07		10:07:53		70.41		32		10-Jan-08		10:25:59		73.4		40.5

		30-Nov-07		12:07:10		71.6		31.5		30-Nov-07		12:06:20		71		31		30-Nov-07		12:07:53		71.6		31.5		10-Jan-08		12:25:59		74.6		39.5

		30-Nov-07		14:07:10		72.8		30		30-Nov-07		14:06:20		71		31		30-Nov-07		14:07:53		71		35		10-Jan-08		14:25:59		74.6		39

		30-Nov-07		16:07:10		73.4		28		30-Nov-07		16:06:20		71		29		30-Nov-07		16:07:53		71		32.5		10-Jan-08		16:25:59		74.6		39

		30-Nov-07		18:07:10		73.4		26.5		30-Nov-07		18:06:20		69.8		26.5		30-Nov-07		18:07:53		69.8		31		10-Jan-08		18:25:59		73.4		39.5

		30-Nov-07		20:07:10		72.21		26		30-Nov-07		20:06:20		69.2		27.5		30-Nov-07		20:07:53		69.2		29		10-Jan-08		20:25:59		74.01		38.5

		30-Nov-07		22:07:10		71		27.5		30-Nov-07		22:06:20		68		30.5		30-Nov-07		22:07:53		68		31		10-Jan-08		22:25:59		70.41		43

		1-Dec-07		0:07:10		69.8		28.5		1-Dec-07		0:06:20		67.4		32		1-Dec-07		0:07:53		66.81		32.5		11-Jan-08		0:25:59		68.61		42.5

		1-Dec-07		2:07:10		69.2		28.5		1-Dec-07		2:06:20		66.81		31.5		1-Dec-07		2:07:53		65.01		33		11-Jan-08		2:25:59		67.4		43.5

		1-Dec-07		4:07:10		68.61		28		1-Dec-07		4:06:20		66.2		30.5		1-Dec-07		4:07:53		64.4		33		11-Jan-08		4:25:59		66.2		44

		1-Dec-07		6:07:10		68.61		28		1-Dec-07		6:06:20		66.2		30.5		1-Dec-07		6:07:53		66.81		30.5		11-Jan-08		6:25:59		68		44.5

		1-Dec-07		8:07:10		70.41		27		1-Dec-07		8:06:20		68		29		1-Dec-07		8:07:53		69.2		29.5		11-Jan-08		8:25:59		71.6		42

		1-Dec-07		10:07:10		71		27.5		1-Dec-07		10:06:20		70.41		29.5		1-Dec-07		10:07:53		71		29		11-Jan-08		10:25:59		74.01		41.5

		1-Dec-07		12:07:10		72.21		26.5		1-Dec-07		12:06:20		71.6		27		1-Dec-07		12:07:53		71		29.5		11-Jan-08		12:25:59		74.6		41

		1-Dec-07		14:07:10		72.8		24.5		1-Dec-07		14:06:20		71		26		1-Dec-07		14:07:53		70.41		29		11-Jan-08		14:25:59		74.01		43

		1-Dec-07		16:07:10		72.8		24.5		1-Dec-07		16:06:20		71		25.5		1-Dec-07		16:07:53		70.41		28		11-Jan-08		16:25:59		73.4		44.5

		1-Dec-07		18:07:10		72.8		26.5		1-Dec-07		18:06:20		69.8		28.5		1-Dec-07		18:07:53		70.41		30.5		11-Jan-08		18:25:59		71.6		45.5

		1-Dec-07		20:07:10		71.6		24.5		1-Dec-07		20:06:20		68		26		1-Dec-07		20:07:53		68.61		28		11-Jan-08		20:25:59		69.2		46.5

		1-Dec-07		22:07:10		69.8		24.5		1-Dec-07		22:06:20		66.81		27.5		1-Dec-07		22:07:53		66.2		28.5		11-Jan-08		22:25:59		68.61		47

		2-Dec-07		0:07:10		68.61		26		2-Dec-07		0:06:20		66.2		28		2-Dec-07		0:07:53		64.4		31.5		12-Jan-08		0:25:59		67.4		47.5

		2-Dec-07		2:07:10		68		25		2-Dec-07		2:06:20		65.6		28		2-Dec-07		2:07:53		63.21		30.5		12-Jan-08		2:25:59		66.81		48

		2-Dec-07		4:07:10		67.4		24.5		2-Dec-07		4:06:20		65.6		26.5		2-Dec-07		4:07:53		62		29.5		12-Jan-08		4:25:59		66.2		48

		2-Dec-07		6:07:10		66.81		24		2-Dec-07		6:06:20		65.6		26		2-Dec-07		6:07:53		61.41		29		12-Jan-08		6:25:59		66.2		49

		2-Dec-07		8:07:10		67.4		23		2-Dec-07		8:06:20		67.4		24.5		2-Dec-07		8:07:53		66.81		25.5		12-Jan-08		8:25:59		69.8		44.5

		2-Dec-07		10:07:10		67.4		24.5		2-Dec-07		10:06:20		67.4		26		2-Dec-07		10:07:53		68.61		25		12-Jan-08		10:25:59		71.6		43.5

		2-Dec-07		12:07:10		68		27		2-Dec-07		12:06:20		68		28.5		2-Dec-07		12:07:53		68.61		28		12-Jan-08		12:25:59		70.41		45

		2-Dec-07		14:07:10		68.61		27.5		2-Dec-07		14:06:20		68		28.5		2-Dec-07		14:07:53		69.2		29		12-Jan-08		14:25:59		71		44.5

		2-Dec-07		16:07:10		69.2		28		2-Dec-07		16:06:20		68		29.5		2-Dec-07		16:07:53		68		30		12-Jan-08		16:25:59		70.41		44

		2-Dec-07		18:07:10		69.2		28.5		2-Dec-07		18:06:20		68		30		2-Dec-07		18:07:53		67.4		31		12-Jan-08		18:25:59		69.8		44

		2-Dec-07		20:07:10		68		30		2-Dec-07		20:06:20		66.81		33		2-Dec-07		20:07:53		67.4		31		12-Jan-08		20:25:59		68.61		44.5

		2-Dec-07		22:07:10		67.4		29.5		2-Dec-07		22:06:20		66.2		32.5		2-Dec-07		22:07:53		63.8		33.5		12-Jan-08		22:25:59		67.4		46

		3-Dec-07		0:07:10		66.81		29.5		3-Dec-07		0:06:20		65.6		32		3-Dec-07		0:07:53		62.6		33.5		13-Jan-08		0:25:59		66.2		46.5

		3-Dec-07		2:07:10		66.81		30		3-Dec-07		2:06:20		66.2		33		3-Dec-07		2:07:53		62		34.5		13-Jan-08		2:25:59		66.2		47

		3-Dec-07		4:07:10		66.81		32.5		3-Dec-07		4:06:20		66.2		36		3-Dec-07		4:07:53		62.6		37.5		13-Jan-08		4:25:59		65.6		47

		3-Dec-07		6:07:10		66.81		35		3-Dec-07		6:06:20		66.2		39		3-Dec-07		6:07:53		62.6		40		13-Jan-08		6:25:59		65.01		47

		3-Dec-07		8:07:10		68		35.5		3-Dec-07		8:06:20		67.4		38		3-Dec-07		8:07:53		68.61		36		13-Jan-08		8:25:59		65.01		47.5

		3-Dec-07		10:07:10		68		35		3-Dec-07		10:06:20		67.4		37		3-Dec-07		10:07:53		68		36.5		13-Jan-08		10:25:59		65.01		48.5

		3-Dec-07		12:07:10		68		36		3-Dec-07		12:06:20		67.4		38		3-Dec-07		12:07:53		67.4		37.5		13-Jan-08		12:25:59		65.01		50

		3-Dec-07		14:07:10		68.61		36.5		3-Dec-07		14:06:20		68		39		3-Dec-07		14:07:53		68		38		13-Jan-08		14:25:59		65.6		51

		3-Dec-07		16:07:10		69.2		39		3-Dec-07		16:06:20		68		42.5		3-Dec-07		16:07:53		67.4		41		13-Jan-08		16:25:59		66.81		50

		3-Dec-07		18:07:10		69.2		39.5		3-Dec-07		18:06:20		68		42.5		3-Dec-07		18:07:53		67.4		42		13-Jan-08		18:25:59		67.4		49.5

		3-Dec-07		20:07:10		68.61		41		3-Dec-07		20:06:20		67.4		44.5		3-Dec-07		20:07:53		67.4		43		13-Jan-08		20:25:59		66.2		49.5

		3-Dec-07		22:07:10		68.61		44.5		3-Dec-07		22:06:20		66.81		50		3-Dec-07		22:07:53		66.2		47.5		13-Jan-08		22:25:59		65.6		49

		4-Dec-07		0:07:10		68.61		43		4-Dec-07		0:06:20		66.81		47		4-Dec-07		0:07:53		66.2		46.5		14-Jan-08		0:25:59		65.01		48

		4-Dec-07		2:07:10		68.61		42		4-Dec-07		2:06:20		66.81		45.5		4-Dec-07		2:07:53		66.2		45.5		14-Jan-08		2:25:59		64.4		48.5

		4-Dec-07		4:07:10		68.61		40.5		4-Dec-07		4:06:20		67.4		43		4-Dec-07		4:07:53		66.2		44.5		14-Jan-08		4:25:59		64.4		49

		4-Dec-07		6:07:10		68.61		40		4-Dec-07		6:06:20		67.4		42		4-Dec-07		6:07:53		66.2		44		14-Jan-08		6:25:59		64.4		49.5

		4-Dec-07		8:07:10		71.6		37		4-Dec-07		8:06:20		69.2		39		4-Dec-07		8:07:53		69.2		41		14-Jan-08		8:25:59		65.01		50.5

		4-Dec-07		10:07:10		72.8		39		4-Dec-07		10:06:20		71		42		4-Dec-07		10:07:53		70.41		43.5		14-Jan-08		10:25:59		65.6		49.5

		4-Dec-07		12:07:10		74.6		37.5		4-Dec-07		12:06:20		71.6		39		4-Dec-07		12:07:53		71		38.5		14-Jan-08		12:25:59		66.2		49

		4-Dec-07		14:07:10		73.4		38		4-Dec-07		14:06:20		71		42.5		4-Dec-07		14:07:53		71		39.5		14-Jan-08		14:25:59		66.81		48.5

		4-Dec-07		16:07:10		74.01		39.5		4-Dec-07		16:06:20		71.6		41.5		4-Dec-07		16:07:53		70.41		40		14-Jan-08		16:25:59		66.81		49

		4-Dec-07		18:07:10		74.01		40		4-Dec-07		18:06:20		70.41		42		4-Dec-07		18:07:53		71		45		14-Jan-08		18:25:59		66.81		49.5

		4-Dec-07		20:07:10		72.8		40.5		4-Dec-07		20:06:20		69.8		44		4-Dec-07		20:07:53		70.41		44		14-Jan-08		20:25:59		66.2		49

		4-Dec-07		22:07:10		72.21		44		4-Dec-07		22:06:20		69.8		50.5		4-Dec-07		22:07:53		69.8		46.5		14-Jan-08		22:25:59		65.01		49

		5-Dec-07		0:07:10		72.21		47		5-Dec-07		0:06:20		69.2		53.5		5-Dec-07		0:07:53		69.8		49.5		15-Jan-08		0:25:59		64.4		47.5

		5-Dec-07		2:07:10		71.6		48.5		5-Dec-07		2:06:20		69.2		54.5		5-Dec-07		2:07:53		69.2		51		15-Jan-08		2:25:59		63.8		47

		5-Dec-07		4:07:10		71		49.5		5-Dec-07		4:06:20		69.2		55		5-Dec-07		4:07:53		68.61		52.5		15-Jan-08		4:25:59		63.8		46.5

		5-Dec-07		6:07:10		71		50.5		5-Dec-07		6:06:20		68.61		56		5-Dec-07		6:07:53		68		53.5		15-Jan-08		6:25:59		64.4		46.5

		5-Dec-07		8:07:10		73.4		50		5-Dec-07		8:06:20		69.8		57.5		5-Dec-07		8:07:53		71		53		15-Jan-08		8:25:59		67.4		44

		5-Dec-07		10:07:10		74.01		49		5-Dec-07		10:06:20		71		44		5-Dec-07		10:07:53		71		57.5		15-Jan-08		10:25:59		71		43.5

		5-Dec-07		12:07:10		74.01		48		5-Dec-07		12:06:20		71.6		54		5-Dec-07		12:07:53		71		51		15-Jan-08		12:25:59		70.41		43

		5-Dec-07		14:07:10		74.01		49		5-Dec-07		14:06:20		71.6		54		5-Dec-07		14:07:53		71		48.5		15-Jan-08		14:25:59		69.8		44

		5-Dec-07		16:07:10		74.01		51		5-Dec-07		16:06:20		71.6		54		5-Dec-07		16:07:53		71		59.5		15-Jan-08		16:25:59		70.41		45

		5-Dec-07		18:07:10		73.4		50.5		5-Dec-07		18:06:20		69.8		57		5-Dec-07		18:07:53		71		47.5		15-Jan-08		18:25:59		71.6		43.5

		5-Dec-07		20:07:10		73.4		50		5-Dec-07		20:06:20		69.8		56		5-Dec-07		20:07:53		71		54.5		15-Jan-08		20:25:59		69.2		43

		5-Dec-07		22:07:10		72.8		50.5		5-Dec-07		22:06:20		69.8		56.5		5-Dec-07		22:07:53		70.41		55		15-Jan-08		22:25:59		66.81		43.5

		6-Dec-07		0:07:10		72.21		51.5		6-Dec-07		0:06:20		69.2		57		6-Dec-07		0:07:53		70.41		54.5		16-Jan-08		0:25:59		65.01		43.5

		6-Dec-07		2:07:10		71.6		51.5		6-Dec-07		2:06:20		69.2		57		6-Dec-07		2:07:53		69.8		54		16-Jan-08		2:25:59		64.4		43.5

		6-Dec-07		4:07:10		71.6		52		6-Dec-07		4:06:20		68.61		57.5		6-Dec-07		4:07:53		69.8		54		16-Jan-08		4:25:59		63.8		43.5

		6-Dec-07		6:07:10		71		50		6-Dec-07		6:06:20		68		54		6-Dec-07		6:07:53		69.2		53		16-Jan-08		6:25:59		64.4		42.5

		6-Dec-07		8:07:10		72.8		47.5		6-Dec-07		8:06:20		69.8		52		6-Dec-07		8:07:53		71		52		16-Jan-08		8:25:59		66.81		39.5

		6-Dec-07		10:07:10		74.01		45.5		6-Dec-07		10:06:20		71		45		6-Dec-07		10:07:53		71		50		16-Jan-08		10:25:59		70.41		38

		6-Dec-07		12:07:10		74.01		46		6-Dec-07		12:06:20		71		55		6-Dec-07		12:07:53		71		48		16-Jan-08		12:25:59		71		39.5

		6-Dec-07		14:07:10		74.01		46		6-Dec-07		14:06:20		71		57		6-Dec-07		14:07:53		71		54.5		16-Jan-08		14:25:59		72.21		40.5

		6-Dec-07		16:07:10		74.6		47.5		6-Dec-07		16:06:20		71		47.5		6-Dec-07		16:07:53		70.41		51.5		16-Jan-08		16:25:59		72.21		43

		6-Dec-07		18:07:10		74.01		39		6-Dec-07		18:06:20		69.8		41		6-Dec-07		18:07:53		69.8		45		16-Jan-08		18:25:59		72.8		41.5

		6-Dec-07		20:07:10		73.4		38		6-Dec-07		20:06:20		69.8		40		6-Dec-07		20:07:53		69.8		43.5		16-Jan-08		20:25:59		71		41.5

		6-Dec-07		22:07:10		72.21		40		6-Dec-07		22:06:20		69.2		44		6-Dec-07		22:07:53		70.41		44		16-Jan-08		22:25:59		68.61		41.5

		7-Dec-07		0:07:10		71.6		42		7-Dec-07		0:06:20		68		47		7-Dec-07		0:07:53		69.8		44.5		17-Jan-08		0:25:59		66.2		41.5

		7-Dec-07		2:07:10		70.41		42.5		7-Dec-07		2:06:20		67.4		48		7-Dec-07		2:07:53		69.2		45		17-Jan-08		2:25:59		65.01		41.5

		7-Dec-07		4:07:10		69.8		43		7-Dec-07		4:06:20		66.81		48.5		7-Dec-07		4:07:53		68.61		45.5		17-Jan-08		4:25:59		64.4		41.5

		7-Dec-07		6:07:10		69.8		43.5		7-Dec-07		6:06:20		66.81		49		7-Dec-07		6:07:53		68		46.5		17-Jan-08		6:25:59		65.01		39.5

		7-Dec-07		8:07:10		72.21		42		7-Dec-07		8:06:20		68.61		47.5		7-Dec-07		8:07:53		70.41		45		17-Jan-08		8:25:59		66.81		36.5

		7-Dec-07		10:07:10		73.4		42.5		7-Dec-07		10:06:20		71		49.5		7-Dec-07		10:07:53		71		48		17-Jan-08		10:25:59		71		33

		7-Dec-07		12:07:10		72.8		45		7-Dec-07		12:06:20		71		44.5		7-Dec-07		12:07:53		70.41		50.5		17-Jan-08		12:25:59		71.6		27

		7-Dec-07		14:07:10		72.21		47		7-Dec-07		14:06:20		71		47		7-Dec-07		14:07:53		71.6		52.5		17-Jan-08		14:25:59		72.8		25.5

		7-Dec-07		16:07:10		72.21		46		7-Dec-07		16:06:20		71		50		7-Dec-07		16:07:53		70.41		50		17-Jan-08		16:25:59		72.21		23.5

		7-Dec-07		18:07:10		72.21		45.5		7-Dec-07		18:06:20		69.2		50.5		7-Dec-07		18:07:53		70.41		51.5		17-Jan-08		18:25:59		72.21		23

		7-Dec-07		20:07:10		71		47		7-Dec-07		20:06:20		68.61		51		7-Dec-07		20:07:53		69.8		49		17-Jan-08		20:25:59		71.6		23

		7-Dec-07		22:07:10		69.8		47.5		7-Dec-07		22:06:20		67.4		52.5		7-Dec-07		22:07:53		69.8		48.5		17-Jan-08		22:25:59		69.2		24.5

		8-Dec-07		0:07:10		69.2		48		8-Dec-07		0:06:20		66.81		52.5		8-Dec-07		0:07:53		69.2		49		18-Jan-08		0:25:59		67.4		25.5

		8-Dec-07		2:07:10		68.61		44.5		8-Dec-07		2:06:20		66.81		47		8-Dec-07		2:07:53		68		46.5		18-Jan-08		2:25:59		66.2		26

		8-Dec-07		4:07:10		68.61		44		8-Dec-07		4:06:20		66.2		47		8-Dec-07		4:07:53		66.81		47		18-Jan-08		4:25:59		65.01		26

		8-Dec-07		6:07:10		68		43		8-Dec-07		6:06:20		66.2		45.5		8-Dec-07		6:07:53		67.4		45		18-Jan-08		6:25:59		66.2		26.5

		8-Dec-07		8:07:10		71		39		8-Dec-07		8:06:20		68		41		8-Dec-07		8:07:53		69.8		42		18-Jan-08		8:25:59		68.61		26

		8-Dec-07		10:07:10		72.21		37		8-Dec-07		10:06:20		69.8		40.5		8-Dec-07		10:07:53		71.6		40.5		18-Jan-08		10:25:59		72.21		27.5

		8-Dec-07		12:07:10		71.6		37.5		8-Dec-07		12:06:20		71		40.5		8-Dec-07		12:07:53		71		41		18-Jan-08		12:25:59		71.6		28

		8-Dec-07		14:07:10		71.6		36.5		8-Dec-07		14:06:20		71		40		8-Dec-07		14:07:53		71		35		18-Jan-08		14:25:59		72.21		29.5

		8-Dec-07		16:07:10		71.6		35.5		8-Dec-07		16:06:20		71		38		8-Dec-07		16:07:53		70.41		38.5		18-Jan-08		16:25:59		72.8		29

		8-Dec-07		18:07:10		71.6		35.5		8-Dec-07		18:06:20		69.8		35.5		8-Dec-07		18:07:53		69.8		37.5		18-Jan-08		18:25:59		72.21		30

		8-Dec-07		20:07:10		70.41		35		8-Dec-07		20:06:20		67.4		36.5		8-Dec-07		20:07:53		69.2		37		18-Jan-08		20:25:59		71.6		31.5

		8-Dec-07		22:07:10		69.2		33.5		8-Dec-07		22:06:20		66.81		36		8-Dec-07		22:07:53		67.4		37		18-Jan-08		22:25:59		68.61		32

		9-Dec-07		0:07:10		68.61		33.5		9-Dec-07		0:06:20		66.81		35.5		9-Dec-07		0:07:53		66.2		37		19-Jan-08		0:25:59		66.81		32.5

		9-Dec-07		2:07:10		68		33		9-Dec-07		2:06:20		66.2		35		9-Dec-07		2:07:53		65.6		37		19-Jan-08		2:25:59		65.01		33

		9-Dec-07		4:07:10		68		32.5		9-Dec-07		4:06:20		66.2		34		9-Dec-07		4:07:53		64.4		37		19-Jan-08		4:25:59		64.4		33

		9-Dec-07		6:07:10		67.4		32		9-Dec-07		6:06:20		66.2		33.5		9-Dec-07		6:07:53		63.8		36.5		19-Jan-08		6:25:59		66.2		32

		9-Dec-07		8:07:10		68		30.5		9-Dec-07		8:06:20		67.4		31.5		9-Dec-07		8:07:53		67.4		33		19-Jan-08		8:25:59		68.61		30

		9-Dec-07		10:07:10		68.61		30.5		9-Dec-07		10:06:20		68		31		9-Dec-07		10:07:53		68.61		31.5		19-Jan-08		10:25:59		70.41		31

		9-Dec-07		12:07:10		68.61		29.5		9-Dec-07		12:06:20		68.61		29		9-Dec-07		12:07:53		69.8		30		19-Jan-08		12:25:59		71		32.5

		9-Dec-07		14:07:10		68.61		28.5		9-Dec-07		14:06:20		68		28		9-Dec-07		14:07:53		70.41		30		19-Jan-08		14:25:59		71.6		33

		9-Dec-07		16:07:10		69.2		25		9-Dec-07		16:06:20		68		22.5		9-Dec-07		16:07:53		69.2		28.5		19-Jan-08		16:25:59		72.8		32.5

		9-Dec-07		18:07:10		69.2		24		9-Dec-07		18:06:20		68		23		9-Dec-07		18:07:53		68.61		27.5		19-Jan-08		18:25:59		72.8		33

		9-Dec-07		20:07:10		68.61		24		9-Dec-07		20:06:20		67.4		23.5		9-Dec-07		20:07:53		67.4		27		19-Jan-08		20:25:59		72.21		32

		9-Dec-07		22:07:10		68		24		9-Dec-07		22:06:20		66.81		24		9-Dec-07		22:07:53		66.2		27		19-Jan-08		22:25:59		68		34.5

		10-Dec-07		0:07:10		67.4		24		10-Dec-07		0:06:20		66.2		24.5		10-Dec-07		0:07:53		65.6		27.5		20-Jan-08		0:25:59		66.2		34.5

		10-Dec-07		2:07:10		67.4		24.5		10-Dec-07		2:06:20		66.2		25		10-Dec-07		2:07:53		64.4		28		20-Jan-08		2:25:59		65.01		34.5

		10-Dec-07		4:07:10		66.81		25		10-Dec-07		4:06:20		65.6		26.5		10-Dec-07		4:07:53		63.8		28.5		20-Jan-08		4:25:59		63.8		34

		10-Dec-07		6:07:10		66.2		26		10-Dec-07		6:06:20		65.6		28		10-Dec-07		6:07:53		63.21		29.5		20-Jan-08		6:25:59		63.21		33.5

		10-Dec-07		8:07:10		66.81		26		10-Dec-07		8:06:20		67.4		27		10-Dec-07		8:07:53		68.61		26.5		20-Jan-08		8:25:59		63.21		32.5

		10-Dec-07		10:07:10		67.4		26.5		10-Dec-07		10:06:20		67.4		27.5		10-Dec-07		10:07:53		67.4		27.5		20-Jan-08		10:25:59		63.21		33

		10-Dec-07		12:07:10		68		27.5		10-Dec-07		12:06:20		68		28		10-Dec-07		12:07:53		68		29		20-Jan-08		12:25:59		63.8		37

		10-Dec-07		14:07:10		68.61		28.5		10-Dec-07		14:06:20		68		29.5		10-Dec-07		14:07:53		68		30		20-Jan-08		14:25:59		65.01		39

		10-Dec-07		16:07:10		69.2		28.5		10-Dec-07		16:06:20		68.61		29		10-Dec-07		16:07:53		68		31.5		20-Jan-08		16:25:59		66.2		37.5

		10-Dec-07		18:07:10		69.2		30		10-Dec-07		18:06:20		68		31.5		10-Dec-07		18:07:53		67.4		32.5		20-Jan-08		18:25:59		66.81		37

		10-Dec-07		20:07:10		68.61		31		10-Dec-07		20:06:20		66.81		33.5		10-Dec-07		20:07:53		66.81		33.5		20-Jan-08		20:25:59		65.6		37

		10-Dec-07		22:07:10		68		32.5		10-Dec-07		22:06:20		66.2		35.5		10-Dec-07		22:07:53		65.6		35		20-Jan-08		22:25:59		65.01		37

		11-Dec-07		0:07:10		67.4		33.5		11-Dec-07		0:06:20		66.2		36.5		11-Dec-07		0:07:53		65.01		36.5		21-Jan-08		0:25:59		64.4		37

		11-Dec-07		2:07:10		66.81		32		11-Dec-07		2:06:20		66.2		34.5		11-Dec-07		2:07:53		64.4		36		21-Jan-08		2:25:59		63.8		38

		11-Dec-07		4:07:10		66.81		31.5		11-Dec-07		4:06:20		66.2		33		11-Dec-07		4:07:53		63.21		35.5		21-Jan-08		4:25:59		63.8		38.5

		11-Dec-07		6:07:10		66.81		30.5		11-Dec-07		6:06:20		66.2		32		11-Dec-07		6:07:53		67.4		31.5		21-Jan-08		6:25:59		63.21		38

		11-Dec-07		8:07:10		68.61		28.5		11-Dec-07		8:06:20		67.4		30		11-Dec-07		8:07:53		68		30.5		21-Jan-08		8:25:59		63.21		38

		11-Dec-07		10:07:10		69.2		30		11-Dec-07		10:06:20		69.8		31.5		11-Dec-07		10:07:53		69.2		31		21-Jan-08		10:25:59		63.8		38

		11-Dec-07		12:07:10		71.6		31.5		11-Dec-07		12:06:20		70.41		34		11-Dec-07		12:07:53		71.6		32.5		21-Jan-08		12:25:59		65.01		39

		11-Dec-07		14:07:10		71.6		32.5		11-Dec-07		14:06:20		70.41		34		11-Dec-07		14:07:53		71		35.5		21-Jan-08		14:25:59		65.6		36

		11-Dec-07		16:07:10		72.21		32.5		11-Dec-07		16:06:20		69.8		34.5		11-Dec-07		16:07:53		71		35		21-Jan-08		16:25:59		65.6		36

		11-Dec-07		18:07:10		72.21		31		11-Dec-07		18:06:20		69.8		31		11-Dec-07		18:07:53		71		34.5		21-Jan-08		18:25:59		65.6		35.5

		11-Dec-07		20:07:10		70.41		32.5		11-Dec-07		20:06:20		67.4		36		11-Dec-07		20:07:53		70.41		33.5		21-Jan-08		20:25:59		65.01		36

		11-Dec-07		22:07:10		69.2		27		11-Dec-07		22:06:20		66.81		26.5		11-Dec-07		22:07:53		68		31		21-Jan-08		22:25:59		63.8		36.5

		12-Dec-07		0:07:10		68.61		25		12-Dec-07		0:06:20		66.81		24		12-Dec-07		0:07:53		66.81		29		22-Jan-08		0:25:59		63.21		36

		12-Dec-07		2:07:10		68		22		12-Dec-07		2:06:20		66.81		20		12-Dec-07		2:07:53		66.2		26		22-Jan-08		2:25:59		63.21		35

		12-Dec-07		4:07:10		67.4		19.5		12-Dec-07		4:06:20		66.2		17		12-Dec-07		4:07:53		65.6		23.5		22-Jan-08		4:25:59		62.6		33.5

		12-Dec-07		6:07:10		67.4		18.5		12-Dec-07		6:06:20		66.2		16.5		12-Dec-07		6:07:53		65.01		22.5		22-Jan-08		6:25:59		64.4		32.5

		12-Dec-07		8:07:10		69.8		17.5		12-Dec-07		8:06:20		68		16		12-Dec-07		8:07:53		68		20.5		22-Jan-08		8:25:59		66.81		31

		12-Dec-07		10:07:10		71.6		19.5		12-Dec-07		10:06:20		70.41		20		12-Dec-07		10:07:53		71		22		22-Jan-08		10:25:59		69.8		31.5

		12-Dec-07		12:07:10		72.21		18.5		12-Dec-07		12:06:20		71		18		12-Dec-07		12:07:53		71		22.5		22-Jan-08		12:25:59		74.6		30.5

		12-Dec-07		14:07:10		72.21		17.5		12-Dec-07		14:06:20		71		18.5		12-Dec-07		14:07:53		71.6		23		22-Jan-08		14:25:59		72.8		34

		12-Dec-07		16:07:10		72.21		17		12-Dec-07		16:06:20		71		19		12-Dec-07		16:07:53		70.41		22		22-Jan-08		16:25:59		73.4		34.5

		12-Dec-07		18:07:10		72.21		19		12-Dec-07		18:06:20		69.2		19		12-Dec-07		18:07:53		70.41		23.5		22-Jan-08		18:25:59		73.4		33.5

		12-Dec-07		20:07:10		70.41		22		12-Dec-07		20:06:20		67.4		24		12-Dec-07		20:07:53		69.8		24		22-Jan-08		20:25:59		72.21		34

		12-Dec-07		22:07:10		69.2		22.5		12-Dec-07		22:06:20		66.81		26		12-Dec-07		22:07:53		68.61		25		22-Jan-08		22:25:59		67.4		36

		13-Dec-07		0:07:10		68.61		23		13-Dec-07		0:06:20		66.2		26		13-Dec-07		0:07:53		66.81		25.5		23-Jan-08		0:25:59		65.6		37.5

		13-Dec-07		2:07:10		67.4		23		13-Dec-07		2:06:20		66.2		26		13-Dec-07		2:07:53		65.01		26.5		23-Jan-08		2:25:59		64.4		38

		13-Dec-07		4:07:10		66.81		23.5		13-Dec-07		4:06:20		66.2		25.5		13-Dec-07		4:07:53		63.8		27.5		23-Jan-08		4:25:59		63.8		38

		13-Dec-07		6:07:10		67.4		24.5		13-Dec-07		6:06:20		66.2		27		13-Dec-07		6:07:53		67.4		25.5		23-Jan-08		6:25:59		66.2		37.5

		13-Dec-07		8:07:10		70.41		24.5		13-Dec-07		8:06:20		68		27		13-Dec-07		8:07:53		68.61		26.5		23-Jan-08		8:25:59		68.61		34.5

		13-Dec-07		10:07:10		71.6		25		13-Dec-07		10:06:20		70.41		27.5		13-Dec-07		10:07:53		70.41		27.5		23-Jan-08		10:25:59		72.21		33

		13-Dec-07		12:07:10		72.21		26.5		13-Dec-07		12:06:20		71		28.5		13-Dec-07		12:07:53		70.41		30		23-Jan-08		12:25:59		74.01		31.5

		13-Dec-07		14:07:10		72.21		25.5		13-Dec-07		14:06:20		71		27		13-Dec-07		14:07:53		70.41		30.5		23-Jan-08		14:25:59		72.8		31.5

		13-Dec-07		16:07:10		72.21		22.5		13-Dec-07		16:06:20		71		23.5		13-Dec-07		16:07:53		70.41		28		23-Jan-08		16:25:59		72.21		31.5

		13-Dec-07		18:07:10		72.8		23.5		13-Dec-07		18:06:20		69.8		24		13-Dec-07		18:07:53		69.8		27.5		23-Jan-08		18:25:59		72.8		30.5

		13-Dec-07		20:07:10		70.41		25.5		13-Dec-07		20:06:20		67.4		28.5		13-Dec-07		20:07:53		69.2		28		23-Jan-08		20:25:59		72.8		30

		13-Dec-07		22:07:10		69.2		25.5		13-Dec-07		22:06:20		66.81		29		13-Dec-07		22:07:53		68		28.5		23-Jan-08		22:25:59		68		32

		14-Dec-07		0:07:10		68		26		14-Dec-07		0:06:20		66.2		29		14-Dec-07		0:07:53		66.2		29		24-Jan-08		0:25:59		65.6		33

		14-Dec-07		2:07:10		67.4		26.5		14-Dec-07		2:06:20		66.2		29		14-Dec-07		2:07:53		64.4		30		24-Jan-08		2:25:59		64.4		34

		14-Dec-07		4:07:10		66.81		26		14-Dec-07		4:06:20		66.2		28.5		14-Dec-07		4:07:53		63.21		30.5		24-Jan-08		4:25:59		63.8		35

		14-Dec-07		6:07:10		66.81		25.5		14-Dec-07		6:06:20		66.2		27		14-Dec-07		6:07:53		66.2		27		24-Jan-08		6:25:59		65.6		36

		14-Dec-07		8:07:10		69.2		24		14-Dec-07		8:06:20		67.4		26		14-Dec-07		8:07:53		68.61		26.5		24-Jan-08		8:25:59		68		34.5

		14-Dec-07		10:07:10		69.8		26		14-Dec-07		10:06:20		69.8		28		14-Dec-07		10:07:53		69.8		27.5		24-Jan-08		10:25:59		71.6		34.5

		14-Dec-07		12:07:10		71		28		14-Dec-07		12:06:20		70.41		30.5		14-Dec-07		12:07:53		71.6		28.5		24-Jan-08		12:25:59		74.01		33.5

		14-Dec-07		14:07:10		71.6		28		14-Dec-07		14:06:20		71		29.5		14-Dec-07		14:07:53		71		28.5		24-Jan-08		14:25:59		71.6		35

		14-Dec-07		16:07:10		72.21		29		14-Dec-07		16:06:20		71.6		30		14-Dec-07		16:07:53		69.8		32		24-Jan-08		16:25:59		72.21		34.5

		14-Dec-07		18:07:10		73.4		30		14-Dec-07		18:06:20		69.8		33		14-Dec-07		18:07:53		70.41		33.5		24-Jan-08		18:25:59		72.21		33.5

		14-Dec-07		20:07:10		71		30.5		14-Dec-07		20:06:20		69.2		33		14-Dec-07		20:07:53		69.2		32		24-Jan-08		20:25:59		72.21		33.5

		14-Dec-07		22:07:10		69.2		29.5		14-Dec-07		22:06:20		66.81		32.5		14-Dec-07		22:07:53		68		31.5		24-Jan-08		22:25:59		68		36

		15-Dec-07		0:07:10		68		29		15-Dec-07		0:06:20		66.2		32		15-Dec-07		0:07:53		65.6		32		25-Jan-08		0:25:59		65.6		36.5

		15-Dec-07		2:07:10		67.4		28		15-Dec-07		2:06:20		66.2		30.5		15-Dec-07		2:07:53		63.8		32		25-Jan-08		2:25:59		65.01		37.5

		15-Dec-07		4:07:10		66.81		27		15-Dec-07		4:06:20		65.6		29		15-Dec-07		4:07:53		63.21		31.5		25-Jan-08		4:25:59		64.4		38.5

		15-Dec-07		6:07:10		66.81		27		15-Dec-07		6:06:20		66.2		28.5		15-Dec-07		6:07:53		67.4		27.5		25-Jan-08		6:25:59		66.2		38

		15-Dec-07		8:07:10		68.61		25		15-Dec-07		8:06:20		67.4		26		15-Dec-07		8:07:53		68.61		27		25-Jan-08		8:25:59		69.2		36

		15-Dec-07		10:07:10		70.41		27		15-Dec-07		10:06:20		69.8		28.5		15-Dec-07		10:07:53		70.41		28.5		25-Jan-08		10:25:59		72.8		36

		15-Dec-07		12:07:10		71.6		29.5		15-Dec-07		12:06:20		71		29.5		15-Dec-07		12:07:53		71.6		30		25-Jan-08		12:25:59		74.01		34.5

		15-Dec-07		14:07:10		71.6		30.5		15-Dec-07		14:06:20		71		31.5		15-Dec-07		14:07:53		70.41		30		25-Jan-08		14:25:59		73.4		35

		15-Dec-07		16:07:10		71.6		30.5		15-Dec-07		16:06:20		71		31.5		15-Dec-07		16:07:53		71		32.5		25-Jan-08		16:25:59		74.01		35.5

		15-Dec-07		18:07:10		72.8		33		15-Dec-07		18:06:20		69.8		37		15-Dec-07		18:07:53		70.41		35.5		25-Jan-08		18:25:59		72.8		35

		15-Dec-07		20:07:10		71		34.5		15-Dec-07		20:06:20		67.4		39		15-Dec-07		20:07:53		69.2		35.5		25-Jan-08		20:25:59		72.21		34

		15-Dec-07		22:07:10		69.2		33.5		15-Dec-07		22:06:20		66.81		37.5		15-Dec-07		22:07:53		67.4		35.5		25-Jan-08		22:25:59		69.2		36

		16-Dec-07		0:07:10		68.61		34		16-Dec-07		0:06:20		66.2		38		16-Dec-07		0:07:53		66.2		36.5		26-Jan-08		0:25:59		67.4		36.5

		16-Dec-07		2:07:10		68		34		16-Dec-07		2:06:20		66.2		38		16-Dec-07		2:07:53		65.6		37.5		26-Jan-08		2:25:59		66.2		37

		16-Dec-07		4:07:10		68		35		16-Dec-07		4:06:20		66.2		39		16-Dec-07		4:07:53		65.01		38.5		26-Jan-08		4:25:59		65.6		37

		16-Dec-07		6:07:10		67.4		35		16-Dec-07		6:06:20		66.2		38		16-Dec-07		6:07:53		64.4		39		26-Jan-08		6:25:59		66.81		37

		16-Dec-07		8:07:10		68		34		16-Dec-07		8:06:20		67.4		36.5		16-Dec-07		8:07:53		66.81		37		26-Jan-08		8:25:59		70.41		37

		16-Dec-07		10:07:10		68		34.5		16-Dec-07		10:06:20		67.4		36.5		16-Dec-07		10:07:53		66.81		36		26-Jan-08		10:25:59		73.4		38

		16-Dec-07		12:07:10		68		35		16-Dec-07		12:06:20		68		37		16-Dec-07		12:07:53		67.4		36.5		26-Jan-08		12:25:59		72.8		39

		16-Dec-07		14:07:10		68.61		37		16-Dec-07		14:06:20		68		39.5		16-Dec-07		14:07:53		66.81		39		26-Jan-08		14:25:59		73.4		39.5

		16-Dec-07		16:07:10		69.2		39		16-Dec-07		16:06:20		68		42.5		16-Dec-07		16:07:53		67.4		41.5		26-Jan-08		16:25:59		73.4		39.5

		16-Dec-07		18:07:10		69.2		40.5		16-Dec-07		18:06:20		68		44		16-Dec-07		18:07:53		68		42.5		26-Jan-08		18:25:59		73.4		40

		16-Dec-07		20:07:10		68.61		40.5		16-Dec-07		20:06:20		66.81		44		16-Dec-07		20:07:53		67.4		42		26-Jan-08		20:25:59		72.8		41

		16-Dec-07		22:07:10		68		40.5		16-Dec-07		22:06:20		66.81		44		16-Dec-07		22:07:53		66.2		43		26-Jan-08		22:25:59		69.8		43

		17-Dec-07		0:07:10		68		41		17-Dec-07		0:06:20		66.2		44.5		17-Dec-07		0:07:53		66.2		43.5		27-Jan-08		0:25:59		68		44

		17-Dec-07		2:07:10		67.4		41		17-Dec-07		2:06:20		66.2		44.5		17-Dec-07		2:07:53		65.6		44		27-Jan-08		2:25:59		67.4		45.5

		17-Dec-07		4:07:10		67.4		40.5		17-Dec-07		4:06:20		66.2		44.5		17-Dec-07		4:07:53		65.01		44		27-Jan-08		4:25:59		66.81		46.5

		17-Dec-07		6:07:10		66.81		40.5		17-Dec-07		6:06:20		66.2		43.5		17-Dec-07		6:07:53		65.01		43.5		27-Jan-08		6:25:59		66.2		47

		17-Dec-07		8:07:10		68		40		17-Dec-07		8:06:20		67.4		42.5		17-Dec-07		8:07:53		66.81		41.5		27-Jan-08		8:25:59		66.2		46.5

		17-Dec-07		10:07:10		68		40.5		17-Dec-07		10:06:20		67.4		43		17-Dec-07		10:07:53		67.4		42		27-Jan-08		10:25:59		66.2		45.5

		17-Dec-07		12:07:10		68		40.5		17-Dec-07		12:06:20		67.4		42.5		17-Dec-07		12:07:53		67.4		42.5		27-Jan-08		12:25:59		66.81		45

		17-Dec-07		14:07:10		68.61		37		17-Dec-07		14:06:20		68		37		17-Dec-07		14:07:53		67.4		40		27-Jan-08		14:25:59		67.4		46

		17-Dec-07		16:07:10		68.61		37.5		17-Dec-07		16:06:20		67.4		39.5		17-Dec-07		16:07:53		67.4		40.5		27-Jan-08		16:25:59		68		45.5

		17-Dec-07		18:07:10		68.61		38		17-Dec-07		18:06:20		68		39.5		17-Dec-07		18:07:53		67.4		40		27-Jan-08		18:25:59		67.4		44.5

		17-Dec-07		20:07:10		68		40		17-Dec-07		20:06:20		66.81		43.5		17-Dec-07		20:07:53		66.81		42		27-Jan-08		20:25:59		66.81		44

		17-Dec-07		22:07:10		68		42.5		17-Dec-07		22:06:20		66.2		47		17-Dec-07		22:07:53		65.6		45		27-Jan-08		22:25:59		66.2		44

		18-Dec-07		0:07:10		67.4		43.5		18-Dec-07		0:06:20		66.2		48.5		18-Dec-07		0:07:53		65.6		46.5		28-Jan-08		0:25:59		66.2		44.5

		18-Dec-07		2:07:10		67.4		43.5		18-Dec-07		2:06:20		66.81		46.5		18-Dec-07		2:07:53		65.6		46.5		28-Jan-08		2:25:59		66.2		46

		18-Dec-07		4:07:10		67.4		42		18-Dec-07		4:06:20		66.2		44.5		18-Dec-07		4:07:53		65.01		45.5		28-Jan-08		4:25:59		65.6		46.5

		18-Dec-07		6:07:10		67.4		43		18-Dec-07		6:06:20		66.2		46		18-Dec-07		6:07:53		66.81		43.5		28-Jan-08		6:25:59		65.6		47

		18-Dec-07		8:07:10		69.8		41		18-Dec-07		8:06:20		68		44.5		18-Dec-07		8:07:53		69.2		43		28-Jan-08		8:25:59		65.6		47.5

		18-Dec-07		10:07:10		71		42		18-Dec-07		10:06:20		71		39		18-Dec-07		10:07:53		71.6		41.5		28-Jan-08		10:25:59		66.81		47.5

		18-Dec-07		12:07:10		71.6		41		18-Dec-07		12:06:20		71.6		43.5		18-Dec-07		12:07:53		71.6		43.5		28-Jan-08		12:25:59		68		47

		18-Dec-07		14:07:10		71.6		41		18-Dec-07		14:06:20		71		45		18-Dec-07		14:07:53		71		45.5		28-Jan-08		14:25:59		68.61		46.5

		18-Dec-07		16:07:10		72.21		44		18-Dec-07		16:06:20		71		39.5		18-Dec-07		16:07:53		71		46		28-Jan-08		16:25:59		68.61		46.5

		18-Dec-07		18:07:10		72.21		42		18-Dec-07		18:06:20		69.2		45		18-Dec-07		18:07:53		71.6		40.5		28-Jan-08		18:25:59		69.2		46.5

		18-Dec-07		20:07:10		71		41.5		18-Dec-07		20:06:20		68		45		18-Dec-07		20:07:53		70.41		42.5		28-Jan-08		20:25:59		67.4		47.5

		18-Dec-07		22:07:10		69.8		43		18-Dec-07		22:06:20		66.81		48.5		18-Dec-07		22:07:53		68.61		44.5		28-Jan-08		22:25:59		66.2		46

		19-Dec-07		0:07:10		69.2		44		19-Dec-07		0:06:20		66.81		48.5		19-Dec-07		0:07:53		68		45.5		29-Jan-08		0:25:59		65.01		42.5

		19-Dec-07		2:07:10		68.61		44.5		19-Dec-07		2:06:20		66.81		49		19-Dec-07		2:07:53		67.4		46.5		29-Jan-08		2:25:59		64.4		41

		19-Dec-07		4:07:10		68.61		44.5		19-Dec-07		4:06:20		66.81		48.5		19-Dec-07		4:07:53		66.81		47.5		29-Jan-08		4:25:59		64.4		40.5

		19-Dec-07		6:07:10		68		45		19-Dec-07		6:06:20		66.81		48.5		19-Dec-07		6:07:53		68		46		29-Jan-08		6:25:59		66.2		39

		19-Dec-07		8:07:10		70.41		43		19-Dec-07		8:06:20		68.61		46		19-Dec-07		8:07:53		69.8		44.5		29-Jan-08		8:25:59		68.61		37

		19-Dec-07		10:07:10		71.6		42		19-Dec-07		10:06:20		71		48.5		19-Dec-07		10:07:53		71		43.5		29-Jan-08		10:25:59		73.4		35.5

		19-Dec-07		12:07:10		72.21		44		19-Dec-07		12:06:20		71.6		49.5		19-Dec-07		12:07:53		70.41		50		29-Jan-08		12:25:59		71		37

		19-Dec-07		14:07:10		72.21		45.5		19-Dec-07		14:06:20		71		53.5		19-Dec-07		14:07:53		69.8		49.5		29-Jan-08		14:25:59		71.6		36

		19-Dec-07		16:07:10		72.8		45.5		19-Dec-07		16:06:20		71		47		19-Dec-07		16:07:53		70.41		47		29-Jan-08		16:25:59		72.8		35.5

		19-Dec-07		18:07:10		72.21		41.5		19-Dec-07		18:06:20		69.2		44		19-Dec-07		18:07:53		69.8		44.5		29-Jan-08		18:25:59		72.21		35.5

		19-Dec-07		20:07:10		71		41		19-Dec-07		20:06:20		67.4		44.5		19-Dec-07		20:07:53		69.2		43		29-Jan-08		20:25:59		72.21		33.5

		19-Dec-07		22:07:10		69.8		39		19-Dec-07		22:06:20		66.81		42		19-Dec-07		22:07:53		68		42		29-Jan-08		22:25:59		68		36

		20-Dec-07		0:07:10		68.61		38.5		20-Dec-07		0:06:20		66.2		42		20-Dec-07		0:07:53		66.2		42		30-Jan-08		0:25:59		66.2		36

		20-Dec-07		2:07:10		68.61		39		20-Dec-07		2:06:20		66.2		43		20-Dec-07		2:07:53		65.6		43		30-Jan-08		2:25:59		65.01		36

		20-Dec-07		4:07:10		68		40		20-Dec-07		4:06:20		66.2		43.5		20-Dec-07		4:07:53		65.01		44		30-Jan-08		4:25:59		63.8		35

		20-Dec-07		6:07:10		68		40		20-Dec-07		6:06:20		66.2		43.5		20-Dec-07		6:07:53		67.4		41.5		30-Jan-08		6:25:59		66.2		34

		20-Dec-07		8:07:10		70.41		39		20-Dec-07		8:06:20		68		42.5		20-Dec-07		8:07:53		69.8		41		30-Jan-08		8:25:59		69.2		33

		20-Dec-07		10:07:10		72.21		39		20-Dec-07		10:06:20		70.41		42		20-Dec-07		10:07:53		71.6		39.5		30-Jan-08		10:25:59		72.8		33.5

		20-Dec-07		12:07:10		72.21		41		20-Dec-07		12:06:20		71		45.5		20-Dec-07		12:07:53		71.6		43		30-Jan-08		12:25:59		73.4		34

		20-Dec-07		14:07:10		72.8		39.5		20-Dec-07		14:06:20		70.41		47.5		20-Dec-07		14:07:53		71.6		42		30-Jan-08		14:25:59		72.8		37.5

		20-Dec-07		16:07:10		72.21		43		20-Dec-07		16:06:20		70.41		43		20-Dec-07		16:07:53		70.41		46		30-Jan-08		16:25:59		72.8		39.5

		20-Dec-07		18:07:10		72.8		41.5		20-Dec-07		18:06:20		69.2		45.5		20-Dec-07		18:07:53		70.41		44.5		30-Jan-08		18:25:59		72.21		37.5

		20-Dec-07		20:07:10		71.6		42.5		20-Dec-07		20:06:20		68.61		47.5		20-Dec-07		20:07:53		69.8		45		30-Jan-08		20:25:59		72.21		34.5

		20-Dec-07		22:07:10		70.41		44.5		20-Dec-07		22:06:20		68		49.5		20-Dec-07		22:07:53		69.2		46.5		30-Jan-08		22:25:59		69.2		36

		21-Dec-07		0:07:10		69.8		46		21-Dec-07		0:06:20		67.4		51.5		21-Dec-07		0:07:53		68		47.5		31-Jan-08		0:25:59		67.4		36.5

		21-Dec-07		2:07:10		69.2		46		21-Dec-07		2:06:20		67.4		51		21-Dec-07		2:07:53		68		49		31-Jan-08		2:25:59		66.2		36.5

		21-Dec-07		4:07:10		69.2		46.5		21-Dec-07		4:06:20		66.81		51.5		21-Dec-07		4:07:53		67.4		49		31-Jan-08		4:25:59		65.6		37

		21-Dec-07		6:07:10		68.61		44.5		21-Dec-07		6:06:20		66.81		47		21-Dec-07		6:07:53		67.4		47		31-Jan-08		6:25:59		66.81		36

		21-Dec-07		8:07:10		71		38.5		21-Dec-07		8:06:20		68		39		21-Dec-07		8:07:53		69.8		42		31-Jan-08		8:25:59		70.41		34.5

		21-Dec-07		10:07:10		71.6		38.5		21-Dec-07		10:06:20		69.8		38		21-Dec-07		10:07:53		71.6		39.5		31-Jan-08		10:25:59		74.01		34

		21-Dec-07		12:07:10		72.21		37		21-Dec-07		12:06:20		69.8		38.5		21-Dec-07		12:07:53		71		40		31-Jan-08		12:25:59		71		36

		21-Dec-07		14:07:10		72.21		35.5		21-Dec-07		14:06:20		70.41		35		21-Dec-07		14:07:53		71		40.5		31-Jan-08		14:25:59		72.21		35.5

		21-Dec-07		16:07:10		72.21		33		21-Dec-07		16:06:20		70.41		32.5		21-Dec-07		16:07:53		71		35.5		31-Jan-08		16:25:59		72.21		35

		21-Dec-07		18:07:10		71.6		31.5		21-Dec-07		18:06:20		69.2		30.5		21-Dec-07		18:07:53		70.41		34		31-Jan-08		18:25:59		72.21		35.5

		21-Dec-07		20:07:10		69.8		32		21-Dec-07		20:06:20		67.4		34		21-Dec-07		20:07:53		69.2		33.5		31-Jan-08		20:25:59		72.21		35.5

		21-Dec-07		22:07:10		69.2		32		21-Dec-07		22:06:20		66.81		34		21-Dec-07		22:07:53		67.4		34.5		31-Jan-08		22:25:59		69.2		38

		22-Dec-07		0:07:10		68.61		31.5		22-Dec-07		0:06:20		66.2		33.5		22-Dec-07		0:07:53		65.6		35		1-Feb-08		0:25:59		67.4		38.5

		22-Dec-07		2:07:10		68		31		22-Dec-07		2:06:20		66.2		33		22-Dec-07		2:07:53		64.4		35		1-Feb-08		2:25:59		66.2		39

		22-Dec-07		4:07:10		67.4		30		22-Dec-07		4:06:20		66.2		31.5		22-Dec-07		4:07:53		63.21		35		1-Feb-08		4:25:59		65.6		40

		22-Dec-07		6:07:10		67.4		29.5		22-Dec-07		6:06:20		66.2		30.5		22-Dec-07		6:07:53		66.2		31.5		1-Feb-08		6:25:59		66.81		40

		22-Dec-07		8:07:10		69.2		28		22-Dec-07		8:06:20		69.2		29		22-Dec-07		8:07:53		68.61		31.5		1-Feb-08		8:25:59		70.41		39

		22-Dec-07		10:07:10		71		28		22-Dec-07		10:06:20		70.41		30		22-Dec-07		10:07:53		70.41		31		1-Feb-08		10:25:59		73.4		40

		22-Dec-07		12:07:10		71		28.5		22-Dec-07		12:06:20		70.41		29.5		22-Dec-07		12:07:53		71.6		28.5		1-Feb-08		12:25:59		72.21		41

		22-Dec-07		14:07:10		71		26.5		22-Dec-07		14:06:20		69.2		26		22-Dec-07		14:07:53		69.8		30		1-Feb-08		14:25:59		72.8		42.5

		22-Dec-07		16:07:10		71		26.5		22-Dec-07		16:06:20		69.2		26		22-Dec-07		16:07:53		69.2		29.5		1-Feb-08		16:25:59		72.8		44

		22-Dec-07		18:07:10		70.41		26.5		22-Dec-07		18:06:20		69.2		26		22-Dec-07		18:07:53		69.2		29.5		1-Feb-08		18:25:59		72.21		45.5

		22-Dec-07		20:07:10		69.8		28		22-Dec-07		20:06:20		66.81		31		22-Dec-07		20:07:53		68		31.5		1-Feb-08		20:25:59		72.8		41

		22-Dec-07		22:07:10		68.61		28.5		22-Dec-07		22:06:20		66.2		31		22-Dec-07		22:07:53		66.2		31.5		1-Feb-08		22:25:59		69.8		42

		23-Dec-07		0:07:10		68		28		23-Dec-07		0:06:20		65.6		31		23-Dec-07		0:07:53		64.4		31.5		2-Feb-08		0:25:59		67.4		41.5

		23-Dec-07		2:07:10		66.81		27.5		23-Dec-07		2:06:20		65.6		30		23-Dec-07		2:07:53		63.21		32		2-Feb-08		2:25:59		65.6		40.5

		23-Dec-07		4:07:10		66.81		27		23-Dec-07		4:06:20		65.6		29.5		23-Dec-07		4:07:53		62		31.5		2-Feb-08		4:25:59		64.4		39.5

		23-Dec-07		6:07:10		66.2		26.5		23-Dec-07		6:06:20		65.6		28		23-Dec-07		6:07:53		61.41		31.5		2-Feb-08		6:25:59		65.6		37

		23-Dec-07		8:07:10		66.81		26.5		23-Dec-07		8:06:20		66.81		28		23-Dec-07		8:07:53		67.4		28		2-Feb-08		8:25:59		68		34.5

		23-Dec-07		10:07:10		67.4		28		23-Dec-07		10:06:20		67.4		29.5		23-Dec-07		10:07:53		68		28		2-Feb-08		10:25:59		71		38.5

		23-Dec-07		12:07:10		67.4		30		23-Dec-07		12:06:20		67.4		31.5		23-Dec-07		12:07:53		68		30.5		2-Feb-08		12:25:59		71.6		37

		23-Dec-07		14:07:10		68		29.5		23-Dec-07		14:06:20		67.4		30.5		23-Dec-07		14:07:53		68		31		2-Feb-08		14:25:59		71.6		39

		23-Dec-07		16:07:10		68		29.5		23-Dec-07		16:06:20		68		30.5		23-Dec-07		16:07:53		68		31.5		2-Feb-08		16:25:59		71.6		39

		23-Dec-07		18:07:10		68.61		29.5		23-Dec-07		18:06:20		67.4		30		23-Dec-07		18:07:53		68		31.5		2-Feb-08		18:25:59		71.6		39

		23-Dec-07		20:07:10		68		31.5		23-Dec-07		20:06:20		66.2		34		23-Dec-07		20:07:53		68.61		31.5		2-Feb-08		20:25:59		71.6		38.5

		23-Dec-07		22:07:10		67.4		32		23-Dec-07		22:06:20		66.2		34.5		23-Dec-07		22:07:53		68.61		32		2-Feb-08		22:25:59		68.61		39.5

		24-Dec-07		0:07:10		66.81		32		24-Dec-07		0:06:20		65.6		34.5		24-Dec-07		0:07:53		68.61		31.5		3-Feb-08		0:25:59		66.81		40.5

		24-Dec-07		2:07:10		66.81		31.5		24-Dec-07		2:06:20		66.2		33.5		24-Dec-07		2:07:53		68.61		31.5		3-Feb-08		2:25:59		66.2		41

		24-Dec-07		4:07:10		66.81		31.5		24-Dec-07		4:06:20		65.6		34		24-Dec-07		4:07:53		68.61		31.5		3-Feb-08		4:25:59		65.6		42

		24-Dec-07		6:07:10		66.81		31.5		24-Dec-07		6:06:20		65.6		33		24-Dec-07		6:07:53		68		31		3-Feb-08		6:25:59		65.01		42.5

		24-Dec-07		8:07:10		67.4		31		24-Dec-07		8:06:20		67.4		32		24-Dec-07		8:07:53		69.2		30.5		3-Feb-08		8:25:59		65.01		43

		24-Dec-07		10:07:10		67.4		32		24-Dec-07		10:06:20		67.4		33.5		24-Dec-07		10:07:53		69.2		31		3-Feb-08		10:25:59		66.2		43

		24-Dec-07		12:07:10		68		32.5		24-Dec-07		12:06:20		67.4		33.5		24-Dec-07		12:07:53		68.61		32		3-Feb-08		12:25:59		66.81		45

		24-Dec-07		14:07:10		68.61		36		24-Dec-07		14:06:20		68		38.5		24-Dec-07		14:07:53		69.2		35.5		3-Feb-08		14:25:59		67.4		46

		24-Dec-07		16:07:10		69.2		40		24-Dec-07		16:06:20		68.61		44		24-Dec-07		16:07:53		69.8		39.5		3-Feb-08		16:25:59		67.4		48.5

		24-Dec-07		18:07:10		69.8		43		24-Dec-07		18:06:20		68.61		48		24-Dec-07		18:07:53		69.8		43		3-Feb-08		18:25:59		66.81		50.5

		24-Dec-07		20:07:10		68.61		43		24-Dec-07		20:06:20		66.81		47.5		24-Dec-07		20:07:53		69.2		42.5		3-Feb-08		20:25:59		66.81		50

		24-Dec-07		22:07:10		68		41.5		24-Dec-07		22:06:20		66.2		46		24-Dec-07		22:07:53		69.8		40.5		3-Feb-08		22:25:59		66.2		51.5

		25-Dec-07		0:07:10		68		41.5		25-Dec-07		0:06:20		66.2		45		25-Dec-07		0:07:53		69.8		40		4-Feb-08		0:25:59		66.2		52.5

		25-Dec-07		2:07:10		67.4		40.5		25-Dec-07		2:06:20		66.2		44.5		25-Dec-07		2:07:53		69.8		39		4-Feb-08		2:25:59		66.2		51.5

		25-Dec-07		4:07:10		67.4		40.5		25-Dec-07		4:06:20		66.2		43.5		25-Dec-07		4:07:53		69.8		38		4-Feb-08		4:25:59		65.6		49.5

		25-Dec-07		6:07:10		67.4		39.5		25-Dec-07		6:06:20		66.2		42		25-Dec-07		6:07:53		69.8		37		4-Feb-08		6:25:59		65.6		48.5

		25-Dec-07		8:07:10		69.2		37.5		25-Dec-07		8:06:20		67.4		40		25-Dec-07		8:07:53		69.2		38		4-Feb-08		8:25:59		65.6		47

		25-Dec-07		10:07:10		69.8		33.5		25-Dec-07		10:06:20		68		34.5		25-Dec-07		10:07:53		68.61		35		4-Feb-08		10:25:59		66.2		46

		25-Dec-07		12:07:10		71		31.5		25-Dec-07		12:06:20		69.2		31		25-Dec-07		12:07:53		69.2		33.5		4-Feb-08		12:25:59		66.81		46.5

		25-Dec-07		14:07:10		70.41		30		25-Dec-07		14:06:20		69.2		28		25-Dec-07		14:07:53		69.8		31.5		4-Feb-08		14:25:59		67.4		46

		25-Dec-07		16:07:10		70.41		27.5		25-Dec-07		16:06:20		68.61		26		25-Dec-07		16:07:53		70.41		30.5		4-Feb-08		16:25:59		67.4		45.5

		25-Dec-07		18:07:10		70.41		29.5		25-Dec-07		18:06:20		68.61		29		25-Dec-07		18:07:53		70.41		30.5		4-Feb-08		18:25:59		67.4		45

		25-Dec-07		20:07:10		69.2		32		25-Dec-07		20:06:20		66.81		34.5		25-Dec-07		20:07:53		69.2		33		4-Feb-08		20:25:59		66.2		45

		25-Dec-07		22:07:10		68		30		25-Dec-07		22:06:20		66.2		31.5		25-Dec-07		22:07:53		67.4		32		4-Feb-08		22:25:59		65.6		45

		26-Dec-07		0:07:10		67.4		29.5		26-Dec-07		0:06:20		65.6		31		26-Dec-07		0:07:53		65.6		31.5		5-Feb-08		0:25:59		65.6		44.5

		26-Dec-07		2:07:10		66.81		28.5		26-Dec-07		2:06:20		65.6		30		26-Dec-07		2:07:53		64.4		31.5		5-Feb-08		2:25:59		65.01		44.5

		26-Dec-07		4:07:10		66.2		28		26-Dec-07		4:06:20		65.6		29.5		26-Dec-07		4:07:53		62.6		31		5-Feb-08		4:25:59		65.01		44

		26-Dec-07		6:07:10		66.2		27.5		26-Dec-07		6:06:20		65.6		29		26-Dec-07		6:07:53		66.81		28.5		5-Feb-08		6:25:59		66.2		42.5

		26-Dec-07		8:07:10		66.81		26.5		26-Dec-07		8:06:20		66.81		27		26-Dec-07		8:07:53		68		27.5		5-Feb-08		8:25:59		69.8		39.5

		26-Dec-07		10:07:10		67.4		26.5		26-Dec-07		10:06:20		67.4		27.5		26-Dec-07		10:07:53		68.61		27.5		5-Feb-08		10:25:59		72.8		37.5

		26-Dec-07		12:07:10		67.4		27.5		26-Dec-07		12:06:20		67.4		28		26-Dec-07		12:07:53		68.61		28.5		5-Feb-08		12:25:59		71.6		37.5

		26-Dec-07		14:07:10		68		28		26-Dec-07		14:06:20		68		28		26-Dec-07		14:07:53		68.61		29.5		5-Feb-08		14:25:59		71.6		36

		26-Dec-07		16:07:10		68.61		29.5		26-Dec-07		16:06:20		68		30.5		26-Dec-07		16:07:53		68.61		31		5-Feb-08		16:25:59		72.8		34.5

		26-Dec-07		18:07:10		68.61		32.5		26-Dec-07		18:06:20		68		35		26-Dec-07		18:07:53		68.61		34		5-Feb-08		18:25:59		72.8		34.5

		26-Dec-07		20:07:10		68		33.5		26-Dec-07		20:06:20		66.81		36		26-Dec-07		20:07:53		69.2		34		5-Feb-08		20:25:59		72.21		34

		26-Dec-07		22:07:10		67.4		34		26-Dec-07		22:06:20		66.2		36.5		26-Dec-07		22:07:53		67.4		34.5		5-Feb-08		22:25:59		69.2		36

		27-Dec-07		0:07:10		66.81		34.5		27-Dec-07		0:06:20		66.2		38		27-Dec-07		0:07:53		66.2		36		6-Feb-08		0:25:59		67.4		37

		27-Dec-07		2:07:10		66.81		34		27-Dec-07		2:06:20		66.2		36		27-Dec-07		2:07:53		65.01		36		6-Feb-08		2:25:59		66.2		38

		27-Dec-07		4:07:10		66.2		32.5		27-Dec-07		4:06:20		65.6		34		27-Dec-07		4:07:53		63.8		35		6-Feb-08		4:25:59		65.6		38

		27-Dec-07		6:07:10		66.2		31.5		27-Dec-07		6:06:20		65.6		32.5		27-Dec-07		6:07:53		68		31.5		6-Feb-08		6:25:59		66.81		39.5

		27-Dec-07		8:07:10		68		30		27-Dec-07		8:06:20		67.4		31		27-Dec-07		8:07:53		70.41		30.5		6-Feb-08		8:25:59		70.41		36.5

		27-Dec-07		10:07:10		69.2		30.5		27-Dec-07		10:06:20		69.8		31.5		27-Dec-07		10:07:53		71		30.5		6-Feb-08		10:25:59		72.8		35.5

		27-Dec-07		12:07:10		71		28.5		27-Dec-07		12:06:20		70.41		28.5		27-Dec-07		12:07:53		71		29		6-Feb-08		12:25:59		71		37

		27-Dec-07		14:07:10		70.41		25.5		27-Dec-07		14:06:20		70.41		24.5		27-Dec-07		14:07:53		71		25.5		6-Feb-08		14:25:59		72.21		37

		27-Dec-07		16:07:10		71		22.5		27-Dec-07		16:06:20		71		22		27-Dec-07		16:07:53		69.8		24		6-Feb-08		16:25:59		72.8		34.5

		27-Dec-07		18:07:10		70.41		23		27-Dec-07		18:06:20		68.61		23.5		27-Dec-07		18:07:53		69.2		24.5		6-Feb-08		18:25:59		72.8		35

		27-Dec-07		20:07:10		69.8		24		27-Dec-07		20:06:20		66.81		26		27-Dec-07		20:07:53		68		26		6-Feb-08		20:25:59		72.8		37

		27-Dec-07		22:07:10		68		24		27-Dec-07		22:06:20		66.2		26		27-Dec-07		22:07:53		66.2		27		6-Feb-08		22:25:59		69.8		38

		28-Dec-07		0:07:10		67.4		24.5		28-Dec-07		0:06:20		65.6		26		28-Dec-07		0:07:53		65.01		27.5		7-Feb-08		0:25:59		68		38.5

		28-Dec-07		2:07:10		66.81		24		28-Dec-07		2:06:20		65.6		26		28-Dec-07		2:07:53		63.21		28		7-Feb-08		2:25:59		66.81		38.5

		28-Dec-07		4:07:10		66.2		24		28-Dec-07		4:06:20		65.6		25.5		28-Dec-07		4:07:53		62.6		28		7-Feb-08		4:25:59		66.2		38.5

		28-Dec-07		6:07:10		66.2		24.5		28-Dec-07		6:06:20		65.6		25.5		28-Dec-07		6:07:53		66.2		26		7-Feb-08		6:25:59		67.4		38.5

		28-Dec-07		8:07:10		68		23.5		28-Dec-07		8:06:20		67.4		24.5		28-Dec-07		8:07:53		68		25.5		7-Feb-08		8:25:59		71.6		38

		28-Dec-07		10:07:10		69.2		24		28-Dec-07		10:06:20		69.2		25.5		28-Dec-07		10:07:53		69.8		25		7-Feb-08		10:25:59		72.21		37.5

		28-Dec-07		12:07:10		70.41		25		28-Dec-07		12:06:20		70.41		26		28-Dec-07		12:07:53		71		26		7-Feb-08		12:25:59		71.6		40.5

		28-Dec-07		14:07:10		70.41		25.5		28-Dec-07		14:06:20		70.41		26		28-Dec-07		14:07:53		71		27		7-Feb-08		14:25:59		71.6		40

		28-Dec-07		16:07:10		71		26.5		28-Dec-07		16:06:20		70.41		27.5		28-Dec-07		16:07:53		71		25		7-Feb-08		16:25:59		72.8		38

		28-Dec-07		18:07:10		71		28.5		28-Dec-07		18:06:20		68.61		31.5		28-Dec-07		18:07:53		71		29.5		7-Feb-08		18:25:59		72.8		37.5

		28-Dec-07		20:07:10		71		31.5		28-Dec-07		20:06:20		66.81		37		28-Dec-07		20:07:53		69.8		32.5		7-Feb-08		20:25:59		72.21		36

		28-Dec-07		22:07:10		69.8		33		28-Dec-07		22:06:20		66.2		38.5		28-Dec-07		22:07:53		68		34.5		7-Feb-08		22:25:59		69.2		37.5

		29-Dec-07		0:07:10		68.61		34		29-Dec-07		0:06:20		66.2		39		29-Dec-07		0:07:53		66.81		36		8-Feb-08		0:25:59		67.4		38.5

		29-Dec-07		2:07:10		68		34		29-Dec-07		2:06:20		66.2		37.5		29-Dec-07		2:07:53		66.2		36.5		8-Feb-08		2:25:59		66.81		39

		29-Dec-07		4:07:10		67.4		34		29-Dec-07		4:06:20		66.2		38		29-Dec-07		4:07:53		65.01		37		8-Feb-08		4:25:59		65.6		39.5

		29-Dec-07		6:07:10		68		33.5		29-Dec-07		6:06:20		65.6		36.5		29-Dec-07		6:07:53		66.81		35.5		8-Feb-08		6:25:59		67.4		39.5

		29-Dec-07		8:07:10		69.8		32		29-Dec-07		8:06:20		68		34.5		29-Dec-07		8:07:53		68.61		35.5		8-Feb-08		8:25:59		71		37.5

		29-Dec-07		10:07:10		70.41		32		29-Dec-07		10:06:20		69.8		33		29-Dec-07		10:07:53		70.41		33.5		8-Feb-08		10:25:59		71.6		38

		29-Dec-07		12:07:10		72.21		33		29-Dec-07		12:06:20		70.41		35		29-Dec-07		12:07:53		71.6		34		8-Feb-08		12:25:59		71		39

		29-Dec-07		14:07:10		72.8		32.5		29-Dec-07		14:06:20		71		34		29-Dec-07		14:07:53		71.6		34		8-Feb-08		14:25:59		72.21		40

		29-Dec-07		16:07:10		72.8		32		29-Dec-07		16:06:20		71		35		29-Dec-07		16:07:53		70.41		34.5		8-Feb-08		16:25:59		73.4		41

		29-Dec-07		18:07:10		72.21		32		29-Dec-07		18:06:20		69.2		35		29-Dec-07		18:07:53		69.2		35.5		8-Feb-08		18:25:59		74.01		40

		29-Dec-07		20:07:10		71		33		29-Dec-07		20:06:20		67.4		37.5		29-Dec-07		20:07:53		68		36.5		8-Feb-08		20:25:59		72.21		40.5

		29-Dec-07		22:07:10		69.2		34		29-Dec-07		22:06:20		66.81		38.5		29-Dec-07		22:07:53		66.2		37.5		8-Feb-08		22:25:59		70.41		41.5

		30-Dec-07		0:07:10		68		34.5		30-Dec-07		0:06:20		66.2		38.5		30-Dec-07		0:07:53		65.01		38.5		9-Feb-08		0:25:59		69.2		41.5

		30-Dec-07		2:07:10		67.4		35.5		30-Dec-07		2:06:20		65.6		39		30-Dec-07		2:07:53		63.8		40		9-Feb-08		2:25:59		68		41

		30-Dec-07		4:07:10		67.4		36		30-Dec-07		4:06:20		66.2		39.5		30-Dec-07		4:07:53		63.8		41		9-Feb-08		4:25:59		66.2		40.5

		30-Dec-07		6:07:10		66.81		37		30-Dec-07		6:06:20		65.6		40.5		30-Dec-07		6:07:53		63.21		42		9-Feb-08		6:25:59		67.4		39.5

		30-Dec-07		8:07:10		67.4		37		30-Dec-07		8:06:20		67.4		39		30-Dec-07		8:07:53		69.2		37		9-Feb-08		8:25:59		71		36.5

		30-Dec-07		10:07:10		68		37.5		30-Dec-07		10:06:20		67.4		40		30-Dec-07		10:07:53		67.4		39.5		9-Feb-08		10:25:59		71		37.5

		30-Dec-07		12:07:10		68		39		30-Dec-07		12:06:20		67.4		41.5		30-Dec-07		12:07:53		67.4		39.5		9-Feb-08		12:25:59		70.41		39

		30-Dec-07		14:07:10		68		40		30-Dec-07		14:06:20		67.4		42.5		30-Dec-07		14:07:53		67.4		40.5		9-Feb-08		14:25:59		71.6		37.5

		30-Dec-07		16:07:10		68		41		30-Dec-07		16:06:20		67.4		43.5		30-Dec-07		16:07:53		66.81		42.5		9-Feb-08		16:25:59		72.8		34

		30-Dec-07		18:07:10		68		41.5		30-Dec-07		18:06:20		67.4		44		30-Dec-07		18:07:53		66.81		43.5		9-Feb-08		18:25:59		73.4		33.5

		30-Dec-07		20:07:10		67.4		42.5		30-Dec-07		20:06:20		66.2		46		30-Dec-07		20:07:53		67.4		43		9-Feb-08		20:25:59		71.6		37.5

		30-Dec-07		22:07:10		66.81		43		30-Dec-07		22:06:20		66.2		46.5		30-Dec-07		22:07:53		65.01		45.5		9-Feb-08		22:25:59		69.8		38.5

		31-Dec-07		0:07:10		66.81		43.5		31-Dec-07		0:06:20		66.2		46.5		31-Dec-07		0:07:53		64.4		47		10-Feb-08		0:25:59		68		39

		31-Dec-07		2:07:10		66.81		44		31-Dec-07		2:06:20		66.2		47		31-Dec-07		2:07:53		63.8		48		10-Feb-08		2:25:59		66.2		39

		31-Dec-07		4:07:10		66.81		44		31-Dec-07		4:06:20		66.2		47		31-Dec-07		4:07:53		63.21		49		10-Feb-08		4:25:59		65.6		39.5

		31-Dec-07		6:07:10		66.81		42.5		31-Dec-07		6:06:20		65.6		44		31-Dec-07		6:07:53		63.21		48		10-Feb-08		6:25:59		64.4		40

		31-Dec-07		8:07:10		66.81		39.5		31-Dec-07		8:06:20		67.4		40		31-Dec-07		8:07:53		66.2		42		10-Feb-08		8:25:59		64.4		39.5

		31-Dec-07		10:07:10		67.4		38		31-Dec-07		10:06:20		67.4		38.5		31-Dec-07		10:07:53		68		38.5		10-Feb-08		10:25:59		65.01		40.5

		31-Dec-07		12:07:10		67.4		36.5		31-Dec-07		12:06:20		67.4		37		31-Dec-07		12:07:53		66.81		38		10-Feb-08		12:25:59		66.81		43

		31-Dec-07		14:07:10		68		34.5		31-Dec-07		14:06:20		68		34		31-Dec-07		14:07:53		67.4		36.5		10-Feb-08		14:25:59		68.61		44

		31-Dec-07		16:07:10		68		32		31-Dec-07		16:06:20		67.4		31.5		31-Dec-07		16:07:53		67.4		35		10-Feb-08		16:25:59		69.8		42

		31-Dec-07		18:07:10		68		30.5		31-Dec-07		18:06:20		68		30		31-Dec-07		18:07:53		67.4		33.5		10-Feb-08		18:25:59		71		42.5

		31-Dec-07		20:07:10		67.4		31		31-Dec-07		20:06:20		66.2		31.5		31-Dec-07		20:07:53		65.6		33.5		10-Feb-08		20:25:59		69.8		42.5

		31-Dec-07		22:07:10		66.81		31.5		31-Dec-07		22:06:20		65.6		33		31-Dec-07		22:07:53		63.8		35		10-Feb-08		22:25:59		68		43

		1-Jan-08		0:07:10		66.2		30.5		1-Jan-08		0:06:20		65.6		31.5		1-Jan-08		0:07:53		63.21		34.5		11-Feb-08		0:25:59		66.81		43

		1-Jan-08		2:07:10		66.2		29.5		1-Jan-08		2:06:20		65.6		30		1-Jan-08		2:07:53		62		33.5		11-Feb-08		2:25:59		65.6		43

		1-Jan-08		4:07:10		66.2		29		1-Jan-08		4:06:20		65.6		29.5		1-Jan-08		4:07:53		61.41		33.5		11-Feb-08		4:25:59		65.01		43

		1-Jan-08		6:07:10		66.2		28.5		1-Jan-08		6:06:20		65.6		29.5		1-Jan-08		6:07:53		67.4		29		11-Feb-08		6:25:59		64.4		42.5

		1-Jan-08		8:07:10		67.4		27		1-Jan-08		8:06:20		68.61		27.5		1-Jan-08		8:07:53		69.2		28.5		11-Feb-08		8:25:59		64.4		41.5

		1-Jan-08		10:07:10		68.61		27.5		1-Jan-08		10:06:20		69.2		28.5		1-Jan-08		10:07:53		69.8		29		11-Feb-08		10:25:59		65.6		41.5

		1-Jan-08		12:07:10		69.8		29		1-Jan-08		12:06:20		69.2		28.5		1-Jan-08		12:07:53		71.6		29		11-Feb-08		12:25:59		68		45

		1-Jan-08		14:07:10		71		29.5		1-Jan-08		14:06:20		70.41		30.5		1-Jan-08		14:07:53		71		31.5		11-Feb-08		14:25:59		69.2		45

		1-Jan-08		16:07:10		71.6		28.5		1-Jan-08		16:06:20		69.2		29		1-Jan-08		16:07:53		69.8		30.5		11-Feb-08		16:25:59		70.41		44.5

		1-Jan-08		18:07:10		71.6		29		1-Jan-08		18:06:20		69.2		30		1-Jan-08		18:07:53		69.8		31.5		11-Feb-08		18:25:59		71		45

		1-Jan-08		20:07:10		70.41		28.5		1-Jan-08		20:06:20		67.4		31		1-Jan-08		20:07:53		68.61		31.5		11-Feb-08		20:25:59		69.8		45

		1-Jan-08		22:07:10		68.61		28.5		1-Jan-08		22:06:20		66.81		31		1-Jan-08		22:07:53		66.2		31.5		11-Feb-08		22:25:59		68		45.5

		2-Jan-08		0:07:10		67.4		28.5		2-Jan-08		0:06:20		66.2		30.5		2-Jan-08		0:07:53		63.8		32		12-Feb-08		0:25:59		66.81		45.5

		2-Jan-08		2:07:10		66.81		29		2-Jan-08		2:06:20		65.6		31		2-Jan-08		2:07:53		62		33		12-Feb-08		2:25:59		65.6		45

		2-Jan-08		4:07:10		66.2		27.5		2-Jan-08		4:06:20		65.6		29.5		2-Jan-08		4:07:53		60.8		33		12-Feb-08		4:25:59		65.01		45

		2-Jan-08		6:07:10		66.81		27		2-Jan-08		6:06:20		65.6		29		2-Jan-08		6:07:53		66.81		28.5		12-Feb-08		6:25:59		66.2		44

		2-Jan-08		8:07:10		67.4		26		2-Jan-08		8:06:20		66.81		27.5		2-Jan-08		8:07:53		67.4		27.5		12-Feb-08		8:25:59		69.2		40.5

		2-Jan-08		10:07:10		68		26.5		2-Jan-08		10:06:20		67.4		28		2-Jan-08		10:07:53		67.4		28		12-Feb-08		10:25:59		72.8		40

		2-Jan-08		12:07:10		69.2		29.5		2-Jan-08		12:06:20		68		31.5		2-Jan-08		12:07:53		67.4		31		12-Feb-08		12:25:59		71.6		43

		2-Jan-08		14:07:10		70.41		31.5		2-Jan-08		14:06:20		68.61		33.5		2-Jan-08		14:07:53		68		33.5		12-Feb-08		14:25:59		72.8		43.5

		2-Jan-08		16:07:10		71.6		32		2-Jan-08		16:06:20		69.2		34		2-Jan-08		16:07:53		69.2		34.5		12-Feb-08		16:25:59		74.01		43.5

		2-Jan-08		18:07:10		72.21		31		2-Jan-08		18:06:20		69.2		33		2-Jan-08		18:07:53		68.61		34.5		12-Feb-08		18:25:59		74.01		44.5

		2-Jan-08		20:07:10		71.6		31		2-Jan-08		20:06:20		68		34		2-Jan-08		20:07:53		68		34.5		12-Feb-08		20:25:59		71.6		43.5

		2-Jan-08		22:07:10		69.2		31		2-Jan-08		22:06:20		66.81		35.5		2-Jan-08		22:07:53		66.81		34.5		12-Feb-08		22:25:59		70.41		44.5

		3-Jan-08		0:07:10		68		32		3-Jan-08		0:06:20		66.2		35.5		3-Jan-08		0:07:53		64.4		36		13-Feb-08		0:25:59		68.61		44.5

		3-Jan-08		2:07:10		66.81		31.5		3-Jan-08		2:06:20		66.2		34		3-Jan-08		2:07:53		63.21		36.5		13-Feb-08		2:25:59		67.4		44

		3-Jan-08		4:07:10		66.2		31.5		3-Jan-08		4:06:20		66.2		34		3-Jan-08		4:07:53		62		36.5		13-Feb-08		4:25:59		66.2		44

		3-Jan-08		6:07:10		66.81		31.5		3-Jan-08		6:06:20		65.6		34		3-Jan-08		6:07:53		66.81		33.5		13-Feb-08		6:25:59		66.81		43.5

		3-Jan-08		8:07:10		68.61		29.5		3-Jan-08		8:06:20		67.4		31.5		3-Jan-08		8:07:53		68		32.5		13-Feb-08		8:25:59		72.21		39.5

		3-Jan-08		10:07:10		69.2		30.5		3-Jan-08		10:06:20		69.8		32.5		3-Jan-08		10:07:53		69.8		32		13-Feb-08		10:25:59		71.6		40.5

		3-Jan-08		12:07:10		71.6		32		3-Jan-08		12:06:20		71		32.5		3-Jan-08		12:07:53		72.21		32.5		13-Feb-08		12:25:59		72.21		43

		3-Jan-08		14:07:10		72.8		31		3-Jan-08		14:06:20		71		30.5		3-Jan-08		14:07:53		71		35		13-Feb-08		14:25:59		74.01		43.5

		3-Jan-08		16:07:10		72.21		32.5		3-Jan-08		16:06:20		71		34.5		3-Jan-08		16:07:53		70.41		33.5		13-Feb-08		16:25:59		74.6		44.5

		3-Jan-08		18:07:10		72.21		32.5		3-Jan-08		18:06:20		69.2		35		3-Jan-08		18:07:53		70.41		35.5		13-Feb-08		18:25:59		74.01		44

		3-Jan-08		20:07:10		71.6		34		3-Jan-08		20:06:20		68		39		3-Jan-08		20:07:53		69.8		36.5		13-Feb-08		20:25:59		72.21		43.5

		3-Jan-08		22:07:10		70.41		33.5		3-Jan-08		22:06:20		66.81		37.5		3-Jan-08		22:07:53		68		36.5		13-Feb-08		22:25:59		71		43.5

		4-Jan-08		0:07:10		69.2		33		4-Jan-08		0:06:20		66.2		37		4-Jan-08		0:07:53		66.2		36.5		14-Feb-08		0:25:59		68.61		43.5

		4-Jan-08		2:07:10		68.61		34.5		4-Jan-08		2:06:20		66.2		39		4-Jan-08		2:07:53		65.01		38.5		14-Feb-08		2:25:59		67.4		43.5

		4-Jan-08		4:07:10		68		35		4-Jan-08		4:06:20		66.2		39.5		4-Jan-08		4:07:53		65.01		39.5		14-Feb-08		4:25:59		66.2		43.5

		4-Jan-08		6:07:10		68.61		36.5		4-Jan-08		6:06:20		66.2		41		4-Jan-08		6:07:53		66.81		40		14-Feb-08		6:25:59		66.81		44

		4-Jan-08		8:07:10		71		37.5		4-Jan-08		8:06:20		68.61		42		4-Jan-08		8:07:53		70.41		39.5		14-Feb-08		8:25:59		70.41		41

		4-Jan-08		10:07:10		72.21		39		4-Jan-08		10:06:20		70.41		40		4-Jan-08		10:07:53		71.6		40.5		14-Feb-08		10:25:59		71.6		37

		4-Jan-08		12:07:10		73.4		40		4-Jan-08		12:06:20		71		46.5		4-Jan-08		12:07:53		71		45.5		14-Feb-08		12:25:59		71.6		36.5

		4-Jan-08		14:07:10		72.8		42.5		4-Jan-08		14:06:20		71		47.5		4-Jan-08		14:07:53		71		45.5		14-Feb-08		14:25:59		72.8		36

		4-Jan-08		16:07:10		73.4		43.5		4-Jan-08		16:06:20		70.41		49		4-Jan-08		16:07:53		71.6		41.5		14-Feb-08		16:25:59		73.4		32

		4-Jan-08		18:07:10		72.8		42.5		4-Jan-08		18:06:20		69.8		47.5		4-Jan-08		18:07:53		71		42		14-Feb-08		18:25:59		73.4		29

		4-Jan-08		20:07:10		71.6		42.5		4-Jan-08		20:06:20		69.2		48		4-Jan-08		20:07:53		69.8		45.5		14-Feb-08		20:25:59		71.6		28

		4-Jan-08		22:07:10		71		43		4-Jan-08		22:06:20		68		49.5		4-Jan-08		22:07:53		69.2		46.5		14-Feb-08		22:25:59		70.41		31.5

		5-Jan-08		0:07:10		69.8		43.5		5-Jan-08		0:06:20		67.4		50.5		5-Jan-08		0:07:53		69.2		46.5		15-Feb-08		0:25:59		68.61		32.5

		5-Jan-08		2:07:10		69.2		44		5-Jan-08		2:06:20		67.4		51		5-Jan-08		2:07:53		68.61		47		15-Feb-08		2:25:59		67.4		33

		5-Jan-08		4:07:10		69.2		45		5-Jan-08		4:06:20		67.4		52.5		5-Jan-08		4:07:53		68.61		48		15-Feb-08		4:25:59		66.2		33.5

		5-Jan-08		6:07:10		68.61		46		5-Jan-08		6:06:20		67.4		53.5		5-Jan-08		6:07:53		68		49		15-Feb-08		6:25:59		66.81		33.5

		5-Jan-08		8:07:10		69.8		47		5-Jan-08		8:06:20		69.2		53.5		5-Jan-08		8:07:53		70.41		53		15-Feb-08		8:25:59		70.41		32

		5-Jan-08		10:07:10		71		49.5		5-Jan-08		10:06:20		70.41		56.5		5-Jan-08		10:07:53		71		49		15-Feb-08		10:25:59		71.6		30.5

		5-Jan-08		12:07:10		71		49.5		5-Jan-08		12:06:20		71		51		5-Jan-08		12:07:53		71		54.5		15-Feb-08		12:25:59		72.21		30

		5-Jan-08		14:07:10		70.41		46		5-Jan-08		14:06:20		70.41		47		5-Jan-08		14:07:53		72.21		45.5		15-Feb-08		14:25:59		72.8		30.5

		5-Jan-08		16:07:10		69.8		45.5		5-Jan-08		16:06:20		71		46		5-Jan-08		16:07:53		71		46		15-Feb-08		16:25:59		73.4		29.5

		5-Jan-08		18:07:10		73.4		41.5		5-Jan-08		18:06:20		74.01		42		5-Jan-08		18:07:53		74.01		42.5		15-Feb-08		18:25:59		74.01		30

		5-Jan-08		20:07:10		69.2		42.5		5-Jan-08		20:06:20		68		44.5		5-Jan-08		20:07:53		69.2		43.5		15-Feb-08		20:25:59		71		30

		5-Jan-08		22:07:10		68		41.5		5-Jan-08		22:06:20		66.81		43.5		5-Jan-08		22:07:53		68		44		15-Feb-08		22:25:59		69.2		31.5

		6-Jan-08		0:07:10		67.4		41		6-Jan-08		0:06:20		66.81		42.5		6-Jan-08		0:07:53		67.4		43.5		16-Feb-08		0:25:59		68		33

		6-Jan-08		2:07:10		66.81		39.5		6-Jan-08		2:06:20		66.81		39.5		6-Jan-08		2:07:53		66.2		42.5		16-Feb-08		2:25:59		66.2		34

		6-Jan-08		4:07:10		66.2		41		6-Jan-08		4:06:20		66.2		42		6-Jan-08		4:07:53		65.6		43		16-Feb-08		4:25:59		65.6		35

		6-Jan-08		6:07:10		65.6		41		6-Jan-08		6:06:20		66.2		41		6-Jan-08		6:07:53		65.01		43.5		16-Feb-08		6:25:59		66.2		36

		6-Jan-08		8:07:10		65.6		42		6-Jan-08		8:06:20		68		40		6-Jan-08		8:07:53		66.81		41		16-Feb-08		8:25:59		69.2		34

		6-Jan-08		10:07:10		65.6		43.5		6-Jan-08		10:06:20		68		42.5		6-Jan-08		10:07:53		66.81		42.5		16-Feb-08		10:25:59		71.6		34.5

		6-Jan-08		12:07:10		65.6		44.5		6-Jan-08		12:06:20		68		42.5		6-Jan-08		12:07:53		67.4		43		16-Feb-08		12:25:59		72.21		34

		6-Jan-08		14:07:10		65.6		45.5		6-Jan-08		14:06:20		68		44		6-Jan-08		14:07:53		67.4		45		16-Feb-08		14:25:59		72.8		34

		6-Jan-08		16:07:10		66.2		45		6-Jan-08		16:06:20		68		43.5		6-Jan-08		16:07:53		68		44.5		16-Feb-08		16:25:59		74.6		37

		6-Jan-08		18:07:10		66.2		45		6-Jan-08		18:06:20		68		44		6-Jan-08		18:07:53		67.4		45		16-Feb-08		18:25:59		74.01		37

		6-Jan-08		20:07:10		66.2		45		6-Jan-08		20:06:20		66.81		44.5		6-Jan-08		20:07:53		67.4		44		16-Feb-08		20:25:59		71.6		37.5

		6-Jan-08		22:07:10		65.6		43		6-Jan-08		22:06:20		66.81		42.5		6-Jan-08		22:07:53		66.2		43.5		16-Feb-08		22:25:59		69.2		38

		7-Jan-08		0:07:10		65.01		42.5		7-Jan-08		0:06:20		66.2		41.5		7-Jan-08		0:07:53		65.6		43		17-Feb-08		0:25:59		68		39

		7-Jan-08		2:07:10		65.01		42.5		7-Jan-08		2:06:20		66.2		41		7-Jan-08		2:07:53		65.6		43		17-Feb-08		2:25:59		67.4		39.5

		7-Jan-08		4:07:10		64.4		41.5		7-Jan-08		4:06:20		66.2		40		7-Jan-08		4:07:53		65.01		42		17-Feb-08		4:25:59		66.81		40.5

		7-Jan-08		6:07:10		64.4		40		7-Jan-08		6:06:20		66.2		38		7-Jan-08		6:07:53		64.4		41		17-Feb-08		6:25:59		66.81		41

		7-Jan-08		8:07:10		64.4		40.5		7-Jan-08		8:06:20		67.4		37		7-Jan-08		8:07:53		66.81		38.5		17-Feb-08		8:25:59		66.2		41

		7-Jan-08		10:07:10		64.4		39		7-Jan-08		10:06:20		67.4		35.5		7-Jan-08		10:07:53		67.4		36.5		17-Feb-08		10:25:59		66.2		41

		7-Jan-08		12:07:10		64.4		41		7-Jan-08		12:06:20		68		38.5		7-Jan-08		12:07:53		67.4		38.5		17-Feb-08		12:25:59		66.81		42

		7-Jan-08		14:07:10		65.01		43		7-Jan-08		14:06:20		68		41		7-Jan-08		14:07:53		67.4		41		17-Feb-08		14:25:59		67.4		43

		7-Jan-08		16:07:10		65.6		42.5		7-Jan-08		16:06:20		68		39.5		7-Jan-08		16:07:53		68		40.5		17-Feb-08		16:25:59		68.61		42

		7-Jan-08		18:07:10		65.6		41.5		7-Jan-08		18:06:20		68		39.5		7-Jan-08		18:07:53		68		40		17-Feb-08		18:25:59		69.2		41

		7-Jan-08		20:07:10		65.6		42		7-Jan-08		20:06:20		66.81		41.5		7-Jan-08		20:07:53		66.81		41		17-Feb-08		20:25:59		68		41.5

		7-Jan-08		22:07:10		65.01		43.5		7-Jan-08		22:06:20		66.81		42.5		7-Jan-08		22:07:53		65.6		43		17-Feb-08		22:25:59		67.4		42

		8-Jan-08		0:07:10		65.01		44.5		8-Jan-08		0:06:20		66.81		43		8-Jan-08		0:07:53		65.6		44		18-Feb-08		0:25:59		66.2		42

		8-Jan-08		2:07:10		64.4		44		8-Jan-08		2:06:20		66.81		42.5		8-Jan-08		2:07:53		65.01		44		18-Feb-08		2:25:59		65.6		42.5

		8-Jan-08		4:07:10		64.4		44.5		8-Jan-08		4:06:20		66.2		42.5		8-Jan-08		4:07:53		65.01		44		18-Feb-08		4:25:59		65.01		43.5

		8-Jan-08		6:07:10		64.4		44		8-Jan-08		6:06:20		66.2		41.5		8-Jan-08		6:07:53		66.81		41.5		18-Feb-08		6:25:59		65.01		44

		8-Jan-08		8:07:10		65.6		41		8-Jan-08		8:06:20		68		37.5		8-Jan-08		8:07:53		69.2		38.5		18-Feb-08		8:25:59		65.6		43

		8-Jan-08		10:07:10		66.2		39.5		8-Jan-08		10:06:20		69.8		35.5		8-Jan-08		10:07:53		71		36.5		18-Feb-08		10:25:59		66.2		42.5

		8-Jan-08		12:07:10		67.4		42		8-Jan-08		12:06:20		71.6		40.5		8-Jan-08		12:07:53		72.21		39		18-Feb-08		12:25:59		67.4		42

		8-Jan-08		14:07:10		68		38.5		8-Jan-08		14:06:20		71.6		35.5		8-Jan-08		14:07:53		70.41		40.5		18-Feb-08		14:25:59		68		42.5

		8-Jan-08		16:07:10		68.61		35.5		8-Jan-08		16:06:20		71		33.5		8-Jan-08		16:07:53		71		35.5		18-Feb-08		16:25:59		68		43.5

		8-Jan-08		18:07:10		68.61		34		8-Jan-08		18:06:20		69.2		34		8-Jan-08		18:07:53		70.41		36		18-Feb-08		18:25:59		68		43.5

		8-Jan-08		20:07:10		68		34.5		8-Jan-08		20:06:20		67.4		36		8-Jan-08		20:07:53		69.2		36		18-Feb-08		20:25:59		67.4		43.5

		8-Jan-08		22:07:10		67.4		35.5		8-Jan-08		22:06:20		66.81		36.5		8-Jan-08		22:07:53		67.4		38		18-Feb-08		22:25:59		66.2		43.5

		9-Jan-08		0:07:10		66.81		36.5		9-Jan-08		0:06:20		66.81		37		9-Jan-08		0:07:53		65.6		38.5		19-Feb-08		0:25:59		65.6		44.5

		9-Jan-08		2:07:10		65.6		37.5		9-Jan-08		2:06:20		66.81		37.5		9-Jan-08		2:07:53		64.4		39.5		19-Feb-08		2:25:59		65.6		45

		9-Jan-08		4:07:10		65.01		38		9-Jan-08		4:06:20		66.2		38		9-Jan-08		4:07:53		63.21		41		19-Feb-08		4:25:59		65.01		45.5

		9-Jan-08		6:07:10		65.01		39		9-Jan-08		6:06:20		66.2		38.5		9-Jan-08		6:07:53		67.4		38		19-Feb-08		6:25:59		66.2		45

		9-Jan-08		8:07:10		65.6		39		9-Jan-08		8:06:20		68		37.5		9-Jan-08		8:07:53		68.61		39		19-Feb-08		8:25:59		69.8		42.5

		9-Jan-08		10:07:10		66.81		41		9-Jan-08		10:06:20		71		37.5		9-Jan-08		10:07:53		70.41		39.5		19-Feb-08		10:25:59		72.21		40.5

		9-Jan-08		12:07:10		67.4		42.5		9-Jan-08		12:06:20		71		42		9-Jan-08		12:07:53		71		41.5		19-Feb-08		12:25:59		71.6		40.5

		9-Jan-08		14:07:10		68.61		44.5		9-Jan-08		14:06:20		72.8		43.5		9-Jan-08		14:07:53		71.6		42.5		19-Feb-08		14:25:59		71.6		40.5

		9-Jan-08		16:07:10		69.2		46		9-Jan-08		16:06:20		74.01		42.5		9-Jan-08		16:07:53		71		44		19-Feb-08		16:25:59		72.21		40.5

		9-Jan-08		18:07:10		69.8		46		9-Jan-08		18:06:20		71		46		9-Jan-08		18:07:53		71.6		38.5		19-Feb-08		18:25:59		71.6		41

		9-Jan-08		20:07:10		70.41		45		9-Jan-08		20:06:20		69.8		45		9-Jan-08		20:07:53		70.41		44.5		19-Feb-08		20:25:59		71.6		41

		9-Jan-08		22:07:10		69.2		42.5		9-Jan-08		22:06:20		68		44.5		9-Jan-08		22:07:53		68.61		43.5		19-Feb-08		22:25:59		69.2		41.5

		10-Jan-08		0:07:10		68		44		10-Jan-08		0:06:20		66.81		46.5		10-Jan-08		0:07:53		67.4		45		20-Feb-08		0:25:59		67.4		42

		10-Jan-08		2:07:10		67.4		45		10-Jan-08		2:06:20		66.81		47		10-Jan-08		2:07:53		66.2		46.5		20-Feb-08		2:25:59		66.81		42.5

		10-Jan-08		4:07:10		66.81		45.5		10-Jan-08		4:06:20		66.81		46		10-Jan-08		4:07:53		65.6		47		20-Feb-08		4:25:59		66.2		43.5

		10-Jan-08		6:07:10		66.2		46		10-Jan-08		6:06:20		67.4		45.5		10-Jan-08		6:07:53		66.81		45.5		20-Feb-08		6:25:59		66.81		43.5

		10-Jan-08		8:07:10		66.81		45		10-Jan-08		8:06:20		69.8		41.5		10-Jan-08		8:07:53		70.41		43		20-Feb-08		8:25:59		71.6		42

		10-Jan-08		10:07:10		68		44.5		10-Jan-08		10:06:20		70.41		41		10-Jan-08		10:07:53		72.21		41.5		20-Feb-08		10:25:59		72.8		41

		10-Jan-08		12:07:10		68.61		43.5		10-Jan-08		12:06:20		70.41		39		10-Jan-08		12:07:53		71.6		42		20-Feb-08		12:25:59		72.8		41.5

		10-Jan-08		14:07:10		69.2		43.5		10-Jan-08		14:06:20		70.41		45		10-Jan-08		14:07:53		71.6		44		20-Feb-08		14:25:59		72.21		43.5

		10-Jan-08		16:07:10		69.2		43		10-Jan-08		16:06:20		70.41		39.5		10-Jan-08		16:07:53		71		43		20-Feb-08		16:25:59		72.21		45.5

		10-Jan-08		18:07:10		69.2		43		10-Jan-08		18:06:20		68.61		44		10-Jan-08		18:07:53		70.41		43.5		20-Feb-08		18:25:59		71.6		45.5

		10-Jan-08		20:07:10		69.2		42.5		10-Jan-08		20:06:20		68		44.5		10-Jan-08		20:07:53		69.2		42.5		20-Feb-08		20:25:59		71.6		45.5

		10-Jan-08		22:07:10		68.61		43		10-Jan-08		22:06:20		67.4		45		10-Jan-08		22:07:53		68		44		20-Feb-08		22:25:59		70.41		45.5

		11-Jan-08		0:07:10		68		43.5		11-Jan-08		0:06:20		67.4		44.5		11-Jan-08		0:07:53		67.4		44.5		21-Feb-08		0:25:59		68.61		46

		11-Jan-08		2:07:10		67.4		44		11-Jan-08		2:06:20		67.4		45.5		11-Jan-08		2:07:53		66.81		45.5		21-Feb-08		2:25:59		68		46

		11-Jan-08		4:07:10		67.4		44		11-Jan-08		4:06:20		67.4		45		11-Jan-08		4:07:53		65.6		46.5		21-Feb-08		4:25:59		66.81		46.5

		11-Jan-08		6:07:10		66.81		44.5		11-Jan-08		6:06:20		67.4		45		11-Jan-08		6:07:53		68		45		21-Feb-08		6:25:59		66.81		47

		11-Jan-08		8:07:10		67.4		45		11-Jan-08		8:06:20		67.4		45		11-Jan-08		8:07:53		69.8		44		21-Feb-08		8:25:59		71		44.5

		11-Jan-08		10:07:10		68		46		11-Jan-08		10:06:20		72.21		42.5		11-Jan-08		10:07:53		71.6		43		21-Feb-08		10:25:59		72.21		44

		11-Jan-08		12:07:10		69.2		46.5		11-Jan-08		12:06:20		72.8		44		11-Jan-08		12:07:53		71.6		47		21-Feb-08		12:25:59		72.8		43.5

		11-Jan-08		14:07:10		70.41		47.5		11-Jan-08		14:06:20		72.8		46		11-Jan-08		14:07:53		71		41.5		21-Feb-08		14:25:59		73.4		42

		11-Jan-08		16:07:10		70.41		47		11-Jan-08		16:06:20		73.4		40		11-Jan-08		16:07:53		71		48.5		21-Feb-08		16:25:59		74.01		40.5

		11-Jan-08		18:07:10		70.41		47		11-Jan-08		18:06:20		71		46.5		11-Jan-08		18:07:53		70.41		44.5		21-Feb-08		18:25:59		73.4		41

		11-Jan-08		20:07:10		69.8		46		11-Jan-08		20:06:20		69.2		48		11-Jan-08		20:07:53		70.41		44.5		21-Feb-08		20:25:59		72.21		40.5

		11-Jan-08		22:07:10		68.61		47		11-Jan-08		22:06:20		68		49.5		11-Jan-08		22:07:53		69.2		47		21-Feb-08		22:25:59		71		41

		12-Jan-08		0:07:10		68		48		12-Jan-08		0:06:20		68		49.5		12-Jan-08		0:07:53		68		48		22-Feb-08		0:25:59		69.8		41

		12-Jan-08		2:07:10		67.4		49		12-Jan-08		2:06:20		68		50		12-Jan-08		2:07:53		67.4		49		22-Feb-08		2:25:59		68.61		42

		12-Jan-08		4:07:10		66.81		48.5		12-Jan-08		4:06:20		67.4		48.5		12-Jan-08		4:07:53		66.81		49		22-Feb-08		4:25:59		67.4		43

		12-Jan-08		6:07:10		66.81		47.5		12-Jan-08		6:06:20		67.4		46.5		12-Jan-08		6:07:53		67.4		47.5		22-Feb-08		6:25:59		67.4		43.5

		12-Jan-08		8:07:10		66.81		46		12-Jan-08		8:06:20		69.2		43		12-Jan-08		8:07:53		69.8		45		22-Feb-08		8:25:59		71.6		42

		12-Jan-08		10:07:10		68		45.5		12-Jan-08		10:06:20		72.8		38		12-Jan-08		10:07:53		71.6		43		22-Feb-08		10:25:59		72.8		41

		12-Jan-08		12:07:10		68		45.5		12-Jan-08		12:06:20		71		45		12-Jan-08		12:07:53		71		41		22-Feb-08		12:25:59		72.8		42.5

		12-Jan-08		14:07:10		68		44.5		12-Jan-08		14:06:20		70.41		42		12-Jan-08		14:07:53		69.8		44		22-Feb-08		14:25:59		72.21		42

		12-Jan-08		16:07:10		68		45		12-Jan-08		16:06:20		68.61		44		12-Jan-08		16:07:53		70.41		43.5		22-Feb-08		16:25:59		72.21		43.5

		12-Jan-08		18:07:10		67.4		45		12-Jan-08		18:06:20		68.61		44.5		12-Jan-08		18:07:53		69.8		43.5		22-Feb-08		18:25:59		72.21		44

		12-Jan-08		20:07:10		67.4		45.5		12-Jan-08		20:06:20		68		45.5		12-Jan-08		20:07:53		69.2		44		22-Feb-08		20:25:59		72.21		43.5

		12-Jan-08		22:07:10		66.81		45.5		12-Jan-08		22:06:20		66.81		46.5		12-Jan-08		22:07:53		69.2		44.5		22-Feb-08		22:25:59		70.41		44.5

		13-Jan-08		0:07:10		65.6		47		13-Jan-08		0:06:20		66.2		48		13-Jan-08		0:07:53		69.2		43.5		23-Feb-08		0:25:59		68.61		45

		13-Jan-08		2:07:10		65.01		47.5		13-Jan-08		2:06:20		66.2		47.5		13-Jan-08		2:07:53		69.2		43		23-Feb-08		2:25:59		68		45.5

		13-Jan-08		4:07:10		65.01		48		13-Jan-08		4:06:20		66.2		47		13-Jan-08		4:07:53		69.8		42.5		23-Feb-08		4:25:59		67.4		45.5

		13-Jan-08		6:07:10		64.4		49		13-Jan-08		6:06:20		66.2		48		13-Jan-08		6:07:53		69.8		43		23-Feb-08		6:25:59		67.4		45

		13-Jan-08		8:07:10		64.4		49		13-Jan-08		8:06:20		67.4		45.5		13-Jan-08		8:07:53		69.8		42.5		23-Feb-08		8:25:59		72.8		42.5

		13-Jan-08		10:07:10		64.4		49.5		13-Jan-08		10:06:20		68		45.5		13-Jan-08		10:07:53		69.8		42.5		23-Feb-08		10:25:59		72.8		42.5

		13-Jan-08		12:07:10		65.01		50		13-Jan-08		12:06:20		68		47		13-Jan-08		12:07:53		69.8		45		23-Feb-08		12:25:59		71.6		42.5

		13-Jan-08		14:07:10		65.6		49.5		13-Jan-08		14:06:20		68.61		46		13-Jan-08		14:07:53		69.8		44		23-Feb-08		14:25:59		71.6		43

		13-Jan-08		16:07:10		66.2		49.5		13-Jan-08		16:06:20		69.2		46		13-Jan-08		16:07:53		69.8		45.5		23-Feb-08		16:25:59		72.8		41

		13-Jan-08		18:07:10		66.81		49.5		13-Jan-08		18:06:20		69.2		45		13-Jan-08		18:07:53		69.8		46.5		23-Feb-08		18:25:59		72.8		38.5

		13-Jan-08		20:07:10		66.81		48.5		13-Jan-08		20:06:20		68		47.5		13-Jan-08		20:07:53		69.2		45.5		23-Feb-08		20:25:59		71.6		38

		13-Jan-08		22:07:10		66.2		47		13-Jan-08		22:06:20		66.2		46		13-Jan-08		22:07:53		69.2		43		23-Feb-08		22:25:59		69.2		38.5

		14-Jan-08		0:07:10		65.01		46.5		14-Jan-08		0:06:20		65.6		45.5		14-Jan-08		0:07:53		69.2		41		24-Feb-08		0:25:59		66.81		39.5

		14-Jan-08		2:07:10		64.4		48		14-Jan-08		2:06:20		65.6		47		14-Jan-08		2:07:53		69.8		41.5		24-Feb-08		2:25:59		65.6		40

		14-Jan-08		4:07:10		64.4		49.5		14-Jan-08		4:06:20		65.6		48		14-Jan-08		4:07:53		69.8		42		24-Feb-08		4:25:59		64.4		40

		14-Jan-08		6:07:10		64.4		50.5		14-Jan-08		6:06:20		66.2		49		14-Jan-08		6:07:53		69.8		42.5		24-Feb-08		6:25:59		64.4		40.5

		14-Jan-08		8:07:10		64.4		51.5		14-Jan-08		8:06:20		68		47		14-Jan-08		8:07:53		69.8		43		24-Feb-08		8:25:59		65.01		40.5

		14-Jan-08		10:07:10		64.4		50		14-Jan-08		10:06:20		68		45.5		14-Jan-08		10:07:53		69.8		42		24-Feb-08		10:25:59		65.01		41.5

		14-Jan-08		12:07:10		65.01		49		14-Jan-08		12:06:20		68		44.5		14-Jan-08		12:07:53		70.41		39.5		24-Feb-08		12:25:59		65.6		42.5

		14-Jan-08		14:07:10		65.01		49		14-Jan-08		14:06:20		68		45		14-Jan-08		14:07:53		69.8		38.5		24-Feb-08		14:25:59		66.2		43.5

		14-Jan-08		16:07:10		65.6		49.5		14-Jan-08		16:06:20		68.61		46.5		14-Jan-08		16:07:53		69.8		42.5		24-Feb-08		16:25:59		65.6		43.5

		14-Jan-08		18:07:10		66.2		49.5		14-Jan-08		18:06:20		68.61		47		14-Jan-08		18:07:53		69.8		45		24-Feb-08		18:25:59		65.01		44

		14-Jan-08		20:07:10		66.2		48.5		14-Jan-08		20:06:20		67.4		47		14-Jan-08		20:07:53		69.8		44		24-Feb-08		20:25:59		64.4		45

		14-Jan-08		22:07:10		65.6		47		14-Jan-08		22:06:20		66.2		46		14-Jan-08		22:07:53		69.8		41.5		24-Feb-08		22:25:59		64.4		46

		15-Jan-08		0:07:10		64.4		44		15-Jan-08		0:06:20		65.6		42		15-Jan-08		0:07:53		69.2		39		25-Feb-08		0:25:59		64.4		47.5

		15-Jan-08		2:07:10		63.8		45		15-Jan-08		2:06:20		65.6		43		15-Jan-08		2:07:53		69.8		38.5		25-Feb-08		2:25:59		64.4		48

		15-Jan-08		4:07:10		63.8		45		15-Jan-08		4:06:20		65.6		42.5		15-Jan-08		4:07:53		69.8		38		25-Feb-08		4:25:59		64.4		49

		15-Jan-08		6:07:10		63.21		46		15-Jan-08		6:06:20		65.6		44		15-Jan-08		6:07:53		69.8		38.5		25-Feb-08		6:25:59		64.4		49.5

		15-Jan-08		8:07:10		63.8		47		15-Jan-08		8:06:20		67.4		42.5		15-Jan-08		8:07:53		71		39.5		25-Feb-08		8:25:59		65.01		49.5

		15-Jan-08		10:07:10		65.01		47.5		15-Jan-08		10:06:20		70.41		41.5		15-Jan-08		10:07:53		71		37		25-Feb-08		10:25:59		66.2		49.5

		15-Jan-08		12:07:10		65.6		47.5		15-Jan-08		12:06:20		70.41		43		15-Jan-08		12:07:53		71		43.5		25-Feb-08		12:25:59		66.81		49.5

		15-Jan-08		14:07:10		66.2		48		15-Jan-08		14:06:20		70.41		46.5		15-Jan-08		14:07:53		71		43.5		25-Feb-08		14:25:59		67.4		50

		15-Jan-08		16:07:10		66.81		49.5		15-Jan-08		16:06:20		71		44		15-Jan-08		16:07:53		70.41		45		25-Feb-08		16:25:59		67.4		50

		15-Jan-08		18:07:10		66.81		48		15-Jan-08		18:06:20		69.2		44		15-Jan-08		18:07:53		70.41		43.5		25-Feb-08		18:25:59		67.4		49.5

		15-Jan-08		20:07:10		66.81		45.5		15-Jan-08		20:06:20		67.4		44		15-Jan-08		20:07:53		69.8		41.5		25-Feb-08		20:25:59		66.81		49

		15-Jan-08		22:07:10		65.6		43.5		15-Jan-08		22:06:20		65.6		42.5		15-Jan-08		22:07:53		68.61		41		25-Feb-08		22:25:59		66.2		49

		16-Jan-08		0:07:10		65.01		43		16-Jan-08		0:06:20		65.6		41		16-Jan-08		0:07:53		66.81		40		26-Feb-08		0:25:59		65.6		49.5

		16-Jan-08		2:07:10		64.4		42.5		16-Jan-08		2:06:20		65.01		41.5		16-Jan-08		2:07:53		65.6		41		26-Feb-08		2:25:59		65.01		50

		16-Jan-08		4:07:10		63.8		42.5		16-Jan-08		4:06:20		65.6		40		16-Jan-08		4:07:53		64.4		41		26-Feb-08		4:25:59		64.4		49.5

		16-Jan-08		6:07:10		63.21		42		16-Jan-08		6:06:20		65.01		40		16-Jan-08		6:07:53		67.4		38		26-Feb-08		6:25:59		66.2		48

		16-Jan-08		8:07:10		63.8		41		16-Jan-08		8:06:20		67.4		37		16-Jan-08		8:07:53		69.2		36.5		26-Feb-08		8:25:59		69.8		45

		16-Jan-08		10:07:10		65.01		41		16-Jan-08		10:06:20		70.41		36		16-Jan-08		10:07:53		71		36		26-Feb-08		10:25:59		72.21		44

		16-Jan-08		12:07:10		65.6		42.5		16-Jan-08		12:06:20		71		35		16-Jan-08		12:07:53		71.6		36		26-Feb-08		12:25:59		72.21		43.5

		16-Jan-08		14:07:10		66.81		44.5		16-Jan-08		14:06:20		71		39		16-Jan-08		14:07:53		70.41		43.5		26-Feb-08		14:25:59		72.8		43

		16-Jan-08		16:07:10		68		46		16-Jan-08		16:06:20		71.6		40.5		16-Jan-08		16:07:53		69.8		44.5		26-Feb-08		16:25:59		73.4		42

		16-Jan-08		18:07:10		68		44.5		16-Jan-08		18:06:20		69.8		42		16-Jan-08		18:07:53		69.8		43.5		26-Feb-08		18:25:59		73.4		42.5

		16-Jan-08		20:07:10		68		44		16-Jan-08		20:06:20		68.61		43.5		16-Jan-08		20:07:53		69.2		43		26-Feb-08		20:25:59		72.21		42.5

		16-Jan-08		22:07:10		67.4		42		16-Jan-08		22:06:20		66.81		43		16-Jan-08		22:07:53		68.61		40.5		26-Feb-08		22:25:59		70.41		43.5

		17-Jan-08		0:07:10		66.2		40.5		17-Jan-08		0:06:20		65.6		41		17-Jan-08		0:07:53		66.81		39.5		27-Feb-08		0:25:59		68		43.5

		17-Jan-08		2:07:10		65.01		40.5		17-Jan-08		2:06:20		65.6		39		17-Jan-08		2:07:53		65.6		39.5		27-Feb-08		2:25:59		66.81		43.5

		17-Jan-08		4:07:10		63.8		40		17-Jan-08		4:06:20		65.6		38.5		17-Jan-08		4:07:53		64.4		39.5		27-Feb-08		4:25:59		65.6		43.5

		17-Jan-08		6:07:10		63.8		39.5		17-Jan-08		6:06:20		65.6		37		17-Jan-08		6:07:53		66.2		37		27-Feb-08		6:25:59		66.81		43.5

		17-Jan-08		8:07:10		64.4		38.5		17-Jan-08		8:06:20		68		34.5		17-Jan-08		8:07:53		69.2		35.5		27-Feb-08		8:25:59		71.6		41

		17-Jan-08		10:07:10		65.01		35		17-Jan-08		10:06:20		70.41		29.5		17-Jan-08		10:07:53		71.6		31		27-Feb-08		10:25:59		72.21		41

		17-Jan-08		12:07:10		66.2		29		17-Jan-08		12:06:20		71		21.5		17-Jan-08		12:07:53		69.8		23.5		27-Feb-08		12:25:59		72.21		42.5

		17-Jan-08		14:07:10		67.4		27		17-Jan-08		14:06:20		71		22.5		17-Jan-08		14:07:53		71		23.5		27-Feb-08		14:25:59		74.01		40

		17-Jan-08		16:07:10		68		25		17-Jan-08		16:06:20		70.41		21.5		17-Jan-08		16:07:53		70.41		24.5		27-Feb-08		16:25:59		74.01		40

		17-Jan-08		18:07:10		68.61		24		17-Jan-08		18:06:20		69.8		19		17-Jan-08		18:07:53		69.8		22.5		27-Feb-08		18:25:59		74.01		41.5

		17-Jan-08		20:07:10		68.61		22		17-Jan-08		20:06:20		69.8		18		17-Jan-08		20:07:53		70.41		23		27-Feb-08		20:25:59		72.8		42.5

		17-Jan-08		22:07:10		68.61		20.5		17-Jan-08		22:06:20		69.2		17.5		17-Jan-08		22:07:53		70.41		24		27-Feb-08		22:25:59		71.6		43

		18-Jan-08		0:07:10		68		20		18-Jan-08		0:06:20		68		18		18-Jan-08		0:07:53		69.2		23		28-Feb-08		0:25:59		69.8		43

		18-Jan-08		2:07:10		67.4		21.5		18-Jan-08		2:06:20		66.2		22		18-Jan-08		2:07:53		68		24		28-Feb-08		2:25:59		68.61		44

		18-Jan-08		4:07:10		66.2		21		18-Jan-08		4:06:20		66.2		20		18-Jan-08		4:07:53		66.81		23.5		28-Feb-08		4:25:59		67.4		44

		18-Jan-08		6:07:10		65.6		24.5		18-Jan-08		6:06:20		65.6		26		18-Jan-08		6:07:53		65.6		26		28-Feb-08		6:25:59		67.4		43.5

		18-Jan-08		8:07:10		65.6		26.5		18-Jan-08		8:06:20		67.4		26		18-Jan-08		8:07:53		69.8		26		28-Feb-08		8:25:59		71		41

		18-Jan-08		10:07:10		66.81		29		18-Jan-08		10:06:20		70.41		27.5		18-Jan-08		10:07:53		71.6		27		28-Feb-08		10:25:59		72.21		41

		18-Jan-08		12:07:10		67.4		28.5		18-Jan-08		12:06:20		71		26.5		18-Jan-08		12:07:53		71		28		28-Feb-08		12:25:59		72.8		42.5

		18-Jan-08		14:07:10		68		29		18-Jan-08		14:06:20		71		28		18-Jan-08		14:07:53		71		29		28-Feb-08		14:25:59		74.01		42.5

		18-Jan-08		16:07:10		68.61		29		18-Jan-08		16:06:20		70.41		29.5		18-Jan-08		16:07:53		71		31.5		28-Feb-08		16:25:59		75.2		43.5

		18-Jan-08		18:07:10		69.2		30		18-Jan-08		18:06:20		69.8		29.5		18-Jan-08		18:07:53		70.41		31.5		28-Feb-08		18:25:59		74.6		43.5

		18-Jan-08		20:07:10		69.2		32		18-Jan-08		20:06:20		68.61		34		18-Jan-08		20:07:53		71		32.5		28-Feb-08		20:25:59		72.21		44

		18-Jan-08		22:07:10		68		32		18-Jan-08		22:06:20		66.81		34.5		18-Jan-08		22:07:53		69.8		32		28-Feb-08		22:25:59		71.6		44.5

		19-Jan-08		0:07:10		66.81		32.5		19-Jan-08		0:06:20		66.2		34		19-Jan-08		0:07:53		68		32.5		29-Feb-08		0:25:59		69.2		44

		19-Jan-08		2:07:10		66.2		32.5		19-Jan-08		2:06:20		65.6		33		19-Jan-08		2:07:53		66.2		32.5		29-Feb-08		2:25:59		68		43.5

		19-Jan-08		4:07:10		65.01		32.5		19-Jan-08		4:06:20		65.6		32.5		19-Jan-08		4:07:53		65.01		32.5		29-Feb-08		4:25:59		66.81		43

		19-Jan-08		6:07:10		64.4		32.5		19-Jan-08		6:06:20		65.6		32		19-Jan-08		6:07:53		67.4		30		29-Feb-08		6:25:59		67.4		42.5

		19-Jan-08		8:07:10		65.01		32		19-Jan-08		8:06:20		68		29.5		19-Jan-08		8:07:53		69.2		31		29-Feb-08		8:25:59		70.41		40

		19-Jan-08		10:07:10		65.6		33		19-Jan-08		10:06:20		68.61		31		19-Jan-08		10:07:53		71.6		30		29-Feb-08		10:25:59		72.21		40.5

		19-Jan-08		12:07:10		65.6		35.5		19-Jan-08		12:06:20		70.41		33.5		19-Jan-08		12:07:53		71		30.5		29-Feb-08		12:25:59		73.4		42

		19-Jan-08		14:07:10		66.2		35.5		19-Jan-08		14:06:20		70.41		33.5		19-Jan-08		14:07:53		71		34.5		29-Feb-08		14:25:59		74.6		41.5

		19-Jan-08		16:07:10		67.4		35		19-Jan-08		16:06:20		71		32		19-Jan-08		16:07:53		71		34.5		29-Feb-08		16:25:59		74.6		41.5

		19-Jan-08		18:07:10		68		35.5		19-Jan-08		18:06:20		69.8		34		19-Jan-08		18:07:53		70.41		35		29-Feb-08		18:25:59		74.01		43.5

		19-Jan-08		20:07:10		68		34		19-Jan-08		20:06:20		68		34.5		19-Jan-08		20:07:53		69.8		34		29-Feb-08		20:25:59		72.21		42.5

		19-Jan-08		22:07:10		67.4		34.5		19-Jan-08		22:06:20		66.2		36.5		19-Jan-08		22:07:53		68.61		35		29-Feb-08		22:25:59		71		43.5

		20-Jan-08		0:07:10		66.2		34		20-Jan-08		0:06:20		65.6		35		20-Jan-08		0:07:53		67.4		34		1-Mar-08		0:25:59		69.8		43

		20-Jan-08		2:07:10		65.6		34		20-Jan-08		2:06:20		65.6		34		20-Jan-08		2:07:53		65.6		34		1-Mar-08		2:25:59		68.61		43.5

		20-Jan-08		4:07:10		64.4		33		20-Jan-08		4:06:20		65.6		33		20-Jan-08		4:07:53		64.4		33.5		1-Mar-08		4:25:59		68		44

		20-Jan-08		6:07:10		63.8		32.5		20-Jan-08		6:06:20		65.6		31		20-Jan-08		6:07:53		63.21		33.5		1-Mar-08		6:25:59		68		44.5

		20-Jan-08		8:07:10		63.8		31.5		20-Jan-08		8:06:20		67.4		28		20-Jan-08		8:07:53		67.4		29		1-Mar-08		8:25:59		71.6		42

		20-Jan-08		10:07:10		63.8		32		20-Jan-08		10:06:20		68		30		20-Jan-08		10:07:53		66.81		29.5		1-Mar-08		10:25:59		72.8		41.5

		20-Jan-08		12:07:10		64.4		36.5		20-Jan-08		12:06:20		68.61		35		20-Jan-08		12:07:53		67.4		33		1-Mar-08		12:25:59		72.21		43

		20-Jan-08		14:07:10		65.01		37		20-Jan-08		14:06:20		68.61		35		20-Jan-08		14:07:53		67.4		35.5		1-Mar-08		14:25:59		72.8		44

		20-Jan-08		16:07:10		66.2		36.5		20-Jan-08		16:06:20		69.8		33.5		20-Jan-08		16:07:53		68.61		35.5		1-Mar-08		16:25:59		74.01		45

		20-Jan-08		18:07:10		66.81		36.5		20-Jan-08		18:06:20		69.2		34.5		20-Jan-08		18:07:53		69.8		35.5		1-Mar-08		18:25:59		73.4		43.5

		20-Jan-08		20:07:10		66.81		34.5		20-Jan-08		20:06:20		68		33.5		20-Jan-08		20:07:53		69.2		34		1-Mar-08		20:25:59		72.21		43

		20-Jan-08		22:07:10		66.2		35		20-Jan-08		22:06:20		66.2		35.5		20-Jan-08		22:07:53		67.4		34.5		1-Mar-08		22:25:59		71		43

		21-Jan-08		0:07:10		65.01		35		21-Jan-08		0:06:20		65.6		35		21-Jan-08		0:07:53		65.6		34.5		2-Mar-08		0:25:59		69.2		43

		21-Jan-08		2:07:10		64.4		38.5		21-Jan-08		2:06:20		65.6		39		21-Jan-08		2:07:53		65.01		37		2-Mar-08		2:25:59		68.61		44

		21-Jan-08		4:07:10		64.4		38.5		21-Jan-08		4:06:20		65.6		38		21-Jan-08		4:07:53		64.4		38		2-Mar-08		4:25:59		67.4		44.5

		21-Jan-08		6:07:10		63.8		37		21-Jan-08		6:06:20		65.6		36		21-Jan-08		6:07:53		63.8		37.5		2-Mar-08		6:25:59		67.4		44.5

		21-Jan-08		8:07:10		63.8		38		21-Jan-08		8:06:20		67.4		35		21-Jan-08		8:07:53		66.81		34.5		2-Mar-08		8:25:59		67.4		44

		21-Jan-08		10:07:10		63.8		38.5		21-Jan-08		10:06:20		68		35		21-Jan-08		10:07:53		66.81		35.5		2-Mar-08		10:25:59		68		43.5

		21-Jan-08		12:07:10		64.4		40		21-Jan-08		12:06:20		68		36.5		21-Jan-08		12:07:53		67.4		36		2-Mar-08		12:25:59		69.2		42

		21-Jan-08		14:07:10		64.4		35		21-Jan-08		14:06:20		68		31		21-Jan-08		14:07:53		67.4		33.5		2-Mar-08		14:25:59		70.41		40.5

		21-Jan-08		16:07:10		65.01		34.5		21-Jan-08		16:06:20		68		32		21-Jan-08		16:07:53		67.4		34		2-Mar-08		16:25:59		69.8		39

		21-Jan-08		18:07:10		65.6		33.5		21-Jan-08		18:06:20		68		31		21-Jan-08		18:07:53		67.4		33.5		2-Mar-08		18:25:59		69.8		38

		21-Jan-08		20:07:10		65.6		34.5		21-Jan-08		20:06:20		66.2		34		21-Jan-08		20:07:53		66.81		34		2-Mar-08		20:25:59		68.61		39

		21-Jan-08		22:07:10		65.01		34.5		21-Jan-08		22:06:20		65.6		34		21-Jan-08		22:07:53		65.01		34.5		2-Mar-08		22:25:59		67.4		39.5

		22-Jan-08		0:07:10		64.4		34.5		22-Jan-08		0:06:20		65.6		33.5		22-Jan-08		0:07:53		63.8		35		3-Mar-08		0:25:59		66.81		40

		22-Jan-08		2:07:10		63.8		34		22-Jan-08		2:06:20		65.01		32		22-Jan-08		2:07:53		62.6		34		3-Mar-08		2:25:59		65.6		40

		22-Jan-08		4:07:10		63.21		32.5		22-Jan-08		4:06:20		65.01		30.5		22-Jan-08		4:07:53		61.41		33.5		3-Mar-08		4:25:59		65.01		39.5

		22-Jan-08		6:07:10		62.6		31.5		22-Jan-08		6:06:20		65.01		30		22-Jan-08		6:07:53		66.81		29.5		3-Mar-08		6:25:59		64.4		39.5

		22-Jan-08		8:07:10		63.21		32		22-Jan-08		8:06:20		67.4		28.5		22-Jan-08		8:07:53		68		30		3-Mar-08		8:25:59		65.01		38.5

		22-Jan-08		10:07:10		64.4		33.5		22-Jan-08		10:06:20		69.2		30		22-Jan-08		10:07:53		70.41		30.5		3-Mar-08		10:25:59		66.2		38

		22-Jan-08		12:07:10		65.01		36		22-Jan-08		12:06:20		70.41		32.5		22-Jan-08		12:07:53		71.6		31		3-Mar-08		12:25:59		66.81		38

		22-Jan-08		14:07:10		66.2		37.5		22-Jan-08		14:06:20		71		35.5		22-Jan-08		14:07:53		71		36		3-Mar-08		14:25:59		67.4		35.5

		22-Jan-08		16:07:10		66.81		39		22-Jan-08		16:06:20		71		34.5		22-Jan-08		16:07:53		70.41		37		3-Mar-08		16:25:59		68.61		33.5

		22-Jan-08		18:07:10		67.4		37		22-Jan-08		18:06:20		68.61		36		22-Jan-08		18:07:53		69.8		36		3-Mar-08		18:25:59		68.61		31.5

		22-Jan-08		20:07:10		67.4		36.5		22-Jan-08		20:06:20		68		36.5		22-Jan-08		20:07:53		69.8		35		3-Mar-08		20:25:59		68.61		31

		22-Jan-08		22:07:10		66.81		37		22-Jan-08		22:06:20		67.4		36.5		22-Jan-08		22:07:53		67.4		36		3-Mar-08		22:25:59		68		33

		23-Jan-08		0:07:10		65.6		37.5		23-Jan-08		0:06:20		67.4		36.5		23-Jan-08		0:07:53		65.6		37.5		4-Mar-08		0:25:59		66.81		35

		23-Jan-08		2:07:10		65.01		37		23-Jan-08		2:06:20		67.4		35.5		23-Jan-08		2:07:53		65.01		38		4-Mar-08		2:25:59		66.2		37

		23-Jan-08		4:07:10		64.4		37.5		23-Jan-08		4:06:20		66.81		35.5		23-Jan-08		4:07:53		63.8		38.5		4-Mar-08		4:25:59		65.6		37.5

		23-Jan-08		6:07:10		64.4		37		23-Jan-08		6:06:20		66.81		35		23-Jan-08		6:07:53		67.4		35.5		4-Mar-08		6:25:59		66.2		37.5

		23-Jan-08		8:07:10		65.01		36		23-Jan-08		8:06:20		68		33		23-Jan-08		8:07:53		69.2		34		4-Mar-08		8:25:59		69.2		35.5

		23-Jan-08		10:07:10		65.6		36.5		23-Jan-08		10:06:20		69.2		34		23-Jan-08		10:07:53		71		35		4-Mar-08		10:25:59		71.6		36.5

		23-Jan-08		12:07:10		66.2		36		23-Jan-08		12:06:20		69.8		33		23-Jan-08		12:07:53		71		34		4-Mar-08		12:25:59		72.21		36.5

		23-Jan-08		14:07:10		66.81		34.5		23-Jan-08		14:06:20		70.41		32		23-Jan-08		14:07:53		70.41		35		4-Mar-08		14:25:59		73.4		33.5

		23-Jan-08		16:07:10		66.81		33.5		23-Jan-08		16:06:20		69.8		31.5		23-Jan-08		16:07:53		70.41		32		4-Mar-08		16:25:59		74.01		33.5

		23-Jan-08		18:07:10		66.81		33		23-Jan-08		18:06:20		69.2		31		23-Jan-08		18:07:53		69.2		32		4-Mar-08		18:25:59		74.01		33

		23-Jan-08		20:07:10		66.81		32.5		23-Jan-08		20:06:20		68		31		23-Jan-08		20:07:53		68		32.5		4-Mar-08		20:25:59		72.21		32

		23-Jan-08		22:07:10		66.2		32.5		23-Jan-08		22:06:20		67.4		32		23-Jan-08		22:07:53		68		32.5		4-Mar-08		22:25:59		71		33.5

		24-Jan-08		0:07:10		65.6		33.5		24-Jan-08		0:06:20		66.81		32.5		24-Jan-08		0:07:53		66.2		33		5-Mar-08		0:25:59		69.2		34.5

		24-Jan-08		2:07:10		65.01		34		24-Jan-08		2:06:20		67.4		32.5		24-Jan-08		2:07:53		64.4		34.5		5-Mar-08		2:25:59		68		35.5

		24-Jan-08		4:07:10		64.4		35.5		24-Jan-08		4:06:20		67.4		34		24-Jan-08		4:07:53		63.8		36		5-Mar-08		4:25:59		66.81		36

		24-Jan-08		6:07:10		64.4		37		24-Jan-08		6:06:20		66.81		35		24-Jan-08		6:07:53		68		34		5-Mar-08		6:25:59		66.81		36.5

		24-Jan-08		8:07:10		65.01		37		24-Jan-08		8:06:20		68		35		24-Jan-08		8:07:53		69.2		35.5		5-Mar-08		8:25:59		69.8		34

		24-Jan-08		10:07:10		65.6		38		24-Jan-08		10:06:20		71		33.5		24-Jan-08		10:07:53		71		35		5-Mar-08		10:25:59		72.21		36

		24-Jan-08		12:07:10		66.81		39		24-Jan-08		12:06:20		71		36		24-Jan-08		12:07:53		71		37		5-Mar-08		12:25:59		72.8		36.5

		24-Jan-08		14:07:10		68		38		24-Jan-08		14:06:20		71		37		24-Jan-08		14:07:53		71		38.5		5-Mar-08		14:25:59		74.01		36.5

		24-Jan-08		16:07:10		68		36		24-Jan-08		16:06:20		71		34		24-Jan-08		16:07:53		71.6		35		5-Mar-08		16:25:59		74.6		35.5

		24-Jan-08		18:07:10		68.61		34.5		24-Jan-08		18:06:20		68.61		33.5		24-Jan-08		18:07:53		71		34		5-Mar-08		18:25:59		74.6		36.5

		24-Jan-08		20:07:10		68		35.5		24-Jan-08		20:06:20		68		36.5		24-Jan-08		20:07:53		69.8		35		5-Mar-08		20:25:59		72.8		37

		24-Jan-08		22:07:10		67.4		36.5		24-Jan-08		22:06:20		67.4		37		24-Jan-08		22:07:53		68		36		5-Mar-08		22:25:59		71		37

		25-Jan-08		0:07:10		66.2		36.5		25-Jan-08		0:06:20		67.4		36		25-Jan-08		0:07:53		66.2		37		6-Mar-08		0:25:59		69.2		37

		25-Jan-08		2:07:10		65.6		37.5		25-Jan-08		2:06:20		66.81		37		25-Jan-08		2:07:53		65.01		38		6-Mar-08		2:25:59		68		37.5

		25-Jan-08		4:07:10		65.01		39		25-Jan-08		4:06:20		67.4		37.5		25-Jan-08		4:07:53		64.4		39.5		6-Mar-08		4:25:59		66.81		38

		25-Jan-08		6:07:10		64.4		39.5		25-Jan-08		6:06:20		67.4		38		25-Jan-08		6:07:53		66.81		38		6-Mar-08		6:25:59		66.81		37.5

		25-Jan-08		8:07:10		65.01		39		25-Jan-08		8:06:20		68		36.5		25-Jan-08		8:07:53		69.2		36		6-Mar-08		8:25:59		70.41		35.5

		25-Jan-08		10:07:10		65.6		40.5		25-Jan-08		10:06:20		69.8		37		25-Jan-08		10:07:53		71.6		36		6-Mar-08		10:25:59		71.6		36.5

		25-Jan-08		12:07:10		66.81		39.5		25-Jan-08		12:06:20		69.8		37.5		25-Jan-08		12:07:53		72.21		36		6-Mar-08		12:25:59		72.8		35.5

		25-Jan-08		14:07:10		67.4		38		25-Jan-08		14:06:20		69.8		37.5		25-Jan-08		14:07:53		71		37.5		6-Mar-08		14:25:59		74.01		32.5

		25-Jan-08		16:07:10		68.61		37.5		25-Jan-08		16:06:20		70.41		37		25-Jan-08		16:07:53		70.41		38		6-Mar-08		16:25:59		74.6		31

		25-Jan-08		18:07:10		68.61		36		25-Jan-08		18:06:20		68		36.5		25-Jan-08		18:07:53		69.8		36		6-Mar-08		18:25:59		68.61		44.5

		25-Jan-08		20:07:10		68.61		35		25-Jan-08		20:06:20		67.4		37		25-Jan-08		20:07:53		68.61		36		6-Mar-08		20:25:59		68.61		44

		25-Jan-08		22:07:10		68		35.5		25-Jan-08		22:06:20		66.81		37		25-Jan-08		22:07:53		67.4		37.5		6-Mar-08		22:25:59		68.61		42.5

		26-Jan-08		0:07:10		67.4		35.5		26-Jan-08		0:06:20		66.81		36		26-Jan-08		0:07:53		66.81		37.5		7-Mar-08		0:25:59		68.61		44

		26-Jan-08		2:07:10		66.81		36		26-Jan-08		2:06:20		66.81		36.5		26-Jan-08		2:07:53		65.6		37.5		7-Mar-08		2:25:59		68		43

		26-Jan-08		4:07:10		66.2		35		26-Jan-08		4:06:20		66.81		35		26-Jan-08		4:07:53		65.6		37.5		7-Mar-08		4:25:59		69.2		44

		26-Jan-08		6:07:10		65.6		37.5		26-Jan-08		6:06:20		66.81		38		26-Jan-08		6:07:53		68.61		36.5		7-Mar-08		6:25:59		68.61		43.5

		26-Jan-08		8:07:10		66.2		39.5		26-Jan-08		8:06:20		67.4		40		26-Jan-08		8:07:53		69.2		38.5		7-Mar-08		8:25:59		68.61		44.5

		26-Jan-08		10:07:10		67.4		42		26-Jan-08		10:06:20		69.8		42		26-Jan-08		10:07:53		71.6		40.5		7-Mar-08		10:25:59		68.61		44.5

		26-Jan-08		12:07:10		68.61		41		26-Jan-08		12:06:20		69.2		42.5		26-Jan-08		12:07:53		71		43		7-Mar-08		12:25:59		68.61		45

		26-Jan-08		14:07:10		69.8		42		26-Jan-08		14:06:20		71		44		26-Jan-08		14:07:53		71		38.5		7-Mar-08		14:25:59		68.61		45

		26-Jan-08		16:07:10		70.41		43.5		26-Jan-08		16:06:20		70.41		46.5		26-Jan-08		16:07:53		70.41		44.5		7-Mar-08		16:25:59		68.61		44

		26-Jan-08		18:07:10		69.8		42.5		26-Jan-08		18:06:20		68.61		45.5		26-Jan-08		18:07:53		69.2		44		7-Mar-08		18:25:59		68.61		44.5

		26-Jan-08		20:07:10		69.2		44.5		26-Jan-08		20:06:20		68		48		26-Jan-08		20:07:53		68.61		45.5		7-Mar-08		20:25:59		68.61		46.5

		26-Jan-08		22:07:10		68.61		46.5		26-Jan-08		22:06:20		68		49.5		26-Jan-08		22:07:53		68		47.5		7-Mar-08		22:25:59		68.61		45.5

		27-Jan-08		0:07:10		68.61		47.5		27-Jan-08		0:06:20		67.4		51		27-Jan-08		0:07:53		67.4		48		8-Mar-08		0:25:59		68.61		44.5

		27-Jan-08		2:07:10		68		48.5		27-Jan-08		2:06:20		67.4		51.5		27-Jan-08		2:07:53		67.4		48.5		8-Mar-08		2:25:59		68		45

		27-Jan-08		4:07:10		68		49		27-Jan-08		4:06:20		67.4		51		27-Jan-08		4:07:53		67.4		49		8-Mar-08		4:25:59		68		44

		27-Jan-08		6:07:10		67.4		48		27-Jan-08		6:06:20		67.4		49		27-Jan-08		6:07:53		66.81		49		8-Mar-08		6:25:59		68		45

		27-Jan-08		8:07:10		67.4		44.5		27-Jan-08		8:06:20		68		43.5		27-Jan-08		8:07:53		68		45.5		8-Mar-08		8:25:59		68.61		45

		27-Jan-08		10:07:10		67.4		40.5		27-Jan-08		10:06:20		67.4		39.5		27-Jan-08		10:07:53		68		43		8-Mar-08		10:25:59		68.61		45

		27-Jan-08		12:07:10		67.4		39.5		27-Jan-08		12:06:20		67.4		39		27-Jan-08		12:07:53		67.4		42		8-Mar-08		12:25:59		68.61		45

		27-Jan-08		14:07:10		67.4		39		27-Jan-08		14:06:20		68		38.5		27-Jan-08		14:07:53		68		42		8-Mar-08		14:25:59		68.61		45

		27-Jan-08		16:07:10		67.4		39.5		27-Jan-08		16:06:20		68		39		27-Jan-08		16:07:53		68		41		8-Mar-08		16:25:59		68.61		45

		27-Jan-08		18:07:10		68		40		27-Jan-08		18:06:20		68.61		40.5		27-Jan-08		18:07:53		68.61		41.5		8-Mar-08		18:25:59		68.61		44.5

		27-Jan-08		20:07:10		68		39.5		27-Jan-08		20:06:20		67.4		40.5		27-Jan-08		20:07:53		68		42		8-Mar-08		20:25:59		68.61		45.5

		27-Jan-08		22:07:10		67.4		41		27-Jan-08		22:06:20		67.4		42		27-Jan-08		22:07:53		67.4		42.5		8-Mar-08		22:25:59		68.61		45

		28-Jan-08		0:07:10		67.4		43.5		28-Jan-08		0:06:20		67.4		46.5		28-Jan-08		0:07:53		67.4		44		9-Mar-08		0:25:59		68		45

		28-Jan-08		2:07:10		66.81		47.5		28-Jan-08		2:06:20		67.4		49		28-Jan-08		2:07:53		66.81		46.5		9-Mar-08		2:25:59		68		45

		28-Jan-08		4:07:10		66.81		46.5		28-Jan-08		4:06:20		67.4		47		28-Jan-08		4:07:53		66.81		46.5		9-Mar-08		4:25:59		68.61		45

		28-Jan-08		6:07:10		66.81		47.5		28-Jan-08		6:06:20		67.4		48.5		28-Jan-08		6:07:53		66.81		47.5		9-Mar-08		6:25:59		68.61		44.5

		28-Jan-08		8:07:10		66.81		48.5		28-Jan-08		8:06:20		68		48.5		28-Jan-08		8:07:53		67.4		47		9-Mar-08		8:25:59		68.61		45.5

		28-Jan-08		10:07:10		66.81		49.5		28-Jan-08		10:06:20		68		49		28-Jan-08		10:07:53		67.4		47.5		9-Mar-08		10:25:59		68.61		45

		28-Jan-08		12:07:10		66.81		48		28-Jan-08		12:06:20		68		47.5		28-Jan-08		12:07:53		68		47.5		9-Mar-08		12:25:59		68.61		45.5

		28-Jan-08		14:07:10		66.81		45.5		28-Jan-08		14:06:20		68		45		28-Jan-08		14:07:53		68		46		9-Mar-08		14:25:59		68.61		45

		28-Jan-08		16:07:10		67.4		47.5		28-Jan-08		16:06:20		68		49		28-Jan-08		16:07:53		68		47.5		9-Mar-08		16:25:59		68.61		45

		28-Jan-08		18:07:10		68		48.5		28-Jan-08		18:06:20		68		49		28-Jan-08		18:07:53		67.4		48.5		9-Mar-08		18:25:59		68.61		45

		28-Jan-08		20:07:10		68		49		28-Jan-08		20:06:20		67.4		50.5		28-Jan-08		20:07:53		67.4		49		9-Mar-08		20:25:59		68.61		46

		28-Jan-08		22:07:10		67.4		40.5		28-Jan-08		22:06:20		66.81		37.5		28-Jan-08		22:07:53		66.2		41.5		9-Mar-08		22:25:59		68.61		45

		29-Jan-08		0:07:10		66.2		36.5		29-Jan-08		0:06:20		66.2		35		29-Jan-08		0:07:53		63.8		38		10-Mar-08		0:25:59		68		45

		29-Jan-08		2:07:10		65.6		36.5		29-Jan-08		2:06:20		66.81		35.5		29-Jan-08		2:07:53		63.21		39		10-Mar-08		2:25:59		68.61		45

		29-Jan-08		4:07:10		65.6		36.5		29-Jan-08		4:06:20		66.81		35		29-Jan-08		4:07:53		62.6		39.5		10-Mar-08		4:25:59		68.61		45.5

		29-Jan-08		6:07:10		65.6		36		29-Jan-08		6:06:20		66.81		35		29-Jan-08		6:07:53		66.81		36.5		10-Mar-08		6:25:59		68.61		45.5

		29-Jan-08		8:07:10		65.6		36		29-Jan-08		8:06:20		67.4		34.5		29-Jan-08		8:07:53		69.2		35		10-Mar-08		8:25:59		68		45.5

		29-Jan-08		10:07:10		66.2		37.5		29-Jan-08		10:06:20		69.8		34.5		29-Jan-08		10:07:53		70.41		36.5		10-Mar-08		10:25:59		68		45.5

		29-Jan-08		12:07:10		67.4		37.5		29-Jan-08		12:06:20		70.41		35.5		29-Jan-08		12:07:53		71		37		10-Mar-08		12:25:59		68.61		45.5

		29-Jan-08		14:07:10		68.61		35		29-Jan-08		14:06:20		71		31		29-Jan-08		14:07:53		70.41		38		10-Mar-08		14:25:59		68.61		45

		29-Jan-08		16:07:10		69.2		34.5		29-Jan-08		16:06:20		69.8		34		29-Jan-08		16:07:53		70.41		35.5		10-Mar-08		16:25:59		68.61		45.5

		29-Jan-08		18:07:10		69.8		33.5		29-Jan-08		18:06:20		69.2		34		29-Jan-08		18:07:53		69.8		35		10-Mar-08		18:25:59		68.61		45

		29-Jan-08		20:07:10		69.2		32.5		29-Jan-08		20:06:20		67.4		33.5		29-Jan-08		20:07:53		68		35		10-Mar-08		20:25:59		68.61		45

		29-Jan-08		22:07:10		68.61		32.5		29-Jan-08		22:06:20		67.4		33.5		29-Jan-08		22:07:53		66.2		35.5		10-Mar-08		22:25:59		68		45

		30-Jan-08		0:07:10		68		31.5		30-Jan-08		0:06:20		66.81		32.5		30-Jan-08		0:07:53		65.01		35.5		11-Mar-08		0:25:59		68.61		45

		30-Jan-08		2:07:10		67.4		30.5		30-Jan-08		2:06:20		66.81		30.5		30-Jan-08		2:07:53		63.21		34.5		11-Mar-08		2:25:59		68.61		45

		30-Jan-08		4:07:10		66.81		30		30-Jan-08		4:06:20		66.81		30		30-Jan-08		4:07:53		62		34		11-Mar-08		4:25:59		68.61		46

		30-Jan-08		6:07:10		66.81		31		30-Jan-08		6:06:20		66.81		31		30-Jan-08		6:07:53		67.4		31.5		11-Mar-08		6:25:59		68.61		45.5

		30-Jan-08		8:07:10		66.81		31.5		30-Jan-08		8:06:20		67.4		31.5		30-Jan-08		8:07:53		69.2		33		11-Mar-08		8:25:59		68.61		44.5

		30-Jan-08		10:07:10		67.4		33.5		30-Jan-08		10:06:20		69.8		32.5		30-Jan-08		10:07:53		70.41		35		11-Mar-08		10:25:59		68		45

		30-Jan-08		12:07:10		68.61		36		30-Jan-08		12:06:20		71		36		30-Jan-08		12:07:53		71		37.5		11-Mar-08		12:25:59		68.61		46

		30-Jan-08		14:07:10		69.8		39		30-Jan-08		14:06:20		71.6		40.5		30-Jan-08		14:07:53		71		42		11-Mar-08		14:25:59		68		49.5

		30-Jan-08		16:07:10		71.6		40.5		30-Jan-08		16:06:20		71.6		43		30-Jan-08		16:07:53		71		42		11-Mar-08		16:25:59		68.61		46

		30-Jan-08		18:07:10		71		36		30-Jan-08		18:06:20		68.61		36.5		30-Jan-08		18:07:53		69.8		38		11-Mar-08		18:25:59		68		45

		30-Jan-08		20:07:10		70.41		33		30-Jan-08		20:06:20		68		34		30-Jan-08		20:07:53		68.61		36.5		11-Mar-08		20:25:59		68.61		45

		30-Jan-08		22:07:10		69.8		31.5		30-Jan-08		22:06:20		68		32.5		30-Jan-08		22:07:53		67.4		36		11-Mar-08		22:25:59		68.61		45.5

		31-Jan-08		0:07:10		69.2		32		31-Jan-08		0:06:20		68		33.5		31-Jan-08		0:07:53		65.6		36.5		12-Mar-08		0:25:59		68.61		45

		31-Jan-08		2:07:10		68.61		33		31-Jan-08		2:06:20		68		34		31-Jan-08		2:07:53		65.01		37		12-Mar-08		2:25:59		68		45

		31-Jan-08		4:07:10		68.61		33.5		31-Jan-08		4:06:20		68		34.5		31-Jan-08		4:07:53		64.4		38		12-Mar-08		4:25:59		68		46

		31-Jan-08		6:07:10		68		33.5		31-Jan-08		6:06:20		68		34.5		31-Jan-08		6:07:53		66.81		36		12-Mar-08		6:25:59		68		45

		31-Jan-08		8:07:10		69.8		32.5		31-Jan-08		8:06:20		68		34		31-Jan-08		8:07:53		68.61		35.5		12-Mar-08		8:25:59		68.61		46

		31-Jan-08		10:07:10		71.6		33		31-Jan-08		10:06:20		71		34.5		31-Jan-08		10:07:53		71.6		36.5		12-Mar-08		10:25:59		68.61		45.5

		31-Jan-08		12:07:10		71.6		33.5		31-Jan-08		12:06:20		71		33.5		31-Jan-08		12:07:53		70.41		38		12-Mar-08		12:25:59		68		46

		31-Jan-08		14:07:10		71.6		33.5		31-Jan-08		14:06:20		71		36		31-Jan-08		14:07:53		71.6		36		12-Mar-08		14:25:59		68		46.5

		31-Jan-08		16:07:10		71.6		33.5		31-Jan-08		16:06:20		71		35.5		31-Jan-08		16:07:53		69.8		37		12-Mar-08		16:25:59		68.61		48.5

		31-Jan-08		18:07:10		71		34		31-Jan-08		18:06:20		68.61		37		31-Jan-08		18:07:53		71		36.5		12-Mar-08		18:25:59		68.61		47.5

		31-Jan-08		20:07:10		69.2		36		31-Jan-08		20:06:20		68.61		38		31-Jan-08		20:07:53		70.41		37.5		12-Mar-08		20:25:59		68.61		45.5

		31-Jan-08		22:07:10		67.4		37.5		31-Jan-08		22:06:20		68		38		31-Jan-08		22:07:53		69.2		38.5		12-Mar-08		22:25:59		68.61		45.5

		1-Feb-08		0:07:10		66.2		39		1-Feb-08		0:06:20		68		38		1-Feb-08		0:07:53		67.4		39		13-Mar-08		0:25:59		68		46

		1-Feb-08		2:07:10		65.01		40.5		1-Feb-08		2:06:20		68		38		1-Feb-08		2:07:53		66.2		40		13-Mar-08		2:25:59		68		45

		1-Feb-08		4:07:10		64.4		42		1-Feb-08		4:06:20		68		39		1-Feb-08		4:07:53		65.6		41		13-Mar-08		4:25:59		68.61		45

		1-Feb-08		6:07:10		63.8		43		1-Feb-08		6:06:20		68		39		1-Feb-08		6:07:53		66.81		40.5		13-Mar-08		6:25:59		68.61		45

		1-Feb-08		8:07:10		66.2		42		1-Feb-08		8:06:20		68		40.5		1-Feb-08		8:07:53		69.8		40		13-Mar-08		8:25:59		68.61		45.5

		1-Feb-08		10:07:10		68.61		42		1-Feb-08		10:06:20		71		41.5		1-Feb-08		10:07:53		71.6		42		13-Mar-08		10:25:59		68		45.5

		1-Feb-08		12:07:10		69.2		43		1-Feb-08		12:06:20		71		43		1-Feb-08		12:07:53		71		46		13-Mar-08		12:25:59		68.61		45

		1-Feb-08		14:07:10		69.8		45		1-Feb-08		14:06:20		71		44		1-Feb-08		14:07:53		71		40		13-Mar-08		14:25:59		68.61		47

		1-Feb-08		16:07:10		70.41		46.5		1-Feb-08		16:06:20		71		45		1-Feb-08		16:07:53		70.41		48		13-Mar-08		16:25:59		68.61		47

		1-Feb-08		18:07:10		69.2		48.5		1-Feb-08		18:06:20		69.2		50		1-Feb-08		18:07:53		70.41		48		13-Mar-08		18:25:59		68		45.5

		1-Feb-08		20:07:10		68		44.5		1-Feb-08		20:06:20		68.61		43.5		1-Feb-08		20:07:53		70.41		43.5		13-Mar-08		20:25:59		68.61		45

		1-Feb-08		22:07:10		66.81		41.5		1-Feb-08		22:06:20		68		39.5		1-Feb-08		22:07:53		69.2		41		13-Mar-08		22:25:59		68.61		45.5

		2-Feb-08		0:07:10		65.6		40		2-Feb-08		0:06:20		68		37.5		2-Feb-08		0:07:53		66.81		40		14-Mar-08		0:25:59		68.61		47.5

		2-Feb-08		2:07:10		64.4		38		2-Feb-08		2:06:20		68		34		2-Feb-08		2:07:53		64.4		39		14-Mar-08		2:25:59		68		46

		2-Feb-08		4:07:10		63.21		37.5		2-Feb-08		4:06:20		68		33		2-Feb-08		4:07:53		62.6		38		14-Mar-08		4:25:59		68		47

		2-Feb-08		6:07:10		62.6		36.5		2-Feb-08		6:06:20		68		32		2-Feb-08		6:07:53		67.4		33.5		14-Mar-08		6:25:59		68		46.5

		2-Feb-08		8:07:10		63.8		35		2-Feb-08		8:06:20		67.4		31.5		2-Feb-08		8:07:53		68		33.5		14-Mar-08		8:25:59		68.61		47.5

		2-Feb-08		10:07:10		66.2		36		2-Feb-08		10:06:20		71		33		2-Feb-08		10:07:53		70.41		35.5		14-Mar-08		10:25:59		68		48

		2-Feb-08		12:07:10		68.61		38		2-Feb-08		12:06:20		72.8		36		2-Feb-08		12:07:53		71		39.5		14-Mar-08		12:25:59		68.61		45.5

		2-Feb-08		14:07:10		69.2		38		2-Feb-08		14:06:20		71.6		36.5		2-Feb-08		14:07:53		69.8		39.5		14-Mar-08		14:25:59		68.61		45

		2-Feb-08		16:07:10		68.61		38		2-Feb-08		16:06:20		71		36.5		2-Feb-08		16:07:53		69.8		39		14-Mar-08		16:25:59		68.61		45

		2-Feb-08		18:07:10		68		37.5		2-Feb-08		18:06:20		71		35.5		2-Feb-08		18:07:53		71		39		14-Mar-08		18:25:59		68.61		45

		2-Feb-08		20:07:10		67.4		37		2-Feb-08		20:06:20		68.61		35.5		2-Feb-08		20:07:53		69.2		40		14-Mar-08		20:25:59		68.61		45

		2-Feb-08		22:07:10		66.81		36.5		2-Feb-08		22:06:20		68		34		2-Feb-08		22:07:53		67.4		44		14-Mar-08		22:25:59		68.61		45

		3-Feb-08		0:07:10		66.81		35.5		3-Feb-08		0:06:20		68		33		3-Feb-08		0:07:53		66.81		41		15-Mar-08		0:25:59		68.61		45.5

		3-Feb-08		2:07:10		66.2		35		3-Feb-08		2:06:20		68		33		3-Feb-08		2:07:53		65.6		42		15-Mar-08		2:25:59		68.61		46

		3-Feb-08		4:07:10		66.2		34.5		3-Feb-08		4:06:20		68		33		3-Feb-08		4:07:53		65.01		43		15-Mar-08		4:25:59		68.61		45.5

		3-Feb-08		6:07:10		66.2		34.5		3-Feb-08		6:06:20		68		33.5		3-Feb-08		6:07:53		64.4		44		15-Mar-08		6:25:59		68.61		46

		3-Feb-08		8:07:10		66.2		35.5		3-Feb-08		8:06:20		69.8		33		3-Feb-08		8:07:53		67.4		41.5		15-Mar-08		8:25:59		68.61		45.5

		3-Feb-08		10:07:10		66.2		36.5		3-Feb-08		10:06:20		66.81		36.5		3-Feb-08		10:07:53		67.4		42		15-Mar-08		10:25:59		68.61		45

		3-Feb-08		12:07:10		66.81		40		3-Feb-08		12:06:20		65.6		44.5		3-Feb-08		12:07:53		68		47.5		15-Mar-08		12:25:59		68.61		45

		3-Feb-08		14:07:10		66.2		43.5		3-Feb-08		14:06:20		66.2		47.5		3-Feb-08		14:07:53		67.4		49		15-Mar-08		14:25:59		68.61		44.5

		3-Feb-08		16:07:10		66.2		46		3-Feb-08		16:06:20		66.2		49		3-Feb-08		16:07:53		68		49		15-Mar-08		16:25:59		68		44.5

		3-Feb-08		18:07:10		66.2		47.5		3-Feb-08		18:06:20		66.2		50		3-Feb-08		18:07:53		68.61		51		15-Mar-08		18:25:59		68		44.5

		3-Feb-08		20:07:10		66.2		49.5		3-Feb-08		20:06:20		66.81		52		3-Feb-08		20:07:53		67.4		51.5		15-Mar-08		20:25:59		68.61		45

		3-Feb-08		22:07:10		66.2		51.5		3-Feb-08		22:06:20		66.81		53.5		3-Feb-08		22:07:53		68		54		15-Mar-08		22:25:59		68		45

		4-Feb-08		0:07:10		66.2		51.5		4-Feb-08		0:06:20		67.4		52.5		4-Feb-08		0:07:53		68		54		16-Mar-08		0:25:59		68		44.5

		4-Feb-08		2:07:10		66.2		49		4-Feb-08		2:06:20		66.81		48		4-Feb-08		2:07:53		67.4		50.5		16-Mar-08		2:25:59		68.61		44.5

		4-Feb-08		4:07:10		66.2		45		4-Feb-08		4:06:20		65.6		45		4-Feb-08		4:07:53		66.81		47.5		16-Mar-08		4:25:59		68		46

		4-Feb-08		6:07:10		65.6		43		4-Feb-08		6:06:20		65.6		44		4-Feb-08		6:07:53		66.81		47.5		16-Mar-08		6:25:59		68		39

		4-Feb-08		8:07:10		65.6		40.5		4-Feb-08		8:06:20		65.01		41		4-Feb-08		8:07:53		68		45.5		16-Mar-08		8:25:59		68.61		45.5

		4-Feb-08		10:07:10		65.6		41		4-Feb-08		10:06:20		65.6		42.5		4-Feb-08		10:07:53		68.61		45		16-Mar-08		10:25:59		68.61		45.5

		4-Feb-08		12:07:10		65.6		41.5		4-Feb-08		12:06:20		66.2		41		4-Feb-08		12:07:53		68		46		16-Mar-08		12:25:59		68.61		45.5

		4-Feb-08		14:07:10		65.6		40.5		4-Feb-08		14:06:20		66.81		38		4-Feb-08		14:07:53		68		46		16-Mar-08		14:25:59		68.61		35

		4-Feb-08		16:07:10		66.2		39		4-Feb-08		16:06:20		66.81		38		4-Feb-08		16:07:53		68		45		16-Mar-08		16:25:59		68.61		45

		4-Feb-08		18:07:10		66.2		38.5		4-Feb-08		18:06:20		66.81		36.5		4-Feb-08		18:07:53		68		45		16-Mar-08		18:25:59		68.61		45

		4-Feb-08		20:07:10		66.2		37.5		4-Feb-08		20:06:20		65.6		38		4-Feb-08		20:07:53		68		45.5		16-Mar-08		20:25:59		68.61		45

		4-Feb-08		22:07:10		65.6		37.5		4-Feb-08		22:06:20		65.6		38.5		4-Feb-08		22:07:53		67.4		46		16-Mar-08		22:25:59		68		46

		5-Feb-08		0:07:10		65.6		37		5-Feb-08		0:06:20		65.01		38		5-Feb-08		0:07:53		66.81		46.5		17-Mar-08		0:25:59		68.61		44

		5-Feb-08		2:07:10		65.6		36		5-Feb-08		2:06:20		65.6		35.5		5-Feb-08		2:07:53		66.81		46		17-Mar-08		2:25:59		68.61		44

		5-Feb-08		4:07:10		65.6		34.5		5-Feb-08		4:06:20		65.01		35		5-Feb-08		4:07:53		66.2		46		17-Mar-08		4:25:59		68.61		45

		5-Feb-08		6:07:10		65.6		33.5		5-Feb-08		6:06:20		65.01		33		5-Feb-08		6:07:53		66.81		46		17-Mar-08		6:25:59		68		43.5

		5-Feb-08		8:07:10		65.6		33		5-Feb-08		8:06:20		65.01		33.5		5-Feb-08		8:07:53		70.41		39.5		17-Mar-08		8:25:59		68.61		44

		5-Feb-08		10:07:10		65.6		34.5		5-Feb-08		10:06:20		68.61		32.5		5-Feb-08		10:07:53		71		41.5		17-Mar-08		10:25:59		68.61		43

		5-Feb-08		12:07:10		66.2		34.5		5-Feb-08		12:06:20		71		30.5		5-Feb-08		12:07:53		70.41		42.5		17-Mar-08		12:25:59		68		35.5

		5-Feb-08		14:07:10		66.81		32		5-Feb-08		14:06:20		70.41		29.5		5-Feb-08		14:07:53		71		39.5		17-Mar-08		14:25:59		68.61		27.5

		5-Feb-08		16:07:10		67.4		31		5-Feb-08		16:06:20		70.41		28.5		5-Feb-08		16:07:53		71		34.5		17-Mar-08		16:25:59		68.61		26

		5-Feb-08		18:07:10		68		34		5-Feb-08		18:06:20		69.8		29		5-Feb-08		18:07:53		70.41		37.5		17-Mar-08		18:25:59		68		34

		5-Feb-08		20:07:10		67.4		41.5		5-Feb-08		20:06:20		68		32		5-Feb-08		20:07:53		71		36		17-Mar-08		20:25:59		68		44

		5-Feb-08		22:07:10		66.81		35.5		5-Feb-08		22:06:20		67.4		33		5-Feb-08		22:07:53		69.8		39		17-Mar-08		22:25:59		68.61		44

		6-Feb-08		0:07:10		66.81		34.5		6-Feb-08		0:06:20		67.4		33.5		6-Feb-08		0:07:53		68		36.5		18-Mar-08		0:25:59		68.61		37.5

		6-Feb-08		2:07:10		66.81		34		6-Feb-08		2:06:20		67.4		33		6-Feb-08		2:07:53		66.81		36.5		18-Mar-08		2:25:59		68.61		36.5

		6-Feb-08		4:07:10		66.2		34		6-Feb-08		4:06:20		67.4		32.5		6-Feb-08		4:07:53		66.2		37		18-Mar-08		4:25:59		68		44.5

		6-Feb-08		6:07:10		66.2		33		6-Feb-08		6:06:20		68		31.5		6-Feb-08		6:07:53		67.4		36		18-Mar-08		6:25:59		68		42

		6-Feb-08		8:07:10		66.2		32		6-Feb-08		8:06:20		68		30.5		6-Feb-08		8:07:53		68		35		18-Mar-08		8:25:59		68.61		43.5

		6-Feb-08		10:07:10		66.81		34		6-Feb-08		10:06:20		69.8		31.5		6-Feb-08		10:07:53		70.41		36.5		18-Mar-08		10:25:59		68		39.5

		6-Feb-08		12:07:10		67.4		34.5		6-Feb-08		12:06:20		71		31.5		6-Feb-08		12:07:53		69.8		39.5		18-Mar-08		12:25:59		68.61		43.5

		6-Feb-08		14:07:10		67.4		34.5		6-Feb-08		14:06:20		69.2		34.5		6-Feb-08		14:07:53		71		36		18-Mar-08		14:25:59		68		40

		6-Feb-08		16:07:10		68.61		33		6-Feb-08		16:06:20		71		31		6-Feb-08		16:07:53		71		35		18-Mar-08		16:25:59		68.61		46

		6-Feb-08		18:07:10		68		37		6-Feb-08		18:06:20		69.8		33		6-Feb-08		18:07:53		71		38		18-Mar-08		18:25:59		68.61		44.5

		6-Feb-08		20:07:10		66.81		41		6-Feb-08		20:06:20		68		37.5		6-Feb-08		20:07:53		70.41		39		18-Mar-08		20:25:59		68.61		44.5

		6-Feb-08		22:07:10		66.2		44		6-Feb-08		22:06:20		67.4		38		6-Feb-08		22:07:53		69.8		39		18-Mar-08		22:25:59		68.61		44.5

		7-Feb-08		0:07:10		66.2		45		7-Feb-08		0:06:20		68		36		7-Feb-08		0:07:53		68.61		39.5		19-Mar-08		0:25:59		68		41

		7-Feb-08		2:07:10		65.6		46		7-Feb-08		2:06:20		67.4		35.5		7-Feb-08		2:07:53		67.4		40		19-Mar-08		2:25:59		68		45

		7-Feb-08		4:07:10		65.6		46		7-Feb-08		4:06:20		68		34		7-Feb-08		4:07:53		66.81		40		19-Mar-08		4:25:59		68		45

		7-Feb-08		6:07:10		65.6		46.5		7-Feb-08		6:06:20		68		33		7-Feb-08		6:07:53		66.81		39.5		19-Mar-08		6:25:59		68.61		44.5

		7-Feb-08		8:07:10		65.6		47		7-Feb-08		8:06:20		67.4		33		7-Feb-08		8:07:53		69.8		38		19-Mar-08		8:25:59		68.61		44.5

		7-Feb-08		10:07:10		65.6		46.5		7-Feb-08		10:06:20		72.21		33.5		7-Feb-08		10:07:53		71.6		37.5		19-Mar-08		10:25:59		68.61		46.5

		7-Feb-08		12:07:10		66.81		46		7-Feb-08		12:06:20		74.01		36.5		7-Feb-08		12:07:53		69.8		44.5		19-Mar-08		12:25:59		68.61		47.5

		7-Feb-08		14:07:10		67.4		46		7-Feb-08		14:06:20		71.6		34		7-Feb-08		14:07:53		71		47		19-Mar-08		14:25:59		68.61		45

		7-Feb-08		16:07:10		67.4		46		7-Feb-08		16:06:20		69.8		37		7-Feb-08		16:07:53		70.41		43.5		19-Mar-08		16:25:59		68.61		44.5

		7-Feb-08		18:07:10		67.4		46		7-Feb-08		18:06:20		69.2		34		7-Feb-08		18:07:53		70.41		41		19-Mar-08		18:25:59		68.61		47.5

		7-Feb-08		20:07:10		66.2		46.5		7-Feb-08		20:06:20		69.2		34		7-Feb-08		20:07:53		69.8		39		19-Mar-08		20:25:59		68		48

		7-Feb-08		22:07:10		66.2		47		7-Feb-08		22:06:20		66.81		36		7-Feb-08		22:07:53		69.8		38		19-Mar-08		22:25:59		68.61		45

		8-Feb-08		0:07:10		65.6		48		8-Feb-08		0:06:20		65.6		37.5		8-Feb-08		0:07:53		68.61		38.5		20-Mar-08		0:25:59		68.61		45

		8-Feb-08		2:07:10		65.01		48.5		8-Feb-08		2:06:20		65.6		37.5		8-Feb-08		2:07:53		67.4		39		20-Mar-08		2:25:59		68		40

		8-Feb-08		4:07:10		65.01		49		8-Feb-08		4:06:20		65.6		36.5		8-Feb-08		4:07:53		66.81		39.5		20-Mar-08		4:25:59		68		39

		8-Feb-08		6:07:10		65.01		49		8-Feb-08		6:06:20		65.6		36		8-Feb-08		6:07:53		66.81		39		20-Mar-08		6:25:59		68.61		38.5

		8-Feb-08		8:07:10		65.01		48.5		8-Feb-08		8:06:20		68		33.5		8-Feb-08		8:07:53		69.8		37		20-Mar-08		8:25:59		68		44.5

		8-Feb-08		10:07:10		65.01		49		8-Feb-08		10:06:20		70.41		35		8-Feb-08		10:07:53		71.6		38		20-Mar-08		10:25:59		68.61		45

		8-Feb-08		12:07:10		66.2		48		8-Feb-08		12:06:20		70.41		35.5		8-Feb-08		12:07:53		70.41		39		20-Mar-08		12:25:59		68.61		45.5

		8-Feb-08		14:07:10		66.81		48.5		8-Feb-08		14:06:20		71		38.5		8-Feb-08		14:07:53		71.6		46.5		20-Mar-08		14:25:59		68.61		46

		8-Feb-08		16:07:10		68.61		49.5		8-Feb-08		16:06:20		71		39		8-Feb-08		16:07:53		69.8		49		20-Mar-08		16:25:59		68		47

		8-Feb-08		18:07:10		68.61		44.5		8-Feb-08		18:06:20		69.8		41		8-Feb-08		18:07:53		71		47		20-Mar-08		18:25:59		68.61		45

		8-Feb-08		20:07:10		68.61		42.5		8-Feb-08		20:06:20		69.8		40.5		8-Feb-08		20:07:53		69.8		44.5		20-Mar-08		20:25:59		68.61		45

		8-Feb-08		22:07:10		68		45		8-Feb-08		22:06:20		68		44		8-Feb-08		22:07:53		70.41		42.5		20-Mar-08		22:25:59		68.61		44.5

		9-Feb-08		0:07:10		66.81		44		9-Feb-08		0:06:20		66.2		44		9-Feb-08		0:07:53		69.8		41		21-Mar-08		0:25:59		68.61		45

		9-Feb-08		2:07:10		66.2		44		9-Feb-08		2:06:20		66.2		40.5		9-Feb-08		2:07:53		68.61		40		21-Mar-08		2:25:59		68		45.5

		9-Feb-08		4:07:10		66.2		42		9-Feb-08		4:06:20		66.2		37		9-Feb-08		4:07:53		67.4		38.5		21-Mar-08		4:25:59		68		36.5

		9-Feb-08		6:07:10		65.6		40.5		9-Feb-08		6:06:20		66.2		36		9-Feb-08		6:07:53		67.4		37.5		21-Mar-08		6:25:59		68		45.5

		9-Feb-08		8:07:10		65.6		39.5		9-Feb-08		8:06:20		68		32		9-Feb-08		8:07:53		69.2		36		21-Mar-08		8:25:59		68		36

		9-Feb-08		10:07:10		66.2		40		9-Feb-08		10:06:20		71		35		9-Feb-08		10:07:53		71.6		35.5		21-Mar-08		10:25:59		67.4		46.5

		9-Feb-08		12:07:10		67.4		46.5		9-Feb-08		12:06:20		69.2		33.5		9-Feb-08		12:07:53		71		38.5		21-Mar-08		12:25:59		68.61		42

		9-Feb-08		14:07:10		69.8		47.5		9-Feb-08		14:06:20		68.61		33		9-Feb-08		14:07:53		71		34.5		21-Mar-08		14:25:59		68.61		32.5

		9-Feb-08		16:07:10		72.8		42		9-Feb-08		16:06:20		68.61		28.5		9-Feb-08		16:07:53		71		38.5		21-Mar-08		16:25:59		68		32.5

		9-Feb-08		18:07:10		71		48		9-Feb-08		18:06:20		68		29		9-Feb-08		18:07:53		70.41		35.5		21-Mar-08		18:25:59		68		42.5

		9-Feb-08		20:07:10		67.4		48.5		9-Feb-08		20:06:20		68.61		38.5		9-Feb-08		20:07:53		69.8		39.5		21-Mar-08		20:25:59		68.61		37

		9-Feb-08		22:07:10		65.6		51		9-Feb-08		22:06:20		67.4		38.5		9-Feb-08		22:07:53		69.8		38.5		21-Mar-08		22:25:59		68.61		36.5

		10-Feb-08		0:07:10		65.01		49.5		10-Feb-08		0:06:20		66.2		39		10-Feb-08		0:07:53		69.2		37.5		22-Mar-08		0:25:59		68		34.5

		10-Feb-08		2:07:10		65.01		49		10-Feb-08		2:06:20		65.6		38		10-Feb-08		2:07:53		68		37.5		22-Mar-08		2:25:59		68		42.5

		10-Feb-08		4:07:10		65.01		50		10-Feb-08		4:06:20		65.6		36.5		10-Feb-08		4:07:53		66.81		37.5		22-Mar-08		4:25:59		68		38

		10-Feb-08		6:07:10		65.01		51		10-Feb-08		6:06:20		65.6		35.5		10-Feb-08		6:07:53		66.2		38		22-Mar-08		6:25:59		68		35

		10-Feb-08		8:07:10		65.01		50		10-Feb-08		8:06:20		66.2		34		10-Feb-08		8:07:53		66.81		37		22-Mar-08		8:25:59		68		43.5

		10-Feb-08		10:07:10		65.01		49.5		10-Feb-08		10:06:20		67.4		36		10-Feb-08		10:07:53		68		37		22-Mar-08		10:25:59		68		41

		10-Feb-08		12:07:10		66.2		51		10-Feb-08		12:06:20		67.4		40.5		10-Feb-08		12:07:53		69.8		38.5		22-Mar-08		12:25:59		68.61		43.5

		10-Feb-08		14:07:10		68.61		49.5		10-Feb-08		14:06:20		68		41.5		10-Feb-08		14:07:53		70.41		41		22-Mar-08		14:25:59		68		37

		10-Feb-08		16:07:10		69.8		49		10-Feb-08		16:06:20		68		44		10-Feb-08		16:07:53		70.41		45		22-Mar-08		16:25:59		68.61		45

		10-Feb-08		18:07:10		69.8		49.5		10-Feb-08		18:06:20		68		39.5		10-Feb-08		18:07:53		70.41		42		22-Mar-08		18:25:59		68		44.5

		10-Feb-08		20:07:10		67.4		47.5		10-Feb-08		20:06:20		68.61		39.5		10-Feb-08		20:07:53		69.8		46.5		22-Mar-08		20:25:59		68		38.5

		10-Feb-08		22:07:10		66.2		49.5		10-Feb-08		22:06:20		68		39.5		10-Feb-08		22:07:53		70.41		42		22-Mar-08		22:25:59		68		38.5

		11-Feb-08		0:07:10		65.6		49.5		11-Feb-08		0:06:20		66.2		42		11-Feb-08		0:07:53		69.8		41.5		23-Mar-08		0:25:59		68		39

		11-Feb-08		2:07:10		65.01		50		11-Feb-08		2:06:20		66.2		42		11-Feb-08		2:07:53		68.61		42		23-Mar-08		2:25:59		68.61		36.5

		11-Feb-08		4:07:10		65.01		50		11-Feb-08		4:06:20		65.6		40		11-Feb-08		4:07:53		68		41.5		23-Mar-08		4:25:59		68		35.5

		11-Feb-08		6:07:10		65.01		50.5		11-Feb-08		6:06:20		65.6		38		11-Feb-08		6:07:53		67.4		42.5		23-Mar-08		6:25:59		68.61		43.5

		11-Feb-08		8:07:10		65.01		50		11-Feb-08		8:06:20		66.2		36.5		11-Feb-08		8:07:53		68		41.5		23-Mar-08		8:25:59		68		36

		11-Feb-08		10:07:10		65.01		51		11-Feb-08		10:06:20		66.81		39		11-Feb-08		10:07:53		68		42.5		23-Mar-08		10:25:59		68.61		44

		11-Feb-08		12:07:10		66.2		51.5		11-Feb-08		12:06:20		68		41.5		11-Feb-08		12:07:53		69.8		41.5		23-Mar-08		12:25:59		68		40

		11-Feb-08		14:07:10		68		51		11-Feb-08		14:06:20		67.4		43.5		11-Feb-08		14:07:53		69.8		44		23-Mar-08		14:25:59		68.61		44.5

		11-Feb-08		16:07:10		70.41		51		11-Feb-08		16:06:20		68		42		11-Feb-08		16:07:53		70.41		46.5		23-Mar-08		16:25:59		68.61		33

		11-Feb-08		18:07:10		69.8		50.5		11-Feb-08		18:06:20		68		48.5		11-Feb-08		18:07:53		70.41		46		23-Mar-08		18:25:59		68.61		44.5

		11-Feb-08		20:07:10		66.2		52		11-Feb-08		20:06:20		68.61		45.5		11-Feb-08		20:07:53		70.41		46		23-Mar-08		20:25:59		68.61		43.5

		11-Feb-08		22:07:10		65.6		52		11-Feb-08		22:06:20		67.4		44.5		11-Feb-08		22:07:53		70.41		43.5		23-Mar-08		22:25:59		68		45

		12-Feb-08		0:07:10		65.6		51.5		12-Feb-08		0:06:20		66.2		44.5		12-Feb-08		0:07:53		69.2		41.5		24-Mar-08		0:25:59		68		38.5

		12-Feb-08		2:07:10		65.01		50		12-Feb-08		2:06:20		66.2		42		12-Feb-08		2:07:53		68.61		41		24-Mar-08		2:25:59		68.61		39.5

		12-Feb-08		4:07:10		65.01		52		12-Feb-08		4:06:20		65.6		41.5		12-Feb-08		4:07:53		68		41		24-Mar-08		4:25:59		68.61		36

		12-Feb-08		6:07:10		65.01		50		12-Feb-08		6:06:20		65.6		40.5		12-Feb-08		6:07:53		67.4		41		24-Mar-08		6:25:59		68		35.5

		12-Feb-08		8:07:10		65.01		51		12-Feb-08		8:06:20		66.81		37.5		12-Feb-08		8:07:53		69.8		38		24-Mar-08		8:25:59		68.61		33.5

		12-Feb-08		10:07:10		65.6		49.5		12-Feb-08		10:06:20		71		39		12-Feb-08		10:07:53		71		41.5		24-Mar-08		10:25:59		68		37.5

		12-Feb-08		12:07:10		67.4		49.5		12-Feb-08		12:06:20		72.21		42.5		12-Feb-08		12:07:53		70.41		39.5		24-Mar-08		12:25:59		68.61		37.5

		12-Feb-08		14:07:10		70.41		50		12-Feb-08		14:06:20		72.8		41.5		12-Feb-08		14:07:53		71		44		24-Mar-08		14:25:59		68.61		38.5

		12-Feb-08		16:07:10		72.8		49.5		12-Feb-08		16:06:20		71.6		38.5		12-Feb-08		16:07:53		70.41		47.5		24-Mar-08		16:25:59		68		45

		12-Feb-08		18:07:10		71.6		49.5		12-Feb-08		18:06:20		70.41		48.5		12-Feb-08		18:07:53		70.41		50.5		24-Mar-08		18:25:59		68		42.5

		12-Feb-08		20:07:10		67.4		51		12-Feb-08		20:06:20		69.8		43.5		12-Feb-08		20:07:53		69.8		49		24-Mar-08		20:25:59		68		44.5

		12-Feb-08		22:07:10		66.2		52		12-Feb-08		22:06:20		69.2		43.5		12-Feb-08		22:07:53		70.41		45.5		24-Mar-08		22:25:59		68.61		40

		13-Feb-08		0:07:10		66.2		48.5		13-Feb-08		0:06:20		68.61		42.5		13-Feb-08		0:07:53		69.8		42.5		25-Mar-08		0:25:59		68.61		44

		13-Feb-08		2:07:10		65.6		49		13-Feb-08		2:06:20		68.61		40.5		13-Feb-08		2:07:53		69.2		41.5		25-Mar-08		2:25:59		68		38

		13-Feb-08		4:07:10		65.6		48.5		13-Feb-08		4:06:20		68.61		38		13-Feb-08		4:07:53		68.61		40.5		25-Mar-08		4:25:59		68.61		44.5

		13-Feb-08		6:07:10		65.6		50.5		13-Feb-08		6:06:20		68.61		36.5		13-Feb-08		6:07:53		67.4		41		25-Mar-08		6:25:59		68		37.5

		13-Feb-08		8:07:10		65.6		50		13-Feb-08		8:06:20		69.2		36.5		13-Feb-08		8:07:53		69.8		40		25-Mar-08		8:25:59		68		38

		13-Feb-08		10:07:10		66.2		50.5		13-Feb-08		10:06:20		70.41		37.5		13-Feb-08		10:07:53		71.6		42		25-Mar-08		10:25:59		67.4		42.5

		13-Feb-08		12:07:10		67.4		50.5		13-Feb-08		12:06:20		71		43		13-Feb-08		12:07:53		71		47		25-Mar-08		12:25:59		68		44.5

		13-Feb-08		14:07:10		73.4		46		13-Feb-08		14:06:20		71.6		43.5		13-Feb-08		14:07:53		71		52.5		25-Mar-08		14:25:59		68		46

		13-Feb-08		16:07:10		73.4		48.5		13-Feb-08		16:06:20		71.6		40		13-Feb-08		16:07:53		71		50.5		25-Mar-08		16:25:59		68		45.5

		13-Feb-08		18:07:10		71		48		13-Feb-08		18:06:20		70.41		45		13-Feb-08		18:07:53		70.41		47		25-Mar-08		18:25:59		68		44

		13-Feb-08		20:07:10		66.2		53		13-Feb-08		20:06:20		69.8		44		13-Feb-08		20:07:53		70.41		42.5		25-Mar-08		20:25:59		68		42.5

		13-Feb-08		22:07:10		65.6		53		13-Feb-08		22:06:20		69.2		43.5		13-Feb-08		22:07:53		70.41		44		25-Mar-08		22:25:59		68.61		41.5

		14-Feb-08		0:07:10		65.6		50.5		14-Feb-08		0:06:20		68.61		41		14-Feb-08		0:07:53		70.41		42		26-Mar-08		0:25:59		68.61		40.5

		14-Feb-08		2:07:10		65.01		51		14-Feb-08		2:06:20		68.61		39		14-Feb-08		2:07:53		69.2		40		26-Mar-08		2:25:59		68.61		40

		14-Feb-08		4:07:10		65.01		49		14-Feb-08		4:06:20		68.61		39		14-Feb-08		4:07:53		68.61		40.5		26-Mar-08		4:25:59		68.61		39

		14-Feb-08		6:07:10		65.01		51		14-Feb-08		6:06:20		68.61		38.5		14-Feb-08		6:07:53		68		40.5		26-Mar-08		6:25:59		68.61		40

		14-Feb-08		8:07:10		65.6		49.5		14-Feb-08		8:06:20		68.61		37		14-Feb-08		8:07:53		71		40		26-Mar-08		8:25:59		68		41.5

		14-Feb-08		10:07:10		67.4		46.5		14-Feb-08		10:06:20		69.8		30		14-Feb-08		10:07:53		70.41		39		26-Mar-08		10:25:59		68		42.5

		14-Feb-08		12:07:10		68		46.5		14-Feb-08		12:06:20		70.41		30.5		14-Feb-08		12:07:53		71		33		26-Mar-08		12:25:59		68.61		43.5

		14-Feb-08		14:07:10		66.2		46.5		14-Feb-08		14:06:20		72.21		28.5		14-Feb-08		14:07:53		71		38.5		26-Mar-08		14:25:59		68		43

		14-Feb-08		16:07:10		65.6		47		14-Feb-08		16:06:20		72.8		24		14-Feb-08		16:07:53		71		37.5		26-Mar-08		16:25:59		68		42

		14-Feb-08		18:07:10		65.01		49		14-Feb-08		18:06:20		71.6		16.5		14-Feb-08		18:07:53		71		30.5		26-Mar-08		18:25:59		68		40.5

		14-Feb-08		20:07:10		64.4		47		14-Feb-08		20:06:20		71		17		14-Feb-08		20:07:53		70.41		30		26-Mar-08		20:25:59		68.61		38

		14-Feb-08		22:07:10		64.4		49		14-Feb-08		22:06:20		70.41		27.5		14-Feb-08		22:07:53		71		32		26-Mar-08		22:25:59		68		37.5

		15-Feb-08		0:07:10		64.4		49		15-Feb-08		0:06:20		70.41		26		15-Feb-08		0:07:53		70.41		32		27-Mar-08		0:25:59		68		38

		15-Feb-08		2:07:10		64.4		46.5		15-Feb-08		2:06:20		70.41		23.5		15-Feb-08		2:07:53		69.2		31		27-Mar-08		2:25:59		67.4		37.5

		15-Feb-08		4:07:10		64.4		50.5		15-Feb-08		4:06:20		70.41		21		15-Feb-08		4:07:53		68.61		31		27-Mar-08		4:25:59		67.4		36.5

		15-Feb-08		6:07:10		64.4		49		15-Feb-08		6:06:20		70.41		19.5		15-Feb-08		6:07:53		68		30.5		27-Mar-08		6:25:59		67.4		35

		15-Feb-08		8:07:10		64.4		50.5		15-Feb-08		8:06:20		70.41		19.5		15-Feb-08		8:07:53		70.41		31		27-Mar-08		8:25:59		68		35.5

		15-Feb-08		10:07:10		65.01		33.5		15-Feb-08		10:06:20		72.21		19.5		15-Feb-08		10:07:53		71		30.5		27-Mar-08		10:25:59		67.4		37

		15-Feb-08		12:07:10		65.6		48		15-Feb-08		12:06:20		72.8		19		15-Feb-08		12:07:53		71		29.5		27-Mar-08		12:25:59		68		36.5

		15-Feb-08		14:07:10		65.6		49		15-Feb-08		14:06:20		72.8		19.5		15-Feb-08		14:07:53		71		34.5		27-Mar-08		14:25:59		68		39

		15-Feb-08		16:07:10		65.6		48.5		15-Feb-08		16:06:20		73.4		19		15-Feb-08		16:07:53		71		34		27-Mar-08		16:25:59		68		39.5

		15-Feb-08		18:07:10		65.6		49.5		15-Feb-08		18:06:20		71.6		20.5		15-Feb-08		18:07:53		70.41		32		27-Mar-08		18:25:59		68.61		37.5

		15-Feb-08		20:07:10		65.01		43.5		15-Feb-08		20:06:20		71		24.5		15-Feb-08		20:07:53		70.41		31.5		27-Mar-08		20:25:59		68.61		37

		15-Feb-08		22:07:10		65.01		49		15-Feb-08		22:06:20		70.41		26.5		15-Feb-08		22:07:53		69.8		31.5		27-Mar-08		22:25:59		68.61		34.5

		16-Feb-08		0:07:10		65.6		50		16-Feb-08		0:06:20		70.41		26.5		16-Feb-08		0:07:53		69.2		32		28-Mar-08		0:25:59		68		34.5

		16-Feb-08		2:07:10		65.01		50		16-Feb-08		2:06:20		70.41		26.5		16-Feb-08		2:07:53		68.61		33		28-Mar-08		2:25:59		67.4		33

		16-Feb-08		4:07:10		65.01		51		16-Feb-08		4:06:20		70.41		27		16-Feb-08		4:07:53		68		33.5		28-Mar-08		4:25:59		66.81		31.5

		16-Feb-08		6:07:10		65.01		50		16-Feb-08		6:06:20		70.41		26.5		16-Feb-08		6:07:53		66.81		34		28-Mar-08		6:25:59		67.4		31.5

		16-Feb-08		8:07:10		65.01		51		16-Feb-08		8:06:20		70.41		27		16-Feb-08		8:07:53		69.2		33		28-Mar-08		8:25:59		68		30.5

		16-Feb-08		10:07:10		65.6		51		16-Feb-08		10:06:20		71.6		27.5		16-Feb-08		10:07:53		71.6		33.5		28-Mar-08		10:25:59		68		29

		16-Feb-08		12:07:10		65.01		50		16-Feb-08		12:06:20		73.4		28		16-Feb-08		12:07:53		70.41		39		28-Mar-08		12:25:59		68		26

		16-Feb-08		14:07:10		65.6		50		16-Feb-08		14:06:20		73.4		27		16-Feb-08		14:07:53		71		33		28-Mar-08		14:25:59		68.61		25.5

		16-Feb-08		16:07:10		65.6		51.5		16-Feb-08		16:06:20		73.4		37.5		16-Feb-08		16:07:53		71.6		36.5		28-Mar-08		16:25:59		68		23.5

		16-Feb-08		18:07:10		65.01		51		16-Feb-08		18:06:20		67.4		41		16-Feb-08		18:07:53		70.41		40		28-Mar-08		18:25:59		68.61		23.5

		16-Feb-08		20:07:10		65.01		50.5		16-Feb-08		20:06:20		66.2		43		16-Feb-08		20:07:53		71		39.5		28-Mar-08		20:25:59		68		26.5

		16-Feb-08		22:07:10		65.01		52		16-Feb-08		22:06:20		66.81		41		16-Feb-08		22:07:53		70.41		39		28-Mar-08		22:25:59		68		32.5

		17-Feb-08		0:07:10		65.01		52		17-Feb-08		0:06:20		66.2		40		17-Feb-08		0:07:53		69.8		38		29-Mar-08		0:25:59		67.4		33.5

		17-Feb-08		2:07:10		65.01		52.5		17-Feb-08		2:06:20		66.2		40.5		17-Feb-08		2:07:53		69.2		39.5		29-Mar-08		2:25:59		67.4		34

		17-Feb-08		4:07:10		65.01		53		17-Feb-08		4:06:20		66.2		41.5		17-Feb-08		4:07:53		68.61		39.5		29-Mar-08		4:25:59		66.81		34

		17-Feb-08		6:07:10		65.01		53		17-Feb-08		6:06:20		66.2		41		17-Feb-08		6:07:53		68.61		40		29-Mar-08		6:25:59		67.4		33.5

		17-Feb-08		8:07:10		65.01		52		17-Feb-08		8:06:20		65.6		40		17-Feb-08		8:07:53		70.41		39		29-Mar-08		8:25:59		68		34

		17-Feb-08		10:07:10		65.01		52		17-Feb-08		10:06:20		65.6		40.5		17-Feb-08		10:07:53		71		37.5		29-Mar-08		10:25:59		67.4		30.5

		17-Feb-08		12:07:10		65.01		52.5		17-Feb-08		12:06:20		66.81		40.5		17-Feb-08		12:07:53		71		38.5		29-Mar-08		12:25:59		68		37

		17-Feb-08		14:07:10		65.01		52		17-Feb-08		14:06:20		67.4		40.5		17-Feb-08		14:07:53		70.41		41.5		29-Mar-08		14:25:59		68		39.5

		17-Feb-08		16:07:10		65.01		53		17-Feb-08		16:06:20		68		38		17-Feb-08		16:07:53		71		43.5		29-Mar-08		16:25:59		68		42

		17-Feb-08		18:07:10		65.01		52.5		17-Feb-08		18:06:20		66.81		42.5		17-Feb-08		18:07:53		70.41		41.5		29-Mar-08		18:25:59		68		42.5

		17-Feb-08		20:07:10		65.01		52.5		17-Feb-08		20:06:20		66.81		42.5		17-Feb-08		20:07:53		69.8		40.5		29-Mar-08		20:25:59		68		43

		17-Feb-08		22:07:10		65.01		53		17-Feb-08		22:06:20		66.81		40.5		17-Feb-08		22:07:53		69.8		39		29-Mar-08		22:25:59		68		43.5

		18-Feb-08		0:07:10		65.01		52		18-Feb-08		0:06:20		66.2		39.5		18-Feb-08		0:07:53		69.2		38.5		30-Mar-08		0:25:59		68		43.5

		18-Feb-08		2:07:10		65.01		52.5		18-Feb-08		2:06:20		66.2		42.5		18-Feb-08		2:07:53		68.61		40		30-Mar-08		2:25:59		68.61		42.5

		18-Feb-08		4:07:10		65.01		52		18-Feb-08		4:06:20		65.6		41.5		18-Feb-08		4:07:53		68		40.5		30-Mar-08		4:25:59		68.61		41.5

		18-Feb-08		6:07:10		65.01		51.5		18-Feb-08		6:06:20		65.6		41.5		18-Feb-08		6:07:53		68		40.5		30-Mar-08		6:25:59		68.61		40

		18-Feb-08		8:07:10		65.01		52		18-Feb-08		8:06:20		65.6		40		18-Feb-08		8:07:53		67.4		40.5		30-Mar-08		8:25:59		68.61		39

		18-Feb-08		10:07:10		65.01		51.5		18-Feb-08		10:06:20		65.6		41		18-Feb-08		10:07:53		67.4		40.5		30-Mar-08		10:25:59		68.61		39

		18-Feb-08		12:07:10		65.01		52		18-Feb-08		12:06:20		66.2		41.5		18-Feb-08		12:07:53		67.4		41		30-Mar-08		12:25:59		68.61		40

		18-Feb-08		14:07:10		65.01		52.5		18-Feb-08		14:06:20		67.4		42		18-Feb-08		14:07:53		68.61		41.5		30-Mar-08		14:25:59		68.61		40.5

		18-Feb-08		16:07:10		65.01		53.5		18-Feb-08		16:06:20		66.81		45.5		18-Feb-08		16:07:53		69.8		42		30-Mar-08		16:25:59		68.61		40

		18-Feb-08		18:07:10		65.01		54		18-Feb-08		18:06:20		66.2		45		18-Feb-08		18:07:53		69.8		42.5		30-Mar-08		18:25:59		68.61		38.5

		18-Feb-08		20:07:10		65.01		52.5		18-Feb-08		20:06:20		66.81		41.5		18-Feb-08		20:07:53		69.2		41		30-Mar-08		20:25:59		68.61		37

		18-Feb-08		22:07:10		65.01		53		18-Feb-08		22:06:20		66.2		42.5		18-Feb-08		22:07:53		68.61		40.5		30-Mar-08		22:25:59		68.61		32.5

		19-Feb-08		0:07:10		65.01		51		19-Feb-08		0:06:20		66.2		41.5		19-Feb-08		0:07:53		68.61		41		31-Mar-08		0:25:59		68.61		32

		19-Feb-08		2:07:10		65.01		52.5		19-Feb-08		2:06:20		66.2		42.5		19-Feb-08		2:07:53		68		41.5		31-Mar-08		2:25:59		67.4		33

		19-Feb-08		4:07:10		65.01		51		19-Feb-08		4:06:20		66.2		43		19-Feb-08		4:07:53		68		41.5		31-Mar-08		4:25:59		66.81		33.5

		19-Feb-08		6:07:10		65.01		53		19-Feb-08		6:06:20		66.2		43		19-Feb-08		6:07:53		68		42		31-Mar-08		6:25:59		67.4		32.5

		19-Feb-08		8:07:10		65.01		52		19-Feb-08		8:06:20		66.81		42.5		19-Feb-08		8:07:53		68		42.5		31-Mar-08		8:25:59		68		32

		19-Feb-08		10:07:10		65.01		52.5		19-Feb-08		10:06:20		66.2		43.5		19-Feb-08		10:07:53		68.61		42.5		31-Mar-08		10:25:59		68.61		28.5

		19-Feb-08		12:07:10		65.01		52.5		19-Feb-08		12:06:20		66.2		43.5		19-Feb-08		12:07:53		69.2		42.5		31-Mar-08		12:25:59		67.4		25.5

		19-Feb-08		14:07:10		65.01		52		19-Feb-08		14:06:20		66.81		43		19-Feb-08		14:07:53		69.8		42		31-Mar-08		14:25:59		68		24

		19-Feb-08		16:07:10		65.01		52.5		19-Feb-08		16:06:20		66.2		44.5		19-Feb-08		16:07:53		69.8		42.5		31-Mar-08		16:25:59		68.61		24.5

		19-Feb-08		18:07:10		65.01		51.5		19-Feb-08		18:06:20		66.81		43		19-Feb-08		18:07:53		69.8		42		31-Mar-08		18:25:59		68		27.5

		19-Feb-08		20:07:10		65.01		52		19-Feb-08		20:06:20		66.2		43		19-Feb-08		20:07:53		69.8		41.5		31-Mar-08		20:25:59		68		27

		19-Feb-08		22:07:10		65.01		52		19-Feb-08		22:06:20		66.2		42		19-Feb-08		22:07:53		69.8		40.5		31-Mar-08		22:25:59		68		27.5

		20-Feb-08		0:07:10		65.01		52.5		20-Feb-08		0:06:20		66.81		39.5		20-Feb-08		0:07:53		69.8		40		1-Apr-08		0:25:59		67.4		29

		20-Feb-08		2:07:10		65.01		52		20-Feb-08		2:06:20		66.81		40.5		20-Feb-08		2:07:53		69.2		40		1-Apr-08		2:25:59		67.4		29

		20-Feb-08		4:07:10		65.01		52		20-Feb-08		4:06:20		66.81		40.5		20-Feb-08		4:07:53		69.2		40		1-Apr-08		4:25:59		68		28

		20-Feb-08		6:07:10		65.01		52.5		20-Feb-08		6:06:20		66.81		41		20-Feb-08		6:07:53		69.2		40.5		1-Apr-08		6:25:59		68.61		28.5

		20-Feb-08		8:07:10		65.6		51.5		20-Feb-08		8:06:20		67.4		41		20-Feb-08		8:07:53		71		41		1-Apr-08		8:25:59		68		30

		20-Feb-08		10:07:10		65.6		51.5		20-Feb-08		10:06:20		66.81		42		20-Feb-08		10:07:53		71		39.5		1-Apr-08		10:25:59		67.4		31

		20-Feb-08		12:07:10		66.2		51		20-Feb-08		12:06:20		66.81		48.5		20-Feb-08		12:07:53		71		42.5		1-Apr-08		12:25:59		68		25

		20-Feb-08		14:07:10		65.6		52.5		20-Feb-08		14:06:20		66.81		51.5		20-Feb-08		14:07:53		71		39		1-Apr-08		14:25:59		68		29.5

		20-Feb-08		16:07:10		66.81		52.5		20-Feb-08		16:06:20		67.4		48.5		20-Feb-08		16:07:53		70.41		43.5		1-Apr-08		16:25:59		68		31

		20-Feb-08		18:07:10		66.2		52		20-Feb-08		18:06:20		67.4		51.5		20-Feb-08		18:07:53		70.41		48		1-Apr-08		18:25:59		68		29.5

		20-Feb-08		20:07:10		66.2		51		20-Feb-08		20:06:20		66.2		55		20-Feb-08		20:07:53		70.41		47		1-Apr-08		20:25:59		67.4		30.5

		20-Feb-08		22:07:10		66.2		52.5		20-Feb-08		22:06:20		67.4		51.5		20-Feb-08		22:07:53		71		45.5		1-Apr-08		22:25:59		68		29.5

		21-Feb-08		0:07:10		66.2		52.5		21-Feb-08		0:06:20		67.4		50.5		21-Feb-08		0:07:53		70.41		45.5		2-Apr-08		0:25:59		68		32.5

		21-Feb-08		2:07:10		65.6		52.5		21-Feb-08		2:06:20		66.81		47		21-Feb-08		2:07:53		69.8		44		2-Apr-08		2:25:59		68		33.5

		21-Feb-08		4:07:10		65.6		52		21-Feb-08		4:06:20		66.81		47.5		21-Feb-08		4:07:53		69.2		44		2-Apr-08		4:25:59		68		33

		21-Feb-08		6:07:10		65.6		52.5		21-Feb-08		6:06:20		66.81		47		21-Feb-08		6:07:53		68.61		44.5		2-Apr-08		6:25:59		68		31

		21-Feb-08		8:07:10		66.2		52		21-Feb-08		8:06:20		67.4		47		21-Feb-08		8:07:53		71		41.5		2-Apr-08		8:25:59		68		33.5

		21-Feb-08		10:07:10		66.2		52		21-Feb-08		10:06:20		67.4		48.5		21-Feb-08		10:07:53		72.21		44.5		2-Apr-08		10:25:59		68		33

		21-Feb-08		12:07:10		65.6		51.5		21-Feb-08		12:06:20		66.81		49.5		21-Feb-08		12:07:53		70.41		48		2-Apr-08		12:25:59		68.61		33

		21-Feb-08		14:07:10		65.6		51		21-Feb-08		14:06:20		68		41		21-Feb-08		14:07:53		71.6		48.5		2-Apr-08		14:25:59		68		36.5

		21-Feb-08		16:07:10		66.81		50.5		21-Feb-08		16:06:20		68		40.5		21-Feb-08		16:07:53		71		47.5		2-Apr-08		16:25:59		68		34

		21-Feb-08		18:07:10		66.2		52		21-Feb-08		18:06:20		67.4		42.5		21-Feb-08		18:07:53		70.41		45.5		2-Apr-08		18:25:59		68		34

		21-Feb-08		20:07:10		66.2		52.5		21-Feb-08		20:06:20		66.81		44.5		21-Feb-08		20:07:53		70.41		43.5		2-Apr-08		20:25:59		68		37

		21-Feb-08		22:07:10		66.2		51.5		21-Feb-08		22:06:20		67.4		45		21-Feb-08		22:07:53		71		42.5		2-Apr-08		22:25:59		68.61		36.5

		22-Feb-08		0:07:10		66.2		49.5		22-Feb-08		0:06:20		66.81		43		22-Feb-08		0:07:53		70.41		41.5		3-Apr-08		0:25:59		68.61		36.5

		22-Feb-08		2:07:10		65.6		51.5		22-Feb-08		2:06:20		66.81		43.5		22-Feb-08		2:07:53		69.8		41		3-Apr-08		2:25:59		68		36

		22-Feb-08		4:07:10		65.6		52		22-Feb-08		4:06:20		66.81		43.5		22-Feb-08		4:07:53		69.2		41.5		3-Apr-08		4:25:59		67.4		35

		22-Feb-08		6:07:10		66.2		51.5		22-Feb-08		6:06:20		66.81		44		22-Feb-08		6:07:53		69.2		42		3-Apr-08		6:25:59		69.2		34

		22-Feb-08		8:07:10		66.2		51		22-Feb-08		8:06:20		66.2		46		22-Feb-08		8:07:53		71		44		3-Apr-08		8:25:59		67.4		36.5

		22-Feb-08		10:07:10		66.81		48		22-Feb-08		10:06:20		66.2		48		22-Feb-08		10:07:53		71.6		43		3-Apr-08		10:25:59		68		36.5

		22-Feb-08		12:07:10		66.81		48.5		22-Feb-08		12:06:20		67.4		43.5		22-Feb-08		12:07:53		71		39		3-Apr-08		12:25:59		68		37.5

		22-Feb-08		14:07:10		66.81		49		22-Feb-08		14:06:20		68		44.5		22-Feb-08		14:07:53		71		44		3-Apr-08		14:25:59		68		39

		22-Feb-08		16:07:10		66.2		50		22-Feb-08		16:06:20		68		48		22-Feb-08		16:07:53		71		40		3-Apr-08		16:25:59		68		37.5

		22-Feb-08		18:07:10		66.2		51.5		22-Feb-08		18:06:20		66.81		48		22-Feb-08		18:07:53		71		46.5		3-Apr-08		18:25:59		68.61		35

		22-Feb-08		20:07:10		66.2		49		22-Feb-08		20:06:20		67.4		49.5		22-Feb-08		20:07:53		70.41		42		3-Apr-08		20:25:59		68		35.5

		22-Feb-08		22:07:10		66.2		51		22-Feb-08		22:06:20		66.81		51.5		22-Feb-08		22:07:53		70.41		45.5		3-Apr-08		22:25:59		68.61		34

		23-Feb-08		0:07:10		65.6		50.5		23-Feb-08		0:06:20		66.81		49.5		23-Feb-08		0:07:53		70.41		44.5		4-Apr-08		0:25:59		68		34

		23-Feb-08		2:07:10		65.6		49		23-Feb-08		2:06:20		67.4		48		23-Feb-08		2:07:53		69.8		43.5		4-Apr-08		2:25:59		68		33.5

		23-Feb-08		4:07:10		65.6		49		23-Feb-08		4:06:20		67.4		46		23-Feb-08		4:07:53		69.8		43		4-Apr-08		4:25:59		68		35

		23-Feb-08		6:07:10		65.6		46.5		23-Feb-08		6:06:20		66.81		47		23-Feb-08		6:07:53		69.2		43		4-Apr-08		6:25:59		68.61		36.5

		23-Feb-08		8:07:10		66.2		48.5		23-Feb-08		8:06:20		66.2		48		23-Feb-08		8:07:53		71		40.5		4-Apr-08		8:25:59		68		38

		23-Feb-08		10:07:10		66.2		49.5		23-Feb-08		10:06:20		67.4		48		23-Feb-08		10:07:53		71.6		48.5		4-Apr-08		10:25:59		67.4		39

		23-Feb-08		12:07:10		66.81		48.5		23-Feb-08		12:06:20		67.4		47.5		23-Feb-08		12:07:53		71		49.5		4-Apr-08		12:25:59		73.4		36.5

		23-Feb-08		14:07:10		66.81		48.5		23-Feb-08		14:06:20		67.4		47		23-Feb-08		14:07:53		71		45.5		4-Apr-08		14:25:59		74.01		36

		23-Feb-08		16:07:10		66.81		44		23-Feb-08		16:06:20		68		41.5		23-Feb-08		16:07:53		71.6		45.5		4-Apr-08		16:25:59		74.6		37.5

		23-Feb-08		18:07:10		66.2		48		23-Feb-08		18:06:20		67.4		39.5		23-Feb-08		18:07:53		71		42.5		4-Apr-08		18:25:59		74.01		36.5

		23-Feb-08		20:07:10		66.2		48		23-Feb-08		20:06:20		66.81		38		23-Feb-08		20:07:53		70.41		40		4-Apr-08		20:25:59		73.4		36.5

		23-Feb-08		22:07:10		66.2		48.5		23-Feb-08		22:06:20		66.2		38.5		23-Feb-08		22:07:53		69.8		40.5		4-Apr-08		22:25:59		71.6		37

		24-Feb-08		0:07:10		65.6		49.5		24-Feb-08		0:06:20		65.01		38		24-Feb-08		0:07:53		69.2		38		5-Apr-08		0:25:59		70.41		36.5

		24-Feb-08		2:07:10		65.6		41.5		24-Feb-08		2:06:20		64.4		38		24-Feb-08		2:07:53		68		38		5-Apr-08		2:25:59		69.2		36.5

		24-Feb-08		4:07:10		65.6		48		24-Feb-08		4:06:20		63.8		37		24-Feb-08		4:07:53		66.81		37.5		5-Apr-08		4:25:59		68.61		38

		24-Feb-08		6:07:10		65.6		48		24-Feb-08		6:06:20		63.8		38		24-Feb-08		6:07:53		66.2		38.5		5-Apr-08		6:25:59		69.2		37.5

		24-Feb-08		8:07:10		66.2		48		24-Feb-08		8:06:20		64.4		38.5		24-Feb-08		8:07:53		68		38		5-Apr-08		8:25:59		70.41		38.5

		24-Feb-08		10:07:10		66.81		43		24-Feb-08		10:06:20		65.01		42		24-Feb-08		10:07:53		67.4		39.5		5-Apr-08		10:25:59		71.6		38.5

		24-Feb-08		12:07:10		66.81		47		24-Feb-08		12:06:20		66.2		42		24-Feb-08		12:07:53		68		40		5-Apr-08		12:25:59		72.8		38.5

		24-Feb-08		14:07:10		66.2		48		24-Feb-08		14:06:20		66.2		42.5		24-Feb-08		14:07:53		68		41		5-Apr-08		14:25:59		73.4		38.5

		24-Feb-08		16:07:10		66.2		48		24-Feb-08		16:06:20		65.6		44.5		24-Feb-08		16:07:53		68		42		5-Apr-08		16:25:59		74.01		38.5

		24-Feb-08		18:07:10		66.2		49		24-Feb-08		18:06:20		65.01		41.5		24-Feb-08		18:07:53		67.4		41.5		5-Apr-08		18:25:59		73.4		37.5

		24-Feb-08		20:07:10		65.6		45		24-Feb-08		20:06:20		65.6		44		24-Feb-08		20:07:53		66.81		42.5		5-Apr-08		20:25:59		72.8		37

		24-Feb-08		22:07:10		66.2		49		24-Feb-08		22:06:20		65.6		48		24-Feb-08		22:07:53		66.81		44.5		5-Apr-08		22:25:59		71.6		36.5

		25-Feb-08		0:07:10		66.2		49		25-Feb-08		0:06:20		66.2		47.5		25-Feb-08		0:07:53		67.4		45		6-Apr-08		0:25:59		69.8		36

		25-Feb-08		2:07:10		66.2		49		25-Feb-08		2:06:20		66.81		48		25-Feb-08		2:07:53		67.4		45.5		6-Apr-08		2:25:59		68		36.5

		25-Feb-08		4:07:10		66.2		49.5		25-Feb-08		4:06:20		66.81		49		25-Feb-08		4:07:53		67.4		46		6-Apr-08		4:25:59		67.4		37

		25-Feb-08		6:07:10		66.2		48		25-Feb-08		6:06:20		66.81		50		25-Feb-08		6:07:53		67.4		47		6-Apr-08		6:25:59		66.81		36.5

		25-Feb-08		8:07:10		66.2		49.5		25-Feb-08		8:06:20		66.81		51		25-Feb-08		8:07:53		67.4		48		6-Apr-08		8:25:59		66.81		36.5

		25-Feb-08		10:07:10		66.2		51.5		25-Feb-08		10:06:20		67.4		51.5		25-Feb-08		10:07:53		67.4		49.5		6-Apr-08		10:25:59		68.61		38

		25-Feb-08		12:07:10		66.2		52		25-Feb-08		12:06:20		66.81		52.5		25-Feb-08		12:07:53		68		49		6-Apr-08		12:25:59		70.41		38.5

		25-Feb-08		14:07:10		66.2		53		25-Feb-08		14:06:20		67.4		52		25-Feb-08		14:07:53		68		49.5		6-Apr-08		14:25:59		71.6		37.5

		25-Feb-08		16:07:10		66.2		49.5		25-Feb-08		16:06:20		66.2		52.5		25-Feb-08		16:07:53		68		49		6-Apr-08		16:25:59		72.21		37

		25-Feb-08		18:07:10		66.2		50.5		25-Feb-08		18:06:20		67.4		49.5		25-Feb-08		18:07:53		68		48		6-Apr-08		18:25:59		72.8		36.5

		25-Feb-08		20:07:10		66.2		50		25-Feb-08		20:06:20		67.4		47.5		25-Feb-08		20:07:53		68		47.5		6-Apr-08		20:25:59		72.21		36.5

		25-Feb-08		22:07:10		66.2		50		25-Feb-08		22:06:20		66.81		48		25-Feb-08		22:07:53		68		47		6-Apr-08		22:25:59		71		37

		26-Feb-08		0:07:10		66.2		49.5		26-Feb-08		0:06:20		66.81		49.5		26-Feb-08		0:07:53		68		47		7-Apr-08		0:25:59		69.2		37

		26-Feb-08		2:07:10		65.6		50.5		26-Feb-08		2:06:20		66.2		49		26-Feb-08		2:07:53		67.4		47		7-Apr-08		2:25:59		68.61		37.5

		26-Feb-08		4:07:10		65.6		49		26-Feb-08		4:06:20		65.6		47		26-Feb-08		4:07:53		67.4		45.5		7-Apr-08		4:25:59		67.4		37.5

		26-Feb-08		6:07:10		65.6		49		26-Feb-08		6:06:20		65.6		48		26-Feb-08		6:07:53		66.81		45.5		7-Apr-08		6:25:59		66.81		38

		26-Feb-08		8:07:10		66.2		49		26-Feb-08		8:06:20		66.2		46.5		26-Feb-08		8:07:53		69.8		44		7-Apr-08		8:25:59		66.81		38.5

		26-Feb-08		10:07:10		66.81		49		26-Feb-08		10:06:20		66.81		48.5		26-Feb-08		10:07:53		71.6		42		7-Apr-08		10:25:59		68		39.5

		26-Feb-08		12:07:10		66.81		49.5		26-Feb-08		12:06:20		67.4		46.5		26-Feb-08		12:07:53		70.41		49.5		7-Apr-08		12:25:59		68.61		40

		26-Feb-08		14:07:10		66.81		48		26-Feb-08		14:06:20		67.4		45.5		26-Feb-08		14:07:53		71.6		51		7-Apr-08		14:25:59		69.8		39

		26-Feb-08		16:07:10		66.81		47.5		26-Feb-08		16:06:20		67.4		44.5		26-Feb-08		16:07:53		71		50.5		7-Apr-08		16:25:59		70.41		37.5

		26-Feb-08		18:07:10		66.2		49		26-Feb-08		18:06:20		67.4		47		26-Feb-08		18:07:53		71		50.5		7-Apr-08		18:25:59		71		36

		26-Feb-08		20:07:10		66.2		48.5		26-Feb-08		20:06:20		66.2		48.5		26-Feb-08		20:07:53		70.41		46		7-Apr-08		20:25:59		69.8		35

		26-Feb-08		22:07:10		65.6		50		26-Feb-08		22:06:20		66.81		46		26-Feb-08		22:07:53		70.41		44.5		7-Apr-08		22:25:59		68.61		35

		27-Feb-08		0:07:10		65.6		47.5		27-Feb-08		0:06:20		66.2		45		27-Feb-08		0:07:53		69.8		41.5		8-Apr-08		0:25:59		68		35.5

		27-Feb-08		2:07:10		65.6		49		27-Feb-08		2:06:20		65.01		43.5		27-Feb-08		2:07:53		68.61		41		8-Apr-08		2:25:59		66.81		36.5

		27-Feb-08		4:07:10		66.2		49		27-Feb-08		4:06:20		65.01		43.5		27-Feb-08		4:07:53		68		41		8-Apr-08		4:25:59		66.2		37

		27-Feb-08		6:07:10		66.2		48		27-Feb-08		6:06:20		65.01		44		27-Feb-08		6:07:53		67.4		41.5		8-Apr-08		6:25:59		67.4		36

		27-Feb-08		8:07:10		66.2		47.5		27-Feb-08		8:06:20		65.6		41		27-Feb-08		8:07:53		69.8		40		8-Apr-08		8:25:59		68.61		35.5

		27-Feb-08		10:07:10		66.2		47		27-Feb-08		10:06:20		66.81		44.5		27-Feb-08		10:07:53		71.6		38		8-Apr-08		10:25:59		71.6		36

		27-Feb-08		12:07:10		66.81		48.5		27-Feb-08		12:06:20		68		44.5		27-Feb-08		12:07:53		71		40.5		8-Apr-08		12:25:59		72.8		35

		27-Feb-08		14:07:10		66.81		46.5		27-Feb-08		14:06:20		67.4		44		27-Feb-08		14:07:53		70.41		39.5		8-Apr-08		14:25:59		74.01		33.5

		27-Feb-08		16:07:10		66.81		47		27-Feb-08		16:06:20		68.61		42		27-Feb-08		16:07:53		70.41		49.5		8-Apr-08		16:25:59		74.01		35.5

		27-Feb-08		18:07:10		66.2		50		27-Feb-08		18:06:20		68		48.5		27-Feb-08		18:07:53		70.41		42.5		8-Apr-08		18:25:59		73.4		34.5

		27-Feb-08		20:07:10		66.2		49.5		27-Feb-08		20:06:20		66.81		51.5		27-Feb-08		20:07:53		70.41		42.5		8-Apr-08		20:25:59		72.8		34.5

		27-Feb-08		22:07:10		66.2		49.5		27-Feb-08		22:06:20		66.81		50		27-Feb-08		22:07:53		71		46		8-Apr-08		22:25:59		72.21		34

		28-Feb-08		0:07:10		66.2		48.5		28-Feb-08		0:06:20		66.2		49.5		28-Feb-08		0:07:53		71		43		9-Apr-08		0:25:59		70.41		35

		28-Feb-08		2:07:10		66.2		49		28-Feb-08		2:06:20		66.81		47.5		28-Feb-08		2:07:53		70.41		42.5		9-Apr-08		2:25:59		69.2		35

		28-Feb-08		4:07:10		65.6		49		28-Feb-08		4:06:20		66.2		46.5		28-Feb-08		4:07:53		69.8		41.5		9-Apr-08		4:25:59		68.61		35.5

		28-Feb-08		6:07:10		65.6		50		28-Feb-08		6:06:20		65.6		45		28-Feb-08		6:07:53		69.2		41		9-Apr-08		6:25:59		69.2		36

		28-Feb-08		8:07:10		66.2		48		28-Feb-08		8:06:20		65.6		42.5		28-Feb-08		8:07:53		70.41		41.5		9-Apr-08		8:25:59		70.41		36.5

		28-Feb-08		10:07:10		66.2		47.5		28-Feb-08		10:06:20		67.4		46		28-Feb-08		10:07:53		71		39		9-Apr-08		10:25:59		72.8		35.5

		28-Feb-08		12:07:10		66.81		49		28-Feb-08		12:06:20		68		48		28-Feb-08		12:07:53		71		41		9-Apr-08		12:25:59		74.01		35

		28-Feb-08		14:07:10		66.81		49.5		28-Feb-08		14:06:20		68.61		47		28-Feb-08		14:07:53		71		40		9-Apr-08		14:25:59		74.01		34

		28-Feb-08		16:07:10		66.81		51.5		28-Feb-08		16:06:20		67.4		56		28-Feb-08		16:07:53		71		51.5		9-Apr-08		16:25:59		74.01		34.5

		28-Feb-08		18:07:10		66.2		51.5		28-Feb-08		18:06:20		68		49.5		28-Feb-08		18:07:53		71		52		9-Apr-08		18:25:59		74.01		34.5

		28-Feb-08		20:07:10		66.2		48.5		28-Feb-08		20:06:20		66.81		53		28-Feb-08		20:07:53		71.6		47		9-Apr-08		20:25:59		72.8		33.5

		28-Feb-08		22:07:10		66.2		50		28-Feb-08		22:06:20		67.4		49.5		28-Feb-08		22:07:53		72.21		44		9-Apr-08		22:25:59		71		33.5

		29-Feb-08		0:07:10		65.6		49		29-Feb-08		0:06:20		66.81		48		29-Feb-08		0:07:53		71.6		42.5		10-Apr-08		0:25:59		69.2		33.5

		29-Feb-08		2:07:10		65.6		49		29-Feb-08		2:06:20		66.2		46		29-Feb-08		2:07:53		70.41		41.5		10-Apr-08		2:25:59		68		34.5

		29-Feb-08		4:07:10		66.2		49		29-Feb-08		4:06:20		65.01		44.5		29-Feb-08		4:07:53		69.2		40.5		10-Apr-08		4:25:59		66.81		35

		29-Feb-08		6:07:10		65.6		48.5		29-Feb-08		6:06:20		65.01		42		29-Feb-08		6:07:53		68.61		39.5		10-Apr-08		6:25:59		68		34.5

		29-Feb-08		8:07:10		66.2		48		29-Feb-08		8:06:20		65.01		40		29-Feb-08		8:07:53		71		38		10-Apr-08		8:25:59		69.2		35

		29-Feb-08		10:07:10		66.2		48		29-Feb-08		10:06:20		66.81		45.5		29-Feb-08		10:07:53		72.21		42.5		10-Apr-08		10:25:59		72.21		36

		29-Feb-08		12:07:10		66.81		48.5		29-Feb-08		12:06:20		66.81		47.5		29-Feb-08		12:07:53		71.6		47		10-Apr-08		12:25:59		74.01		35.5

		29-Feb-08		14:07:10		66.81		50.5		29-Feb-08		14:06:20		68.61		47.5		29-Feb-08		14:07:53		71		45		10-Apr-08		14:25:59		74.6		36.5

		29-Feb-08		16:07:10		66.81		51.5		29-Feb-08		16:06:20		68		45.5		29-Feb-08		16:07:53		70.41		44		10-Apr-08		16:25:59		74.01		37

		29-Feb-08		18:07:10		66.2		52		29-Feb-08		18:06:20		67.4		54		29-Feb-08		18:07:53		71		52		10-Apr-08		18:25:59		73.4		34.5

		29-Feb-08		20:07:10		66.2		49		29-Feb-08		20:06:20		67.4		48.5		29-Feb-08		20:07:53		69.8		50		10-Apr-08		20:25:59		72.8		35

		29-Feb-08		22:07:10		65.6		50		29-Feb-08		22:06:20		66.81		49.5		29-Feb-08		22:07:53		71.6		44.5		10-Apr-08		22:25:59		71.6		35

		1-Mar-08		0:07:10		65.6		48.5		1-Mar-08		0:06:20		66.81		47		1-Mar-08		0:07:53		71.6		42		11-Apr-08		0:25:59		70.41		35.5

		1-Mar-08		2:07:10		65.6		48.5		1-Mar-08		2:06:20		66.2		49		1-Mar-08		2:07:53		71		42		11-Apr-08		2:25:59		69.2		35

		1-Mar-08		4:07:10		65.6		49.5		1-Mar-08		4:06:20		66.2		48.5		1-Mar-08		4:07:53		70.41		42.5		11-Apr-08		4:25:59		68.61		35.5

		1-Mar-08		6:07:10		65.6		49		1-Mar-08		6:06:20		65.6		48		1-Mar-08		6:07:53		70.41		42.5		11-Apr-08		6:25:59		69.2		35.5

		1-Mar-08		8:07:10		66.2		48.5		1-Mar-08		8:06:20		66.2		46.5		1-Mar-08		8:07:53		71		43.5		11-Apr-08		8:25:59		71		36

		1-Mar-08		10:07:10		66.2		48.5		1-Mar-08		10:06:20		67.4		45		1-Mar-08		10:07:53		71		46		11-Apr-08		10:25:59		72.8		36.5

		1-Mar-08		12:07:10		66.81		49.5		1-Mar-08		12:06:20		66.81		49.5		1-Mar-08		12:07:53		71		48		11-Apr-08		12:25:59		74.6		36.5

		1-Mar-08		14:07:10		66.81		49		1-Mar-08		14:06:20		68		51.5		1-Mar-08		14:07:53		71		40		11-Apr-08		14:25:59		74.6		36

		1-Mar-08		16:07:10		66.81		51.5		1-Mar-08		16:06:20		68		56		1-Mar-08		16:07:53		71		51.5		11-Apr-08		16:25:59		74.6		36.5

		1-Mar-08		18:07:10		66.2		49		1-Mar-08		18:06:20		66.81		50.5		1-Mar-08		18:07:53		70.41		48.5		11-Apr-08		18:25:59		74.01		36

		1-Mar-08		20:07:10		65.6		49.5		1-Mar-08		20:06:20		66.81		49		1-Mar-08		20:07:53		69.8		46.5		11-Apr-08		20:25:59		74.01		36

		1-Mar-08		22:07:10		65.6		49		1-Mar-08		22:06:20		66.81		47		1-Mar-08		22:07:53		69.8		44		11-Apr-08		22:25:59		72.8		36.5

		2-Mar-08		0:07:10		65.6		49		2-Mar-08		0:06:20		66.81		48.5		2-Mar-08		0:07:53		69.8		43.5		12-Apr-08		0:25:59		71.6		37

		2-Mar-08		2:07:10		65.6		49		2-Mar-08		2:06:20		66.81		48.5		2-Mar-08		2:07:53		69.8		43.5		12-Apr-08		2:25:59		69.8		37

		2-Mar-08		4:07:10		65.6		49		2-Mar-08		4:06:20		66.2		48.5		2-Mar-08		4:07:53		69.2		43.5		12-Apr-08		4:25:59		69.2		37.5

		2-Mar-08		6:07:10		65.6		49		2-Mar-08		6:06:20		66.2		48		2-Mar-08		6:07:53		69.2		43.5		12-Apr-08		6:25:59		69.8		37

		2-Mar-08		8:07:10		65.6		49		2-Mar-08		8:06:20		66.81		45		2-Mar-08		8:07:53		71.6		41		12-Apr-08		8:25:59		71		37

		2-Mar-08		10:07:10		66.2		48.5		2-Mar-08		10:06:20		68		42		2-Mar-08		10:07:53		71		36.5		12-Apr-08		10:25:59		73.4		39

		2-Mar-08		12:07:10		66.2		49		2-Mar-08		12:06:20		67.4		35.5		2-Mar-08		12:07:53		70.41		40.5		12-Apr-08		12:25:59		74.6		38.5

		2-Mar-08		14:07:10		65.6		48		2-Mar-08		14:06:20		66.81		34.5		2-Mar-08		14:07:53		71		36.5		12-Apr-08		14:25:59		75.2		36.5

		2-Mar-08		16:07:10		65.6		47		2-Mar-08		16:06:20		67.4		35.5		2-Mar-08		16:07:53		70.41		35		12-Apr-08		16:25:59		74.6		36

		2-Mar-08		18:07:10		65.6		48.5		2-Mar-08		18:06:20		66.2		34.5		2-Mar-08		18:07:53		69.8		34.5		12-Apr-08		18:25:59		74.01		35

		2-Mar-08		20:07:10		65.6		47.5		2-Mar-08		20:06:20		66.2		36.5		2-Mar-08		20:07:53		69.8		35.5		12-Apr-08		20:25:59		73.4		33

		2-Mar-08		22:07:10		65.6		48		2-Mar-08		22:06:20		66.81		37.5		2-Mar-08		22:07:53		69.2		36.5		12-Apr-08		22:25:59		72.8		34.5

		3-Mar-08		0:07:10		65.6		47		3-Mar-08		0:06:20		66.2		37		3-Mar-08		0:07:53		68.61		36.5		13-Apr-08		0:25:59		71.6		35.5

		3-Mar-08		2:07:10		65.6		46.5		3-Mar-08		2:06:20		65.6		35		3-Mar-08		2:07:53		68		36.5		13-Apr-08		2:25:59		70.41		36.5

		3-Mar-08		4:07:10		65.6		49.5		3-Mar-08		4:06:20		65.01		34.5		3-Mar-08		4:07:53		67.4		36		13-Apr-08		4:25:59		69.8		36.5

		3-Mar-08		6:07:10		65.6		48.5		3-Mar-08		6:06:20		65.01		33		3-Mar-08		6:07:53		66.81		36		13-Apr-08		6:25:59		69.8		36.5

		3-Mar-08		8:07:10		66.2		47.5		3-Mar-08		8:06:20		65.01		32.5		3-Mar-08		8:07:53		67.4		34.5		13-Apr-08		8:25:59		69.8		36.5

		3-Mar-08		10:07:10		65.01		47		3-Mar-08		10:06:20		66.2		30.5		3-Mar-08		10:07:53		68		34		13-Apr-08		10:25:59		71.6		38.5

		3-Mar-08		12:07:10		65.6		48		3-Mar-08		12:06:20		67.4		27.5		3-Mar-08		12:07:53		69.2		31.5		13-Apr-08		12:25:59		74.01		37.5

		3-Mar-08		14:07:10		66.2		44.5		3-Mar-08		14:06:20		68		21.5		3-Mar-08		14:07:53		69.8		29		13-Apr-08		14:25:59		74.01		37.5

		3-Mar-08		16:07:10		66.2		44.5		3-Mar-08		16:06:20		68		19		3-Mar-08		16:07:53		69.8		29		13-Apr-08		16:25:59		72.8		38

		3-Mar-08		18:07:10		66.2		45		3-Mar-08		18:06:20		67.4		19		3-Mar-08		18:07:53		69.2		29.5		13-Apr-08		18:25:59		72.8		37.5

		3-Mar-08		20:07:10		65.6		46		3-Mar-08		20:06:20		66.81		19.5		3-Mar-08		20:07:53		70.41		28		13-Apr-08		20:25:59		72.8		37

		3-Mar-08		22:07:10		65.6		47.5		3-Mar-08		22:06:20		67.4		26		3-Mar-08		22:07:53		70.41		29.5		13-Apr-08		22:25:59		72.8		39.5

		4-Mar-08		0:07:10		65.6		48		4-Mar-08		0:06:20		66.2		34		4-Mar-08		0:07:53		69.8		32		14-Apr-08		0:25:59		71.6		39.5

		4-Mar-08		2:07:10		65.6		48.5		4-Mar-08		2:06:20		65.6		35.5		4-Mar-08		2:07:53		69.2		33.5		14-Apr-08		2:25:59		71		39

		4-Mar-08		4:07:10		65.6		46.5		4-Mar-08		4:06:20		65.01		35.5		4-Mar-08		4:07:53		68		34		14-Apr-08		4:25:59		69.8		38.5

		4-Mar-08		6:07:10		66.2		47.5		4-Mar-08		6:06:20		64.4		35		4-Mar-08		6:07:53		67.4		34.5		14-Apr-08		6:25:59		69.2		38.5

		4-Mar-08		8:07:10		66.2		47.5		4-Mar-08		8:06:20		65.01		34		4-Mar-08		8:07:53		69.2		34		14-Apr-08		8:25:59		68.61		39

		4-Mar-08		10:07:10		66.2		46		4-Mar-08		10:06:20		67.4		35.5		4-Mar-08		10:07:53		72.21		36		14-Apr-08		10:25:59		71		40.5

		4-Mar-08		12:07:10		66.81		47		4-Mar-08		12:06:20		68		34.5		4-Mar-08		12:07:53		71		40.5		14-Apr-08		12:25:59		72.8		40

		4-Mar-08		14:07:10		66.81		46		4-Mar-08		14:06:20		68		29		4-Mar-08		14:07:53		71		40		14-Apr-08		14:25:59		74.01		39

		4-Mar-08		16:07:10		66.81		47		4-Mar-08		16:06:20		68.61		31		4-Mar-08		16:07:53		70.41		37		14-Apr-08		16:25:59		74.01		39

		4-Mar-08		18:07:10		66.2		47.5		4-Mar-08		18:06:20		68		30		4-Mar-08		18:07:53		70.41		34.5		14-Apr-08		18:25:59		72.8		39.5

		4-Mar-08		20:07:10		66.2		45.5		4-Mar-08		20:06:20		67.4		30		4-Mar-08		20:07:53		69.8		34		14-Apr-08		20:25:59		72.8		40

		4-Mar-08		22:07:10		65.6		48		4-Mar-08		22:06:20		66.2		32		4-Mar-08		22:07:53		70.41		34		14-Apr-08		22:25:59		71.6		39.5

		5-Mar-08		0:07:10		65.6		47		5-Mar-08		0:06:20		67.4		33		5-Mar-08		0:07:53		71		33.5		15-Apr-08		0:25:59		71		39.5

		5-Mar-08		2:07:10		65.6		47.5		5-Mar-08		2:06:20		65.6		34.5		5-Mar-08		2:07:53		69.8		33.5		15-Apr-08		2:25:59		69.8		39

		5-Mar-08		4:07:10		65.6		48.5		5-Mar-08		4:06:20		65.01		35.5		5-Mar-08		4:07:53		68.61		33.5		15-Apr-08		4:25:59		68.61		39

		5-Mar-08		6:07:10		66.2		49		5-Mar-08		6:06:20		64.4		35		5-Mar-08		6:07:53		67.4		34		15-Apr-08		6:25:59		69.2		39

		5-Mar-08		8:07:10		66.2		47		5-Mar-08		8:06:20		65.01		34.5		5-Mar-08		8:07:53		69.8		33		15-Apr-08		8:25:59		70.41		39.5

		5-Mar-08		10:07:10		66.2		46		5-Mar-08		10:06:20		66.81		37.5		5-Mar-08		10:07:53		72.21		34.5		15-Apr-08		10:25:59		72.8		40.5

		5-Mar-08		12:07:10		66.81		46.5		5-Mar-08		12:06:20		68		38		5-Mar-08		12:07:53		71		42.5		15-Apr-08		12:25:59		74.6		38.5

		5-Mar-08		14:07:10		66.81		47		5-Mar-08		14:06:20		68		38		5-Mar-08		14:07:53		71		36.5		15-Apr-08		14:25:59		74.6		37

		5-Mar-08		16:07:10		66.81		45.5		5-Mar-08		16:06:20		68		35.5		5-Mar-08		16:07:53		70.41		37		15-Apr-08		16:25:59		74.01		36.5

		5-Mar-08		18:07:10		66.81		47.5		5-Mar-08		18:06:20		68		38.5		5-Mar-08		18:07:53		69.8		43		15-Apr-08		18:25:59		73.4		35

		5-Mar-08		20:07:10		66.2		48		5-Mar-08		20:06:20		67.4		42		5-Mar-08		20:07:53		70.41		41.5		15-Apr-08		20:25:59		72.21		34

		5-Mar-08		22:07:10		66.2		48		5-Mar-08		22:06:20		67.4		36.5		5-Mar-08		22:07:53		70.41		39		15-Apr-08		22:25:59		71		33.5

		6-Mar-08		0:07:10		65.6		48.5		6-Mar-08		0:06:20		66.2		38		6-Mar-08		0:07:53		70.41		36.5		16-Apr-08		0:25:59		69.2		33.5

		6-Mar-08		2:07:10		65.6		48.5		6-Mar-08		2:06:20		65.6		38		6-Mar-08		2:07:53		69.8		36		16-Apr-08		2:25:59		68		34

		6-Mar-08		4:07:10		65.6		48.5		6-Mar-08		4:06:20		65.01		37.5		6-Mar-08		4:07:53		68.61		36		16-Apr-08		4:25:59		67.4		35

		6-Mar-08		6:07:10		66.2		48.5		6-Mar-08		6:06:20		65.01		36		6-Mar-08		6:07:53		67.4		36		16-Apr-08		6:25:59		68		34

		6-Mar-08		8:07:10		66.2		47.5		6-Mar-08		8:06:20		65.01		35		6-Mar-08		8:07:53		70.41		34.5		16-Apr-08		8:25:59		70.41		34.5

		6-Mar-08		10:07:10		66.81		46		6-Mar-08		10:06:20		67.4		36.5		6-Mar-08		10:07:53		71.6		35		16-Apr-08		10:25:59		72.8		35

		6-Mar-08		12:07:10		66.81		46.5		6-Mar-08		12:06:20		68		34.5		6-Mar-08		12:07:53		70.41		44.5		16-Apr-08		12:25:59		74.6		34.5

		6-Mar-08		14:07:10		66.81		46.5		6-Mar-08		14:06:20		68.61		28		6-Mar-08		14:07:53		70.41		41		16-Apr-08		14:25:59		74.6		33.5

		6-Mar-08		16:07:10		66.81		43.5		6-Mar-08		16:06:20		68.61		25		6-Mar-08		16:07:53		70.41		39		16-Apr-08		16:25:59		74.01		33.5

		6-Mar-08		18:07:10		66.2		41.5		6-Mar-08		18:06:20		68		29.5		6-Mar-08		18:07:53		69.8		38.5		16-Apr-08		18:25:59		73.4		33

		6-Mar-08		20:07:10		66.2		48.5		6-Mar-08		20:06:20		66.81		37.5		6-Mar-08		20:07:53		71		37.5		16-Apr-08		20:25:59		72.8		32

		6-Mar-08		22:07:10		65.6		47		6-Mar-08		22:06:20		66.81		40		6-Mar-08		22:07:53		71.6		37		16-Apr-08		22:25:59		71.6		32

		7-Mar-08		0:07:10		65.6		48.5		7-Mar-08		0:06:20		66.2		39		7-Mar-08		0:07:53		70.41		36.5		17-Apr-08		0:25:59		69.8		32.5

		7-Mar-08		2:07:10		65.6		48.5		7-Mar-08		2:06:20		65.01		38		7-Mar-08		2:07:53		69.2		36		17-Apr-08		2:25:59		68.61		34

		7-Mar-08		4:07:10		65.6		42.5		7-Mar-08		4:06:20		64.4		37.5		7-Mar-08		4:07:53		68.61		36		17-Apr-08		4:25:59		68		34.5

		7-Mar-08		6:07:10		65.6		47		7-Mar-08		6:06:20		63.8		36.5		7-Mar-08		6:07:53		67.4		36		17-Apr-08		6:25:59		69.2		34

		7-Mar-08		8:07:10		66.2		48		7-Mar-08		8:06:20		65.01		35.5		7-Mar-08		8:07:53		70.41		35		17-Apr-08		8:25:59		71		34.5

		7-Mar-08		10:07:10		65.6		46.5		7-Mar-08		10:06:20		66.81		37.5		7-Mar-08		10:07:53		71.6		33.5		17-Apr-08		10:25:59		74.01		35

		7-Mar-08		12:07:10		66.2		48		7-Mar-08		12:06:20		67.4		39.5		7-Mar-08		12:07:53		71		39.5		17-Apr-08		12:25:59		75.2		34.5

		7-Mar-08		14:07:10		66.2		43.5		7-Mar-08		14:06:20		68		39		7-Mar-08		14:07:53		71.6		38.5		17-Apr-08		14:25:59		75.2		34.5

		7-Mar-08		16:07:10		66.81		47.5		7-Mar-08		16:06:20		68		40		7-Mar-08		16:07:53		70.41		36.5		17-Apr-08		16:25:59		74.6		34.5

		7-Mar-08		18:07:10		66.2		48		7-Mar-08		18:06:20		68		36.5		7-Mar-08		18:07:53		70.41		35		17-Apr-08		18:25:59		74.01		34

		7-Mar-08		20:07:10		66.2		48		7-Mar-08		20:06:20		66.81		40.5		7-Mar-08		20:07:53		69.8		36		17-Apr-08		20:25:59		74.01		35

		7-Mar-08		22:07:10		65.6		48.5		7-Mar-08		22:06:20		66.81		39		7-Mar-08		22:07:53		70.41		38		17-Apr-08		22:25:59		73.4		35

		8-Mar-08		0:07:10		65.6		43		8-Mar-08		0:06:20		66.2		40.5		8-Mar-08		0:07:53		69.8		37		18-Apr-08		0:25:59		71.6		35

		8-Mar-08		2:07:10		65.6		48.5		8-Mar-08		2:06:20		65.01		41.5		8-Mar-08		2:07:53		69.2		37		18-Apr-08		2:25:59		70.41		36

		8-Mar-08		4:07:10		65.6		48		8-Mar-08		4:06:20		64.4		39.5		8-Mar-08		4:07:53		68		37		18-Apr-08		4:25:59		69.2		36

		8-Mar-08		6:07:10		65.6		48.5		8-Mar-08		6:06:20		63.8		38.5		8-Mar-08		6:07:53		67.4		36.5		18-Apr-08		6:25:59		69.8		36

		8-Mar-08		8:07:10		66.2		47.5		8-Mar-08		8:06:20		65.6		37		8-Mar-08		8:07:53		69.2		36		18-Apr-08		8:25:59		71.6		36

		8-Mar-08		10:07:10		66.2		42		8-Mar-08		10:06:20		67.4		39.5		8-Mar-08		10:07:53		71		38.5		18-Apr-08		10:25:59		74.01		37.5

		8-Mar-08		12:07:10		66.2		48		8-Mar-08		12:06:20		68		38.5		8-Mar-08		12:07:53		70.41		43		18-Apr-08		12:25:59		75.2		39

		8-Mar-08		14:07:10		66.2		47		8-Mar-08		14:06:20		67.4		38.5		8-Mar-08		14:07:53		71		36		18-Apr-08		14:25:59		75.2		38

		8-Mar-08		16:07:10		66.2		48		8-Mar-08		16:06:20		67.4		40		8-Mar-08		16:07:53		70.41		42		18-Apr-08		16:25:59		75.2		38

		8-Mar-08		18:07:10		66.2		49		8-Mar-08		18:06:20		67.4		44		8-Mar-08		18:07:53		70.41		42		18-Apr-08		18:25:59		74.6		37

		8-Mar-08		20:07:10		65.6		43.5		8-Mar-08		20:06:20		66.81		41.5		8-Mar-08		20:07:53		69.8		40		18-Apr-08		20:25:59		74.6		38

		8-Mar-08		22:07:10		65.6		48.5		8-Mar-08		22:06:20		66.2		45.5		8-Mar-08		22:07:53		70.41		40.5		18-Apr-08		22:25:59		73.4		37.5

		9-Mar-08		0:07:10		65.6		48.5		9-Mar-08		0:06:20		66.81		44.5		9-Mar-08		0:07:53		70.41		40		19-Apr-08		0:25:59		71.6		37.5

		9-Mar-08		2:07:10		65.6		47		9-Mar-08		2:06:20		66.2		43.5		9-Mar-08		2:07:53		69.8		39		19-Apr-08		2:25:59		71		38.5

		9-Mar-08		4:07:10		65.6		48		9-Mar-08		4:06:20		65.01		42.5		9-Mar-08		4:07:53		69.2		38.5		19-Apr-08		4:25:59		70.41		39.5

		9-Mar-08		6:07:10		65.6		42		9-Mar-08		6:06:20		64.4		42		9-Mar-08		6:07:53		68.61		38.5		19-Apr-08		6:25:59		71.6		39.5

		9-Mar-08		8:07:10		65.6		48		9-Mar-08		8:06:20		65.01		39		9-Mar-08		8:07:53		71		37		19-Apr-08		8:25:59		72.21		39

		9-Mar-08		10:07:10		66.2		48.5		9-Mar-08		10:06:20		66.81		43.5		9-Mar-08		10:07:53		71		34.5		19-Apr-08		10:25:59		73.4		40

		9-Mar-08		12:07:10		66.2		48.5		9-Mar-08		12:06:20		67.4		43		9-Mar-08		12:07:53		71.6		46		19-Apr-08		12:25:59		74.01		40.5

		9-Mar-08		14:07:10		66.2		47.5		9-Mar-08		14:06:20		68		35		9-Mar-08		14:07:53		71		43		19-Apr-08		14:25:59		75.2		41

		9-Mar-08		16:07:10		66.2		44		9-Mar-08		16:06:20		67.4		37.5		9-Mar-08		16:07:53		71		36.5		19-Apr-08		16:25:59		74.6		39.5

		9-Mar-08		18:07:10		66.2		47.5		9-Mar-08		18:06:20		67.4		31.5		9-Mar-08		18:07:53		69.8		36		19-Apr-08		18:25:59		74.01		38.5

		9-Mar-08		20:07:10		66.2		47.5		9-Mar-08		20:06:20		67.4		44.5		9-Mar-08		20:07:53		69.8		42		19-Apr-08		20:25:59		74.01		38.5

		9-Mar-08		22:07:10		65.6		48.5		9-Mar-08		22:06:20		66.2		47.5		9-Mar-08		22:07:53		71.6		40		19-Apr-08		22:25:59		72.8		37.5

		10-Mar-08		0:07:10		65.6		48.5		10-Mar-08		0:06:20		66.81		44.5		10-Mar-08		0:07:53		71		39.5		20-Apr-08		0:25:59		71		38

		10-Mar-08		2:07:10		65.6		48		10-Mar-08		2:06:20		66.2		44.5		10-Mar-08		2:07:53		70.41		39		20-Apr-08		2:25:59		69.8		38

		10-Mar-08		4:07:10		65.6		49		10-Mar-08		4:06:20		65.01		44		10-Mar-08		4:07:53		69.8		38.5		20-Apr-08		4:25:59		68.61		37.5

		10-Mar-08		6:07:10		65.6		49.5		10-Mar-08		6:06:20		64.4		42		10-Mar-08		6:07:53		68.61		38.5		20-Apr-08		6:25:59		68		37.5

		10-Mar-08		8:07:10		65.6		48		10-Mar-08		8:06:20		63.8		40.5		10-Mar-08		8:07:53		68		38		20-Apr-08		8:25:59		67.4		36.5

		10-Mar-08		10:07:10		65.6		48		10-Mar-08		10:06:20		66.2		41.5		10-Mar-08		10:07:53		69.2		39		20-Apr-08		10:25:59		68		37.5

		10-Mar-08		12:07:10		65.6		49		10-Mar-08		12:06:20		66.81		41		10-Mar-08		12:07:53		69.8		40		20-Apr-08		12:25:59		69.2		36.5

		10-Mar-08		14:07:10		66.2		47.5		10-Mar-08		14:06:20		68		37.5		10-Mar-08		14:07:53		70.41		41		20-Apr-08		14:25:59		70.41		33.5

		10-Mar-08		16:07:10		66.2		48		10-Mar-08		16:06:20		68		34.5		10-Mar-08		16:07:53		69.8		41.5		20-Apr-08		16:25:59		70.41		33

		10-Mar-08		18:07:10		66.2		48		10-Mar-08		18:06:20		68		33.5		10-Mar-08		18:07:53		70.41		39.5		20-Apr-08		18:25:59		70.41		32

		10-Mar-08		20:07:10		66.2		48		10-Mar-08		20:06:20		67.4		43		10-Mar-08		20:07:53		71		42		20-Apr-08		20:25:59		69.8		32

		10-Mar-08		22:07:10		65.6		49		10-Mar-08		22:06:20		66.2		45		10-Mar-08		22:07:53		71.6		40.5		20-Apr-08		22:25:59		68.61		33

		11-Mar-08		0:07:10		65.6		49		11-Mar-08		0:06:20		66.81		44.5		11-Mar-08		0:07:53		71		39.5		21-Apr-08		0:25:59		67.4		33.5

		11-Mar-08		2:07:10		65.6		49		11-Mar-08		2:06:20		66.2		45		11-Mar-08		2:07:53		70.41		39.5		21-Apr-08		2:25:59		66.81		34

		11-Mar-08		4:07:10		65.6		48.5		11-Mar-08		4:06:20		65.6		45		11-Mar-08		4:07:53		69.8		39		21-Apr-08		4:25:59		65.6		35

		11-Mar-08		6:07:10		65.6		48		11-Mar-08		6:06:20		65.01		45		11-Mar-08		6:07:53		71		39.5		21-Apr-08		6:25:59		65.01		35.5

		11-Mar-08		8:07:10		66.2		48		11-Mar-08		8:06:20		66.81		43		11-Mar-08		8:07:53		71.6		35.5		21-Apr-08		8:25:59		64.4		36.5

		11-Mar-08		10:07:10		66.81		47.5		11-Mar-08		10:06:20		67.4		43.5		11-Mar-08		10:07:53		71		37		21-Apr-08		10:25:59		65.6		37.5

		11-Mar-08		12:07:10		66.2		48		11-Mar-08		12:06:20		67.4		44		11-Mar-08		12:07:53		71		43		21-Apr-08		12:25:59		66.81		36

		11-Mar-08		14:07:10		66.81		52.5		11-Mar-08		14:06:20		68.61		52		11-Mar-08		14:07:53		70.41		48.5		21-Apr-08		14:25:59		68.61		36

		11-Mar-08		16:07:10		66.2		49.5		11-Mar-08		16:06:20		67.4		49		11-Mar-08		16:07:53		70.41		53		21-Apr-08		16:25:59		69.8		34.5

		11-Mar-08		18:07:10		66.2		49		11-Mar-08		18:06:20		68		45		11-Mar-08		18:07:53		71		42		21-Apr-08		18:25:59		69.8		33

		11-Mar-08		20:07:10		65.6		48.5		11-Mar-08		20:06:20		66.81		46		11-Mar-08		20:07:53		70.41		43		21-Apr-08		20:25:59		69.2		33

		11-Mar-08		22:07:10		65.6		48.5		11-Mar-08		22:06:20		67.4		45.5		11-Mar-08		22:07:53		71		42		21-Apr-08		22:25:59		68.61		34.5

		12-Mar-08		0:07:10		65.6		49		12-Mar-08		0:06:20		66.81		45.5		12-Mar-08		0:07:53		71.6		40.5		22-Apr-08		0:25:59		67.4		34.5

		12-Mar-08		2:07:10		65.6		49		12-Mar-08		2:06:20		66.81		45		12-Mar-08		2:07:53		70.41		40.5		22-Apr-08		2:25:59		66.2		35

		12-Mar-08		4:07:10		65.6		49		12-Mar-08		4:06:20		65.6		44.5		12-Mar-08		4:07:53		69.8		39.5		22-Apr-08		4:25:59		65.6		36

		12-Mar-08		6:07:10		65.6		49		12-Mar-08		6:06:20		65.01		44		12-Mar-08		6:07:53		70.41		39.5		22-Apr-08		6:25:59		66.81		34

		12-Mar-08		8:07:10		66.2		48		12-Mar-08		8:06:20		66.2		42.5		12-Mar-08		8:07:53		71		40.5		22-Apr-08		8:25:59		68		34.5

		12-Mar-08		10:07:10		66.2		49		12-Mar-08		10:06:20		66.81		50		12-Mar-08		10:07:53		70.41		45		22-Apr-08		10:25:59		72.21		36

		12-Mar-08		12:07:10		66.2		50		12-Mar-08		12:06:20		66.81		48		12-Mar-08		12:07:53		71.6		50		22-Apr-08		12:25:59		73.4		35.5

		12-Mar-08		14:07:10		66.2		49.5		12-Mar-08		14:06:20		68		50.5		12-Mar-08		14:07:53		71		41.5		22-Apr-08		14:25:59		73.4		35.5

		12-Mar-08		16:07:10		66.2		51.5		12-Mar-08		16:06:20		66.81		59.5		12-Mar-08		16:07:53		71		50.5		22-Apr-08		16:25:59		73.4		35.5

		12-Mar-08		18:07:10		66.2		51.5		12-Mar-08		18:06:20		67.4		48.5		12-Mar-08		18:07:53		70.41		50		22-Apr-08		18:25:59		72.8		35

		12-Mar-08		20:07:10		65.6		50		12-Mar-08		20:06:20		67.4		51.5		12-Mar-08		20:07:53		70.41		48		22-Apr-08		20:25:59		72.21		34.5

		12-Mar-08		22:07:10		65.6		49		12-Mar-08		22:06:20		67.4		49		12-Mar-08		22:07:53		70.41		44.5		22-Apr-08		22:25:59		71		34

		13-Mar-08		0:07:10		65.6		49		13-Mar-08		0:06:20		66.81		47.5		13-Mar-08		0:07:53		70.41		42		23-Apr-08		0:25:59		69.8		34

		13-Mar-08		2:07:10		65.6		49		13-Mar-08		2:06:20		65.6		46		13-Mar-08		2:07:53		70.41		41		23-Apr-08		2:25:59		68.61		34.5

		13-Mar-08		4:07:10		65.6		49.5		13-Mar-08		4:06:20		65.01		47		13-Mar-08		4:07:53		69.2		41		23-Apr-08		4:25:59		67.4		35

		13-Mar-08		6:07:10		65.6		49		13-Mar-08		6:06:20		65.6		48.5		13-Mar-08		6:07:53		70.41		42.5		23-Apr-08		6:25:59		68.61		34.5

		13-Mar-08		8:07:10		66.2		48		13-Mar-08		8:06:20		67.4		46.5		13-Mar-08		8:07:53		71		44		23-Apr-08		8:25:59		70.41		34.5

		13-Mar-08		10:07:10		66.2		48		13-Mar-08		10:06:20		66.81		46.5		13-Mar-08		10:07:53		71.6		41.5		23-Apr-08		10:25:59		71.6		35.5

		13-Mar-08		12:07:10		66.2		48.5		13-Mar-08		12:06:20		66.81		47.5		13-Mar-08		12:07:53		71		43		23-Apr-08		12:25:59		72.21		37.5

		13-Mar-08		14:07:10		66.81		49		13-Mar-08		14:06:20		67.4		46.5		13-Mar-08		14:07:53		71		46.5		23-Apr-08		14:25:59		72.8		39

		13-Mar-08		16:07:10		66.81		49.5		13-Mar-08		16:06:20		67.4		52		13-Mar-08		16:07:53		70.41		41.5		23-Apr-08		16:25:59		73.4		40.5

		13-Mar-08		18:07:10		66.2		49		13-Mar-08		18:06:20		66.81		49		13-Mar-08		18:07:53		71		44.5		23-Apr-08		18:25:59		73.4		40.5

		13-Mar-08		20:07:10		66.2		48.5		13-Mar-08		20:06:20		66.2		48		13-Mar-08		20:07:53		71		43.5		23-Apr-08		20:25:59		72.8		41.5

		13-Mar-08		22:07:10		66.2		49		13-Mar-08		22:06:20		67.4		46.5		13-Mar-08		22:07:53		72.21		41.5		23-Apr-08		22:25:59		71.6		41.5

		14-Mar-08		0:07:10		66.2		49.5		14-Mar-08		0:06:20		67.4		51		14-Mar-08		0:07:53		71.6		42		24-Apr-08		0:25:59		70.41		42

		14-Mar-08		2:07:10		65.6		50.5		14-Mar-08		2:06:20		67.4		52		14-Mar-08		2:07:53		71.6		43		24-Apr-08		2:25:59		69.2		42

		14-Mar-08		4:07:10		65.6		50.5		14-Mar-08		4:06:20		66.81		53		14-Mar-08		4:07:53		71.6		43.5		24-Apr-08		4:25:59		68.61		42.5

		14-Mar-08		6:07:10		66.2		50.5		14-Mar-08		6:06:20		67.4		53.5		14-Mar-08		6:07:53		71		40.5		24-Apr-08		6:25:59		69.2		42

		14-Mar-08		8:07:10		66.2		49.5		14-Mar-08		8:06:20		66.81		52		14-Mar-08		8:07:53		70.41		50		24-Apr-08		8:25:59		71		42

		14-Mar-08		10:07:10		66.2		51		14-Mar-08		10:06:20		67.4		52.5		14-Mar-08		10:07:53		71		51.5		24-Apr-08		10:25:59		72.8		43

		14-Mar-08		12:07:10		66.2		49.5		14-Mar-08		12:06:20		68		48		14-Mar-08		12:07:53		71		50.5		24-Apr-08		12:25:59		74.01		43

		14-Mar-08		14:07:10		66.81		48.5		14-Mar-08		14:06:20		68.61		47.5		14-Mar-08		14:07:53		71		52.5		24-Apr-08		14:25:59		74.01		40.5

		14-Mar-08		16:07:10		66.2		48		14-Mar-08		16:06:20		68		45.5		14-Mar-08		16:07:53		70.41		44		24-Apr-08		16:25:59		74.01		38.5

		14-Mar-08		18:07:10		65.6		48.5		14-Mar-08		18:06:20		66.81		46		14-Mar-08		18:07:53		70.41		43		24-Apr-08		18:25:59		72.8		36.5

		14-Mar-08		20:07:10		65.6		48.5		14-Mar-08		20:06:20		67.4		45		14-Mar-08		20:07:53		69.8		43		24-Apr-08		20:25:59		72.8		36.5

		14-Mar-08		22:07:10		65.6		48.5		14-Mar-08		22:06:20		67.4		45.5		14-Mar-08		22:07:53		71		41		24-Apr-08		22:25:59		71.6		35

		15-Mar-08		0:07:10		65.6		49		15-Mar-08		0:06:20		66.2		45		15-Mar-08		0:07:53		70.41		40.5		25-Apr-08		0:25:59		69.8		35

		15-Mar-08		2:07:10		65.6		49		15-Mar-08		2:06:20		65.6		44		15-Mar-08		2:07:53		69.8		39.5		25-Apr-08		2:25:59		68		35.5

		15-Mar-08		4:07:10		65.6		49		15-Mar-08		4:06:20		65.01		42.5		15-Mar-08		4:07:53		69.2		39		25-Apr-08		4:25:59		66.81		37

		15-Mar-08		6:07:10		66.2		48.5		15-Mar-08		6:06:20		65.6		44.5		15-Mar-08		6:07:53		69.2		42		25-Apr-08		6:25:59		68		36.5

		15-Mar-08		8:07:10		66.2		47.5		15-Mar-08		8:06:20		66.2		44		15-Mar-08		8:07:53		71		42		25-Apr-08		8:25:59		69.2		36.5

		15-Mar-08		10:07:10		66.81		48		15-Mar-08		10:06:20		67.4		46.5		15-Mar-08		10:07:53		71		47		25-Apr-08		10:25:59		72.8		38.5

		15-Mar-08		12:07:10		66.2		48		15-Mar-08		12:06:20		67.4		46.5		15-Mar-08		12:07:53		71		46.5		25-Apr-08		12:25:59		74.01		37

		15-Mar-08		14:07:10		66.2		48		15-Mar-08		14:06:20		67.4		41		15-Mar-08		14:07:53		71.6		44		25-Apr-08		14:25:59		74.6		36.5

		15-Mar-08		16:07:10		66.2		47.5		15-Mar-08		16:06:20		66.81		38		15-Mar-08		16:07:53		70.41		39.5		25-Apr-08		16:25:59		74.6		37.5

		15-Mar-08		18:07:10		65.6		48		15-Mar-08		18:06:20		66.81		40		15-Mar-08		18:07:53		69.8		38.5		25-Apr-08		18:25:59		74.01		35.5

		15-Mar-08		20:07:10		65.6		42.5		15-Mar-08		20:06:20		65.6		41		15-Mar-08		20:07:53		69.8		37.5		25-Apr-08		20:25:59		74.6		35.5

		15-Mar-08		22:07:10		65.6		49		15-Mar-08		22:06:20		65.01		41.5		15-Mar-08		22:07:53		69.2		37		25-Apr-08		22:25:59		74.01		35.5

		16-Mar-08		0:07:10		65.01		49		16-Mar-08		0:06:20		64.4		42		16-Mar-08		0:07:53		68.61		38		26-Apr-08		0:25:59		72.8		35

		16-Mar-08		2:07:10		65.01		50		16-Mar-08		2:06:20		63.8		43.5		16-Mar-08		2:07:53		68		38.5		26-Apr-08		2:25:59		71		36

		16-Mar-08		4:07:10		65.01		49		16-Mar-08		4:06:20		63.21		44		16-Mar-08		4:07:53		67.4		39		26-Apr-08		4:25:59		69.8		36.5

		16-Mar-08		6:07:10		65.01		49.5		16-Mar-08		6:06:20		63.21		43		16-Mar-08		6:07:53		68		39		26-Apr-08		6:25:59		70.41		37.5

		16-Mar-08		8:07:10		65.6		48		16-Mar-08		8:06:20		62		41.5		16-Mar-08		8:07:53		70.41		36.5		26-Apr-08		8:25:59		72.21		37

		16-Mar-08		10:07:10		65.6		49		16-Mar-08		10:06:20		64.4		44		16-Mar-08		10:07:53		71.6		38.5		26-Apr-08		10:25:59		74.01		38

		16-Mar-08		12:07:10		65.6		44		16-Mar-08		12:06:20		65.6		38		16-Mar-08		12:07:53		71		34		26-Apr-08		12:25:59		75.2		37.5

		16-Mar-08		14:07:10		65.6		38		16-Mar-08		14:06:20		66.2		34.5		16-Mar-08		14:07:53		70.41		33.5		26-Apr-08		14:25:59		73.4		34

		16-Mar-08		16:07:10		65.6		46		16-Mar-08		16:06:20		67.4		33		16-Mar-08		16:07:53		69.8		31.5		26-Apr-08		16:25:59		73.4		35.5

		16-Mar-08		18:07:10		65.6		41		16-Mar-08		18:06:20		66.2		36		16-Mar-08		18:07:53		69.2		34.5		26-Apr-08		18:25:59		73.4		37

		16-Mar-08		20:07:10		65.6		44		16-Mar-08		20:06:20		65.6		40		16-Mar-08		20:07:53		69.2		37		26-Apr-08		20:25:59		73.4		37

		16-Mar-08		22:07:10		65.6		48.5		16-Mar-08		22:06:20		65.6		37.5		16-Mar-08		22:07:53		68.61		36.5		26-Apr-08		22:25:59		72.8		36.5

		17-Mar-08		0:07:10		65.6		47.5		17-Mar-08		0:06:20		65.01		36		17-Mar-08		0:07:53		68		36		27-Apr-08		0:25:59		72.21		36.5

		17-Mar-08		2:07:10		65.6		47		17-Mar-08		2:06:20		64.4		34.5		17-Mar-08		2:07:53		67.4		35		27-Apr-08		2:25:59		71		36

		17-Mar-08		4:07:10		65.6		47.5		17-Mar-08		4:06:20		64.4		34		17-Mar-08		4:07:53		66.81		35		27-Apr-08		4:25:59		70.41		36.5

		17-Mar-08		6:07:10		65.01		38		17-Mar-08		6:06:20		64.4		34.5		17-Mar-08		6:07:53		66.2		35		27-Apr-08		6:25:59		69.8		36

		17-Mar-08		8:07:10		65.01		46.5		17-Mar-08		8:06:20		63.8		34.5		17-Mar-08		8:07:53		67.4		34.5		27-Apr-08		8:25:59		69.8		37.5

		17-Mar-08		10:07:10		65.6		38.5		17-Mar-08		10:06:20		65.01		34		17-Mar-08		10:07:53		68.61		33.5		27-Apr-08		10:25:59		71		40

		17-Mar-08		12:07:10		65.6		33.5		17-Mar-08		12:06:20		67.4		30		17-Mar-08		12:07:53		69.8		31.5		27-Apr-08		12:25:59		72.8		39.5

		17-Mar-08		14:07:10		65.6		42		17-Mar-08		14:06:20		66.81		23		17-Mar-08		14:07:53		69.8		30		27-Apr-08		14:25:59		74.01		38.5

		17-Mar-08		16:07:10		65.6		40		17-Mar-08		16:06:20		66.81		22		17-Mar-08		16:07:53		69.8		29		27-Apr-08		16:25:59		73.4		40.5

		17-Mar-08		18:07:10		65.6		36.5		17-Mar-08		18:06:20		66.2		31.5		17-Mar-08		18:07:53		69.8		31		27-Apr-08		18:25:59		73.4		40.5

		17-Mar-08		20:07:10		65.6		47.5		17-Mar-08		20:06:20		66.2		34.5		17-Mar-08		20:07:53		69.8		33		27-Apr-08		20:25:59		73.4		40.5

		17-Mar-08		22:07:10		65.6		47.5		17-Mar-08		22:06:20		66.81		35		17-Mar-08		22:07:53		70.41		34		27-Apr-08		22:25:59		73.4		38.5

		18-Mar-08		0:07:10		65.6		48		18-Mar-08		0:06:20		66.2		36		18-Mar-08		0:07:53		69.8		33.5		28-Apr-08		0:25:59		72.8		37.5

		18-Mar-08		2:07:10		65.6		39		18-Mar-08		2:06:20		65.01		37		18-Mar-08		2:07:53		68.61		34		28-Apr-08		2:25:59		72.21		39.5

		18-Mar-08		4:07:10		65.6		48		18-Mar-08		4:06:20		65.01		37.5		18-Mar-08		4:07:53		68		35		28-Apr-08		4:25:59		71.6		39.5

		18-Mar-08		6:07:10		66.2		47		18-Mar-08		6:06:20		65.01		37.5		18-Mar-08		6:07:53		69.2		34.5		28-Apr-08		6:25:59		70.41		39.5

		18-Mar-08		8:07:10		66.81		42		18-Mar-08		8:06:20		66.2		36.5		18-Mar-08		8:07:53		71.6		34.5		28-Apr-08		8:25:59		69.8		39.5

		18-Mar-08		10:07:10		66.2		38.5		18-Mar-08		10:06:20		67.4		35.5		18-Mar-08		10:07:53		71.6		39.5		28-Apr-08		10:25:59		71.6		41.5

		18-Mar-08		12:07:10		66.2		42		18-Mar-08		12:06:20		66.81		34.5		18-Mar-08		12:07:53		71.6		37		28-Apr-08		12:25:59		74.01		40

		18-Mar-08		14:07:10		66.81		46		18-Mar-08		14:06:20		66.2		39		18-Mar-08		14:07:53		71.6		34.5		28-Apr-08		14:25:59		74.01		39.5

		18-Mar-08		16:07:10		66.81		47.5		18-Mar-08		16:06:20		65.6		45		18-Mar-08		16:07:53		71.6		40		28-Apr-08		16:25:59		73.4		41.5

		18-Mar-08		18:07:10		66.81		46.5		18-Mar-08		18:06:20		65.6		45.5		18-Mar-08		18:07:53		70.41		37.5		28-Apr-08		18:25:59		73.4		41

		18-Mar-08		20:07:10		66.2		47		18-Mar-08		20:06:20		65.6		47		18-Mar-08		20:07:53		70.41		42.5		28-Apr-08		20:25:59		73.4		40.5

		18-Mar-08		22:07:10		66.2		47.5		18-Mar-08		22:06:20		65.01		47		18-Mar-08		22:07:53		71.6		40.5		28-Apr-08		22:25:59		73.4		39.5

		19-Mar-08		0:07:10		65.6		48		19-Mar-08		0:06:20		65.6		44.5		19-Mar-08		0:07:53		72.21		39		29-Apr-08		0:25:59		72.8		38.5

		19-Mar-08		2:07:10		65.6		48.5		19-Mar-08		2:06:20		64.4		49.5		19-Mar-08		2:07:53		71.6		39		29-Apr-08		2:25:59		71.6		38.5

		19-Mar-08		4:07:10		65.6		48		19-Mar-08		4:06:20		65.6		46.5		19-Mar-08		4:07:53		71		39		29-Apr-08		4:25:59		70.41		38.5

		19-Mar-08		6:07:10		66.2		47		19-Mar-08		6:06:20		65.6		45.5		19-Mar-08		6:07:53		71.6		39.5		29-Apr-08		6:25:59		70.41		38

		19-Mar-08		8:07:10		66.2		47		19-Mar-08		8:06:20		65.01		47		19-Mar-08		8:07:53		70.41		38		29-Apr-08		8:25:59		69.8		39.5

		19-Mar-08		10:07:10		66.2		47		19-Mar-08		10:06:20		66.2		47		19-Mar-08		10:07:53		70.41		37.5		29-Apr-08		10:25:59		72.8		40.5

		19-Mar-08		12:07:10		66.81		48.5		19-Mar-08		12:06:20		66.2		48		19-Mar-08		12:07:53		71.6		50.5		29-Apr-08		12:25:59		73.4		42.5

		19-Mar-08		14:07:10		66.81		49		19-Mar-08		14:06:20		66.2		51		19-Mar-08		14:07:53		71		41		29-Apr-08		14:25:59		73.4		43

		19-Mar-08		16:07:10		66.81		46.5		19-Mar-08		16:06:20		66.2		44		19-Mar-08		16:07:53		71.6		42.5		29-Apr-08		16:25:59		74.01		42.5

		19-Mar-08		18:07:10		66.2		47.5		19-Mar-08		18:06:20		66.2		45		19-Mar-08		18:07:53		70.41		40		29-Apr-08		18:25:59		74.01		41

		19-Mar-08		20:07:10		66.2		49		19-Mar-08		20:06:20		65.01		51.5		19-Mar-08		20:07:53		70.41		45		29-Apr-08		20:25:59		74.6		41

		19-Mar-08		22:07:10		65.6		48		19-Mar-08		22:06:20		65.6		52.5		19-Mar-08		22:07:53		71		44.5		29-Apr-08		22:25:59		74.01		40

		20-Mar-08		0:07:10		65.6		47		20-Mar-08		0:06:20		65.01		50.5		20-Mar-08		0:07:53		71		41.5		30-Apr-08		0:25:59		72.8		36.5

		20-Mar-08		2:07:10		65.6		48.5		20-Mar-08		2:06:20		65.6		47.5		20-Mar-08		2:07:53		71		40		30-Apr-08		2:25:59		71		36

		20-Mar-08		4:07:10		65.6		48.5		20-Mar-08		4:06:20		65.01		44.5		20-Mar-08		4:07:53		70.41		39		30-Apr-08		4:25:59		70.41		36

		20-Mar-08		6:07:10		65.6		41		20-Mar-08		6:06:20		64.4		43.5		20-Mar-08		6:07:53		70.41		38.5		30-Apr-08		6:25:59		70.41		36

		20-Mar-08		8:07:10		66.2		47		20-Mar-08		8:06:20		65.6		45		20-Mar-08		8:07:53		71.6		41		30-Apr-08		8:25:59		71		36

		20-Mar-08		10:07:10		66.2		45		20-Mar-08		10:06:20		65.6		49		20-Mar-08		10:07:53		71		45.5		30-Apr-08		10:25:59		72.8		36

		20-Mar-08		12:07:10		66.2		48		20-Mar-08		12:06:20		65.01		51.5		20-Mar-08		12:07:53		69.8		47		30-Apr-08		12:25:59		72.8		34.5

		20-Mar-08		14:07:10		66.81		47.5		20-Mar-08		14:06:20		65.6		53.5		20-Mar-08		14:07:53		71		51.5		30-Apr-08		14:25:59		73.4		33.5

		20-Mar-08		16:07:10		66.2		50		20-Mar-08		16:06:20		65.6		55.5		20-Mar-08		16:07:53		69.8		50.5		30-Apr-08		16:25:59		73.4		34

		20-Mar-08		18:07:10		66.2		48.5		20-Mar-08		18:06:20		65.6		56		20-Mar-08		18:07:53		69.8		48.5		30-Apr-08		18:25:59		72.8		32

		20-Mar-08		20:07:10		65.6		48.5		20-Mar-08		20:06:20		66.2		46		20-Mar-08		20:07:53		70.41		44		30-Apr-08		20:25:59		73.4		32

		20-Mar-08		22:07:10		65.6		48.5		20-Mar-08		22:06:20		65.6		47.5		20-Mar-08		22:07:53		71		41.5		30-Apr-08		22:25:59		72.21		31

		21-Mar-08		0:07:10		65.6		43		21-Mar-08		0:06:20		65.01		44		21-Mar-08		0:07:53		70.41		40		1-May-08		0:25:59		70.41		31.5

		21-Mar-08		2:07:10		65.6		49		21-Mar-08		2:06:20		65.01		41		21-Mar-08		2:07:53		69.8		38		1-May-08		2:25:59		69.2		31

		21-Mar-08		4:07:10		65.01		39.5		21-Mar-08		4:06:20		64.4		40		21-Mar-08		4:07:53		68.61		37.5		1-May-08		4:25:59		68		31

		21-Mar-08		6:07:10		65.6		48.5		21-Mar-08		6:06:20		64.4		39		21-Mar-08		6:07:53		69.2		37		1-May-08		6:25:59		70.41		30.5

		21-Mar-08		8:07:10		65.6		37.5		21-Mar-08		8:06:20		65.01		37.5		21-Mar-08		8:07:53		71		33		1-May-08		8:25:59		69.2		30

		21-Mar-08		10:07:10		66.2		47		21-Mar-08		10:06:20		66.2		39		21-Mar-08		10:07:53		71		40		1-May-08		10:25:59		71		30

		21-Mar-08		12:07:10		66.2		42.5		21-Mar-08		12:06:20		66.2		32		21-Mar-08		12:07:53		71		37		1-May-08		12:25:59		72.8		29

		21-Mar-08		14:07:10		66.2		46		21-Mar-08		14:06:20		66.81		30.5		21-Mar-08		14:07:53		70.41		31.5		1-May-08		14:25:59		73.4		28

		21-Mar-08		16:07:10		66.2		34.5		21-Mar-08		16:06:20		66.81		33		21-Mar-08		16:07:53		70.41		35.5		1-May-08		16:25:59		72.8		28

		21-Mar-08		18:07:10		66.2		46.5		21-Mar-08		18:06:20		66.2		36		21-Mar-08		18:07:53		70.41		33.5		1-May-08		18:25:59		73.4		29

		21-Mar-08		20:07:10		65.6		40		21-Mar-08		20:06:20		65.6		37		21-Mar-08		20:07:53		70.41		36.5		1-May-08		20:25:59		73.4		29.5

		21-Mar-08		22:07:10		65.6		39		21-Mar-08		22:06:20		65.01		37.5		21-Mar-08		22:07:53		70.41		35		1-May-08		22:25:59		72.8		29.5

		22-Mar-08		0:07:10		65.6		37		22-Mar-08		0:06:20		65.6		35		22-Mar-08		0:07:53		69.8		33.5		2-May-08		0:25:59		71.6		29.5

		22-Mar-08		2:07:10		65.01		36.5		22-Mar-08		2:06:20		65.6		35.5		22-Mar-08		2:07:53		69.2		33.5		2-May-08		2:25:59		70.41		30

		22-Mar-08		4:07:10		65.01		47		22-Mar-08		4:06:20		65.6		35		22-Mar-08		4:07:53		68.61		34		2-May-08		4:25:59		69.2		30

		22-Mar-08		6:07:10		65.6		46		22-Mar-08		6:06:20		65.6		34.5		22-Mar-08		6:07:53		69.2		33.5		2-May-08		6:25:59		71		30.5

		22-Mar-08		8:07:10		65.6		36		22-Mar-08		8:06:20		65.6		34.5		22-Mar-08		8:07:53		71		32.5		2-May-08		8:25:59		69.8		31.5

		22-Mar-08		10:07:10		66.2		41.5		22-Mar-08		10:06:20		65.6		37		22-Mar-08		10:07:53		70.41		34		2-May-08		10:25:59		72.21		32

		22-Mar-08		12:07:10		66.2		42		22-Mar-08		12:06:20		66.81		33.5		22-Mar-08		12:07:53		70.41		32.5		2-May-08		12:25:59		72.8		30.5

		22-Mar-08		14:07:10		66.81		45		22-Mar-08		14:06:20		66.2		33		22-Mar-08		14:07:53		71		33		2-May-08		14:25:59		73.4		28

		22-Mar-08		16:07:10		66.2		41.5		22-Mar-08		16:06:20		65.6		40		22-Mar-08		16:07:53		71		33		2-May-08		16:25:59		74.01		30

		22-Mar-08		18:07:10		66.2		47		22-Mar-08		18:06:20		65.01		40		22-Mar-08		18:07:53		70.41		34.5		2-May-08		18:25:59		72.8		31

		22-Mar-08		20:07:10		65.6		47		22-Mar-08		20:06:20		66.2		43		22-Mar-08		20:07:53		69.8		39.5		2-May-08		20:25:59		74.01		31.5

		22-Mar-08		22:07:10		65.6		47.5		22-Mar-08		22:06:20		65.01		42.5		22-Mar-08		22:07:53		70.41		38.5		2-May-08		22:25:59		74.01		30.5

		23-Mar-08		0:07:10		65.6		47.5		23-Mar-08		0:06:20		65.6		42		23-Mar-08		0:07:53		71		37		3-May-08		0:25:59		73.4		29.5

		23-Mar-08		2:07:10		65.6		40.5		23-Mar-08		2:06:20		65.01		40		23-Mar-08		2:07:53		70.41		36.5		3-May-08		2:25:59		72.21		30.5

		23-Mar-08		4:07:10		65.6		49		23-Mar-08		4:06:20		65.01		38.5		23-Mar-08		4:07:53		69.2		35		3-May-08		4:25:59		70.41		31.5

		23-Mar-08		6:07:10		65.01		38.5		23-Mar-08		6:06:20		65.6		38		23-Mar-08		6:07:53		69.8		35.5		3-May-08		6:25:59		70.41		32

		23-Mar-08		8:07:10		65.6		46		23-Mar-08		8:06:20		65.01		37.5		23-Mar-08		8:07:53		71		34.5		3-May-08		8:25:59		70.41		33.5

		23-Mar-08		10:07:10		65.6		41.5		23-Mar-08		10:06:20		66.2		40.5		23-Mar-08		10:07:53		70.41		34.5		3-May-08		10:25:59		72.8		34.5

		23-Mar-08		12:07:10		66.2		47		23-Mar-08		12:06:20		66.2		42.5		23-Mar-08		12:07:53		69.8		34.5		3-May-08		12:25:59		73.4		34

		23-Mar-08		14:07:10		66.2		42.5		23-Mar-08		14:06:20		65.6		43		23-Mar-08		14:07:53		70.41		43.5		3-May-08		14:25:59		73.4		35.5

		23-Mar-08		16:07:10		66.2		36		23-Mar-08		16:06:20		65.6		36		23-Mar-08		16:07:53		71		38.5		3-May-08		16:25:59		74.01		35

		23-Mar-08		18:07:10		66.2		43.5		23-Mar-08		18:06:20		66.2		42		23-Mar-08		18:07:53		70.41		40		3-May-08		18:25:59		73.4		36.5

		23-Mar-08		20:07:10		65.6		44		23-Mar-08		20:06:20		65.6		45.5		23-Mar-08		20:07:53		69.8		41.5		3-May-08		20:25:59		74.01		36.5

		23-Mar-08		22:07:10		65.6		48		23-Mar-08		22:06:20		65.01		46.5		23-Mar-08		22:07:53		71		39.5		3-May-08		22:25:59		74.01		35

		24-Mar-08		0:07:10		65.6		47.5		24-Mar-08		0:06:20		65.01		44.5		24-Mar-08		0:07:53		71		37.5		4-May-08		0:25:59		72.21		34.5

		24-Mar-08		2:07:10		65.6		43		24-Mar-08		2:06:20		65.6		41		24-Mar-08		2:07:53		69.8		36		4-May-08		2:25:59		70.41		35

		24-Mar-08		4:07:10		65.6		47.5		24-Mar-08		4:06:20		65.01		39.5		24-Mar-08		4:07:53		68.61		36		4-May-08		4:25:59		69.2		34.5

		24-Mar-08		6:07:10		65.01		47.5		24-Mar-08		6:06:20		64.4		38.5		24-Mar-08		6:07:53		68		35.5		4-May-08		6:25:59		69.2		34.5

		24-Mar-08		8:07:10		65.01		36		24-Mar-08		8:06:20		63.8		36.5		24-Mar-08		8:07:53		66.81		35		4-May-08		8:25:59		69.8		35

		24-Mar-08		10:07:10		65.6		47.5		24-Mar-08		10:06:20		65.6		39		24-Mar-08		10:07:53		69.8		35		4-May-08		10:25:59		71.6		37

		24-Mar-08		12:07:10		65.6		39.5		24-Mar-08		12:06:20		66.2		38		24-Mar-08		12:07:53		70.41		36.5		4-May-08		12:25:59		73.4		37

		24-Mar-08		14:07:10		66.2		43.5		24-Mar-08		14:06:20		65.6		39		24-Mar-08		14:07:53		69.8		39		4-May-08		14:25:59		74.6		38

		24-Mar-08		16:07:10		66.2		47.5		24-Mar-08		16:06:20		65.6		45.5		24-Mar-08		16:07:53		70.41		42		4-May-08		16:25:59		74.01		38

		24-Mar-08		18:07:10		66.2		45.5		24-Mar-08		18:06:20		66.2		50		24-Mar-08		18:07:53		69.8		45		4-May-08		18:25:59		73.4		40.5

		24-Mar-08		20:07:10		65.6		47.5		24-Mar-08		20:06:20		66.2		45.5		24-Mar-08		20:07:53		71		42.5		4-May-08		20:25:59		73.4		40

		24-Mar-08		22:07:10		65.6		43		24-Mar-08		22:06:20		65.6		45		24-Mar-08		22:07:53		71.6		39.5		4-May-08		22:25:59		72.8		39

		25-Mar-08		0:07:10		65.6		42.5		25-Mar-08		0:06:20		65.01		46		25-Mar-08		0:07:53		71		38.5		5-May-08		0:25:59		71.6		38.5

		25-Mar-08		2:07:10		65.6		41		25-Mar-08		2:06:20		65.6		42		25-Mar-08		2:07:53		69.8		37.5		5-May-08		2:25:59		71		38

		25-Mar-08		4:07:10		65.6		46		25-Mar-08		4:06:20		65.6		42.5		25-Mar-08		4:07:53		69.2		37		5-May-08		4:25:59		69.8		37.5

		25-Mar-08		6:07:10		65.6		39.5		25-Mar-08		6:06:20		65.6		41		25-Mar-08		6:07:53		69.8		37.5		5-May-08		6:25:59		68.61		37.5

		25-Mar-08		8:07:10		65.6		40		25-Mar-08		8:06:20		65.6		41.5		25-Mar-08		8:07:53		71.6		37		5-May-08		8:25:59		68.61		38

		25-Mar-08		10:07:10		66.2		44.5		25-Mar-08		10:06:20		66.2		49		25-Mar-08		10:07:53		70.41		44.5		5-May-08		10:25:59		69.8		40.5

		25-Mar-08		12:07:10		66.81		46.5		25-Mar-08		12:06:20		66.2		53.5		25-Mar-08		12:07:53		71.6		38.5		5-May-08		12:25:59		71.6		41.5

		25-Mar-08		14:07:10		66.81		47.5		25-Mar-08		14:06:20		66.2		59.5		25-Mar-08		14:07:53		71		46		5-May-08		14:25:59		72.8		41.5

		25-Mar-08		16:07:10		66.81		48.5		25-Mar-08		16:06:20		65.6		53.5		25-Mar-08		16:07:53		71		49		5-May-08		16:25:59		73.4		40.5

		25-Mar-08		18:07:10		66.2		47		25-Mar-08		18:06:20		65.6		57.5		25-Mar-08		18:07:53		70.41		50.5		5-May-08		18:25:59		73.4		39.5

		25-Mar-08		20:07:10		66.2		45.5		25-Mar-08		20:06:20		65.6		55		25-Mar-08		20:07:53		70.41		51		5-May-08		20:25:59		72.8		39

		25-Mar-08		22:07:10		65.6		45		25-Mar-08		22:06:20		65.6		51		25-Mar-08		22:07:53		70.41		46		5-May-08		22:25:59		72.21		38

		26-Mar-08		0:07:10		65.6		44		26-Mar-08		0:06:20		65.6		49		26-Mar-08		0:07:53		69.8		42.5		6-May-08		0:25:59		71.6		37.5

		26-Mar-08		2:07:10		65.6		43		26-Mar-08		2:06:20		65.6		47.5		26-Mar-08		2:07:53		69.8		40.5		6-May-08		2:25:59		70.41		38

		26-Mar-08		4:07:10		65.6		42		26-Mar-08		4:06:20		65.6		45.5		26-Mar-08		4:07:53		69.8		39		6-May-08		4:25:59		69.2		37.5

		26-Mar-08		6:07:10		65.6		43		26-Mar-08		6:06:20		64.4		49.5		26-Mar-08		6:07:53		70.41		40.5		6-May-08		6:25:59		69.8		37.5

		26-Mar-08		8:07:10		66.2		44		26-Mar-08		8:06:20		65.6		50.5		26-Mar-08		8:07:53		71.6		41.5		6-May-08		8:25:59		69.8		40

		26-Mar-08		10:07:10		66.2		45		26-Mar-08		10:06:20		65.01		53		26-Mar-08		10:07:53		71		45.5		6-May-08		10:25:59		72.21		41.5

		26-Mar-08		12:07:10		66.2		46		26-Mar-08		12:06:20		65.6		53.5		26-Mar-08		12:07:53		71		49		6-May-08		12:25:59		73.4		43.5

		26-Mar-08		14:07:10		66.81		45.5		26-Mar-08		14:06:20		65.6		53.5		26-Mar-08		14:07:53		71		48.5		6-May-08		14:25:59		73.4		43

		26-Mar-08		16:07:10		66.2		44		26-Mar-08		16:06:20		66.2		50.5		26-Mar-08		16:07:53		70.41		39.5		6-May-08		16:25:59		74.01		43

		26-Mar-08		18:07:10		65.6		43		26-Mar-08		18:06:20		66.2		45		26-Mar-08		18:07:53		70.41		48		6-May-08		18:25:59		74.01		40

		26-Mar-08		20:07:10		65.6		41		26-Mar-08		20:06:20		65.6		41.5		26-Mar-08		20:07:53		70.41		43.5		6-May-08		20:25:59		73.4		40

		26-Mar-08		22:07:10		65.6		40.5		26-Mar-08		22:06:20		64.4		44		26-Mar-08		22:07:53		72.21		37.5		6-May-08		22:25:59		72.21		39.5

		27-Mar-08		0:07:10		65.6		41		27-Mar-08		0:06:20		65.6		43		27-Mar-08		0:07:53		71.6		36.5		7-May-08		0:25:59		71.6		40

		27-Mar-08		2:07:10		65.01		39.5		27-Mar-08		2:06:20		64.4		42.5		27-Mar-08		2:07:53		70.41		36		7-May-08		2:25:59		71		40

		27-Mar-08		4:07:10		65.01		38		27-Mar-08		4:06:20		63.8		41.5		27-Mar-08		4:07:53		69.8		35		7-May-08		4:25:59		69.8		40

		27-Mar-08		6:07:10		65.01		37		27-Mar-08		6:06:20		63.8		40.5		27-Mar-08		6:07:53		70.41		35		7-May-08		6:25:59		71		40.5

		27-Mar-08		8:07:10		65.6		37		27-Mar-08		8:06:20		63.8		39		27-Mar-08		8:07:53		71.6		34.5		7-May-08		8:25:59		71.6		41.5

		27-Mar-08		10:07:10		65.6		40		27-Mar-08		10:06:20		66.2		41		27-Mar-08		10:07:53		71.6		35		7-May-08		10:25:59		73.4		41

		27-Mar-08		12:07:10		65.6		39		27-Mar-08		12:06:20		69.2		36.5		27-Mar-08		12:07:53		71		42		7-May-08		12:25:59		73.4		43

		27-Mar-08		14:07:10		66.2		40		27-Mar-08		14:06:20		69.2		37		27-Mar-08		14:07:53		71		35.5		7-May-08		14:25:59		73.4		45.5

		27-Mar-08		16:07:10		65.6		43		27-Mar-08		16:06:20		68.61		41.5		27-Mar-08		16:07:53		70.41		37		7-May-08		16:25:59		73.4		44.5

		27-Mar-08		18:07:10		65.6		41		27-Mar-08		18:06:20		68.61		38		27-Mar-08		18:07:53		70.41		42		7-May-08		18:25:59		73.4		43

		27-Mar-08		20:07:10		65.6		40		27-Mar-08		20:06:20		68		38.5		27-Mar-08		20:07:53		72.8		36		7-May-08		20:25:59		74.01		42

		27-Mar-08		22:07:10		65.6		37.5		27-Mar-08		22:06:20		66.81		36		27-Mar-08		22:07:53		74.6		32		7-May-08		22:25:59		74.01		37.5

		28-Mar-08		0:07:10		65.01		36.5		28-Mar-08		0:06:20		65.6		36.5		28-Mar-08		0:07:53		71.6		32.5		8-May-08		0:25:59		73.4		37

		28-Mar-08		2:07:10		65.01		35		28-Mar-08		2:06:20		64.4		35.5		28-Mar-08		2:07:53		69.8		32		8-May-08		2:25:59		71.6		37

		28-Mar-08		4:07:10		65.01		33.5		28-Mar-08		4:06:20		63.8		35		28-Mar-08		4:07:53		68.61		31.5		8-May-08		4:25:59		70.41		37.5

		28-Mar-08		6:07:10		65.01		33		28-Mar-08		6:06:20		63.21		35		28-Mar-08		6:07:53		69.2		32		8-May-08		6:25:59		73.4		35.5

		28-Mar-08		8:07:10		65.6		32		28-Mar-08		8:06:20		64.4		34		28-Mar-08		8:07:53		70.41		32		8-May-08		8:25:59		72.8		35.5

		28-Mar-08		10:07:10		65.6		30.5		28-Mar-08		10:06:20		66.2		31		28-Mar-08		10:07:53		71		33		8-May-08		10:25:59		72.8		37.5

		28-Mar-08		12:07:10		65.6		28		28-Mar-08		12:06:20		68.61		27		28-Mar-08		12:07:53		71		29.5		8-May-08		12:25:59		72.8		38.5

		28-Mar-08		14:07:10		66.2		28		28-Mar-08		14:06:20		69.2		25.5		28-Mar-08		14:07:53		70.41		32.5		8-May-08		14:25:59		73.4		39.5

		28-Mar-08		16:07:10		66.2		23.5		28-Mar-08		16:06:20		69.2		22		28-Mar-08		16:07:53		70.41		28.5		8-May-08		16:25:59		74.01		39.5

		28-Mar-08		18:07:10		65.6		24.5		28-Mar-08		18:06:20		69.2		21		28-Mar-08		18:07:53		71		26.5		8-May-08		18:25:59		73.4		39

		28-Mar-08		20:07:10		65.6		26		28-Mar-08		20:06:20		68.61		23.5		28-Mar-08		20:07:53		71.6		26.5		8-May-08		20:25:59		74.01		39.5

		28-Mar-08		22:07:10		65.01		35		28-Mar-08		22:06:20		67.4		34		28-Mar-08		22:07:53		74.6		28.5		8-May-08		22:25:59		74.01		37.5

		29-Mar-08		0:07:10		65.01		35		29-Mar-08		0:06:20		65.6		35.5		29-Mar-08		0:07:53		72.8		29.5		9-May-08		0:25:59		72.8		37

		29-Mar-08		2:07:10		65.01		36		29-Mar-08		2:06:20		65.01		37.5		29-Mar-08		2:07:53		71		30.5		9-May-08		2:25:59		71		36.5

		29-Mar-08		4:07:10		65.01		35.5		29-Mar-08		4:06:20		64.4		37.5		29-Mar-08		4:07:53		69.8		31		9-May-08		4:25:59		69.2		36.5

		29-Mar-08		6:07:10		65.6		34.5		29-Mar-08		6:06:20		64.4		37		29-Mar-08		6:07:53		70.41		33		9-May-08		6:25:59		72.8		35.5

		29-Mar-08		8:07:10		65.01		36.5		29-Mar-08		8:06:20		65.6		37.5		29-Mar-08		8:07:53		70.41		35		9-May-08		8:25:59		73.4		36.5

		29-Mar-08		10:07:10		65.6		32		29-Mar-08		10:06:20		68		32.5		29-Mar-08		10:07:53		70.41		35.5		9-May-08		10:25:59		73.4		38.5

		29-Mar-08		12:07:10		64.4		39		29-Mar-08		12:06:20		69.2		32		29-Mar-08		12:07:53		71		36.5		9-May-08		12:25:59		72.21		41

		29-Mar-08		14:07:10		66.81		38.5		29-Mar-08		14:06:20		68		38		29-Mar-08		14:07:53		71		44		9-May-08		14:25:59		72.21		41.5

		29-Mar-08		16:07:10		66.81		43		29-Mar-08		16:06:20		65.6		51		29-Mar-08		16:07:53		71		43		9-May-08		16:25:59		73.4		39.5

		29-Mar-08		18:07:10		66.81		44.5		29-Mar-08		18:06:20		64.4		55.5		29-Mar-08		18:07:53		72.21		42.5		9-May-08		18:25:59		72.8		39

		29-Mar-08		20:07:10		66.81		44.5		29-Mar-08		20:06:20		65.01		55		29-Mar-08		20:07:53		71		45.5		9-May-08		20:25:59		73.4		38.5

		29-Mar-08		22:07:10		66.81		45		29-Mar-08		22:06:20		64.4		57		29-Mar-08		22:07:53		70.41		44		9-May-08		22:25:59		72.8		37.5

		30-Mar-08		0:07:10		66.81		45		30-Mar-08		0:06:20		65.01		56		30-Mar-08		0:07:53		70.41		42.5		10-May-08		0:25:59		72.21		36

		30-Mar-08		2:07:10		66.81		44.5		30-Mar-08		2:06:20		65.01		54.5		30-Mar-08		2:07:53		69.8		43		10-May-08		2:25:59		72.21		35

		30-Mar-08		4:07:10		66.81		43.5		30-Mar-08		4:06:20		64.4		53.5		30-Mar-08		4:07:53		69.8		42		10-May-08		4:25:59		72.21		35

		30-Mar-08		6:07:10		66.81		41.5		30-Mar-08		6:06:20		65.01		50		30-Mar-08		6:07:53		69.8		41.5		10-May-08		6:25:59		72.21		34

		30-Mar-08		8:07:10		67.4		40.5		30-Mar-08		8:06:20		65.01		47.5		30-Mar-08		8:07:53		69.8		40		10-May-08		8:25:59		71		36

		30-Mar-08		10:07:10		67.4		39.5		30-Mar-08		10:06:20		64.4		47.5		30-Mar-08		10:07:53		69.8		39.5		10-May-08		10:25:59		73.4		36

		30-Mar-08		12:07:10		68		40.5		30-Mar-08		12:06:20		64.4		48		30-Mar-08		12:07:53		69.8		41		10-May-08		12:25:59		74.6		34.5

		30-Mar-08		14:07:10		67.4		42		30-Mar-08		14:06:20		65.01		51		30-Mar-08		14:07:53		70.41		37.5		10-May-08		14:25:59		75.2		33.5

		30-Mar-08		16:07:10		67.4		40.5		30-Mar-08		16:06:20		65.01		46.5		30-Mar-08		16:07:53		70.41		39		10-May-08		16:25:59		75.2		35.5

		30-Mar-08		18:07:10		67.4		39.5		30-Mar-08		18:06:20		65.01		45.5		30-Mar-08		18:07:53		69.8		43		10-May-08		18:25:59		75.2		35.5

		30-Mar-08		20:07:10		68		37		30-Mar-08		20:06:20		64.4		43		30-Mar-08		20:07:53		70.41		39.5		10-May-08		20:25:59		74.6		36

		30-Mar-08		22:07:10		68		33		30-Mar-08		22:06:20		64.4		37		30-Mar-08		22:07:53		71		35.5		10-May-08		22:25:59		74.6		34.5

		31-Mar-08		0:07:10		68		32		31-Mar-08		0:06:20		65.01		35		31-Mar-08		0:07:53		69.8		33		11-May-08		0:25:59		74.01		34

		31-Mar-08		2:07:10		67.4		32		31-Mar-08		2:06:20		64.4		35.5		31-Mar-08		2:07:53		69.8		32.5		11-May-08		2:25:59		72.21		34

		31-Mar-08		4:07:10		67.4		32.5		31-Mar-08		4:06:20		63.8		37		31-Mar-08		4:07:53		68.61		32.5		11-May-08		4:25:59		71.6		34

		31-Mar-08		6:07:10		68		32.5		31-Mar-08		6:06:20		63.21		38.5		31-Mar-08		6:07:53		68		33		11-May-08		6:25:59		72.21		34

		31-Mar-08		8:07:10		67.4		31		31-Mar-08		8:06:20		63.8		36		31-Mar-08		8:07:53		68		32.5		11-May-08		8:25:59		72.21		34.5

		31-Mar-08		10:07:10		67.4		28.5		31-Mar-08		10:06:20		64.4		32		31-Mar-08		10:07:53		69.2		31		11-May-08		10:25:59		72.8		35

		31-Mar-08		12:07:10		67.4		25.5		31-Mar-08		12:06:20		64.4		29.5		31-Mar-08		12:07:53		69.8		29.5		11-May-08		12:25:59		74.01		35

		31-Mar-08		14:07:10		68		23.5		31-Mar-08		14:06:20		65.01		25.5		31-Mar-08		14:07:53		69.8		27.5		11-May-08		14:25:59		75.81		35.5

		31-Mar-08		16:07:10		67.4		24		31-Mar-08		16:06:20		65.01		26		31-Mar-08		16:07:53		69.2		28		11-May-08		16:25:59		77		34.5

		31-Mar-08		18:07:10		67.4		26.5		31-Mar-08		18:06:20		65.01		29.5		31-Mar-08		18:07:53		69.8		28.5		11-May-08		18:25:59		78.2		35

		31-Mar-08		20:07:10		68		26.5		31-Mar-08		20:06:20		64.4		30		31-Mar-08		20:07:53		71		28.5		11-May-08		20:25:59		77.61		36

		31-Mar-08		22:07:10		67.4		27		31-Mar-08		22:06:20		64.4		30.5		31-Mar-08		22:07:53		70.41		27.5		11-May-08		22:25:59		75.81		37

		1-Apr-08		0:07:10		67.4		27.5		1-Apr-08		0:06:20		64.4		31.5		1-Apr-08		0:07:53		69.2		27.5		12-May-08		0:25:59		74.01		37.5

		1-Apr-08		2:07:10		67.4		28		1-Apr-08		2:06:20		63.8		32.5		1-Apr-08		2:07:53		68.61		28		12-May-08		2:25:59		72.8		38

		1-Apr-08		4:07:10		67.4		28		1-Apr-08		4:06:20		62.6		32.5		1-Apr-08		4:07:53		67.4		28.5		12-May-08		4:25:59		72.21		38

		1-Apr-08		6:07:10		67.4		28.5		1-Apr-08		6:06:20		62		34		1-Apr-08		6:07:53		66.81		29.5		12-May-08		6:25:59		72.21		37.5

		1-Apr-08		8:07:10		68		28.5		1-Apr-08		8:06:20		63.21		34		1-Apr-08		8:07:53		69.8		29.5		12-May-08		8:25:59		72.21		38.5

		1-Apr-08		10:07:10		67.4		30.5		1-Apr-08		10:06:20		65.01		34.5		1-Apr-08		10:07:53		71		31.5		12-May-08		10:25:59		71.6		40

		1-Apr-08		12:07:10		66.81		27		1-Apr-08		12:06:20		65.6		30		1-Apr-08		12:07:53		71		34		12-May-08		12:25:59		72.8		41

		1-Apr-08		14:07:10		66.81		30		1-Apr-08		14:06:20		66.2		31		1-Apr-08		14:07:53		71		35		12-May-08		14:25:59		74.01		36

		1-Apr-08		16:07:10		66.81		31		1-Apr-08		16:06:20		65.6		34		1-Apr-08		16:07:53		71		36.5		12-May-08		16:25:59		74.6		32

		1-Apr-08		18:07:10		66.81		29.5		1-Apr-08		18:06:20		65.01		32.5		1-Apr-08		18:07:53		71		33.5		12-May-08		18:25:59		76.4		31

		1-Apr-08		20:07:10		67.4		30.5		1-Apr-08		20:06:20		65.01		32.5		1-Apr-08		20:07:53		70.41		32		12-May-08		20:25:59		75.81		31.5

		1-Apr-08		22:07:10		67.4		29		1-Apr-08		22:06:20		64.4		32		1-Apr-08		22:07:53		70.41		32		12-May-08		22:25:59		74.01		31

		2-Apr-08		0:07:10		66.81		33		2-Apr-08		0:06:20		65.01		37		2-Apr-08		0:07:53		70.41		31		13-May-08		0:25:59		72.8		31

		2-Apr-08		2:07:10		66.81		34		2-Apr-08		2:06:20		64.4		38.5		2-Apr-08		2:07:53		70.41		31		13-May-08		2:25:59		71.6		31

		2-Apr-08		4:07:10		66.81		33		2-Apr-08		4:06:20		64.4		38		2-Apr-08		4:07:53		70.41		32		13-May-08		4:25:59		71.6		31

		2-Apr-08		6:07:10		66.81		31.5		2-Apr-08		6:06:20		65.01		35		2-Apr-08		6:07:53		71		32		13-May-08		6:25:59		71.6		30

		2-Apr-08		8:07:10		66.81		33.5		2-Apr-08		8:06:20		65.01		37.5		2-Apr-08		8:07:53		71.6		33.5		13-May-08		8:25:59		71.6		30

		2-Apr-08		10:07:10		66.81		33.5		2-Apr-08		10:06:20		66.2		35.5		2-Apr-08		10:07:53		70.41		35		13-May-08		10:25:59		74.01		29.5

		2-Apr-08		12:07:10		66.81		33		2-Apr-08		12:06:20		66.81		33		2-Apr-08		12:07:53		71		36		13-May-08		12:25:59		74.01		29.5

		2-Apr-08		14:07:10		66.81		39		2-Apr-08		14:06:20		67.4		42.5		2-Apr-08		14:07:53		71.6		34.5		13-May-08		14:25:59		75.2		29.5

		2-Apr-08		16:07:10		67.4		34		2-Apr-08		16:06:20		67.4		31.5		2-Apr-08		16:07:53		71.6		36.5		13-May-08		16:25:59		75.2		30

		2-Apr-08		18:07:10		66.81		35		2-Apr-08		18:06:20		66.2		36		2-Apr-08		18:07:53		71		32.5		13-May-08		18:25:59		75.2		30

		2-Apr-08		20:07:10		67.4		36.5		2-Apr-08		20:06:20		66.81		37		2-Apr-08		20:07:53		71		37		13-May-08		20:25:59		74.6		30.5

		2-Apr-08		22:07:10		66.81		37.5		2-Apr-08		22:06:20		65.6		41.5		2-Apr-08		22:07:53		75.2		33		13-May-08		22:25:59		74.01		29.5

		3-Apr-08		0:07:10		66.81		37.5		3-Apr-08		0:06:20		66.2		42		3-Apr-08		0:07:53		71.6		34		14-May-08		0:25:59		73.4		29.5

		3-Apr-08		2:07:10		66.81		36.5		3-Apr-08		2:06:20		65.6		40.5		3-Apr-08		2:07:53		70.41		34.5		14-May-08		2:25:59		72.21		30

		3-Apr-08		4:07:10		67.4		34.5		3-Apr-08		4:06:20		64.4		38.5		3-Apr-08		4:07:53		69.2		33.5		14-May-08		4:25:59		71.6		30.5

		3-Apr-08		6:07:10		67.4		35.5		3-Apr-08		6:06:20		64.4		38		3-Apr-08		6:07:53		69.2		33		14-May-08		6:25:59		72.21		31

		3-Apr-08		8:07:10		67.4		35.5		3-Apr-08		8:06:20		65.01		38.5		3-Apr-08		8:07:53		71		31		14-May-08		8:25:59		71.6		32.5

		3-Apr-08		10:07:10		65.01		39		3-Apr-08		10:06:20		66.2		41		3-Apr-08		10:07:53		71.6		34.5		14-May-08		10:25:59		74.6		33

		3-Apr-08		12:07:10		66.81		38		3-Apr-08		12:06:20		66.81		39		3-Apr-08		12:07:53		71		34.5		14-May-08		12:25:59		74.01		32

		3-Apr-08		14:07:10		66.81		40		3-Apr-08		14:06:20		67.4		41.5		3-Apr-08		14:07:53		71		38		14-May-08		14:25:59		74.01		30.5

		3-Apr-08		16:07:10		66.81		38		3-Apr-08		16:06:20		66.2		40		3-Apr-08		16:07:53		71.6		42.5		14-May-08		16:25:59		74.6		29

		3-Apr-08		18:07:10		66.81		35.5		3-Apr-08		18:06:20		66.81		36		3-Apr-08		18:07:53		71		32		14-May-08		18:25:59		74.01		29

		3-Apr-08		20:07:10		67.4		35.5		3-Apr-08		20:06:20		66.2		37.5		3-Apr-08		20:07:53		71		32.5		14-May-08		20:25:59		74.6		33

		3-Apr-08		22:07:10		67.4		34.5		3-Apr-08		22:06:20		65.6		37		3-Apr-08		22:07:53		72.21		34		14-May-08		22:25:59		75.2		33

		4-Apr-08		0:07:10		67.4		34.5		4-Apr-08		0:06:20		66.2		37.5		4-Apr-08		0:07:53		72.21		33.5		15-May-08		0:25:59		74.6		33.5

		4-Apr-08		2:07:10		66.81		34		4-Apr-08		2:06:20		65.6		36.5		4-Apr-08		2:07:53		70.41		32.5		15-May-08		2:25:59		74.01		34

		4-Apr-08		4:07:10		66.81		35		4-Apr-08		4:06:20		65.01		38		4-Apr-08		4:07:53		69.8		32		15-May-08		4:25:59		73.4		35

		4-Apr-08		6:07:10		66.81		37		4-Apr-08		6:06:20		65.6		40.5		4-Apr-08		6:07:53		69.8		34		15-May-08		6:25:59		73.4		36.5

		4-Apr-08		8:07:10		67.4		37.5		4-Apr-08		8:06:20		66.81		42		4-Apr-08		8:07:53		72.21		33.5		15-May-08		8:25:59		73.4		39

		4-Apr-08		10:07:10		68		38.5		4-Apr-08		10:06:20		66.81		42		4-Apr-08		10:07:53		71.6		36		15-May-08		10:25:59		74.6		40

		4-Apr-08		12:07:10		74.6		35		4-Apr-08		12:06:20		74.6		35.5		4-Apr-08		12:07:53		71.6		42.5		15-May-08		12:25:59		74.01		41.5

		4-Apr-08		14:07:10		66.81		38.5		4-Apr-08		14:06:20		67.4		38.5		4-Apr-08		14:07:53		71.6		45		15-May-08		14:25:59		74.01		38.5

		4-Apr-08		16:07:10		66.81		42		4-Apr-08		16:06:20		66.81		45		4-Apr-08		16:07:53		71		45		15-May-08		16:25:59		74.01		38.5

		4-Apr-08		18:07:10		66.81		40.5		4-Apr-08		18:06:20		66.81		43.5		4-Apr-08		18:07:53		71.6		44		15-May-08		18:25:59		73.4		38.5

		4-Apr-08		20:07:10		66.81		45.5		4-Apr-08		20:06:20		65.6		44		4-Apr-08		20:07:53		71.6		43		15-May-08		20:25:59		75.2		38.5

		4-Apr-08		22:07:10		66.81		45.5		4-Apr-08		22:06:20		66.2		43		4-Apr-08		22:07:53		71.6		35.5		15-May-08		22:25:59		76.4		36

		5-Apr-08		0:07:10		67.4		45		5-Apr-08		0:06:20		65.6		42		5-Apr-08		0:07:53		71		39.5		16-May-08		0:25:59		76.4		35.5

		5-Apr-08		2:07:10		66.81		46.5		5-Apr-08		2:06:20		65.01		43.5		5-Apr-08		2:07:53		70.41		37.5		16-May-08		2:25:59		75.81		35.5

		5-Apr-08		4:07:10		66.81		46.5		5-Apr-08		4:06:20		65.01		44.5		5-Apr-08		4:07:53		69.8		38		16-May-08		4:25:59		75.2		35.5

		5-Apr-08		6:07:10		66.81		46		5-Apr-08		6:06:20		65.01		43		5-Apr-08		6:07:53		70.41		39		16-May-08		6:25:59		75.2		35

		5-Apr-08		8:07:10		68		43.5		5-Apr-08		8:06:20		65.6		43.5		5-Apr-08		8:07:53		71		41		16-May-08		8:25:59		74.6		36.5

		5-Apr-08		10:07:10		67.4		47		5-Apr-08		10:06:20		67.4		40		5-Apr-08		10:07:53		70.41		39		16-May-08		10:25:59		74.01		38.5

		5-Apr-08		12:07:10		67.4		45.5		5-Apr-08		12:06:20		67.4		38.5		5-Apr-08		12:07:53		71		44		16-May-08		12:25:59		73.4		40.5

		5-Apr-08		14:07:10		66.81		47		5-Apr-08		14:06:20		68.61		40.5		5-Apr-08		14:07:53		74.6		35.5		16-May-08		14:25:59		72.8		40.5

		5-Apr-08		16:07:10		66.81		46		5-Apr-08		16:06:20		67.4		43		5-Apr-08		16:07:53		71.6		45.5		16-May-08		16:25:59		73.4		40.5

		5-Apr-08		18:07:10		66.81		46.5		5-Apr-08		18:06:20		66.81		40		5-Apr-08		18:07:53		73.4		40		16-May-08		18:25:59		74.01		40.5

		5-Apr-08		20:07:10		67.4		46.5		5-Apr-08		20:06:20		67.4		40.5		5-Apr-08		20:07:53		75.2		37		16-May-08		20:25:59		75.2		40.5

		5-Apr-08		22:07:10		66.81		46		5-Apr-08		22:06:20		67.4		36.5		5-Apr-08		22:07:53		73.4		36.5		16-May-08		22:25:59		77		40

		6-Apr-08		0:07:10		66.81		46		6-Apr-08		0:06:20		66.81		37		6-Apr-08		0:07:53		71		36		17-May-08		0:25:59		76.4		39

		6-Apr-08		2:07:10		66.81		46.5		6-Apr-08		2:06:20		65.6		37.5		6-Apr-08		2:07:53		69.8		35.5		17-May-08		2:25:59		75.2		39

		6-Apr-08		4:07:10		66.81		47		6-Apr-08		4:06:20		65.01		38		6-Apr-08		4:07:53		68.61		36		17-May-08		4:25:59		74.6		39

		6-Apr-08		6:07:10		67.4		46		6-Apr-08		6:06:20		65.01		37.5		6-Apr-08		6:07:53		67.4		36.5		17-May-08		6:25:59		74.6		40

		6-Apr-08		8:07:10		67.4		47		6-Apr-08		8:06:20		65.01		37.5		6-Apr-08		8:07:53		67.4		36.5		17-May-08		8:25:59		74.6		41.5

		6-Apr-08		10:07:10		67.4		45		6-Apr-08		10:06:20		66.81		37		6-Apr-08		10:07:53		69.2		36.5		17-May-08		10:25:59		74.01		43

		6-Apr-08		12:07:10		67.4		46		6-Apr-08		12:06:20		68		35.5		6-Apr-08		12:07:53		70.41		36.5		17-May-08		12:25:59		73.4		46.5

		6-Apr-08		14:07:10		67.4		46		6-Apr-08		14:06:20		68		37		6-Apr-08		14:07:53		70.41		39		17-May-08		14:25:59		74.01		45.5

		6-Apr-08		16:07:10		68		45.5		6-Apr-08		16:06:20		68		39		6-Apr-08		16:07:53		70.41		40.5		17-May-08		16:25:59		74.01		45

		6-Apr-08		18:07:10		67.4		46.5		6-Apr-08		18:06:20		67.4		38.5		6-Apr-08		18:07:53		71		40		17-May-08		18:25:59		73.4		42.5

		6-Apr-08		20:07:10		68		45.5		6-Apr-08		20:06:20		67.4		39.5		6-Apr-08		20:07:53		72.21		38		17-May-08		20:25:59		75.2		42.5

		6-Apr-08		22:07:10		67.4		43.5		6-Apr-08		22:06:20		67.4		39.5		6-Apr-08		22:07:53		71.6		37		17-May-08		22:25:59		75.81		40

		7-Apr-08		0:07:10		67.4		44		7-Apr-08		0:06:20		66.81		39		7-Apr-08		0:07:53		71		36.5		18-May-08		0:25:59		75.2		39.5

		7-Apr-08		2:07:10		68		46		7-Apr-08		2:06:20		66.2		37.5		7-Apr-08		2:07:53		69.8		36		18-May-08		2:25:59		74.6		40

		7-Apr-08		4:07:10		67.4		45		7-Apr-08		4:06:20		65.6		38		7-Apr-08		4:07:53		69.2		36.5		18-May-08		4:25:59		73.4		40

		7-Apr-08		6:07:10		67.4		45.5		7-Apr-08		6:06:20		65.6		38		7-Apr-08		6:07:53		68.61		37		18-May-08		6:25:59		73.4		39.5

		7-Apr-08		8:07:10		67.4		46.5		7-Apr-08		8:06:20		65.6		39		7-Apr-08		8:07:53		68		37		18-May-08		8:25:59		74.01		40.5

		7-Apr-08		10:07:10		67.4		46		7-Apr-08		10:06:20		66.81		40		7-Apr-08		10:07:53		69.8		37.5		18-May-08		10:25:59		75.81		41.5

		7-Apr-08		12:07:10		68		45		7-Apr-08		12:06:20		66.81		44		7-Apr-08		12:07:53		69.8		39		18-May-08		12:25:59		77.61		42

		7-Apr-08		14:07:10		67.4		45		7-Apr-08		14:06:20		67.4		36		7-Apr-08		14:07:53		71		37		18-May-08		14:25:59		79.41		43

		7-Apr-08		16:07:10		67.4		45.5		7-Apr-08		16:06:20		66.81		35.5		7-Apr-08		16:07:53		71.6		35.5		18-May-08		16:25:59		79.41		41.5

		7-Apr-08		18:07:10		67.4		45.5		7-Apr-08		18:06:20		67.4		33		7-Apr-08		18:07:53		72.21		34.5		18-May-08		18:25:59		78.2		41.5

		7-Apr-08		20:07:10		67.4		44.5		7-Apr-08		20:06:20		66.81		31.5		7-Apr-08		20:07:53		71.6		33		18-May-08		20:25:59		77.61		41

		7-Apr-08		22:07:10		68		46		7-Apr-08		22:06:20		67.4		32.5		7-Apr-08		22:07:53		71		33		18-May-08		22:25:59		76.4		40

		8-Apr-08		0:07:10		67.4		44.5		8-Apr-08		0:06:20		66.81		34		8-Apr-08		0:07:53		69.8		33		19-May-08		0:25:59		74.6		39.5

		8-Apr-08		2:07:10		67.4		46.5		8-Apr-08		2:06:20		66.2		35.5		8-Apr-08		2:07:53		69.2		34		19-May-08		2:25:59		73.4		39

		8-Apr-08		4:07:10		67.4		45.5		8-Apr-08		4:06:20		65.6		35.5		8-Apr-08		4:07:53		68		34.5		19-May-08		4:25:59		72.21		39

		8-Apr-08		6:07:10		67.4		46		8-Apr-08		6:06:20		65.01		35		8-Apr-08		6:07:53		68		35		19-May-08		6:25:59		72.21		39.5

		8-Apr-08		8:07:10		67.4		46.5		8-Apr-08		8:06:20		66.2		35		8-Apr-08		8:07:53		71.6		35		19-May-08		8:25:59		72.21		40

		8-Apr-08		10:07:10		67.4		45		8-Apr-08		10:06:20		68		31.5		8-Apr-08		10:07:53		71.6		33.5		19-May-08		10:25:59		72.8		41.5

		8-Apr-08		12:07:10		66.81		46.5		8-Apr-08		12:06:20		68		29.5		8-Apr-08		12:07:53		71.6		34.5		19-May-08		12:25:59		74.6		41.5

		8-Apr-08		14:07:10		66.81		47		8-Apr-08		14:06:20		67.4		28.5		8-Apr-08		14:07:53		71		34.5		19-May-08		14:25:59		75.81		42

		8-Apr-08		16:07:10		66.81		46.5		8-Apr-08		16:06:20		67.4		35		8-Apr-08		16:07:53		71		37		19-May-08		16:25:59		77		41.5

		8-Apr-08		18:07:10		66.81		46		8-Apr-08		18:06:20		66.81		33		8-Apr-08		18:07:53		71.6		35		19-May-08		18:25:59		77.61		40

		8-Apr-08		20:07:10		66.81		46.5		8-Apr-08		20:06:20		66.81		38.5		8-Apr-08		20:07:53		71		34.5		19-May-08		20:25:59		77		39.5

		8-Apr-08		22:07:10		67.4		47		8-Apr-08		22:06:20		66.2		34		8-Apr-08		22:07:53		71.6		37.5		19-May-08		22:25:59		74.6		39.5

		9-Apr-08		0:07:10		66.81		45.5		9-Apr-08		0:06:20		66.2		38		9-Apr-08		0:07:53		71		35.5		20-May-08		0:25:59		73.4		40

		9-Apr-08		2:07:10		66.81		48		9-Apr-08		2:06:20		66.2		35.5		9-Apr-08		2:07:53		70.41		35		20-May-08		2:25:59		72.21		40

		9-Apr-08		4:07:10		66.81		47.5		9-Apr-08		4:06:20		66.2		36		9-Apr-08		4:07:53		69.8		34.5		20-May-08		4:25:59		72.21		40

		9-Apr-08		6:07:10		66.81		44		9-Apr-08		6:06:20		66.2		37		9-Apr-08		6:07:53		69.8		35.5		20-May-08		6:25:59		72.21		40.5

		9-Apr-08		8:07:10		66.81		47.5		9-Apr-08		8:06:20		66.81		37		9-Apr-08		8:07:53		71		38		20-May-08		8:25:59		71.6		42

		9-Apr-08		10:07:10		66.81		46		9-Apr-08		10:06:20		67.4		34		9-Apr-08		10:07:53		71		34.5		20-May-08		10:25:59		73.4		42.5

		9-Apr-08		12:07:10		66.81		45		9-Apr-08		12:06:20		68		32		9-Apr-08		12:07:53		71		38.5		20-May-08		12:25:59		74.01		43.5

		9-Apr-08		14:07:10		66.81		45		9-Apr-08		14:06:20		68.61		29.5		9-Apr-08		14:07:53		70.41		38.5		20-May-08		14:25:59		74.01		44.5

		9-Apr-08		16:07:10		66.81		47		9-Apr-08		16:06:20		67.4		36		9-Apr-08		16:07:53		71		41.5		20-May-08		16:25:59		74.6		44

		9-Apr-08		18:07:10		66.81		46.5		9-Apr-08		18:06:20		68		34		9-Apr-08		18:07:53		71.6		39.5		20-May-08		18:25:59		74.01		43.5

		9-Apr-08		20:07:10		67.4		47		9-Apr-08		20:06:20		67.4		33.5		9-Apr-08		20:07:53		75.2		35		20-May-08		20:25:59		74.6		43

		9-Apr-08		22:07:10		66.81		47		9-Apr-08		22:06:20		66.81		34.5		9-Apr-08		22:07:53		72.8		34.5		20-May-08		22:25:59		74.01		41

		10-Apr-08		0:07:10		66.81		47.5		10-Apr-08		0:06:20		66.2		33.5		10-Apr-08		0:07:53		70.41		33.5		21-May-08		0:25:59		72.8		41

		10-Apr-08		2:07:10		66.81		47		10-Apr-08		2:06:20		65.6		34.5		10-Apr-08		2:07:53		69.8		33		21-May-08		2:25:59		72.21		41

		10-Apr-08		4:07:10		66.81		47		10-Apr-08		4:06:20		65.01		34.5		10-Apr-08		4:07:53		69.2		33.5		21-May-08		4:25:59		72.21		41

		10-Apr-08		6:07:10		67.4		46		10-Apr-08		6:06:20		65.6		34.5		10-Apr-08		6:07:53		68.61		34.5		21-May-08		6:25:59		72.21		40.5

		10-Apr-08		8:07:10		66.81		47		10-Apr-08		8:06:20		66.2		34.5		10-Apr-08		8:07:53		69.8		35		21-May-08		8:25:59		72.21		42

		10-Apr-08		10:07:10		66.81		47.5		10-Apr-08		10:06:20		68		34		10-Apr-08		10:07:53		70.41		38		21-May-08		10:25:59		73.4		42.5

		10-Apr-08		12:07:10		66.81		47		10-Apr-08		12:06:20		69.2		34		10-Apr-08		12:07:53		70.41		35		21-May-08		12:25:59		73.4		43

		10-Apr-08		14:07:10		66.81		47.5		10-Apr-08		14:06:20		69.8		36		10-Apr-08		14:07:53		71		42.5		21-May-08		14:25:59		74.01		44

		10-Apr-08		16:07:10		66.81		46.5		10-Apr-08		16:06:20		69.2		39.5		10-Apr-08		16:07:53		70.41		47		21-May-08		16:25:59		74.01		41

		10-Apr-08		18:07:10		66.81		47.5		10-Apr-08		18:06:20		68		32		10-Apr-08		18:07:53		69.8		35.5		21-May-08		18:25:59		74.01		35

		10-Apr-08		20:07:10		66.81		46.5		10-Apr-08		20:06:20		67.4		37		10-Apr-08		20:07:53		70.41		41.5		21-May-08		20:25:59		73.4		34.5

		10-Apr-08		22:07:10		66.81		47		10-Apr-08		22:06:20		67.4		37		10-Apr-08		22:07:53		71		37.5		21-May-08		22:25:59		74.01		35

		11-Apr-08		0:07:10		66.81		47.5		11-Apr-08		0:06:20		68		36.5		11-Apr-08		0:07:53		69.2		38		22-May-08		0:25:59		73.4		34.5

		11-Apr-08		2:07:10		66.81		46.5		11-Apr-08		2:06:20		66.81		36.5		11-Apr-08		2:07:53		69.8		36.5		22-May-08		2:25:59		72.21		34.5

		11-Apr-08		4:07:10		66.81		46.5		11-Apr-08		4:06:20		66.2		37.5		11-Apr-08		4:07:53		69.8		35.5		22-May-08		4:25:59		71.6		34

		11-Apr-08		6:07:10		66.81		46.5		11-Apr-08		6:06:20		65.6		37.5		11-Apr-08		6:07:53		69.2		36.5		22-May-08		6:25:59		72.21		32.5

		11-Apr-08		8:07:10		66.81		47.5		11-Apr-08		8:06:20		66.81		38		11-Apr-08		8:07:53		70.41		38.5		22-May-08		8:25:59		71.6		33.5

		11-Apr-08		10:07:10		66.81		48		11-Apr-08		10:06:20		68		36.5		11-Apr-08		10:07:53		70.41		36		22-May-08		10:25:59		73.4		34

		11-Apr-08		12:07:10		66.2		48.5		11-Apr-08		12:06:20		68.61		35		11-Apr-08		12:07:53		71		39.5		22-May-08		12:25:59		73.4		35

		11-Apr-08		14:07:10		66.81		48		11-Apr-08		14:06:20		68.61		34.5		11-Apr-08		14:07:53		70.41		45.5		22-May-08		14:25:59		74.01		35

		11-Apr-08		16:07:10		66.2		45.5		11-Apr-08		16:06:20		68.61		40		11-Apr-08		16:07:53		70.41		47.5		22-May-08		16:25:59		74.01		35

		11-Apr-08		18:07:10		66.81		48		11-Apr-08		18:06:20		68.61		37.5		11-Apr-08		18:07:53		71		45.5		22-May-08		18:25:59		74.01		34.5

		11-Apr-08		20:07:10		66.81		47.5		11-Apr-08		20:06:20		68.61		39.5		11-Apr-08		20:07:53		70.41		42		22-May-08		20:25:59		73.4		34.5

		11-Apr-08		22:07:10		66.81		47		11-Apr-08		22:06:20		67.4		42.5		11-Apr-08		22:07:53		70.41		43		22-May-08		22:25:59		72.8		33.5

		12-Apr-08		0:07:10		66.81		48		12-Apr-08		0:06:20		68		41.5		12-Apr-08		0:07:53		69.8		41.5		23-May-08		0:25:59		72.21		33

		12-Apr-08		2:07:10		66.81		47		12-Apr-08		2:06:20		66.81		42		12-Apr-08		2:07:53		69.8		39		23-May-08		2:25:59		71		32.5

		12-Apr-08		4:07:10		66.81		47.5		12-Apr-08		4:06:20		66.2		41		12-Apr-08		4:07:53		70.41		38.5		23-May-08		4:25:59		71.6		31.5

		12-Apr-08		6:07:10		66.81		47.5		12-Apr-08		6:06:20		66.2		40.5		12-Apr-08		6:07:53		70.41		38		23-May-08		6:25:59		71.6		30.5

		12-Apr-08		8:07:10		66.81		48.5		12-Apr-08		8:06:20		68		39.5		12-Apr-08		8:07:53		69.8		36		23-May-08		8:25:59		71		31.5

		12-Apr-08		10:07:10		66.81		47.5		12-Apr-08		10:06:20		68.61		43		12-Apr-08		10:07:53		70.41		43		23-May-08		10:25:59		73.4		31

		12-Apr-08		12:07:10		66.81		47		12-Apr-08		12:06:20		68		39		12-Apr-08		12:07:53		69.8		47.5		23-May-08		12:25:59		73.4		29.5

		12-Apr-08		14:07:10		67.4		46.5		12-Apr-08		14:06:20		68.61		33.5		12-Apr-08		14:07:53		70.41		40.5		23-May-08		14:25:59		74.01		29

		12-Apr-08		16:07:10		67.4		48		12-Apr-08		16:06:20		67.4		35		12-Apr-08		16:07:53		72.21		40		23-May-08		16:25:59		74.6		30

		12-Apr-08		18:07:10		67.4		45.5		12-Apr-08		18:06:20		67.4		34		12-Apr-08		18:07:53		68		45		23-May-08		18:25:59		74.01		31

		12-Apr-08		20:07:10		67.4		46.5		12-Apr-08		20:06:20		66.81		32.5		12-Apr-08		20:07:53		68		45		23-May-08		20:25:59		74.01		32

		12-Apr-08		22:07:10		67.4		46.5		12-Apr-08		22:06:20		66.2		38.5		12-Apr-08		22:07:53		68		44		23-May-08		22:25:59		74.6		31.5

		13-Apr-08		0:07:10		67.4		46		13-Apr-08		0:06:20		66.81		41		13-Apr-08		0:07:53		66.81		46		24-May-08		0:25:59		73.4		31.5

		13-Apr-08		2:07:10		67.4		46		13-Apr-08		2:06:20		65.6		42		13-Apr-08		2:07:53		66.81		45.5		24-May-08		2:25:59		72.21		32

		13-Apr-08		4:07:10		68		45.5		13-Apr-08		4:06:20		65.6		41		13-Apr-08		4:07:53		66.2		46.5		24-May-08		4:25:59		71.6		32

		13-Apr-08		6:07:10		68		46.5		13-Apr-08		6:06:20		66.81		40		13-Apr-08		6:07:53		66.2		47		24-May-08		6:25:59		72.21		31.5

		13-Apr-08		8:07:10		67.4		46.5		13-Apr-08		8:06:20		66.2		40.5		13-Apr-08		8:07:53		66.2		47.5		24-May-08		8:25:59		71.6		33

		13-Apr-08		10:07:10		68		47		13-Apr-08		10:06:20		66.81		42		13-Apr-08		10:07:53		66.81		47		24-May-08		10:25:59		74.01		33.5

		13-Apr-08		12:07:10		67.4		46		13-Apr-08		12:06:20		67.4		41.5		13-Apr-08		12:07:53		67.4		45.5		24-May-08		12:25:59		73.4		35

		13-Apr-08		14:07:10		67.4		46.5		13-Apr-08		14:06:20		67.4		43		13-Apr-08		14:07:53		67.4		46		24-May-08		14:25:59		74.01		35

		13-Apr-08		16:07:10		67.4		46		13-Apr-08		16:06:20		66.81		40		13-Apr-08		16:07:53		68		45.5		24-May-08		16:25:59		74.01		34.5

		13-Apr-08		18:07:10		67.4		46.5		13-Apr-08		18:06:20		66.81		38.5		13-Apr-08		18:07:53		67.4		45.5		24-May-08		18:25:59		74.01		34.5

		13-Apr-08		20:07:10		68		46		13-Apr-08		20:06:20		66.2		43.5		13-Apr-08		20:07:53		67.4		46		24-May-08		20:25:59		74.01		35.5

		13-Apr-08		22:07:10		67.4		47.5		13-Apr-08		22:06:20		66.2		53.5		13-Apr-08		22:07:53		67.4		46.5		24-May-08		22:25:59		74.01		35

		14-Apr-08		0:07:10		67.4		46		14-Apr-08		0:06:20		66.2		48.5		14-Apr-08		0:07:53		66.81		47		25-May-08		0:25:59		72.8		35.5

		14-Apr-08		2:07:10		67.4		46		14-Apr-08		2:06:20		66.2		46		14-Apr-08		2:07:53		66.81		47		25-May-08		2:25:59		72.21		36

		14-Apr-08		4:07:10		67.4		46		14-Apr-08		4:06:20		65.6		45.5		14-Apr-08		4:07:53		66.2		47.5		25-May-08		4:25:59		71.6		36.5

		14-Apr-08		6:07:10		68.61		46		14-Apr-08		6:06:20		65.6		44		14-Apr-08		6:07:53		66.2		48		25-May-08		6:25:59		71.6		37

		14-Apr-08		8:07:10		67.4		46		14-Apr-08		8:06:20		66.2		41.5		14-Apr-08		8:07:53		66.2		47		25-May-08		8:25:59		71.6		37.5

		14-Apr-08		10:07:10		68		46		14-Apr-08		10:06:20		66.2		43		14-Apr-08		10:07:53		66.2		48		25-May-08		10:25:59		71.6		38.5

		14-Apr-08		12:07:10		67.4		46		14-Apr-08		12:06:20		67.4		43		14-Apr-08		12:07:53		66.81		47		25-May-08		12:25:59		71.6		40

		14-Apr-08		14:07:10		67.4		48		14-Apr-08		14:06:20		67.4		45.5		14-Apr-08		14:07:53		67.4		48.5		25-May-08		14:25:59		71.6		40.5

		14-Apr-08		16:07:10		67.4		46		14-Apr-08		16:06:20		66.81		43		14-Apr-08		16:07:53		66.81		47		25-May-08		16:25:59		71.6		40

		14-Apr-08		18:07:10		67.4		47		14-Apr-08		18:06:20		66.81		46.5		14-Apr-08		18:07:53		66.81		48		25-May-08		18:25:59		71.6		41

		14-Apr-08		20:07:10		67.4		47		14-Apr-08		20:06:20		66.2		50		14-Apr-08		20:07:53		66.2		48		25-May-08		20:25:59		71.6		41

		14-Apr-08		22:07:10		68		45.5		14-Apr-08		22:06:20		66.2		46		14-Apr-08		22:07:53		66.2		48		25-May-08		22:25:59		71.6		41

		15-Apr-08		0:07:10		67.4		46		15-Apr-08		0:06:20		65.6		49		15-Apr-08		0:07:53		66.81		47		26-May-08		0:25:59		71.6		40

		15-Apr-08		2:07:10		67.4		47		15-Apr-08		2:06:20		66.2		46		15-Apr-08		2:07:53		66.81		47.5		26-May-08		2:25:59		71.6		38.5

		15-Apr-08		4:07:10		67.4		44		15-Apr-08		4:06:20		65.6		45		15-Apr-08		4:07:53		66.81		47.5		26-May-08		4:25:59		71.6		37.5

		15-Apr-08		6:07:10		68		46		15-Apr-08		6:06:20		65.01		45		15-Apr-08		6:07:53		66.2		48		26-May-08		6:25:59		71.6		37

		15-Apr-08		8:07:10		67.4		45.5		15-Apr-08		8:06:20		67.4		45		15-Apr-08		8:07:53		65.6		49.5		26-May-08		8:25:59		71.6		37.5

		15-Apr-08		10:07:10		67.4		47		15-Apr-08		10:06:20		69.2		44		15-Apr-08		10:07:53		65.01		49		26-May-08		10:25:59		71.6		39.5

		15-Apr-08		12:07:10		67.4		47		15-Apr-08		12:06:20		69.8		37.5		15-Apr-08		12:07:53		65.6		49		26-May-08		12:25:59		72.21		38.5

		15-Apr-08		14:07:10		67.4		41		15-Apr-08		14:06:20		71		33.5		15-Apr-08		14:07:53		66.2		47.5		26-May-08		14:25:59		72.8		38

		15-Apr-08		16:07:10		67.4		45.5		15-Apr-08		16:06:20		70.41		32.5		15-Apr-08		16:07:53		66.81		47		26-May-08		16:25:59		73.4		36.5

		15-Apr-08		18:07:10		67.4		45.5		15-Apr-08		18:06:20		69.2		31.5		15-Apr-08		18:07:53		68		45.5		26-May-08		18:25:59		74.01		36

		15-Apr-08		20:07:10		67.4		45		15-Apr-08		20:06:20		69.2		29		15-Apr-08		20:07:53		67.4		45		26-May-08		20:25:59		74.01		35.5

		15-Apr-08		22:07:10		68		45.5		15-Apr-08		22:06:20		68		31.5		15-Apr-08		22:07:53		67.4		45		26-May-08		22:25:59		72.21		37

		16-Apr-08		0:07:10		67.4		37		16-Apr-08		0:06:20		66.81		34.5		16-Apr-08		0:07:53		67.4		45.5		27-May-08		0:25:59		72.21		37.5

		16-Apr-08		2:07:10		67.4		46.5		16-Apr-08		2:06:20		65.6		33		16-Apr-08		2:07:53		68		44.5		27-May-08		2:25:59		71.6		37.5

		16-Apr-08		4:07:10		67.4		45		16-Apr-08		4:06:20		65.01		33		16-Apr-08		4:07:53		68		45		27-May-08		4:25:59		71.6		37.5

		16-Apr-08		6:07:10		67.4		45.5		16-Apr-08		6:06:20		65.01		33.5		16-Apr-08		6:07:53		68		44.5		27-May-08		6:25:59		72.21		37.5

		16-Apr-08		8:07:10		67.4		46		16-Apr-08		8:06:20		68		32.5		16-Apr-08		8:07:53		67.4		44		27-May-08		8:25:59		71		39

		16-Apr-08		10:07:10		69.2		34		16-Apr-08		10:06:20		70.41		30		16-Apr-08		10:07:53		66.2		47.5		27-May-08		10:25:59		71		39.5

		16-Apr-08		12:07:10		69.8		44		16-Apr-08		12:06:20		68.61		27.5		16-Apr-08		12:07:53		66.2		48		27-May-08		12:25:59		72.21		40.5

		16-Apr-08		14:07:10		70.41		43		16-Apr-08		14:06:20		69.8		26		16-Apr-08		14:07:53		66.2		49.5		27-May-08		14:25:59		72.8		40

		16-Apr-08		16:07:10		70.41		46		16-Apr-08		16:06:20		69.2		28		16-Apr-08		16:07:53		67.4		47		27-May-08		16:25:59		72.8		39.5

		16-Apr-08		18:07:10		70.41		45.5		16-Apr-08		18:06:20		68.61		31		16-Apr-08		18:07:53		68		48		27-May-08		18:25:59		72.8		41

		16-Apr-08		20:07:10		69.2		44.5		16-Apr-08		20:06:20		68		30		16-Apr-08		20:07:53		67.4		44.5		27-May-08		20:25:59		72.8		40.5

		16-Apr-08		22:07:10		69.2		44.5		16-Apr-08		22:06:20		68		30		16-Apr-08		22:07:53		68		45		27-May-08		22:25:59		72.21		39.5

		17-Apr-08		0:07:10		70.41		46		17-Apr-08		0:06:20		67.4		31.5		17-Apr-08		0:07:53		68		41		28-May-08		0:25:59		72.21		39.5

		17-Apr-08		2:07:10		70.41		43.5		17-Apr-08		2:06:20		66.2		33		17-Apr-08		2:07:53		68		48.5		28-May-08		2:25:59		72.21		40

		17-Apr-08		4:07:10		69.8		46		17-Apr-08		4:06:20		65.6		34		17-Apr-08		4:07:53		68		46.5		28-May-08		4:25:59		71.6		40

		17-Apr-08		6:07:10		69.8		46		17-Apr-08		6:06:20		65.6		34.5		17-Apr-08		6:07:53		68		47		28-May-08		6:25:59		72.21		40.5

		17-Apr-08		8:07:10		71		44.5		17-Apr-08		8:06:20		69.2		33		17-Apr-08		8:07:53		67.4		48		28-May-08		8:25:59		71.6		42.5

		17-Apr-08		10:07:10		70.41		44.5		17-Apr-08		10:06:20		70.41		31.5		17-Apr-08		10:07:53		66.81		45.5		28-May-08		10:25:59		73.4		42

		17-Apr-08		12:07:10		71		45.5		17-Apr-08		12:06:20		71		29		17-Apr-08		12:07:53		68		48.5		28-May-08		12:25:59		74.01		41

		17-Apr-08		14:07:10		71		45.5		17-Apr-08		14:06:20		69.2		29.5		17-Apr-08		14:07:53		67.4		49.5		28-May-08		14:25:59		74.01		41.5

		17-Apr-08		16:07:10		71		45.5		17-Apr-08		16:06:20		68.61		31.5		17-Apr-08		16:07:53		68		48		28-May-08		16:25:59		74.6		39.5

		17-Apr-08		18:07:10		71		46.5		17-Apr-08		18:06:20		70.41		31		17-Apr-08		18:07:53		68.61		48		28-May-08		18:25:59		75.2		38

		17-Apr-08		20:07:10		71		44.5		17-Apr-08		20:06:20		69.8		34.5		17-Apr-08		20:07:53		67.4		46.5		28-May-08		20:25:59		74.6		39.5

		17-Apr-08		22:07:10		69.8		42.5		17-Apr-08		22:06:20		69.8		36.5		17-Apr-08		22:07:53		67.4		46		28-May-08		22:25:59		74.01		38

		18-Apr-08		0:07:10		70.41		45.5		18-Apr-08		0:06:20		68.61		38		18-Apr-08		0:07:53		68		48.5		29-May-08		0:25:59		72.8		38

		18-Apr-08		2:07:10		70.41		42.5		18-Apr-08		2:06:20		67.4		39		18-Apr-08		2:07:53		68		47.5		29-May-08		2:25:59		72.21		38

		18-Apr-08		4:07:10		69.8		46.5		18-Apr-08		4:06:20		66.2		39.5		18-Apr-08		4:07:53		68		47.5		29-May-08		4:25:59		72.21		38.5

		18-Apr-08		6:07:10		69.8		46		18-Apr-08		6:06:20		65.6		40		18-Apr-08		6:07:53		68		42		29-May-08		6:25:59		72.8		38.5

		18-Apr-08		8:07:10		70.41		46.5		18-Apr-08		8:06:20		68.61		39		18-Apr-08		8:07:53		67.4		49		29-May-08		8:25:59		72.8		40

		18-Apr-08		10:07:10		70.41		46		18-Apr-08		10:06:20		71		37.5		18-Apr-08		10:07:53		67.4		47.5		29-May-08		10:25:59		74.01		39

		18-Apr-08		12:07:10		71		44		18-Apr-08		12:06:20		72.21		36.5		18-Apr-08		12:07:53		68		49		29-May-08		12:25:59		74.6		39.5

		18-Apr-08		14:07:10		70.41		44.5		18-Apr-08		14:06:20		71		34.5		18-Apr-08		14:07:53		66.81		49.5		29-May-08		14:25:59		75.2		39

		18-Apr-08		16:07:10		70.41		42.5		18-Apr-08		16:06:20		71		39		18-Apr-08		16:07:53		67.4		49		29-May-08		16:25:59		74.6		39

		18-Apr-08		18:07:10		70.41		45		18-Apr-08		18:06:20		70.41		38		18-Apr-08		18:07:53		68		47.5		29-May-08		18:25:59		74.6		38

		18-Apr-08		20:07:10		70.41		44.5		18-Apr-08		20:06:20		69.8		41		18-Apr-08		20:07:53		67.4		48.5		29-May-08		20:25:59		74.6		39.5

		18-Apr-08		22:07:10		70.41		45.5		18-Apr-08		22:06:20		69.2		41		18-Apr-08		22:07:53		68		48.5		29-May-08		22:25:59		74.6		38.5

		19-Apr-08		0:07:10		69.8		44.5		19-Apr-08		0:06:20		68		42.5		19-Apr-08		0:07:53		67.4		49		30-May-08		0:25:59		74.01		38.5

		19-Apr-08		2:07:10		69.8		45		19-Apr-08		2:06:20		67.4		45		19-Apr-08		2:07:53		67.4		49		30-May-08		2:25:59		72.8		38.5

		19-Apr-08		4:07:10		69.8		40		19-Apr-08		4:06:20		66.81		45		19-Apr-08		4:07:53		68		46.5		30-May-08		4:25:59		72.21		39

		19-Apr-08		6:07:10		69.8		45.5		19-Apr-08		6:06:20		66.81		45		19-Apr-08		6:07:53		68		49		30-May-08		6:25:59		72.21		39.5

		19-Apr-08		8:07:10		69.8		45		19-Apr-08		8:06:20		71		41		19-Apr-08		8:07:53		66.81		50		30-May-08		8:25:59		72.21		41.5

		19-Apr-08		10:07:10		69.8		45		19-Apr-08		10:06:20		71.6		40.5		19-Apr-08		10:07:53		66.81		50		30-May-08		10:25:59		74.6		41.5

		19-Apr-08		12:07:10		70.41		44.5		19-Apr-08		12:06:20		71.6		39		19-Apr-08		12:07:53		66.81		50		30-May-08		12:25:59		74.6		41.5

		19-Apr-08		14:07:10		70.41		42		19-Apr-08		14:06:20		72.8		41		19-Apr-08		14:07:53		66.81		48		30-May-08		14:25:59		74.6		41.5

		19-Apr-08		16:07:10		70.41		45		19-Apr-08		16:06:20		69.8		42.5		19-Apr-08		16:07:53		67.4		48		30-May-08		16:25:59		75.2		40.5

		19-Apr-08		18:07:10		69.8		45		19-Apr-08		18:06:20		69.8		43.5		19-Apr-08		18:07:53		67.4		49.5		30-May-08		18:25:59		74.6		39

		19-Apr-08		20:07:10		69.8		42		19-Apr-08		20:06:20		68.61		41		19-Apr-08		20:07:53		67.4		46		30-May-08		20:25:59		74.6		41

		19-Apr-08		22:07:10		69.8		44.5		19-Apr-08		22:06:20		68.61		39		19-Apr-08		22:07:53		67.4		49.5		30-May-08		22:25:59		74.6		39.5

		20-Apr-08		0:07:10		69.2		44		20-Apr-08		0:06:20		67.4		40		20-Apr-08		0:07:53		67.4		49.5		31-May-08		0:25:59		74.01		39

		20-Apr-08		2:07:10		69.2		44.5		20-Apr-08		2:06:20		66.2		40		20-Apr-08		2:07:53		67.4		48		31-May-08		2:25:59		72.8		39.5

		20-Apr-08		4:07:10		68.61		45.5		20-Apr-08		4:06:20		65.01		38.5		20-Apr-08		4:07:53		66.81		48.5		31-May-08		4:25:59		72.21		40

		20-Apr-08		6:07:10		68.61		46.5		20-Apr-08		6:06:20		65.01		36		20-Apr-08		6:07:53		67.4		48.5		31-May-08		6:25:59		71.6		41

		20-Apr-08		8:07:10		68.61		47		20-Apr-08		8:06:20		65.01		33.5		20-Apr-08		8:07:53		67.4		47.5		31-May-08		8:25:59		71.6		42

		20-Apr-08		10:07:10		68.61		46		20-Apr-08		10:06:20		67.4		30		20-Apr-08		10:07:53		68		47.5		31-May-08		10:25:59		73.4		42.5

		20-Apr-08		12:07:10		69.2		43.5		20-Apr-08		12:06:20		69.2		26		20-Apr-08		12:07:53		67.4		44.5		31-May-08		12:25:59		74.6		42

		20-Apr-08		14:07:10		69.2		43.5		20-Apr-08		14:06:20		69.2		23		20-Apr-08		14:07:53		66.81		36.5		31-May-08		14:25:59		75.2		43.5

		20-Apr-08		16:07:10		69.2		45		20-Apr-08		16:06:20		69.2		23.5		20-Apr-08		16:07:53		67.4		47.5		31-May-08		16:25:59		74.6		43

		20-Apr-08		18:07:10		69.2		44		20-Apr-08		18:06:20		69.8		23		20-Apr-08		18:07:53		67.4		44.5		31-May-08		18:25:59		74.6		44.5

		20-Apr-08		20:07:10		69.2		45.5		20-Apr-08		20:06:20		68		25.5		20-Apr-08		20:07:53		67.4		47		31-May-08		20:25:59		74.6		43

		20-Apr-08		22:07:10		68.61		45		20-Apr-08		22:06:20		66.81		27.5		20-Apr-08		22:07:53		67.4		47.5		31-May-08		22:25:59		74.01		41

		21-Apr-08		0:07:10		68.61		46.5		21-Apr-08		0:06:20		65.6		29		21-Apr-08		0:07:53		67.4		48.5		1-Jun-08		0:25:59		72.8		41

		21-Apr-08		2:07:10		68		44.5		21-Apr-08		2:06:20		65.01		30.5		21-Apr-08		2:07:53		66.81		37.5		1-Jun-08		2:25:59		72.21		40.5

		21-Apr-08		4:07:10		68		46.5		21-Apr-08		4:06:20		63.8		31.5		21-Apr-08		4:07:53		66.81		47.5		1-Jun-08		4:25:59		71.6		40.5

		21-Apr-08		6:07:10		68		47.5		21-Apr-08		6:06:20		63.21		33		21-Apr-08		6:07:53		67.4		47.5		1-Jun-08		6:25:59		72.21		40.5

		21-Apr-08		8:07:10		68		44		21-Apr-08		8:06:20		63.21		33		21-Apr-08		8:07:53		67.4		47.5		1-Jun-08		8:25:59		72.21		40.5

		21-Apr-08		10:07:10		68		47.5		21-Apr-08		10:06:20		65.01		29		21-Apr-08		10:07:53		67.4		47.5		1-Jun-08		10:25:59		72.21		40.5

		21-Apr-08		12:07:10		68		42.5		21-Apr-08		12:06:20		67.4		24.5		21-Apr-08		12:07:53		67.4		42		1-Jun-08		12:25:59		73.4		41

		21-Apr-08		14:07:10		68.61		45.5		21-Apr-08		14:06:20		69.2		27.5		21-Apr-08		14:07:53		67.4		48		1-Jun-08		14:25:59		74.6		41.5

		21-Apr-08		16:07:10		68.61		45		21-Apr-08		16:06:20		69.2		29.5		21-Apr-08		16:07:53		67.4		48		1-Jun-08		16:25:59		75.81		41

		21-Apr-08		18:07:10		68.61		45		21-Apr-08		18:06:20		69.2		27		21-Apr-08		18:07:53		66.81		46.5		1-Jun-08		18:25:59		77		39.5

		21-Apr-08		20:07:10		69.2		45		21-Apr-08		20:06:20		68		30		21-Apr-08		20:07:53		67.4		48		1-Jun-08		20:25:59		76.4		39.5

		21-Apr-08		22:07:10		68.61		46.5		21-Apr-08		22:06:20		66.2		32		21-Apr-08		22:07:53		67.4		48.5		1-Jun-08		22:25:59		74.6		39

		22-Apr-08		0:07:10		68.61		45		22-Apr-08		0:06:20		65.01		30		22-Apr-08		0:07:53		67.4		48		2-Jun-08		0:25:59		72.8		39

		22-Apr-08		2:07:10		68		47		22-Apr-08		2:06:20		64.4		32		22-Apr-08		2:07:53		67.4		48		2-Jun-08		2:25:59		72.21		38.5

		22-Apr-08		4:07:10		67.4		47		22-Apr-08		4:06:20		63.8		32.5		22-Apr-08		4:07:53		66.81		41		2-Jun-08		4:25:59		72.21		38

		22-Apr-08		6:07:10		68		46.5		22-Apr-08		6:06:20		63.21		34		22-Apr-08		6:07:53		67.4		48		2-Jun-08		6:25:59		71.6		37.5

		22-Apr-08		8:07:10		68.61		47		22-Apr-08		8:06:20		66.81		33.5		22-Apr-08		8:07:53		66.81		49		2-Jun-08		8:25:59		71.6		38

		22-Apr-08		10:07:10		69.2		44.5		22-Apr-08		10:06:20		71		29.5		22-Apr-08		10:07:53		66.2		49.5		2-Jun-08		10:25:59		72.21		39

		22-Apr-08		12:07:10		69.8		44		22-Apr-08		12:06:20		71		27.5		22-Apr-08		12:07:53		66.81		48		2-Jun-08		12:25:59		73.4		38.5

		22-Apr-08		14:07:10		69.8		46		22-Apr-08		14:06:20		71		31		22-Apr-08		14:07:53		66.2		49.5		2-Jun-08		14:25:59		75.2		38

		22-Apr-08		16:07:10		69.2		44.5		22-Apr-08		16:06:20		69.8		32.5		22-Apr-08		16:07:53		67.4		47.5		2-Jun-08		16:25:59		75.81		38

		22-Apr-08		18:07:10		69.2		45		22-Apr-08		18:06:20		69.8		32		22-Apr-08		18:07:53		68		46.5		2-Jun-08		18:25:59		76.4		37

		22-Apr-08		20:07:10		69.8		45		22-Apr-08		20:06:20		69.2		31.5		22-Apr-08		20:07:53		68		46.5		2-Jun-08		20:25:59		75.81		37

		22-Apr-08		22:07:10		69.8		43.5		22-Apr-08		22:06:20		68		32		22-Apr-08		22:07:53		68		47		2-Jun-08		22:25:59		74.01		37.5

		23-Apr-08		0:07:10		69.2		45		23-Apr-08		0:06:20		66.81		32		23-Apr-08		0:07:53		67.4		47.5		3-Jun-08		0:25:59		72.21		37

		23-Apr-08		2:07:10		68.61		45		23-Apr-08		2:06:20		65.6		33		23-Apr-08		2:07:53		67.4		47		3-Jun-08		2:25:59		72.21		36.5

		23-Apr-08		4:07:10		68.61		46.5		23-Apr-08		4:06:20		65.01		34.5		23-Apr-08		4:07:53		67.4		47.5		3-Jun-08		4:25:59		71.6		36

		23-Apr-08		6:07:10		68.61		43.5		23-Apr-08		6:06:20		64.4		35.5		23-Apr-08		6:07:53		67.4		47.5		3-Jun-08		6:25:59		72.21		35.5

		23-Apr-08		8:07:10		69.2		42.5		23-Apr-08		8:06:20		66.81		35.5		23-Apr-08		8:07:53		67.4		48		3-Jun-08		8:25:59		71.6		37.5

		23-Apr-08		10:07:10		69.8		46		23-Apr-08		10:06:20		70.41		32.5		23-Apr-08		10:07:53		67.4		48		3-Jun-08		10:25:59		74.01		38

		23-Apr-08		12:07:10		69.2		45.5		23-Apr-08		12:06:20		71		35.5		23-Apr-08		12:07:53		66.81		49.5		3-Jun-08		12:25:59		74.01		39

		23-Apr-08		14:07:10		69.8		45		23-Apr-08		14:06:20		71.6		41		23-Apr-08		14:07:53		66.2		50.5		3-Jun-08		14:25:59		74.6		39.5

		23-Apr-08		16:07:10		70.41		47		23-Apr-08		16:06:20		69.8		49		23-Apr-08		16:07:53		67.4		50.5		3-Jun-08		16:25:59		74.6		39

		23-Apr-08		18:07:10		70.41		44.5		23-Apr-08		18:06:20		69.2		47.5		23-Apr-08		18:07:53		68		50		3-Jun-08		18:25:59		74.6		38.5

		23-Apr-08		20:07:10		70.41		46		23-Apr-08		20:06:20		69.8		49.5		23-Apr-08		20:07:53		68		50		3-Jun-08		20:25:59		74.6		34.5

		23-Apr-08		22:07:10		70.41		46.5		23-Apr-08		22:06:20		69.2		48.5		23-Apr-08		22:07:53		68		50		3-Jun-08		22:25:59		74.6		31.5

		24-Apr-08		0:07:10		70.41		47		24-Apr-08		0:06:20		68		47		24-Apr-08		0:07:53		68		49.5		4-Jun-08		0:25:59		73.4		32.5

		24-Apr-08		2:07:10		69.8		44.5		24-Apr-08		2:06:20		66.81		47.5		24-Apr-08		2:07:53		68		49.5		4-Jun-08		2:25:59		72.8		33.5

		24-Apr-08		4:07:10		69.8		46.5		24-Apr-08		4:06:20		66.2		46		24-Apr-08		4:07:53		68		48.5		4-Jun-08		4:25:59		72.21		34

		24-Apr-08		6:07:10		69.8		46.5		24-Apr-08		6:06:20		65.6		44.5		24-Apr-08		6:07:53		68		49		4-Jun-08		6:25:59		72.21		33.5

		24-Apr-08		8:07:10		70.41		47		24-Apr-08		8:06:20		68		44		24-Apr-08		8:07:53		67.4		50		4-Jun-08		8:25:59		72.21		37

		24-Apr-08		10:07:10		70.41		46		24-Apr-08		10:06:20		70.41		46		24-Apr-08		10:07:53		68		49.5		4-Jun-08		10:25:59		74.01		41.5

		24-Apr-08		12:07:10		70.41		46.5		24-Apr-08		12:06:20		69.8		44.5		24-Apr-08		12:07:53		68		50		4-Jun-08		12:25:59		74.01		44

		24-Apr-08		14:07:10		70.41		46		24-Apr-08		14:06:20		71		36		24-Apr-08		14:07:53		68		49		4-Jun-08		14:25:59		74.01		44.5

		24-Apr-08		16:07:10		70.41		44.5		24-Apr-08		16:06:20		69.8		32		24-Apr-08		16:07:53		68		48		4-Jun-08		16:25:59		73.4		42

		24-Apr-08		18:07:10		69.8		44		24-Apr-08		18:06:20		70.41		31		24-Apr-08		18:07:53		68		45		4-Jun-08		18:25:59		73.4		39

		24-Apr-08		20:07:10		70.41		46		24-Apr-08		20:06:20		69.8		30.5		24-Apr-08		20:07:53		69.2		46.5		4-Jun-08		20:25:59		74.6		39.5

		24-Apr-08		22:07:10		70.41		46		24-Apr-08		22:06:20		68		33		24-Apr-08		22:07:53		68		48.5		4-Jun-08		22:25:59		74.6		38

		25-Apr-08		0:07:10		69.8		45		25-Apr-08		0:06:20		66.2		34		25-Apr-08		0:07:53		68		48.5		5-Jun-08		0:25:59		74.01		37.5

		25-Apr-08		2:07:10		69.2		46		25-Apr-08		2:06:20		65.01		35.5		25-Apr-08		2:07:53		68.61		46		5-Jun-08		2:25:59		72.8		36.5

		25-Apr-08		4:07:10		69.2		45		25-Apr-08		4:06:20		63.8		36		25-Apr-08		4:07:53		68		47.5		5-Jun-08		4:25:59		72.21		36

		25-Apr-08		6:07:10		69.8		45		25-Apr-08		6:06:20		63.21		36		25-Apr-08		6:07:53		68.61		47.5		5-Jun-08		6:25:59		72.21		35.5

		25-Apr-08		8:07:10		69.8		46		25-Apr-08		8:06:20		66.81		35.5		25-Apr-08		8:07:53		68.61		47.5		5-Jun-08		8:25:59		72.21		35.5

		25-Apr-08		10:07:10		69.8		45		25-Apr-08		10:06:20		70.41		32.5		25-Apr-08		10:07:53		67.4		49.5		5-Jun-08		10:25:59		74.01		35.5

		25-Apr-08		12:07:10		70.41		42.5		25-Apr-08		12:06:20		71		28.5		25-Apr-08		12:07:53		68.61		48		5-Jun-08		12:25:59		73.4		35

		25-Apr-08		14:07:10		70.41		45.5		25-Apr-08		14:06:20		71		28		25-Apr-08		14:07:53		68		47.5		5-Jun-08		14:25:59		73.4		34

		25-Apr-08		16:07:10		70.41		46		25-Apr-08		16:06:20		71.6		32.5		25-Apr-08		16:07:53		68.61		48.5		5-Jun-08		16:25:59		74.01		34.5

		25-Apr-08		18:07:10		70.41		45.5		25-Apr-08		18:06:20		70.41		31		25-Apr-08		18:07:53		68		40.5		5-Jun-08		18:25:59		73.4		35

		25-Apr-08		20:07:10		70.41		41.5		25-Apr-08		20:06:20		71		32.5		25-Apr-08		20:07:53		68		48		5-Jun-08		20:25:59		74.01		35.5

		25-Apr-08		22:07:10		69.8		45		25-Apr-08		22:06:20		70.41		35.5		25-Apr-08		22:07:53		68		46		5-Jun-08		22:25:59		74.6		34

		26-Apr-08		0:07:10		70.41		46		26-Apr-08		0:06:20		69.2		36.5		26-Apr-08		0:07:53		68		49		6-Jun-08		0:25:59		74.01		34.5

		26-Apr-08		2:07:10		69.8		45.5		26-Apr-08		2:06:20		67.4		38.5		26-Apr-08		2:07:53		68.61		48		6-Jun-08		2:25:59		72.21		35

		26-Apr-08		4:07:10		69.8		44.5		26-Apr-08		4:06:20		66.2		39		26-Apr-08		4:07:53		68		48		6-Jun-08		4:25:59		71.6		35

		26-Apr-08		6:07:10		69.8		46		26-Apr-08		6:06:20		65.6		38.5		26-Apr-08		6:07:53		68.61		48		6-Jun-08		6:25:59		71.6		35

		26-Apr-08		8:07:10		70.41		46.5		26-Apr-08		8:06:20		68.61		37.5		26-Apr-08		8:07:53		68.61		48.5		6-Jun-08		8:25:59		72.21		37

		26-Apr-08		10:07:10		70.41		45.5		26-Apr-08		10:06:20		71		35.5		26-Apr-08		10:07:53		68		46.5		6-Jun-08		10:25:59		73.4		37.5

		26-Apr-08		12:07:10		71		46.5		26-Apr-08		12:06:20		71		32.5		26-Apr-08		12:07:53		68.61		49		6-Jun-08		12:25:59		73.4		35.5

		26-Apr-08		14:07:10		71		32		26-Apr-08		14:06:20		69.2		31		26-Apr-08		14:07:53		67.4		36		6-Jun-08		14:25:59		74.01		37.5

		26-Apr-08		16:07:10		71		35		26-Apr-08		16:06:20		68.61		36		26-Apr-08		16:07:53		67.4		39.5		6-Jun-08		16:25:59		74.01		38.5

		26-Apr-08		18:07:10		71		39.5		26-Apr-08		18:06:20		69.2		39.5		26-Apr-08		18:07:53		68.61		42.5		6-Jun-08		18:25:59		73.4		38.5

		26-Apr-08		20:07:10		70.41		38		26-Apr-08		20:06:20		69.2		41		26-Apr-08		20:07:53		68.61		41		6-Jun-08		20:25:59		74.01		41

		26-Apr-08		22:07:10		69.8		38		26-Apr-08		22:06:20		68		42		26-Apr-08		22:07:53		68.61		40.5		6-Jun-08		22:25:59		74.6		39

		27-Apr-08		0:07:10		69.8		36.5		27-Apr-08		0:06:20		68		39.5		27-Apr-08		0:07:53		68.61		39.5		7-Jun-08		0:25:59		74.01		38.5

		27-Apr-08		2:07:10		70.41		36.5		27-Apr-08		2:06:20		68		39.5		27-Apr-08		2:07:53		68.61		39.5		7-Jun-08		2:25:59		72.8		39

		27-Apr-08		4:07:10		70.41		37.5		27-Apr-08		4:06:20		66.81		42.5		27-Apr-08		4:07:53		68.61		39.5		7-Jun-08		4:25:59		71.6		38.5

		27-Apr-08		6:07:10		69.8		36		27-Apr-08		6:06:20		67.4		40.5		27-Apr-08		6:07:53		68		39		7-Jun-08		6:25:59		72.21		37.5

		27-Apr-08		8:07:10		69.8		37.5		27-Apr-08		8:06:20		68		42		27-Apr-08		8:07:53		68.61		40.5		7-Jun-08		8:25:59		72.21		38

		27-Apr-08		10:07:10		70.41		40		27-Apr-08		10:06:20		69.2		43		27-Apr-08		10:07:53		68.61		42.5		7-Jun-08		10:25:59		73.4		37.5

		27-Apr-08		12:07:10		71		40		27-Apr-08		12:06:20		69.2		42.5		27-Apr-08		12:07:53		68		44		7-Jun-08		12:25:59		73.4		36

		27-Apr-08		14:07:10		71		40		27-Apr-08		14:06:20		69.2		40.5		27-Apr-08		14:07:53		69.2		42.5		7-Jun-08		14:25:59		73.4		34

		27-Apr-08		16:07:10		71		43		27-Apr-08		16:06:20		69.2		47		27-Apr-08		16:07:53		69.2		46		7-Jun-08		16:25:59		73.4		33.5

		27-Apr-08		18:07:10		71		42.5		27-Apr-08		18:06:20		69.2		43.5		27-Apr-08		18:07:53		69.2		44		7-Jun-08		18:25:59		73.4		34

		27-Apr-08		20:07:10		71.6		38		27-Apr-08		20:06:20		68		43.5		27-Apr-08		20:07:53		68.61		42.5		7-Jun-08		20:25:59		74.01		35

		27-Apr-08		22:07:10		71		37.5		27-Apr-08		22:06:20		68		42.5		27-Apr-08		22:07:53		68.61		41		7-Jun-08		22:25:59		74.01		33.5

		28-Apr-08		0:07:10		70.41		38.5		28-Apr-08		0:06:20		68		40		28-Apr-08		0:07:53		68.61		40		8-Jun-08		0:25:59		73.4		33

		28-Apr-08		2:07:10		69.8		39.5		28-Apr-08		2:06:20		68		45		28-Apr-08		2:07:53		68.61		42		8-Jun-08		2:25:59		72.21		33

		28-Apr-08		4:07:10		69.2		39.5		28-Apr-08		4:06:20		67.4		47.5		28-Apr-08		4:07:53		68		41.5		8-Jun-08		4:25:59		71.6		33

		28-Apr-08		6:07:10		69.2		39.5		28-Apr-08		6:06:20		67.4		45		28-Apr-08		6:07:53		68		41.5		8-Jun-08		6:25:59		71.6		33

		28-Apr-08		8:07:10		70.41		40		28-Apr-08		8:06:20		68		47		28-Apr-08		8:07:53		68.61		42.5		8-Jun-08		8:25:59		71.6		33

		28-Apr-08		10:07:10		70.41		40.5		28-Apr-08		10:06:20		68		47.5		28-Apr-08		10:07:53		68.61		43		8-Jun-08		10:25:59		72.21		34

		28-Apr-08		12:07:10		71		40		28-Apr-08		12:06:20		68.61		44		28-Apr-08		12:07:53		69.2		43		8-Jun-08		12:25:59		74.6		33

		28-Apr-08		14:07:10		71		43		28-Apr-08		14:06:20		69.2		43		28-Apr-08		14:07:53		69.2		45.5		8-Jun-08		14:25:59		75.81		31.5

		28-Apr-08		16:07:10		71		44		28-Apr-08		16:06:20		68.61		52		28-Apr-08		16:07:53		69.2		47		8-Jun-08		16:25:59		77		30.5

		28-Apr-08		18:07:10		71		41.5		28-Apr-08		18:06:20		69.2		46		28-Apr-08		18:07:53		68.61		45		8-Jun-08		18:25:59		77		31.5

		28-Apr-08		20:07:10		71		39		28-Apr-08		20:06:20		68.61		45		28-Apr-08		20:07:53		68.61		43		8-Jun-08		20:25:59		77		33.5

		28-Apr-08		22:07:10		71		38.5		28-Apr-08		22:06:20		68.61		43.5		28-Apr-08		22:07:53		68.61		41.5		8-Jun-08		22:25:59		75.81		34.5

		29-Apr-08		0:07:10		69.2		38.5		29-Apr-08		0:06:20		68		45		29-Apr-08		0:07:53		68		41		9-Jun-08		0:25:59		74.6		34

		29-Apr-08		2:07:10		69.8		38		29-Apr-08		2:06:20		67.4		44.5		29-Apr-08		2:07:53		68.61		40.5		9-Jun-08		2:25:59		74.01		34.5

		29-Apr-08		4:07:10		69.8		37.5		29-Apr-08		4:06:20		66.81		44		29-Apr-08		4:07:53		68.61		40		9-Jun-08		4:25:59		72.8		35

		29-Apr-08		6:07:10		69.2		36.5		29-Apr-08		6:06:20		66.2		44		29-Apr-08		6:07:53		68.61		39		9-Jun-08		6:25:59		72.21		35.5

		29-Apr-08		8:07:10		69.8		38.5		29-Apr-08		8:06:20		68		44.5		29-Apr-08		8:07:53		68		41		9-Jun-08		8:25:59		72.21		36.5

		29-Apr-08		10:07:10		70.41		39.5		29-Apr-08		10:06:20		69.8		45		29-Apr-08		10:07:53		68		43		9-Jun-08		10:25:59		74.01		37

		29-Apr-08		12:07:10		71		42		29-Apr-08		12:06:20		70.41		48.5		29-Apr-08		12:07:53		69.2		44.5		9-Jun-08		12:25:59		76.4		36

		29-Apr-08		14:07:10		71		42.5		29-Apr-08		14:06:20		70.41		48		29-Apr-08		14:07:53		68.61		46.5		9-Jun-08		14:25:59		77.61		35

		29-Apr-08		16:07:10		71		43		29-Apr-08		16:06:20		69.8		49		29-Apr-08		16:07:53		68.61		47		9-Jun-08		16:25:59		78.8		34.5

		29-Apr-08		18:07:10		71.6		41.5		29-Apr-08		18:06:20		69.2		48.5		29-Apr-08		18:07:53		68.61		45.5		9-Jun-08		18:25:59		78.2		35.5

		29-Apr-08		20:07:10		71		40		29-Apr-08		20:06:20		69.2		46.5		29-Apr-08		20:07:53		68.61		43.5		9-Jun-08		20:25:59		78.2		35.5

		29-Apr-08		22:07:10		71		39		29-Apr-08		22:06:20		69.2		47.5		29-Apr-08		22:07:53		68.61		42.5		9-Jun-08		22:25:59		76.4		35.5

		30-Apr-08		0:07:10		69.2		33		30-Apr-08		0:06:20		68		34		30-Apr-08		0:07:53		68		35.5		10-Jun-08		0:25:59		74.6		35.5

		30-Apr-08		2:07:10		69.2		35.5		30-Apr-08		2:06:20		68.61		37.5		30-Apr-08		2:07:53		68.61		37.5		10-Jun-08		2:25:59		73.4		36

		30-Apr-08		4:07:10		69.8		35		30-Apr-08		4:06:20		67.4		38.5		30-Apr-08		4:07:53		68.61		37		10-Jun-08		4:25:59		72.8		36

		30-Apr-08		6:07:10		70.41		35		30-Apr-08		6:06:20		69.2		39		30-Apr-08		6:07:53		68.61		38		10-Jun-08		6:25:59		72.21		37

		30-Apr-08		8:07:10		70.41		34		30-Apr-08		8:06:20		69.8		34		30-Apr-08		8:07:53		68		36.5		10-Jun-08		8:25:59		72.8		39

		30-Apr-08		10:07:10		69.2		34		30-Apr-08		10:06:20		69.8		35		30-Apr-08		10:07:53		67.4		37.5		10-Jun-08		10:25:59		73.4		38.5

		30-Apr-08		12:07:10		69.8		32.5		30-Apr-08		12:06:20		69.8		35		30-Apr-08		12:07:53		68		36		10-Jun-08		12:25:59		72.8		39

		30-Apr-08		14:07:10		69.8		33.5		30-Apr-08		14:06:20		69.2		34		30-Apr-08		14:07:53		68.61		36		10-Jun-08		14:25:59		72.8		39

		30-Apr-08		16:07:10		69.8		34		30-Apr-08		16:06:20		69.2		35		30-Apr-08		16:07:53		68.61		36.5		10-Jun-08		16:25:59		72.21		40

		30-Apr-08		18:07:10		69.8		31		30-Apr-08		18:06:20		69.2		32		30-Apr-08		18:07:53		68		33.5		10-Jun-08		18:25:59		72.8		42.5

		30-Apr-08		20:07:10		68.61		31.5		30-Apr-08		20:06:20		68.61		31.5		30-Apr-08		20:07:53		68		33.5		10-Jun-08		20:25:59		74.6		43

		30-Apr-08		22:07:10		69.2		31		30-Apr-08		22:06:20		68.61		32.5		30-Apr-08		22:07:53		68.61		33.5		10-Jun-08		22:25:59		76.4		40.5

		1-May-08		0:07:10		68.61		31.5		1-May-08		0:06:20		67.4		34		1-May-08		0:07:53		68		34		11-Jun-08		0:25:59		75.81		40.5

		1-May-08		2:07:10		68.61		30.5		1-May-08		2:06:20		66.2		33		1-May-08		2:07:53		68		32.5		11-Jun-08		2:25:59		75.2		39

		1-May-08		4:07:10		68		29.5		1-May-08		4:06:20		65.6		32		1-May-08		4:07:53		68		31		11-Jun-08		4:25:59		74.01		38

		1-May-08		6:07:10		68.61		29		1-May-08		6:06:20		65.6		31.5		1-May-08		6:07:53		68		30.5		11-Jun-08		6:25:59		72.8		37.5

		1-May-08		8:07:10		69.2		28		1-May-08		8:06:20		69.2		30		1-May-08		8:07:53		68.61		30.5		11-Jun-08		8:25:59		72.21		37

		1-May-08		10:07:10		69.8		26		1-May-08		10:06:20		70.41		27.5		1-May-08		10:07:53		68.61		29		11-Jun-08		10:25:59		72.8		33

		1-May-08		12:07:10		69.8		24		1-May-08		12:06:20		70.41		24.5		1-May-08		12:07:53		68.61		27		11-Jun-08		12:25:59		72.8		30.5

		1-May-08		14:07:10		70.41		25		1-May-08		14:06:20		71		26		1-May-08		14:07:53		69.8		27		11-Jun-08		14:25:59		74.01		30.5

		1-May-08		16:07:10		71		25.5		1-May-08		16:06:20		69.8		27.5		1-May-08		16:07:53		69.2		27.5		11-Jun-08		16:25:59		74.01		30.5

		1-May-08		18:07:10		70.41		29		1-May-08		18:06:20		70.41		29.5		1-May-08		18:07:53		69.8		30		11-Jun-08		18:25:59		73.4		32

		1-May-08		20:07:10		69.2		29.5		1-May-08		20:06:20		69.2		30		1-May-08		20:07:53		69.2		31		11-Jun-08		20:25:59		74.6		32.5

		1-May-08		22:07:10		69.2		30.5		1-May-08		22:06:20		69.8		30.5		1-May-08		22:07:53		69.2		32		11-Jun-08		22:25:59		75.2		32

		2-May-08		0:07:10		69.8		30.5		2-May-08		0:06:20		68		33		2-May-08		0:07:53		69.2		32.5		12-Jun-08		0:25:59		74.6		32

		2-May-08		2:07:10		69.8		30.5		2-May-08		2:06:20		67.4		33.5		2-May-08		2:07:53		69.2		32		12-Jun-08		2:25:59		73.4		32.5

		2-May-08		4:07:10		69.2		30.5		2-May-08		4:06:20		66.81		34		2-May-08		4:07:53		69.2		31.5		12-Jun-08		4:25:59		72.21		32.5

		2-May-08		6:07:10		69.2		30		2-May-08		6:06:20		66.81		34		2-May-08		6:07:53		69.2		32		12-Jun-08		6:25:59		71.6		32.5

		2-May-08		8:07:10		69.8		30.5		2-May-08		8:06:20		69.2		33		2-May-08		8:07:53		69.8		32		12-Jun-08		8:25:59		72.21		34.5

		2-May-08		10:07:10		69.8		30		2-May-08		10:06:20		69.8		31.5		2-May-08		10:07:53		69.8		31.5		12-Jun-08		10:25:59		73.4		34.5

		2-May-08		12:07:10		70.41		27		2-May-08		12:06:20		69.8		28		2-May-08		12:07:53		70.41		29.5		12-Jun-08		12:25:59		73.4		32.5

		2-May-08		14:07:10		71		23.5		2-May-08		14:06:20		71		25.5		2-May-08		14:07:53		69.8		26		12-Jun-08		14:25:59		72.8		29

		2-May-08		16:07:10		70.41		29.5		2-May-08		16:06:20		69.8		31		2-May-08		16:07:53		69.2		31		12-Jun-08		16:25:59		73.4		27.5

		2-May-08		18:07:10		70.41		30.5		2-May-08		18:06:20		70.41		31.5		2-May-08		18:07:53		69.8		32		12-Jun-08		18:25:59		73.4		29

		2-May-08		20:07:10		71		34		2-May-08		20:06:20		70.41		34		2-May-08		20:07:53		69.8		34		12-Jun-08		20:25:59		74.6		31.5

		2-May-08		22:07:10		70.41		29		2-May-08		22:06:20		70.41		30		2-May-08		22:07:53		70.41		31		12-Jun-08		22:25:59		75.2		32.5

		3-May-08		0:07:10		69.2		30		3-May-08		0:06:20		69.2		31		3-May-08		0:07:53		69.8		31.5		13-Jun-08		0:25:59		74.6		33

		3-May-08		2:07:10		70.41		33		3-May-08		2:06:20		68.61		36		3-May-08		2:07:53		69.8		34		13-Jun-08		2:25:59		73.4		33.5

		3-May-08		4:07:10		70.41		32.5		3-May-08		4:06:20		67.4		36		3-May-08		4:07:53		69.8		33.5		13-Jun-08		4:25:59		72.8		34

		3-May-08		6:07:10		70.41		32		3-May-08		6:06:20		66.81		36.5		3-May-08		6:07:53		69.8		33.5		13-Jun-08		6:25:59		71.6		35

		3-May-08		8:07:10		70.41		33.5		3-May-08		8:06:20		69.8		35.5		3-May-08		8:07:53		69.2		35		13-Jun-08		8:25:59		72.21		37

		3-May-08		10:07:10		70.41		34		3-May-08		10:06:20		70.41		35.5		3-May-08		10:07:53		69.8		35.5		13-Jun-08		10:25:59		72.21		37

		3-May-08		12:07:10		71		33.5		3-May-08		12:06:20		71		34		3-May-08		12:07:53		69.8		34.5		13-Jun-08		12:25:59		72.21		30.5

		3-May-08		14:07:10		71		36.5		3-May-08		14:06:20		71.6		35		3-May-08		14:07:53		69.8		36.5		13-Jun-08		14:25:59		73.4		27.5

		3-May-08		16:07:10		71		34		3-May-08		16:06:20		70.41		35.5		3-May-08		16:07:53		69.8		36.5		13-Jun-08		16:25:59		73.4		30.5

		3-May-08		18:07:10		71		37.5		3-May-08		18:06:20		71		40		3-May-08		18:07:53		69.8		39		13-Jun-08		18:25:59		73.4		28.5

		3-May-08		20:07:10		71		36.5		3-May-08		20:06:20		70.41		40		3-May-08		20:07:53		69.8		38		13-Jun-08		20:25:59		74.6		29

		3-May-08		22:07:10		71		35.5		3-May-08		22:06:20		69.8		39		3-May-08		22:07:53		69.8		37		13-Jun-08		22:25:59		75.81		29.5

		4-May-08		0:07:10		71		35		4-May-08		0:06:20		68		40		4-May-08		0:07:53		69.2		37		14-Jun-08		0:25:59		75.2		30.5

		4-May-08		2:07:10		70.41		35		4-May-08		2:06:20		66.81		41		4-May-08		2:07:53		69.8		36.5		14-Jun-08		2:25:59		74.01		31.5

		4-May-08		4:07:10		70.41		34.5		4-May-08		4:06:20		66.2		41		4-May-08		4:07:53		69.2		35.5		14-Jun-08		4:25:59		72.8		32

		4-May-08		6:07:10		69.8		33.5		4-May-08		6:06:20		65.6		40		4-May-08		6:07:53		69.8		35		14-Jun-08		6:25:59		72.21		33.5

		4-May-08		8:07:10		70.41		35.5		4-May-08		8:06:20		66.81		41.5		4-May-08		8:07:53		70.41		36		14-Jun-08		8:25:59		72.21		35.5

		4-May-08		10:07:10		70.41		36		4-May-08		10:06:20		69.8		39		4-May-08		10:07:53		70.41		37.5		14-Jun-08		10:25:59		72.8		37

		4-May-08		12:07:10		71		37		4-May-08		12:06:20		71		39.5		4-May-08		12:07:53		70.41		39		14-Jun-08		12:25:59		72.8		39.5

		4-May-08		14:07:10		71		39.5		4-May-08		14:06:20		70.41		45.5		4-May-08		14:07:53		68.61		42.5		14-Jun-08		14:25:59		73.4		38

		4-May-08		16:07:10		71		39.5		4-May-08		16:06:20		70.41		44.5		4-May-08		16:07:53		68.61		43.5		14-Jun-08		16:25:59		72.8		38.5

		4-May-08		18:07:10		71		40		4-May-08		18:06:20		69.8		48		4-May-08		18:07:53		69.2		43		14-Jun-08		18:25:59		73.4		38.5

		4-May-08		20:07:10		71		38.5		4-May-08		20:06:20		69.2		47		4-May-08		20:07:53		68.61		42		14-Jun-08		20:25:59		74.01		37

		4-May-08		22:07:10		71		38		4-May-08		22:06:20		69.8		44		4-May-08		22:07:53		68.61		40.5		14-Jun-08		22:25:59		74.01		37.5

		5-May-08		0:07:10		71		37.5		5-May-08		0:06:20		68.61		44		5-May-08		0:07:53		70.41		39.5		15-Jun-08		0:25:59		72.8		37

		5-May-08		2:07:10		71		37		5-May-08		2:06:20		68		44.5		5-May-08		2:07:53		70.41		38.5		15-Jun-08		2:25:59		72.21		37.5

		5-May-08		4:07:10		70.41		36.5		5-May-08		4:06:20		66.81		44.5		5-May-08		4:07:53		69.8		37.5		15-Jun-08		4:25:59		71.6		37.5

		5-May-08		6:07:10		69.8		35		5-May-08		6:06:20		66.2		43		5-May-08		6:07:53		69.8		37		15-Jun-08		6:25:59		71.6		37.5

		5-May-08		8:07:10		69.8		37		5-May-08		8:06:20		66.2		44.5		5-May-08		8:07:53		69.8		37.5		15-Jun-08		8:25:59		72.21		38

		5-May-08		10:07:10		69.8		38		5-May-08		10:06:20		68.61		44		5-May-08		10:07:53		69.8		39		15-Jun-08		10:25:59		72.21		39

		5-May-08		12:07:10		70.41		40		5-May-08		12:06:20		70.41		45		5-May-08		12:07:53		71		40.5		15-Jun-08		12:25:59		73.4		40

		5-May-08		14:07:10		71		40		5-May-08		14:06:20		71		44.5		5-May-08		14:07:53		71		41.5		15-Jun-08		14:25:59		74.6		41

		5-May-08		16:07:10		71		38		5-May-08		16:06:20		69.8		42		5-May-08		16:07:53		70.41		40		15-Jun-08		16:25:59		75.2		41.5

		5-May-08		18:07:10		71		37.5		5-May-08		18:06:20		70.41		41.5		5-May-08		18:07:53		70.41		39		15-Jun-08		18:25:59		75.81		41

		5-May-08		20:07:10		71		37		5-May-08		20:06:20		70.41		41.5		5-May-08		20:07:53		69.8		38.5		15-Jun-08		20:25:59		75.2		40

		5-May-08		22:07:10		70.41		37		5-May-08		22:06:20		69.8		41		5-May-08		22:07:53		69.8		38.5		15-Jun-08		22:25:59		74.01		39.5

		6-May-08		0:07:10		71		36.5		6-May-08		0:06:20		69.2		42		6-May-08		0:07:53		70.41		38		16-Jun-08		0:25:59		72.8		39

		6-May-08		2:07:10		71		36.5		6-May-08		2:06:20		67.4		43		6-May-08		2:07:53		70.41		37.5		16-Jun-08		2:25:59		72.21		39

		6-May-08		4:07:10		70.41		36		6-May-08		4:06:20		66.81		43		6-May-08		4:07:53		69.8		37		16-Jun-08		4:25:59		71.6		39

		6-May-08		6:07:10		69.8		35.5		6-May-08		6:06:20		65.6		43		6-May-08		6:07:53		69.2		37		16-Jun-08		6:25:59		71		39

		6-May-08		8:07:10		70.41		38		6-May-08		8:06:20		68		43.5		6-May-08		8:07:53		68.61		42		16-Jun-08		8:25:59		70.41		39.5

		6-May-08		10:07:10		70.41		39		6-May-08		10:06:20		71		44		6-May-08		10:07:53		67.4		41.5		16-Jun-08		10:25:59		70.41		40.5

		6-May-08		12:07:10		70.41		40.5		6-May-08		12:06:20		71.6		45		6-May-08		12:07:53		67.4		44		16-Jun-08		12:25:59		72.21		41.5

		6-May-08		14:07:10		71		40.5		6-May-08		14:06:20		71		44.5		6-May-08		14:07:53		67.4		44.5		16-Jun-08		14:25:59		73.4		42.5

		6-May-08		16:07:10		71		40		6-May-08		16:06:20		70.41		46.5		6-May-08		16:07:53		68.61		43.5		16-Jun-08		16:25:59		74.6		41

		6-May-08		18:07:10		70.41		39		6-May-08		18:06:20		69.2		45.5		6-May-08		18:07:53		68.61		41		16-Jun-08		18:25:59		75.2		40

		6-May-08		20:07:10		70.41		39.5		6-May-08		20:06:20		68.61		45		6-May-08		20:07:53		68.61		41.5		16-Jun-08		20:25:59		75.2		39

		6-May-08		22:07:10		70.41		38		6-May-08		22:06:20		69.2		44		6-May-08		22:07:53		68.61		41		16-Jun-08		22:25:59		74.01		38.5

		7-May-08		0:07:10		70.41		38.5		7-May-08		0:06:20		68.61		45		7-May-08		0:07:53		68.61		41		17-Jun-08		0:25:59		72.21		38

		7-May-08		2:07:10		70.41		38.5		7-May-08		2:06:20		68		46.5		7-May-08		2:07:53		68		41.5		17-Jun-08		2:25:59		71		37.5

		7-May-08		4:07:10		69.8		38		7-May-08		4:06:20		67.4		47		7-May-08		4:07:53		68.61		40.5		17-Jun-08		4:25:59		70.41		38.5

		7-May-08		6:07:10		70.41		39		7-May-08		6:06:20		66.81		47.5		7-May-08		6:07:53		68		42		17-Jun-08		6:25:59		70.41		39.5

		7-May-08		8:07:10		70.41		39		7-May-08		8:06:20		69.8		45		7-May-08		8:07:53		68.61		41.5		17-Jun-08		8:25:59		70.41		41.5

		7-May-08		10:07:10		71		38.5		7-May-08		10:06:20		70.41		45		7-May-08		10:07:53		68		42		17-Jun-08		10:25:59		71.6		42.5

		7-May-08		12:07:10		71		40.5		7-May-08		12:06:20		70.41		47		7-May-08		12:07:53		68		43.5		17-Jun-08		12:25:59		73.4		42.5

		7-May-08		14:07:10		71		43.5		7-May-08		14:06:20		69.8		51		7-May-08		14:07:53		68.61		46.5		17-Jun-08		14:25:59		74.01		43.5

		7-May-08		16:07:10		71		43		7-May-08		16:06:20		70.41		56		7-May-08		16:07:53		68.61		46.5		17-Jun-08		16:25:59		74.6		41

		7-May-08		18:07:10		70.41		43.5		7-May-08		18:06:20		71		50		7-May-08		18:07:53		68		46.5		17-Jun-08		18:25:59		74.01		40

		7-May-08		20:07:10		71		36.5		7-May-08		20:06:20		70.41		39		7-May-08		20:07:53		68		41		17-Jun-08		20:25:59		74.01		39.5

		7-May-08		22:07:10		71		34.5		7-May-08		22:06:20		69.8		36		7-May-08		22:07:53		68		38		17-Jun-08		22:25:59		74.01		38.5

		8-May-08		0:07:10		69.8		37		8-May-08		0:06:20		69.8		40.5		8-May-08		0:07:53		68		40		18-Jun-08		0:25:59		72.8		38

		8-May-08		2:07:10		70.41		37		8-May-08		2:06:20		68.61		41		8-May-08		2:07:53		69.2		39		18-Jun-08		2:25:59		71.6		37.5

		8-May-08		4:07:10		70.41		36		8-May-08		4:06:20		68		41.5		8-May-08		4:07:53		69.8		37.5		18-Jun-08		4:25:59		70.41		38.5

		8-May-08		6:07:10		71		34.5		8-May-08		6:06:20		68		39.5		8-May-08		6:07:53		68.61		38		18-Jun-08		6:25:59		70.41		39.5

		8-May-08		8:07:10		71		34.5		8-May-08		8:06:20		69.8		37		8-May-08		8:07:53		68.61		38		18-Jun-08		8:25:59		70.41		41.5

		8-May-08		10:07:10		70.41		36		8-May-08		10:06:20		70.41		38.5		8-May-08		10:07:53		68.61		38		18-Jun-08		10:25:59		72.8		42

		8-May-08		12:07:10		70.41		37		8-May-08		12:06:20		71		38.5		8-May-08		12:07:53		67.4		40.5		18-Jun-08		12:25:59		72.8		41.5

		8-May-08		14:07:10		70.41		39		8-May-08		14:06:20		71		41		8-May-08		14:07:53		67.4		43		18-Jun-08		14:25:59		72.8		42.5

		8-May-08		16:07:10		71		38.5		8-May-08		16:06:20		70.41		43		8-May-08		16:07:53		68		41.5		18-Jun-08		16:25:59		73.4		43

		8-May-08		18:07:10		71		39		8-May-08		18:06:20		71		41.5		8-May-08		18:07:53		68.61		42		18-Jun-08		18:25:59		74.01		34.5

		8-May-08		20:07:10		71		38		8-May-08		20:06:20		70.41		43.5		8-May-08		20:07:53		68		41.5		18-Jun-08		20:25:59		74.6		32

		8-May-08		22:07:10		70.41		37		8-May-08		22:06:20		69.8		41		8-May-08		22:07:53		68		40		18-Jun-08		22:25:59		74.6		30.5

		9-May-08		0:07:10		70.41		37		9-May-08		0:06:20		68.61		41.5		9-May-08		0:07:53		68		40		19-Jun-08		0:25:59		74.01		30.5

		9-May-08		2:07:10		70.41		36.5		9-May-08		2:06:20		67.4		42		9-May-08		2:07:53		68.61		39		19-Jun-08		2:25:59		73.4		31.5

		9-May-08		4:07:10		69.8		35.5		9-May-08		4:06:20		66.81		42.5		9-May-08		4:07:53		69.2		38		19-Jun-08		4:25:59		72.21		33

		9-May-08		6:07:10		71		35.5		9-May-08		6:06:20		66.81		41.5		9-May-08		6:07:53		69.2		37.5		19-Jun-08		6:25:59		71		33.5

		9-May-08		8:07:10		71		37		9-May-08		8:06:20		69.8		42		9-May-08		8:07:53		69.2		39		19-Jun-08		8:25:59		71		35.5

		9-May-08		10:07:10		70.41		38		9-May-08		10:06:20		71		40.5		9-May-08		10:07:53		68.61		40		19-Jun-08		10:25:59		72.8		35.5

		9-May-08		12:07:10		70.41		40		9-May-08		12:06:20		71.6		43		9-May-08		12:07:53		69.2		41.5		19-Jun-08		12:25:59		73.4		33.5

		9-May-08		14:07:10		70.41		39		9-May-08		14:06:20		69.8		45.5		9-May-08		14:07:53		68		42.5		19-Jun-08		14:25:59		72.21		35.5

		9-May-08		16:07:10		70.41		38		9-May-08		16:06:20		69.2		43		9-May-08		16:07:53		67.4		42.5		19-Jun-08		16:25:59		72.21		33.5

		9-May-08		18:07:10		70.41		38.5		9-May-08		18:06:20		68.61		42.5		9-May-08		18:07:53		68.61		41.5		19-Jun-08		18:25:59		74.01		28.5

		9-May-08		20:07:10		70.41		37		9-May-08		20:06:20		68.61		42		9-May-08		20:07:53		68		40		19-Jun-08		20:25:59		74.6		29

		9-May-08		22:07:10		69.8		36.5		9-May-08		22:06:20		68		41.5		9-May-08		22:07:53		68.61		39		19-Jun-08		22:25:59		75.2		27.5

		10-May-08		0:07:10		69.8		35.5		10-May-08		0:06:20		68		40.5		10-May-08		0:07:53		68		39		20-Jun-08		0:25:59		74.6		30

		10-May-08		2:07:10		69.8		34.5		10-May-08		2:06:20		66.81		40.5		10-May-08		2:07:53		68		37.5		20-Jun-08		2:25:59		73.4		31

		10-May-08		4:07:10		69.8		34		10-May-08		4:06:20		66.2		40.5		10-May-08		4:07:53		68.61		37		20-Jun-08		4:25:59		72.8		31.5

		10-May-08		6:07:10		70.41		33.5		10-May-08		6:06:20		65.6		39.5		10-May-08		6:07:53		68.61		35.5		20-Jun-08		6:25:59		71.6		32.5

		10-May-08		8:07:10		70.41		35.5		10-May-08		8:06:20		68		41.5		10-May-08		8:07:53		67.4		38.5		20-Jun-08		8:25:59		72.21		35

		10-May-08		10:07:10		69.8		34		10-May-08		10:06:20		70.41		35		10-May-08		10:07:53		68		37.5		20-Jun-08		10:25:59		73.4		36.5

		10-May-08		12:07:10		71		33.5		10-May-08		12:06:20		71		34.5		10-May-08		12:07:53		68.61		36.5		20-Jun-08		12:25:59		72.8		35

		10-May-08		14:07:10		71.6		32		10-May-08		14:06:20		70.41		34.5		10-May-08		14:07:53		68		35.5		20-Jun-08		14:25:59		72.8		33.5

		10-May-08		16:07:10		71.6		35		10-May-08		16:06:20		69.8		38.5		10-May-08		16:07:53		67.4		40.5		20-Jun-08		16:25:59		72.8		34

		10-May-08		18:07:10		71.6		36		10-May-08		18:06:20		69.2		39.5		10-May-08		18:07:53		67.4		41.5		20-Jun-08		18:25:59		72.8		31

		10-May-08		20:07:10		71		35.5		10-May-08		20:06:20		68.61		40.5		10-May-08		20:07:53		68		39.5		20-Jun-08		20:25:59		74.6		31.5

		10-May-08		22:07:10		70.41		35.5		10-May-08		22:06:20		68.61		39.5		10-May-08		22:07:53		68		38.5		20-Jun-08		22:25:59		75.81		30.5

		11-May-08		0:07:10		70.41		35.5		11-May-08		0:06:20		68.61		39.5		11-May-08		0:07:53		68		38.5		21-Jun-08		0:25:59		75.2		31.5

		11-May-08		2:07:10		70.41		35		11-May-08		2:06:20		67.4		40		11-May-08		2:07:53		68		38		21-Jun-08		2:25:59		74.01		32

		11-May-08		4:07:10		69.8		34		11-May-08		4:06:20		66.81		40.5		11-May-08		4:07:53		68.61		37		21-Jun-08		4:25:59		73.4		32.5

		11-May-08		6:07:10		70.41		34.5		11-May-08		6:06:20		68		39		11-May-08		6:07:53		68.61		36.5		21-Jun-08		6:25:59		72.21		34

		11-May-08		8:07:10		70.41		35.5		11-May-08		8:06:20		69.8		39		11-May-08		8:07:53		68		38.5		21-Jun-08		8:25:59		72.8		35.5

		11-May-08		10:07:10		70.41		35		11-May-08		10:06:20		69.8		36.5		11-May-08		10:07:53		68.61		37.5		21-Jun-08		10:25:59		72.8		35.5

		11-May-08		12:07:10		71		35.5		11-May-08		12:06:20		70.41		38		11-May-08		12:07:53		68.61		39		21-Jun-08		12:25:59		72.8		33.5

		11-May-08		14:07:10		71.6		38		11-May-08		14:06:20		69.2		41		11-May-08		14:07:53		68.61		41.5		21-Jun-08		14:25:59		72.8		32

		11-May-08		16:07:10		71.6		37.5		11-May-08		16:06:20		68.61		40		11-May-08		16:07:53		68.61		40.5		21-Jun-08		16:25:59		73.4		30

		11-May-08		18:07:10		71.6		38.5		11-May-08		18:06:20		69.2		44		11-May-08		18:07:53		68.61		42.5		21-Jun-08		18:25:59		71.6		27

		11-May-08		20:07:10		71.6		39		11-May-08		20:06:20		69.2		50		11-May-08		20:07:53		68.61		43.5		21-Jun-08		20:25:59		74.01		26.5

		11-May-08		22:07:10		71		38.5		11-May-08		22:06:20		68.61		46.5		11-May-08		22:07:53		69.2		41.5		21-Jun-08		22:25:59		75.81		25.5

		12-May-08		0:07:10		69.8		38.5		12-May-08		0:06:20		68.61		47.5		12-May-08		0:07:53		69.2		41		22-Jun-08		0:25:59		75.81		27.5

		12-May-08		2:07:10		70.41		39		12-May-08		2:06:20		68.61		47.5		12-May-08		2:07:53		69.8		41		22-Jun-08		2:25:59		75.2		29

		12-May-08		4:07:10		70.41		38		12-May-08		4:06:20		68		47		12-May-08		4:07:53		69.8		40		22-Jun-08		4:25:59		74.01		29.5

		12-May-08		6:07:10		71		38		12-May-08		6:06:20		67.4		47		12-May-08		6:07:53		69.8		40		22-Jun-08		6:25:59		74.6		30

		12-May-08		8:07:10		71		38.5		12-May-08		8:06:20		67.4		47.5		12-May-08		8:07:53		69.8		40.5		22-Jun-08		8:25:59		75.2		30.5

		12-May-08		10:07:10		70.41		39		12-May-08		10:06:20		68.61		45		12-May-08		10:07:53		69.8		40.5		22-Jun-08		10:25:59		77		31

		12-May-08		12:07:10		70.41		40		12-May-08		12:06:20		69.2		44.5		12-May-08		12:07:53		69.8		41.5		22-Jun-08		12:25:59		78.2		29.5

		12-May-08		14:07:10		71		33		12-May-08		14:06:20		69.2		32		12-May-08		14:07:53		69.8		34.5		22-Jun-08		14:25:59		79.41		28.5

		12-May-08		16:07:10		71		29.5		12-May-08		16:06:20		69.8		29.5		12-May-08		16:07:53		69.8		31		22-Jun-08		16:25:59		79.41		27

		12-May-08		18:07:10		71.6		31.5		12-May-08		18:06:20		69.8		33		12-May-08		18:07:53		69.8		33		22-Jun-08		18:25:59		78.8		25

		12-May-08		20:07:10		71.6		30.5		12-May-08		20:06:20		69.2		33		12-May-08		20:07:53		69.8		33		22-Jun-08		20:25:59		78.8		25

		12-May-08		22:07:10		70.41		30.5		12-May-08		22:06:20		68		33		12-May-08		22:07:53		69.8		32.5		22-Jun-08		22:25:59		77.61		27

		13-May-08		0:07:10		68.61		31		13-May-08		0:06:20		68.61		32.5		13-May-08		0:07:53		68.61		32.5		23-Jun-08		0:25:59		76.4		29

		13-May-08		2:07:10		68		32		13-May-08		2:06:20		68		33		13-May-08		2:07:53		68		33		23-Jun-08		2:25:59		75.2		31

		13-May-08		4:07:10		68		31.5		13-May-08		4:06:20		68.61		32		13-May-08		4:07:53		68		32.5		23-Jun-08		4:25:59		74.01		32

		13-May-08		6:07:10		68		30.5		13-May-08		6:06:20		68.61		31		13-May-08		6:07:53		68		32		23-Jun-08		6:25:59		73.4		32.5

		13-May-08		8:07:10		68.61		29		13-May-08		8:06:20		69.2		31		13-May-08		8:07:53		68.61		31.5		23-Jun-08		8:25:59		72.8		34

		13-May-08		10:07:10		69.8		28		13-May-08		10:06:20		70.41		29.5		13-May-08		10:07:53		68.61		30.5		23-Jun-08		10:25:59		74.01		35.5

		13-May-08		12:07:10		71		27.5		13-May-08		12:06:20		71.6		29		13-May-08		12:07:53		68.61		30.5		23-Jun-08		12:25:59		75.2		35.5

		13-May-08		14:07:10		71.6		28.5		13-May-08		14:06:20		71		30		13-May-08		14:07:53		68.61		31.5		23-Jun-08		14:25:59		76.4		36

		13-May-08		16:07:10		71.6		29.5		13-May-08		16:06:20		69.2		32.5		13-May-08		16:07:53		68.61		33		23-Jun-08		16:25:59		77		36

		13-May-08		18:07:10		71.6		30.5		13-May-08		18:06:20		70.41		33		13-May-08		18:07:53		68.61		34.5		23-Jun-08		18:25:59		77.61		35.5

		13-May-08		20:07:10		71		30		13-May-08		20:06:20		69.8		31.5		13-May-08		20:07:53		68		33.5		23-Jun-08		20:25:59		77.61		34.5

		13-May-08		22:07:10		70.41		30.5		13-May-08		22:06:20		70.41		31.5		13-May-08		22:07:53		68.61		33		23-Jun-08		22:25:59		75.81		34.5

		14-May-08		0:07:10		69.2		31		14-May-08		0:06:20		69.8		32		14-May-08		0:07:53		68		33.5		24-Jun-08		0:25:59		74.6		34.5

		14-May-08		2:07:10		68		32.5		14-May-08		2:06:20		69.2		33.5		14-May-08		2:07:53		68		34.5		24-Jun-08		2:25:59		73.4		34.5

		14-May-08		4:07:10		68		33		14-May-08		4:06:20		69.2		34		14-May-08		4:07:53		68		34.5		24-Jun-08		4:25:59		72.21		34.5

		14-May-08		6:07:10		68.61		33		14-May-08		6:06:20		69.2		34		14-May-08		6:07:53		68		35		24-Jun-08		6:25:59		71		36.5

		14-May-08		8:07:10		69.2		34		14-May-08		8:06:20		70.41		36.5		14-May-08		8:07:53		68		36		24-Jun-08		8:25:59		71		39

		14-May-08		10:07:10		71		34		14-May-08		10:06:20		71		36		14-May-08		10:07:53		67.4		38		24-Jun-08		10:25:59		72.21		40.5

		14-May-08		12:07:10		71.6		28.5		14-May-08		12:06:20		70.41		31.5		14-May-08		12:07:53		68		33		24-Jun-08		12:25:59		72.21		41.5

		14-May-08		14:07:10		71.6		29.5		14-May-08		14:06:20		70.41		32		14-May-08		14:07:53		68		34		24-Jun-08		14:25:59		73.4		39.5

		14-May-08		16:07:10		71.6		26.5		14-May-08		16:06:20		71		28		14-May-08		16:07:53		68		30		24-Jun-08		16:25:59		74.01		39

		14-May-08		18:07:10		71.6		27.5		14-May-08		18:06:20		71		28		14-May-08		18:07:53		68		30.5		24-Jun-08		18:25:59		74.01		38.5

		14-May-08		20:07:10		71.6		35		14-May-08		20:06:20		70.41		39.5		14-May-08		20:07:53		68		39.5		24-Jun-08		20:25:59		74.01		39.5

		14-May-08		22:07:10		71		36		14-May-08		22:06:20		69.8		41		14-May-08		22:07:53		68		40		24-Jun-08		22:25:59		75.2		37

		15-May-08		0:07:10		70.41		36.5		15-May-08		0:06:20		69.8		41		15-May-08		0:07:53		68.61		39.5		25-Jun-08		0:25:59		73.4		37

		15-May-08		2:07:10		69.8		37		15-May-08		2:06:20		69.2		42		15-May-08		2:07:53		68.61		39.5		25-Jun-08		2:25:59		72.21		37

		15-May-08		4:07:10		69.8		38		15-May-08		4:06:20		69.8		42.5		15-May-08		4:07:53		69.2		40.5		25-Jun-08		4:25:59		71		37

		15-May-08		6:07:10		70.41		39		15-May-08		6:06:20		69.8		42.5		15-May-08		6:07:53		68.61		41		25-Jun-08		6:25:59		70.41		38

		15-May-08		8:07:10		71		40		15-May-08		8:06:20		70.41		48.5		15-May-08		8:07:53		68		43.5		25-Jun-08		8:25:59		70.41		40.5

		15-May-08		10:07:10		71.6		40.5		15-May-08		10:06:20		71		46		15-May-08		10:07:53		67.4		46.5		25-Jun-08		10:25:59		72.8		41.5

		15-May-08		12:07:10		71.6		40.5		15-May-08		12:06:20		70.41		46.5		15-May-08		12:07:53		68		46.5		25-Jun-08		12:25:59		73.4		41

		15-May-08		14:07:10		71.6		38		15-May-08		14:06:20		69.8		41		15-May-08		14:07:53		68		43		25-Jun-08		14:25:59		72.8		42

		15-May-08		16:07:10		71.6		37.5		15-May-08		16:06:20		69.8		40.5		15-May-08		16:07:53		68		42.5		25-Jun-08		16:25:59		72.8		41.5

		15-May-08		18:07:10		71.6		39		15-May-08		18:06:20		68.61		42.5		15-May-08		18:07:53		69.2		43		25-Jun-08		18:25:59		74.01		39.5

		15-May-08		20:07:10		71.6		39		15-May-08		20:06:20		68.61		44		15-May-08		20:07:53		68.61		43.5		25-Jun-08		20:25:59		74.01		41

		15-May-08		22:07:10		71.6		37.5		15-May-08		22:06:20		68		44		15-May-08		22:07:53		68.61		42		25-Jun-08		22:25:59		74.6		38.5

		16-May-08		0:07:10		72.21		37		16-May-08		0:06:20		68		42.5		16-May-08		0:07:53		68.61		41.5		26-Jun-08		0:25:59		74.01		37.5

		16-May-08		2:07:10		71.6		37		16-May-08		2:06:20		68		43		16-May-08		2:07:53		69.2		40.5		26-Jun-08		2:25:59		72.8		37.5

		16-May-08		4:07:10		71.6		36.5		16-May-08		4:06:20		68		43		16-May-08		4:07:53		69.2		40.5		26-Jun-08		4:25:59		71.6		38

		16-May-08		6:07:10		71.6		36		16-May-08		6:06:20		68.61		42		16-May-08		6:07:53		69.2		39.5		26-Jun-08		6:25:59		71		38.5

		16-May-08		8:07:10		72.21		36.5		16-May-08		8:06:20		69.8		42		16-May-08		8:07:53		68.61		41		26-Jun-08		8:25:59		71		40.5

		16-May-08		10:07:10		71.6		38		16-May-08		10:06:20		69.2		43		16-May-08		10:07:53		68		43		26-Jun-08		10:25:59		73.4		40.5

		16-May-08		12:07:10		71.6		39.5		16-May-08		12:06:20		70.41		43.5		16-May-08		12:07:53		68		44		26-Jun-08		12:25:59		72.21		43

		16-May-08		14:07:10		71.6		39		16-May-08		14:06:20		70.41		43		16-May-08		14:07:53		68		44		26-Jun-08		14:25:59		72.21		44

		16-May-08		16:07:10		71.6		40		16-May-08		16:06:20		69.2		46		16-May-08		16:07:53		68.61		45		26-Jun-08		16:25:59		72.21		43.5

		16-May-08		18:07:10		71.6		40.5		16-May-08		18:06:20		69.2		45		16-May-08		18:07:53		68.61		45		26-Jun-08		18:25:59		71.6		43

		16-May-08		20:07:10		71.6		42		16-May-08		20:06:20		69.2		48.5		16-May-08		20:07:53		69.2		46.5		26-Jun-08		20:25:59		72.8		40.5

		16-May-08		22:07:10		72.21		41		16-May-08		22:06:20		68.61		54.5		16-May-08		22:07:53		68		46.5		26-Jun-08		22:25:59		73.4		40.5

		17-May-08		0:07:10		72.21		39.5		17-May-08		0:06:20		68.61		50		17-May-08		0:07:53		68.61		44.5		27-Jun-08		0:25:59		72.8		39.5

		17-May-08		2:07:10		72.21		39		17-May-08		2:06:20		68.61		47		17-May-08		2:07:53		68.61		43.5		27-Jun-08		2:25:59		71.6		39

		17-May-08		4:07:10		71.6		39		17-May-08		4:06:20		68		51		17-May-08		4:07:53		68.61		43		27-Jun-08		4:25:59		71		39

		17-May-08		6:07:10		71.6		39		17-May-08		6:06:20		68.61		53		17-May-08		6:07:53		69.2		43		27-Jun-08		6:25:59		70.41		39.5

		17-May-08		8:07:10		72.21		40		17-May-08		8:06:20		69.8		55.5		17-May-08		8:07:53		68		45.5		27-Jun-08		8:25:59		70.41		41

		17-May-08		10:07:10		72.21		40.5		17-May-08		10:06:20		69.8		53.5		17-May-08		10:07:53		68		46		27-Jun-08		10:25:59		72.8		42.5

		17-May-08		12:07:10		71		44.5		17-May-08		12:06:20		69.8		50		17-May-08		12:07:53		68.61		49.5		27-Jun-08		12:25:59		72.21		43

		17-May-08		14:07:10		71.6		45		17-May-08		14:06:20		70.41		52.5		17-May-08		14:07:53		68		51		27-Jun-08		14:25:59		72.21		44.5

		17-May-08		16:07:10		71.6		44.5		17-May-08		16:06:20		69.8		51		17-May-08		16:07:53		68.61		49.5		27-Jun-08		16:25:59		72.8		44

		17-May-08		18:07:10		71.6		41.5		17-May-08		18:06:20		69.2		45.5		17-May-08		18:07:53		68.61		45.5		27-Jun-08		18:25:59		72.8		41

		17-May-08		20:07:10		71.6		41.5		17-May-08		20:06:20		68.61		49		17-May-08		20:07:53		68.61		46		27-Jun-08		20:25:59		73.4		41.5

		17-May-08		22:07:10		72.21		39.5		17-May-08		22:06:20		69.2		48		17-May-08		22:07:53		68		44.5		27-Jun-08		22:25:59		74.01		40

		18-May-08		0:07:10		72.21		39		18-May-08		0:06:20		68		50.5		18-May-08		0:07:53		68.61		43.5		28-Jun-08		0:25:59		73.4		39.5

		18-May-08		2:07:10		71.6		40		18-May-08		2:06:20		68		52		18-May-08		2:07:53		68.61		43.5		28-Jun-08		2:25:59		72.21		39.5

		18-May-08		4:07:10		71		40		18-May-08		4:06:20		68		52.5		18-May-08		4:07:53		69.2		43		28-Jun-08		4:25:59		71.6		39.5

		18-May-08		6:07:10		70.41		39.5		18-May-08		6:06:20		68		50.5		18-May-08		6:07:53		69.2		42		28-Jun-08		6:25:59		71		40

		18-May-08		8:07:10		71		40.5		18-May-08		8:06:20		68.61		53.5		18-May-08		8:07:53		68.61		44		28-Jun-08		8:25:59		71		42

		18-May-08		10:07:10		71.6		42.5		18-May-08		10:06:20		69.2		56.5		18-May-08		10:07:53		68.61		46.5		28-Jun-08		10:25:59		73.4		43

		18-May-08		12:07:10		71.6		44.5		18-May-08		12:06:20		69.2		53.5		18-May-08		12:07:53		68.61		49.5		28-Jun-08		12:25:59		72.8		44

		18-May-08		14:07:10		72.21		48.5		18-May-08		14:06:20		69.2		58.5		18-May-08		14:07:53		68.61		54		28-Jun-08		14:25:59		72.21		45

		18-May-08		16:07:10		72.21		45		18-May-08		16:06:20		68.61		63.5		18-May-08		16:07:53		68.61		51.5		28-Jun-08		16:25:59		72.8		45.5

		18-May-08		18:07:10		72.21		43		18-May-08		18:06:20		68.61		60.5		18-May-08		18:07:53		68.61		49.5		28-Jun-08		18:25:59		72.8		43.5

		18-May-08		20:07:10		72.21		40.5		18-May-08		20:06:20		68.61		52.5		18-May-08		20:07:53		68		46		28-Jun-08		20:25:59		72.8		43.5

		18-May-08		22:07:10		72.21		39		18-May-08		22:06:20		68		51.5		18-May-08		22:07:53		68.61		43.5		28-Jun-08		22:25:59		72.8		42.5

		19-May-08		0:07:10		71		39		19-May-08		0:06:20		68		49.5		19-May-08		0:07:53		69.2		42		29-Jun-08		0:25:59		72.21		42.5

		19-May-08		2:07:10		70.41		39.5		19-May-08		2:06:20		68		49		19-May-08		2:07:53		69.2		42		29-Jun-08		2:25:59		71.6		42.5

		19-May-08		4:07:10		70.41		39		19-May-08		4:06:20		67.4		48		19-May-08		4:07:53		69.2		41.5		29-Jun-08		4:25:59		71		43

		19-May-08		6:07:10		71		39		19-May-08		6:06:20		67.4		49		19-May-08		6:07:53		69.2		41.5		29-Jun-08		6:25:59		71		43.5

		19-May-08		8:07:10		71		39.5		19-May-08		8:06:20		68		49		19-May-08		8:07:53		69.2		42		29-Jun-08		8:25:59		71		44

		19-May-08		10:07:10		70.41		40.5		19-May-08		10:06:20		68		48.5		19-May-08		10:07:53		69.2		43		29-Jun-08		10:25:59		71.6		44.5

		19-May-08		12:07:10		71		41.5		19-May-08		12:06:20		68.61		51		19-May-08		12:07:53		69.2		44.5		29-Jun-08		12:25:59		72.21		45.5

		19-May-08		14:07:10		71.6		41.5		19-May-08		14:06:20		68		54.5		19-May-08		14:07:53		69.8		45		29-Jun-08		14:25:59		74.01		45.5

		19-May-08		16:07:10		72.21		42		19-May-08		16:06:20		68.61		51.5		19-May-08		16:07:53		69.2		46		29-Jun-08		16:25:59		75.2		44.5

		19-May-08		18:07:10		72.21		40		19-May-08		18:06:20		68		55		19-May-08		18:07:53		69.2		44.5		29-Jun-08		18:25:59		75.81		43.5

		19-May-08		20:07:10		72.21		39		19-May-08		20:06:20		68.61		50.5		19-May-08		20:07:53		69.2		43		29-Jun-08		20:25:59		75.2		43

		19-May-08		22:07:10		71		39		19-May-08		22:06:20		67.4		52.5		19-May-08		22:07:53		69.2		42		29-Jun-08		22:25:59		74.01		42.5

		20-May-08		0:07:10		71		39.5		20-May-08		0:06:20		67.4		51		20-May-08		0:07:53		69.2		42		30-Jun-08		0:25:59		72.21		42.5

		20-May-08		2:07:10		71		39.5		20-May-08		2:06:20		68		50		20-May-08		2:07:53		69.2		42		30-Jun-08		2:25:59		71.6		42.5

		20-May-08		4:07:10		70.41		39.5		20-May-08		4:06:20		67.4		49.5		20-May-08		4:07:53		69.2		41.5		30-Jun-08		4:25:59		71		42.5

		20-May-08		6:07:10		71		39.5		20-May-08		6:06:20		68		49.5		20-May-08		6:07:53		69.2		41.5		30-Jun-08		6:25:59		70.41		43

		20-May-08		8:07:10		71		39		20-May-08		8:06:20		68.61		50.5		20-May-08		8:07:53		68.61		44		30-Jun-08		8:25:59		70.41		43.5

		20-May-08		10:07:10		71		39		20-May-08		10:06:20		71		44.5		20-May-08		10:07:53		68.61		43		30-Jun-08		10:25:59		70.41		44

		20-May-08		12:07:10		71		41		20-May-08		12:06:20		71		49.5		20-May-08		12:07:53		68		45		30-Jun-08		12:25:59		72.21		44.5

		20-May-08		14:07:10		71		43		20-May-08		14:06:20		71		55.5		20-May-08		14:07:53		68		48		30-Jun-08		14:25:59		73.4		44.5

		20-May-08		16:07:10		71.6		42		20-May-08		16:06:20		70.41		49.5		20-May-08		16:07:53		68.61		46.5		30-Jun-08		16:25:59		74.6		44.5

		20-May-08		18:07:10		71.6		41		20-May-08		18:06:20		69.8		51		20-May-08		18:07:53		69.2		44.5		30-Jun-08		18:25:59		75.2		43

		20-May-08		20:07:10		71		39		20-May-08		20:06:20		69.8		48.5		20-May-08		20:07:53		69.2		42.5		30-Jun-08		20:25:59		75.2		42.5

		20-May-08		22:07:10		71		39.5		20-May-08		22:06:20		69.8		48		20-May-08		22:07:53		69.8		41.5		30-Jun-08		22:25:59		73.4		42

		21-May-08		0:07:10		70.41		40		21-May-08		0:06:20		69.2		48.5		21-May-08		0:07:53		69.2		42		1-Jul-08		0:25:59		72.21		42

		21-May-08		2:07:10		70.41		40		21-May-08		2:06:20		68.61		48.5		21-May-08		2:07:53		69.8		42		1-Jul-08		2:25:59		71.6		42

		21-May-08		4:07:10		71		39.5		21-May-08		4:06:20		68.61		48		21-May-08		4:07:53		69.2		41.5		1-Jul-08		4:25:59		71		42

		21-May-08		6:07:10		71		39.5		21-May-08		6:06:20		68		48.5		21-May-08		6:07:53		69.8		41		1-Jul-08		6:25:59		71		43

		21-May-08		8:07:10		71		39.5		21-May-08		8:06:20		70.41		48.5		21-May-08		8:07:53		68.61		42		1-Jul-08		8:25:59		70.41		45

		21-May-08		10:07:10		71		40		21-May-08		10:06:20		71		47		21-May-08		10:07:53		68		43		1-Jul-08		10:25:59		72.21		45

		21-May-08		12:07:10		71		41		21-May-08		12:06:20		71		51		21-May-08		12:07:53		68.61		44.5		1-Jul-08		12:25:59		72.21		45

		21-May-08		14:07:10		71		44		21-May-08		14:06:20		71.6		54		21-May-08		14:07:53		68		48.5		1-Jul-08		14:25:59		72.8		46.5

		21-May-08		16:07:10		71		39.5		21-May-08		16:06:20		71		45		21-May-08		16:07:53		69.2		43.5		1-Jul-08		16:25:59		72.8		46.5

		21-May-08		18:07:10		71.6		32		21-May-08		18:06:20		71		34		21-May-08		18:07:53		69.2		36.5		1-Jul-08		18:25:59		72.8		44.5

		21-May-08		20:07:10		71		30		21-May-08		20:06:20		70.41		30		21-May-08		20:07:53		69.8		31.5		1-Jul-08		20:25:59		74.01		42

		21-May-08		22:07:10		70.41		36		21-May-08		22:06:20		70.41		39		21-May-08		22:07:53		69.8		38		1-Jul-08		22:25:59		74.01		43.5

		22-May-08		0:07:10		69.2		35		22-May-08		0:06:20		69.2		37.5		22-May-08		0:07:53		68.61		37		2-Jul-08		0:25:59		73.4		43

		22-May-08		2:07:10		68.61		34.5		22-May-08		2:06:20		69.2		35.5		22-May-08		2:07:53		68.61		36.5		2-Jul-08		2:25:59		72.21		43

		22-May-08		4:07:10		68.61		34		22-May-08		4:06:20		69.2		35		22-May-08		4:07:53		68.61		35		2-Jul-08		4:25:59		72.21		43.5

		22-May-08		6:07:10		69.8		32.5		22-May-08		6:06:20		69.2		34.5		22-May-08		6:07:53		69.2		34.5		2-Jul-08		6:25:59		71.6		44.5

		22-May-08		8:07:10		69.8		32.5		22-May-08		8:06:20		71		34.5		22-May-08		8:07:53		68.61		35		2-Jul-08		8:25:59		71		46.5

		22-May-08		10:07:10		70.41		33.5		22-May-08		10:06:20		71.6		34		22-May-08		10:07:53		68.61		35.5		2-Jul-08		10:25:59		72.21		47.5

		22-May-08		12:07:10		71		33.5		22-May-08		12:06:20		70.41		35.5		22-May-08		12:07:53		69.2		36		2-Jul-08		12:25:59		72.21		46.5

		22-May-08		14:07:10		71		34.5		22-May-08		14:06:20		69.8		37		22-May-08		14:07:53		68.61		38		2-Jul-08		14:25:59		72.21		47.5

		22-May-08		16:07:10		71		35		22-May-08		16:06:20		69.2		38		22-May-08		16:07:53		68.61		38.5		2-Jul-08		16:25:59		72.8		45.5

		22-May-08		18:07:10		71		35		22-May-08		18:06:20		68.61		37.5		22-May-08		18:07:53		68		38		2-Jul-08		18:25:59		72.8		44.5

		22-May-08		20:07:10		70.41		34.5		22-May-08		20:06:20		68.61		37		22-May-08		20:07:53		68		37		2-Jul-08		20:25:59		73.4		42.5

		22-May-08		22:07:10		69.2		33.5		22-May-08		22:06:20		68		36.5		22-May-08		22:07:53		68.61		36		2-Jul-08		22:25:59		74.01		43

		23-May-08		0:07:10		68.61		33.5		23-May-08		0:06:20		68		36		23-May-08		0:07:53		68		35.5		3-Jul-08		0:25:59		72.8		42.5

		23-May-08		2:07:10		68		32.5		23-May-08		2:06:20		68		34.5		23-May-08		2:07:53		68		34.5		3-Jul-08		2:25:59		71.6		42

		23-May-08		4:07:10		68.61		31		23-May-08		4:06:20		68		32.5		23-May-08		4:07:53		68.61		33		3-Jul-08		4:25:59		71		42.5

		23-May-08		6:07:10		69.8		30		23-May-08		6:06:20		68		32		23-May-08		6:07:53		69.2		32		3-Jul-08		6:25:59		70.41		43

		23-May-08		8:07:10		69.8		30		23-May-08		8:06:20		68.61		33		23-May-08		8:07:53		69.2		32		3-Jul-08		8:25:59		71		44.5

		23-May-08		10:07:10		70.41		30		23-May-08		10:06:20		68.61		32.5		23-May-08		10:07:53		68		32		3-Jul-08		10:25:59		72.21		45

		23-May-08		12:07:10		71		25		23-May-08		12:06:20		69.2		27.5		23-May-08		12:07:53		68		28.5		3-Jul-08		12:25:59		71.6		46.5

		23-May-08		14:07:10		71		28.5		23-May-08		14:06:20		68.61		30		23-May-08		14:07:53		67.4		31		3-Jul-08		14:25:59		72.21		46

		23-May-08		16:07:10		71		29.5		23-May-08		16:06:20		68		33		23-May-08		16:07:53		68.61		32.5		3-Jul-08		16:25:59		72.21		45.5

		23-May-08		18:07:10		71		32		23-May-08		18:06:20		68.61		34.5		23-May-08		18:07:53		68.61		35		3-Jul-08		18:25:59		73.4		44

		23-May-08		20:07:10		71		33.5		23-May-08		20:06:20		69.2		36		23-May-08		20:07:53		68.61		36		3-Jul-08		20:25:59		74.01		42

		23-May-08		22:07:10		70.41		33		23-May-08		22:06:20		68.61		37		23-May-08		22:07:53		68.61		36		3-Jul-08		22:25:59		74.6		42

		24-May-08		0:07:10		69.2		33.5		24-May-08		0:06:20		68		37		24-May-08		0:07:53		68.61		36		4-Jul-08		0:25:59		73.4		41.5

		24-May-08		2:07:10		68.61		33.5		24-May-08		2:06:20		68		37		24-May-08		2:07:53		68		36		4-Jul-08		2:25:59		72.21		41.5

		24-May-08		4:07:10		69.2		33		24-May-08		4:06:20		67.4		37		24-May-08		4:07:53		68.61		35		4-Jul-08		4:25:59		71.6		41.5

		24-May-08		6:07:10		70.41		32.5		24-May-08		6:06:20		68		36		24-May-08		6:07:53		69.2		34.5		4-Jul-08		6:25:59		71		42

		24-May-08		8:07:10		70.41		32.5		24-May-08		8:06:20		67.4		38.5		24-May-08		8:07:53		68.61		35.5		4-Jul-08		8:25:59		71		44.5

		24-May-08		10:07:10		70.41		34		24-May-08		10:06:20		70.41		36		24-May-08		10:07:53		68.61		36.5		4-Jul-08		10:25:59		71.6		45

		24-May-08		12:07:10		71		35		24-May-08		12:06:20		71		36		24-May-08		12:07:53		69.2		36.5		4-Jul-08		12:25:59		72.21		48.5

		24-May-08		14:07:10		71		34		24-May-08		14:06:20		71		37		24-May-08		14:07:53		68		37.5		4-Jul-08		14:25:59		73.4		50

		24-May-08		16:07:10		71		34.5		24-May-08		16:06:20		69.8		37		24-May-08		16:07:53		69.2		37		4-Jul-08		16:25:59		72.8		49

		24-May-08		18:07:10		70.41		35.5		24-May-08		18:06:20		70.41		39		24-May-08		18:07:53		69.2		38		4-Jul-08		18:25:59		73.4		48.5

		24-May-08		20:07:10		70.41		36.5		24-May-08		20:06:20		69.8		41		24-May-08		20:07:53		68.61		39		4-Jul-08		20:25:59		74.01		46

		24-May-08		22:07:10		71		36.5		24-May-08		22:06:20		69.2		42.5		24-May-08		22:07:53		68.61		39.5		4-Jul-08		22:25:59		74.01		47

		25-May-08		0:07:10		70.41		37		25-May-08		0:06:20		69.2		42.5		25-May-08		0:07:53		69.2		39.5		5-Jul-08		0:25:59		73.4		46.5

		25-May-08		2:07:10		70.41		37		25-May-08		2:06:20		68.61		42.5		25-May-08		2:07:53		69.2		39		5-Jul-08		2:25:59		72.21		46

		25-May-08		4:07:10		70.41		37.5		25-May-08		4:06:20		68.61		43		25-May-08		4:07:53		69.2		39		5-Jul-08		4:25:59		71.6		45.5

		25-May-08		6:07:10		70.41		37.5		25-May-08		6:06:20		68.61		45		25-May-08		6:07:53		69.2		39.5		5-Jul-08		6:25:59		71		46.5

		25-May-08		8:07:10		70.41		38		25-May-08		8:06:20		68.61		45		25-May-08		8:07:53		69.2		39.5		5-Jul-08		8:25:59		71		48

		25-May-08		10:07:10		70.41		39.5		25-May-08		10:06:20		68.61		48		25-May-08		10:07:53		69.2		41.5		5-Jul-08		10:25:59		72.21		48

		25-May-08		12:07:10		70.41		40		25-May-08		12:06:20		69.2		50		25-May-08		12:07:53		69.8		42		5-Jul-08		12:25:59		72.21		48.5

		25-May-08		14:07:10		69.8		37.5		25-May-08		14:06:20		68.61		46		25-May-08		14:07:53		69.8		40		5-Jul-08		14:25:59		73.4		48

		25-May-08		16:07:10		69.8		38.5		25-May-08		16:06:20		68.61		44.5		25-May-08		16:07:53		69.2		39.5		5-Jul-08		16:25:59		73.4		47.5

		25-May-08		18:07:10		69.8		39.5		25-May-08		18:06:20		69.2		48.5		25-May-08		18:07:53		69.8		41		5-Jul-08		18:25:59		73.4		46.5

		25-May-08		20:07:10		70.41		40		25-May-08		20:06:20		69.2		50		25-May-08		20:07:53		69.2		41.5		5-Jul-08		20:25:59		72.8		45.5

		25-May-08		22:07:10		70.41		40		25-May-08		22:06:20		68.61		48		25-May-08		22:07:53		69.2		41		5-Jul-08		22:25:59		72.8		47

		26-May-08		0:07:10		70.41		39		26-May-08		0:06:20		68		47		26-May-08		0:07:53		69.2		40.5		6-Jul-08		0:25:59		72.21		46

		26-May-08		2:07:10		70.41		37.5		26-May-08		2:06:20		67.4		45		26-May-08		2:07:53		69.2		39		6-Jul-08		2:25:59		72.21		45.5

		26-May-08		4:07:10		70.41		36.5		26-May-08		4:06:20		66.81		44		26-May-08		4:07:53		69.2		38		6-Jul-08		4:25:59		71		45.5

		26-May-08		6:07:10		70.41		36.5		26-May-08		6:06:20		66.81		44.5		26-May-08		6:07:53		69.8		38		6-Jul-08		6:25:59		71		45

		26-May-08		8:07:10		70.41		38.5		26-May-08		8:06:20		67.4		45.5		26-May-08		8:07:53		69.8		39		6-Jul-08		8:25:59		70.41		45.5

		26-May-08		10:07:10		69.8		37		26-May-08		10:06:20		69.2		43		26-May-08		10:07:53		69.2		39.5		6-Jul-08		10:25:59		71.6		47.5

		26-May-08		12:07:10		69.8		37		26-May-08		12:06:20		69.2		40.5		26-May-08		12:07:53		69.2		38.5		6-Jul-08		12:25:59		73.4		48.5

		26-May-08		14:07:10		70.41		37		26-May-08		14:06:20		69.2		40		26-May-08		14:07:53		69.8		38.5		6-Jul-08		14:25:59		75.2		49

		26-May-08		16:07:10		70.41		36		26-May-08		16:06:20		69.2		39		26-May-08		16:07:53		69.2		38		6-Jul-08		16:25:59		77		47.5

		26-May-08		18:07:10		70.41		35.5		26-May-08		18:06:20		68.61		38.5		26-May-08		18:07:53		69.2		37		6-Jul-08		18:25:59		77.61		45.5

		26-May-08		20:07:10		70.41		36		26-May-08		20:06:20		69.2		38.5		26-May-08		20:07:53		69.8		37.5		6-Jul-08		20:25:59		78.2		45

		26-May-08		22:07:10		69.8		37.5		26-May-08		22:06:20		69.2		44		26-May-08		22:07:53		69.2		39.5		6-Jul-08		22:25:59		77		45.5

		27-May-08		0:07:10		70.41		38		27-May-08		0:06:20		68.61		44.5		27-May-08		0:07:53		69.8		39.5		7-Jul-08		0:25:59		75.81		45.5

		27-May-08		2:07:10		70.41		37.5		27-May-08		2:06:20		68		45		27-May-08		2:07:53		69.8		39		7-Jul-08		2:25:59		74.6		44.5

		27-May-08		4:07:10		70.41		37.5		27-May-08		4:06:20		67.4		45.5		27-May-08		4:07:53		69.8		39		7-Jul-08		4:25:59		74.01		44.5

		27-May-08		6:07:10		70.41		37		27-May-08		6:06:20		67.4		45		27-May-08		6:07:53		69.2		38.5		7-Jul-08		6:25:59		72.8		44

		27-May-08		8:07:10		70.41		38		27-May-08		8:06:20		68		45		27-May-08		8:07:53		69.2		39.5		7-Jul-08		8:25:59		72.21		44.5

		27-May-08		10:07:10		69.8		37.5		27-May-08		10:06:20		69.2		42.5		27-May-08		10:07:53		69.2		39		7-Jul-08		10:25:59		73.4		46.5

		27-May-08		12:07:10		70.41		39		27-May-08		12:06:20		69.2		45		27-May-08		12:07:53		69.2		40		7-Jul-08		12:25:59		74.6		48

		27-May-08		14:07:10		70.41		38.5		27-May-08		14:06:20		68.61		45		27-May-08		14:07:53		69.2		40.5		7-Jul-08		14:25:59		76.4		49

		27-May-08		16:07:10		70.41		39		27-May-08		16:06:20		69.2		45.5		27-May-08		16:07:53		69.2		40.5		7-Jul-08		16:25:59		77.61		47.5

		27-May-08		18:07:10		70.41		39		27-May-08		18:06:20		69.2		46		27-May-08		18:07:53		69.2		40.5		7-Jul-08		18:25:59		78.2		46

		27-May-08		20:07:10		70.41		38.5		27-May-08		20:06:20		69.2		46		27-May-08		20:07:53		69.8		40		7-Jul-08		20:25:59		78.2		44.5

		27-May-08		22:07:10		70.41		39		27-May-08		22:06:20		69.2		45		27-May-08		22:07:53		69.8		40		7-Jul-08		22:25:59		76.4		43.5

		28-May-08		0:07:10		70.41		38.5		28-May-08		0:06:20		69.2		46		28-May-08		0:07:53		69.8		40		8-Jul-08		0:25:59		75.2		42.5

		28-May-08		2:07:10		70.41		39		28-May-08		2:06:20		69.2		46.5		28-May-08		2:07:53		69.2		40.5		8-Jul-08		2:25:59		74.01		42.5

		28-May-08		4:07:10		70.41		39		28-May-08		4:06:20		68.61		47		28-May-08		4:07:53		69.8		40.5		8-Jul-08		4:25:59		72.8		42

		28-May-08		6:07:10		70.41		39.5		28-May-08		6:06:20		69.2		47.5		28-May-08		6:07:53		69.2		41		8-Jul-08		6:25:59		72.21		41.5

		28-May-08		8:07:10		70.41		39		28-May-08		8:06:20		69.2		50		28-May-08		8:07:53		69.2		41.5		8-Jul-08		8:25:59		71.6		46

		28-May-08		10:07:10		71		38.5		28-May-08		10:06:20		69.8		45		28-May-08		10:07:53		68.61		41		8-Jul-08		10:25:59		72.8		47

		28-May-08		12:07:10		71		38.5		28-May-08		12:06:20		69.8		44		28-May-08		12:07:53		69.2		41.5		8-Jul-08		12:25:59		72.8		49

		28-May-08		14:07:10		71		39		28-May-08		14:06:20		69.2		43.5		28-May-08		14:07:53		68.61		42.5		8-Jul-08		14:25:59		72.8		49

		28-May-08		16:07:10		71		38		28-May-08		16:06:20		69.8		45.5		28-May-08		16:07:53		68.61		41.5		8-Jul-08		16:25:59		73.4		48.5

		28-May-08		18:07:10		71		37.5		28-May-08		18:06:20		71		41.5		28-May-08		18:07:53		69.2		40.5		8-Jul-08		18:25:59		73.4		47

		28-May-08		20:07:10		71		37.5		28-May-08		20:06:20		70.41		42.5		28-May-08		20:07:53		69.2		40		8-Jul-08		20:25:59		74.6		45.5

		28-May-08		22:07:10		70.41		37.5		28-May-08		22:06:20		71		41.5		28-May-08		22:07:53		69.2		39		8-Jul-08		22:25:59		75.2		45

		29-May-08		0:07:10		70.41		37.5		29-May-08		0:06:20		69.8		43		29-May-08		0:07:53		69.2		39.5		9-Jul-08		0:25:59		75.2		44

		29-May-08		2:07:10		70.41		38		29-May-08		2:06:20		69.2		44		29-May-08		2:07:53		69.8		39.5		9-Jul-08		2:25:59		74.6		44

		29-May-08		4:07:10		70.41		38		29-May-08		4:06:20		68.61		45		29-May-08		4:07:53		69.8		39.5		9-Jul-08		4:25:59		74.01		43.5

		29-May-08		6:07:10		70.41		38.5		29-May-08		6:06:20		68.61		45.5		29-May-08		6:07:53		69.8		40		9-Jul-08		6:25:59		73.4		42

		29-May-08		8:07:10		71		38.5		29-May-08		8:06:20		69.8		46.5		29-May-08		8:07:53		69.2		40.5		9-Jul-08		8:25:59		72.21		45.5

		29-May-08		10:07:10		71		36.5		29-May-08		10:06:20		69.2		41.5		29-May-08		10:07:53		68.61		39.5		9-Jul-08		10:25:59		72.8		50

		29-May-08		12:07:10		71		37.5		29-May-08		12:06:20		69.8		43		29-May-08		12:07:53		69.2		40		9-Jul-08		12:25:59		72.8		50.5

		29-May-08		14:07:10		71		37.5		29-May-08		14:06:20		69.2		41.5		29-May-08		14:07:53		68.61		40.5		9-Jul-08		14:25:59		72.21		49.5

		29-May-08		16:07:10		71		37		29-May-08		16:06:20		69.8		41		29-May-08		16:07:53		68.61		40.5		9-Jul-08		16:25:59		72.8		48.5

		29-May-08		18:07:10		71		38		29-May-08		18:06:20		70.41		42.5		29-May-08		18:07:53		68.61		41		9-Jul-08		18:25:59		73.4		47.5

		29-May-08		20:07:10		71		38		29-May-08		20:06:20		70.41		44.5		29-May-08		20:07:53		69.2		40.5		9-Jul-08		20:25:59		74.01		45

		29-May-08		22:07:10		71		38		29-May-08		22:06:20		70.41		43.5		29-May-08		22:07:53		69.8		40		9-Jul-08		22:25:59		75.81		44

		30-May-08		0:07:10		69.8		38.5		30-May-08		0:06:20		69.2		47		30-May-08		0:07:53		67.4		42.5		10-Jul-08		0:25:59		75.2		44

		30-May-08		2:07:10		70.41		39		30-May-08		2:06:20		68.61		46.5		30-May-08		2:07:53		69.2		41		10-Jul-08		2:25:59		74.6		44

		30-May-08		4:07:10		71		39		30-May-08		4:06:20		68.61		47.5		30-May-08		4:07:53		69.8		40.5		10-Jul-08		4:25:59		74.01		44.5

		30-May-08		6:07:10		71		38.5		30-May-08		6:06:20		68		47.5		30-May-08		6:07:53		69.8		40.5		10-Jul-08		6:25:59		73.4		43

		30-May-08		8:07:10		70.41		39.5		30-May-08		8:06:20		70.41		48.5		30-May-08		8:07:53		68.61		42		10-Jul-08		8:25:59		73.4		46

		30-May-08		10:07:10		71		39		30-May-08		10:06:20		71		44.5		30-May-08		10:07:53		68.61		41.5		10-Jul-08		10:25:59		74.01		47.5

		30-May-08		12:07:10		71.6		39		30-May-08		12:06:20		69.2		49		30-May-08		12:07:53		69.2		41.5		10-Jul-08		12:25:59		72.8		49.5

		30-May-08		14:07:10		71		39.5		30-May-08		14:06:20		69.2		45.5		30-May-08		14:07:53		69.2		42.5		10-Jul-08		14:25:59		72.21		51

		30-May-08		16:07:10		71		39.5		30-May-08		16:06:20		69.2		49		30-May-08		16:07:53		68		44		10-Jul-08		16:25:59		72.8		50.5

		30-May-08		18:07:10		71		39		30-May-08		18:06:20		69.2		47.5		30-May-08		18:07:53		68.61		42		10-Jul-08		18:25:59		73.4		49

		30-May-08		20:07:10		71		38.5		30-May-08		20:06:20		69.2		44		30-May-08		20:07:53		69.2		41		10-Jul-08		20:25:59		74.6		46

		30-May-08		22:07:10		70.41		38.5		30-May-08		22:06:20		68.61		45		30-May-08		22:07:53		69.2		41		10-Jul-08		22:25:59		75.81		47

		31-May-08		0:07:10		71		39.5		31-May-08		0:06:20		68		49.5		31-May-08		0:07:53		69.2		42		11-Jul-08		0:25:59		75.81		46

		31-May-08		2:07:10		70.41		39		31-May-08		2:06:20		68		49.5		31-May-08		2:07:53		69.2		41		11-Jul-08		2:25:59		74.6		46.5

		31-May-08		4:07:10		70.41		39		31-May-08		4:06:20		68		49		31-May-08		4:07:53		69.8		40.5		11-Jul-08		4:25:59		74.01		46.5

		31-May-08		6:07:10		70.41		39		31-May-08		6:06:20		68		51.5		31-May-08		6:07:53		68.61		41.5		11-Jul-08		6:25:59		73.4		44.5

		31-May-08		8:07:10		71		39		31-May-08		8:06:20		68		45.5		31-May-08		8:07:53		68		42.5		11-Jul-08		8:25:59		72.21		47.5

		31-May-08		10:07:10		70.41		39.5		31-May-08		10:06:20		69.2		51		31-May-08		10:07:53		68		42.5		11-Jul-08		10:25:59		73.4		50.5

		31-May-08		12:07:10		71		40		31-May-08		12:06:20		69.2		49		31-May-08		12:07:53		68		44		11-Jul-08		12:25:59		72.8		51

		31-May-08		14:07:10		71		42		31-May-08		14:06:20		69.2		48		31-May-08		14:07:53		68.61		45.5		11-Jul-08		14:25:59		72.8		51.5

		31-May-08		16:07:10		71		40.5		31-May-08		16:06:20		69.2		51		31-May-08		16:07:53		68.61		45		11-Jul-08		16:25:59		72.8		49

		31-May-08		18:07:10		71		40.5		31-May-08		18:06:20		68.61		52.5		31-May-08		18:07:53		68		45		11-Jul-08		18:25:59		73.4		47.5

		31-May-08		20:07:10		71		39.5		31-May-08		20:06:20		68.61		52		31-May-08		20:07:53		68.61		43		11-Jul-08		20:25:59		74.01		46.5

		31-May-08		22:07:10		70.41		39		31-May-08		22:06:20		69.2		48		31-May-08		22:07:53		69.8		41		11-Jul-08		22:25:59		75.2		45

		1-Jun-08		0:07:10		70.41		39.5		1-Jun-08		0:06:20		68.61		47.5		1-Jun-08		0:07:53		68.61		41.5		12-Jul-08		0:25:59		74.6		43.5

		1-Jun-08		2:07:10		70.41		39		1-Jun-08		2:06:20		68.61		47.5		1-Jun-08		2:07:53		69.2		41		12-Jul-08		2:25:59		73.4		44

		1-Jun-08		4:07:10		70.41		39		1-Jun-08		4:06:20		68.61		47.5		1-Jun-08		4:07:53		69.2		41.5		12-Jul-08		4:25:59		72.21		44.5

		1-Jun-08		6:07:10		70.41		39		1-Jun-08		6:06:20		67.4		50.5		1-Jun-08		6:07:53		69.8		41		12-Jul-08		6:25:59		72.21		44

		1-Jun-08		8:07:10		70.41		39.5		1-Jun-08		8:06:20		67.4		51		1-Jun-08		8:07:53		69.2		41.5		12-Jul-08		8:25:59		71.6		46.5

		1-Jun-08		10:07:10		70.41		39.5		1-Jun-08		10:06:20		67.4		50		1-Jun-08		10:07:53		69.8		41		12-Jul-08		10:25:59		72.8		48

		1-Jun-08		12:07:10		70.41		39.5		1-Jun-08		12:06:20		67.4		50.5		1-Jun-08		12:07:53		69.2		42		12-Jul-08		12:25:59		74.6		46.5

		1-Jun-08		14:07:10		71		41		1-Jun-08		14:06:20		68.61		52		1-Jun-08		14:07:53		69.2		43.5		12-Jul-08		14:25:59		74.6		46.5

		1-Jun-08		16:07:10		71		40		1-Jun-08		16:06:20		69.2		50		1-Jun-08		16:07:53		69.2		43.5		12-Jul-08		16:25:59		75.81		45

		1-Jun-08		18:07:10		71.6		39.5		1-Jun-08		18:06:20		69.2		47.5		1-Jun-08		18:07:53		69.2		43		12-Jul-08		18:25:59		75.2		44.5

		1-Jun-08		20:07:10		71.6		38.5		1-Jun-08		20:06:20		68.61		47		1-Jun-08		20:07:53		69.2		42		12-Jul-08		20:25:59		75.81		41.5

		1-Jun-08		22:07:10		70.41		38.5		1-Jun-08		22:06:20		68		47.5		1-Jun-08		22:07:53		68.61		41		12-Jul-08		22:25:59		76.4		43

		2-Jun-08		0:07:10		70.41		38.5		2-Jun-08		0:06:20		68.61		46		2-Jun-08		0:07:53		68.61		41		13-Jul-08		0:25:59		76.4		43

		2-Jun-08		2:07:10		70.41		38		2-Jun-08		2:06:20		68		46		2-Jun-08		2:07:53		68.61		40.5		13-Jul-08		2:25:59		75.81		44

		2-Jun-08		4:07:10		70.41		37		2-Jun-08		4:06:20		67.4		45		2-Jun-08		4:07:53		68.61		39.5		13-Jul-08		4:25:59		75.81		44

		2-Jun-08		6:07:10		69.8		36		2-Jun-08		6:06:20		66.2		44		2-Jun-08		6:07:53		68.61		38.5		13-Jul-08		6:25:59		75.81		44.5

		2-Jun-08		8:07:10		70.41		38		2-Jun-08		8:06:20		66.81		46		2-Jun-08		8:07:53		69.2		40		13-Jul-08		8:25:59		75.81		44.5

		2-Jun-08		10:07:10		69.8		37		2-Jun-08		10:06:20		68.61		40.5		2-Jun-08		10:07:53		68.61		39.5		13-Jul-08		10:25:59		75.81		44.5

		2-Jun-08		12:07:10		70.41		38		2-Jun-08		12:06:20		69.2		41		2-Jun-08		12:07:53		69.2		39.5		13-Jul-08		12:25:59		76.4		44

		2-Jun-08		14:07:10		71		39		2-Jun-08		14:06:20		69.8		42		2-Jun-08		14:07:53		69.2		41.5		13-Jul-08		14:25:59		77.61		44.5

		2-Jun-08		16:07:10		71		38.5		2-Jun-08		16:06:20		69.2		45.5		2-Jun-08		16:07:53		65.01		46		13-Jul-08		16:25:59		78.8		43.5

		2-Jun-08		18:07:10		71		38.5		2-Jun-08		18:06:20		68.61		45		2-Jun-08		18:07:53		67.4		43		13-Jul-08		18:25:59		78.8		43

		2-Jun-08		20:07:10		71		37.5		2-Jun-08		20:06:20		67.4		47		2-Jun-08		20:07:53		66.81		43.5		13-Jul-08		20:25:59		78.8		43.5

		2-Jun-08		22:07:10		69.8		37		2-Jun-08		22:06:20		68		45		2-Jun-08		22:07:53		67.4		42		13-Jul-08		22:25:59		77.61		42.5

		3-Jun-08		0:07:10		69.8		37		3-Jun-08		0:06:20		67.4		44		3-Jun-08		0:07:53		67.4		41		14-Jul-08		0:25:59		77		42.5

		3-Jun-08		2:07:10		70.41		36.5		3-Jun-08		2:06:20		66.81		43.5		3-Jun-08		2:07:53		66.81		40.5		14-Jul-08		2:25:59		76.4		42.5

		3-Jun-08		4:07:10		69.8		35		3-Jun-08		4:06:20		66.2		43		3-Jun-08		4:07:53		67.4		39.5		14-Jul-08		4:25:59		75.81		42.5

		3-Jun-08		6:07:10		70.41		35.5		3-Jun-08		6:06:20		66.2		42.5		3-Jun-08		6:07:53		67.4		38.5		14-Jul-08		6:25:59		75.2		42

		3-Jun-08		8:07:10		70.41		37		3-Jun-08		8:06:20		68		42		3-Jun-08		8:07:53		68.61		39.5		14-Jul-08		8:25:59		74.6		42.5

		3-Jun-08		10:07:10		71		37		3-Jun-08		10:06:20		68		44.5		3-Jun-08		10:07:53		67.4		41.5		14-Jul-08		10:25:59		75.2		42.5

		3-Jun-08		12:07:10		71		37.5		3-Jun-08		12:06:20		71		41		3-Jun-08		12:07:53		68		41.5		14-Jul-08		12:25:59		76.4		43

		3-Jun-08		14:07:10		71		39.5		3-Jun-08		14:06:20		70.41		45.5		3-Jun-08		14:07:53		66.81		45		14-Jul-08		14:25:59		77		43.5

		3-Jun-08		16:07:10		71		39.5		3-Jun-08		16:06:20		69.2		44.5		3-Jun-08		16:07:53		67.4		44.5		14-Jul-08		16:25:59		78.2		43.5

		3-Jun-08		18:07:10		71		39.5		3-Jun-08		18:06:20		69.2		45		3-Jun-08		18:07:53		67.4		44.5		14-Jul-08		18:25:59		78.8		43

		3-Jun-08		20:07:10		71		30.5		3-Jun-08		20:06:20		69.2		31.5		3-Jun-08		20:07:53		67.4		34.5		14-Jul-08		20:25:59		78.8		42.5

		3-Jun-08		22:07:10		70.41		27		3-Jun-08		22:06:20		68.61		29.5		3-Jun-08		22:07:53		68		31		14-Jul-08		22:25:59		77.61		41.5

		4-Jun-08		0:07:10		69.2		34		4-Jun-08		0:06:20		68.61		37		4-Jun-08		0:07:53		68		37		15-Jul-08		0:25:59		77		41

		4-Jun-08		2:07:10		69.2		35.5		4-Jun-08		2:06:20		68		40		4-Jun-08		2:07:53		68		38		15-Jul-08		2:25:59		76.4		41

		4-Jun-08		4:07:10		68.61		35		4-Jun-08		4:06:20		67.4		39.5		4-Jun-08		4:07:53		68		37.5		15-Jul-08		4:25:59		75.81		41.5

		4-Jun-08		6:07:10		69.8		34.5		4-Jun-08		6:06:20		68		39		4-Jun-08		6:07:53		68.61		37		15-Jul-08		6:25:59		75.2		41

		4-Jun-08		8:07:10		69.8		38.5		4-Jun-08		8:06:20		68		46		4-Jun-08		8:07:53		68		40.5		15-Jul-08		8:25:59		74.01		43.5

		4-Jun-08		10:07:10		70.41		41		4-Jun-08		10:06:20		69.8		53		4-Jun-08		10:07:53		68		45		15-Jul-08		10:25:59		74.6		45

		4-Jun-08		12:07:10		71		42.5		4-Jun-08		12:06:20		69.8		50		4-Jun-08		12:07:53		68		46.5		15-Jul-08		12:25:59		75.2		44.5

		4-Jun-08		14:07:10		70.41		41.5		4-Jun-08		14:06:20		69.2		53		4-Jun-08		14:07:53		66.81		47		15-Jul-08		14:25:59		75.81		45

		4-Jun-08		16:07:10		70.41		40		4-Jun-08		16:06:20		70.41		44.5		4-Jun-08		16:07:53		67.4		44.5		15-Jul-08		16:25:59		75.81		44

		4-Jun-08		18:07:10		71		38		4-Jun-08		18:06:20		70.41		38.5		4-Jun-08		18:07:53		67.4		42		15-Jul-08		18:25:59		76.4		42.5

		4-Jun-08		20:07:10		71		38		4-Jun-08		20:06:20		70.41		42		4-Jun-08		20:07:53		67.4		43		15-Jul-08		20:25:59		77		39.5

		4-Jun-08		22:07:10		71		37.5		4-Jun-08		22:06:20		69.8		43		4-Jun-08		22:07:53		67.4		42.5		15-Jul-08		22:25:59		77		41

		5-Jun-08		0:07:10		70.41		38		5-Jun-08		0:06:20		69.2		44		5-Jun-08		0:07:53		68		41.5		16-Jul-08		0:25:59		76.4		41.5

		5-Jun-08		2:07:10		69.8		36		5-Jun-08		2:06:20		69.8		38.5		5-Jun-08		2:07:53		68.61		39		16-Jul-08		2:25:59		75.81		41.5

		5-Jun-08		4:07:10		68.61		36		5-Jun-08		4:06:20		69.2		38.5		5-Jun-08		4:07:53		68		38.5		16-Jul-08		4:25:59		75.81		42

		5-Jun-08		6:07:10		68.61		36		5-Jun-08		6:06:20		68.61		38.5		5-Jun-08		6:07:53		68		38		16-Jul-08		6:25:59		75.2		41

		5-Jun-08		8:07:10		69.2		35		5-Jun-08		8:06:20		69.2		39.5		5-Jun-08		8:07:53		68		38		16-Jul-08		8:25:59		74.6		43.5

		5-Jun-08		10:07:10		70.41		35		5-Jun-08		10:06:20		71		36.5		5-Jun-08		10:07:53		68		38.5		16-Jul-08		10:25:59		75.2		44.5

		5-Jun-08		12:07:10		70.41		34.5		5-Jun-08		12:06:20		69.8		35		5-Jun-08		12:07:53		68.61		37		16-Jul-08		12:25:59		75.2		43.5

		5-Jun-08		14:07:10		70.41		32		5-Jun-08		14:06:20		69.2		34.5		5-Jun-08		14:07:53		68.61		35		16-Jul-08		14:25:59		75.81		45

		5-Jun-08		16:07:10		70.41		34.5		5-Jun-08		16:06:20		70.41		36.5		5-Jun-08		16:07:53		68.61		37.5		16-Jul-08		16:25:59		75.2		43.5

		5-Jun-08		18:07:10		71		35		5-Jun-08		18:06:20		69.8		36		5-Jun-08		18:07:53		68.61		37.5

		5-Jun-08		20:07:10		71		35.5		5-Jun-08		20:06:20		69.2		38.5		5-Jun-08		20:07:53		69.2		38

		5-Jun-08		22:07:10		71		35		5-Jun-08		22:06:20		68.61		39		5-Jun-08		22:07:53		69.2		37.5

		6-Jun-08		0:07:10		69.8		35.5		6-Jun-08		0:06:20		68		41		6-Jun-08		0:07:53		68.61		38.5

		6-Jun-08		2:07:10		69.2		36		6-Jun-08		2:06:20		67.4		41		6-Jun-08		2:07:53		68.61		38

		6-Jun-08		4:07:10		69.2		36		6-Jun-08		4:06:20		67.4		41.5		6-Jun-08		4:07:53		68.61		38.5

		6-Jun-08		6:07:10		69.2		36		6-Jun-08		6:06:20		67.4		41.5		6-Jun-08		6:07:53		68		38.5

		6-Jun-08		8:07:10		69.8		36.5		6-Jun-08		8:06:20		68		42		6-Jun-08		8:07:53		68.61		39.5

		6-Jun-08		10:07:10		70.41		36		6-Jun-08		10:06:20		68		42		6-Jun-08		10:07:53		68		40

		6-Jun-08		12:07:10		70.41		33		6-Jun-08		12:06:20		69.8		36		6-Jun-08		12:07:53		68		37.5

		6-Jun-08		14:07:10		70.41		38.5		6-Jun-08		14:06:20		69.2		40.5		6-Jun-08		14:07:53		67.4		42

		6-Jun-08		16:07:10		70.41		39.5		6-Jun-08		16:06:20		69.8		43		6-Jun-08		16:07:53		68		43

		6-Jun-08		18:07:10		71		38.5		6-Jun-08		18:06:20		69.2		44.5		6-Jun-08		18:07:53		68		42.5

		6-Jun-08		20:07:10		71		39.5		6-Jun-08		20:06:20		69.2		47		6-Jun-08		20:07:53		68.61		43

		6-Jun-08		22:07:10		71		39		6-Jun-08		22:06:20		68.61		51.5		6-Jun-08		22:07:53		68.61		43

		7-Jun-08		0:07:10		70.41		38.5		7-Jun-08		0:06:20		68.61		45		7-Jun-08		0:07:53		69.2		41

		7-Jun-08		2:07:10		69.8		38		7-Jun-08		2:06:20		68		48.5		7-Jun-08		2:07:53		69.2		40.5

		7-Jun-08		4:07:10		69.2		38		7-Jun-08		4:06:20		67.4		45.5		7-Jun-08		4:07:53		68.61		40

		7-Jun-08		6:07:10		69.2		37.5		7-Jun-08		6:06:20		67.4		43.5		7-Jun-08		6:07:53		68.61		39.5

		7-Jun-08		8:07:10		69.8		37.5		7-Jun-08		8:06:20		68.61		44		7-Jun-08		8:07:53		68.61		39.5

		7-Jun-08		10:07:10		70.41		36		7-Jun-08		10:06:20		68.61		40		7-Jun-08		10:07:53		68		39.5

		7-Jun-08		12:07:10		70.41		34.5		7-Jun-08		12:06:20		70.41		36.5		7-Jun-08		12:07:53		69.2		37

		7-Jun-08		14:07:10		70.41		31.5		7-Jun-08		14:06:20		69.8		32.5		7-Jun-08		14:07:53		68.61		33.5

		7-Jun-08		16:07:10		71		32		7-Jun-08		16:06:20		68.61		34.5		7-Jun-08		16:07:53		68		35

		7-Jun-08		18:07:10		70.41		34.5		7-Jun-08		18:06:20		68.61		36.5		7-Jun-08		18:07:53		68.61		36.5

		7-Jun-08		20:07:10		71		34.5		7-Jun-08		20:06:20		69.2		38		7-Jun-08		20:07:53		69.2		37

		7-Jun-08		22:07:10		70.41		34		7-Jun-08		22:06:20		68.61		38		7-Jun-08		22:07:53		68.61		36.5

		8-Jun-08		0:07:10		69.8		34		8-Jun-08		0:06:20		68		38		8-Jun-08		0:07:53		68.61		36.5

		8-Jun-08		2:07:10		69.2		34		8-Jun-08		2:06:20		68		37.5		8-Jun-08		2:07:53		68.61		36

		8-Jun-08		4:07:10		69.2		34		8-Jun-08		4:06:20		68		37		8-Jun-08		4:07:53		68.61		35.5

		8-Jun-08		6:07:10		69.8		33		8-Jun-08		6:06:20		67.4		37		8-Jun-08		6:07:53		68.61		35.5

		8-Jun-08		8:07:10		69.8		33.5		8-Jun-08		8:06:20		68		36.5		8-Jun-08		8:07:53		68.61		35.5

		8-Jun-08		10:07:10		70.41		34.5		8-Jun-08		10:06:20		68		37		8-Jun-08		10:07:53		69.2		35.5

		8-Jun-08		12:07:10		71		33		8-Jun-08		12:06:20		68.61		34.5		8-Jun-08		12:07:53		69.2		35

		8-Jun-08		14:07:10		71		30.5		8-Jun-08		14:06:20		68.61		32		8-Jun-08		14:07:53		69.2		33

		8-Jun-08		16:07:10		71.6		31		8-Jun-08		16:06:20		69.2		33.5		8-Jun-08		16:07:53		68.61		34.5

		8-Jun-08		18:07:10		71.6		34.5		8-Jun-08		18:06:20		68.61		37.5		8-Jun-08		18:07:53		68.61		38

		8-Jun-08		20:07:10		71.6		36.5		8-Jun-08		20:06:20		68.61		45		8-Jun-08		20:07:53		68.61		40.5

		8-Jun-08		22:07:10		71		37		8-Jun-08		22:06:20		68.61		44		8-Jun-08		22:07:53		68.61		40

		9-Jun-08		0:07:10		71		36		9-Jun-08		0:06:20		68.61		40.5		9-Jun-08		0:07:53		69.2		38.5

		9-Jun-08		2:07:10		70.41		36.5		9-Jun-08		2:06:20		68		43		9-Jun-08		2:07:53		69.2		38

		9-Jun-08		4:07:10		69.8		36.5		9-Jun-08		4:06:20		68		43		9-Jun-08		4:07:53		69.2		38.5

		9-Jun-08		6:07:10		69.2		37		9-Jun-08		6:06:20		67.4		43.5		9-Jun-08		6:07:53		69.2		39

		9-Jun-08		8:07:10		69.8		38		9-Jun-08		8:06:20		67.4		45		9-Jun-08		8:07:53		69.2		39

		9-Jun-08		10:07:10		70.41		38.5		9-Jun-08		10:06:20		68.61		43.5		9-Jun-08		10:07:53		69.2		40

		9-Jun-08		12:07:10		71		38		9-Jun-08		12:06:20		68.61		42.5		9-Jun-08		12:07:53		69.8		40.5

		9-Jun-08		14:07:10		71		38		9-Jun-08		14:06:20		68.61		41.5		9-Jun-08		14:07:53		69.2		40.5

		9-Jun-08		16:07:10		72.21		38.5		9-Jun-08		16:06:20		68.61		44.5		9-Jun-08		16:07:53		69.8		42

		9-Jun-08		18:07:10		71.6		39		9-Jun-08		18:06:20		68.61		46.5		9-Jun-08		18:07:53		69.2		43

		9-Jun-08		20:07:10		71.6		38		9-Jun-08		20:06:20		68		48		9-Jun-08		20:07:53		69.2		41.5

		9-Jun-08		22:07:10		71		37.5		9-Jun-08		22:06:20		68		47		9-Jun-08		22:07:53		69.2		40

		10-Jun-08		0:07:10		70.41		37.5		10-Jun-08		0:06:20		68		45.5		10-Jun-08		0:07:53		69.2		39.5

		10-Jun-08		2:07:10		69.8		37		10-Jun-08		2:06:20		67.4		46		10-Jun-08		2:07:53		69.2		39.5

		10-Jun-08		4:07:10		69.8		38		10-Jun-08		4:06:20		68		47		10-Jun-08		4:07:53		69.2		39.5

		10-Jun-08		6:07:10		69.8		38		10-Jun-08		6:06:20		68		44.5		10-Jun-08		6:07:53		69.8		39.5

		10-Jun-08		8:07:10		71		38.5		10-Jun-08		8:06:20		68.61		48		10-Jun-08		8:07:53		69.2		41

		10-Jun-08		10:07:10		71		37.5		10-Jun-08		10:06:20		69.2		43		10-Jun-08		10:07:53		69.2		40.5

		10-Jun-08		12:07:10		71		38		10-Jun-08		12:06:20		70.41		40		10-Jun-08		12:07:53		69.2		40.5

		10-Jun-08		14:07:10		71		37.5		10-Jun-08		14:06:20		71.6		37.5		10-Jun-08		14:07:53		68.61		39.5

		10-Jun-08		16:07:10		70.41		40		10-Jun-08		16:06:20		70.41		41		10-Jun-08		16:07:53		68.61		42

		10-Jun-08		18:07:10		70.41		44		10-Jun-08		18:06:20		71.6		47.5		10-Jun-08		18:07:53		69.2		46.5

		10-Jun-08		20:07:10		71		42		10-Jun-08		20:06:20		71		47		10-Jun-08		20:07:53		68.61		46

		10-Jun-08		22:07:10		71.6		41		10-Jun-08		22:06:20		71		51		10-Jun-08		22:07:53		69.2		44.5

		11-Jun-08		0:07:10		71.6		40.5		11-Jun-08		0:06:20		71		47.5		11-Jun-08		0:07:53		68.61		45

		11-Jun-08		2:07:10		71.6		36.5		11-Jun-08		2:06:20		71		40.5		11-Jun-08		2:07:53		69.2		40

		11-Jun-08		4:07:10		71		37.5		11-Jun-08		4:06:20		69.8		44		11-Jun-08		4:07:53		69.2		40.5

		11-Jun-08		6:07:10		70.41		36.5		11-Jun-08		6:06:20		69.8		41		11-Jun-08		6:07:53		69.2		39

		11-Jun-08		8:07:10		71		35.5		11-Jun-08		8:06:20		70.41		39		11-Jun-08		8:07:53		68		39

		11-Jun-08		10:07:10		71		27.5		11-Jun-08		10:06:20		70.41		29.5		11-Jun-08		10:07:53		67.4		31.5

		11-Jun-08		12:07:10		71		24		11-Jun-08		12:06:20		69.8		24.5		11-Jun-08		12:07:53		68.61		27

		11-Jun-08		14:07:10		71.6		27.5		11-Jun-08		14:06:20		70.41		30.5		11-Jun-08		14:07:53		68		31.5

		11-Jun-08		16:07:10		71		28.5		11-Jun-08		16:06:20		69.8		30		11-Jun-08		16:07:53		68.61		31.5

		11-Jun-08		18:07:10		71		31.5		11-Jun-08		18:06:20		69.8		33		11-Jun-08		18:07:53		68.61		34

		11-Jun-08		20:07:10		71		33.5		11-Jun-08		20:06:20		69.8		35		11-Jun-08		20:07:53		68.61		36

		11-Jun-08		22:07:10		71.6		33.5		11-Jun-08		22:06:20		69.2		37		11-Jun-08		22:07:53		68.61		37

		12-Jun-08		0:07:10		70.41		34		12-Jun-08		0:06:20		69.2		36.5		12-Jun-08		0:07:53		68.61		36.5

		12-Jun-08		2:07:10		69.8		33.5		12-Jun-08		2:06:20		68.61		36.5		12-Jun-08		2:07:53		68.61		36

		12-Jun-08		4:07:10		69.2		34		12-Jun-08		4:06:20		68.61		37		12-Jun-08		4:07:53		68.61		36

		12-Jun-08		6:07:10		68.61		34.5		12-Jun-08		6:06:20		68		37		12-Jun-08		6:07:53		68		36.5

		12-Jun-08		8:07:10		69.8		34.5		12-Jun-08		8:06:20		69.2		37.5		12-Jun-08		8:07:53		68.61		36.5

		12-Jun-08		10:07:10		71		34		12-Jun-08		10:06:20		71		36		12-Jun-08		10:07:53		68.61		37

		12-Jun-08		12:07:10		71		29.5		12-Jun-08		12:06:20		71.6		30		12-Jun-08		12:07:53		69.8		32

		12-Jun-08		14:07:10		71		24.5		12-Jun-08		14:06:20		72.8		26		12-Jun-08		14:07:53		69.8		28.5

		12-Jun-08		16:07:10		71		26.5		12-Jun-08		16:06:20		71.6		20.5		12-Jun-08		16:07:53		69.2		28

		12-Jun-08		18:07:10		70.41		27.5		12-Jun-08		18:06:20		71		27.5		12-Jun-08		18:07:53		69.2		29.5

		12-Jun-08		20:07:10		70.41		35.5		12-Jun-08		20:06:20		71		38.5		12-Jun-08		20:07:53		69.2		38

		12-Jun-08		22:07:10		71		35.5		12-Jun-08		22:06:20		70.41		40		12-Jun-08		22:07:53		69.2		38

		13-Jun-08		0:07:10		70.41		36		13-Jun-08		0:06:20		70.41		39.5		13-Jun-08		0:07:53		69.2		37.5

		13-Jun-08		2:07:10		69.8		36		13-Jun-08		2:06:20		69.8		39.5		13-Jun-08		2:07:53		69.2		37.5

		13-Jun-08		4:07:10		69.8		36.5		13-Jun-08		4:06:20		69.8		40.5		13-Jun-08		4:07:53		69.2		38

		13-Jun-08		6:07:10		69.2		36.5		13-Jun-08		6:06:20		69.8		39.5		13-Jun-08		6:07:53		69.2		37.5

		13-Jun-08		8:07:10		70.41		37		13-Jun-08		8:06:20		70.41		39.5		13-Jun-08		8:07:53		69.2		39

		13-Jun-08		10:07:10		71		36.5		13-Jun-08		10:06:20		70.41		38.5		13-Jun-08		10:07:53		69.2		38.5

		13-Jun-08		12:07:10		71		24		13-Jun-08		12:06:20		71.6		25		13-Jun-08		12:07:53		69.8		28

		13-Jun-08		14:07:10		71		22.5		13-Jun-08		14:06:20		71.6		23.5		13-Jun-08		14:07:53		69.2		25

		13-Jun-08		16:07:10		70.41		29		13-Jun-08		16:06:20		72.21		30		13-Jun-08		16:07:53		69.8		31.5

		13-Jun-08		18:07:10		71		26.5		13-Jun-08		18:06:20		71		27		13-Jun-08		18:07:53		69.8		29

		13-Jun-08		20:07:10		71		29		13-Jun-08		20:06:20		71.6		27.5		13-Jun-08		20:07:53		68.61		29.5

		13-Jun-08		22:07:10		71.6		32.5		13-Jun-08		22:06:20		71		33.5		13-Jun-08		22:07:53		69.2		34.5

		14-Jun-08		0:07:10		71		33		14-Jun-08		0:06:20		70.41		35.5		14-Jun-08		0:07:53		69.2		35.5

		14-Jun-08		2:07:10		70.41		34.5		14-Jun-08		2:06:20		70.41		37		14-Jun-08		2:07:53		69.2		36

		14-Jun-08		4:07:10		69.8		34.5		14-Jun-08		4:06:20		69.8		38.5		14-Jun-08		4:07:53		69.2		36.5

		14-Jun-08		6:07:10		69.8		35.5		14-Jun-08		6:06:20		69.8		38.5		14-Jun-08		6:07:53		68.61		37

		14-Jun-08		8:07:10		70.41		36		14-Jun-08		8:06:20		71		38.5		14-Jun-08		8:07:53		69.2		38

		14-Jun-08		10:07:10		71		36.5		14-Jun-08		10:06:20		71		39.5		14-Jun-08		10:07:53		68.61		39.5

		14-Jun-08		12:07:10		70.41		39		14-Jun-08		12:06:20		71.6		42		14-Jun-08		12:07:53		69.2		41.5

		14-Jun-08		14:07:10		71		37.5		14-Jun-08		14:06:20		72.8		37		14-Jun-08		14:07:53		69.2		39.5

		14-Jun-08		16:07:10		70.41		39		14-Jun-08		16:06:20		71		41		14-Jun-08		16:07:53		69.8		41

		14-Jun-08		18:07:10		70.41		39		14-Jun-08		18:06:20		71		42.5		14-Jun-08		18:07:53		68.61		42

		14-Jun-08		20:07:10		70.41		38		14-Jun-08		20:06:20		70.41		45		14-Jun-08		20:07:53		68.61		41.5

		14-Jun-08		22:07:10		70.41		38		14-Jun-08		22:06:20		71		45		14-Jun-08		22:07:53		68.61		40.5

		15-Jun-08		0:07:10		70.41		38.5		15-Jun-08		0:06:20		69.8		43.5		15-Jun-08		0:07:53		68.61		40.5

		15-Jun-08		2:07:10		70.41		38		15-Jun-08		2:06:20		69.8		44		15-Jun-08		2:07:53		68.61		40.5

		15-Jun-08		4:07:10		69.8		37.5		15-Jun-08		4:06:20		69.2		44		15-Jun-08		4:07:53		68.61		40

		15-Jun-08		6:07:10		69.8		38		15-Jun-08		6:06:20		69.2		45		15-Jun-08		6:07:53		68.61		40.5

		15-Jun-08		8:07:10		70.41		39		15-Jun-08		8:06:20		69.2		45.5		15-Jun-08		8:07:53		68.61		41

		15-Jun-08		10:07:10		70.41		39		15-Jun-08		10:06:20		69.8		45		15-Jun-08		10:07:53		68.61		41

		15-Jun-08		12:07:10		70.41		40		15-Jun-08		12:06:20		70.41		46.5		15-Jun-08		12:07:53		69.2		42

		15-Jun-08		14:07:10		71		41.5		15-Jun-08		14:06:20		71		47.5		15-Jun-08		14:07:53		69.2		44

		15-Jun-08		16:07:10		71		41.5		15-Jun-08		16:06:20		70.41		51.5		15-Jun-08		16:07:53		69.2		44.5

		15-Jun-08		18:07:10		71		40.5		15-Jun-08		18:06:20		70.41		50		15-Jun-08		18:07:53		69.2		43.5

		15-Jun-08		20:07:10		71		38.5		15-Jun-08		20:06:20		69.8		47		15-Jun-08		20:07:53		69.2		41.5

		15-Jun-08		22:07:10		71		38.5		15-Jun-08		22:06:20		70.41		45.5		15-Jun-08		22:07:53		69.2		41

		16-Jun-08		0:07:10		70.41		38.5		16-Jun-08		0:06:20		69.8		44.5		16-Jun-08		0:07:53		69.2		40.5

		16-Jun-08		2:07:10		70.41		38		16-Jun-08		2:06:20		69.2		44.5		16-Jun-08		2:07:53		69.2		40

		16-Jun-08		4:07:10		70.41		38		16-Jun-08		4:06:20		68.61		45		16-Jun-08		4:07:53		69.2		40

		16-Jun-08		6:07:10		69.8		37.5		16-Jun-08		6:06:20		68.61		44.5		16-Jun-08		6:07:53		69.2		39.5

		16-Jun-08		8:07:10		69.8		38		16-Jun-08		8:06:20		68.61		44.5		16-Jun-08		8:07:53		69.2		40

		16-Jun-08		10:07:10		69.8		38.5		16-Jun-08		10:06:20		69.8		44.5		16-Jun-08		10:07:53		69.2		40

		16-Jun-08		12:07:10		70.41		40.5		16-Jun-08		12:06:20		69.8		47		16-Jun-08		12:07:53		69.2		41.5

		16-Jun-08		14:07:10		70.41		42		16-Jun-08		14:06:20		70.41		49.5		16-Jun-08		14:07:53		69.2		43.5

		16-Jun-08		16:07:10		71		40.5		16-Jun-08		16:06:20		71		46		16-Jun-08		16:07:53		69.2		43

		16-Jun-08		18:07:10		71		39.5		16-Jun-08		18:06:20		71		43.5		16-Jun-08		18:07:53		69.2		42.5

		16-Jun-08		20:07:10		71		38		16-Jun-08		20:06:20		70.41		44.5		16-Jun-08		20:07:53		69.2		41

		16-Jun-08		22:07:10		70.41		38		16-Jun-08		22:06:20		70.41		43		16-Jun-08		22:07:53		69.2		40

		17-Jun-08		0:07:10		70.41		37.5		17-Jun-08		0:06:20		69.8		42		17-Jun-08		0:07:53		69.2		39.5

		17-Jun-08		2:07:10		69.8		36.5		17-Jun-08		2:06:20		68.61		43		17-Jun-08		2:07:53		69.2		39

		17-Jun-08		4:07:10		69.8		38		17-Jun-08		4:06:20		68		45.5		17-Jun-08		4:07:53		69.2		40

		17-Jun-08		6:07:10		69.8		38		17-Jun-08		6:06:20		68		45.5		17-Jun-08		6:07:53		69.2		40

		17-Jun-08		8:07:10		70.41		38.5		17-Jun-08		8:06:20		70.41		45		17-Jun-08		8:07:53		68.61		41

		17-Jun-08		10:07:10		70.41		39		17-Jun-08		10:06:20		71		44		17-Jun-08		10:07:53		68.61		41

		17-Jun-08		12:07:10		71		39.5		17-Jun-08		12:06:20		69.8		45.5		17-Jun-08		12:07:53		69.2		42

		17-Jun-08		14:07:10		71		41.5		17-Jun-08		14:06:20		70.41		48.5		17-Jun-08		14:07:53		68		45

		17-Jun-08		16:07:10		71		40		17-Jun-08		16:06:20		70.41		45		17-Jun-08		16:07:53		69.2		43.5

		17-Jun-08		18:07:10		71		39.5		17-Jun-08		18:06:20		70.41		46		17-Jun-08		18:07:53		69.8		41.5

		17-Jun-08		20:07:10		70.41		38.5		17-Jun-08		20:06:20		69.8		44.5		17-Jun-08		20:07:53		69.8		40

		17-Jun-08		22:07:10		70.41		38		17-Jun-08		22:06:20		69.8		43		17-Jun-08		22:07:53		69.8		39.5

		18-Jun-08		0:07:10		70.41		37.5		18-Jun-08		0:06:20		69.2		43		18-Jun-08		0:07:53		69.8		39

		18-Jun-08		2:07:10		70.41		37.5		18-Jun-08		2:06:20		68		43.5		18-Jun-08		2:07:53		69.8		38.5

		18-Jun-08		4:07:10		70.41		38		18-Jun-08		4:06:20		67.4		46		18-Jun-08		4:07:53		69.8		39

		18-Jun-08		6:07:10		70.41		38		18-Jun-08		6:06:20		66.81		46.5		18-Jun-08		6:07:53		69.8		39

		18-Jun-08		8:07:10		70.41		39		18-Jun-08		8:06:20		70.41		43.5		18-Jun-08		8:07:53		69.2		40.5

		18-Jun-08		10:07:10		71		38.5		18-Jun-08		10:06:20		70.41		44.5		18-Jun-08		10:07:53		68.61		41

		18-Jun-08		12:07:10		71		39		18-Jun-08		12:06:20		69.8		44.5		18-Jun-08		12:07:53		69.8		41

		18-Jun-08		14:07:10		71		42		18-Jun-08		14:06:20		69.8		46.5		18-Jun-08		14:07:53		69.2		44.5

		18-Jun-08		16:07:10		71		43.5		18-Jun-08		16:06:20		69.8		51.5		18-Jun-08		16:07:53		69.2		46

		18-Jun-08		18:07:10		71		29		18-Jun-08		18:06:20		69.2		31		18-Jun-08		18:07:53		69.2		32

		18-Jun-08		20:07:10		71		28		18-Jun-08		20:06:20		68.61		29		18-Jun-08		20:07:53		69.2		30

		18-Jun-08		22:07:10		71		29.5		18-Jun-08		22:06:20		68.61		31		18-Jun-08		22:07:53		69.2		31.5

		19-Jun-08		0:07:10		70.41		29		19-Jun-08		0:06:20		68.61		31.5		19-Jun-08		0:07:53		69.2		31

		19-Jun-08		2:07:10		69.8		34		19-Jun-08		2:06:20		68		37		19-Jun-08		2:07:53		69.2		35.5

		19-Jun-08		4:07:10		69.2		35		19-Jun-08		4:06:20		67.4		39.5		19-Jun-08		4:07:53		68.61		36.5

		19-Jun-08		6:07:10		69.8		34		19-Jun-08		6:06:20		67.4		39		19-Jun-08		6:07:53		69.2		35.5

		19-Jun-08		8:07:10		69.8		35.5		19-Jun-08		8:06:20		68		41.5		19-Jun-08		8:07:53		69.2		37.5

		19-Jun-08		10:07:10		71		33.5		19-Jun-08		10:06:20		70.41		36.5		19-Jun-08		10:07:53		69.2		36.5

		19-Jun-08		12:07:10		71		31		19-Jun-08		12:06:20		70.41		33		19-Jun-08		12:07:53		69.8		33

		19-Jun-08		14:07:10		70.41		34.5		19-Jun-08		14:06:20		71		36		19-Jun-08		14:07:53		69.8		36

		19-Jun-08		16:07:10		70.41		31		19-Jun-08		16:06:20		69.2		32.5		19-Jun-08		16:07:53		69.8		32.5

		19-Jun-08		18:07:10		71		25		19-Jun-08		18:06:20		69.2		26		19-Jun-08		18:07:53		69.2		27

		19-Jun-08		20:07:10		71		26		19-Jun-08		20:06:20		69.2		27		19-Jun-08		20:07:53		69.2		27.5

		19-Jun-08		22:07:10		71		30.5		19-Jun-08		22:06:20		68.61		31.5		19-Jun-08		22:07:53		69.2		31.5

		20-Jun-08		0:07:10		71		33		20-Jun-08		0:06:20		68		37		20-Jun-08		0:07:53		68.61		35.5

		20-Jun-08		2:07:10		70.41		33.5		20-Jun-08		2:06:20		68		37.5		20-Jun-08		2:07:53		68.61		35.5

		20-Jun-08		4:07:10		69.8		33.5		20-Jun-08		4:06:20		68		38		20-Jun-08		4:07:53		68.61		36

		20-Jun-08		6:07:10		69.2		34.5		20-Jun-08		6:06:20		67.4		39		20-Jun-08		6:07:53		68		36.5

		20-Jun-08		8:07:10		69.8		35.5		20-Jun-08		8:06:20		68.61		39		20-Jun-08		8:07:53		68.61		37.5

		20-Jun-08		10:07:10		71		35.5		20-Jun-08		10:06:20		70.41		38		20-Jun-08		10:07:53		68.61		38

		20-Jun-08		12:07:10		70.41		34		20-Jun-08		12:06:20		72.21		34.5		20-Jun-08		12:07:53		68.61		36.5

		20-Jun-08		14:07:10		70.41		31		20-Jun-08		14:06:20		69.8		32		20-Jun-08		14:07:53		68		33.5

		20-Jun-08		16:07:10		70.41		32.5		20-Jun-08		16:06:20		71		34.5		20-Jun-08		16:07:53		68.61		35.5

		20-Jun-08		18:07:10		70.41		29		20-Jun-08		18:06:20		69.2		30		20-Jun-08		18:07:53		68.61		31

		20-Jun-08		20:07:10		71		31.5		20-Jun-08		20:06:20		68		34.5		20-Jun-08		20:07:53		68.61		34.5

		20-Jun-08		22:07:10		71		32.5		20-Jun-08		22:06:20		68		36		20-Jun-08		22:07:53		68.61		35

		21-Jun-08		0:07:10		71		34.5		21-Jun-08		0:06:20		68.61		38.5		21-Jun-08		0:07:53		68.61		37

		21-Jun-08		2:07:10		70.41		35		21-Jun-08		2:06:20		67.4		41		21-Jun-08		2:07:53		68.61		37

		21-Jun-08		4:07:10		70.41		36		21-Jun-08		4:06:20		67.4		41		21-Jun-08		4:07:53		69.2		37.5

		21-Jun-08		6:07:10		69.8		36		21-Jun-08		6:06:20		68		43		21-Jun-08		6:07:53		68.61		38.5

		21-Jun-08		8:07:10		71		36		21-Jun-08		8:06:20		68.61		43		21-Jun-08		8:07:53		68.61		39

		21-Jun-08		10:07:10		71		35		21-Jun-08		10:06:20		69.2		37		21-Jun-08		10:07:53		69.2		37

		21-Jun-08		12:07:10		70.41		30.5		21-Jun-08		12:06:20		71		31.5		21-Jun-08		12:07:53		69.2		33

		21-Jun-08		14:07:10		71		30		21-Jun-08		14:06:20		70.41		30.5		21-Jun-08		14:07:53		69.2		31.5

		21-Jun-08		16:07:10		71		26.5		21-Jun-08		16:06:20		71.6		26.5		21-Jun-08		16:07:53		68.61		29

		21-Jun-08		18:07:10		70.41		23		21-Jun-08		18:06:20		70.41		24		21-Jun-08		18:07:53		69.2		26

		21-Jun-08		20:07:10		71		22.5		21-Jun-08		20:06:20		71		22.5		21-Jun-08		20:07:53		69.2		24.5

		21-Jun-08		22:07:10		71		27.5		21-Jun-08		22:06:20		70.41		29		21-Jun-08		22:07:53		69.2		30

		22-Jun-08		0:07:10		71		31		22-Jun-08		0:06:20		70.41		34		22-Jun-08		0:07:53		68.61		34.5

		22-Jun-08		2:07:10		71		31.5		22-Jun-08		2:06:20		69.8		35		22-Jun-08		2:07:53		68.61		35.5

		22-Jun-08		4:07:10		71		32.5		22-Jun-08		4:06:20		69.8		34.5		22-Jun-08		4:07:53		68.61		35.5

		22-Jun-08		6:07:10		70.41		33		22-Jun-08		6:06:20		69.2		35.5		22-Jun-08		6:07:53		68.61		35.5

		22-Jun-08		8:07:10		71		33.5		22-Jun-08		8:06:20		69.2		36.5		22-Jun-08		8:07:53		69.8		35.5

		22-Jun-08		10:07:10		71		34.5		22-Jun-08		10:06:20		70.41		37		22-Jun-08		10:07:53		69.8		37

		22-Jun-08		12:07:10		71.6		32		22-Jun-08		12:06:20		71		34.5		22-Jun-08		12:07:53		69.2		36

		22-Jun-08		14:07:10		71.6		29.5		22-Jun-08		14:06:20		71		32.5		22-Jun-08		14:07:53		69.8		33.5

		22-Jun-08		16:07:10		72.21		26		22-Jun-08		16:06:20		70.41		29		22-Jun-08		16:07:53		69.2		30.5

		22-Jun-08		18:07:10		72.21		22.5		22-Jun-08		18:06:20		70.41		25.5		22-Jun-08		18:07:53		69.2		26.5

		22-Jun-08		20:07:10		72.21		30.5		22-Jun-08		20:06:20		70.41		31.5		22-Jun-08		20:07:53		69.8		31.5

		22-Jun-08		22:07:10		71.6		31		22-Jun-08		22:06:20		70.41		34.5		22-Jun-08		22:07:53		69.2		34

		23-Jun-08		0:07:10		71		34.5		23-Jun-08		0:06:20		69.2		39		23-Jun-08		0:07:53		69.2		36.5

		23-Jun-08		2:07:10		70.41		35.5		23-Jun-08		2:06:20		69.8		41.5		23-Jun-08		2:07:53		69.2		38

		23-Jun-08		4:07:10		70.41		36		23-Jun-08		4:06:20		69.2		42		23-Jun-08		4:07:53		69.8		38

		23-Jun-08		6:07:10		70.41		35.5		23-Jun-08		6:06:20		68.61		42		23-Jun-08		6:07:53		69.8		37.5

		23-Jun-08		8:07:10		70.41		37		23-Jun-08		8:06:20		69.2		44		23-Jun-08		8:07:53		69.8		38.5

		23-Jun-08		10:07:10		71		38		23-Jun-08		10:06:20		69.2		45		23-Jun-08		10:07:53		69.8		39.5

		23-Jun-08		12:07:10		71		38.5		23-Jun-08		12:06:20		69.8		42.5		23-Jun-08		12:07:53		69.8		39.5

		23-Jun-08		14:07:10		71		39		23-Jun-08		14:06:20		70.41		44.5		23-Jun-08		14:07:53		69.8		41

		23-Jun-08		16:07:10		71.6		39.5		23-Jun-08		16:06:20		69.8		46.5		23-Jun-08		16:07:53		69.8		42

		23-Jun-08		18:07:10		71.6		38		23-Jun-08		18:06:20		70.41		42.5		23-Jun-08		18:07:53		69.2		41

		23-Jun-08		20:07:10		71.6		37		23-Jun-08		20:06:20		69.8		43		23-Jun-08		20:07:53		69.8		39.5

		23-Jun-08		22:07:10		71		36		23-Jun-08		22:06:20		69.2		42.5		23-Jun-08		22:07:53		69.8		38.5

		24-Jun-08		0:07:10		69.8		36.5		24-Jun-08		0:06:20		69.2		42		24-Jun-08		0:07:53		69.2		38.5

		24-Jun-08		2:07:10		70.41		36.5		24-Jun-08		2:06:20		68.61		42		24-Jun-08		2:07:53		69.8		38

		24-Jun-08		4:07:10		70.41		36		24-Jun-08		4:06:20		68		42.5		24-Jun-08		4:07:53		69.8		37.5

		24-Jun-08		6:07:10		70.41		37.5		24-Jun-08		6:06:20		67.4		45.5		24-Jun-08		6:07:53		69.8		38.5

		24-Jun-08		8:07:10		70.41		38.5		24-Jun-08		8:06:20		69.8		44.5		24-Jun-08		8:07:53		69.8		40

		24-Jun-08		10:07:10		70.41		38		24-Jun-08		10:06:20		71		44		24-Jun-08		10:07:53		69.2		40.5

		24-Jun-08		12:07:10		70.41		39.5		24-Jun-08		12:06:20		71.6		42.5		24-Jun-08		12:07:53		69.8		41

		24-Jun-08		14:07:10		70.41		38.5		24-Jun-08		14:06:20		71		42.5		24-Jun-08		14:07:53		68		42.5

		24-Jun-08		16:07:10		71		39		24-Jun-08		16:06:20		69.2		47		24-Jun-08		16:07:53		68		42.5

		24-Jun-08		18:07:10		71		38.5		24-Jun-08		18:06:20		69.2		45.5		24-Jun-08		18:07:53		69.2		41.5

		24-Jun-08		20:07:10		70.41		38.5		24-Jun-08		20:06:20		68.61		47		24-Jun-08		20:07:53		69.2		40.5

		24-Jun-08		22:07:10		70.41		38		24-Jun-08		22:06:20		68.61		44		24-Jun-08		22:07:53		69.2		39.5

		25-Jun-08		0:07:10		70.41		38.5		25-Jun-08		0:06:20		68		43.5		25-Jun-08		0:07:53		69.2		40

		25-Jun-08		2:07:10		70.41		37.5		25-Jun-08		2:06:20		67.4		46.5		25-Jun-08		2:07:53		69.8		39

		25-Jun-08		4:07:10		70.41		37.5		25-Jun-08		4:06:20		67.4		45		25-Jun-08		4:07:53		69.8		39

		25-Jun-08		6:07:10		70.41		37		25-Jun-08		6:06:20		66.81		45		25-Jun-08		6:07:53		69.8		38.5

		25-Jun-08		8:07:10		69.8		38.5		25-Jun-08		8:06:20		68		44		25-Jun-08		8:07:53		68.61		40.5

		25-Jun-08		10:07:10		70.41		39		25-Jun-08		10:06:20		69.8		46.5		25-Jun-08		10:07:53		68.61		42

		25-Jun-08		12:07:10		70.41		40.5		25-Jun-08		12:06:20		69.8		44		25-Jun-08		12:07:53		68		43.5

		25-Jun-08		14:07:10		70.41		42		25-Jun-08		14:06:20		69.8		47		25-Jun-08		14:07:53		67.4		46.5

		25-Jun-08		16:07:10		70.41		41.5		25-Jun-08		16:06:20		69.8		50		25-Jun-08		16:07:53		68.61		45

		25-Jun-08		18:07:10		71		39.5		25-Jun-08		18:06:20		69.2		48		25-Jun-08		18:07:53		68.61		43.5

		25-Jun-08		20:07:10		71		38.5		25-Jun-08		20:06:20		69.2		44		25-Jun-08		20:07:53		69.2		42

		25-Jun-08		22:07:10		71		38		25-Jun-08		22:06:20		69.8		43.5		25-Jun-08		22:07:53		69.2		40.5

		26-Jun-08		0:07:10		70.41		38		26-Jun-08		0:06:20		68.61		46		26-Jun-08		0:07:53		69.2		40

		26-Jun-08		2:07:10		69.8		38		26-Jun-08		2:06:20		68.61		44.5		26-Jun-08		2:07:53		68.61		39.5

		26-Jun-08		4:07:10		70.41		38		26-Jun-08		4:06:20		68.61		44		26-Jun-08		4:07:53		69.2		39.5

		26-Jun-08		6:07:10		70.41		37.5		26-Jun-08		6:06:20		68		44.5		26-Jun-08		6:07:53		69.8		39

		26-Jun-08		8:07:10		70.41		39		26-Jun-08		8:06:20		69.2		44		26-Jun-08		8:07:53		68		41.5

		26-Jun-08		10:07:10		70.41		39		26-Jun-08		10:06:20		69.2		45		26-Jun-08		10:07:53		68.61		41.5

		26-Jun-08		12:07:10		70.41		40.5		26-Jun-08		12:06:20		71		43.5		26-Jun-08		12:07:53		68.61		43

		26-Jun-08		14:07:10		70.41		42.5		26-Jun-08		14:06:20		70.41		47.5		26-Jun-08		14:07:53		68		46

		26-Jun-08		16:07:10		70.41		42.5		26-Jun-08		16:06:20		68.61		49.5		26-Jun-08		16:07:53		68.61		45.5

		26-Jun-08		18:07:10		70.41		41.5		26-Jun-08		18:06:20		69.2		47		26-Jun-08		18:07:53		69.2		43.5

		26-Jun-08		20:07:10		70.41		40		26-Jun-08		20:06:20		69.2		47.5		26-Jun-08		20:07:53		69.2		42

		26-Jun-08		22:07:10		70.41		39		26-Jun-08		22:06:20		69.2		46.5		26-Jun-08		22:07:53		69.2		41

		27-Jun-08		0:07:10		69.8		38		27-Jun-08		0:06:20		68		47.5		27-Jun-08		0:07:53		68.61		40.5

		27-Jun-08		2:07:10		69.8		38		27-Jun-08		2:06:20		67.4		46		27-Jun-08		2:07:53		69.2		40

		27-Jun-08		4:07:10		70.41		38		27-Jun-08		4:06:20		68		45		27-Jun-08		4:07:53		69.8		39

		27-Jun-08		6:07:10		69.8		37.5		27-Jun-08		6:06:20		67.4		45		27-Jun-08		6:07:53		69.8		39

		27-Jun-08		8:07:10		70.41		39		27-Jun-08		8:06:20		68.61		49.5		27-Jun-08		8:07:53		69.2		40.5

		27-Jun-08		10:07:10		70.41		39.5		27-Jun-08		10:06:20		69.8		44.5		27-Jun-08		10:07:53		68.61		42

		27-Jun-08		12:07:10		70.41		41		27-Jun-08		12:06:20		70.41		50.5		27-Jun-08		12:07:53		69.2		43

		27-Jun-08		14:07:10		70.41		43		27-Jun-08		14:06:20		71		48.5		27-Jun-08		14:07:53		68		46

		27-Jun-08		16:07:10		70.41		42.5		27-Jun-08		16:06:20		70.41		48.5		27-Jun-08		16:07:53		68		46

		27-Jun-08		18:07:10		70.41		40		27-Jun-08		18:06:20		70.41		44		27-Jun-08		18:07:53		68.61		43

		27-Jun-08		20:07:10		70.41		39		27-Jun-08		20:06:20		70.41		44.5		27-Jun-08		20:07:53		68.61		42

		27-Jun-08		22:07:10		70.41		38.5		27-Jun-08		22:06:20		70.41		45		27-Jun-08		22:07:53		69.2		41

		28-Jun-08		0:07:10		69.8		38.5		28-Jun-08		0:06:20		69.2		46		28-Jun-08		0:07:53		68.61		41

		28-Jun-08		2:07:10		69.8		38.5		28-Jun-08		2:06:20		69.2		45		28-Jun-08		2:07:53		68.61		40.5

		28-Jun-08		4:07:10		69.2		38.5		28-Jun-08		4:06:20		69.2		44.5		28-Jun-08		4:07:53		68.61		40

		28-Jun-08		6:07:10		69.2		39.5		28-Jun-08		6:06:20		69.2		45.5		28-Jun-08		6:07:53		68.61		40.5

		28-Jun-08		8:07:10		69.8		39.5		28-Jun-08		8:06:20		70.41		44		28-Jun-08		8:07:53		68.61		41.5

		28-Jun-08		10:07:10		71		40.5		28-Jun-08		10:06:20		71		50.5		28-Jun-08		10:07:53		68.61		43

		28-Jun-08		12:07:10		70.41		42.5		28-Jun-08		12:06:20		71.6		48		28-Jun-08		12:07:53		69.8		44

		28-Jun-08		14:07:10		70.41		43.5		28-Jun-08		14:06:20		71.6		53.5		28-Jun-08		14:07:53		68.61		46

		28-Jun-08		16:07:10		70.41		44		28-Jun-08		16:06:20		71		50		28-Jun-08		16:07:53		69.2		46.5

		28-Jun-08		18:07:10		71		40.5		28-Jun-08		18:06:20		70.41		51		28-Jun-08		18:07:53		69.2		43.5

		28-Jun-08		20:07:10		71		39.5		28-Jun-08		20:06:20		70.41		49.5		28-Jun-08		20:07:53		69.2		42

		28-Jun-08		22:07:10		70.41		39.5		28-Jun-08		22:06:20		69.8		49		28-Jun-08		22:07:53		69.8		41

		29-Jun-08		0:07:10		69.8		39.5		29-Jun-08		0:06:20		69.8		49.5		29-Jun-08		0:07:53		69.2		41.5

		29-Jun-08		2:07:10		69.8		40		29-Jun-08		2:06:20		69.2		49		29-Jun-08		2:07:53		69.2		41.5

		29-Jun-08		4:07:10		69.8		40		29-Jun-08		4:06:20		69.2		50		29-Jun-08		4:07:53		69.8		41.5

		29-Jun-08		6:07:10		69.8		40		29-Jun-08		6:06:20		69.2		50.5		29-Jun-08		6:07:53		69.8		41

		29-Jun-08		8:07:10		69.8		40		29-Jun-08		8:06:20		69.8		50.5		29-Jun-08		8:07:53		69.8		41.5

		29-Jun-08		10:07:10		70.41		40.5		29-Jun-08		10:06:20		69.2		47		29-Jun-08		10:07:53		69.8		41.5

		29-Jun-08		12:07:10		70.41		41.5		29-Jun-08		12:06:20		69.2		53.5		29-Jun-08		12:07:53		69.8		42.5

		29-Jun-08		14:07:10		70.41		42.5		29-Jun-08		14:06:20		69.8		48		29-Jun-08		14:07:53		70.41		44

		29-Jun-08		16:07:10		71		43		29-Jun-08		16:06:20		69.8		52.5		29-Jun-08		16:07:53		70.41		44.5

		29-Jun-08		18:07:10		71		42		29-Jun-08		18:06:20		70.41		53		29-Jun-08		18:07:53		70.41		44

		29-Jun-08		20:07:10		71		40		29-Jun-08		20:06:20		69.2		52		29-Jun-08		20:07:53		69.8		42

		29-Jun-08		22:07:10		70.41		39.5		29-Jun-08		22:06:20		69.2		50		29-Jun-08		22:07:53		69.8		41

		30-Jun-08		0:07:10		69.2		40		30-Jun-08		0:06:20		69.2		48.5		30-Jun-08		0:07:53		69.2		41

		30-Jun-08		2:07:10		69.2		40		30-Jun-08		2:06:20		69.2		48.5		30-Jun-08		2:07:53		69.8		41

		30-Jun-08		4:07:10		69.2		40		30-Jun-08		4:06:20		69.2		49		30-Jun-08		4:07:53		69.2		41

		30-Jun-08		6:07:10		69.2		40		30-Jun-08		6:06:20		69.2		49		30-Jun-08		6:07:53		69.2		41

		30-Jun-08		8:07:10		69.2		40		30-Jun-08		8:06:20		69.2		49		30-Jun-08		8:07:53		69.8		41

		30-Jun-08		10:07:10		69.2		40		30-Jun-08		10:06:20		69.8		47.5		30-Jun-08		10:07:53		69.8		41

		30-Jun-08		12:07:10		70.41		41.5		30-Jun-08		12:06:20		69.8		49.5		30-Jun-08		12:07:53		70.41		42

		30-Jun-08		14:07:10		70.41		43		30-Jun-08		14:06:20		70.41		48		30-Jun-08		14:07:53		70.41		43.5

		30-Jun-08		16:07:10		71		43		30-Jun-08		16:06:20		70.41		50.5		30-Jun-08		16:07:53		70.41		44.5

		30-Jun-08		18:07:10		71		41.5		30-Jun-08		18:06:20		69.8		50		30-Jun-08		18:07:53		70.41		43.5

		30-Jun-08		20:07:10		71		40		30-Jun-08		20:06:20		69.8		50		30-Jun-08		20:07:53		70.41		42

		30-Jun-08		22:07:10		69.8		39.5		30-Jun-08		22:06:20		69.8		48.5		30-Jun-08		22:07:53		69.8		40.5

		1-Jul-08		0:07:10		69.8		40		1-Jul-08		0:06:20		69.2		48.5		1-Jul-08		0:07:53		69.2		41

		1-Jul-08		2:07:10		69.2		40		1-Jul-08		2:06:20		69.2		48.5		1-Jul-08		2:07:53		69.2		41

		1-Jul-08		4:07:10		69.8		40.5		1-Jul-08		4:06:20		68.61		49		1-Jul-08		4:07:53		69.8		41

		1-Jul-08		6:07:10		69.8		40		1-Jul-08		6:06:20		68.61		49.5		1-Jul-08		6:07:53		69.8		41

		1-Jul-08		8:07:10		70.41		40.5		1-Jul-08		8:06:20		71		48.5		1-Jul-08		8:07:53		69.8		41

		1-Jul-08		10:07:10		70.41		40		1-Jul-08		10:06:20		71		47.5		1-Jul-08		10:07:53		69.8		41.5

		1-Jul-08		12:07:10		70.41		42		1-Jul-08		12:06:20		70.41		46		1-Jul-08		12:07:53		70.41		43.5

		1-Jul-08		14:07:10		71		44		1-Jul-08		14:06:20		70.41		48		1-Jul-08		14:07:53		69.8		45

		1-Jul-08		16:07:10		70.41		44.5		1-Jul-08		16:06:20		70.41		57.5		1-Jul-08		16:07:53		69.2		47

		1-Jul-08		18:07:10		71		43		1-Jul-08		18:06:20		70.41		53		1-Jul-08		18:07:53		69.2		45.5

		1-Jul-08		20:07:10		71		41		1-Jul-08		20:06:20		70.41		53.5		1-Jul-08		20:07:53		69.2		44

		1-Jul-08		22:07:10		71		40		1-Jul-08		22:06:20		69.8		52		1-Jul-08		22:07:53		69.8		42

		2-Jul-08		0:07:10		70.41		40		2-Jul-08		0:06:20		69.2		52		2-Jul-08		0:07:53		69.2		41.5

		2-Jul-08		2:07:10		69.8		40		2-Jul-08		2:06:20		69.2		52		2-Jul-08		2:07:53		69.2		42

		2-Jul-08		4:07:10		69.8		40		2-Jul-08		4:06:20		69.8		51.5		2-Jul-08		4:07:53		69.8		41.5

		2-Jul-08		6:07:10		69.8		40.5		2-Jul-08		6:06:20		69.2		53		2-Jul-08		6:07:53		69.2		42

		2-Jul-08		8:07:10		70.41		41		2-Jul-08		8:06:20		70.41		49		2-Jul-08		8:07:53		69.2		42.5

		2-Jul-08		10:07:10		70.41		40.5		2-Jul-08		10:06:20		69.8		46.5		2-Jul-08		10:07:53		69.8		42

		2-Jul-08		12:07:10		71		42.5		2-Jul-08		12:06:20		70.41		54		2-Jul-08		12:07:53		69.8		43.5

		2-Jul-08		14:07:10		70.41		44.5		2-Jul-08		14:06:20		70.41		50.5		2-Jul-08		14:07:53		69.2		46.5

		2-Jul-08		16:07:10		71		44.5		2-Jul-08		16:06:20		70.41		57.5		2-Jul-08		16:07:53		69.2		47

		2-Jul-08		18:07:10		71		43		2-Jul-08		18:06:20		69.8		49		2-Jul-08		18:07:53		69.8		45

		2-Jul-08		20:07:10		71		41		2-Jul-08		20:06:20		69.8		52		2-Jul-08		20:07:53		69.8		43

		2-Jul-08		22:07:10		70.41		40		2-Jul-08		22:06:20		69.8		49.5		2-Jul-08		22:07:53		69.8		41.5

		3-Jul-08		0:07:10		69.2		40		3-Jul-08		0:06:20		69.8		49		3-Jul-08		0:07:53		69.2		41.5

		3-Jul-08		2:07:10		70.41		40		3-Jul-08		2:06:20		69.2		48		3-Jul-08		2:07:53		69.8		41

		3-Jul-08		4:07:10		70.41		40		3-Jul-08		4:06:20		68.61		49		3-Jul-08		4:07:53		69.8		41

		3-Jul-08		6:07:10		69.8		40		3-Jul-08		6:06:20		68		49.5		3-Jul-08		6:07:53		69.8		41

		3-Jul-08		8:07:10		70.41		40.5		3-Jul-08		8:06:20		69.8		49		3-Jul-08		8:07:53		69.8		41.5

		3-Jul-08		10:07:10		70.41		41		3-Jul-08		10:06:20		70.41		45		3-Jul-08		10:07:53		69.8		41.5

		3-Jul-08		12:07:10		70.41		43		3-Jul-08		12:06:20		71		45.5		3-Jul-08		12:07:53		69.8		43.5

		3-Jul-08		14:07:10		70.41		44.5		3-Jul-08		14:06:20		71		47		3-Jul-08		14:07:53		69.2		46

		3-Jul-08		16:07:10		70.41		44		3-Jul-08		16:06:20		69.8		53		3-Jul-08		16:07:53		69.2		46

		3-Jul-08		18:07:10		70.41		43		3-Jul-08		18:06:20		70.41		49		3-Jul-08		18:07:53		69.8		44.5

		3-Jul-08		20:07:10		70.41		41.5		3-Jul-08		20:06:20		70.41		51.5		3-Jul-08		20:07:53		69.8		43.5

		3-Jul-08		22:07:10		71		40		3-Jul-08		22:06:20		69.2		51		3-Jul-08		22:07:53		69.8		42

		4-Jul-08		0:07:10		69.8		39.5		4-Jul-08		0:06:20		69.2		49.5		4-Jul-08		0:07:53		69.2		41.5

		4-Jul-08		2:07:10		69.2		40.5		4-Jul-08		2:06:20		69.2		47.5		4-Jul-08		2:07:53		69.2		41.5

		4-Jul-08		4:07:10		69.8		40		4-Jul-08		4:06:20		68.61		48		4-Jul-08		4:07:53		69.2		41.5

		4-Jul-08		6:07:10		69.8		39.5		4-Jul-08		6:06:20		69.8		44		4-Jul-08		6:07:53		69.2		41.5

		4-Jul-08		8:07:10		69.8		40		4-Jul-08		8:06:20		69.8		50.5		4-Jul-08		8:07:53		69.2		41.5

		4-Jul-08		10:07:10		71		42		4-Jul-08		10:06:20		69.8		50.5		4-Jul-08		10:07:53		69.2		43

		4-Jul-08		12:07:10		70.41		47		4-Jul-08		12:06:20		71.6		55		4-Jul-08		12:07:53		69.2		48

		4-Jul-08		14:07:10		71		47.5		4-Jul-08		14:06:20		71		55		4-Jul-08		14:07:53		69.2		50

		4-Jul-08		16:07:10		71		48		4-Jul-08		16:06:20		71.6		57		4-Jul-08		16:07:53		69.2		50

		4-Jul-08		18:07:10		71.6		46		4-Jul-08		18:06:20		71.6		54		4-Jul-08		18:07:53		69.2		49.5

		4-Jul-08		20:07:10		71.6		43.5		4-Jul-08		20:06:20		71.6		59		4-Jul-08		20:07:53		69.2		46.5

		4-Jul-08		22:07:10		71		41.5		4-Jul-08		22:06:20		69.8		56.5		4-Jul-08		22:07:53		69.2		45

		5-Jul-08		0:07:10		70.41		42		5-Jul-08		0:06:20		69.8		56.5		5-Jul-08		0:07:53		68.61		44.5

		5-Jul-08		2:07:10		69.8		41		5-Jul-08		2:06:20		69.8		54.5		5-Jul-08		2:07:53		69.2		43.5

		5-Jul-08		4:07:10		69.8		41		5-Jul-08		4:06:20		69.2		53		5-Jul-08		4:07:53		69.2		42.5

		5-Jul-08		6:07:10		69.2		41.5		5-Jul-08		6:06:20		68.61		54.5		5-Jul-08		6:07:53		68.61		43

		5-Jul-08		8:07:10		69.8		42		5-Jul-08		8:06:20		69.2		55		5-Jul-08		8:07:53		69.2		44

		5-Jul-08		10:07:10		71		43		5-Jul-08		10:06:20		69.8		51.5		5-Jul-08		10:07:53		69.2		45

		5-Jul-08		12:07:10		71		45		5-Jul-08		12:06:20		69.8		53.5		5-Jul-08		12:07:53		69.2		47.5

		5-Jul-08		14:07:10		71.6		45.5		5-Jul-08		14:06:20		70.41		55		5-Jul-08		14:07:53		69.2		48.5

		5-Jul-08		16:07:10		71.6		46		5-Jul-08		16:06:20		70.41		55.5		5-Jul-08		16:07:53		69.2		49.5

		5-Jul-08		18:07:10		71.6		45		5-Jul-08		18:06:20		70.41		59.5		5-Jul-08		18:07:53		68.61		48.5

		5-Jul-08		20:07:10		71		42.5		5-Jul-08		20:06:20		69.8		58		5-Jul-08		20:07:53		69.2		46

		5-Jul-08		22:07:10		71		41.5		5-Jul-08		22:06:20		69.2		57.5		5-Jul-08		22:07:53		69.2		45

		6-Jul-08		0:07:10		70.41		41		6-Jul-08		0:06:20		69.2		56		6-Jul-08		0:07:53		69.2		43.5

		6-Jul-08		2:07:10		69.8		40.5		6-Jul-08		2:06:20		68.61		54.5		6-Jul-08		2:07:53		68.61		43

		6-Jul-08		4:07:10		69.8		40.5		6-Jul-08		4:06:20		69.2		52.5		6-Jul-08		4:07:53		68.61		42.5

		6-Jul-08		6:07:10		69.2		41.5		6-Jul-08		6:06:20		69.2		51.5		6-Jul-08		6:07:53		68.61		42.5

		6-Jul-08		8:07:10		69.8		41.5		6-Jul-08		8:06:20		69.2		53		6-Jul-08		8:07:53		68.61		43.5

		6-Jul-08		10:07:10		71		43		6-Jul-08		10:06:20		69.8		55.5		6-Jul-08		10:07:53		69.2		45

		6-Jul-08		12:07:10		71		47		6-Jul-08		12:06:20		70.41		58.5		6-Jul-08		12:07:53		69.2		49

		6-Jul-08		14:07:10		71.6		49		6-Jul-08		14:06:20		70.41		57.5		6-Jul-08		14:07:53		69.2		52

		6-Jul-08		16:07:10		72.21		46		6-Jul-08		16:06:20		70.41		54		6-Jul-08		16:07:53		69.2		51

		6-Jul-08		18:07:10		72.21		47		6-Jul-08		18:06:20		69.8		61		6-Jul-08		18:07:53		69.2		51

		6-Jul-08		20:07:10		72.21		45		6-Jul-08		20:06:20		70.41		54.5		6-Jul-08		20:07:53		69.2		50

		6-Jul-08		22:07:10		72.21		43		6-Jul-08		22:06:20		69.8		62		6-Jul-08		22:07:53		68.61		48

		7-Jul-08		0:07:10		71.6		41.5		7-Jul-08		0:06:20		69.8		57		7-Jul-08		0:07:53		69.2		45

		7-Jul-08		2:07:10		71		41		7-Jul-08		2:06:20		69.8		52		7-Jul-08		2:07:53		69.2		44.5

		7-Jul-08		4:07:10		70.41		41		7-Jul-08		4:06:20		69.2		54		7-Jul-08		4:07:53		69.2		43.5

		7-Jul-08		6:07:10		69.8		40.5		7-Jul-08		6:06:20		69.2		52.5		7-Jul-08		6:07:53		68.61		43

		7-Jul-08		8:07:10		70.41		41.5		7-Jul-08		8:06:20		69.2		53.5		7-Jul-08		8:07:53		69.2		43.5

		7-Jul-08		10:07:10		71		44		7-Jul-08		10:06:20		69.2		58		7-Jul-08		10:07:53		69.2		46

		7-Jul-08		12:07:10		71.6		47.5		7-Jul-08		12:06:20		69.8		62		7-Jul-08		12:07:53		69.2		50

		7-Jul-08		14:07:10		71.6		50.5		7-Jul-08		14:06:20		70.41		59.5		7-Jul-08		14:07:53		69.2		54

		7-Jul-08		16:07:10		72.21		48.5		7-Jul-08		16:06:20		69.8		62		7-Jul-08		16:07:53		69.8		52.5

		7-Jul-08		18:07:10		72.21		46.5		7-Jul-08		18:06:20		70.41		59.5		7-Jul-08		18:07:53		69.2		52

		7-Jul-08		20:07:10		72.21		42.5		7-Jul-08		20:06:20		69.8		55		7-Jul-08		20:07:53		68.61		47.5

		7-Jul-08		22:07:10		72.21		40.5		7-Jul-08		22:06:20		69.8		50		7-Jul-08		22:07:53		69.2		44.5

		8-Jul-08		0:07:10		71		40		8-Jul-08		0:06:20		69.2		52		8-Jul-08		0:07:53		69.2		43.5

		8-Jul-08		2:07:10		70.41		40.5		8-Jul-08		2:06:20		69.2		51		8-Jul-08		2:07:53		69.2		42.5

		8-Jul-08		4:07:10		69.8		40.5		8-Jul-08		4:06:20		68.61		51.5		8-Jul-08		4:07:53		68.61		42.5

		8-Jul-08		6:07:10		69.2		40.5		8-Jul-08		6:06:20		69.2		51.5		8-Jul-08		6:07:53		68.61		42.5

		8-Jul-08		8:07:10		70.41		41.5		8-Jul-08		8:06:20		69.8		53.5		8-Jul-08		8:07:53		68.61		44

		8-Jul-08		10:07:10		71.6		44		8-Jul-08		10:06:20		69.8		50.5		8-Jul-08		10:07:53		68.61		47.5

		8-Jul-08		12:07:10		71		49		8-Jul-08		12:06:20		69.8		54		8-Jul-08		12:07:53		69.2		51

		8-Jul-08		14:07:10		71		49.5		8-Jul-08		14:06:20		70.41		55.5		8-Jul-08		14:07:53		69.2		53.5

		8-Jul-08		16:07:10		71		50		8-Jul-08		16:06:20		70.41		58.5		8-Jul-08		16:07:53		68.61		53.5

		8-Jul-08		18:07:10		71		49		8-Jul-08		18:06:20		70.41		55.5		8-Jul-08		18:07:53		68.61		52.5

		8-Jul-08		20:07:10		71		45		8-Jul-08		20:06:20		71		57.5		8-Jul-08		20:07:53		68		50

		8-Jul-08		22:07:10		71.6		43		8-Jul-08		22:06:20		70.41		53		8-Jul-08		22:07:53		68.61		47.5

		9-Jul-08		0:07:10		71.6		42		9-Jul-08		0:06:20		70.41		52		9-Jul-08		0:07:53		69.2		46

		9-Jul-08		2:07:10		71		41.5		9-Jul-08		2:06:20		69.8		50		9-Jul-08		2:07:53		69.2		44.5

		9-Jul-08		4:07:10		71		41.5		9-Jul-08		4:06:20		69.2		53.5		9-Jul-08		4:07:53		69.2		44

		9-Jul-08		6:07:10		70.41		41		9-Jul-08		6:06:20		69.2		52.5		9-Jul-08		6:07:53		69.2		43.5

		9-Jul-08		8:07:10		71		42.5		9-Jul-08		8:06:20		70.41		56.5		9-Jul-08		8:07:53		68.61		45

		9-Jul-08		10:07:10		71		45.5		9-Jul-08		10:06:20		71		53		9-Jul-08		10:07:53		69.2		48.5

		9-Jul-08		12:07:10		71		49		9-Jul-08		12:06:20		71.6		51		9-Jul-08		12:07:53		69.8		50.5

		9-Jul-08		14:07:10		70.41		47.5		9-Jul-08		14:06:20		71.6		51		9-Jul-08		14:07:53		68.61		51

		9-Jul-08		16:07:10		70.41		49		9-Jul-08		16:06:20		71.6		52.5		9-Jul-08		16:07:53		69.8		50

		9-Jul-08		18:07:10		70.41		48.5		9-Jul-08		18:06:20		70.41		53		9-Jul-08		18:07:53		69.8		50

		9-Jul-08		20:07:10		71		44		9-Jul-08		20:06:20		71		53		9-Jul-08		20:07:53		69.2		47.5

		9-Jul-08		22:07:10		71.6		43		9-Jul-08		22:06:20		70.41		54		9-Jul-08		22:07:53		69.8		46

		10-Jul-08		0:07:10		71.6		42		10-Jul-08		0:06:20		69.8		54.5		10-Jul-08		0:07:53		69.2		45

		10-Jul-08		2:07:10		71.6		41.5		10-Jul-08		2:06:20		69.8		54		10-Jul-08		2:07:53		69.8		44

		10-Jul-08		4:07:10		71		42		10-Jul-08		4:06:20		69.2		58		10-Jul-08		4:07:53		69.8		44

		10-Jul-08		6:07:10		71		41.5		10-Jul-08		6:06:20		69.8		55.5		10-Jul-08		6:07:53		69.8		43.5

		10-Jul-08		8:07:10		71		42.5		10-Jul-08		8:06:20		69.8		58.5		10-Jul-08		8:07:53		69.8		45

		10-Jul-08		10:07:10		71		44.5		10-Jul-08		10:06:20		69.8		58.5		10-Jul-08		10:07:53		68		48.5

		10-Jul-08		12:07:10		70.41		49		10-Jul-08		12:06:20		69.8		56.5		10-Jul-08		12:07:53		69.2		50.5

		10-Jul-08		14:07:10		70.41		52.5		10-Jul-08		14:06:20		71.6		54		10-Jul-08		14:07:53		69.2		54.5

		10-Jul-08		16:07:10		70.41		51		10-Jul-08		16:06:20		71.6		60		10-Jul-08		16:07:53		68.61		54

		10-Jul-08		18:07:10		70.41		49.5		10-Jul-08		18:06:20		70.41		63		10-Jul-08		18:07:53		69.8		51

		10-Jul-08		20:07:10		71		46		10-Jul-08		20:06:20		70.41		58.5		10-Jul-08		20:07:53		69.8		48.5

		10-Jul-08		22:07:10		71.6		43.5		10-Jul-08		22:06:20		70.41		57		10-Jul-08		22:07:53		69.8		47

		11-Jul-08		0:07:10		71.6		42.5		11-Jul-08		0:06:20		69.8		61		11-Jul-08		0:07:53		69.2		46.5

		11-Jul-08		2:07:10		71.6		42.5		11-Jul-08		2:06:20		69.8		53.5		11-Jul-08		2:07:53		69.8		45.5

		11-Jul-08		4:07:10		71		42		11-Jul-08		4:06:20		69.8		53.5		11-Jul-08		4:07:53		69.2		44.5

		11-Jul-08		6:07:10		71		41.5		11-Jul-08		6:06:20		69.8		57		11-Jul-08		6:07:53		69.2		44.5

		11-Jul-08		8:07:10		71		42.5		11-Jul-08		8:06:20		71.6		49		11-Jul-08		8:07:53		69.8		45

		11-Jul-08		10:07:10		71		45.5		11-Jul-08		10:06:20		72.21		56.5		11-Jul-08		10:07:53		68.61		48

		11-Jul-08		12:07:10		71		48.5		11-Jul-08		12:06:20		69.8		63		11-Jul-08		12:07:53		69.2		50.5

		11-Jul-08		14:07:10		71		49.5		11-Jul-08		14:06:20		70.41		55.5		11-Jul-08		14:07:53		69.2		52.5

		11-Jul-08		16:07:10		71		47		11-Jul-08		16:06:20		69.8		63.5		11-Jul-08		16:07:53		69.2		49.5

		11-Jul-08		18:07:10		71		45		11-Jul-08		18:06:20		70.41		54		11-Jul-08		18:07:53		69.2		47.5

		11-Jul-08		20:07:10		71		42.5		11-Jul-08		20:06:20		70.41		53		11-Jul-08		20:07:53		69.2		45.5

		11-Jul-08		22:07:10		71		40.5		11-Jul-08		22:06:20		70.41		52.5		11-Jul-08		22:07:53		69.8		43.5

		12-Jul-08		0:07:10		70.41		41		12-Jul-08		0:06:20		69.2		53		12-Jul-08		0:07:53		69.2		43

		12-Jul-08		2:07:10		70.41		41		12-Jul-08		2:06:20		69.2		52.5		12-Jul-08		2:07:53		69.8		42.5

		12-Jul-08		4:07:10		69.8		40.5		12-Jul-08		4:06:20		69.2		52.5		12-Jul-08		4:07:53		69.2		42.5

		12-Jul-08		6:07:10		69.8		40.5		12-Jul-08		6:06:20		69.2		52.5		12-Jul-08		6:07:53		69.2		42.5

		12-Jul-08		8:07:10		70.41		41.5		12-Jul-08		8:06:20		69.2		55		12-Jul-08		8:07:53		69.2		43

		12-Jul-08		10:07:10		71		42.5		12-Jul-08		10:06:20		69.2		57.5		12-Jul-08		10:07:53		69.2		44.5

		12-Jul-08		12:07:10		71		45.5		12-Jul-08		12:06:20		68.61		53.5		12-Jul-08		12:07:53		69.8		46.5

		12-Jul-08		14:07:10		70.41		45.5		12-Jul-08		14:06:20		69.2		52.5		12-Jul-08		14:07:53		69.8		47.5

		12-Jul-08		16:07:10		70.41		45.5		12-Jul-08		16:06:20		69.2		63.5		12-Jul-08		16:07:53		69.8		47.5

		12-Jul-08		18:07:10		70.41		44.5		12-Jul-08		18:06:20		69.8		54		12-Jul-08		18:07:53		70.41		46.5

		12-Jul-08		20:07:10		71		42.5		12-Jul-08		20:06:20		70.41		54		12-Jul-08		20:07:53		70.41		45

		12-Jul-08		22:07:10		71		42.5		12-Jul-08		22:06:20		69.8		59.5		12-Jul-08		22:07:53		70.41		44.5

		13-Jul-08		0:07:10		71		42.5		13-Jul-08		0:06:20		69.8		60		13-Jul-08		0:07:53		69.8		44

		13-Jul-08		2:07:10		71		42.5		13-Jul-08		2:06:20		69.2		60.5		13-Jul-08		2:07:53		70.41		44.5

		13-Jul-08		4:07:10		71		42.5		13-Jul-08		4:06:20		69.2		60		13-Jul-08		4:07:53		70.41		44.5

		13-Jul-08		6:07:10		71		42.5		13-Jul-08		6:06:20		69.2		61		13-Jul-08		6:07:53		70.41		44.5

		13-Jul-08		8:07:10		71		42.5		13-Jul-08		8:06:20		68.61		59		13-Jul-08		8:07:53		69.8		44

		13-Jul-08		10:07:10		71		43		13-Jul-08		10:06:20		69.2		59.5		13-Jul-08		10:07:53		70.41		44.5

		13-Jul-08		12:07:10		71		45		13-Jul-08		12:06:20		69.2		59		13-Jul-08		12:07:53		69.8		46

		13-Jul-08		14:07:10		71		45		13-Jul-08		14:06:20		70.41		54		13-Jul-08		14:07:53		69.8		47

		13-Jul-08		16:07:10		71.6		44.5		13-Jul-08		16:06:20		69.8		55.5		13-Jul-08		16:07:53		69.8		47

		13-Jul-08		18:07:10		71.6		44		13-Jul-08		18:06:20		69.2		58.5		13-Jul-08		18:07:53		69.2		47

		13-Jul-08		20:07:10		71.6		43		13-Jul-08		20:06:20		69.2		57.5		13-Jul-08		20:07:53		69.8		46.5

		13-Jul-08		22:07:10		71		42.5		13-Jul-08		22:06:20		69.2		60.5		13-Jul-08		22:07:53		70.41		45.5

		14-Jul-08		0:07:10		71		42.5		14-Jul-08		0:06:20		69.2		58		14-Jul-08		0:07:53		70.41		44.5

		14-Jul-08		2:07:10		70.41		42		14-Jul-08		2:06:20		69.2		52		14-Jul-08		2:07:53		70.41		43.5

		14-Jul-08		4:07:10		70.41		42		14-Jul-08		4:06:20		69.2		57.5		14-Jul-08		4:07:53		69.8		43

		14-Jul-08		6:07:10		69.8		41		14-Jul-08		6:06:20		69.2		55.5		14-Jul-08		6:07:53		69.8		42.5

		14-Jul-08		8:07:10		69.8		42		14-Jul-08		8:06:20		69.2		56.5		14-Jul-08		8:07:53		69.8		43

		14-Jul-08		10:07:10		70.41		44		14-Jul-08		10:06:20		69.2		53.5		14-Jul-08		10:07:53		70.41		44.5

		14-Jul-08		12:07:10		70.41		47		14-Jul-08		12:06:20		69.8		62		14-Jul-08		12:07:53		70.41		47

		14-Jul-08		14:07:10		71		47		14-Jul-08		14:06:20		69.8		59.5		14-Jul-08		14:07:53		70.41		48

		14-Jul-08		16:07:10		71		47		14-Jul-08		16:06:20		69.8		60.5		14-Jul-08		16:07:53		70.41		48.5

		14-Jul-08		18:07:10		71		45		14-Jul-08		18:06:20		70.41		57		14-Jul-08		18:07:53		70.41		47

		14-Jul-08		20:07:10		71		43.5		14-Jul-08		20:06:20		69.8		59.5		14-Jul-08		20:07:53		70.41		46

		14-Jul-08		22:07:10		71		42.5		14-Jul-08		22:06:20		69.2		59.5		14-Jul-08		22:07:53		70.41		44.5

		15-Jul-08		0:07:10		70.41		42		15-Jul-08		0:06:20		69.2		57		15-Jul-08		0:07:53		70.41		43.5

		15-Jul-08		2:07:10		70.41		42		15-Jul-08		2:06:20		68.61		56		15-Jul-08		2:07:53		70.41		43.5

		15-Jul-08		4:07:10		69.8		41.5		15-Jul-08		4:06:20		68.61		59		15-Jul-08		4:07:53		69.8		43

		15-Jul-08		6:07:10		69.8		42		15-Jul-08		6:06:20		69.2		56.5		15-Jul-08		6:07:53		69.8		43

		15-Jul-08		8:07:10		70.41		42		15-Jul-08		8:06:20		68		53.5		15-Jul-08		8:07:53		69.8		43.5

		15-Jul-08		10:07:10		71		42		15-Jul-08		10:06:20		69.2		54.5		15-Jul-08		10:07:53		69.8		44

		15-Jul-08		12:07:10		71		44.5		15-Jul-08		12:06:20		69.2		60		15-Jul-08		12:07:53		69.8		45

		15-Jul-08		14:07:10		71		46.5		15-Jul-08		14:06:20		69.2		62		15-Jul-08		14:07:53		69.2		48.5

		15-Jul-08		16:07:10		70.41		45.5		15-Jul-08		16:06:20		69.2		57.5		15-Jul-08		16:07:53		69.8		47.5

		15-Jul-08		18:07:10		70.41		44.5		15-Jul-08		18:06:20		69.8		54.5		15-Jul-08		18:07:53		69.8		46

		15-Jul-08		20:07:10		71		42.5		15-Jul-08		20:06:20		70.41		53.5		15-Jul-08		20:07:53		69.8		44.5

		15-Jul-08		22:07:10		71		41.5		15-Jul-08		22:06:20		69.2		54.5		15-Jul-08		22:07:53		69.8		43.5

		16-Jul-08		0:07:10		70.41		41.5		16-Jul-08		0:06:20		69.2		57		16-Jul-08		0:07:53		69.2		43

		16-Jul-08		2:07:10		69.8		41.5		16-Jul-08		2:06:20		69.8		55.5		16-Jul-08		2:07:53		69.2		43.5

		16-Jul-08		4:07:10		69.8		41.5		16-Jul-08		4:06:20		68.61		56.5		16-Jul-08		4:07:53		69.2		43

		16-Jul-08		6:07:10		69.8		41		16-Jul-08		6:06:20		69.2		56		16-Jul-08		6:07:53		69.2		43

		16-Jul-08		8:07:10		70.41		41.5		16-Jul-08		8:06:20		68.61		58.5		16-Jul-08		8:07:53		69.2		43

		16-Jul-08		10:07:10		70.41		42		16-Jul-08		10:06:20		69.8		55		16-Jul-08		10:07:53		68.61		44.5

		16-Jul-08		12:07:10		71		42.5		16-Jul-08		12:06:20		69.8		51		16-Jul-08		12:07:53		69.2		44.5

		16-Jul-08		14:07:10		71		44.5		16-Jul-08		14:06:20		69.8		51		16-Jul-08		14:07:53		68.61		47.5

		16-Jul-08		16:07:10		71		45		16-Jul-08		16:06:20		70.41		57		16-Jul-08		16:07:53		68.61		48

		automated instrument that measured temp-humidity is no longer in use.  Temp and humidity data and charts are generated in "CER Pressure" tab. JH 1-29-09





		



CER 1 Temperature(°F)

CER 2 Temperature(°F)

CER 3 Temperature(°F)

Date

Temperature (Deg. F)

Figure 9.  CER Temperature



		



CER 1 Humidity(%)

CER 3 Humidity(%)

QA Humidity(%)

CER 2 Humidity(%)

Date

Humidity (%)

Figure 10.  CER Relative Humidity



		






_1294660137.xls
Airstrip Count

		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148

		39206		39206		39206		39148		39148

		39230		39230		39230		39167		39167

		39267		39267		39267		39206		39206

		39297		39297		39297		39230		39230

		39349		39349		39349		39267		39267

		39392		39392		39392		39297		39297

		39427		39427		39427		39349		39349

		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713



CER 1

CER 2

CER3

Alert Level

Action Level

Date

Average CER Count

Figure 1.  Average Airstrip Count

3.625

6

29

10

15

5.375

7.5

28

10

15

13.125

13.25

28.75

10

15

13.25

11

27.75

10

15

4.25

5.25

24.5

10

15

4

1.75

11.75

10

15

4.25

9.25

10

15

19.5

5.5

22.5

10

15

5.75

4.25

13

10

15

3.25

1

4.75

10

15

11.625

8

18.25

10

15

3.875

1.75

10.5

10

15

4.125

2

10

35

45

1.125

0.5

3.5

35

45

3

1.25

6.5

35

45

3.25

0.75

5.25

35

45

2

0.75

2.75

35

45

6.375

1.75

8.25

35

45

13.5

1.25

10.25

35

45

2.6666666667

2.6666666667

11.25

35

45

6.2

4

3.75

35

45

6.2666666667

2

3.75

35

45

7.6666666667

3

7.5

35

45

9.4

2.8888888889

9

35

45

8.4

3.4444444444

6.5

35

45

6.5333333333

2.3333333333

8.5

35

45



Contact Plate Count

		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148

		39206		39206		39206		39148		39148

		39230		39230		39230		39167		39167

		39267		39267		39267		39206		39206

		39297		39297		39297		39230		39230

		39349		39349		39349		39267		39267

		39392		39392		39392		39297		39297

		39427		39427		39427		39392		39392

		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

Alert Level

Action Level

Date

Contact Plate Count

Figure 2. Average Contact Plate Count

1.4285714286

0.25

2.5

10

15

3.7142857143

2.75

4

10

15

1.1428571429

1.75

0.8333333333

10

15

2.4285714286

3

2.5

10

15

2.4285714286

0.75

3.1666666667

10

15

5.5714285714

3.25

5

10

15

5.2857142857

5.2

10

15

2.7142857143

1.5

2

10

15

1.1428571429

0

2

10

15

3.1428571429

1

3.25

10

15

3.4285714286

3.25

2.25

10

15

1.5714285714

0.75

1.5

10

15

1.7142857143

1

2.25

6

7

0.5714285714

0.5

2.25

6

7

1.5714285714

0.5

3

6

7

2

0.75

2.5

6

7

0.7142857143

0.25

1.75

6

7

3.4285714286

1.25

3.25

6

7

4

1

3.75

6

7

1.5333333333

1

3

6

7

2

1

2.25

6

7

1.7333333333

0.6666666667

1.5

6

7

0.9333333333

0.4444444444

1.5

6

7

0.9333333333

0.7777777778

2.5

6

7

1.1333333333

0.6666666667

1.75

6

7

0.9333333333

0.6666666667

1.5

6

7



0.5micron Count

		38776		38776		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126		39126		39126

		39148		39167		39167		39148		39148		39148		39148

		39148		39206		39206		39148		39148		39148		39148

		39167		39230		39230		39167		39167		39167		39167

		39206		39267		39267		39206		39206		39206		39206

		39230		39297		39297		39230		39230		39297		39297

		39267		39349		39349		39267		39267		39349		39349

		39297		39392		39392		39297		39297		39392		39392

		39392		39427		39427		39392		39392		39427		39427

		39545		39545		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

CER 1,3 Alert Level

CER 1,3 Action Level

CER 2 Alert Level

CER 2 Action Level

Date

0.5um/cu ft Count

Figure 3.  Average 0.5mm/cu ft Count

194

383

3263.8

5000

10000

5000

10000

339.5

338.3333333333

1210.4

5000

10000

5000

10000

362.75

719.3333333333

2800.4

5000

10000

5000

10000

688.125

416.3333333333

1999.6

5000

10000

5000

10000

618.75

336.6666666667

2033

5000

10000

5000

10000

692.625

1000

1857.4

5000

10000

5000

10000

401.375

1423.2

5000

10000

5000

10000

523.125

842

2313.2

5000

10000

5000

10000

273

292.3333333333

624.4

5000

10000

5000

10000

588.875

620

1580.4

5000

10000

5000

10000

714

474.6666666667

1255.6

5000

10000

5000

10000

755.625

587.3333333333

1139.8

5000

10000

5000

10000

772.875

643

1484

3800

4500

1250

1500

244

896.6666666667

1571.2

3800

4500

1250

1500

551.75

704.3333333333

2714

3800

4500

1250

1500

678.625

553

1781.8

3800

4500

1250

1500

369.625

300

731.6

3800

4500

1250

1500

664

478

1178.6

3800

4500

1250

1500

835.625

525

1260.6

3800

4500

1250

1500

699

83.7777777778

1354.8

3800

4500

1250

1500

635

204.4444444444

620.8

3800

4500

1250

1500

606

181.3333333333

750.8

3800

4500

1250

1500

606

109.5555555556

474.6

3800

4500

1250

1500

612.0666666667

156.7777777778

659.8

3800

4500

1250

1500

285.1333333333

190.5555555556

945.2

3800

4500

1250

1500

474

216.3333333333

768.6

3800

4500

1250

1500



5.0micron Count

		38776		38776		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148		39148		39148

		39206		39206		39206		39148		39148		39148		39148

		39230		39230		39230		39167		39167		39167		39167

		39267		39267		39267		39206		39206		39267		39267

		39297		39297		39297		39230		39230		39297		39297

		39349		39349		39349		39267		39267		39349		39349

		39392		39392		39392		39297		39297		39392		39392

		39427		39427		39427		39392		39392		39427		39427

		39545		39545		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

CER 1,3 Alert Level

CER 1,3 Action Level

CER 2 Alert Level

CER 2 Action Level

Date

5.0um/cu ft Count

Figure 4.  Average 5.0mm/cu ft Count

14.125

48.6666666667

226.8

30

50

30

50

33.625

49.3333333333

104.4

30

50

30

50

36.25

49

211.4

30

50

30

50

126.75

76.6666666667

305.2

30

50

30

50

67.875

37.3333333333

344.6

30

50

30

50

71.75

72.3333333333

166.4

30

50

30

50

43.5

235

30

50

30

50

65.125

37.3333333333

219.4

30

50

30

50

33.125

31.3333333333

50.6

30

50

30

50

47.75

50.6666666667

99.4

30

50

30

50

43.875

32.3333333333

79.2

30

50

30

50

47.125

44.3333333333

92.8

30

50

30

50

49

43.3333333333

92.2

410

500

90

105

30.75

75.6666666667

129.2

410

500

90

105

78.875

89

258.4

410

500

90

105

60

44

147

410

500

90

105

28.375

22.6666666667

53

410

500

90

105

26.125

20.3333333333

58

410

500

90

105

45.125

24.3333333333

80.8

410

500

90

105

37.3333333333

10

69.2

410

500

90

105

34.6

12.5555555556

33.2

410

500

90

105

29

9.3333333333

34

410

500

90

105

29

7.1111111111

33

410

500

90

105

30.0666666667

8.8888888889

27.6

410

500

78

83

18.7333333333

11.5555555556

43.4

410

500

78

83

24.3333333333

9.8888888889

37.6

410

500

78

83



CER 1

				AIRSTRIPS:																																																																																																		CONTACT PLATES:																																																																																																		PARTICLE COUNTS

				A						B						C						D						E						F						G						H						I						J						K						L						M						N						O						Average								A						B						C						D						E						F						G						H						I						J						K						L						M						N						O						Average								A				B				C				D				E				F				G				H				I				J				K				L				M				N				O				Average

		Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 1		Date		Alert Level		Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 1		Date		Alert Level		Action Level		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		CER 1 0.5um/ cu ft		Date		CER 1,3 Alert Level		CER 1,3 Action Level		CER 1 5.0um/cu ft		Date		CER 1,3 Alert Level		CER 1,3 Action Level

		2/28/06		2		0		2		4		0		4		5		0		5		4		0		4		8		0		8		0		0		0		3		0		3		3		0		3																																												4		2/28/06		10		15		0		0		0		0		0		0		1		0		1		0		0		0		2		0		2		0		0		0		3		0		3		4		0		4						0						0						0						0						0						0						0		1		2/28/06		10		15		207		8		291		16		133		12		278		21		134		13		25		5		262		22		222		16																														194		02/28/06		5000		10000		14		2/28/06		30		50

		3/30/06		4		0		4		4		0		4		7		0		7		6		0		6		10		0		10		2		0		2		6		0		6		4		0		4																																												5		3/30/06		10		15		1		0		1		3		0		3		6		0		6		3		0		3		2		0		2		5		0		5		3		0		3		3		0		3						0						0						0						0						0						0						0		4		3/30/06		10		15		310		48		483		69		134		18		263		24		444		31		679		40		199		8		204		31																														340		03/30/06		5000		10000		34		3/30/06		30		50

		4/28/06		4		0		4		12		0		12		12		0		12		15		0		15		17		0		17		6		4		10		12		0		12		23		0		23																																												13		4/28/06		10		15		0		0		0		2		0		2		2		0		2		0		0		0		0		0		0		0		0		0		4		0		4		0		0		0						0						0						0						0						0						0						0		1		4/28/06		10		15		487		81		221		21		261		19		390		32		480		60		287		23		321		19		455		35																														363		04/28/06		5000		10000		36		4/28/06		30		50

		5/30/06		6		0		6		10		0		10		12		0		12		17		0		17		19		0		19		9		0		9		12		0		12		21		0		21																																												13		5/30/06		10		15		1		0		1		4		0		4		3		0		3		0		0		0		1		0		1		0		0		0		7		0		7		1		0		1						0						0						0						0						0						0						0		2		5/30/06		10		15		678		124		1084		137		214		36		113		21		1478		449		220		32		1009		120		709		95																														688		05/30/06		5000		10000		127		5/30/06		30		50

		7/7/06		4		0		4		2		0		2		6		0		6		4		0		4		8		0		8		1		0		1		4		0		4		5		0		5																																												4		7/7/06		10		15		1		0		1		2		0		2		1		0		1		2		0		2		2		0		2		1		0		1		4		0		4		4		0		4						0						0						0						0						0						0						0		2		7/7/06		10		15		631		86		779		72		1234		81		282		38		464		75		694		93		564		65		302		33																														619		07/07/06		5000		10000		68		7/7/06		30		50

		9/5/06		4		0		4		4		0		4		6		0		6		5		0		5		2		0		2		2		0		2		4		0		4		5		0		5																																												4		9/5/06		10		15		4		0		4		6		0		6		4		0		4		3		0		3		6		0		6		5		0		5		5		0		5		6		0		6						0						0						0						0						0						0						0		6		9/5/06		10		15		1056		113		622		73		227		35		828		84		603		57		875		95		545		56		785		61																														693		09/05/06		5000		10000		72		9/5/06		30		50

		10/5/06		5		0		5		4		0		4		4		0		4		5		0		5		6		0		6		4		0		4		3		0		3		3		0		3																																												4		10/5/06		10		15		5		0		5		6		0		6		4		0		4		4		0		4		5		0		5		3		0		3		6		0		6		4		0		4						0						0						0						0						0						0						0		5		10/5/06		10		15		122		14		263		18		352		48		540		69		361		38		421		63		389		41		763		57																														401		10/05/06		5000		10000		44		10/5/06		30		50

		11/14/06		11		0		11		27		0		27		10		0		10		24		0		24		26		0		26		32		0		32		12		0		12		14		0		14																																												20		11/14/06		10		15		1		0		1		1		0		1		0		0		0		0		0		0		5		0		5		1		0		1		2		0		2		9		0		9						0						0						0						0						0						0						0		3		11/14/06		10		15		596		71		455		67		641		77		585		62		991		81		357		52		62		60		498		51																														523		11/14/06		5000		10000		65		11/14/06		30		50

		12/20/06		2		0		2		1		0		1		5		0		5		1		0		1		13		0		13		7		0		7		13		0		13		4		0		4																																												6		12/20/06		10		15		1		0		1		2		0		2		0		0		0		1		0		1		3		0		3		1		0		1		0		0		0		0		0		0						0						0						0						0						0						0						0		1		12/20/06		10		15		367		35		390		46		168		18		321		30		343		32		191		14		90		25		314		65																														273		12/20/06		5000		10000		33		12/20/06		30		50

		1/16/07		3		0		3		2		0		2		4		0		4		6		0		6		2		0		2		2		0		2		3		0		3		4		0		4																																												3		1/16/07		10		15		2		0		2		2		0		2		1		0		1		3		0		3		4		0		4		2		0		2		4		0		4		4		0		4						0						0						0						0						0						0						0		3		1/16/07		10		15		361		21		449		56		304		35		265		31		761		42		804		62		901		64		866		71																														589		01/16/07		5000		10000		48		1/16/07		30		50

		2/13/07		11		0		11		5		0		5		10		0		10		6		0		6		24		0		24		6		0		6		10		0		10		21		0		21																																												12		2/13/07		10		15		1		0		1		8		0		8		3		0		3		2		0		2		0		0		0		4		0		4		2		0		2		4		0		4						0						0						0						0						0						0						0		3		2/13/07		10		15		611		41		862		50		841		42		942		61		744		40		622		33		402		24		688		60																														714		02/13/07		5000		10000		44		2/13/07		30		50

		3/26/07		3		0		3		4		0		4		4		0		4		6		0		6		2		0		2		4		0		4		6		0		6		2		0		2																																												4		3/7/07		10		15		1		0		1		1		0		1		2		0		2		0		0		0		1		0		1		2		0		2		2		0		2		2		0		2						0						0						0						0						0						0						0		2		3/7/07		10		15		721		51		640		42		871		48		901		52		844		48		408		36		799		49		861		51																														756		03/07/07		5000		10000		47		3/7/07		30		50

		5/4/07		4		0		4		4		0		4		3		0		3		4		0		4		6		0		6		2		0		2		6		0		6		4		0		4																																												4		3/7/07		35		45		2		0		2		1		0		1		2		0		2		1		0		1		0		0		0		1		0		1		2		0		2		3		0		3						0						0						0						0						0						0						0		2		3/7/07		6		7		641		41		722		52		699		47		944		61		872		45		698		41		662		37		945		68																														773		03/07/07		3800		4500		49		3/7/07		410		500

		5/28/07		1		0		1		1		0		1		2		0		2		0		0		0		2		0		2		1		0		1		1		0		1		1		0		1																																												1		3/26/07		35		45		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1						0						0						0						0						0						0						0		1		3/26/07		6		7		161		17		200		21		251		36		275		28		320		53		101		15		460		55		184		21																														244		03/26/07		3800		4500		31		3/26/07		410		500

		7/4/07		2		0		2		3		0		3		3		0		3		3		0		3		2		0		2		4		0		4		4		0		4		3		0		3																																												3		5/4/07		35		45		2		0		2		2		0		2		1		0		1		0		0		0		1		0		1		1		0		1		2		0		2		2		0		2						0						0						0						0						0						0						0		2		5/4/07		6		7		346		64		339		37		537		77		301		55		492		86		292		31		896		120		1211		161																														552		05/04/07		3800		4500		79		5/4/07		410		500

		8/3/07		4		0		4		2		0		2		3		0		3		2		0		2		2		0		2		4		0		4		4		0		4		5		0		5																																												3		5/28/07		35		45		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		3		0		3		3		0		3		2		0		2						0						0						0						0						0						0						0		2		5/28/07		6		7		221		20		107		19		647		49		587		37		744		87		907		78		1241		101		975		89																														679		05/28/07		3800		4500		60		5/28/07		410		500

		9/24/07		2		0		2		1		0		1		1		0		1		2		0		2		3		0		3		3		0		3		2		0		2		2		0		2																																												2		7/4/07		35		45		0		0		0		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		2		0		2		2		0		2						0						0						0						0						0						0						0		1		7/4/07		6		7		310		27		488		31		210		20		401		29		121		18		404		31		601		41		422		30																														370		07/04/07		3800		4500		28		7/4/07		410		500

		11/6/07		6		0		6		4		0		4		4		0		4		4		0		4		8		0		8		7		0		7		8		0		8		10		0		10																																												6		8/3/07		35		45		2		0		2		2		0		2		3		0		3		1		0		1		3		0		3		5		0		5		4		0		4		4		0		4						0						0						0						0						0						0						0		3		8/3/07		6		7		523		33		678		25		498		14		671		22		687		23		721		33		856		34		678		25																														664		08/03/07		3800		4500		26		8/3/07		410		500

		12/11/07		10		0		10		9		0		9		11		0		11		12		0		12		12		0		12		15		0		15		21		0		21		18		0		18																																												14		9/24/07		35		45		2		0		2		1		0		1		3		0		3		4		0		4		4		0		4		4		0		4		3		0		3		7		0		7						0						0						0						0						0						0						0		4		11/6/07		6		7		678		36		761		31		734		34		891		44		851		33		781		33		1011		81		978		69																														836		11/06/07		3800		4500		45		11/6/07		410		500

		4/7/08		6		0		6		5		0		5		7		0		7		6		0		6		0		0		0		0		0		0		2		0		2		4		0		4		4		0		4		3		0		3		2		0		2		0		0		0		0		0		0		0		0		0		1		0		1		3		4/7/08		35		45		2		0		2		1		0		1		3		0		3		3		0		3		2		0		2		1		0		1		1		0		1		0		0		0		2		0		2		0		0		0		2		0		2		1		0		1		1		0		1		2		0		2		2		0		2		2		4/7/08		6		7		989		45		1045		58		1349		61		1305		60		689		46		430		30		1027		60		899		42		621		24		318		19		501		24		313		33		295		13		303		21		401		24		699		04/07/08		3800		4500		37		4/7/08		410		500

		5/7/08		9		0		9		8		0		8		7		0		7		8		0		8		3		0		3		3		0		3		3		0		3		7		0		7		7		0		7		4		0		4		8		0		8		4		0		4		8		0		8		9		0		9		5		0		5		6		5/7/08		35		45		3		0		3		2		0		2		2		0		2		2		0		2		3		0		3		3		0		3		2		0		2		1		0		1		1		0		1		1		0		1		2		0		2		2		0		2		2		0		2		2		0		2		2		0		2		2		5/7/08		6		7		782		44		671		39		724		41		454		22		576		33		430		30		671		32		572		28		781		37		671		32		677		33		476		41		672		31		781		43		587		33		635		05/07/08		3800		4500		35		5/7/08		410		500

		6/3/08		8		0		8		8		0		8		4		0		4		5		0		5		6		0		6		6		0		6		5		0		5		5		0		5		5		0		5		4		0		4		7		0		7		8		0		8		8		0		8		9		0		9		6		0		6		6		6/3/08		35		45		3		0		3		1		0		1		1		0		1		2		0		2		1		0		1		3		0		3		1		0		1		2		0		2		2		0		2		0		0		0		2		0		2		1		0		1		2		0		2		2		0		2		3		0		3		2		6/3/08		6		7		621		33		393		22		891		31		671		25		1192		44		671		19		781		22		245		19		1325		44		601		41		418		31		351		29		301		21		290		23		339		31		606		06/03/08		3800		4500		29		6/3/08		410		500

		7/1/08		9		0		9		9		0		9		7		0		7		9		0		9		8		0		8		5		0		5		8		0		8		8		0		8		8		0		8		6		0		6		11		0		11		6		0		6		9		0		9		9		0		9		3		0		3		8		7/1/08		35		45		1		0		1		2		0		2		0		0		0		1		0		1		1		0		1		1		0		1		0		0		0		0		0		0		2		0		2		1		0		1		1		0		1		2		0		2		0		0		0		1		0		1		1		0		1		1		7/1/08		6		7		621		33		393		22		891		31		671		25		1192		44		671		19		781		22		245		19		1325		44		601		41		418		31		351		29		301		21		290		23		339		31		606		07/01/08		3800		4500		29		7/1/08		410		500

		7/21/08		11		0		11		11		0		11		5		0		5		5		0		5		12		0		12		11		0		11		12		0		12		6		0		6		6		0		6		9		0		9		14		0		14		15		0		15		11		0		11		6		0		6		7		0		7		9		7/21/08		35		45		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		7/21/08		6		7		232		23		452		26		337		27		671		33		476		27		501		28		488		28		782		37		561		27		442		28		891		38		590		29		876		31		991		42		891		27		612		07/21/08		3800		4500		30		7/21/08		410		500

		9/4/08		10		0		10		9		0		9		6		0		6		7		0		7		7		0		7		9		0		9		6		0		6		9		0		9		11		0		11		12		0		12		10		0		10		9		0		9		6		0		6		6		0		6		9		0		9		8		9/4/08		35		45		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		9/4/08		6		7		219		19		140		14		275		16		101		9		244		16		301		21		189		19		181		17		176		17		215		21		414		24		409		21		357		21		454		19		602		27		285		09/04/08		3800		4500		19		9/4/08		410		500

		9/22/08		5		0		5		5		0		5		9		0		9		5		0		5		5		0		5		9		0		9		11		0		11		4		0		4		11		0		11		5		0		5		5		0		5		6		0		6		6		0		6		8		0		8		4		0		4		7		9/22/08		35		45		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		0		0		0		2		0		2		1		0		1		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		9/22/08		6		7		332		21		254		19		354		21		548		31		369		22		584		26		651		22		448		26		296		19		489		29		336		21		754		32		565		26		665		29		465		21		474		09/22/08		3800		4500		24		9/22/08		410		500

		11/6/08		3		0		3		3		0		3		5		0		5		4		0		4		4		0		4		3		0		3		4		0		4		4		0		4		4		0		4		5		0		5		5		0		5		3		0		3		3		0		3		3		0		3		4		0		4		4		11/6/08		35		45		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		1		0		1		0		11/6/08		6		7		721		31		867		39		253		12		458		22		357		20		445		28		432		22		685		31		591		28		241		9		219		8		473		19		501		21		765		33		801		36		521		11/06/08		3800		4500		24		11/6/08		410		500

		12/1/08		2		0		2		0		0		0		0		0		0		2		0		2		2		0		2		3		0		3		0		0		0		1		0		1		4		0		4		3		0		3		2		0		2		1		0		1		0		0		0		2		0		2		3		0		3		2		12/1/08		35		45		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		1		12/1/08		6		7		110		9		89		9		122		13		25		6		59		8		131		18		40		7		274		19		157		12		88		6		150		9		114		8		517		32		180		15		234		21		153		12/01/08		3800		4500		13		12/1/08		410		500

		12/16/08		3		0		3		2		0		2		3		0		3		2		0		2		2		0		2		3		0		3		4		0		4		3		0		3		5		0		5		4		0		4		4		0		4		3		0		3		3		0		3		3		0		3		3		0		3		3		12/16/08		35		45		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		1		0		1		1		12/16/08		6		7		291		18		178		11		271		19		189		14		177		14		276		18		198		11		187		14		278		17		91		7		87		6		287		16		376		21		301		17		227		19		228		12/16/08		3800		4500		15		12/16/08		410		500



&L&"Arial Narrow,Bold"&14CER 1&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER 2

										AIRSTRIPS:																																																												CONTACT PLATES:																																																						PARTICLE COUNTS

				A						B						C						D						E						F						G						H						I						Average						A						B						C						D						E						F						G						H						I						Average						A				B				C				D				E				F				G				H				I				Average

		Sample Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 2		Alert Level		Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 2		Total Alert Level		Total Action Level		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		CER 2 0.5um/cu ft		Date		CER 2 Alert Level		CER 2 Action Level		CER 2 5.0um/cu ft		Date		CER 2 Alert Level		CER 2 Action Level

		2/28/06								6		0		6		0		0		0		9		0		9		9		0		9																										6		10		15								0		0		0		0		0		0		1		0		1		0		0		0																										0		10		15		297		39		288		43		0		0		564		64																						383		2/28/06		5000		10000		49		02/28/06		30		50

		3/30/06								9		0		9		1		0		1		8		0		8		12		0		12																										8		10		15								2		0		2		0		0		0		6		0		6		3		0		3																										3		10		15		460		68		264		39		0		0		291		41																						338		3/30/06		5000		10000		49		03/30/06		30		50

		4/28/06								29		0		29		0		0		0		22		0		22		2		0		2																										13		10		15								2		0		2		2		0		2		0		0		0		3		0		3																										2		10		15		1084		67		543		41		0		0		531		39																						719		4/28/06		5000		10000		49		04/28/06		30		50

		5/30/06								21		0		21		0		0		0		19		0		19		4		0		4																										11		10		15								4		0		4		2		0		2		1		0		1		5		0		5																										3		10		15		435		87		354		66		0		0		460		77																						416		5/30/06		5000		10000		77		05/30/06		30		50

		7/7/06								5		0		5		0		0		0		8		0		8		8		0		8																										5		10		15								0		0		0		0		0		0		2		0		2		1		0		1																										1		10		15		232		33		299		39		0		0		479		40																						337		7/7/06		5000		10000		37		07/07/06		30		50

		9/5/06								3		0		3		0		0		0		2		0		2		2		0		2																										2		10		15								4		0		4		0		0		0		4		0		4		5		0		5																										3		10		15		1289		79		289		30		0		0		1422		108																						1000		9/5/06		5000		10000		72		09/05/06		30		50

		10/5/06																																																																																																																																																																10/5/06		5000		10000				10/05/06		30		50

		11/14/06								16		0		16		0		0		0		4		0		4		2		0		2																										6		10		15								1		0		1		0		0		0		4		0		4		1		0		1																										2		10		15		961		41		877		40		0		0		688		31																						842		11/14/06		5000		10000		37		11/14/06		30		50

		12/20/06								5		0		5		4		0		4		6		0		6		2		0		2																										4		10		15								0		0		0		0		0		0		0		0		0		0		0		0																										0		10		15		463		36		141		17		0		0		273		41																						292		12/20/06		5000		10000		31		12/20/06		30		50

		1/16/07								2		0		2		0		0		0		1		0		1		1		0		1																										1		10		15								1		0		1		0		0		0		1		0		1		2		0		2																										1		10		15		781		62		451		32		0		0		628		58																						620		1/16/07		5000		10000		51		01/16/07		30		50

		2/13/07								12		0		12		0		0		0		10		0		10		10		0		10																										8		10		15								4		0		4		0		0		0		4		0		4		4		1		5																										3		10		15		640		31		285		44		0		0		499		22																						475		2/13/07		5000		10000		32		02/13/07		30		50

		3/26/07								2		0		2		0		0		0		2		0		2		3		0		3																										2		35		45								1		0		1		0		0		0		1		0		1		1		0		1																										1		6		7		490		40		684		51		0		0		588		42																						587		3/7/07		5000		10000		44		03/07/07		30		50

		5/4/07								2		0		2		0		0		0		3		0		3		3		0		3																										2		35		45								1		0		1		0		0		0		1		0		1		2		0		2																										1		6		7		640		41		585		37		0		0		704		52																						643		3/7/07		1250		1500		43		03/07/07		90		105

		5/28/07								0		0		0		0		0		0		1		0		1		1		0		1																										1		35		45								1		0		1		0		0		0		0		0		0		1		0		1																										1		6		7		1104		101		944		81		0		0		642		45																						897		3/26/07		1250		1500		76		03/26/07		90		105

		7/4/07								1		0		1		0		0		0		2		0		2		2		0		2																										1		35		45								0		0		0		0		0		0		1		0		1		1		0		1																										1		6		7		10		0		962		123		0		0		1141		132																						704		5/4/07		1250		1500		89		07/04/07		90		105

		8/3/07								0		0		0		0		0		0		1		0		1		2		0		2																										1		35		45								1		0		1		0		0		0		1		0		1		1		0		1																										1		6		7		0		0		784		61		0		0		875		71																						553		8/3/07		1250		1500		44		08/03/07		90		105

		9/24/07								1		0		1		0		0		0		1		0		1		1		0		1																										1		35		45								0		0		0		0		0		0		0		0		0		1		0		1																										0		6		7		0		0		199		19		0		0		701		49																						300		9/24/07		1250		1500		23		09/24/07		90		105

		11/6/07								1		0		1		0		0		0		3		0		3		3		0		3																										2		35		45								1		0		1		0		0		0		2		0		2		2		0		2																										1		6		7		4		0		563		22		0		0		867		39																						478		11/6/07		1250		1500		20		11/06/07		90		105

		12/11/07								0		0		0		0		0		0		2		0		2		3		0		3																										1		35		45								0		0		0		0		0		0		3		0		3		1		0		1																										1		6		7		2		0		672		36		0		0		901		37																						525		12/11/07		1250		1500		24		12/11/07		90		105

		4/7/08		0		0		0		4		0		4		7		0		7		0		0		0		4		0		4		0		0		0		6		0		6		3		0		3		0		0		0		3		35		45		0		0		0		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		2		0		2		2		0		2		0		0		0		1		6		7		0		0		162		23		208		25		0		0		93		19		0		0		90		6		201		17		0		0		84		4/7/08		1250		1500		10		04/07/08		90		105

		5/7/08		0		0		0		3		0		3		9		0		9		0		0		0		8		0		8		0		0		0		8		0		8		8		0		8		0		0		0		4		35		45		0		0		0		2		0		2		3		0		3		0		0		0		2		0		2		0		0		0		1		0		1		1		0		1		0		0		0		1		6		7		0		0		401		24		489		25		0		0		281		22		0		0		187		18		482		24		0		0		204		5/7/08		1250		1500		13		05/07/08		90		105

		6/3/08		0		0		0		3		0		3		3		0		3		0		0		0		5		0		5		0		0		0		5		0		5		2		0		2		0		0		0		2		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		0		1		0		0		0		1		6		7		0		0		267		10		498		22		0		0		268		22		0		0		301		19		298		11		0		0		181		6/3/08		1250		1500		9		06/03/08		90		105

		7/1/08		0		0		0		8		0		8		0		0		0		8		0		8		6		0		6		0		0		0		3		0		3		2		0		2		0		0		0		3		35		45		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		0		6		7		0		0		403		22		0		0		153		11		287		19		1		0		21		1		121		11		0		0		110		7/1/08		1250		1500		7		07/01/08		90		105

		7/21/08		0		0		0		6		0		6		0		0		0		7		0		7		7		0		7		0		0		0		4		0		4		2		0		2		0		0		0		3		35		45		0		0		0		2		0		2		0		0		0		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		0		0		0		1		6		7		0		0		376		19		0		0		298		17		337		21		0		0		109		8		291		15		0		0		157		7/21/08		1250		1500		9		07/21/08		78		83

		9/4/08		0		0		0		7		0		7		9		0		9		0		0		0		4		0		4		0		0		0		4		0		4		4		0		4		3		0		3		3		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		6		7		0		0		210		19		175		11		0		0		361		18		0		0		101		7		162		9		706		40		191		9/4/08		1250		1500		12		09/04/08		78		83

		9/22/08		0		0		0		5		0		5		4		0		4		0		0		0		4		0		4		0		0		0		2		0		2		4		0		4		2		0		2		2		35		45		0		0		0		2		0		2		0		0		0		0		0		0		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		1		6		7		0		0		332		21		296		15		0		0		194		9		0		0		265		11		295		11		565		22		216		9/22/08		1250		1500		10		09/22/08		78		83

		11/6/08		0		0		0		2		0		2		3		0		3		0		0		0		2		0		2		0		0		0		3		0		3		3		0		3		2		0		2		2		35		45		0		0		0		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		6		7		0		0		776		22		409		19		0		0		292		8		0		0		301		16		228		11		220		9		247		11/6/08		1250		1500		9		11/06/08		78		83

		12/1/08		0		0		0		3		0		3		2		0		2		0		0		0		3		0		3		0		0		0		2		0		2		0		0		0		1		0		1		1		35		45		0		0		0		1		0		1		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		6		7		0		0		290		12		203		11		0		0		221		12		0		0		313		21		19		3		148		10		133		12/1/08		1250		1500		8		12/01/08		78		83

		12/16/08		0		0		0		4		0		4		3		0		3		0		0		0		3		0		3		0		0		0		3		0		3		0		0		0		1		0		1		2		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		6		7		0		0		199		9		289		16		0		0		167		7		0		0		267		17		89		6		177		11		132		12/16/08		1250		1500		7		12/16/08		78		83



&L&"Arial Narrow,Bold"&14CER 2&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER 3

				AIRSTRIPS:																														CONTACT PLATES:																																				PARTICLE COUNTS

				A						B						D						E						Average						A						B						C						D						E						Average						A				B				C				D				E				Average

		Sample Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER3		Total Alert Level		Total Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 3		Total Alert Level		Total Action Level		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		CER 3 0.5um/cu ft		0.5um/cu ft Alert Level		0.5um/cu ft Action Level		CER 3 5.0um/cu ft		5.0um/cu ft Alert Level		5.0um/cu ft Action Level

		2/28/06		29		1		30		21		0		21		28		0		28		37		0		37		29		10		15		3		0		3		3		0		3		3		0		3		2		0		2		4		0		4		3		10		15		4411		344		3943		271		3664		229		3068		212		1233		78		3264		5000		10000		227		30		50

		3/30/06		32		1		33		26		0		26		21		0		21		32		0		32		28		10		15		5		0		5		4		0		4		6		0		6		4		0		4		5		0		5		4		10		15		1261		119		979		81		1461		101		1721		120		630		101		1210		5000		10000		104		30		50

		4/28/06		29		2		31		32		0		32		23		0		23		29		0		29		29		10		15		2		0		2		3		0		3		0		0		0		0		0		0		0		0		0		1		10		15		4536		307		3293		245		2424		222		2637		211		1112		72		2800		5000		10000		211		30		50

		5/30/06		31		0		31		29		0		29		21		1		22		29		0		29		28		10		15		4		0		4		5		0		5		2		0		2		1		0		1		3		0		3		3		10		15		1914		327		2122		327		2561		413		1572		207		1829		252		2000		5000		10000		305		30		50

		7/7/06		26		0		26		19		0		19		22		0		22		31		0		31		25		10		15		4		0		4		5		0		5		3		0		3		2		0		2		5		0		5		3		10		15		2150		382		2668		423		2561		401		2022		399		764		118		2033		5000		10000		345		30		50

		9/5/06		10		0		10		12		0		12		11		0		11		14		0		14		12		10		15		6		0		6		4		0		4		4		0		4		6		0		6		5		0		5		5		10		15		2286		180		2142		171		1829		162		1749		171		1281		148		1857		5000		10000		166		30		50

		10/5/06		9		0		9		10		0		10		10		0		10		8		0		8		9		10		15		7		0		7		5		0		5		6		0		6		4		0		4		4		0		4		5		10		15		1679		346		793		137		1841		241		1429		248		1374		203		1423		5000		10000		235		30		50

		11/14/06		19		2		21		26		0		26		26		0		26		17		0		17		23		10		15		2		0		2		1		0		1		0		0		0		1		0		1		6		0		6		2		10		15		2241		243		2301		231		1974		198		2475		224		2575		201		2313		5000		10000		219		30		50

		12/20/06		10		0		10		13		0		13		13		0		13		16		0		16		13		10		15		5		0		5		1		0		1		0		0		0		3		0		3		1		0		1		2		10		15		406		33		727		46		923		94		604		41		462		39		624		5000		10000		51		30		50

		1/16/07		4		0		4		5		0		5		7		0		7		3		0		3		5		10		15		3		0		3		2		0		2		3		0		3		4		0		4		4		0		4		3		10		15		485		41		1785		101		1986		128		1785		109		1861		118		1580		5000		10000		99		30		50

		2/13/07		12		0		12		22		0		22		18		0		18		21		0		21		18		10		15		2		0		2		4		0		4		2		0		2		1		0		1		2		0		2		2		10		15		1261		87		1641		98		901		62		988		61		1487		88		1256		5000		10000		79		30		50

		3/26/07		11		0		11		12		0		12		10		0		10		9		0		9		11		35		45		2		0		2		1		0		1		2		0		2		1		0		1		2		0		2		2		6		7		1421		109		1221		101		866		71		949		82		1242		101		1140		3800		4500		93		410		500

		5/4/07		10		0		10		10		0		10		9		0		9		11		0		11		10		35		45		2		0		2		3		0		3		1		0		1		2		0		2		2		0		2		2		6		7		1741		110		1444		91		1235		81		1479		87		1521		92		1484		3800		4500		92		410		500

		5/28/07		6		0		6		4		0		4		2		0		2		2		0		2		4		35		45		4		0		4		2		0		2		1		0		1		1		0		1		2		0		2		2		6		7		1421		102		1387		100		1842		169		1785		154		1421		121		1571		3800		4500		129		410		500

		7/4/07		7		0		7		6		0		6		6		0		6		7		0		7		7		35		45		4		0		4		3		0		3		2		0		2		1		0		1		4		0		4		3		6		7		3950		375		2745		292		1658		177		2431		201		2786		247		2714		3800		4500		258		410		500

		8/3/07		6		0		6		6		0		6		4		0		4		5		0		5		5		35		45		3		0		3		3		0		3		2		0		2		2		0		2		2		0		2		3		6		7		1672		145		1897		152		1866		149		1987		151		1487		138		1782		3800		4500		147		410		500

		9/24/07		4		0		4		3		0		3		2		0		2		2		0		2		3		35		45		2		0		2		2		0		2		2		0		2		1		0		1		2		0		2		2		6		7		781		61		1011		72		689		49		768		52		409		31		732		3800		4500		53		410		500

		11/6/07		7		0		7		9		0		9		8		0		8		9		0		9		8		35		45		3		0		3		3		0		3		5		0		5		1		0		1		6		0		6		3		6		7		1276		78		1454		65		1109		55		987		45		1067		47		1179		3800		4500		58		410		500

		12/11/07		9		0		9		12		0		12		9		0		9		11		0		11		10		35		45		2		0		2		4		0		4		4		0		4		5		0		5		4		0		4		4		6		7		1853		101		1321		99		901		45		1241		87		987		72		1261		3800		4500		81		410		500

		4/7/08		8		0		8		15		0		15		12		0		12		10		0		10		11		35		45		2		0		2		3		0		3		2		0		2		3		0		3		4		0		4		3		6		7		1047		69		1642		79		1421		67		1677		71		987		60		1355		3800		4500		69		410		500

		5/7/08		3		0		3		4		0		4		4		0		4		4		0		4		4		35		45		4		0		4		3		0		3		4		0		4		1		0		1		1		0		1		2		6		7		561		31		761		44		660		39		451		21		671		31		621		3800		4500		33		410		500

		6/3/08		3		0		3		4		0		4		4		0		4		4		0		4		4		35		45		2		0		2		2		0		2		2		0		2		1		0		1		1		0		1		2		6		7		409		26		391		33		782		34		891		33		1281		44		751		3800		4500		34		410		500

		7/1/08		7		0		7		7		0		7		8		0		8		8		0		8		8		35		45		2		0		2		2		0		2		1		0		1		1		0		1		1		0		1		2		6		7		1121		81		677		42		339		22		125		11		111		9		475		3800		4500		33		410		500

		7/21/08		9		0		9		8		0		8		8		0		8		11		0		11		9		35		45		3		0		3		3		0		3		2		0		2		2		0		2		2		0		2		3		6		7		891		41		781		33		789		31		499		21		339		12		660		3800		4500		28		410		500

		9/4/08		6		0		6		9		0		9		4		0		4		7		0		7		7		35		45		2		0		2		2		0		2		1		0		1		2		0		2		1		0		1		2		6		7		793		37		1044		44		977		39		1011		57		901		40		945		3800		4500		43		410		500

		9/22/08		9		0		9		9		0		9		9		0		9		7		0		7		9		35		45		1		0		1		2		0		2		2		0		2		2		0		2		1		0		1		2		6		7		984		44		564		31		965		33		698		41		632		39		769		3800		4500		38		410		500

		11/6/08		6		0		6		6		0		6		4		0		4		3		0		3		5		35		45		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		1		6		7		1198		81		901		67		789		43		761		41		904		61		911		3800		4500		59		410		500

		12/1/08		7		0		7		7		0		7		6		0		6		7		0		7		7		35		45		2		0		2		1		0		1		2		0		2		1		0		1		1		0		1		1		6		7		1198		81		901		67		789		43		761		41		904		61		911		3800		4500		59		410		500

		12/16/08		8		0		8		8		0		8		6		0		6		9		0		9		8		35		45		1		0		1		2		0		2		1		0		1		1		0		1		1		0		1		1		6		7		892		41		1098		69		892		34		901		44		1167		72		990		3800		4500		52		410		500



&L&"Arial Narrow,Bold"&14CER 3&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER Pressure

		Daily				Monthly				Daily				Monthly				Daily																		Monthly																		Daily								Monthly								Specs

		Date		CER1		Month		CER1		Date		CER Change Room		Month		CER Change Room		Date		CER2		Temp (F)		Relative Humidity (%)		R&D Bio-Safety Cabinet North (left axis)		R&D Bio-Safety Cabinet South (left axis)		Mfg Bio-Safety Cabinet North (left axis)		Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)		Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)		Month		CER 2		Temp (F)		Relative Humidity (%)		R&D Bio-Safety Cabinet North (left axis)		R&D Bio-Safety Cabinet South (left axis)		Mfg Bio-Safety Cabinet North (left axis)		Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)		Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)		Date		CER3		Temp (ºF)		Humidity (%RH)		Month		CER 3		Temp (ºF)		Humidity (%RH)		Date		CER Alert Level		CER Action Level		Bio-Safety Cabinet Alert Level (left axis)		Bio-Safety Cabinet Action  Level (left axis)		Mfg Bio-Safety Cabinet South Alert Level (right axis)		Mfg Bio-Safety Cabinet South Alarm Level (right axis)

		4/24/06		0.05		April-06		0.045		3/31/06		0.05		March-06		0.055		3/31/06		0.09																March-06		0.090																6/19/06		0.05						June-06		0.051						4/30/06		0.05		0.03

		4/24/06		0.05		May-06		0.022		3/31/06		0.06		April-06		0.053		3/31/06		0.09																April-06		0.089																6/19/06		0.06						July-06		0.061						5/31/06		0.05		0.03

		4/25/06		0.05		June-06		0.013		4/4/06		0.05		May-06		0.050		4/4/06		0.09																July-06		0.076																6/28/06		0.03						August-06		0.055						6/30/06		0.05		0.03

		4/25/06		0.04		July-06		0.041		4/4/06		0.05		June-06		0.046		4/4/06		0.09																August-06		0.068																6/28/06		0.06						September-06		0.052						7/31/06		0.05		0.03

		4/26/06		0.06		August-06		0.033		4/5/06		0.05		July-06		0.048		4/5/06		0.09																September-06		0.062																6/29/06		0.03						October-06		0.051						8/31/06		0.05		0.03

		4/26/06		0.04		September-06		0.027		4/5/06		0.06		August-06		0.050		4/5/06		0.09																October-06		0.034																6/29/06		0.06						November-06		0.053						9/30/06		0.05		0.03

		4/27/06		0.04		October-06		0.033		4/6/06		0.05		September-06		0.048		4/6/06		0.09																November-06		0.020																6/30/06		0.06						December-06		0.051						10/31/06		0.05		0.03

		4/27/06		0.045		November-06		0.028		4/6/06		0.06		October-06		0.053		4/6/06		0.09																December-06		0.012																6/30/06		0.06						February-07		0.040						11/30/06		0.05		0.03

		4/28/06		0.05		December-06		0.030		4/7/06		0.055		November-06		0.035		4/7/06		0.09																January-07		0.011																7/5/06		0.03						March-07		0.037						12/31/06		0.05		0.03

		4/28/06		0.04		January-07		0.030		4/7/06		0.05		December-06		0.031		4/7/06		0.09																February-07		0.013																7/5/06		0.03						April-07		0.038						1/31/07		0.05		0.03

		4/29/06		0.035		February-07		0.038		4/10/06		0.055		January-07		0.031		4/10/06		0.095																March-07		0.031																7/6/06		0.06						May-07		0.038						1/28/07		0.05		0.03

		4/29/06		0.035		March-07		0.037		4/10/06		0.055		February-07		0.035		4/10/06		0.09																April-07		0.033																7/6/06		0.06						June-07		0.040						3/7/07		0.05		0.03

		5/1/06		0.025		April-07		0.031		4/11/06		0.055		March-07		0.036		4/11/06		0.095																May-07		0.044																7/7/06		0.06						July-07		0.057						3/7/07		0.03		0.005

		5/1/06		0.03		May-07		0.027		4/11/06		0.055		April-07		0.035		4/11/06		0.095																June-07		0.048																7/7/06		0.06						August-07		0.053						4/30/07		0.03		0.005

		5/2/06		0.025		June-07		0.027		4/12/06		0.055		May-07		0.032		4/12/06		0.09																July-07		0.050																7/10/06		0.06						September-07		0.050						5/16/07		0.03		0.005

		5/2/06		0.03		July-07		0.035		4/12/06		0.055		June-07		0.028		4/12/06		0.09																August-07		0.042																7/10/06		0.06						October-07		0.049						5/16/07		0.015		0.005

		5/3/06		0.015		August-07		0.032		4/13/06		0.055		July-07		0.030		4/13/06		0.09																September-07		0.046						0.610		0.408								7/11/06		0.06						November-07		0.047						5/31/07		0.015		0.005

		5/4/06		0.03		September-07		0.030		4/13/06		0.055		August-07		0.032		4/13/06		0.095																October-07		0.041						0.620		0.420								7/11/06		0.06						December-07		0.043						6/30/07		0.015		0.005

		5/5/06		0.03		October-07		0.030		4/17/06		0.06		September-07		0.029		4/17/06		0.095																November-07		0.035						0.632		0.424								7/12/06		0.06						January-08		0.040						7/31/07		0.015		0.005

		5/5/06		0.03		November-07		0.065		4/17/06		0.055		October-07		0.027		4/17/06		0.09																December-07		0.030						0.643		0.426								7/12/06		0.06						February-08		0.040						8/31/07		0.015		0.005

		5/6/06		0.03		December-07		0.077		4/18/06		0.055		November-07		0.044		4/18/06		0.095																January-08																		7/13/06		0.06						March-08		0.040						9/5/07		0.015		0.005		0.25		0.1

		5/6/06		0.025		January-08		0.088		4/18/06		0.06		December-07		0.043		4/18/06		0.09																February-08		0.049		69.778		46.100		0.281		0.309		0.428		62.091		1180.364		7/13/06		0.06						April-08		0.048		70.864		42.636		9/30/07		0.015		0.005		0.25		0.1

		5/7/06		0.03		February-08		0.035		4/19/06		0.045		January-08		0.032		4/19/06		0.085																March-08		0.063		70.000		39.750		0.272		0.318		0.441		63.000		1193.000		7/14/06		0.06						May-08		0.040		72.696		37.435		10/31/07		0.015		0.005		0.25		0.1

		5/8/06		0.03		March-08		0.041		4/19/06		0.05		February-08		0.035		4/19/06		0.09																April-08		0.053		71.045		41.000		0.276		0.320		0.454		62.333		1196.333		7/14/06		0.06						June-08		0.025		72.136		33.909		11/30/07		0.015		0.005		0.25		0.1

		5/8/06		0.03		April-08		0.043		4/20/06		0.055		March-08		0.039		4/20/06		0.079																May-08		0.043		72.304		35.913		0.282		0.320		0.449		60.652		1194.957		7/17/06		0.06						July-08		0.059		71.920		39.400		12/31/07		0.015		0.005		0.25		0.1

		5/9/06		0.025		May-08		0.041		4/20/06		0.05		April-08		0.040		4/20/06		0.08																June-08		0.043		71.826		33.522		0.288		0.318		0.447		57.913		790.783		7/17/06		0.06						August-08		0.057		71.600		40.040		1/31/08		0.015		0.005		0.25		0.1

		5/9/06		0.025		June-08		0.039		4/24/06		0.06		May-08		0.040		4/21/06		0.085																July-08		0.077		71.800		38.360		0.285		0.320		0.447		59.789		882.526		7/18/06		0.06						September-08		0.059		71.240		38.000		2/29/08		0.015		0.005		0.25		0.1

		5/10/06		0.025		July-08		0.027		4/24/06		0.06		June-08		0.037		4/21/06		0.085																August-08		0.061		71.440		38.480		0.272		0.318		0.448		0.000		0.000		7/18/06		0.06														3/31/08		0.015		0.005		0.25		0.1

		5/10/06		0.025		August-08		0.031		4/25/06		0.06		July-08		0.040		4/25/06		0.086																September-08		0.059		70.640		38.280		0.259		0.319		0.439		0.000		0.000		7/19/06		0.06														4/1/31		0.015		0.005		0.25		0.1

		5/11/06		0.015		September-08		0.030		4/25/06		0.06		August-08		0.041		4/25/06		0.085																																		7/19/06		0.06														5/31/08		0.015		0.005		0.25		0.1

		5/11/06		0.025						4/26/06		0.05		September-08		0.041		4/26/06		0.085																																		7/20/06		0.07														6/30/08		0.015		0.005		0.25		0.1

		5/12/06		0.025						4/26/06		0.02						4/26/06		0.087																																		7/20/06		0.07														7/31/08		0.015		0.005		0.25		0.1

		5/12/06		0.02						4/27/06		0.06						4/27/06		0.085																																		7/21/06		0.07														8/30/08		0.015		0.005		0.25		0.1

		5/15/06		0.02						4/27/06		0.055						4/27/06		0.085																																		7/21/06		0.07														9/30/08		0.015		0.005		0.25		0.1

		5/15/06		0.025						4/28/06		0.04						4/28/06		0.09																																		7/22/06		0.07

		5/16/06		0.01						4/28/06		0.055						4/28/06		0.08																																		7/22/06		0.07

		5/16/06		0.01						4/29/06		0.05						7/25/06		0.085																																		7/24/06		0.07

		5/17/06		0.01						4/29/06		0.05						7/25/06		0.085																																		7/24/06		0.07

		5/17/06		0.025						5/1/06		0.05						7/26/06		0.085																																		7/25/06		0.06

		5/18/06		0.02						5/1/06		0.055						7/26/06		0.075																																		7/25/06		0.06

		5/18/06		0.02						5/2/06		0.05						7/27/06		0.08																																		7/26/06		0.06

		5/19/06		0.03						5/2/06		0.055						7/27/06		0.08																																		7/26/06		0.06

		5/19/06		0.02						5/3/06		0.05						7/28/06		0.075																																		7/27/06		0.06

		5/20/06		0.01						5/4/06		0.045						7/28/06		0.079																																		7/27/06		0.06

		5/20/06		0.02						5/5/06		0.055						7/29/06		0.069																																		8/1/06		0.06

		5/22/06		0.015						5/5/06		0.05						7/29/06		0.07																																		8/1/06		0.06

		5/22/06		0.015						5/6/06		0.065						7/30/06		0.069																																		8/2/06		0.06

		5/23/06		0.015						5/6/06		0.055						7/30/06		0.069																																		8/2/06		0.06

		5/23/06		0.015						5/7/06		0.05						7/31/06		0.075																																		8/3/06		0.06

		5/24/06		0.015						5/8/06		0.05						7/31/06		0.073																																		8/3/06		0.06

		5/24/06		0.015						5/8/06		0.05						8/1/06		0.07																																		8/4/06		0.06

		5/25/06		0.015						5/9/06		0.05						8/1/06		0.075																																		8/4/06		0.06

		5/25/06		0.03						5/9/06		0.055						8/2/06		0.07																																		8/7/06		0.055

		5/30/06		0.015						5/10/06		0.045						8/2/06		0.07																																		8/7/06		0.06

		5/30/06		0.02						5/10/06		0.04						8/3/06		0.07																																		8/8/06		0.06

		6/1/06		0.01						5/11/06		0.045						8/3/06		0.074																																		8/8/06		0.06

		6/1/06		0.01						5/11/06		0.055						8/4/06		0.074																																		8/9/06		0.06

		6/2/06		0.015						5/12/06		0.05						8/4/06		0.074																																		8/9/06		0.06

		6/5/06		0.01						5/12/06		0.06						8/7/06		0.073																																		8/10/06		0.055

		6/5/06		0.013						5/15/06		0.045						8/7/06		0.073																																		8/10/06		0.055

		6/6/06		0.01						5/15/06		0.055						8/8/06		0.073																																		8/11/06		0.055

		6/6/06		0.01						5/16/06		0.05						8/8/06		0.073																																		8/11/06		0.055

		6/7/06		0.01						5/16/06		0.055						8/10/06		0.074																																		8/14/06		0.055

		6/7/06		0.01						5/17/06		0.04						8/10/06		0.071																																		8/14/06		0.055

		6/8/06		0.01						5/17/06		0.045						8/14/06		0.07																																		8/15/06		0.055

		6/8/06		0.01						5/18/06		0.05						8/15/06		0.069																																		8/15/06		0.055

		6/9/06		0.01						5/18/06		0.055						8/16/06		0.069																																		8/16/06		0.055

		6/9/06		0.01						5/19/06		0.04						8/16/06		0.07																																		8/16/06		0.055

		6/12/06		0.03						5/19/06		0.045						8/17/06		0.069																																		8/17/06		0.055

		6/12/06		0.01						5/20/06		0.04						8/17/06		0.069																																		8/17/06		0.06

		6/13/06		0.03						5/20/06		0.043						8/18/06		0.07																																		8/18/06		0.05

		6/13/06		0.01						5/22/06		0.05						8/18/06		0.068																																		8/18/06		0.065

		6/16/06		0.01						5/22/06		0.05						8/21/06		0.065																																		8/19/06		0.05

		6/16/06		0.01						5/23/06		0.05						8/22/06		0.06																																		8/19/06		0.055

		7/6/06		0.05						5/23/06		0.05						8/22/06		0.065																																		8/21/06		0.055

		7/6/06		0.04						5/24/06		0.045						8/23/06		0.065																																		8/21/06		0.05

		7/7/06		0.04						5/24/06		0.05						8/23/06		0.068																																		8/22/06		0.05

		7/8/06		0.04						5/25/06		0.05						8/24/06		0.065																																		8/22/06		0.056

		7/10/06		0.05						5/25/06		0.05						8/24/06		0.055																																		8/23/06		0.055

		7/11/06		0.04						5/30/06		0.045						8/25/06		0.065																																		8/23/06		0.055

		7/12/06		0.05						5/30/06		0.05						8/25/06		0.065																																		8/24/06		0.05

		7/13/06		0.05						6/1/06		0.045						8/28/06		0.065																																		8/24/06		0.05

		7/17/06		0.06						6/1/06		0.05						8/28/06		0.065																																		8/25/06		0.05

		7/18/06		0.04						6/2/06		0.04						8/30/06		0.065																																		8/25/06		0.055

		7/19/06		0.04						6/5/06		0.05						8/30/06		0.063																																		8/26/06		0.05

		7/20/06		0.04						6/5/06		0.055						8/31/06		0.065																																		8/26/06		0.05

		7/21/06		0.033						6/6/06		0.055						8/31/06		0.065																																		8/28/06		0.05

		7/22/06		0.04						6/6/06		0.05						9/1/06		0.06																																		8/28/06		0.05

		7/23/06		0.04						6/7/06		0.055						9/1/06		0.065																																		8/29/06		0.05

		7/24/06		0.04						6/7/06		0.05						9/5/06		0.065																																		8/29/06		0.05

		7/25/06		0.04						6/8/06		0.05						9/5/06		0.065																																		8/30/06		0.05

		7/26/06		0.035						6/8/06		0.05						9/6/06		0.055																																		8/30/06		0.05

		7/26/06		0.04						6/9/06		0.045						9/6/06		0.065																																		8/31/06		0.05

		7/27/06		0.03						6/9/06		0.05						9/7/06		0.055																																		8/31/06		0.05

		7/27/06		0.04						6/12/06		0.01						9/7/06		0.063																																		9/1/06		0.055

		7/28/06		0.04						6/12/06		0.05						9/8/06		0.06																																		9/6/06		0.05

		7/31/06		0.03						6/13/06		0.01						9/8/06		0.063																																		9/6/06		0.05

		8/1/06		0.035						6/13/06		0.05						9/11/06		0.06																																		9/7/06		0.05

		8/2/06		0.03						6/14/06		0.05						9/11/06		0.065																																		9/7/06		0.05

		8/3/06		0.03						6/14/06		0.055						9/12/06		0.06																																		9/8/06		0.05

		8/4/06		0.03						6/15/06		0.055						9/12/06		0.065																																		9/8/06		0.05

		8/7/06		0.03						6/15/06		0.06						9/13/06		0.06																																		9/11/06		0.05

		8/8/06		0.03						6/16/06		0.05						9/13/06		0.065																																		9/11/06		0.05

		8/10/06		0.03						6/16/06		0.04						9/14/06		0.06																																		9/12/06		0.05

		8/10/06		0.05						6/17/06		0.045						9/14/06		0.065																																		9/12/06		0.06

		8/11/06		0.03						6/17/06		0.05						9/15/06		0.06																																		9/13/06		0.05

		8/11/06		0.05						6/19/06		0.05						9/15/06		0.065																																		9/13/06		0.055

		8/14/06		0.03						6/19/06		0.05						9/18/06		0.06																																		9/14/06		0.05

		8/15/06		0.03						6/20/06		0.05						9/18/06		0.063																																		9/14/06		0.04

		8/16/06		0.05						6/20/06		0.05						9/19/06		0.065																																		9/15/06		0.05

		8/16/06		0.03						6/21/06		0.04						9/19/06		0.055																																		9/15/06		0.05

		8/17/06		0.035						6/21/06		0.05						9/20/06		0.065																																		9/18/06		0.055

		8/17/06		0.03						6/22/06		0.04						9/20/06		0.06																																		9/18/06		0.06

		8/18/06		0.03						6/22/06		0.045						9/21/06		0.065																																		9/19/06		0.05

		8/18/06		0.03						6/26/06		0.04						9/21/06		0.062																																		9/19/06		0.055

		8/19/06		0.035						6/27/06		0.04						9/23/06		0.065																																		9/20/06		0.05

		8/19/06		0.03						6/28/06		0.04						9/23/06		0.062																																		9/20/06		0.05

		8/20/06		0.035						6/29/06		0.04						9/25/06		0.059																																		9/21/06		0.055

		8/21/06		0.03						7/5/06		0.04						9/25/06		0.06																																		9/21/06		0.055

		8/21/06		0.03						7/6/06		0.04						10/2/06		0.06																																		9/22/06		0.05

		8/22/06		0.025						7/7/06		0.05						10/2/06		0.05																																		9/22/06		0.055

		8/22/06		0.035						7/8/06		0.05						10/3/06		0.048																																		9/23/06		0.06

		8/23/06		0.035						7/10/06		0.03						10/3/06		0.042																																		9/23/06		0.06

		8/23/06		0.035						7/11/06		0.05						10/4/06		0.048																																		9/25/06		0.05

		8/24/06		0.035						7/12/06		0.04						10/6/06		0.038																																		9/25/06		0.055

		8/24/06		0.035						7/13/06		0.0425						10/9/06		0.055																																		9/26/06		0.05

		8/25/06		0.035						7/17/06		0.04						10/9/06		0.036																																		9/26/06		0.05

		8/25/06		0.035						7/18/06		0.05						10/10/06		0.037																																		9/27/06		0.05

		8/26/06		0.03						7/19/06		0.05						10/10/06		0.032																																		9/27/06		0.05

		8/26/06		0.035						7/20/06		0.05						10/11/06		0.032																																		9/28/06		0.05

		8/28/06		0.03						7/21/06		0.055						10/11/06		0.032																																		9/28/06		0.05

		8/28/06		0.03						7/22/06		0.055						10/12/06		0.033																																		9/29/06		0.05

		8/29/06		0.03						7/23/06		0.055						10/12/06		0.03																																		9/29/06		0.05

		8/29/06		0.03						7/24/06		0.055						10/13/06		0.031																																		10/2/06		0.055

		8/30/06		0.03						7/25/06		0.05						10/13/06		0.03																																		10/2/06		0.06

		8/30/06		0.035						7/26/06		0.055						10/16/06		0.033																																		10/3/06		0.05

		8/31/06		0.03						7/26/06		0.05						10/16/06		0.032																																		10/3/06		0.05

		8/31/06		0.03						7/27/06		0.05						10/17/06		0.032																																		10/4/06		0.055

		9/1/06		0.03						7/27/06		0.05						10/17/06		0.03																																		10/4/06		0.05

		9/5/06		0.03						7/28/06		0.05						10/18/06		0.033																																		10/5/06		0.05

		9/5/06		0.03						7/31/06		0.05						10/18/06		0.03																																		10/5/06		0.05

		9/6/06		0.02						8/1/06		0.05						10/19/06		0.025																																		10/9/06		0.05

		9/7/06		0.02						8/2/06		0.05						10/19/06		0.03																																		10/9/06		0.05

		9/8/06		0.03						8/3/06		0.05						10/20/06		0.03																																		10/10/06		0.05

		9/11/06		0.03						8/4/06		0.05						10/20/06		0.035																																		10/10/06		0.05

		9/11/06		0.03						8/7/06		0.05						10/23/06		0.032																																		10/11/06		0.05

		9/12/06		0.03						8/8/06		0.05						10/23/06		0.026																																		10/11/06		0.05

		9/12/06		0.03						8/11/06		0.03						10/24/06		0.029																																		10/12/06		0.05

		9/13/06		0.025						8/11/06		0.05						10/24/06		0.029																																		10/12/06		0.05

		9/13/06		0.03						8/14/06		0.05						10/26/06		0.03																																		10/13/06		0.05

		9/14/06		0.03						8/15/06		0.035						10/26/06		0.03																																		10/13/06		0.05

		9/15/06		0.03						8/16/06		0.05						10/30/06		0.025																																		10/14/06		0.05

		9/18/06		0.03						8/17/06		0.05						10/30/06		0.023																																		10/14/06		0.05

		9/19/06		0.03						8/17/06		0.05						10/31/06		0.025																																		10/16/06		0.05

		9/19/06		0.03						8/18/06		0.05						10/31/06		0.015																																		10/16/06		0.05

		9/20/06		0.03						8/18/06		0.05						11/1/06		0.026																																		10/17/06		0.05

		9/20/06		0.03						8/19/06		0.05						11/1/06		0.022																																		10/17/06		0.05

		9/21/06		0.02						8/19/06		0.05						11/2/06		0.025																																		10/18/06		0.05

		9/21/06		0.02						8/20/06		0.05						11/2/06		0.015																																		10/18/06		0.05

		9/22/06		0.02						8/21/06		0.05						11/3/06		0.025																																		10/19/06		0.05

		9/22/06		0.02						8/21/06		0.05						11/3/06		0.015																																		10/19/06		0.05

		9/23/06		0.02						8/22/06		0.045						11/6/06		0.025																																		10/20/06		0.05

		9/23/06		0.03						8/22/06		0.05						11/6/06		0.023																																		10/20/06		0.05

		9/25/06		0.02						8/23/06		0.05						11/7/06		0.02																																		10/23/06		0.05

		9/25/06		0.02						8/23/06		0.055						11/7/06		0.018																																		10/23/06		0.055

		9/26/06		0.02						8/24/06		0.05						11/8/06		0.04																																		10/24/06		0.05

		9/26/06		0.02						8/24/06		0.055						11/8/06		0.018																																		10/24/06		0.05

		9/27/06		0.02						8/25/06		0.05						11/9/06		0.02																																		10/25/06		0.05

		9/27/06		0.05						8/25/06		0.055						11/9/06		0.019																																		10/25/06		0.05

		9/28/06		0.03						8/26/06		0.05						11/10/06		0.02																																		10/26/06		0.05

		9/28/06		0.03						8/26/06		0.05						11/10/06		0.015																																		10/26/06		0.05

		9/29/06		0.02						8/28/06		0.05						11/13/06		0.02																																		10/27/06		0.05

		9/29/06		0.03						8/28/06		0.055						11/13/06		0.02																																		10/27/06		0.05

		10/2/06		0.04						8/29/06		0.05						11/14/06		0.02																																		10/28/06		0.05

		10/3/06		0.03						8/29/06		0.05						11/14/06		0.02																																		10/28/06		0.05

		10/3/06		0.03						8/30/06		0.05						11/15/06		0.02																																		10/30/06		0.05

		10/4/06		0.03						8/30/06		0.05						11/15/06		0.02																																		10/30/06		0.05

		10/4/06		0.03						8/31/06		0.05						11/16/06		0.02																																		10/31/06		0.05

		10/5/06		0.04						8/31/06		0.055						11/17/06		0.02																																		10/31/06		0.05

		10/5/06		0.03						9/1/06		0.05						11/17/06		0.018																																		11/1/06		0.05

		10/6/06		0.02						9/5/06		0.045						11/20/06		0.02																																		11/1/06		0.05

		10/7/06		0.05						9/5/06		0.05						11/20/06		0.015																																		11/2/06		0.05

		10/7/06		0.05						9/6/06		0.045						11/21/06		0.02																																		11/2/06		0.055

		10/9/06		0.04						9/7/06		0.05						11/21/06		0.012																																		11/3/06		0.045

		10/9/06		0.04						9/8/06		0.05						11/22/06		0.02																																		11/3/06		0.05

		10/10/06		0.02						9/11/06		0.05						11/22/06		0.02																																		11/6/06		0.05

		10/10/06		0.02						9/11/06		0.05						11/27/06		0.02																																		11/6/06		0.05

		10/11/06		0.03						9/12/06		0.05						11/27/06		0.04																																		11/7/06		0.05

		10/11/06		0.04						9/12/06		0.05						11/28/06		0.02																																		11/7/06		0.055

		10/12/06		0.035						9/13/06		0.05						11/28/06		0.01																																		11/8/06		0.05

		10/12/06		0.035						9/13/06		0.05						11/29/06		0.02																																		11/8/06		0.06

		10/13/06		0.04						9/14/06		0.05						11/29/06		0.015																																		11/9/06		0.05

		10/13/06		0.04						9/15/06		0.05						11/30/06		0.02																																		11/9/06		0.05

		10/14/06		0.04						9/18/06		0.05						11/30/06		0.015																																		11/10/06		0.05

		10/14/06		0.035						9/19/06		0.05						12/1/06		0.01																																		11/10/06		0.05

		10/16/06		0.04						9/19/06		0.05						12/1/06		0.012																																		11/13/06		0.05

		10/16/06		0.035						9/20/06		0.05						12/4/06		0.01																																		11/13/06		0.06

		10/17/06		0.03						9/20/06		0.05						12/4/06		0.015																																		11/14/06		0.06

		10/17/06		0.04						9/21/06		0.05						12/5/06		0.01																																		11/14/06		0.05

		10/18/06		0.03						9/21/06		0.05						12/5/06		0.015																																		11/15/06		0.055

		10/18/06		0.03						9/22/06		0.05						12/6/06		0.01																																		11/15/06		0.05

		10/19/06		0.025						9/22/06		0.05						12/6/06		0.01																																		11/16/06		0.055

		10/19/06		0.02						9/23/06		0.05						12/7/06		0.02																																		11/16/06		0.055

		10/20/06		0.035						9/23/06		0.05						12/7/06		0.01																																		11/17/06		0.05

		10/20/06		0.05						9/25/06		0.05						12/8/06		0.01																																		11/17/06		0.055

		10/21/06		0.04						9/25/06		0.05						12/8/06		0.01																																		11/18/06		0.05

		10/21/06		0.03						9/26/06		0.05						12/11/06		0.01																																		11/18/06		0.065

		10/23/06		0.035						9/26/06		0.05						12/11/06		0.015																																		11/20/06		0.05

		10/23/06		0.04						9/27/06		0.05						12/12/06		0.01																																		11/20/06		0.06

		10/24/06		0.02						9/27/06		0.02						12/12/06		0.015																																		11/21/06		0.05

		10/24/06		0.02						9/28/06		0.03						12/13/06		0.01																																		11/21/06		0.06

		10/25/06		0.035						9/28/06		0.03						12/13/06		0.015																																		11/22/06		0.05

		10/25/06		0.035						9/29/06		0.05						12/14/06		0.02																																		11/22/06		0.05

		10/26/06		0.025						9/29/06		0.05						12/18/06		0.01																																		11/27/06		0.05

		10/26/06		0.045						10/2/06		0.04						12/18/06		0.01																																		11/27/06		0.05

		10/27/06		0.03						10/3/06		0.05						12/19/06		0.01																																		11/28/06		0.055

		10/27/06		0.03						10/3/06		0.05						12/19/06		0.009																																		11/28/06		0.06

		10/28/06		0.03						10/4/06		0.05						12/20/06		0.01																																		11/29/06		0.05

		10/28/06		0.025						10/4/06		0.05						12/20/06		0.01																																		11/29/06		0.055

		10/30/06		0.035						10/5/06		0.04						12/21/06		0.01																																		11/30/06		0.05

		10/30/06		0.035						10/5/06		0.04						12/21/06		0.008																																		11/30/06		0.05

		10/31/06		0.03						10/6/06		0.03						12/22/06		0.01																																		12/1/06		0.05

		11/1/06		0.025						10/7/06		0.03						12/27/06		0.03																																		12/1/06		0.065

		11/2/06		0.035						10/7/06		0.03						12/28/06		0.01																																		12/2/06		0.05

		11/2/06		0.03						10/9/06		0.03						12/28/06		0.01																																		12/2/06		0.065

		11/3/06		0.02						10/9/06		0.03						12/29/06		0.01																																		12/4/06		0.045

		11/6/06		0.015						10/10/06		0.05						12/29/06		0.01																																		12/4/06		0.05

		11/7/06		0.02						10/10/06		0.05						1/2/07		0.01																																		12/5/06		0.045

		11/8/06		0.025						10/11/06		0.03						1/2/07		0.01																																		12/5/06		0.05

		11/9/06		0.03						10/11/06		0.04						1/3/07		0.01																																		12/6/06		0.05

		11/10/06		0.025						10/12/06		0.035						1/3/07		0.01																																		12/6/06		0.05

		11/11/06		0.035						10/12/06		0.035						1/4/07		0.01																																		12/7/06		0.05

		11/13/06		0.035						10/13/06		0.03						1/4/07		0.01																																		12/7/06		0.05

		11/13/06		0.02						10/13/06		0.04						1/5/07		0.01																																		12/8/06		0.05

		11/14/06		0.02						10/14/06		0.03						1/5/07		0.01																																		12/8/06		0.05

		11/14/06		0.02						10/14/06		0.035						1/8/07		0.01																																		12/9/06		0.05

		11/15/06		0.03						10/16/06		0.04						1/8/07		0.01																																		12/9/06		0.05

		11/15/06		0.035						10/16/06		0.04						1/9/07		0.01																																		12/11/06		0.05

		11/16/06		0.035						10/17/06		0.04						1/9/07		0.01																																		12/11/06		0.05

		11/17/06		0.03						10/17/06		0.04						1/10/07		0.01																																		12/12/06		0.05

		11/17/06		0.035						10/18/06		0.04						1/10/07		0.01																																		12/12/06		0.05

		11/18/06		0.03						10/18/06		0.04						1/11/07		0.02																																		12/13/06		0.055

		11/18/06		0.03						10/19/06		0.04						1/11/07		0.01																																		12/13/06		0.055

		11/20/06		0.045						10/19/06		0.04						1/12/07		0.01																																		12/14/06		0.04

		11/21/06		0.035						10/20/06		0.04						1/12/07		0.01																																		12/14/06		0.05

		11/22/06		0.025						10/20/06		0.04						1/15/07		0.02																																		12/15/06		0.05

		11/22/06		0.035						10/21/06		0.03						1/15/07		0.01																																		12/15/06		0.05

		11/27/06		0.03						10/21/06		0.04						1/16/07		0.01																																		2/28/07		0.04

		11/27/06		0.035						10/23/06		0.035						1/16/07		0.015																																		2/28/07		0.04

		11/28/06		0.015						10/23/06		0.04						1/17/07		0.01																																		3/1/07		0.04

		11/29/06		0.015						10/24/06		0.035						1/17/07		0.01																																		3/2/07		0.04

		11/30/06		0.025						10/24/06		0.035						1/18/07		0.01																																		3/3/07		0.04

		12/1/06		0.025						10/25/06		0.03						1/18/07		0.01																																		3/5/07		0.04

		12/2/06		0.025						10/25/06		0.045						1/19/07		0.01																																		3/6/07		0.04

		12/4/06		0.025						10/26/06		0.045						1/19/07		0.01																																		3/7/07		0.04

		12/5/06		0.03						10/26/06		0.04						1/22/07		0.01																																		3/8/07		0.04

		12/6/06		0.03						10/27/06		0.035						1/22/07		0.02																																		3/9/07		0.04

		12/6/06		0.03						10/27/06		0.03						1/23/07		0.01																																		3/12/07		0.045

		12/7/06		0.03						10/28/06		0.03						1/23/07		0.01																																		3/13/07		0.04

		12/7/06		0.035						10/28/06		0.05						1/24/07		0.01																																		3/14/07		0.04

		12/8/06		0.03						10/30/06		0.035						1/24/07		0.005																																		3/15/07		0.03

		12/8/06		0.03						10/30/06		0.035						1/25/07		0.01																																		3/16/07		0.04

		12/9/06		0.03						10/31/06		0.035						1/25/07		0.01																																		3/17/07		0.04

		12/11/06		0.03						11/1/06		0.035						1/26/07		0.01																																		3/19/07		0.03

		12/11/06		0.03						11/2/06		0.035						1/26/07		0.01																																		3/20/07		0.04

		12/12/06		0.03						11/2/06		0.04						1/29/07		0.01																																		3/21/07		0.04

		12/12/06		0.035						11/3/06		0.035						1/29/07		0.01																																		3/22/07		0.03

		12/13/06		0.03						11/6/06		0.05						1/30/07		0.01																																		3/23/07		0.03

		12/13/06		0.03						11/7/06		0.035						1/30/07		0.01																																		3/26/07		0.04

		12/14/06		0.03						11/8/06		0.04						1/31/07		0.01																																		3/27/07		0.03

		12/14/06		0.03						11/9/06		0.035						1/31/07		0.01																																		3/28/07		0.04

		12/15/06		0.03						11/10/06		0.045						2/1/07		0.01																																		3/29/07		0.03

		12/15/06		0.03						11/11/06		0.04						2/1/07		0.005																																		3/30/07		0.04

		12/18/06		0.03						11/13/06		0.04						2/2/07		0.01																																		3/31/07		0.03

		12/18/06		0.03						11/13/06		0.05						2/2/07		0.005																																		4/2/07		0.03

		12/19/06		0.03						11/14/06		0.04						2/5/07		0.01																																		4/3/07		0.045

		12/19/06		0.03						11/14/06		0.04						2/5/07		0.005																																		4/4/07		0.04

		12/20/06		0.03						11/15/06		0.03						2/6/07		0.01																																		4/5/07		0.04

		12/21/06		0.03						11/15/06		0.03						2/6/07		0.005																																		4/6/07		0.04

		12/21/06		0.03						11/16/06		0.03						2/7/07		0.01																																		4/9/07		0.04

		12/22/06		0.02						11/17/06		0.03						2/7/07		0.005																																		4/10/07		0.03

		12/22/06		0.035						11/17/06		0.035						2/8/07		0.01																																		4/11/07		0.04

		12/27/06		0.03						11/18/06		0.03						2/8/07		0.015																																		4/12/07		0.04

		12/27/06		0.03						11/18/06		0.03						2/9/07		0.01																																		4/13/07		0.035

		12/28/06		0.03						11/20/06		0.015						2/9/07		0.018																																		4/16/07		0.035

		12/28/06		0.03						11/21/06		0.03						2/12/07		0.01																																		4/17/07		0.04

		12/29/06		0.03						11/22/06		0.035						2/12/07		0.012																																		4/18/07		0.035

		12/29/06		0.035						11/22/06		0.035						2/13/07		0.01																																		4/19/07		0.04

		1/2/07		0.03						11/27/06		0.035						2/13/07		0.02																																		4/20/07		0.04

		1/2/07		0.03						11/27/06		0.03						2/14/07		0.02																																		4/23/07		0.03

		1/3/07		0.03						11/28/06		0.035						2/14/07		0.015																																		4/24/07		0.04

		1/3/07		0.03						11/29/06		0.035						2/15/07		0.02																																		4/25/07		0.035

		1/4/07		0.03						11/30/06		0.035						2/16/07		0.01																																		4/26/07		0.035

		1/5/07		0.03						12/1/06		0.03						2/20/07		0.015																																		4/27/07		0.035

		1/5/07		0.03						12/2/06		0.03						2/20/07		0.015																																		4/28/07		0.045

		1/8/07		0.03						12/4/06		0.03						2/21/07		0.02																																		4/30/07		0.04

		1/8/07		0.03						12/5/06		0.03						2/21/07		0.015																																		5/1/07		0.04

		1/9/07		0.03						12/6/06		0.03						2/22/07		0.02																																		5/2/07		0.04

		1/9/07		0.03						12/6/06		0.035						2/22/07		0.018																																		5/3/07		0.04

		1/10/07		0.03						12/7/06		0.03						2/23/07		0.02																																		5/4/07		0.04

		1/10/07		0.03						12/7/06		0.03						2/23/07		0.016																																		5/5/07		0.04

		1/11/07		0.03						12/8/06		0.03						2/26/07		0.015																																		5/7/07		0.035

		1/11/07		0.03						12/8/06		0.035						2/26/07		0.014																																		5/8/07		0.04

		1/12/07		0.03						12/9/06		0.03						2/27/07		0.015																																		5/9/07		0.045

		1/13/07		0.03						12/11/06		0.03						2/27/07		0.014																																		5/10/07		0.04

		1/13/07		0.03						12/11/06		0.03						2/28/07		0.01																																		5/11/07		0.035

		1/15/07		0.03						12/12/06		0.03						3/1/07		0.015																																		5/14/07		0.03

		1/15/07		0.03						12/12/06		0.03						3/2/07		0.015																																		5/15/07		0.035

		1/16/07		0.03						12/13/06		0.03						3/5/07		0.01																																		5/16/07		0.045

		1/16/07		0.025						12/13/06		0.03						3/6/07		0.01																																		5/17/07		0.035

		1/17/07		0.02						12/14/06		0.03						3/7/07		0.04																																		5/18/07		0.04

		1/18/07		0.02						12/14/06		0.035						3/8/07		0.04																																		5/19/07		0.04

		1/19/07		0.03						12/15/06		0.03						3/9/07		0.04																																		5/21/07		0.04

		1/19/07		0.03						12/15/06		0.035						3/12/07		0.04																																		5/22/07		0.04

		1/20/07		0.03						12/18/06		0.03						3/13/07		0.04																																		5/23/07		0.045

		1/22/07		0.03						12/18/06		0.03						3/14/07		0.04																																		5/24/07		0.04

		1/23/07		0.03						12/19/06		0.03						3/15/07		0.035																																		5/29/07		0.03

		1/24/07		0.03						12/19/06		0.03						3/16/07		0.04																																		5/30/07		0.03

		1/24/07		0.03						12/20/06		0.03						3/19/07		0.035																																		5/31/07		0.035

		1/25/07		0.03						12/21/06		0.03						3/20/07		0.035																																		6/1/07		0.035

		1/25/07		0.03						12/21/06		0.035						3/21/07		0.035																																		6/2/07		0.05

		1/26/07		0.03						12/22/06		0.03						3/22/07		0.032																																		6/4/07		0.035

		1/26/07		0.035						12/22/06		0.03						3/23/07		0.03																																		6/5/07		0.04

		1/29/07		0.03						12/27/06		0.03						3/26/07		0.03																																		6/6/07		0.04

		1/29/07		0.035						12/27/06		0.03						3/27/07		0.03																																		6/7/07		0.04

		1/30/07		0.035						12/28/06		0.03						3/28/07		0.035																																		6/8/07		0.045

		1/30/07		0.035						12/28/06		0.035						3/29/07		0.035																																		6/9/07		0.04

		1/31/07		0.03						12/29/06		0.03						3/30/07		0.03																																		6/11/07		0.04

		1/31/07		0.035						12/29/06		0.035						4/2/07		0.03																																		6/12/07		0.04

		2/1/07		0.03						1/2/07		0.03						4/3/07		0.025																																		6/13/07		0.04

		2/1/07		0.03						1/2/07		0.03						4/4/07		0.03																																		6/14/07		0.035

		2/2/07		0.03						1/3/07		0.03						4/5/07		0.025																																		6/15/07		0.045

		2/2/07		0.03						1/3/07		0.03						4/6/07		0.03																																		6/16/07		0.05

		2/3/07		0.03						1/4/07		0.03						4/9/07		0.025																																		6/19/07		0.04

		2/3/07		0.035						1/5/07		0.03						4/10/07		0.03																																		6/20/07		0.04

		2/5/07		0.03						1/5/07		0.03						4/11/07		0.03																																		6/21/07		0.035

		2/5/07		0.03						1/8/07		0.03						4/12/07		0.03																																		6/22/07		0.04

		2/6/07		0.03						1/8/07		0.03						4/13/07		0.028																																		6/23/07		0.04

		2/6/07		0.03						1/9/07		0.03						4/16/07		0.032																																		6/25/07		0.04

		2/7/07		0.05						1/9/07		0.03						4/17/07		0.03																																		6/26/07		0.04

		2/7/07		0.04						1/10/07		0.03						4/18/07		0.025																																		6/27/07		0.04

		2/8/07		0.04						1/10/07		0.035						4/19/07		0.025																																		6/28/07		0.04

		2/8/07		0.03						1/11/07		0.03						4/23/07		0.04																																		6/29/07		0.04

		2/10/07		0.03						1/11/07		0.03						4/24/07		0.044																																		7/2/07		0.04

		2/10/07		0.05						1/12/07		0.03						4/25/07		0.049																																		7/3/07		0.045

		2/12/07		0.03						1/13/07		0.03						4/26/07		0.049																																		7/5/07		0.05

		2/13/07		0.035						1/13/07		0.03						4/27/07		0.045																																		7/6/07		0.05

		2/13/07		0.04						1/15/07		0.03						4/30/07		0.045																																		7/9/07		0.045

		2/14/07		0.04						1/15/07		0.03						5/1/07		0.042																																		7/10/07		0.07

		2/14/07		0.04						1/16/07		0.03						5/2/07		0.045																																		7/11/07		0.045

		2/15/07		0.05						1/16/07		0.03						5/3/07		0.042																																		7/12/07		0.055

		2/15/07		0.04						1/17/07		0.03						5/4/07		0.045																																		7/13/07		0.05

		2/16/07		0.04						1/18/07		0.03						5/7/07		0.045																																		7/14/07		0.05

		2/16/07		0.04						1/19/07		0.035						5/8/07		0.045																																		7/16/07		0.055

		2/20/07		0.05						1/19/07		0.03						5/9/07		0.045																																		7/17/07		0.05

		2/20/07		0.05						1/20/07		0.03						5/10/07		0.045																																		7/18/07		0.075

		2/21/07		0.04						1/22/07		0.03						5/11/07		0.045																																		7/19/07		0.07

		2/21/07		0.055						1/23/07		0.03						5/14/07		0.046																																		7/20/07		0.07

		2/22/07		0.04						1/24/07		0.03						5/15/07		0.05																																		7/23/07		0.07

		2/22/07		0.05						1/24/07		0.03						5/16/07		0.055																																		7/24/07		0.07

		2/23/07		0.03						1/25/07		0.03						5/17/07		0.045																																		7/25/07		0.065

		2/23/07		0.05						1/25/07		0.03						5/18/07		0.04																																		7/26/07		0.055

		2/26/07		0.05						1/26/07		0.03						5/21/07		0.044																																		7/27/07		0.06

		2/26/07		0.04						1/26/07		0.035						5/22/07		0.045																																		7/28/07		0.065

		2/27/07		0.03						1/29/07		0.035						5/23/07		0.045																																		7/30/07		0.05

		2/27/07		0.04						1/29/07		0.035						5/24/07		0.04																																		7/31/07		0.06

		2/28/07		0.03						1/30/07		0.03						5/24/07		0.04																																		8/1/07		0.06

		2/28/07		0.03						1/30/07		0.03						5/29/07		0.025																																		8/2/07		0.06

		3/1/07		0.04						1/31/07		0.03						5/30/07		0.045																																		8/3/07		0.06

		3/2/07		0.04						1/31/07		0.035						5/31/07		0.05																																		8/6/07		0.06

		3/5/07		0.04						2/1/07		0.035						6/1/07		0.051																																		8/7/07		0.06

		3/6/07		0.04						2/1/07		0.03						6/4/07		0.044																																		8/8/07		0.05

		3/7/07		0.04						2/2/07		0.03						6/5/07		0.047																																		8/9/07		0.05

		3/8/07		0.04						2/2/07		0.03						6/6/07		0.046																																		8/10/07		0.05

		3/9/07		0.04						2/3/07		0.03						6/7/07		0.05																																		8/11/07		0.05

		3/12/07		0.04						2/3/07		0.03						6/8/07		0.048																																		8/13/07		0.06

		3/13/07		0.03						2/5/07		0.03						6/9/07		0.049																																		8/14/07		0.05

		3/14/07		0.03						2/5/07		0.03						6/11/07		0.049																																		8/15/07		0.05

		3/15/07		0.04						2/6/07		0.03						6/12/07		0.05																																		8/16/07		0.055

		3/16/07		0.04						2/6/07		0.035						6/13/07		0.045																																		8/17/07		0.055

		3/19/07		0.03						2/7/07		0.03						6/14/07		0.048																																		8/20/07		0.05

		3/20/07		0.04						2/7/07		0.03						6/15/07		0.045																																		8/21/07		0.05

		3/21/07		0.035						2/8/07		0.03						6/18/07		0.045																																		8/22/07		0.05

		3/22/07		0.04						2/8/07		0.03						6/19/07		0.045																																		8/23/07		0.05

		3/23/07		0.04						2/10/07		0.03						6/20/07		0.045																																		8/24/07		0.05

		3/26/07		0.035						2/10/07		0.04						6/21/07		0.045																																		8/27/07		0.05

		3/27/07		0.04						2/12/07		0.03						6/25/07		0.042																																		8/28/07		0.05

		3/28/07		0.035						2/13/07		0.035						6/26/07		0.045																																		8/29/07		0.05

		3/29/07		0.035						2/13/07		0.05						6/27/07		0.04																																		8/30/07		0.05

		3/30/07		0.03						2/14/07		0.04						6/28/07		0.063																																		8/31/07		0.05

		3/31/07		0.035						2/14/07		0.04						6/29/07		0.061																																		9/4/07		0.05

		4/2/07		0.04						2/15/07		0.05						7/2/07		0.06																																		9/5/07		0.05

		4/3/07		0.035						2/15/07		0.04						7/3/07		0.062																																		9/6/07		0.05

		4/4/07		0.035						2/16/07		0.04						7/5/07		0.06																																		9/7/07		0.055

		4/5/07		0.035						2/16/07		0.04						7/6/07		0.058																																		9/10/07		0.045

		4/6/07		0.035						2/20/07		0.05						7/9/07		0.06																																		9/11/07		0.05

		4/9/07		0.035						2/20/07		0.05						7/10/07		0.06																																		9/12/07		0.05

		4/10/07		0.03						2/21/07		0.04						7/11/07		0.055																																		9/13/07		0.045

		4/11/07		0.03						2/21/07		0.035						7/12/07		0.056																																		9/14/07		0.05

		4/12/07		0.03						2/22/07		0.04						7/13/07		0.056																																		9/17/07		0.05

		4/13/07		0.03						2/22/07		0.04						7/16/07		0.055																																		9/18/07		0.045

		4/14/07		0.03						2/23/07		0.03						7/17/07		0.05																																		9/19/07		0.05

		4/16/07		0.03						2/23/07		0.04						7/18/07		0.045																																		9/20/07		0.05

		4/17/07		0.03						2/26/07		0.03						7/19/07		0.045																																		9/21/07		0.05

		4/18/07		0.025						2/26/07		0.035						7/20/07		0.04																																		9/22/07		0.05

		4/19/07		0.03						2/27/07		0.03						7/23/07		0.04																																		9/24/07		0.05

		4/20/07		0.035						2/27/07		0.03						7/24/07		0.04																																		9/25/07		0.05

		4/21/07		0.035						2/28/07		0.03						7/25/07		0.04																																		9/26/07		0.05

		4/23/07		0.025						3/1/07		0.03						7/26/07		0.04																																		9/27/07		0.05

		4/24/07		0.02						3/2/07		0.03						7/28/07		0.04																																		9/28/07		0.05

		4/25/07		0.03						3/5/07		0.03						7/30/07		0.044																																		10/1/07		0.05

		4/26/07		0.04						3/6/07		0.03						7/31/07		0.044																																		10/2/07		0.06

		4/27/07		0.025						3/7/07		0.04						8/1/07		0.04																																		10/3/07		0.05

		4/30/07		0.025						3/8/07		0.04						8/2/07		0.04																																		10/4/07		0.05

		5/1/07		0.03						3/9/07		0.04						8/3/07		0.04																																		10/5/07		0.045

		5/2/07		0.02						3/12/07		0.04						8/4/07		0.042																																		10/8/07		0.05

		5/3/07		0.02						3/13/07		0.04						8/6/07		0.04																																		10/9/07		0.05

		5/4/07		0.02						3/14/07		0.03						8/7/07		0.04																																		10/10/07		0.05

		5/5/07		0.02						3/15/07		0.035						8/8/07		0.034																																		10/11/07		0.05

		5/7/07		0.02						3/16/07		0.035						8/9/07		0.032																																		10/12/07		0.05

		5/8/07		0.025						3/19/07		0.035						8/10/07		0.043																																		10/15/07		0.05

		5/9/07		0.03						3/20/07		0.04						8/13/07		0.045																																		10/16/07		0.045

		5/10/07		0.025						3/21/07		0.04						8/14/07		0.045																																		10/17/07		0.05

		5/11/07		0.005						3/22/07		0.04						8/15/07		0.043																																		10/18/07		0.05

		5/14/07		0.035						3/23/07		0.035						8/16/07		0.04																																		10/19/07		0.045

		5/15/07		0.035						3/26/07		0.035						8/17/07		0.04																																		10/22/07		0.05

		5/16/07		0.03						3/27/07		0.04						8/20/07		0.04																																		10/23/07		0.05

		5/17/07		0.03						3/28/07		0.04						8/21/07		0.03																																		10/24/07		0.045

		5/18/07		0.03						3/29/07		0.035						8/22/07		0.04																																		10/25/07		0.045

		5/19/07		0.03						3/30/07		0.03						8/23/07		0.04																																		10/26/07		0.05

		5/21/07		0.025						3/31/07		0.035						8/24/07		0.04																																		10/29/07		0.05

		5/22/07		0.025						4/2/07		0.035						8/27/07		0.045																																		10/30/07		0.045

		5/23/07		0.025						4/3/07		0.035						8/28/07		0.04																																		10/31/07		0.05

		5/24/07		0.02						4/4/07		0.04						8/29/07		0.055																																		11/1/07		0.045

		5/25/07		0.025						4/5/07		0.04						8/30/07		0.055																																		11/2/07		0.05

		5/29/07		0.025						4/6/07		0.04						8/31/07		0.05																																		11/5/07		0.05

		5/30/07		0.048						4/9/07		0.035						9/4/07		0.05																																		11/6/07		0.045

		5/31/07		0.04						4/10/07		0.035						9/5/07		0.04						0.61		0.4																										11/7/07		0.05

		6/1/07		0.025						4/11/07		0.04						9/6/07		0.05						0.61		0.41																										11/8/07		0.05

		6/2/07		0.03						4/12/07		0.035						9/7/07		0.045						0.6		0.41																										11/9/07		0.05

		6/4/07		0.03						4/13/07		0.035						9/8/07		0.04						0.6		0.41																										11/12/07		0.045

		6/5/07		0.0175						4/14/07		0.03						9/10/07		0.055						0.61		0.41																										11/13/07		0.05

		6/6/07		0.03						4/16/07		0.035						9/11/07		0.05						0.61		0.41																										11/14/07		0.045

		6/7/07		0.04						4/17/07		0.035						9/12/07		0.05						0.61		0.41																										11/15/07		0.045

		6/8/07		0.025						4/18/07		0.04						9/13/07		0.05						0.61		0.41																										11/16/07		0.045

		6/9/07		0.02						4/19/07		0.035						9/14/07		0.05						0.6		0.42																										11/19/07		0.045

		6/11/07		0.04						4/20/07		0.04						9/15/07		0.05						0.6		0.4																										11/20/07		0.045

		6/12/07		0.02						4/21/07		0.035						9/17/07		0.054						0.6		0.41																										11/21/07		0.045

		6/13/07		0.03						4/23/07		0.035						9/18/07		0.054						0.61		0.41																										11/26/07		0.045

		6/14/07		0.025						4/24/07		0.02						9/19/07		0.045						0.65		0.4																										11/27/07		0.045

		6/15/07		0.02						4/25/07		0.04						9/20/07		0.045						0.61		0.41																										11/28/07		0.045

		6/18/07		0.025						4/26/07		0.035						9/21/07		0.04						0.6		0.4																										11/29/07		0.045

		6/19/07		0.02						4/27/07		0.04						9/24/07		0.035						0.6		0.4																										11/30/07		0.045

		6/20/07		0.03						4/30/07		0.025						9/25/07		0.04						0.62		0.4																										12/1/07		0.045

		6/21/07		0.016						5/1/07		0.03						9/26/07		0.04						0.62		0.42																										12/3/07		0.045

		6/22/07		0.025						5/2/07		0.03						9/27/07		0.04						0.62		0.42																										12/4/07		0.045

		6/25/07		0.02						5/3/07		0.03						9/28/07		0.05						0.6		0.4																										12/5/07		0.045

		6/26/07		0.025						5/4/07		0.035						10/1/07		0.04						0.62		0.42																										12/6/07		0.045

		6/27/07		0.03						5/5/07		0.035						10/2/07		0.045						0.62		0.42																										12/7/07		0.045

		6/28/07		0.045						5/7/07		0.04						10/3/07		0.045						0.62		0.42																										12/8/07		0.045

		6/29/07		0.025						5/8/07		0.045						10/4/07		0.05						0.61		0.42																										12/10/07		0.045

		7/2/07		0.04						5/9/07		0.03						10/5/07		0.05						0.62		0.42																										12/11/07		0.04

		7/3/07		0.04						5/10/07		0.04						10/8/07		0.05						0.62		0.42																										12/12/07		0.04

		7/5/07		0.04						5/11/07		0.03						10/9/07		0.04						0.62		0.42																										12/13/07		0.04

		7/6/07		0.04						5/14/07		0.03						10/10/07		0.04						0.62		0.42																										12/14/07		0.04

		7/9/07		0.04						5/15/07		0.03						10/11/07		0.05						0.62		0.42																										12/17/07		0.04

		7/10/07		0.03						5/16/07		0.03						10/12/07		0.045						0.62		0.42																										12/18/07		0.045

		7/11/07		0.035						5/17/07		0.03						10/13/07		0.04						0.62		0.42																										12/19/07		0.04

		7/12/07		0.035						5/18/07		0.03						10/15/07		0.04						0.61		0.41																										12/20/07		0.04

		7/13/07		0.03						5/19/07		0.03						10/16/07		0.04						0.62		0.42																										12/26/07		0.04

		7/16/07		0.03						5/21/07		0.03						10/17/07		0.04						0.61		0.41																										12/27/07		0.04

		7/17/07		0.035						5/22/07		0.03						10/18/07		0.04						0.62		0.42																										12/28/07		0.04

		7/18/07		0.03						5/23/07		0.03						10/19/07		0.04						0.62		0.42																										12/31/07		0.05

		7/19/07		0.03						5/24/07		0.03						10/22/07		0.045						0.62		0.42																										1/2/08		0.04

		7/20/07		0.03						5/25/07		0.03						10/23/07		0.05						0.64		0.44																										1/3/08		0.04

		7/23/07		0.04						5/29/07		0.035						10/24/07		0.045						0.62		0.42																										1/4/08		0.04

		7/24/07		0.035						5/30/07		0.02						10/25/07		0.03						0.62		0.42																										1/7/08		0.04

		7/25/07		0.035						5/31/07		0.03						10/26/07		0.035						0.62		0.42																										1/8/08		0.04

		7/26/07		0.04						6/1/07		0.03						10/29/07		0.03						0.62		0.42																										1/9/08		0.04

		7/27/07		0.04						6/2/07		0.03						10/30/07		0.025						0.62		0.42																										1/10/08		0.04

		7/30/07		0.035						6/4/07		0.03						10/31/07		0.03						0.62		0.42																										1/11/08		0.04

		7/31/07		0.035						6/5/07		0.04						11/1/07		0.035						0.62		0.42																										1/14/08		0.04

		8/1/07		0.03						6/6/07		0.025						11/2/07		0.035						0.62		0.42																										1/15/08		0.04

		8/2/07		0.035						6/7/07		0.03						11/5/07		0.025						0.62		0.4																										1/16/08		0.04

		8/3/07		0.04						6/8/07		0.03						11/6/07		0.04						0.62		0.41																										1/17/08		0.04

		8/4/07		0.03						6/9/07		0.025						11/7/07		0.02						0.62		0.42																										1/18/08		0.04

		8/6/07		0.03						6/11/07		0.03						11/8/07		0.03						0.62		0.42																										1/21/08		0.04

		8/7/07		0.035						6/12/07		0.02						11/9/07		0.02						0.62		0.42																										1/22/08		0.04

		8/8/07		0.03						6/13/07		0.03						11/12/07		0.035						0.62		0.42																										1/23/08		0.04

		8/9/07		0.03						6/14/07		0.025						11/13/07		0.04						0.62		0.4																										1/24/08		0.04

		8/10/07		0.04						6/15/07		0.025						11/14/07		0.04						0.62		0.42																										1/25/08		0.045

		8/13/07		0.03						6/18/07		0.03						11/15/07		0.04						0.62		0.42																										1/28/08		0.04

		8/14/07		0.03						6/19/07		0.025						11/16/07		0.035						0.62		0.42																										1/29/08		0.04

		8/15/07		0.03						6/20/07		0.03						11/19/07		0.045						0.66		0.44																										1/30/08		0.04

		8/17/07		0.03						6/21/07		0.03						11/20/07		0.04						0.64		0.42																										1/31/08		0.04

		8/20/07		0.03						6/22/07		0.02						11/21/07		0.04						0.64		0.42																										2/1/08		0.04

		8/21/07		0.03						6/25/07		0.02						11/26/07		0.04						0.66		0.44																										2/4/08		0.04

		8/22/07		0.03						6/26/07		0.02						11/27/07		0.042						0.66		0.44																										2/5/08		0.04

		8/23/07		0.03						6/27/07		0.03						11/28/07		0.04						0.66		0.44																										2/6/08		0.04

		8/24/07		0.03						6/28/07		0.03						11/29/07		0.03						0.64		0.44																										2/7/08		0.04

		8/25/07		0.02						6/29/07		0.04						11/30/07		0.03						0.64		0.44																										2/8/08		0.04

		8/27/07		0.04						7/2/07		0.03						12/3/07		0.04						0.64		0.44																										2/11/08		0.04

		8/28/07		0.035						7/3/07		0.025						12/4/07		0.03						0.64		0.42																										2/12/08		0.04

		8/29/07		0.04						7/5/07		0.03						12/5/07		0.03						0.64		0.44																										2/13/08		0.04

		8/30/07		0.03						7/6/07		0.025						12/6/07		0.03						0.64		0.42																										2/14/08		0.04

		8/31/07		0.03						7/9/07		0.025						12/7/07		0.03						0.64		0.44																										2/15/08		0.04

		9/4/07		0.03						7/10/07		0.03						12/10/07		0.03						0.64		0.44																										2/16/08		0.04

		9/5/07		0.03						7/11/07		0.035						12/11/07		0.03						0.66		0.42																										2/19/08		0.04

		9/6/07		0.035						7/12/07		0.035						12/12/07		0.03						0.6		0.42																										2/20/08		0.045

		9/7/07		0.02						7/13/07		0.03						12/13/07		0.045						0.66		0.42																										2/21/08		0.04

		9/8/07		0.04						7/16/07		0.03						12/14/07		0.03						0.66		0.42																										2/22/08		0.04

		9/10/07		0.025						7/17/07		0.03						12/17/07		0.03						0.64		0.42																										2/25/08		0.04

		9/11/07		0.035						7/18/07		0.025						12/18/07		0.03						0.66		0.4																										2/26/08		0.04

		9/12/07		0.035						7/19/07		0.025						12/19/07		0.02						0.66		0.42																										2/27/08		0.04

		9/13/07		0.03						7/20/07		0.035						12/20/07		0.03						0.64		0.42																										2/28/08		0.04

		9/14/07		0.03						7/23/07		0.03						12/21/07		0.04						0.66		0.42																										2/29/08		0.04

		9/17/07		0.03						7/24/07		0.025						12/26/07		0.03						0.64		0.42																										3/1/08		0.04

		9/18/07		0.025						7/25/07		0.035						12/27/07		0.025						0.62		0.44																										3/2/08		0.04

		9/19/07		0.04						7/26/07		0.03						12/28/07		0.025						0.64		0.44																										3/3/08		0.04

		9/20/07		0.04						7/27/07		0.03						12/31/07		0.02						0.64		0.44																										3/4/08		0.04

		9/21/07		0.03						7/30/07		0.035																																										3/5/08		0.04

		9/24/07		0.025						7/31/07		0.04						2/14/08		0.04						0.292		0.309		0.485		61		1180																				3/6/08		0.04

		9/25/07		0.035						8/1/07		0.03						2/15/08		0.037		69		50		0.28		0.31		0.414		61		1172																				3/7/08		0.04

		9/26/07		0.025						8/2/07		0.035						2/19/08		0.035		69		48		0.293		0.309		0.426		60		1184																				3/8/08		0.04

		9/27/07		0.02						8/3/07		0.03						2/20/08		0.03		70		46		0.26		0.309		0.41		63		1184																				3/10/08		0.04

		9/28/07		0.02						8/4/07		0.03						2/21/08		0.032		70		46		0.29		0.305		0.441		62		1164																				3/11/08		0.04

		9/29/07		0.02						8/6/07		0.03						2/22/08		0.031		70		45		0.281		0.307		0.419		62		1184																				3/12/08		0.04

		10/1/07		0.015						8/7/07		0.025						2/25/08		0.069		70		46		0.288		0.311		0.421		63		1184																				3/13/08		0.04

		10/2/07		0.035						8/8/07		0.03						2/26/08		0.068		70		44		0.281		0.312		0.413		64		1192																				3/14/08		0.04

		10/3/07		0.03						8/9/07		0.045						2/27/08		0.067		70		45		0.288		0.311		0.413		62		1184																				3/15/08		0.04

		10/4/07		0.04						8/10/07		0.04						2/28/08		0.063		70		46		0.283		0.31		0.457		62		1172																				3/17/08		0.04

		10/5/07		0.025						8/13/07		0.04						2/29/08		0.064		70		45		0.256		0.311		0.409		63		1184																				3/18/08		0.04

		10/8/07		0.03						8/14/07		0.04						3/3/08		0.07		70		33		0.285		0.311		0.435		63		1204																				3/19/08		0.04

		10/9/07		0.03						8/15/07		0.04						3/4/08		0.07		70		44		0.261		0.311		0.438		63		1184																				3/20/08		0.04

		10/10/07		0.03						8/17/07		0.04						3/5/08		0.069		70		44		0.291		0.311		0.445		63		1184																				3/21/08		0.04

		10/11/07		0.03						8/20/07		0.03						3/6/08		0.068		70		44		0.281		0.311		0.458		61		1184																				3/22/08		0.04

		10/12/07		0.02						8/21/07		0.03						3/7/08		0.067		70		44		0.282		0.322		0.455		63		1192																				3/24/08		0.04

		10/15/07		0.03						8/22/07		0.035						3/10/08		0.069		70		46		0.264		0.321		0.428		64		1184																				3/25/08		0.04

		10/16/07		0.02						8/23/07		0.03						3/11/08		0.071		70		43		0.285		0.322		0.438		63		1204																				3/26/08		0.045

		10/17/07		0.04						8/24/07		0.035						3/12/08		0.056		70		44		0.261		0.312		0.422		62		1188																				3/27/08		0.04		70		25

		10/18/07		0.04						8/25/07		0.02						3/14/08		0.067		70		43		0.261		0.321		0.451		63		1184																				3/28/08		0.04		70		41

		10/19/07		0.025						8/27/07		0.025						3/17/08		0.069		70		45		0.26		0.32		0.439		63		1196																				3/31/08		0.04		70		28

		10/22/07		0.03						8/28/07		0.025						3/18/08		0.062		70		47		0.279		0.32		0.422		63		1196																				4/1/08		0.04		70		29

		10/23/07		0.03						8/29/07		0.03						3/19/08		0.053		70		44		0.273		0.321		0.419		64		1192																				4/2/08		0.055		70		36

		10/24/07		0.04						8/30/07		0.03						3/20/08		0.064		70		33		0.262		0.321		0.431		64		1192																				4/3/08		0.04		69		40

		10/25/07		0.035						8/31/07		0.03						3/21/08		0.063		70		35		0.277		0.322		0.439		63		1196																				4/4/08		0.045		70		44

		10/26/07		0.045						9/4/07		0.03						3/24/08		0.052		70		42		0.238		0.321		0.418		63		1184																				4/5/08		0.04		70		41

		10/29/07		0.02						9/5/07		0.03						3/25/08		0.057		70		38		0.264		0.319		0.445		63		1192																				4/7/08		0.05		70		44

		10/30/07		0.02						9/6/07		0.03						3/26/08		0.056		70		35		0.276		0.321		0.447		63		1204																				4/8/08		0.05		70		44

		10/31/07		0.02						9/7/07		0.03						3/27/08		0.07		70		24		0.28		0.32		0.46		63		1204																				4/9/08		0.05		70		44

		11/1/07		0.03						9/8/07		0.03						3/28/08		0.05		70		40		0.26		0.32		0.44		63		1192																				4/10/08		0.05		70		44

		11/2/07		0.025						9/10/07		0.02						3/31/08		0.06		70		27		0.3		0.32		0.48		63		1204																				4/11/08		0.05		70		46

		11/5/07		0.03						9/11/07		0.02						4/1/08		0.06		70		28		0.28		0.32		0.46		61		1192																				4/14/08		0.05		72		41

		11/6/07		0.025						9/12/07		0.03						4/2/08		0.06		70		30		0.28		0.32		0.44		63		1204																				4/15/08		0.05		74		42

		11/7/07		0.025						9/13/07		0.02						4/3/08		0.06		70		38		0.28		0.32		0.44		64		1192																				4/16/08		0.05		70		45

		11/8/07		0.085						9/14/07		0.035						4/4/08		0.05		70		44		0.26		0.32		0.44		63		1196																				4/17/08		0.045		72		46

		11/9/07		0.08						9/17/07		0.03						4/5/08		0.05		70		40		0.26		0.32		0.44		63		1196																				4/18/08		0.04		70		48

		11/12/07		0.075						9/18/07		0.03						4/7/08		0.055		70		44		0.26		0.32		0.46		65		1204																				4/19/08		0.05		69		48

		11/13/07		0.08						9/19/07		0.04						4/8/08		0.055		70		44		0.28		0.32		0.44		61		1192																				4/21/08		0.05		73		47

		11/14/07		0.075						9/20/07		0.04						4/9/08		0.055		70		46		0.28		0.32		0.44		63		1196																				4/22/08		0.045		77		46

		11/15/07		0.075						9/21/07		0.03						4/10/08		0.05		70		45		0.28		0.32		0.44		61		1204																				4/23/08		0.05		71		45

		11/16/07		0.07						9/24/07		0.025						4/11/08		0.05		70		42		0.28		0.32		0.44		61		1192																				4/24/08		0.045		73		46

		11/19/07		0.075						9/25/07		0.025						4/14/08		0.05		70		43		0.28		0.32		0.46		61		1196																				4/25/08		0.04		70		46

		11/20/07		0.07						9/26/07		0.03						4/15/08		0.05		73		41		0.28		0.32		0.44		62		1196																				4/30/08		0.06		69		26

		11/21/07		0.075						9/27/07		0.03						4/16/08		0.05		72		43		0.28		0.32		0.48		62		1196																				5/1/08		0.04		75		42

		11/26/07		0.08						9/28/07		0.03						4/17/08		0.05		72		44		0.28		0.32		0.48		62		1196																				5/2/08		0.04		72		35

		11/27/07		0.08						9/29/07		0.025						4/18/08		0.05		72		45		0.28		0.32		0.48		62		1196																				5/3/08		0.04		78		34

		11/28/07		0.08						10/1/07		0.03						4/19/08		0.06		72		44		0.28		0.32		0.48		62		1196																				5/5/08		0.04		71		40

		11/29/07		0.075						10/2/07		0.025						4/21/08		0.055		71		45		0.28		0.32		0.46		64		1196																				5/6/08		0.045		75		40

		11/30/07		0.08						10/3/07		0.03						4/22/08		0.05		72		43		0.28		0.32		0.46		64		1196																				5/7/08		0.05		72		36

		12/3/07		0.07						10/4/07		0.03						4/23/08		0.05		73		42		0.28		0.32		0.48		63		1196																				5/8/08		0.045		72		38

		12/4/07		0.08						10/5/07		0.02						4/24/08		0.055		73		45		0.28		0.32		0.46		63		1196																				5/9/08		0.04		74		34

		12/5/07		0.07						10/8/07		0.03						4/25/08		0.05		73		41		0.26		0.32		0.44		63		1204																				5/10/08		0.045		72		34

		12/6/07		0.08						10/9/07		0.02						4/28/08								0.26		0.32		0.44		63		1204																				5/12/08		0.055		69		28

		12/7/07		0.075						10/10/07		0.025						4/29/08								0.28		0.32		0.44		60		1184																				5/13/08		0.04		75		31

		12/10/07		0.075						10/11/07		0.03						4/30/08		0.06		70		25		0.28		0.32		0.46		60		1192																				5/14/08		0.05		71		38

		12/11/07		0.075						10/12/07		0.02						5/1/08		0.055		73		39		0.28		0.32		0.46		60		1196																				5/15/08		0.04		72		42

		12/12/07		0.075						10/15/07		0.025						5/2/08		0.045		72		34		0.28		0.32		0.46		60		1210																				5/16/08		0.04		71		48

		12/13/07		0.075						10/16/07		0.025						5/3/08		0.05		73		38		0.28		0.32		0.46		60		1210																				5/19/08		0.04		75		42

		12/14/07		0.075						10/17/07		0.03						5/5/08		0.04		72		38		0.28		0.32		0.44		60		1192																				5/20/08		0.04		73		44

		12/17/07		0.08						10/18/07		0.025						5/6/08		0.04		73		42		0.28		0.32		0.44		60		1184																				5/21/08		0.04		71		36

		12/18/07		0.075						10/19/07		0.025						5/7/08		0.04		73		37		0.28		0.32		0.44		62		1196																				5/22/08		0.04		73		30

		12/19/07		0.08						10/22/07		0.025						5/8/08		0.04		73		35		0.28		0.32		0.44		60		1196																				5/23/08		0.04		71		36

		12/20/07		0.08						10/23/07		0.02						5/9/08		0.04		72		34		0.3		0.32		0.46		62		1204																				5/27/08		0.02		73		37

		12/21/07		0.08						10/24/07		0.035						5/10/08		0.04		72		32		0.3		0.32		0.46		62		1204																				5/28/08		0.03		71		39

		12/26/07		0.08						10/25/07		0.025						5/12/08		0.055		68		28		0.26		0.32		0.42		60		1196																				5/29/08		0.03		74		39

		12/27/07		0.08						10/26/07		0.035						5/13/08		0.04		73		31		0.26		0.32		0.46		61		1192																				5/30/08		0.04		72		38

		12/28/07		0.075						10/29/07		0.025						5/14/08		0.045		73		25		0.3		0.32		0.46		60		1184																				5/31/08		0.025		72		39

		12/31/07		0.08						10/30/07		0.03						5/15/08		0.035		73		39		0.3		0.32		0.46		60		1196																				6/2/08		0.025		74		27

		1/2/08		0.09						10/31/07		0.03						5/16/08		0.035		73		45		0.3		0.32		0.44		60		1184																				6/3/08		0.02		71		34

		1/3/08		0.075						11/1/07		0.04						5/19/08		0.045		72		41		0.28		0.32		0.44		60		1204																				6/4/08		0.025		69		33

		1/4/08		0.09						11/2/07		0.03						5/20/08		0.045		73		42		0.28		0.32		0.44		62		1196																				6/5/08		0.025		71		39

		1/7/08		0.125						11/5/07		0.025						5/21/08		0.045		70		35		0.28		0.32		0.46		60		1196																				6/6/08		0.025		71		32

		1/8/08		0.08						11/6/07		0.03						5/22/08		0.045		72		30		0.28		0.32		0.42		61		1176																				6/9/08		0.03		72		43

		1/9/08		0.08						11/7/07		0.035						5/23/08		0.045		73		34		0.28		0.32		0.46		61		1172																				6/10/08		0.03		73		33

		1/10/08		0.08						11/8/07		0.05						5/27/08		0.035		73		36		0.28		0.32		0.44		61		1196																				6/11/08		0.025		70		33

		1/11/08		0.08						11/9/07		0.05						5/28/08		0.04		72		37		0.28		0.32		0.44		61		1204																				6/12/08		0.025		71		35

		1/14/08		0.09						11/12/07		0.03						5/29/08		0.04		73		37		0.26		0.32		0.44		61		1200																				6/13/08		0.025		75		32

		1/15/08		0.085						11/13/07		0.05						5/30/08		0.04		72		37		0.28		0.32		0.48		61		1196																				6/16/08		0.025		72		37

		1/16/08		0.09						11/14/07		0.05						6/2/08		0.04		71		30		0.28		0.28		0.44		60		1200																				6/17/08		0.03		72		26

		1/17/08		0.08						11/15/07		0.05						6/3/08		0.035		72		35		0.28		0.32		0.42		61		1196																				6/18/08		0.025		73		33

		1/18/08		0.09						11/16/07		0.05						6/4/08		0.035		70		33		0.28		0.32		0.44		61		1188																				6/19/08		0.025		71		29

		1/21/08		0.04						11/19/07		0.05						6/5/08		0.035		71		37		0.3		0.32		0.44		61		1192																				6/20/08		0.02		73		33

		1/22/08		0.11						11/20/07		0.05						6/6/08		0.035		71		31		0.28		0.32		0.44		61		1188																				6/21/08		0.025		74		27

		1/23/08		0.09						11/21/07		0.05						6/9/08		0.04		72		40		0.32		0.32		0.48		61		1188																				6/23/08		0.02		72		37

		1/24/08		0.09						11/26/07		0.05						6/10/08		0.04		72		31		0.3		0.32		0.44		55		1172																				6/24/08		0.025		73		35

		1/25/08		0.095						11/27/07		0.05						6/11/08		0.04		70		34		0.3		0.32		0.48		55		1196																				6/25/08		0.03		72		36

		1/28/08		0.09						11/28/07		0.05						6/12/08		0.04		72		31		0.3		0.32		0.48		55		1196																				6/26/08		0.03		74		35

		1/29/08		0.09						11/29/07		0.045						6/13/08		0.05		71		36		0.26		0.32		0.44		55		1208																				6/27/08		0.02		71		39

		1/30/08		0.1						11/30/07		0.05						6/16/08		0.05		73		34		0.3		0.32		0.46		55		1204																				6/30/08		0.02		73		38

		1/31/08		0.105						12/3/07		0.05						6/17/08		0.05		73		24		0.28		0.32		0.44		55		1216																				7/1/08		0.055		73		39

		2/1/08		0.09						12/4/07		0.05						6/18/08		0.05		73		31		0.3		0.32		0.44		55		1196																				7/2/08		0.055		73		38

		2/4/08		0.03						12/5/07		0.045						6/19/08		0.05		71		30		0.28		0.32		0.46		55		1196																				7/3/08		0.065		71		39

		2/5/08		0.04						12/6/07		0.05						6/20/08		0.05		73		28		0.28		0.32		0.46		55		1196																				7/7/08		0.055		75		38

		2/6/08		0.025						12/7/07		0.045						6/21/08		0.045		72		30		0.26		0.32		0.46		55		32																				7/8/08		0.05		72		40

		2/7/08		0.02						12/10/07		0.05						6/23/08		0.05		73		39		0.28		0.32		0.44		57		32																				7/9/08		0.06		73		39

		2/8/08		0.04						12/11/07		0.045						6/24/08		0.05		72		34		0.28		0.32		0.42		60		32																				7/10/08		0.06		74		39

		2/9/08		0.05						12/12/07		0.045						6/25/08		0.04		73		36		0.28		0.32		0.44		60		32																				7/11/08		0.06		71		40

		2/11/08		0.02						12/13/07		0.045						6/26/08		0.04		72		34		0.28		0.32		0.44		60		32																				7/12/08		0.06		73		42

		2/12/08		0.035						12/14/07		0.045						6/27/08		0.04		71		38		0.32		0.32		0.44		60		32																				7/14/08		0.06		72		41

		2/13/08		0.025						12/17/07		0.045						6/30/08		0.04		73		37		0.3		0.32		0.44		60		32																				7/15/08		0.06		71		41

		2/14/08		0.025						12/18/07		0.04						7/1/08		0.035		71		38		0.28		0.32		0.44		60		32																				7/16/08		0.065		72		40

		2/15/08		0.03						12/19/07		0.04						7/2/08		0.07		72		38		0.3		0.32		0.46		60		32																				7/17/08		0.05		71		41

		2/19/08		0.03						12/20/07		0.03						7/3/08		0.08		72		38		0.32		0.32		0.48		57		32																				7/18/08		0.065		72		40

		2/20/08		0.05						12/21/07		0.04						7/7/08		0.06		73		40		0.28		0.32		0.44		57		32																				7/19/08		0.06		72		39

		2/21/08		0.03						12/26/07		0.04						7/8/08		0.06		72		38		0.28		0.32		0.42		60		32																				7/21/08		0.06		71		40

		2/22/08		0.03						12/27/07		0.04						7/9/08		0.06		73		39		0.28		0.32		0.42																								7/22/08		0.05		74		36

		2/23/08		0.035						12/28/07		0.04						7/10/08		0.07		72		40		0.32		0.32		0.48		55		1104																				7/23/08		0.07		72		39

		2/24/08		0.035						12/31/07		0.04						7/11/08		0.065		71		39		0.3		0.32		0.48		55		1104																				7/24/08		0.05		72		37

		2/25/08		0.03						1/2/08		0.04						7/12/08		0.08		73		40																														7/25/08		0.06		71		38

		2/26/08		0.035						1/3/08		0.04						7/14/08		0.08		72		40		0.3		0.32		0.48		61		1200																				7/26/08		0.07		71		38

		2/27/08		0.03						1/4/08		0.04						7/15/08		0.09		71		40		0.28		0.32		0.42		61		1200																				7/28/08		0.06		70		41

		2/28/08		0.03						1/7/08		0.025						7/16/08		0.09		72		39		0.28		0.32		0.42		61		1200																				7/29/08		0.06		70		41

		2/29/08		0.03						1/8/08		0.03						7/17/08		0.08		72		39		0.28		0.32		0.44		61		1200																				7/30/08		0.06		71		39

		3/1/08		0.035						1/9/08		0.03						7/18/08		0.09		72		38		0.3		0.32		0.48		61		1200																				7/31/08		0.065		71		40

		3/3/08		0.03						1/10/08		0.03						7/19/08		0.09		73		37																														8/1/08		0.06		73		36

		3/4/08		0.035						1/11/08		0.03						7/21/08		0.09		72		38		0.28		0.32		0.4		61		1200																				8/2/08		0.06		71		40

		3/5/08		0.043						1/14/08		0.025						7/22/08		0.08		73		37		0.24		0.32		0.42		61		1200																				8/4/08		0.06		72		40

		3/6/08		0.043						1/15/08		0.03						7/23/08		0.09		71		38		0.28		0.32		0.44		61		1200																				8/5/08		0.06		73		39

		3/7/08		0.043						1/16/08		0.03						7/24/08		0.09		72		36		0.26		0.32		0.46		61		1200																				8/6/08		0.06		71		41

		3/10/08		0.043						1/17/08		0.03						7/25/08		0.09		72		36		0.24		0.32		0.42		61		1200																				8/7/08		0.06		72		39

		3/11/08		0.042						1/18/08		0.025						7/26/08		0.09		71		37		0.28		0.32		0.46		61		1200																				8/8/08		0.05		72		40

		3/12/08		0.039						1/21/08		0.035						7/28/08		0.09		71		38		0.3		0.32		0.46		61		1200																				8/9/08		0.055		71		40

		3/13/08		0.03						1/22/08		0.03						7/29/08		0.06		70		40		0.3		0.32		0.44																								8/11/08		0.06		71		39

		3/14/08		0.041						1/23/08		0.035						7/30/08		0.07		71		38		0.3		0.32		0.48																								8/12/08		0.065		71		41

		3/17/08		0.047						1/24/08		0.03						7/31/08		0.075		71		38																														8/13/08		0.055		71		41

		3/18/08		0.048						1/25/08		0.035						8/1/08		0.07		72		37		0.3		0.32		0.48																								8/14/08		0.05		71		41

		3/19/08		0.047						1/28/08		0.035						8/2/08		0.07		72		38																														8/15/08		0.05		72		39

		3/20/08		0.042						1/29/08		0.035						8/4/08		0.07		73		37		0.28		0.32		0.44																								8/16/08		0.06		72		40

		3/21/08		0.043						1/30/08		0.025						8/5/08		0.06		73		37		0.28		0.34		0.48																								8/18/08		0.06		72		41

		3/22/08		0.045						1/31/08		0.03						8/6/08		0.07		71		38		0.28		0.32		0.48																								8/19/08		0.06		72		41

		3/24/08		0.043						2/1/08		0.03						8/7/08		0.06		71		38		0.32		0.32		0.48																								8/20/08		0.06		71		40

		3/25/08		0.045						2/4/08		0.035						8/8/08		0.06		72		38		0.26		0.32		0.44																								8/21/08		0.05		73		44

		3/26/08		0.043						2/5/08		0.025						8/9/08		0.06		71		40																														8/22/08		0.05		72		40

		3/27/08		0.04						2/6/08		0.035						8/11/08		0.07		71		38		0.28		0.32		0.44																								8/23/08		0.05		72		41

		3/28/08		0.04						2/7/08		0.025						8/12/08		0.07		71		40		0.28		0.32		0.44																								8/25/08		0.06		71		40

		3/31/08		0.045						2/8/08		0.02						8/13/08		0.065		71		40		0.28		0.3		0.46																								8/26/08		0.06		70		39

		4/1/08		0.045						2/9/08		0.02						8/14/08		0.05		71		39		0.26		0.32		0.42																								8/27/08		0.05		71		40

		4/2/08		0.045						2/14/08		0.035						8/15/08		0.06		71		38		0.26		0.32		0.42																								8/28/08		0.055		71		40

		4/3/08		0.04						2/15/08		0.033						8/16/08		0.06		71		40																														8/29/08		0.055		72		39

		4/4/08		0.045						2/19/08		0.036						8/18/08		0.065		71		41		0.26		0.32		0.42																								9/2/08		0.055		69		32

		4/5/08		0.045						2/20/08		0.037						8/19/08		0.06		72		40		0.28		0.32		0.44																								9/3/08		0.055		72		39

		4/7/08		0.045						2/21/08		0.037						8/20/08		0.06		71		31		0.26		0.32		0.42																								9/4/08		0.055		70		38

		4/8/08		0.04						2/22/08		0.034						8/21/08		0.05		73		42		0.28		0.32		0.48																								9/5/08		0.06		71		36

		4/9/08		0.04						2/25/08		0.044						8/22/08		0.06		71		38		0.24		0.32		0.44																								9/6/08		0.06		71		39

		4/10/08		0.04						2/26/08		0.043						8/23/08		0.06		72		40																														9/8/08		0.06		74		38

		4/11/08		0.045						2/27/08		0.043						8/25/08		0.06		71		40		0.26		0.32		0.46																								9/9/08		0.06		72		40

		4/14/08		0.045						2/28/08		0.044						8/26/08		0.06		70		38		0.26		0.32		0.44																								9/10/08		0.06		72		40

		4/15/08		0.04						2/29/08		0.046						8/27/08		0.05		71		38		0.26		0.32		0.44																								9/11/08		0.06		71		41

		4/16/08		0.04						3/3/08		0.045						8/28/08		0.05		71		38		0.26		0.3		0.44																								9/12/08		0.06		70		40

		4/17/08		0.04						3/4/08		0.044						8/29/08		0.065		72		38		0.28		0.3		0.44																								9/13/08		0.06		70		41

		4/18/08		0.04						3/5/08		0.039						9/2/08		0.06		69		31		0.24		0.32		0.42																								9/15/08		0.06		70		40

		4/19/08		0.05						3/6/08		0.039						9/3/08		0.06		72		40		0.28		0.32		0.44																								9/16/08		0.06		71		40

		4/21/08		0.05						3/7/08		0.038						9/4/08		0.06		70		37		0.26		0.32		0.44																								9/17/08		0.06		70		30

		4/22/08		0.045						3/10/08		0.037						9/5/08		0.06		70		36		0.26		0.32		0.44																								9/18/08		0.06		71		37

		4/23/08		0.04						3/11/08		0.04						9/6/08		0.06		70		38																														9/19/08		0.06		72		43

		4/24/08		0.04						3/12/08		0.036						9/8/08		0.06		72		41		0.24		0.32		0.42																								9/20/08		0.06		72		42

		4/25/08		0.04						3/14/08		0.039						9/9/08		0.06		71		40		0.24		0.32		0.44																								9/22/08		0.06		71		39

		4/30/08		0.04						3/17/08		0.038						9/10/08		0.06		70		41		0.28		0.32		0.46																								9/23/08		0.065		72		37

		5/1/08		0.04						3/18/08		0.038						9/11/08		0.06		70		41		0.26		0.32		0.42																								9/24/08		0.055		70		33

		5/2/08		0.04						3/19/08		0.037						9/12/08		0.06		70		40		0.28		0.32		0.48																								9/25/08		0.06		72		32

		5/3/08		0.045						3/20/08		0.039						9/13/08		0.06		70		40																														9/26/08		0.06		72		43

		5/5/08		0.04						3/21/08		0.038						9/15/08		0.06		69		41		0.3		0.32		0.44																								9/27/08		0.06		70		37

		5/6/08		0.04						3/24/08		0.038						9/16/08		0.06		69		41		0.24		0.3		0.42																								9/29/08		0.06		71		40

		5/7/08		0.045						3/25/08		0.038						9/17/08		0.07		69		38		0.26		0.32		0.46																								9/30/08		0.06		75		33

		5/8/08		0.04						3/26/08		0.039						9/18/08		0.06		70		38		0.26		0.32		0.42

		5/9/08		0.04						3/27/08		0.045						9/19/08		0.06		73		42		0.26		0.32		0.42

		5/10/08		0.04						3/28/08		0.04						9/20/08		0.05		73		41

		5/12/08		0.04						3/31/08		0.04						9/22/08		0.06		71		38		0.24		0.32		0.44

		5/13/08		0.04						4/1/08		0.04						9/23/08		0.065		71		37		0.26		0.32		0.44

		5/14/08		0.04						4/2/08		0.04						9/24/08		0.055		71		32		0.26		0.32		0.42

		5/15/08		0.04						4/3/08		0.035						9/25/08		0.06		71		32		0.28		0.32		0.48

		5/16/08		0.04						4/4/08		0.04						9/26/08		0.055		73		41		0.24		0.32		0.44

		5/19/08		0.04						4/5/08		0.035						9/27/08		0.06		71		35

		5/20/08		0.04						4/7/08		0.04						9/29/08		0.06		70		40		0.26		0.32		0.44

		5/21/08		0.04						4/8/08		0.04						9/30/08		0.05		71		36		0.24		0.32		0.44

		5/22/08		0.04						4/9/08		0.035						10/1/08								0.24		0.32		0.44

		5/23/08		0.04						4/10/08		0.04						10/2/08								0.24		0.32		0.44

		5/27/08		0.04						4/11/08		0.04

		5/28/08		0.04						4/14/08		0.04

		5/29/08		0.05						4/15/08		0.04

		5/30/08		0.04						4/16/08		0.04

		5/31/08		0.045						4/17/08		0.04

		6/2/08		0.04						4/18/08		0.035

		6/3/08		0.04						4/19/08		0.05

		6/4/08		0.04						4/21/08		0.05

		6/5/08		0.04						4/22/08		0.04

		6/6/08		0.04						4/23/08		0.04

		6/9/08		0.04						4/24/08		0.04

		6/10/08		0.04						4/25/08		0.04

		6/11/08		0.04						4/30/08		0.04

		6/12/08		0.04						5/1/08		0.04

		6/13/08		0.04						5/2/08		0.04

		6/16/08		0.04						5/3/08		0.04

		6/17/08		0.04						5/5/08		0.04

		6/18/08		0.04						5/6/08		0.04

		6/19/08		0.04						5/7/08		0.04

		6/20/08		0.04						5/8/08		0.04

		6/21/08		0.035						5/9/08		0.04

		6/23/08		0.035						5/10/08		0.04

		6/24/08		0.04						5/12/08		0.04

		6/25/08		0.035						5/13/08		0.04

		6/26/08		0.035						5/14/08		0.04

		6/27/08		0.035						5/15/08		0.04

		6/30/08		0.035						5/16/08		0.04

		7/1/08		0.03						5/19/08		0.04

		7/2/08		0.03						5/20/08		0.04

		7/3/08		0.035						5/21/08		0.04

		7/7/08		0.03						5/22/08		0.04

		7/8/08		0.03						5/23/08		0.04

		7/9/08		0.035						5/27/08		0.04

		7/10/08		0.035						5/28/08		0.04

		7/11/08		0.035						5/29/08		0.04

		7/12/08		0.03						5/30/08		0.04

		7/14/08		0.025						6/2/08		0.04

		7/15/08		0.03						6/3/08		0.035

		7/16/08		0.03						6/4/08		0.035

		7/17/08		0.03						6/5/08		0.035

		7/18/08		0.04						6/6/08		0.035

		7/19/08		0.03						6/9/08		0.035

		7/21/08		0.03						6/10/08		0.035

		7/22/08		0.03						6/11/08		0.035

		7/23/08		0.02						6/12/08		0.035

		7/24/08		0.025						6/13/08		0.04

		7/25/08		0.01						6/16/08		0.035

		7/26/08		0.01						6/17/08		0.045

		7/28/08		0.01						6/18/08		0.045

		7/29/08		0.03						6/19/08		0.045

		7/30/08		0.01						6/20/08		0.035

		7/31/08		0.015						6/21/08		0.035

		8/1/08		0.025						6/23/08		0.035

		8/2/08		0.03						6/24/08		0.045

		8/4/08		0.03						6/25/08		0.035

		8/5/08		0.03						6/26/08		0.035

		8/6/08		0.04						6/27/08		0.035

		8/7/08		0.035						6/30/08		0.035

		8/8/08		0.03						7/1/08		0.04

		8/9/08		0.03						7/2/08		0.04

		8/11/08		0.035						7/3/08		0.04

		8/12/08		0.035						7/7/08		0.04

		8/13/08		0.035						7/8/08		0.04

		8/14/08		0.03						7/9/08		0.04

		8/15/08		0.03						7/10/08		0.04

		8/16/08		0.03						7/11/08		0.04

		8/18/08		0.03						7/12/08		0.04

		8/19/08		0.04						7/14/08		0.04

		8/20/08		0.03						7/15/08		0.04

		8/21/08		0.03						7/16/08		0.04

		8/22/08		0.03						7/17/08		0.04

		8/23/08		0.03						7/18/08		0.04

		8/25/08		0.03						7/19/08		0.04

		8/26/08		0.03						7/21/08		0.04

		8/27/08		0.03						7/22/08		0.04

		8/28/08		0.03						7/23/08		0.04

		8/29/08		0.03						7/24/08		0.04

		9/2/08		0.03						7/25/08		0.04

		9/3/08		0.03						7/26/08		0.04

		9/4/08		0.03						7/28/08		0.04

		9/5/08		0.03						7/29/08		0.04

		9/6/08		0.03						7/30/08		0.04

		9/8/08		0.03						7/31/08		0.04

		9/9/08		0.03						8/1/08		0.045

		9/10/08		0.03						8/2/08		0.04

		9/11/08		0.03						8/4/08		0.04

		9/12/08		0.03						8/5/08		0.04

		9/13/08		0.03						8/6/08		0.05

		9/15/08		0.035						8/7/08		0.04

		9/16/08		0.03						8/8/08		0.04

		9/17/08		0.03						8/9/08		0.04

		9/18/08		0.03						8/11/08		0.04

		9/19/08		0.03						8/12/08		0.04

		9/20/08		0.03						8/13/08		0.04

		9/22/08		0.03						8/14/08		0.04

		9/23/08		0.03						8/15/08		0.04

		9/24/08		0.025						8/16/08		0.04

		9/25/08		0.03						8/18/08		0.04

		9/26/08		0.03						8/19/08		0.04

		9/27/08		0.03						8/20/08		0.04

		9/29/08		0.03						8/21/08		0.04

		9/30/08		0.03						8/22/08		0.04

		10/1/08		0.03						8/23/08		0.04

		10/2/08		0.03						8/25/08		0.04

		10/3/08		0.03						8/26/08		0.04

		10/4/08		0.03						8/27/08		0.04

		10/6/08		0.03						8/28/08		0.04

		10/7/08		0.04						8/29/08		0.04

		10/8/08		0.03						9/2/08		0.04

		10/9/08		0.03						9/3/08		0.04

		10/10/08		0.03						9/4/08		0.04

		10/11/08		0.03						9/5/08		0.04

		10/13/08		0.03						9/6/08		0.04

		10/14/08		0.03						9/8/08		0.04

		10/15/08		0.03						9/9/08		0.04

		10/16/08		0.04						9/10/08		0.04

		10/17/08		0.03						9/11/08		0.04

		10/18/08		0.03						9/12/08		0.04

		10/20/08		0.03						9/13/08		0.04

		10/21/08		0.03						9/15/08		0.04

		10/22/08		0.03						9/16/08		0.04

		10/23/08		0.03						9/17/08		0.04

		10/24/08		0.03						9/18/08		0.04

		10/25/08		0.03						9/19/08		0.04

		10/27/08		0.03						9/20/08		0.04

		10/28/08		0.03						9/22/08		0.04

		10/29/08		0.03						9/23/08		0.045

		10/30/08		0.03						9/24/08		0.045

		10/31/08		0.03						9/25/08		0.045

		11/3/08		0.03						9/26/08		0.04

		11/4/08		0.03						9/27/08		0.04

										9/29/08		0.04

										9/30/08		0.04

										10/1/08		0.04

										10/2/08		0.04

										10/3/08		0.04

										10/4/08		0.04

										10/6/08		0.04

										10/7/08		0.05

										10/8/08		0.045

										10/9/08		0.04

										10/10/08		0.04

										10/11/08		0.04

										10/13/08		0.045

										10/14/08		0.04

										10/15/08		0.045

										10/16/08		0.04

										10/17/08		0.04

										10/18/08		0.04

										10/20/08		0.04

										10/21/08		0.04

										10/22/08		0.04

										10/23/08		0.04

										10/24/08		0.04

										10/25/08		0.04

										10/27/08		0.04

										10/28/08		0.04

										10/29/08		0.04

										10/30/08		0.04

										10/31/08		0.04

										11/3/08		0.04

										11/4/08		0.04

										11/5/08		0.05

										11/6/08		0.04

										11/7/08		0.04

										11/8/08		0.045

										11/10/08		0.04

										11/11/08		0.04

										11/12/08		0.04

										11/13/08		0.04

										11/14/08		0.04

										11/15/08		0.04

										11/17/08		0.04

										11/18/08		0.04

										11/19/08		0.04

										11/20/08		0.045

										11/21/08		0.045

										11/22/08		0.04

										11/24/08		0.04

										11/25/08		0.04

										11/26/08		0.04

										12/1/08		0.04





CER Pressure

		



Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)

R&D Bio-Safety Cabinet South (left axis)

Date

Diff. Pressure (Water Column In.)

Mfg Bio-Safety Cabinet South CFM

Figure 7.  CER2 Bio-Safety Cabinet Differential Pressure Daily Run Chart



Conf-Rel

		



Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

R&D Bio-Safety Cabinet South (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)

Date

Diff. Pressure (Water Column In.)

Mfg Bio-Safety Cabinet (cfm)

Figure 8.  Bio-Safety Cabinet Differential Pressure - Monthly Average



Temp-Humid

		



CER1

CER Change Room

CER2

CER3

CER Alert Level

CER Action Level

Date

Diff. Pressure (Water Column In.)

Figure 5.  CER Differential Pressure Daily Run Chart



Sheet1

		



CER1

CER Change Room

CER 2

CER 3

CER Alert Level

CER Action Level

Date

Diff. Pressure (Water Column In.)

Figure 6.  CER Differential Pressure - Monthly Average



		TO:		DCN 0273 File

		FROM:		Andy Pearson

		DATE:		3/3/07

		RE:		Confidence and Reliability Levels for CER Monitoring

		The table below shows 95/95, and 95/99 confidence/reliability levels for  CER and Change Room

		monitoring carried out from Feb 06 to Feb 07.

		Recommended action and alert levels correspond to worst case 95/95 (alert) and 95/99 (action) values.

						95/95 Limit		Recommended Alert Level		95/99 Limit		95/99 Limit		Recommended Action Level

		Airstrips (utl)		CER1		17		35		21		21		45

				CER2		15				20		20

				CER3		34				43		43

		Contact Plates (utl)		CER1		5		6		6		6		7

				CER2		4				5		5

				CER3		6				7		7

		0.5um Particle Counts (utl)		CER1		1092		3800		1324		1324		4500

				CER3		3797				4549		4549

				CER2		1232		1250		1495		1495		1500

		5.0um Particle Counts (utl)		CER1		159		410		200		200		500

				CER3		410				497		497

				CER2		91		90		107		107		105

		Pressure Differential (ltl)		CER1		0.011		0.030		0.003		0.003		0.005

				CER1/2 Chg Rm		0.021				0.013		0.013

				CER2		-0.021				-0.045		-0.045

				CER3		0.040				0.035		0.035

		Andy Pearson

		Sr.Quality Engineer





		CER2								CER1								CER3								QA

		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 2 Temperature(°F)		CER 2 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 1 Temperature(°F)		CER 1 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 3 Temperature(°F)		CER 3 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		QA Temperature(°F)		QA Humidity(%)

		29-Aug-07		16:07:10		75.81		46.5		29-Aug-07		16:06:20		76.4		48		29-Aug-07		16:07:53		75.81		74		9-Oct-07		16:25:59		78.2		33

		29-Aug-07		18:07:10		74.01		40.5		29-Aug-07		18:06:20		70.41		41.5		29-Aug-07		18:07:53		74.6		41.5		9-Oct-07		18:25:59		75.81		35.5

		29-Aug-07		20:07:10		74.6		40.5		29-Aug-07		20:06:20		71.6		43.5		29-Aug-07		20:07:53		73.4		43		9-Oct-07		20:25:59		75.2		34.5

		29-Aug-07		22:07:10		75.81		40.5		29-Aug-07		22:06:20		71.6		46.5		29-Aug-07		22:07:53		74.6		42		9-Oct-07		22:25:59		74.6		35

		30-Aug-07		0:07:10		75.81		40.5		30-Aug-07		0:06:20		71.6		47.5		30-Aug-07		0:07:53		75.2		41.5		10-Oct-07		0:25:59		73.4		36

		30-Aug-07		2:07:10		75.81		41		30-Aug-07		2:06:20		71		49		30-Aug-07		2:07:53		75.81		41.5		10-Oct-07		2:25:59		72.8		37

		30-Aug-07		4:07:10		75.2		42.5		30-Aug-07		4:06:20		71		51		30-Aug-07		4:07:53		75.2		41.5		10-Oct-07		4:25:59		72.21		38

		30-Aug-07		6:07:10		75.81		41		30-Aug-07		6:06:20		71.6		46.5		30-Aug-07		6:07:53		75.2		42		10-Oct-07		6:25:59		72.21		39

		30-Aug-07		8:07:10		75.81		45.5		30-Aug-07		8:06:20		72.21		55.5		30-Aug-07		8:07:53		75.2		44		10-Oct-07		8:25:59		71.6		41.5

		30-Aug-07		10:07:10		74.6		43.5		30-Aug-07		10:06:20		72.21		41.5		30-Aug-07		10:07:53		74.6		45		10-Oct-07		10:25:59		72.8		42.5

		30-Aug-07		12:07:10		74.6		43.5		30-Aug-07		12:06:20		71.6		46		30-Aug-07		12:07:53		72.8		45.5		10-Oct-07		12:25:59		74.01		42.5

		30-Aug-07		14:07:10		74.6		43		30-Aug-07		14:06:20		72.21		43		30-Aug-07		14:07:53		72.21		44.5		10-Oct-07		14:25:59		75.2		43

		30-Aug-07		16:07:10		75.2		43.5		30-Aug-07		16:06:20		72.21		43.5		30-Aug-07		16:07:53		72.8		44.5		10-Oct-07		16:25:59		75.2		42

		30-Aug-07		18:07:10		75.2		45		30-Aug-07		18:06:20		70.41		49.5		30-Aug-07		18:07:53		71.6		46		10-Oct-07		18:25:59		75.2		41

		30-Aug-07		20:07:10		75.2		45.5		30-Aug-07		20:06:20		71.6		52		30-Aug-07		20:07:53		75.81		45		10-Oct-07		20:25:59		74.01		42.5

		30-Aug-07		22:07:10		76.4		45		30-Aug-07		22:06:20		71		53.5		30-Aug-07		22:07:53		75.2		45		10-Oct-07		22:25:59		73.4		43.5

		31-Aug-07		0:07:10		76.4		44.5		31-Aug-07		0:06:20		71		53.5		31-Aug-07		0:07:53		75.2		44.5		11-Oct-07		0:25:59		72.8		44.5

		31-Aug-07		2:07:10		75.81		44.5		31-Aug-07		2:06:20		71.6		53		31-Aug-07		2:07:53		75.2		45.5		11-Oct-07		2:25:59		72.21		45

		31-Aug-07		4:07:10		75.81		45		31-Aug-07		4:06:20		71.6		53		31-Aug-07		4:07:53		72.8		41.5		11-Oct-07		4:25:59		71.6		45.5

		31-Aug-07		6:07:10		75.81		45.5		31-Aug-07		6:06:20		72.21		54		31-Aug-07		6:07:53		71		54.5		11-Oct-07		6:25:59		72.21		45

		31-Aug-07		8:07:10		75.2		44		31-Aug-07		8:06:20		72.21		43.5		31-Aug-07		8:07:53		71.6		50.5		11-Oct-07		8:25:59		71.6		46.5

		31-Aug-07		10:07:10		74.6		45.5		31-Aug-07		10:06:20		72.21		49.5		31-Aug-07		10:07:53		72.21		44.5		11-Oct-07		10:25:59		72.8		48.5

		31-Aug-07		12:07:10		74.6		49.5		31-Aug-07		12:06:20		71.6		60.5		31-Aug-07		12:07:53		72.21		45		11-Oct-07		12:25:59		74.6		44.5

		31-Aug-07		14:07:10		74.6		45.5		31-Aug-07		14:06:20		71.6		44		31-Aug-07		14:07:53		72.8		47		11-Oct-07		14:25:59		75.81		42.5

		31-Aug-07		16:07:10		74.6		48		31-Aug-07		16:06:20		71.6		56.5		31-Aug-07		16:07:53		72.8		43.5		11-Oct-07		16:25:59		76.4		42.5

		31-Aug-07		18:07:10		75.2		46.5		31-Aug-07		18:06:20		70.41		54.5		31-Aug-07		18:07:53		71		50		11-Oct-07		18:25:59		76.4		41

		31-Aug-07		20:07:10		75.2		46		31-Aug-07		20:06:20		71.6		53		31-Aug-07		20:07:53		74.6		50		11-Oct-07		20:25:59		74.6		41.5

		31-Aug-07		22:07:10		76.4		44		31-Aug-07		22:06:20		71.6		48.5		31-Aug-07		22:07:53		75.2		47		11-Oct-07		22:25:59		74.6		41

		1-Sep-07		0:07:10		76.4		42.5		1-Sep-07		0:06:20		71.6		46.5		1-Sep-07		0:07:53		75.2		45.5		12-Oct-07		0:25:59		73.4		41

		1-Sep-07		2:07:10		76.4		44		1-Sep-07		2:06:20		71.6		53		1-Sep-07		2:07:53		74.6		45.5		12-Oct-07		2:25:59		71.6		41

		1-Sep-07		4:07:10		76.4		44		1-Sep-07		4:06:20		71.6		53		1-Sep-07		4:07:53		72.8		50		12-Oct-07		4:25:59		71		41.5

		1-Sep-07		6:07:10		76.4		45		1-Sep-07		6:06:20		73.4		56.5		1-Sep-07		6:07:53		71.6		45		12-Oct-07		6:25:59		70.41		41.5

		1-Sep-07		8:07:10		75.2		42.5		1-Sep-07		8:06:20		72.21		41		1-Sep-07		8:07:53		71.6		53		12-Oct-07		8:25:59		69.8		41.5

		1-Sep-07		10:07:10		74.6		43.5		1-Sep-07		10:06:20		71.6		42		1-Sep-07		10:07:53		72.21		43.5		12-Oct-07		10:25:59		71.6		44.5

		1-Sep-07		12:07:10		74.6		51.5		1-Sep-07		12:06:20		70.41		64		1-Sep-07		12:07:53		71.6		45.5		12-Oct-07		12:25:59		74.6		43.5

		1-Sep-07		14:07:10		74.6		52		1-Sep-07		14:06:20		70.41		64.5		1-Sep-07		14:07:53		71		50.5		12-Oct-07		14:25:59		75.2		42.5

		1-Sep-07		16:07:10		74.6		46.5		1-Sep-07		16:06:20		70.41		52.5		1-Sep-07		16:07:53		71		57.5		12-Oct-07		16:25:59		75.2		42.5

		1-Sep-07		18:07:10		74.6		45.5		1-Sep-07		18:06:20		70.41		50.5		1-Sep-07		18:07:53		71		58.5		12-Oct-07		18:25:59		74.6		40

		1-Sep-07		20:07:10		74.6		49.5		1-Sep-07		20:06:20		71		56		1-Sep-07		20:07:53		71		55.5		12-Oct-07		20:25:59		74.01		40.5

		1-Sep-07		22:07:10		75.2		47		1-Sep-07		22:06:20		71		56		1-Sep-07		22:07:53		72.21		50.5		12-Oct-07		22:25:59		74.01		40

		2-Sep-07		0:07:10		75.2		45		2-Sep-07		0:06:20		71.6		52.5		2-Sep-07		0:07:53		72.21		50		13-Oct-07		0:25:59		72.8		40.5

		2-Sep-07		2:07:10		75.2		44.5		2-Sep-07		2:06:20		71		51		2-Sep-07		2:07:53		71.6		50		13-Oct-07		2:25:59		71.6		41

		2-Sep-07		4:07:10		74.6		44		2-Sep-07		4:06:20		70.41		51.5		2-Sep-07		4:07:53		70.41		49.5		13-Oct-07		4:25:59		71		42.5

		2-Sep-07		6:07:10		74.01		41.5		2-Sep-07		6:06:20		71		45.5		2-Sep-07		6:07:53		69.2		48.5		13-Oct-07		6:25:59		71.6		43

		2-Sep-07		8:07:10		73.4		44		2-Sep-07		8:06:20		69.8		51		2-Sep-07		8:07:53		69.2		51		13-Oct-07		8:25:59		71		46

		2-Sep-07		10:07:10		74.01		48.5		2-Sep-07		10:06:20		70.41		57.5		2-Sep-07		10:07:53		71		48.5		13-Oct-07		10:25:59		72.21		47.5

		2-Sep-07		12:07:10		74.6		49.5		2-Sep-07		12:06:20		70.41		59.5		2-Sep-07		12:07:53		71		53		13-Oct-07		12:25:59		72.8		47

		2-Sep-07		14:07:10		75.81		49.5		2-Sep-07		14:06:20		70.41		60.5		2-Sep-07		14:07:53		71		60		13-Oct-07		14:25:59		72.21		47.5

		2-Sep-07		16:07:10		76.4		43.5		2-Sep-07		16:06:20		70.41		47.5		2-Sep-07		16:07:53		71		46.5		13-Oct-07		16:25:59		74.01		47

		2-Sep-07		18:07:10		76.4		46.5		2-Sep-07		18:06:20		69.8		55.5		2-Sep-07		18:07:53		71		58		13-Oct-07		18:25:59		74.6		44.5

		2-Sep-07		20:07:10		77		44		2-Sep-07		20:06:20		71		52.5		2-Sep-07		20:07:53		74.01		47		13-Oct-07		20:25:59		72.8		45.5

		2-Sep-07		22:07:10		77		41.5		2-Sep-07		22:06:20		71.6		51		2-Sep-07		22:07:53		74.6		44.5		13-Oct-07		22:25:59		71.6		45

		3-Sep-07		0:07:10		76.4		41		3-Sep-07		0:06:20		71		50.5		3-Sep-07		0:07:53		74.01		44.5		14-Oct-07		0:25:59		71		45

		3-Sep-07		2:07:10		75.81		40		3-Sep-07		2:06:20		71		44		3-Sep-07		2:07:53		72.21		45.5		14-Oct-07		2:25:59		69.8		43.5

		3-Sep-07		4:07:10		75.2		39		3-Sep-07		4:06:20		71		41.5		3-Sep-07		4:07:53		71		46.5		14-Oct-07		4:25:59		69.2		43

		3-Sep-07		6:07:10		75.2		40		3-Sep-07		6:06:20		71.6		46		3-Sep-07		6:07:53		69.2		47.5		14-Oct-07		6:25:59		69.2		42.5

		3-Sep-07		8:07:10		74.01		42		3-Sep-07		8:06:20		69.8		49		3-Sep-07		8:07:53		68.61		49.5		14-Oct-07		8:25:59		69.2		41

		3-Sep-07		10:07:10		74.01		43		3-Sep-07		10:06:20		70.41		48		3-Sep-07		10:07:53		70.41		52		14-Oct-07		10:25:59		71		44

		3-Sep-07		12:07:10		74.6		41.5		3-Sep-07		12:06:20		70.41		43.5		3-Sep-07		12:07:53		71		43.5		14-Oct-07		12:25:59		72.21		45

		3-Sep-07		14:07:10		75.2		43		3-Sep-07		14:06:20		70.41		47		3-Sep-07		14:07:53		71.6		52		14-Oct-07		14:25:59		74.01		44.5

		3-Sep-07		16:07:10		75.81		44.5		3-Sep-07		16:06:20		69.8		49.5		3-Sep-07		16:07:53		71.6		52		14-Oct-07		16:25:59		75.2		44.5

		3-Sep-07		18:07:10		76.4		40.5		3-Sep-07		18:06:20		70.41		47		3-Sep-07		18:07:53		71		45		14-Oct-07		18:25:59		75.81		44

		3-Sep-07		20:07:10		77.61		40		3-Sep-07		20:06:20		71.6		45.5		3-Sep-07		20:07:53		75.81		42		14-Oct-07		20:25:59		74.6		44.5

		3-Sep-07		22:07:10		77		41		3-Sep-07		22:06:20		71.6		50.5		3-Sep-07		22:07:53		74.6		43.5		14-Oct-07		22:25:59		73.4		45

		4-Sep-07		0:07:10		76.4		40.5		4-Sep-07		0:06:20		71		50		4-Sep-07		0:07:53		74.6		43.5		15-Oct-07		0:25:59		72.8		45.5

		4-Sep-07		2:07:10		75.81		40		4-Sep-07		2:06:20		71		49.5		4-Sep-07		2:07:53		72.8		44		15-Oct-07		2:25:59		72.21		46

		4-Sep-07		4:07:10		75.81		39.5		4-Sep-07		4:06:20		71.6		47		4-Sep-07		4:07:53		71.6		45		15-Oct-07		4:25:59		71.6		46

		4-Sep-07		6:07:10		74.6		40		4-Sep-07		6:06:20		71		47.5		4-Sep-07		6:07:53		69.8		46.5		15-Oct-07		6:25:59		71		46.5

		4-Sep-07		8:07:10		74.01		39.5		4-Sep-07		8:06:20		70.41		42		4-Sep-07		8:07:53		69.8		48.5		15-Oct-07		8:25:59		70.41		47

		4-Sep-07		10:07:10		74.01		45.5		4-Sep-07		10:06:20		69.8		53.5		4-Sep-07		10:07:53		71		52		15-Oct-07		10:25:59		69.8		47.5

		4-Sep-07		12:07:10		74.01		48		4-Sep-07		12:06:20		69.8		55		4-Sep-07		12:07:53		71		45.5		15-Oct-07		12:25:59		70.41		48.5

		4-Sep-07		14:07:10		74.01		49		4-Sep-07		14:06:20		70.41		52		4-Sep-07		14:07:53		71		58.5		15-Oct-07		14:25:59		71.6		49

		4-Sep-07		16:07:10		74.6		47.5		4-Sep-07		16:06:20		70.41		50		4-Sep-07		16:07:53		71		49		15-Oct-07		16:25:59		73.4		48

		4-Sep-07		18:07:10		74.6		47.5		4-Sep-07		18:06:20		70.41		50		4-Sep-07		18:07:53		71		49.5		15-Oct-07		18:25:59		74.6		45.5

		4-Sep-07		20:07:10		75.2		50		4-Sep-07		20:06:20		71		58.5		4-Sep-07		20:07:53		71.6		55.5		15-Oct-07		20:25:59		72.8		46

		4-Sep-07		22:07:10		75.81		47.5		4-Sep-07		22:06:20		71.6		56		4-Sep-07		22:07:53		74.01		50		15-Oct-07		22:25:59		71.6		46

		5-Sep-07		0:07:10		75.81		46.5		5-Sep-07		0:06:20		71		56.5		5-Sep-07		0:07:53		74.01		49.5		16-Oct-07		0:25:59		71		46

		5-Sep-07		2:07:10		75.81		44.5		5-Sep-07		2:06:20		71		47.5		5-Sep-07		2:07:53		72.8		50.5		16-Oct-07		2:25:59		70.41		46.5

		5-Sep-07		4:07:10		75.2		45.5		5-Sep-07		4:06:20		71		55		5-Sep-07		4:07:53		71.6		49		16-Oct-07		4:25:59		69.8		46

		5-Sep-07		6:07:10		75.2		47		5-Sep-07		6:06:20		71.6		55		5-Sep-07		6:07:53		70.41		48		16-Oct-07		6:25:59		70.41		46.5

		5-Sep-07		8:07:10		75.2		45		5-Sep-07		8:06:20		72.21		45.5		5-Sep-07		8:07:53		71		53		16-Oct-07		8:25:59		69.8		47.5

		5-Sep-07		10:07:10		74.6		51.5		5-Sep-07		10:06:20		72.21		55		5-Sep-07		10:07:53		72.8		46.5		16-Oct-07		10:25:59		71		49.5

		5-Sep-07		12:07:10		74.01		50.5		5-Sep-07		12:06:20		71		56		5-Sep-07		12:07:53		72.21		57.5		16-Oct-07		12:25:59		72.21		52

		5-Sep-07		14:07:10		74.01		48		5-Sep-07		14:06:20		71.6		54.5		5-Sep-07		14:07:53		72.21		54		16-Oct-07		14:25:59		73.4		52.5

		5-Sep-07		16:07:10		74.01		49		5-Sep-07		16:06:20		71		54		5-Sep-07		16:07:53		72.21		51		16-Oct-07		16:25:59		75.2		47.5

		5-Sep-07		18:07:10		74.6		49		5-Sep-07		18:06:20		70.41		60		5-Sep-07		18:07:53		71.6		48.5		16-Oct-07		18:25:59		75.81		47.5

		5-Sep-07		20:07:10		74.6		48		5-Sep-07		20:06:20		71.6		55		5-Sep-07		20:07:53		71		58		16-Oct-07		20:25:59		74.01		48.5

		5-Sep-07		22:07:10		75.81		46.5		5-Sep-07		22:06:20		71		55.5		5-Sep-07		22:07:53		75.2		47		16-Oct-07		22:25:59		73.4		49

		6-Sep-07		0:07:10		75.81		43.5		6-Sep-07		0:06:20		71.6		50.5		6-Sep-07		0:07:53		74.6		47		17-Oct-07		0:25:59		72.21		49

		6-Sep-07		2:07:10		75.2		44.5		6-Sep-07		2:06:20		71		52.5		6-Sep-07		2:07:53		73.4		47		17-Oct-07		2:25:59		71		48

		6-Sep-07		4:07:10		75.2		43.5		6-Sep-07		4:06:20		71.6		51		6-Sep-07		4:07:53		72.21		48.5		17-Oct-07		4:25:59		70.41		47.5

		6-Sep-07		6:07:10		75.2		42.5		6-Sep-07		6:06:20		71.6		48.5		6-Sep-07		6:07:53		71		50.5		17-Oct-07		6:25:59		69.8		46

		6-Sep-07		8:07:10		75.2		45.5		6-Sep-07		8:06:20		72.21		52		6-Sep-07		8:07:53		71.6		48.5		17-Oct-07		8:25:59		69.2		46.5

		6-Sep-07		10:07:10		75.2		43.5		6-Sep-07		10:06:20		72.21		46		6-Sep-07		10:07:53		72.21		49.5		17-Oct-07		10:25:59		70.41		49

		6-Sep-07		12:07:10		74.6		41.5		6-Sep-07		12:06:20		71.6		42.5		6-Sep-07		12:07:53		72.21		52		17-Oct-07		12:25:59		71.6		51.5

		6-Sep-07		14:07:10		74.01		40		6-Sep-07		14:06:20		71.6		40.5		6-Sep-07		14:07:53		72.21		42		17-Oct-07		14:25:59		72.21		53

		6-Sep-07		16:07:10		74.6		40		6-Sep-07		16:06:20		71.6		43		6-Sep-07		16:07:53		72.21		40		17-Oct-07		16:25:59		72.8		54

		6-Sep-07		18:07:10		74.6		38		6-Sep-07		18:06:20		69.8		42		6-Sep-07		18:07:53		72.21		37.5		17-Oct-07		18:25:59		74.01		50.5

		6-Sep-07		20:07:10		75.2		38		6-Sep-07		20:06:20		71.6		43		6-Sep-07		20:07:53		75.2		39.5		17-Oct-07		20:25:59		72.21		48.5

		6-Sep-07		22:07:10		75.81		38.5		6-Sep-07		22:06:20		71.6		45.5		6-Sep-07		22:07:53		75.2		39.5		17-Oct-07		22:25:59		71		48

		7-Sep-07		0:07:10		75.81		39		7-Sep-07		0:06:20		71.6		46.5		7-Sep-07		0:07:53		75.2		39.5		18-Oct-07		0:25:59		70.41		47

		7-Sep-07		2:07:10		75.81		39		7-Sep-07		2:06:20		71.6		46		7-Sep-07		2:07:53		74.01		41		18-Oct-07		2:25:59		69.2		45.5

		7-Sep-07		4:07:10		75.2		39		7-Sep-07		4:06:20		71		46		7-Sep-07		4:07:53		72.21		37		18-Oct-07		4:25:59		68.61		45

		7-Sep-07		6:07:10		75.81		38		7-Sep-07		6:06:20		71.6		44		7-Sep-07		6:07:53		71		45.5		18-Oct-07		6:25:59		69.2		46

		7-Sep-07		8:07:10		75.81		41		7-Sep-07		8:06:20		71.6		50		7-Sep-07		8:07:53		71.6		39.5		18-Oct-07		8:25:59		69.2		47

		7-Sep-07		10:07:10		75.2		38.5		7-Sep-07		10:06:20		71.6		40.5		7-Sep-07		10:07:53		72.21		40		18-Oct-07		10:25:59		70.41		50

		7-Sep-07		12:07:10		74.6		40		7-Sep-07		12:06:20		71		42.5		7-Sep-07		12:07:53		72.21		51.5		18-Oct-07		12:25:59		72.8		48.5

		7-Sep-07		14:07:10		74.6		43		7-Sep-07		14:06:20		71.6		42		7-Sep-07		14:07:53		71.6		42.5		18-Oct-07		14:25:59		74.6		45

		7-Sep-07		16:07:10		75.81		46		7-Sep-07		16:06:20		71		61		7-Sep-07		16:07:53		71.6		44.5		18-Oct-07		16:25:59		75.81		43

		7-Sep-07		18:07:10		75.2		45.5		7-Sep-07		18:06:20		71		48		7-Sep-07		18:07:53		71		53.5		18-Oct-07		18:25:59		75.81		43

		7-Sep-07		20:07:10		75.81		49		7-Sep-07		20:06:20		71.6		57		7-Sep-07		20:07:53		71.6		55		18-Oct-07		20:25:59		74.6		43.5

		7-Sep-07		22:07:10		75.81		48.5		7-Sep-07		22:06:20		71.6		58		7-Sep-07		22:07:53		72.8		52		18-Oct-07		22:25:59		73.4		44

		8-Sep-07		0:07:10		75.2		47.5		8-Sep-07		0:06:20		71		56.5		8-Sep-07		0:07:53		72.8		51		19-Oct-07		0:25:59		72.21		44.5

		8-Sep-07		2:07:10		75.2		47		8-Sep-07		2:06:20		71.6		55		8-Sep-07		2:07:53		72.21		51.5		19-Oct-07		2:25:59		71		44.5

		8-Sep-07		4:07:10		75.2		47		8-Sep-07		4:06:20		71		55.5		8-Sep-07		4:07:53		71.6		51		19-Oct-07		4:25:59		70.41		45

		8-Sep-07		6:07:10		75.81		47		8-Sep-07		6:06:20		71.6		54.5		8-Sep-07		6:07:53		71		55		19-Oct-07		6:25:59		70.41		45.5

		8-Sep-07		8:07:10		75.2		47.5		8-Sep-07		8:06:20		72.21		56		8-Sep-07		8:07:53		71.6		57		19-Oct-07		8:25:59		70.41		46.5

		8-Sep-07		10:07:10		74.6		44.5		8-Sep-07		10:06:20		72.21		45		8-Sep-07		10:07:53		72.21		46.5		19-Oct-07		10:25:59		71.6		47.5

		8-Sep-07		12:07:10		74.6		50.5		8-Sep-07		12:06:20		71		57		8-Sep-07		12:07:53		72.21		45		19-Oct-07		12:25:59		73.4		46

		8-Sep-07		14:07:10		74.01		46		8-Sep-07		14:06:20		72.21		46		8-Sep-07		14:07:53		71.6		46.5		19-Oct-07		14:25:59		75.2		45.5

		8-Sep-07		16:07:10		74.01		53		8-Sep-07		16:06:20		71		67		8-Sep-07		16:07:53		71.6		50.5		19-Oct-07		16:25:59		74.6		49

		8-Sep-07		18:07:10		74.01		53		8-Sep-07		18:06:20		70.41		63		8-Sep-07		18:07:53		71		53.5		19-Oct-07		18:25:59		74.6		50.5

		8-Sep-07		20:07:10		74.6		51		8-Sep-07		20:06:20		71		58		8-Sep-07		20:07:53		70.41		57		19-Oct-07		20:25:59		74.01		51.5

		8-Sep-07		22:07:10		74.6		48		8-Sep-07		22:06:20		71		55		8-Sep-07		22:07:53		70.41		54		19-Oct-07		22:25:59		74.01		51

		9-Sep-07		0:07:10		74.6		45		9-Sep-07		0:06:20		71		46		9-Sep-07		0:07:53		69.8		53		20-Oct-07		0:25:59		73.4		51.5

		9-Sep-07		2:07:10		74.01		45.5		9-Sep-07		2:06:20		71		52.5		9-Sep-07		2:07:53		69.2		52.5		20-Oct-07		2:25:59		72.8		52.5

		9-Sep-07		4:07:10		74.01		46.5		9-Sep-07		4:06:20		71		53.5		9-Sep-07		4:07:53		69.2		55		20-Oct-07		4:25:59		72.8		53

		9-Sep-07		6:07:10		74.01		48.5		9-Sep-07		6:06:20		71.6		56		9-Sep-07		6:07:53		68.61		56		20-Oct-07		6:25:59		72.8		54

		9-Sep-07		8:07:10		74.01		46		9-Sep-07		8:06:20		71		50		9-Sep-07		8:07:53		68.61		57		20-Oct-07		8:25:59		72.8		56.5

		9-Sep-07		10:07:10		73.4		50.5		9-Sep-07		10:06:20		70.41		57.5		9-Sep-07		10:07:53		68.61		58		20-Oct-07		10:25:59		74.01		57.5

		9-Sep-07		12:07:10		73.4		51.5		9-Sep-07		12:06:20		70.41		56.5		9-Sep-07		12:07:53		69.8		57.5		20-Oct-07		12:25:59		75.2		57.5

		9-Sep-07		14:07:10		73.4		55		9-Sep-07		14:06:20		70.41		63.5		9-Sep-07		14:07:53		70.41		54.5		20-Oct-07		14:25:59		75.81		57

		9-Sep-07		16:07:10		74.6		54		9-Sep-07		16:06:20		70.41		64.5		9-Sep-07		16:07:53		71		51		20-Oct-07		16:25:59		75.81		57

		9-Sep-07		18:07:10		75.2		50		9-Sep-07		18:06:20		70.41		55		9-Sep-07		18:07:53		70.41		60		20-Oct-07		18:25:59		75.81		56

		9-Sep-07		20:07:10		75.2		44.5		9-Sep-07		20:06:20		71.6		47		9-Sep-07		20:07:53		70.41		55		20-Oct-07		20:25:59		74.01		54.5

		9-Sep-07		22:07:10		74.6		47		9-Sep-07		22:06:20		71		54.5		9-Sep-07		22:07:53		69.8		54		20-Oct-07		22:25:59		72.8		53

		10-Sep-07		0:07:10		74.6		46		10-Sep-07		0:06:20		71		52.5		10-Sep-07		0:07:53		69.2		53.5		21-Oct-07		0:25:59		71.6		51

		10-Sep-07		2:07:10		74.6		45.5		10-Sep-07		2:06:20		71.6		51		10-Sep-07		2:07:53		68.61		53.5		21-Oct-07		2:25:59		71		50

		10-Sep-07		4:07:10		74.01		45		10-Sep-07		4:06:20		71.6		50		10-Sep-07		4:07:53		68.61		54		21-Oct-07		4:25:59		70.41		49.5

		10-Sep-07		6:07:10		74.01		45		10-Sep-07		6:06:20		71		51		10-Sep-07		6:07:53		68		54.5		21-Oct-07		6:25:59		69.8		47.5

		10-Sep-07		8:07:10		72.8		44.5		10-Sep-07		8:06:20		69.8		50.5		10-Sep-07		8:07:53		67.4		54.5		21-Oct-07		8:25:59		69.2		45.5

		10-Sep-07		10:07:10		72.8		45.5		10-Sep-07		10:06:20		69.8		46.5		10-Sep-07		10:07:53		67.4		55		21-Oct-07		10:25:59		69.2		48

		10-Sep-07		12:07:10		72.8		46		10-Sep-07		12:06:20		70.41		49.5		10-Sep-07		12:07:53		68.61		56		21-Oct-07		12:25:59		70.41		45.5

		10-Sep-07		14:07:10		73.4		49		10-Sep-07		14:06:20		70.41		56.5		10-Sep-07		14:07:53		69.8		59.5		21-Oct-07		14:25:59		71		42

		10-Sep-07		16:07:10		74.01		53.5		10-Sep-07		16:06:20		70.41		62.5		10-Sep-07		16:07:53		70.41		49		21-Oct-07		16:25:59		72.21		39

		10-Sep-07		18:07:10		74.6		52.5		10-Sep-07		18:06:20		70.41		63		10-Sep-07		18:07:53		71		56		21-Oct-07		18:25:59		73.4		36.5

		10-Sep-07		20:07:10		75.2		49		10-Sep-07		20:06:20		71.6		55.5		10-Sep-07		20:07:53		71.6		54.5		21-Oct-07		20:25:59		72.21		38

		10-Sep-07		22:07:10		74.6		48		10-Sep-07		22:06:20		71		56		10-Sep-07		22:07:53		70.41		54		21-Oct-07		22:25:59		71		40

		11-Sep-07		0:07:10		74.6		47		11-Sep-07		0:06:20		71		54.5		11-Sep-07		0:07:53		69.8		53.5		22-Oct-07		0:25:59		69.8		39.5

		11-Sep-07		2:07:10		74.01		45.5		11-Sep-07		2:06:20		71		52		11-Sep-07		2:07:53		68.61		53.5		22-Oct-07		2:25:59		69.2		39.5

		11-Sep-07		4:07:10		74.01		44.5		11-Sep-07		4:06:20		71.6		48.5		11-Sep-07		4:07:53		68		53.5		22-Oct-07		4:25:59		69.2		39

		11-Sep-07		6:07:10		74.01		43		11-Sep-07		6:06:20		71		48		11-Sep-07		6:07:53		68.61		52		22-Oct-07		6:25:59		68.61		38.5

		11-Sep-07		8:07:10		74.01		43.5		11-Sep-07		8:06:20		70.41		45		11-Sep-07		8:07:53		71.6		51.5		22-Oct-07		8:25:59		68		37.5

		11-Sep-07		10:07:10		74.6		46.5		11-Sep-07		10:06:20		71		45.5		11-Sep-07		10:07:53		71.6		48		22-Oct-07		10:25:59		68		37.5

		11-Sep-07		12:07:10		74.01		52.5		11-Sep-07		12:06:20		71		63		11-Sep-07		12:07:53		72.21		46		22-Oct-07		12:25:59		69.2		36

		11-Sep-07		14:07:10		74.6		46.5		11-Sep-07		14:06:20		71.6		45		11-Sep-07		14:07:53		71.6		45		22-Oct-07		14:25:59		72.21		33

		11-Sep-07		16:07:10		75.2		48.5		11-Sep-07		16:06:20		70.41		52		11-Sep-07		16:07:53		71		63		22-Oct-07		16:25:59		72.8		33

		11-Sep-07		18:07:10		74.6		49.5		11-Sep-07		18:06:20		70.41		54		11-Sep-07		18:07:53		71		60.5		22-Oct-07		18:25:59		72.8		32.5

		11-Sep-07		20:07:10		75.2		50.5		11-Sep-07		20:06:20		71		58.5		11-Sep-07		20:07:53		70.41		57.5		22-Oct-07		20:25:59		72.8		31.5

		11-Sep-07		22:07:10		75.2		45.5		11-Sep-07		22:06:20		71.6		51.5		11-Sep-07		22:07:53		72.21		52		22-Oct-07		22:25:59		72.21		35

		12-Sep-07		0:07:10		74.6		46.5		12-Sep-07		0:06:20		71.6		53		12-Sep-07		0:07:53		71.6		51		23-Oct-07		0:25:59		71.6		36

		12-Sep-07		2:07:10		74.6		45.5		12-Sep-07		2:06:20		71.6		51.5		12-Sep-07		2:07:53		71		51		23-Oct-07		2:25:59		70.41		37

		12-Sep-07		4:07:10		74.01		46.5		12-Sep-07		4:06:20		70.41		53.5		12-Sep-07		4:07:53		70.41		52		23-Oct-07		4:25:59		69.8		36.5

		12-Sep-07		6:07:10		74.6		46.5		12-Sep-07		6:06:20		71		53		12-Sep-07		6:07:53		70.41		50		23-Oct-07		6:25:59		69.8		36.5

		12-Sep-07		8:07:10		74.01		45.5		12-Sep-07		8:06:20		71.6		44.5		12-Sep-07		8:07:53		71		48.5		23-Oct-07		8:25:59		68.61		37.5

		12-Sep-07		10:07:10		74.01		47.5		12-Sep-07		10:06:20		72.21		55		12-Sep-07		10:07:53		71.6		56		23-Oct-07		10:25:59		71.6		39

		12-Sep-07		12:07:10		74.6		47		12-Sep-07		12:06:20		71.6		53		12-Sep-07		12:07:53		72.21		52		23-Oct-07		12:25:59		74.6		37.5

		12-Sep-07		14:07:10		74.01		46		12-Sep-07		14:06:20		71.6		43		12-Sep-07		14:07:53		71.6		54		23-Oct-07		14:25:59		75.2		37

		12-Sep-07		16:07:10		74.6		49		12-Sep-07		16:06:20		71		53		12-Sep-07		16:07:53		71.6		46.5		23-Oct-07		16:25:59		75.81		36.5

		12-Sep-07		18:07:10		74.6		53		12-Sep-07		18:06:20		70.41		65		12-Sep-07		18:07:53		71		62.5		23-Oct-07		18:25:59		75.81		35.5

		12-Sep-07		20:07:10		74.6		52		12-Sep-07		20:06:20		71		60.5		12-Sep-07		20:07:53		71		54.5		23-Oct-07		20:25:59		74.6		36

		12-Sep-07		22:07:10		74.6		49		12-Sep-07		22:06:20		71.6		56.5		12-Sep-07		22:07:53		72.8		52.5		23-Oct-07		22:25:59		74.01		37.5

		13-Sep-07		0:07:10		75.2		49		13-Sep-07		0:06:20		71.6		56.5		13-Sep-07		0:07:53		72.8		53		24-Oct-07		0:25:59		73.4		38.5

		13-Sep-07		2:07:10		75.2		48.5		13-Sep-07		2:06:20		71		57		13-Sep-07		2:07:53		72.21		53		24-Oct-07		2:25:59		72.21		39

		13-Sep-07		4:07:10		74.6		48.5		13-Sep-07		4:06:20		70.41		58.5		13-Sep-07		4:07:53		71.6		56		24-Oct-07		4:25:59		71		39.5

		13-Sep-07		6:07:10		75.2		49		13-Sep-07		6:06:20		71		58		13-Sep-07		6:07:53		70.41		50.5		24-Oct-07		6:25:59		71		39

		13-Sep-07		8:07:10		74.6		50		13-Sep-07		8:06:20		71		52.5		13-Sep-07		8:07:53		71		56		24-Oct-07		8:25:59		69.8		39.5

		13-Sep-07		10:07:10		74.01		45.5		13-Sep-07		10:06:20		71.6		44.5		13-Sep-07		10:07:53		71.6		57		24-Oct-07		10:25:59		72.21		42.5

		13-Sep-07		12:07:10		74.6		48		13-Sep-07		12:06:20		71.6		52.5		13-Sep-07		12:07:53		71.6		48		24-Oct-07		12:25:59		75.2		41

		13-Sep-07		14:07:10		74.6		45.5		13-Sep-07		14:06:20		71.6		44		13-Sep-07		14:07:53		70.41		61.5		24-Oct-07		14:25:59		75.81		40.5

		13-Sep-07		16:07:10		74.6		52.5		13-Sep-07		16:06:20		70.41		58		13-Sep-07		16:07:53		71		61.5		24-Oct-07		16:25:59		76.4		40.5

		13-Sep-07		18:07:10		75.2		47		13-Sep-07		18:06:20		70.41		51		13-Sep-07		18:07:53		70.41		59.5		24-Oct-07		18:25:59		75.81		42.5

		13-Sep-07		20:07:10		75.2		48		13-Sep-07		20:06:20		71.6		55.5		13-Sep-07		20:07:53		71.6		55		24-Oct-07		20:25:59		75.2		45

		13-Sep-07		22:07:10		74.6		47.5		13-Sep-07		22:06:20		71		54.5		13-Sep-07		22:07:53		71.6		52.5		24-Oct-07		22:25:59		75.81		44.5

		14-Sep-07		0:07:10		74.6		46.5		14-Sep-07		0:06:20		71.6		53		14-Sep-07		0:07:53		71.6		51.5		25-Oct-07		0:25:59		74.6		43

		14-Sep-07		2:07:10		74.6		46.5		14-Sep-07		2:06:20		71		51.5		14-Sep-07		2:07:53		71.6		51.5		25-Oct-07		2:25:59		73.4		43

		14-Sep-07		4:07:10		74.6		44.5		14-Sep-07		4:06:20		71.6		50		14-Sep-07		4:07:53		71		45		25-Oct-07		4:25:59		72.21		43

		14-Sep-07		6:07:10		74.6		43.5		14-Sep-07		6:06:20		71		49.5		14-Sep-07		6:07:53		71		51		25-Oct-07		6:25:59		71.6		43

		14-Sep-07		8:07:10		74.01		46		14-Sep-07		8:06:20		71.6		54		14-Sep-07		8:07:53		71		53		25-Oct-07		8:25:59		71		42.5

		14-Sep-07		10:07:10		74.6		46.5		14-Sep-07		10:06:20		71.6		55.5		14-Sep-07		10:07:53		72.21		47.5		25-Oct-07		10:25:59		73.4		44

		14-Sep-07		12:07:10		74.01		47.5		14-Sep-07		12:06:20		70.41		53		14-Sep-07		12:07:53		72.21		43		25-Oct-07		12:25:59		75.2		44

		14-Sep-07		14:07:10		74.6		49		14-Sep-07		14:06:20		71.6		56		14-Sep-07		14:07:53		71.6		48		25-Oct-07		14:25:59		75.81		43

		14-Sep-07		16:07:10		75.2		46.5		14-Sep-07		16:06:20		71		53		14-Sep-07		16:07:53		71.6		58.5		25-Oct-07		16:25:59		75.81		41

		14-Sep-07		18:07:10		75.2		50.5		14-Sep-07		18:06:20		71		64.5		14-Sep-07		18:07:53		71		62		25-Oct-07		18:25:59		75.81		44.5

		14-Sep-07		20:07:10		75.2		50		14-Sep-07		20:06:20		71.6		59		14-Sep-07		20:07:53		72.8		55.5		25-Oct-07		20:25:59		75.2		43.5

		14-Sep-07		22:07:10		75.2		50.5		14-Sep-07		22:06:20		71.6		59.5		14-Sep-07		22:07:53		74.01		52.5		25-Oct-07		22:25:59		74.6		42.5

		15-Sep-07		0:07:10		75.2		48.5		15-Sep-07		0:06:20		71		51.5		15-Sep-07		0:07:53		73.4		52		26-Oct-07		0:25:59		73.4		42.5

		15-Sep-07		2:07:10		74.6		48		15-Sep-07		2:06:20		71.6		56		15-Sep-07		2:07:53		73.4		52		26-Oct-07		2:25:59		72.21		43

		15-Sep-07		4:07:10		74.6		48.5		15-Sep-07		4:06:20		71.6		55.5		15-Sep-07		4:07:53		72.21		54.5		26-Oct-07		4:25:59		71		42.5

		15-Sep-07		6:07:10		75.2		49.5		15-Sep-07		6:06:20		71.6		58.5		15-Sep-07		6:07:53		71		51		26-Oct-07		6:25:59		70.41		41.5

		15-Sep-07		8:07:10		75.2		46		15-Sep-07		8:06:20		72.21		49		15-Sep-07		8:07:53		71.6		56		26-Oct-07		8:25:59		69.2		41

		15-Sep-07		10:07:10		74.6		50		15-Sep-07		10:06:20		71.6		57.5		15-Sep-07		10:07:53		71.6		50		26-Oct-07		10:25:59		71		44.5

		15-Sep-07		12:07:10		74.01		51		15-Sep-07		12:06:20		71		51		15-Sep-07		12:07:53		72.21		49.5		26-Oct-07		12:25:59		74.6		43.5

		15-Sep-07		14:07:10		74.6		46.5		15-Sep-07		14:06:20		71.6		47.5		15-Sep-07		14:07:53		71.6		54		26-Oct-07		14:25:59		75.81		43.5

		15-Sep-07		16:07:10		74.6		45.5		15-Sep-07		16:06:20		69.2		50.5		15-Sep-07		16:07:53		71.6		53		26-Oct-07		16:25:59		76.4		43.5

		15-Sep-07		18:07:10		73.4		46		15-Sep-07		18:06:20		68		50		15-Sep-07		18:07:53		71		48.5		26-Oct-07		18:25:59		75.81		44

		15-Sep-07		20:07:10		74.6		45		15-Sep-07		20:06:20		71		52		15-Sep-07		20:07:53		71		50.5		26-Oct-07		20:25:59		74.6		43

		15-Sep-07		22:07:10		75.2		44.5		15-Sep-07		22:06:20		71.6		52		15-Sep-07		22:07:53		72.8		48		26-Oct-07		22:25:59		73.4		42.5

		16-Sep-07		0:07:10		75.2		44		16-Sep-07		0:06:20		71		51.5		16-Sep-07		0:07:53		72.8		48		27-Oct-07		0:25:59		72.21		43

		16-Sep-07		2:07:10		75.2		43		16-Sep-07		2:06:20		71.6		49.5		16-Sep-07		2:07:53		72.21		47.5		27-Oct-07		2:25:59		71		44

		16-Sep-07		4:07:10		74.6		44		16-Sep-07		4:06:20		71		51		16-Sep-07		4:07:53		71		48.5		27-Oct-07		4:25:59		70.41		44.5

		16-Sep-07		6:07:10		74.01		43		16-Sep-07		6:06:20		69.8		44		16-Sep-07		6:07:53		71		49		27-Oct-07		6:25:59		70.41		45.5

		16-Sep-07		8:07:10		73.4		44		16-Sep-07		8:06:20		68.61		54		16-Sep-07		8:07:53		70.41		48		27-Oct-07		8:25:59		70.41		46

		16-Sep-07		10:07:10		73.4		45.5		16-Sep-07		10:06:20		68.61		57		16-Sep-07		10:07:53		69.8		52.5		27-Oct-07		10:25:59		72.21		45.5

		16-Sep-07		12:07:10		72.8		46		16-Sep-07		12:06:20		68.61		47.5		16-Sep-07		12:07:53		70.41		56		27-Oct-07		12:25:59		74.6		44

		16-Sep-07		14:07:10		73.4		44.5		16-Sep-07		14:06:20		68.61		47		16-Sep-07		14:07:53		71		51		27-Oct-07		14:25:59		75.2		42.5

		16-Sep-07		16:07:10		74.6		45		16-Sep-07		16:06:20		68.61		52		16-Sep-07		16:07:53		71		50.5		27-Oct-07		16:25:59		75.2		43.5

		16-Sep-07		18:07:10		74.6		46		16-Sep-07		18:06:20		68.61		59		16-Sep-07		18:07:53		70.41		53		27-Oct-07		18:25:59		74.6		44

		16-Sep-07		20:07:10		75.81		45		16-Sep-07		20:06:20		71		54		16-Sep-07		20:07:53		71.6		51.5		27-Oct-07		20:25:59		72.21		43.5

		16-Sep-07		22:07:10		75.2		44.5		16-Sep-07		22:06:20		71		52.5		16-Sep-07		22:07:53		72.21		49.5		27-Oct-07		22:25:59		71.6		44

		17-Sep-07		0:07:10		75.2		43		17-Sep-07		0:06:20		71		51.5		17-Sep-07		0:07:53		71.6		49		28-Oct-07		0:25:59		70.41		43.5

		17-Sep-07		2:07:10		74.6		42.5		17-Sep-07		2:06:20		70.41		49.5		17-Sep-07		2:07:53		70.41		48.5		28-Oct-07		2:25:59		69.2		42.5

		17-Sep-07		4:07:10		74.01		41.5		17-Sep-07		4:06:20		70.41		47		17-Sep-07		4:07:53		69.8		48		28-Oct-07		4:25:59		68.61		42

		17-Sep-07		6:07:10		73.4		41.5		17-Sep-07		6:06:20		69.8		42		17-Sep-07		6:07:53		69.2		49		28-Oct-07		6:25:59		68.61		41.5

		17-Sep-07		8:07:10		72.21		44.5		17-Sep-07		8:06:20		68		52.5		17-Sep-07		8:07:53		69.2		50		28-Oct-07		8:25:59		68		42

		17-Sep-07		10:07:10		72.8		47.5		17-Sep-07		10:06:20		68.61		57.5		17-Sep-07		10:07:53		70.41		49.5		28-Oct-07		10:25:59		67.4		44.5

		17-Sep-07		12:07:10		72.8		50.5		17-Sep-07		12:06:20		68.61		61		17-Sep-07		12:07:53		71		49.5		28-Oct-07		12:25:59		68.61		45.5

		17-Sep-07		14:07:10		74.01		45.5		17-Sep-07		14:06:20		69.2		52		17-Sep-07		14:07:53		71		57		28-Oct-07		14:25:59		69.8		46

		17-Sep-07		16:07:10		74.6		49.5		17-Sep-07		16:06:20		68.61		58		17-Sep-07		16:07:53		71		51.5		28-Oct-07		16:25:59		71.6		47

		17-Sep-07		18:07:10		74.6		48.5		17-Sep-07		18:06:20		68.61		61.5		17-Sep-07		18:07:53		71		50		28-Oct-07		18:25:59		71.6		45

		17-Sep-07		20:07:10		75.81		46		17-Sep-07		20:06:20		71		55		17-Sep-07		20:07:53		74.01		48		28-Oct-07		20:25:59		70.41		45

		17-Sep-07		22:07:10		75.81		44		17-Sep-07		22:06:20		71.6		52		17-Sep-07		22:07:53		74.6		46.5		28-Oct-07		22:25:59		69.8		44.5

		18-Sep-07		0:07:10		75.2		42.5		18-Sep-07		0:06:20		71		50		18-Sep-07		0:07:53		73.4		45.5		29-Oct-07		0:25:59		69.2		44

		18-Sep-07		2:07:10		75.2		41.5		18-Sep-07		2:06:20		71.6		48		18-Sep-07		2:07:53		72.21		45.5		29-Oct-07		2:25:59		68.61		44

		18-Sep-07		4:07:10		74.6		40.5		18-Sep-07		4:06:20		71		46.5		18-Sep-07		4:07:53		71		45.5		29-Oct-07		4:25:59		68.61		44

		18-Sep-07		6:07:10		74.6		39.5		18-Sep-07		6:06:20		69.8		45		18-Sep-07		6:07:53		70.41		45.5		29-Oct-07		6:25:59		68		43.5

		18-Sep-07		8:07:10		72.8		40		18-Sep-07		8:06:20		69.2		39.5		18-Sep-07		8:07:53		71		44.5		29-Oct-07		8:25:59		67.4		43

		18-Sep-07		10:07:10		73.4		42.5		18-Sep-07		10:06:20		70.41		46.5		18-Sep-07		10:07:53		71.6		42.5		29-Oct-07		10:25:59		68.61		45.5

		18-Sep-07		12:07:10		73.4		44.5		18-Sep-07		12:06:20		69.8		51		18-Sep-07		12:07:53		72.21		43.5		29-Oct-07		12:25:59		70.41		46.5

		18-Sep-07		14:07:10		73.4		42.5		18-Sep-07		14:06:20		69.8		42		18-Sep-07		14:07:53		71.6		43.5		29-Oct-07		14:25:59		72.21		47.5

		18-Sep-07		16:07:10		74.01		47.5		18-Sep-07		16:06:20		69.2		61		18-Sep-07		16:07:53		71		49.5		29-Oct-07		16:25:59		74.6		47.5

		18-Sep-07		18:07:10		74.01		43.5		18-Sep-07		18:06:20		69.2		49.5		18-Sep-07		18:07:53		71		43		29-Oct-07		18:25:59		75.2		47

		18-Sep-07		20:07:10		74.6		44		18-Sep-07		20:06:20		71.6		50		18-Sep-07		20:07:53		71.6		51.5		29-Oct-07		20:25:59		74.01		46

		18-Sep-07		22:07:10		75.2		42.5		18-Sep-07		22:06:20		71.6		50.5		18-Sep-07		22:07:53		73.4		46		29-Oct-07		22:25:59		72.8		46

		19-Sep-07		0:07:10		75.2		42.5		19-Sep-07		0:06:20		71		49.5		19-Sep-07		0:07:53		73.4		44.5		30-Oct-07		0:25:59		71.6		46

		19-Sep-07		2:07:10		74.6		41		19-Sep-07		2:06:20		71		48		19-Sep-07		2:07:53		72.8		44		30-Oct-07		2:25:59		71		46

		19-Sep-07		4:07:10		74.6		40		19-Sep-07		4:06:20		71		46		19-Sep-07		4:07:53		71		44		30-Oct-07		4:25:59		69.8		45.5

		19-Sep-07		6:07:10		74.01		38.5		19-Sep-07		6:06:20		70.41		41.5		19-Sep-07		6:07:53		70.41		43.5		30-Oct-07		6:25:59		69.8		46

		19-Sep-07		8:07:10		72.8		41		19-Sep-07		8:06:20		69.8		48		19-Sep-07		8:07:53		71		42.5		30-Oct-07		8:25:59		69.2		48

		19-Sep-07		10:07:10		72.8		43.5		19-Sep-07		10:06:20		70.41		51.5		19-Sep-07		10:07:53		71.6		45.5		30-Oct-07		10:25:59		71		48

		19-Sep-07		12:07:10		73.4		45.5		19-Sep-07		12:06:20		70.41		56		19-Sep-07		12:07:53		72.21		53		30-Oct-07		12:25:59		72.8		49

		19-Sep-07		14:07:10		74.6		43.5		19-Sep-07		14:06:20		72.21		49		19-Sep-07		14:07:53		71.6		41		30-Oct-07		14:25:59		74.6		48

		19-Sep-07		16:07:10		73.4		42.5		19-Sep-07		16:06:20		68.61		45		19-Sep-07		16:07:53		72.21		48		30-Oct-07		16:25:59		75.2		47.5

		19-Sep-07		18:07:10		73.4		42		19-Sep-07		18:06:20		68.61		43		19-Sep-07		18:07:53		71		50		30-Oct-07		18:25:59		75.2		45

		19-Sep-07		20:07:10		74.6		42		19-Sep-07		20:06:20		70.41		49		19-Sep-07		20:07:53		71		47.5		30-Oct-07		20:25:59		72.8		45.5

		19-Sep-07		22:07:10		74.6		39.5		19-Sep-07		22:06:20		70.41		46.5		19-Sep-07		22:07:53		72.21		42.5		30-Oct-07		22:25:59		71.6		46.5

		20-Sep-07		0:07:10		74.6		38		20-Sep-07		0:06:20		70.41		44		20-Sep-07		0:07:53		71.6		41		31-Oct-07		0:25:59		71		46.5

		20-Sep-07		2:07:10		74.01		37		20-Sep-07		2:06:20		70.41		42		20-Sep-07		2:07:53		71		40.5		31-Oct-07		2:25:59		70.41		47.5

		20-Sep-07		4:07:10		73.4		36		20-Sep-07		4:06:20		70.41		41		20-Sep-07		4:07:53		69.8		40.5		31-Oct-07		4:25:59		70.41		48

		20-Sep-07		6:07:10		72.8		36		20-Sep-07		6:06:20		69.8		40		20-Sep-07		6:07:53		69.8		40		31-Oct-07		6:25:59		70.41		48.5

		20-Sep-07		8:07:10		72.8		37.5		20-Sep-07		8:06:20		69.8		44		20-Sep-07		8:07:53		71		39.5		31-Oct-07		8:25:59		69.8		48

		20-Sep-07		10:07:10		73.4		37.5		20-Sep-07		10:06:20		70.41		45.5		20-Sep-07		10:07:53		71.6		35.5		31-Oct-07		10:25:59		71.6		48

		20-Sep-07		12:07:10		73.4		36		20-Sep-07		12:06:20		69.2		35.5		20-Sep-07		12:07:53		72.21		34.5		31-Oct-07		12:25:59		72.21		47.5

		20-Sep-07		14:07:10		73.4		34		20-Sep-07		14:06:20		69.8		36		20-Sep-07		14:07:53		71.6		39.5		31-Oct-07		14:25:59		73.4		46.5

		20-Sep-07		16:07:10		73.4		34		20-Sep-07		16:06:20		68.61		37.5		20-Sep-07		16:07:53		71		33		31-Oct-07		16:25:59		74.6		46

		20-Sep-07		18:07:10		74.01		34.5		20-Sep-07		18:06:20		68		41.5		20-Sep-07		18:07:53		70.41		38.5		31-Oct-07		18:25:59		75.2		44.5

		20-Sep-07		20:07:10		74.6		36		20-Sep-07		20:06:20		69.8		41		20-Sep-07		20:07:53		72.8		37.5		31-Oct-07		20:25:59		72.8		44.5

		20-Sep-07		22:07:10		74.6		34		20-Sep-07		22:06:20		70.41		39.5		20-Sep-07		22:07:53		72.21		36.5		31-Oct-07		22:25:59		72.21		45.5

		21-Sep-07		0:07:10		74.01		34.5		21-Sep-07		0:06:20		69.8		40.5		21-Sep-07		0:07:53		71.6		37.5		1-Nov-07		0:25:59		70.41		46

		21-Sep-07		2:07:10		74.01		33.5		21-Sep-07		2:06:20		70.41		36		21-Sep-07		2:07:53		71		37		1-Nov-07		2:25:59		69.8		47

		21-Sep-07		4:07:10		73.4		33		21-Sep-07		4:06:20		70.41		38		21-Sep-07		4:07:53		69.8		37		1-Nov-07		4:25:59		69.8		48

		21-Sep-07		6:07:10		73.4		34.5		21-Sep-07		6:06:20		69.8		39.5		21-Sep-07		6:07:53		69.8		39		1-Nov-07		6:25:59		69.8		48.5

		21-Sep-07		8:07:10		72.8		37.5		21-Sep-07		8:06:20		69.8		44.5		21-Sep-07		8:07:53		71		39		1-Nov-07		8:25:59		69.8		48.5

		21-Sep-07		10:07:10		72.8		38.5		21-Sep-07		10:06:20		69.8		41.5		21-Sep-07		10:07:53		71.6		42		1-Nov-07		10:25:59		72.21		48

		21-Sep-07		12:07:10		74.6		37		21-Sep-07		12:06:20		73.4		36		21-Sep-07		12:07:53		71.6		36.5		1-Nov-07		12:25:59		72.8		48.5

		21-Sep-07		14:07:10		74.6		38.5		21-Sep-07		14:06:20		71.6		45		21-Sep-07		14:07:53		71		41.5		1-Nov-07		14:25:59		73.4		48.5

		21-Sep-07		16:07:10		74.6		38		21-Sep-07		16:06:20		70.41		45.5		21-Sep-07		16:07:53		71		41		1-Nov-07		16:25:59		74.01		49.5

		21-Sep-07		18:07:10		74.6		37.5		21-Sep-07		18:06:20		70.41		44		21-Sep-07		18:07:53		71		40.5		1-Nov-07		18:25:59		74.01		48

		21-Sep-07		20:07:10		75.81		35		21-Sep-07		20:06:20		72.21		39		21-Sep-07		20:07:53		71.6		39		1-Nov-07		20:25:59		72.21		48

		21-Sep-07		22:07:10		75.81		33.5		21-Sep-07		22:06:20		72.8		37.5		21-Sep-07		22:07:53		71		38		1-Nov-07		22:25:59		71.6		49

		22-Sep-07		0:07:10		75.2		33		22-Sep-07		0:06:20		72.21		37		22-Sep-07		0:07:53		70.41		38.5		2-Nov-07		0:25:59		71		49

		22-Sep-07		2:07:10		74.6		32.5		22-Sep-07		2:06:20		71.6		36.5		22-Sep-07		2:07:53		68.61		38.5		2-Nov-07		2:25:59		70.41		49.5

		22-Sep-07		4:07:10		73.4		33		22-Sep-07		4:06:20		70.41		37.5		22-Sep-07		4:07:53		68		39.5		2-Nov-07		4:25:59		69.8		49

		22-Sep-07		6:07:10		72.8		33.5		22-Sep-07		6:06:20		69.8		37.5		22-Sep-07		6:07:53		67.4		40.5		2-Nov-07		6:25:59		69.8		48

		22-Sep-07		8:07:10		72.8		33.5		22-Sep-07		8:06:20		71.6		37.5		22-Sep-07		8:07:53		69.2		40		2-Nov-07		8:25:59		71.6		46.5

		22-Sep-07		10:07:10		73.4		36		22-Sep-07		10:06:20		72.21		39		22-Sep-07		10:07:53		71.6		43.5		2-Nov-07		10:25:59		71.6		48

		22-Sep-07		12:07:10		73.4		36.5		22-Sep-07		12:06:20		71.6		40.5		22-Sep-07		12:07:53		71.6		44.5		2-Nov-07		12:25:59		73.4		48

		22-Sep-07		14:07:10		74.01		38		22-Sep-07		14:06:20		71		40.5		22-Sep-07		14:07:53		72.21		43		2-Nov-07		14:25:59		75.2		48

		22-Sep-07		16:07:10		74.6		40.5		22-Sep-07		16:06:20		70.41		47		22-Sep-07		16:07:53		71.6		47		2-Nov-07		16:25:59		75.2		49.5

		22-Sep-07		18:07:10		74.6		38.5		22-Sep-07		18:06:20		70.41		45		22-Sep-07		18:07:53		71		38.5		2-Nov-07		18:25:59		75.2		50

		22-Sep-07		20:07:10		75.2		37.5		22-Sep-07		20:06:20		72.21		42		22-Sep-07		20:07:53		70.41		44		2-Nov-07		20:25:59		74.6		46

		22-Sep-07		22:07:10		75.81		37.5		22-Sep-07		22:06:20		72.8		42.5		22-Sep-07		22:07:53		71.6		43		2-Nov-07		22:25:59		73.4		45.5

		23-Sep-07		0:07:10		75.81		38.5		23-Sep-07		0:06:20		73.4		43.5		23-Sep-07		0:07:53		71.6		44.5		3-Nov-07		0:25:59		71.6		45

		23-Sep-07		2:07:10		75.2		40		23-Sep-07		2:06:20		72.21		46.5		23-Sep-07		2:07:53		71		46.5		3-Nov-07		2:25:59		69.8		44

		23-Sep-07		4:07:10		75.2		41		23-Sep-07		4:06:20		72.8		46		23-Sep-07		4:07:53		71		47.5		3-Nov-07		4:25:59		69.2		43

		23-Sep-07		6:07:10		74.6		42		23-Sep-07		6:06:20		71.6		44		23-Sep-07		6:07:53		71.6		48		3-Nov-07		6:25:59		69.2		42

		23-Sep-07		8:07:10		74.01		44.5		23-Sep-07		8:06:20		69.8		52		23-Sep-07		8:07:53		71		43.5		3-Nov-07		8:25:59		71.6		39.5

		23-Sep-07		10:07:10		73.4		44.5		23-Sep-07		10:06:20		70.41		50.5		23-Sep-07		10:07:53		71.6		56		3-Nov-07		10:25:59		71.6		42.5

		23-Sep-07		12:07:10		74.01		44.5		23-Sep-07		12:06:20		70.41		48		23-Sep-07		12:07:53		71		49		3-Nov-07		12:25:59		75.2		42.5

		23-Sep-07		14:07:10		73.4		48.5		23-Sep-07		14:06:20		70.41		56.5		23-Sep-07		14:07:53		71		54		3-Nov-07		14:25:59		76.4		42.5

		23-Sep-07		16:07:10		74.01		50.5		23-Sep-07		16:06:20		70.41		60		23-Sep-07		16:07:53		70.41		51		3-Nov-07		16:25:59		75.81		42

		23-Sep-07		18:07:10		73.4		50.5		23-Sep-07		18:06:20		70.41		59		23-Sep-07		18:07:53		69.8		56.5		3-Nov-07		18:25:59		75.81		43.5

		23-Sep-07		20:07:10		74.6		49.5		23-Sep-07		20:06:20		72.21		55		23-Sep-07		20:07:53		69.8		56		3-Nov-07		20:25:59		74.6		43

		23-Sep-07		22:07:10		74.6		48		23-Sep-07		22:06:20		72.21		52.5		23-Sep-07		22:07:53		70.41		55.5		3-Nov-07		22:25:59		73.4		43.5

		24-Sep-07		0:07:10		74.6		47.5		24-Sep-07		0:06:20		72.21		52		24-Sep-07		0:07:53		69.8		54.5		4-Nov-07		0:25:59		71.6		43

		24-Sep-07		2:07:10		74.6		47.5		24-Sep-07		2:06:20		72.21		52		24-Sep-07		2:07:53		69.8		55		4-Nov-07		2:25:59		70.41		42

		24-Sep-07		4:07:10		74.6		47		24-Sep-07		4:06:20		72.21		51.5		24-Sep-07		4:07:53		69.8		54.5		4-Nov-07		4:25:59		69.2		41

		24-Sep-07		6:07:10		74.01		46.5		24-Sep-07		6:06:20		71.6		46		24-Sep-07		6:07:53		69.8		54.5		4-Nov-07		6:25:59		68.61		40

		24-Sep-07		8:07:10		73.4		49		24-Sep-07		8:06:20		70.41		56		24-Sep-07		8:07:53		69.2		55		4-Nov-07		8:25:59		67.4		38.5

		24-Sep-07		10:07:10		72.8		50.5		24-Sep-07		10:06:20		69.8		56.5		24-Sep-07		10:07:53		69.8		55.5		4-Nov-07		10:25:59		68		40.5

		24-Sep-07		12:07:10		72.8		51		24-Sep-07		12:06:20		69.2		55.5		24-Sep-07		12:07:53		69.8		56		4-Nov-07		12:25:59		69.2		42.5

		24-Sep-07		14:07:10		73.4		50		24-Sep-07		14:06:20		69.8		56.5		24-Sep-07		14:07:53		70.41		51.5		4-Nov-07		14:25:59		71		43

		24-Sep-07		16:07:10		74.01		46		24-Sep-07		16:06:20		69.8		44		24-Sep-07		16:07:53		70.41		48		4-Nov-07		16:25:59		72.21		43

		24-Sep-07		18:07:10		74.01		45		24-Sep-07		18:06:20		69.8		51		24-Sep-07		18:07:53		71		46.5		4-Nov-07		18:25:59		72.8		41.5

		24-Sep-07		20:07:10		75.2		40		24-Sep-07		20:06:20		72.8		39.5		24-Sep-07		20:07:53		72.21		45		4-Nov-07		20:25:59		71.6		39

		24-Sep-07		22:07:10		75.81		40		24-Sep-07		22:06:20		73.4		43.5		24-Sep-07		22:07:53		71.6		45.5		4-Nov-07		22:25:59		70.41		39.5

		25-Sep-07		0:07:10		74.6		39		25-Sep-07		0:06:20		72.21		43		25-Sep-07		0:07:53		70.41		45		5-Nov-07		0:25:59		69.8		40

		25-Sep-07		2:07:10		74.01		37.5		25-Sep-07		2:06:20		71.6		41		25-Sep-07		2:07:53		69.2		44		5-Nov-07		2:25:59		68.61		40

		25-Sep-07		4:07:10		73.4		37		25-Sep-07		4:06:20		71		40		25-Sep-07		4:07:53		68		43		5-Nov-07		4:25:59		68		39

		25-Sep-07		6:07:10		72.8		36.5		25-Sep-07		6:06:20		69.8		38.5		25-Sep-07		6:07:53		68.61		42		5-Nov-07		6:25:59		67.4		38.5

		25-Sep-07		8:07:10		72.8		37		25-Sep-07		8:06:20		71		41		25-Sep-07		8:07:53		69.2		41		5-Nov-07		8:25:59		66.2		37.5

		25-Sep-07		10:07:10		74.01		38		25-Sep-07		10:06:20		72.21		40		25-Sep-07		10:07:53		71		48		5-Nov-07		10:25:59		67.4		39.5

		25-Sep-07		12:07:10		74.6		39		25-Sep-07		12:06:20		71.6		43		25-Sep-07		12:07:53		71.6		43		5-Nov-07		12:25:59		69.2		40.5

		25-Sep-07		14:07:10		74.01		34.5		25-Sep-07		14:06:20		71.6		37.5		25-Sep-07		14:07:53		71.6		35		5-Nov-07		14:25:59		71		41.5

		25-Sep-07		16:07:10		74.6		36.5		25-Sep-07		16:06:20		70.41		40.5		25-Sep-07		16:07:53		72.21		39		5-Nov-07		16:25:59		72.21		41.5

		25-Sep-07		18:07:10		74.01		33.5		25-Sep-07		18:06:20		70.41		36		25-Sep-07		18:07:53		71.6		37		5-Nov-07		18:25:59		72.8		41

		25-Sep-07		20:07:10		75.81		36.5		25-Sep-07		20:06:20		72.8		40.5		25-Sep-07		20:07:53		71		42.5		5-Nov-07		20:25:59		71.6		42.5

		25-Sep-07		22:07:10		75.81		36		25-Sep-07		22:06:20		72.8		40		25-Sep-07		22:07:53		72.8		40		5-Nov-07		22:25:59		71		43

		26-Sep-07		0:07:10		75.81		35		26-Sep-07		0:06:20		72.8		39		26-Sep-07		0:07:53		71.6		40		6-Nov-07		0:25:59		69.8		42

		26-Sep-07		2:07:10		75.2		34.5		26-Sep-07		2:06:20		72.21		39		26-Sep-07		2:07:53		69.8		40		6-Nov-07		2:25:59		69.2		41.5

		26-Sep-07		4:07:10		74.01		34		26-Sep-07		4:06:20		71		38		26-Sep-07		4:07:53		68.61		40		6-Nov-07		4:25:59		68		40.5

		26-Sep-07		6:07:10		72.8		33.5		26-Sep-07		6:06:20		70.41		36		26-Sep-07		6:07:53		68.61		39.5		6-Nov-07		6:25:59		68		39.5

		26-Sep-07		8:07:10		73.4		33		26-Sep-07		8:06:20		71.6		36.5		26-Sep-07		8:07:53		70.41		37.5		6-Nov-07		8:25:59		69.8		37

		26-Sep-07		10:07:10		74.01		37		26-Sep-07		10:06:20		71.6		38.5		26-Sep-07		10:07:53		71.6		34.5		6-Nov-07		10:25:59		71		39.5

		26-Sep-07		12:07:10		74.6		34.5		26-Sep-07		12:06:20		71.6		36		26-Sep-07		12:07:53		71.6		35.5		6-Nov-07		12:25:59		73.4		39.5

		26-Sep-07		14:07:10		74.6		33		26-Sep-07		14:06:20		71.6		35.5		26-Sep-07		14:07:53		71.6		34		6-Nov-07		14:25:59		75.2		39.5

		26-Sep-07		16:07:10		75.2		32.5		26-Sep-07		16:06:20		71		35.5		26-Sep-07		16:07:53		71.6		34.5		6-Nov-07		16:25:59		75.81		42.5

		26-Sep-07		18:07:10		74.6		31		26-Sep-07		18:06:20		69.8		34.5		26-Sep-07		18:07:53		71		34.5		6-Nov-07		18:25:59		75.2		41.5

		26-Sep-07		20:07:10		75.81		32		26-Sep-07		20:06:20		72.8		35.5		26-Sep-07		20:07:53		71		33.5		6-Nov-07		20:25:59		72.8		41

		26-Sep-07		22:07:10		76.4		31		26-Sep-07		22:06:20		72.8		35.5		26-Sep-07		22:07:53		73.4		34.5		6-Nov-07		22:25:59		71.6		42

		27-Sep-07		0:07:10		76.4		31		27-Sep-07		0:06:20		72.8		35.5		27-Sep-07		0:07:53		72.8		34.5		7-Nov-07		0:25:59		71		43

		27-Sep-07		2:07:10		75.81		30.5		27-Sep-07		2:06:20		72.21		35		27-Sep-07		2:07:53		71.6		34.5		7-Nov-07		2:25:59		69.8		43

		27-Sep-07		4:07:10		75.2		30		27-Sep-07		4:06:20		72.21		34		27-Sep-07		4:07:53		70.41		35		7-Nov-07		4:25:59		69.2		43.5

		27-Sep-07		6:07:10		75.2		30.5		27-Sep-07		6:06:20		72.21		33		27-Sep-07		6:07:53		70.41		35.5		7-Nov-07		6:25:59		69.2		44

		27-Sep-07		8:07:10		74.6		31.5		27-Sep-07		8:06:20		71.6		35		27-Sep-07		8:07:53		71.6		33		7-Nov-07		8:25:59		71		43

		27-Sep-07		10:07:10		74.6		32		27-Sep-07		10:06:20		72.21		37.5		27-Sep-07		10:07:53		71.6		36.5		7-Nov-07		10:25:59		71.6		42.5

		27-Sep-07		12:07:10		74.6		34		27-Sep-07		12:06:20		71.6		37		27-Sep-07		12:07:53		72.21		39		7-Nov-07		12:25:59		72.8		42

		27-Sep-07		14:07:10		74.6		34		27-Sep-07		14:06:20		71		35.5		27-Sep-07		14:07:53		72.21		34		7-Nov-07		14:25:59		74.01		42.5

		27-Sep-07		16:07:10		75.2		33		27-Sep-07		16:06:20		70.41		37.5		27-Sep-07		16:07:53		71.6		34.5		7-Nov-07		16:25:59		74.6		44

		27-Sep-07		18:07:10		75.2		32.5		27-Sep-07		18:06:20		71		36		27-Sep-07		18:07:53		71.6		35.5		7-Nov-07		18:25:59		74.6		43

		27-Sep-07		20:07:10		76.4		30.5		27-Sep-07		20:06:20		72.8		33.5		27-Sep-07		20:07:53		74.6		31.5		7-Nov-07		20:25:59		72.21		42.5

		27-Sep-07		22:07:10		76.4		30.5		27-Sep-07		22:06:20		72.8		34.5		27-Sep-07		22:07:53		75.2		32		7-Nov-07		22:25:59		71.6		42

		28-Sep-07		0:07:10		76.4		30		28-Sep-07		0:06:20		72.8		34.5		28-Sep-07		0:07:53		74.6		32.5		8-Nov-07		0:25:59		69.8		42.5

		28-Sep-07		2:07:10		75.81		29.5		28-Sep-07		2:06:20		72.8		33		28-Sep-07		2:07:53		72.8		33		8-Nov-07		2:25:59		69.2		43

		28-Sep-07		4:07:10		75.2		30		28-Sep-07		4:06:20		72.8		34		28-Sep-07		4:07:53		71.6		34		8-Nov-07		4:25:59		68.61		42.5

		28-Sep-07		6:07:10		75.2		30.5		28-Sep-07		6:06:20		72.8		32.5		28-Sep-07		6:07:53		70.41		35		8-Nov-07		6:25:59		68.61		43

		28-Sep-07		8:07:10		74.6		31.5		28-Sep-07		8:06:20		71		37		28-Sep-07		8:07:53		71.6		31.5		8-Nov-07		8:25:59		71.6		40.5

		28-Sep-07		10:07:10		74.6		32.5		28-Sep-07		10:06:20		71.6		39		28-Sep-07		10:07:53		71.6		38.5		8-Nov-07		10:25:59		71		41.5

		28-Sep-07		12:07:10		74.6		33		28-Sep-07		12:06:20		71.6		36.5		28-Sep-07		12:07:53		72.21		34.5		8-Nov-07		12:25:59		72.8		43.5

		28-Sep-07		14:07:10		74.01		36		28-Sep-07		14:06:20		71		36		28-Sep-07		14:07:53		71.6		40		8-Nov-07		14:25:59		74.01		42.5

		28-Sep-07		16:07:10		75.2		37.5		28-Sep-07		16:06:20		71		44		28-Sep-07		16:07:53		71.6		41.5		8-Nov-07		16:25:59		75.2		43.5

		28-Sep-07		18:07:10		74.6		39		28-Sep-07		18:06:20		70.41		46.5		28-Sep-07		18:07:53		71		45		8-Nov-07		18:25:59		74.01		43

		28-Sep-07		20:07:10		75.81		37		28-Sep-07		20:06:20		72.8		42		28-Sep-07		20:07:53		71.6		42		8-Nov-07		20:25:59		72.21		43.5

		28-Sep-07		22:07:10		75.81		36.5		28-Sep-07		22:06:20		72.8		42		28-Sep-07		22:07:53		72.21		41		8-Nov-07		22:25:59		72.21		45.5

		29-Sep-07		0:07:10		75.2		36.5		29-Sep-07		0:06:20		72.21		42		29-Sep-07		0:07:53		71.6		42		9-Nov-07		0:25:59		71		44.5

		29-Sep-07		2:07:10		75.2		37		29-Sep-07		2:06:20		72.8		42		29-Sep-07		2:07:53		71		42.5		9-Nov-07		2:25:59		69.8		44.5

		29-Sep-07		4:07:10		75.2		37		29-Sep-07		4:06:20		72.8		41		29-Sep-07		4:07:53		71		42.5		9-Nov-07		4:25:59		69.2		45

		29-Sep-07		6:07:10		75.2		35		29-Sep-07		6:06:20		72.8		35		29-Sep-07		6:07:53		69.8		45.5		9-Nov-07		6:25:59		69.2		46.5

		29-Sep-07		8:07:10		74.6		39		29-Sep-07		8:06:20		71.6		42		29-Sep-07		8:07:53		71		45.5		9-Nov-07		8:25:59		71		45

		29-Sep-07		10:07:10		74.01		40.5		29-Sep-07		10:06:20		71		42		29-Sep-07		10:07:53		71.6		46		9-Nov-07		10:25:59		71		46

		29-Sep-07		12:07:10		74.6		39		29-Sep-07		12:06:20		71.6		38.5		29-Sep-07		12:07:53		71.6		48.5		9-Nov-07		12:25:59		72.21		47

		29-Sep-07		14:07:10		74.01		45		29-Sep-07		14:06:20		71.6		54		29-Sep-07		14:07:53		71.6		47		9-Nov-07		14:25:59		74.01		44.5

		29-Sep-07		16:07:10		74.6		42		29-Sep-07		16:06:20		71.6		48.5		29-Sep-07		16:07:53		71.6		52		9-Nov-07		16:25:59		74.01		44.5

		29-Sep-07		18:07:10		74.6		43.5		29-Sep-07		18:06:20		70.41		53		29-Sep-07		18:07:53		71		52		9-Nov-07		18:25:59		74.01		43.5

		29-Sep-07		20:07:10		75.2		36		29-Sep-07		20:06:20		72.21		38		29-Sep-07		20:07:53		70.41		42		9-Nov-07		20:25:59		73.4		43

		29-Sep-07		22:07:10		75.2		32.5		29-Sep-07		22:06:20		72.8		35		29-Sep-07		22:07:53		71		36.5		9-Nov-07		22:25:59		72.21		45

		30-Sep-07		0:07:10		75.2		31		30-Sep-07		0:06:20		73.4		33.5		30-Sep-07		0:07:53		70.41		35.5		10-Nov-07		0:25:59		71		45

		30-Sep-07		2:07:10		74.6		30.5		30-Sep-07		2:06:20		72.8		32.5		30-Sep-07		2:07:53		69.8		34.5		10-Nov-07		2:25:59		69.8		45.5

		30-Sep-07		4:07:10		74.01		30		30-Sep-07		4:06:20		71.6		32.5		30-Sep-07		4:07:53		68.61		34.5		10-Nov-07		4:25:59		69.2		46

		30-Sep-07		6:07:10		73.4		29.5		30-Sep-07		6:06:20		72.21		32.5		30-Sep-07		6:07:53		68		34.5		10-Nov-07		6:25:59		69.2		45.5

		30-Sep-07		8:07:10		72.21		30.5		30-Sep-07		8:06:20		71		34		30-Sep-07		8:07:53		68		34.5		10-Nov-07		8:25:59		71		42.5

		30-Sep-07		10:07:10		72.8		31		30-Sep-07		10:06:20		71.6		34.5		30-Sep-07		10:07:53		70.41		34.5		10-Nov-07		10:25:59		73.4		43

		30-Sep-07		12:07:10		73.4		31		30-Sep-07		12:06:20		71		33.5		30-Sep-07		12:07:53		70.41		32		10-Nov-07		12:25:59		74.01		43

		30-Sep-07		14:07:10		73.4		29		30-Sep-07		14:06:20		70.41		31.5		30-Sep-07		14:07:53		71		31		10-Nov-07		14:25:59		74.6		42

		30-Sep-07		16:07:10		74.01		30		30-Sep-07		16:06:20		69.8		34.5		30-Sep-07		16:07:53		71		31		10-Nov-07		16:25:59		75.2		43

		30-Sep-07		18:07:10		74.01		29		30-Sep-07		18:06:20		69.8		32.5		30-Sep-07		18:07:53		71		31		10-Nov-07		18:25:59		74.6		44

		30-Sep-07		20:07:10		75.2		28		30-Sep-07		20:06:20		72.21		31		30-Sep-07		20:07:53		71.6		32		10-Nov-07		20:25:59		72.8		44.5

		30-Sep-07		22:07:10		75.81		27.5		30-Sep-07		22:06:20		72.8		31		30-Sep-07		22:07:53		71.6		31.5		10-Nov-07		22:25:59		72.21		45.5

		1-Oct-07		0:07:10		75.2		27		1-Oct-07		0:06:20		72.8		30		1-Oct-07		0:07:53		70.41		32		11-Nov-07		0:25:59		70.41		44

		1-Oct-07		2:07:10		74.01		27.5		1-Oct-07		2:06:20		71.6		30.5		1-Oct-07		2:07:53		68.61		32		11-Nov-07		2:25:59		69.2		43

		1-Oct-07		4:07:10		72.8		27.5		1-Oct-07		4:06:20		70.41		30.5		1-Oct-07		4:07:53		68		32.5		11-Nov-07		4:25:59		68.61		43

		1-Oct-07		6:07:10		72.21		27.5		1-Oct-07		6:06:20		69.8		30		1-Oct-07		6:07:53		66.2		33		11-Nov-07		6:25:59		68		43.5

		1-Oct-07		8:07:10		71		28.5		1-Oct-07		8:06:20		68.61		31.5		1-Oct-07		8:07:53		68		32		11-Nov-07		8:25:59		68		44.5

		1-Oct-07		10:07:10		71.6		30		1-Oct-07		10:06:20		69.8		31.5		1-Oct-07		10:07:53		68.61		33.5		11-Nov-07		10:25:59		69.2		46.5

		1-Oct-07		12:07:10		72.21		30		1-Oct-07		12:06:20		70.41		32		1-Oct-07		12:07:53		70.41		33.5		11-Nov-07		12:25:59		69.2		49

		1-Oct-07		14:07:10		73.4		28.5		1-Oct-07		14:06:20		69.8		30		1-Oct-07		14:07:53		70.41		31.5		11-Nov-07		14:25:59		69.8		50.5

		1-Oct-07		16:07:10		73.4		27		1-Oct-07		16:06:20		69.8		29.5		1-Oct-07		16:07:53		70.41		30.5		11-Nov-07		16:25:59		69.8		52

		1-Oct-07		18:07:10		74.01		30		1-Oct-07		18:06:20		69.8		35.5		1-Oct-07		18:07:53		71		32		11-Nov-07		18:25:59		69.8		53

		1-Oct-07		20:07:10		75.81		33		1-Oct-07		20:06:20		72.8		38		1-Oct-07		20:07:53		72.21		37.5		11-Nov-07		20:25:59		69.2		54

		1-Oct-07		22:07:10		75.2		35.5		1-Oct-07		22:06:20		72.21		41		1-Oct-07		22:07:53		72.21		39.5		11-Nov-07		22:25:59		69.2		55

		2-Oct-07		0:07:10		75.2		35.5		2-Oct-07		0:06:20		72.8		41		2-Oct-07		0:07:53		71.6		41		12-Nov-07		0:25:59		69.2		55.5

		2-Oct-07		2:07:10		75.2		36.5		2-Oct-07		2:06:20		72.8		41		2-Oct-07		2:07:53		71		42.5		12-Nov-07		2:25:59		69.2		55.5

		2-Oct-07		4:07:10		75.2		40		2-Oct-07		4:06:20		72.8		46		2-Oct-07		4:07:53		71		46.5		12-Nov-07		4:25:59		69.2		54

		2-Oct-07		6:07:10		75.2		39		2-Oct-07		6:06:20		72.8		41		2-Oct-07		6:07:53		70.41		53.5		12-Nov-07		6:25:59		68.61		50.5

		2-Oct-07		8:07:10		74.6		44.5		2-Oct-07		8:06:20		71.6		46.5		2-Oct-07		8:07:53		71		51.5		12-Nov-07		8:25:59		68		47.5

		2-Oct-07		10:07:10		74.6		40.5		2-Oct-07		10:06:20		71.6		44.5		2-Oct-07		10:07:53		72.21		41		12-Nov-07		10:25:59		68		47.5

		2-Oct-07		12:07:10		74.6		44.5		2-Oct-07		12:06:20		71		47.5		2-Oct-07		12:07:53		72.21		51.5		12-Nov-07		12:25:59		69.2		46

		2-Oct-07		14:07:10		74.6		42		2-Oct-07		14:06:20		71.6		51		2-Oct-07		14:07:53		71.6		50		12-Nov-07		14:25:59		70.41		44

		2-Oct-07		16:07:10		75.2		38.5		2-Oct-07		16:06:20		71.6		46		2-Oct-07		16:07:53		71		46		12-Nov-07		16:25:59		71		42.5

		2-Oct-07		18:07:10		74.6		34		2-Oct-07		18:06:20		71		39.5		2-Oct-07		18:07:53		71		36		12-Nov-07		18:25:59		71		42.5

		2-Oct-07		20:07:10		75.81		37		2-Oct-07		20:06:20		72.8		41.5		2-Oct-07		20:07:53		70.41		44.5		12-Nov-07		20:25:59		69.8		42.5

		2-Oct-07		22:07:10		76.4		36.5		2-Oct-07		22:06:20		72.8		41.5		2-Oct-07		22:07:53		72.8		41		12-Nov-07		22:25:59		68.61		43

		3-Oct-07		0:07:10		75.81		35.5		3-Oct-07		0:06:20		72.8		40		3-Oct-07		0:07:53		72.21		40		13-Nov-07		0:25:59		68		42.5

		3-Oct-07		2:07:10		75.81		34.5		3-Oct-07		2:06:20		72.8		38		3-Oct-07		2:07:53		71		39.5		13-Nov-07		2:25:59		67.4		42.5

		3-Oct-07		4:07:10		74.6		34.5		3-Oct-07		4:06:20		71.6		38.5		3-Oct-07		4:07:53		69.8		39.5		13-Nov-07		4:25:59		67.4		42

		3-Oct-07		6:07:10		74.01		34.5		3-Oct-07		6:06:20		71.6		37.5		3-Oct-07		6:07:53		69.8		40		13-Nov-07		6:25:59		67.4		42.5

		3-Oct-07		8:07:10		73.4		36.5		3-Oct-07		8:06:20		71.6		42		3-Oct-07		8:07:53		71.6		39.5		13-Nov-07		8:25:59		71		40.5

		3-Oct-07		10:07:10		74.6		39		3-Oct-07		10:06:20		71.6		45		3-Oct-07		10:07:53		71.6		43.5		13-Nov-07		10:25:59		71		41

		3-Oct-07		12:07:10		74.6		38.5		3-Oct-07		12:06:20		71.6		37.5		3-Oct-07		12:07:53		72.21		43		13-Nov-07		12:25:59		74.6		39.5

		3-Oct-07		14:07:10		74.6		39		3-Oct-07		14:06:20		71.6		38		3-Oct-07		14:07:53		72.21		42		13-Nov-07		14:25:59		74.6		38.5

		3-Oct-07		16:07:10		74.6		37		3-Oct-07		16:06:20		71		41.5		3-Oct-07		16:07:53		71		42.5		13-Nov-07		16:25:59		75.2		37.5

		3-Oct-07		18:07:10		74.6		38.5		3-Oct-07		18:06:20		69.8		47.5		3-Oct-07		18:07:53		71		38		13-Nov-07		18:25:59		75.2		35.5

		3-Oct-07		20:07:10		75.81		37.5		3-Oct-07		20:06:20		72.8		43		3-Oct-07		20:07:53		71		44		13-Nov-07		20:25:59		73.4		38.5

		3-Oct-07		22:07:10		76.4		36.5		3-Oct-07		22:06:20		72.8		40		3-Oct-07		22:07:53		71.6		41.5		13-Nov-07		22:25:59		72.21		41

		4-Oct-07		0:07:10		75.81		35		4-Oct-07		0:06:20		72.8		39.5		4-Oct-07		0:07:53		71.6		40.5		14-Nov-07		0:25:59		71.6		43

		4-Oct-07		2:07:10		75.2		34.5		4-Oct-07		2:06:20		72.21		38.5		4-Oct-07		2:07:53		70.41		40.5		14-Nov-07		2:25:59		70.41		44.5

		4-Oct-07		4:07:10		74.01		34		4-Oct-07		4:06:20		71		38.5		4-Oct-07		4:07:53		69.2		40		14-Nov-07		4:25:59		69.8		45

		4-Oct-07		6:07:10		74.01		33.5		4-Oct-07		6:06:20		70.41		37		4-Oct-07		6:07:53		68.61		39.5		14-Nov-07		6:25:59		69.8		47

		4-Oct-07		8:07:10		74.01		34.5		4-Oct-07		8:06:20		71.6		39		4-Oct-07		8:07:53		70.41		38		14-Nov-07		8:25:59		73.4		46

		4-Oct-07		10:07:10		74.6		36		4-Oct-07		10:06:20		72.21		41		4-Oct-07		10:07:53		71.6		35.5		14-Nov-07		10:25:59		74.6		47

		4-Oct-07		12:07:10		76.4		36		4-Oct-07		12:06:20		72.21		41.5		4-Oct-07		12:07:53		71.6		45.5		14-Nov-07		12:25:59		74.6		48.5

		4-Oct-07		14:07:10		75.81		35		4-Oct-07		14:06:20		72.21		36		4-Oct-07		14:07:53		72.21		35.5		14-Nov-07		14:25:59		75.2		49.5

		4-Oct-07		16:07:10		76.4		38.5		4-Oct-07		16:06:20		71		41.5		4-Oct-07		16:07:53		71		49		14-Nov-07		16:25:59		75.2		49.5

		4-Oct-07		18:07:10		76.4		33.5		4-Oct-07		18:06:20		70.41		40		4-Oct-07		18:07:53		70.41		41		14-Nov-07		18:25:59		75.2		49.5

		4-Oct-07		20:07:10		76.4		34		4-Oct-07		20:06:20		72.8		38.5		4-Oct-07		20:07:53		72.8		37.5		14-Nov-07		20:25:59		74.6		49

		4-Oct-07		22:07:10		76.4		31.5		4-Oct-07		22:06:20		72.8		35.5		4-Oct-07		22:07:53		72.8		35		14-Nov-07		22:25:59		74.01		52

		5-Oct-07		0:07:10		75.81		30.5		5-Oct-07		0:06:20		72.8		34.5		5-Oct-07		0:07:53		72.21		34.5		15-Nov-07		0:25:59		72.8		50.5

		5-Oct-07		2:07:10		75.2		29		5-Oct-07		2:06:20		72.8		32.5		5-Oct-07		2:07:53		71		33.5		15-Nov-07		2:25:59		71.6		51

		5-Oct-07		4:07:10		74.6		28.5		5-Oct-07		4:06:20		72.8		31		5-Oct-07		4:07:53		69.8		32.5		15-Nov-07		4:25:59		71		50

		5-Oct-07		6:07:10		74.6		29		5-Oct-07		6:06:20		72.21		31.5		5-Oct-07		6:07:53		69.8		33.5		15-Nov-07		6:25:59		69.8		49

		5-Oct-07		8:07:10		74.01		30.5		5-Oct-07		8:06:20		71.6		33.5		5-Oct-07		8:07:53		71		34		15-Nov-07		8:25:59		72.8		44.5

		5-Oct-07		10:07:10		74.6		31.5		5-Oct-07		10:06:20		72.21		36.5		5-Oct-07		10:07:53		71.6		32.5		15-Nov-07		10:25:59		74.6		47

		5-Oct-07		12:07:10		75.2		32		5-Oct-07		12:06:20		71.6		34		5-Oct-07		12:07:53		71.6		33		15-Nov-07		12:25:59		74.6		48.5

		5-Oct-07		14:07:10		75.2		33		5-Oct-07		14:06:20		72.21		39.5		5-Oct-07		14:07:53		71.6		38.5		15-Nov-07		14:25:59		75.2		48

		5-Oct-07		16:07:10		75.81		32		5-Oct-07		16:06:20		70.41		39.5		5-Oct-07		16:07:53		71		35.5		15-Nov-07		16:25:59		75.2		49

		5-Oct-07		18:07:10		75.2		30		5-Oct-07		18:06:20		69.8		35		5-Oct-07		18:07:53		70.41		34.5		15-Nov-07		18:25:59		74.6		50

		5-Oct-07		20:07:10		75.81		29.5		5-Oct-07		20:06:20		72.21		33.5		5-Oct-07		20:07:53		70.41		34.5		15-Nov-07		20:25:59		74.01		50

		5-Oct-07		22:07:10		75.2		29.5		5-Oct-07		22:06:20		72.21		33.5		5-Oct-07		22:07:53		69.8		34.5		15-Nov-07		22:25:59		74.01		49.5

		6-Oct-07		0:07:10		75.2		29.5		6-Oct-07		0:06:20		72.21		33.5		6-Oct-07		0:07:53		69.2		35		16-Nov-07		0:25:59		72.21		49.5

		6-Oct-07		2:07:10		74.01		30		6-Oct-07		2:06:20		71.6		33.5		6-Oct-07		2:07:53		68		35.5		16-Nov-07		2:25:59		71		48.5

		6-Oct-07		4:07:10		72.8		29.5		6-Oct-07		4:06:20		70.41		33		6-Oct-07		4:07:53		66.81		36		16-Nov-07		4:25:59		69.8		48

		6-Oct-07		6:07:10		72.8		29		6-Oct-07		6:06:20		72.21		30		6-Oct-07		6:07:53		68		34.5		16-Nov-07		6:25:59		69.8		47

		6-Oct-07		8:07:10		72.8		29.5		6-Oct-07		8:06:20		71.6		34.5		6-Oct-07		8:07:53		69.2		33		16-Nov-07		8:25:59		72.8		42.5

		6-Oct-07		10:07:10		73.4		30.5		6-Oct-07		10:06:20		71.6		33.5		6-Oct-07		10:07:53		71.6		31		16-Nov-07		10:25:59		74.01		44

		6-Oct-07		12:07:10		74.01		30.5		6-Oct-07		12:06:20		70.41		36		6-Oct-07		12:07:53		71.6		34.5		16-Nov-07		12:25:59		74.6		47

		6-Oct-07		14:07:10		75.2		28		6-Oct-07		14:06:20		69.2		32.5		6-Oct-07		14:07:53		71		30.5		16-Nov-07		14:25:59		74.6		49.5

		6-Oct-07		16:07:10		75.2		27		6-Oct-07		16:06:20		69.2		31.5		6-Oct-07		16:07:53		70.41		31.5		16-Nov-07		16:25:59		75.81		49.5

		6-Oct-07		18:07:10		75.81		27.5		6-Oct-07		18:06:20		69.2		33		6-Oct-07		18:07:53		71		30		16-Nov-07		18:25:59		75.81		49.5

		6-Oct-07		20:07:10		76.4		27.5		6-Oct-07		20:06:20		72.21		31.5		6-Oct-07		20:07:53		70.41		33.5		16-Nov-07		20:25:59		74.01		50

		6-Oct-07		22:07:10		75.81		27		6-Oct-07		22:06:20		73.4		31.5		6-Oct-07		22:07:53		70.41		33		16-Nov-07		22:25:59		73.4		51.5

		7-Oct-07		0:07:10		75.2		27		7-Oct-07		0:06:20		72.8		30.5		7-Oct-07		0:07:53		69.8		32.5		17-Nov-07		0:25:59		72.21		51

		7-Oct-07		2:07:10		74.6		27		7-Oct-07		2:06:20		72.21		31		7-Oct-07		2:07:53		68.61		33		17-Nov-07		2:25:59		71		51.5

		7-Oct-07		4:07:10		74.01		28		7-Oct-07		4:06:20		71.6		31.5		7-Oct-07		4:07:53		68		34		17-Nov-07		4:25:59		70.41		51.5

		7-Oct-07		6:07:10		72.8		28.5		7-Oct-07		6:06:20		71		32		7-Oct-07		6:07:53		66.81		35		17-Nov-07		6:25:59		70.41		52

		7-Oct-07		8:07:10		72.21		29		7-Oct-07		8:06:20		69.2		32.5		7-Oct-07		8:07:53		67.4		34		17-Nov-07		8:25:59		71		50.5

		7-Oct-07		10:07:10		71.6		31		7-Oct-07		10:06:20		68.61		34.5		7-Oct-07		10:07:53		68.61		35		17-Nov-07		10:25:59		71.6		50.5

		7-Oct-07		12:07:10		72.21		29		7-Oct-07		12:06:20		68.61		31		7-Oct-07		12:07:53		70.41		31.5		17-Nov-07		12:25:59		72.8		50

		7-Oct-07		14:07:10		72.8		26.5		7-Oct-07		14:06:20		69.2		28.5		7-Oct-07		14:07:53		70.41		29		17-Nov-07		14:25:59		75.2		49.5

		7-Oct-07		16:07:10		73.4		27		7-Oct-07		16:06:20		69.2		31		7-Oct-07		16:07:53		70.41		30.5		17-Nov-07		16:25:59		75.2		48

		7-Oct-07		18:07:10		74.01		26		7-Oct-07		18:06:20		69.8		29.5		7-Oct-07		18:07:53		71		29		17-Nov-07		18:25:59		74.6		49

		7-Oct-07		20:07:10		75.2		25		7-Oct-07		20:06:20		72.21		28.5		7-Oct-07		20:07:53		71		29		17-Nov-07		20:25:59		72.8		48.5

		7-Oct-07		22:07:10		75.2		26.5		7-Oct-07		22:06:20		72.8		31		7-Oct-07		22:07:53		70.41		31.5		17-Nov-07		22:25:59		72.21		49

		8-Oct-07		0:07:10		74.6		26.5		8-Oct-07		0:06:20		72.21		30.5		8-Oct-07		0:07:53		69.2		31.5		18-Nov-07		0:25:59		71		52

		8-Oct-07		2:07:10		73.4		25.5		8-Oct-07		2:06:20		71		29		8-Oct-07		2:07:53		68		31		18-Nov-07		2:25:59		70.41		51

		8-Oct-07		4:07:10		72.8		26		8-Oct-07		4:06:20		69.8		29		8-Oct-07		4:07:53		66.81		31.5		18-Nov-07		4:25:59		69.8		50.5

		8-Oct-07		6:07:10		71.6		26		8-Oct-07		6:06:20		69.2		29.5		8-Oct-07		6:07:53		65.6		32		18-Nov-07		6:25:59		69.2		51

		8-Oct-07		8:07:10		71		27		8-Oct-07		8:06:20		68.61		30		8-Oct-07		8:07:53		67.4		31		18-Nov-07		8:25:59		68.61		50.5

		8-Oct-07		10:07:10		71.6		28.5		8-Oct-07		10:06:20		68.61		32		8-Oct-07		10:07:53		68		32.5		18-Nov-07		10:25:59		68.61		51

		8-Oct-07		12:07:10		72.21		29.5		8-Oct-07		12:06:20		69.2		33		8-Oct-07		12:07:53		69.8		33		18-Nov-07		12:25:59		69.2		51.5

		8-Oct-07		14:07:10		72.8		31		8-Oct-07		14:06:20		69.2		34.5		8-Oct-07		14:07:53		70.41		34.5		18-Nov-07		14:25:59		69.8		52

		8-Oct-07		16:07:10		73.4		30.5		8-Oct-07		16:06:20		69.2		35.5		8-Oct-07		16:07:53		70.41		35.5		18-Nov-07		16:25:59		71.6		54

		8-Oct-07		18:07:10		74.01		31.5		8-Oct-07		18:06:20		69.2		35		8-Oct-07		18:07:53		71		34		18-Nov-07		18:25:59		72.21		54

		8-Oct-07		20:07:10		75.2		33.5		8-Oct-07		20:06:20		72.21		36		8-Oct-07		20:07:53		71.6		38.5		18-Nov-07		20:25:59		71		53

		8-Oct-07		22:07:10		75.2		34.5		8-Oct-07		22:06:20		72.21		39.5		8-Oct-07		22:07:53		71		40		18-Nov-07		22:25:59		69.8		53

		9-Oct-07		0:07:10		74.6		34		9-Oct-07		0:06:20		72.21		38.5		9-Oct-07		0:07:53		69.8		40		19-Nov-07		0:25:59		69.2		53

		9-Oct-07		2:07:10		74.01		33.5		9-Oct-07		2:06:20		71.6		37.5		9-Oct-07		2:07:53		68.61		40		19-Nov-07		2:25:59		69.2		53

		9-Oct-07		4:07:10		73.4		33		9-Oct-07		4:06:20		71		36.5		9-Oct-07		4:07:53		67.4		39.5		19-Nov-07		4:25:59		68.61		53

		9-Oct-07		6:07:10		73.4		32.5		9-Oct-07		6:06:20		69.8		36		9-Oct-07		6:07:53		68.61		37.5		19-Nov-07		6:25:59		68.61		53

		9-Oct-07		8:07:10		72.8		33.5		9-Oct-07		8:06:20		69.8		38.5		9-Oct-07		8:07:53		70.41		36		19-Nov-07		8:25:59		68		53

		9-Oct-07		10:07:10		73.4		37.5		9-Oct-07		10:06:20		71		45		9-Oct-07		10:07:53		71.6		37		19-Nov-07		10:25:59		68.61		53

		9-Oct-07		12:07:10		74.6		35.5		9-Oct-07		12:06:20		71		41		9-Oct-07		12:07:53		71.6		42		19-Nov-07		12:25:59		68.61		55

		9-Oct-07		14:07:10		74.6		36		9-Oct-07		14:06:20		71		41		9-Oct-07		14:07:53		71.6		38.5		19-Nov-07		14:25:59		69.8		56

		9-Oct-07		16:07:10		75.2		34		9-Oct-07		16:06:20		69.8		42		9-Oct-07		16:07:53		71.6		37		19-Nov-07		16:25:59		71		57.5

		9-Oct-07		18:07:10		74.01		36.5		9-Oct-07		18:06:20		69.2		44.5		9-Oct-07		18:07:53		71		41.5		19-Nov-07		18:25:59		71.6		56.5

		9-Oct-07		20:07:10		75.81		32		9-Oct-07		20:06:20		72.8		35.5		9-Oct-07		20:07:53		71		37.5		19-Nov-07		20:25:59		71		55

		9-Oct-07		22:07:10		76.4		33.5		9-Oct-07		22:06:20		73.4		38.5		9-Oct-07		22:07:53		71.6		39		19-Nov-07		22:25:59		70.41		54.5

		10-Oct-07		0:07:10		75.81		34.5		10-Oct-07		0:06:20		72.8		39.5		10-Oct-07		0:07:53		70.41		41		20-Nov-07		0:25:59		69.2		53.5

		10-Oct-07		2:07:10		75.2		35.5		10-Oct-07		2:06:20		72.21		40.5		10-Oct-07		2:07:53		69.8		42		20-Nov-07		2:25:59		68.61		52.5

		10-Oct-07		4:07:10		74.6		36		10-Oct-07		4:06:20		72.21		40.5		10-Oct-07		4:07:53		69.2		43		20-Nov-07		4:25:59		68		53

		10-Oct-07		6:07:10		74.6		37.5		10-Oct-07		6:06:20		71		44.5		10-Oct-07		6:07:53		69.2		45		20-Nov-07		6:25:59		68.61		54.5

		10-Oct-07		8:07:10		74.01		39		10-Oct-07		8:06:20		71		38.5		10-Oct-07		8:07:53		71.6		44		20-Nov-07		8:25:59		71.6		54

		10-Oct-07		10:07:10		74.01		43		10-Oct-07		10:06:20		69.8		48.5		10-Oct-07		10:07:53		71		44		20-Nov-07		10:25:59		74.01		55

		10-Oct-07		12:07:10		74.6		42.5		10-Oct-07		12:06:20		70.41		48.5		10-Oct-07		12:07:53		71.6		43		20-Nov-07		12:25:59		74.01		53.5

		10-Oct-07		14:07:10		74.6		44.5		10-Oct-07		14:06:20		71		50.5		10-Oct-07		14:07:53		71		51.5		20-Nov-07		14:25:59		73.4		48.5

		10-Oct-07		16:07:10		74.6		42		10-Oct-07		16:06:20		69.8		57		10-Oct-07		16:07:53		70.41		49		20-Nov-07		16:25:59		74.01		45

		10-Oct-07		18:07:10		74.01		41		10-Oct-07		18:06:20		69.8		51		10-Oct-07		18:07:53		70.41		48		20-Nov-07		18:25:59		74.01		43

		10-Oct-07		20:07:10		75.2		41		10-Oct-07		20:06:20		72.21		47		10-Oct-07		20:07:53		69.8		50		20-Nov-07		20:25:59		72.21		43

		10-Oct-07		22:07:10		75.2		43		10-Oct-07		22:06:20		72.21		50.5		10-Oct-07		22:07:53		69.8		50		20-Nov-07		22:25:59		71		44.5

		11-Oct-07		0:07:10		74.6		44		11-Oct-07		0:06:20		72.21		51		11-Oct-07		0:07:53		69.8		51		21-Nov-07		0:25:59		69.8		44

		11-Oct-07		2:07:10		74.6		44		11-Oct-07		2:06:20		71.6		50.5		11-Oct-07		2:07:53		69.2		51		21-Nov-07		2:25:59		68.61		43

		11-Oct-07		4:07:10		74.01		44		11-Oct-07		4:06:20		71.6		49.5		11-Oct-07		4:07:53		69.2		51.5		21-Nov-07		4:25:59		68		42.5

		11-Oct-07		6:07:10		74.01		44		11-Oct-07		6:06:20		71		50.5		11-Oct-07		6:07:53		69.2		51		21-Nov-07		6:25:59		68		41

		11-Oct-07		8:07:10		73.4		44.5		11-Oct-07		8:06:20		70.41		45		11-Oct-07		8:07:53		71		49		21-Nov-07		8:25:59		71.6		37

		11-Oct-07		10:07:10		73.4		43		11-Oct-07		10:06:20		71.6		45		11-Oct-07		10:07:53		71		48		21-Nov-07		10:25:59		71.6		38

		11-Oct-07		12:07:10		74.01		46		11-Oct-07		12:06:20		70.41		51		11-Oct-07		12:07:53		71.6		49		21-Nov-07		12:25:59		72.21		38.5

		11-Oct-07		14:07:10		74.6		41.5		11-Oct-07		14:06:20		71		41		11-Oct-07		14:07:53		71		49.5		21-Nov-07		14:25:59		72.8		37.5

		11-Oct-07		16:07:10		75.2		46.5		11-Oct-07		16:06:20		69.2		59.5		11-Oct-07		16:07:53		70.41		53		21-Nov-07		16:25:59		73.4		37

		11-Oct-07		18:07:10		74.6		39.5		11-Oct-07		18:06:20		69.8		45		11-Oct-07		18:07:53		70.41		47		21-Nov-07		18:25:59		73.4		38

		11-Oct-07		20:07:10		75.2		40		11-Oct-07		20:06:20		72.21		45		11-Oct-07		20:07:53		70.41		46		21-Nov-07		20:25:59		71.6		38

		11-Oct-07		22:07:10		74.6		39.5		11-Oct-07		22:06:20		72.21		44		11-Oct-07		22:07:53		69.8		45.5		21-Nov-07		22:25:59		69.8		38.5

		12-Oct-07		0:07:10		74.01		38.5		12-Oct-07		0:06:20		72.21		42.5		12-Oct-07		0:07:53		68.61		45		22-Nov-07		0:25:59		68.61		38.5

		12-Oct-07		2:07:10		73.4		38		12-Oct-07		2:06:20		71.6		42		12-Oct-07		2:07:53		67.4		45.5		22-Nov-07		2:25:59		67.4		37.5

		12-Oct-07		4:07:10		72.21		38.5		12-Oct-07		4:06:20		71		42.5		12-Oct-07		4:07:53		66.81		46.5		22-Nov-07		4:25:59		66.81		36.5

		12-Oct-07		6:07:10		72.21		38		12-Oct-07		6:06:20		70.41		41.5		12-Oct-07		6:07:53		68.61		44		22-Nov-07		6:25:59		67.4		35

		12-Oct-07		8:07:10		72.21		38		12-Oct-07		8:06:20		70.41		43.5		12-Oct-07		8:07:53		69.8		42		22-Nov-07		8:25:59		70.41		32.5

		12-Oct-07		10:07:10		72.8		43.5		12-Oct-07		10:06:20		71		51.5		12-Oct-07		10:07:53		71.6		40		22-Nov-07		10:25:59		71.6		33.5

		12-Oct-07		12:07:10		73.4		40.5		12-Oct-07		12:06:20		70.41		45.5		12-Oct-07		12:07:53		71.6		49		22-Nov-07		12:25:59		72.21		35

		12-Oct-07		14:07:10		73.4		43.5		12-Oct-07		14:06:20		69.8		41		12-Oct-07		14:07:53		71		44.5		22-Nov-07		14:25:59		73.4		34

		12-Oct-07		16:07:10		74.01		45		12-Oct-07		16:06:20		69.2		56.5		12-Oct-07		16:07:53		71		46.5		22-Nov-07		16:25:59		72.8		32.5

		12-Oct-07		18:07:10		74.01		39.5		12-Oct-07		18:06:20		69.8		46.5		12-Oct-07		18:07:53		70.41		44.5		22-Nov-07		18:25:59		72.8		34.5

		12-Oct-07		20:07:10		74.6		38.5		12-Oct-07		20:06:20		72.21		42		12-Oct-07		20:07:53		70.41		44		22-Nov-07		20:25:59		71		34

		12-Oct-07		22:07:10		75.2		37		12-Oct-07		22:06:20		72.8		40.5		12-Oct-07		22:07:53		69.8		43.5		22-Nov-07		22:25:59		69.2		35

		13-Oct-07		0:07:10		74.6		36.5		13-Oct-07		0:06:20		72.21		40		13-Oct-07		0:07:53		68.61		44		23-Nov-07		0:25:59		68		35

		13-Oct-07		2:07:10		74.01		38		13-Oct-07		2:06:20		72.21		42		13-Oct-07		2:07:53		68		46		23-Nov-07		2:25:59		66.81		34.5

		13-Oct-07		4:07:10		74.01		39.5		13-Oct-07		4:06:20		72.21		44		13-Oct-07		4:07:53		67.4		48.5		23-Nov-07		4:25:59		66.2		34

		13-Oct-07		6:07:10		73.4		40		13-Oct-07		6:06:20		71		46		13-Oct-07		6:07:53		68.61		48		23-Nov-07		6:25:59		66.81		32.5

		13-Oct-07		8:07:10		72.8		44		13-Oct-07		8:06:20		71		45		13-Oct-07		8:07:53		70.41		48.5		23-Nov-07		8:25:59		69.2		30.5

		13-Oct-07		10:07:10		72.8		44		13-Oct-07		10:06:20		71		43		13-Oct-07		10:07:53		71		50		23-Nov-07		10:25:59		71.6		31

		13-Oct-07		12:07:10		73.4		44		13-Oct-07		12:06:20		70.41		54.5		13-Oct-07		12:07:53		71.6		52		23-Nov-07		12:25:59		70.41		33

		13-Oct-07		14:07:10		73.4		46.5		13-Oct-07		14:06:20		70.41		51		13-Oct-07		14:07:53		71		50		23-Nov-07		14:25:59		71		33.5

		13-Oct-07		16:07:10		72.8		49.5		13-Oct-07		16:06:20		69.2		61		13-Oct-07		16:07:53		71		53		23-Nov-07		16:25:59		71		32.5

		13-Oct-07		18:07:10		72.8		44		13-Oct-07		18:06:20		69.8		50		13-Oct-07		18:07:53		70.41		50.5		23-Nov-07		18:25:59		71		34

		13-Oct-07		20:07:10		73.4		43.5		13-Oct-07		20:06:20		71		48		13-Oct-07		20:07:53		69.8		48.5		23-Nov-07		20:25:59		70.41		34.5

		13-Oct-07		22:07:10		73.4		42.5		13-Oct-07		22:06:20		71.6		46.5		13-Oct-07		22:07:53		68.61		49		23-Nov-07		22:25:59		68.61		34.5

		14-Oct-07		0:07:10		72.21		41.5		14-Oct-07		0:06:20		71		45		14-Oct-07		0:07:53		67.4		49		24-Nov-07		0:25:59		67.4		34.5

		14-Oct-07		2:07:10		71.6		40.5		14-Oct-07		2:06:20		69.8		43.5		14-Oct-07		2:07:53		66.2		48		24-Nov-07		2:25:59		66.81		34

		14-Oct-07		4:07:10		71		40		14-Oct-07		4:06:20		69.2		42.5		14-Oct-07		4:07:53		65.6		47.5		24-Nov-07		4:25:59		66.2		33.5

		14-Oct-07		6:07:10		70.41		39		14-Oct-07		6:06:20		68.61		41		14-Oct-07		6:07:53		65.6		46		24-Nov-07		6:25:59		66.81		32.5

		14-Oct-07		8:07:10		71		37.5		14-Oct-07		8:06:20		68.61		40.5		14-Oct-07		8:07:53		67.4		41.5		24-Nov-07		8:25:59		68.61		29.5

		14-Oct-07		10:07:10		71.6		43.5		14-Oct-07		10:06:20		68.61		49		14-Oct-07		10:07:53		68.61		48.5		24-Nov-07		10:25:59		70.41		25.5

		14-Oct-07		12:07:10		72.21		46		14-Oct-07		12:06:20		68.61		49.5		14-Oct-07		12:07:53		69.8		49.5		24-Nov-07		12:25:59		69.8		24

		14-Oct-07		14:07:10		72.8		47		14-Oct-07		14:06:20		69.2		54		14-Oct-07		14:07:53		70.41		50		24-Nov-07		14:25:59		70.41		23

		14-Oct-07		16:07:10		72.8		45.5		14-Oct-07		16:06:20		69.2		45.5		14-Oct-07		16:07:53		70.41		45.5		24-Nov-07		16:25:59		71.6		22.5

		14-Oct-07		18:07:10		73.4		46		14-Oct-07		18:06:20		69.2		53.5		14-Oct-07		18:07:53		70.41		52.5		24-Nov-07		18:25:59		71		22.5

		14-Oct-07		20:07:10		74.6		44.5		14-Oct-07		20:06:20		71.6		49		14-Oct-07		20:07:53		69.8		50.5		24-Nov-07		20:25:59		69.8		24.5

		14-Oct-07		22:07:10		74.01		43		14-Oct-07		22:06:20		72.21		47		14-Oct-07		22:07:53		69.2		50		24-Nov-07		22:25:59		68.61		27

		15-Oct-07		0:07:10		74.01		43		15-Oct-07		0:06:20		72.21		47		15-Oct-07		0:07:53		68.61		51.5		25-Nov-07		0:25:59		67.4		28

		15-Oct-07		2:07:10		74.01		43.5		15-Oct-07		2:06:20		72.21		47		15-Oct-07		2:07:53		68		52		25-Nov-07		2:25:59		66.81		28.5

		15-Oct-07		4:07:10		73.4		43.5		15-Oct-07		4:06:20		71.6		47		15-Oct-07		4:07:53		67.4		52		25-Nov-07		4:25:59		66.2		28.5

		15-Oct-07		6:07:10		72.8		43.5		15-Oct-07		6:06:20		71		43		15-Oct-07		6:07:53		66.81		52.5		25-Nov-07		6:25:59		65.6		28.5

		15-Oct-07		8:07:10		71.6		45		15-Oct-07		8:06:20		69.2		50		15-Oct-07		8:07:53		68.61		49.5		25-Nov-07		8:25:59		65.6		28

		15-Oct-07		10:07:10		71		46.5		15-Oct-07		10:06:20		68.61		52		15-Oct-07		10:07:53		68		52		25-Nov-07		10:25:59		65.6		29

		15-Oct-07		12:07:10		71		46		15-Oct-07		12:06:20		69.2		52		15-Oct-07		12:07:53		68		53		25-Nov-07		12:25:59		66.2		30.5

		15-Oct-07		14:07:10		71.6		48		15-Oct-07		14:06:20		69.2		45		15-Oct-07		14:07:53		69.2		53		25-Nov-07		14:25:59		68		30

		15-Oct-07		16:07:10		72.21		49.5		15-Oct-07		16:06:20		69.2		49.5		15-Oct-07		16:07:53		69.8		53.5		25-Nov-07		16:25:59		68		30.5

		15-Oct-07		18:07:10		72.8		48		15-Oct-07		18:06:20		69.2		54.5		15-Oct-07		18:07:53		69.8		53.5		25-Nov-07		18:25:59		68		31.5

		15-Oct-07		20:07:10		74.01		44		15-Oct-07		20:06:20		71.6		48		15-Oct-07		20:07:53		69.8		50		25-Nov-07		20:25:59		67.4		32

		15-Oct-07		22:07:10		73.4		42.5		15-Oct-07		22:06:20		71.6		45.5		15-Oct-07		22:07:53		68		50		25-Nov-07		22:25:59		66.81		33

		16-Oct-07		0:07:10		72.8		42		16-Oct-07		0:06:20		71		45.5		16-Oct-07		0:07:53		66.81		50.5		26-Nov-07		0:25:59		66.81		33.5

		16-Oct-07		2:07:10		72.21		42		16-Oct-07		2:06:20		71		45.5		16-Oct-07		2:07:53		66.2		51		26-Nov-07		2:25:59		66.2		33.5

		16-Oct-07		4:07:10		72.21		42.5		16-Oct-07		4:06:20		70.41		46		16-Oct-07		4:07:53		65.6		51.5		26-Nov-07		4:25:59		66.2		34

		16-Oct-07		6:07:10		72.21		43		16-Oct-07		6:06:20		70.41		46.5		16-Oct-07		6:07:53		68.61		48.5		26-Nov-07		6:25:59		66.2		34

		16-Oct-07		8:07:10		72.21		45.5		16-Oct-07		8:06:20		70.41		51.5		16-Oct-07		8:07:53		68.61		49.5		26-Nov-07		8:25:59		65.6		34.5

		16-Oct-07		10:07:10		72.8		45.5		16-Oct-07		10:06:20		71.6		54.5		16-Oct-07		10:07:53		71		49.5		26-Nov-07		10:25:59		65.6		35.5

		16-Oct-07		12:07:10		72.8		48.5		16-Oct-07		12:06:20		69.8		44.5		16-Oct-07		12:07:53		71.6		53		26-Nov-07		12:25:59		66.2		36.5

		16-Oct-07		14:07:10		72.8		53		16-Oct-07		14:06:20		71		54		16-Oct-07		14:07:53		71		57.5		26-Nov-07		14:25:59		66.2		35.5

		16-Oct-07		16:07:10		74.01		48.5		16-Oct-07		16:06:20		69.8		59.5		16-Oct-07		16:07:53		70.41		55.5		26-Nov-07		16:25:59		66.81		35

		16-Oct-07		18:07:10		73.4		47.5		16-Oct-07		18:06:20		70.41		57.5		16-Oct-07		18:07:53		69.8		54.5		26-Nov-07		18:25:59		67.4		35.5

		16-Oct-07		20:07:10		74.6		48		16-Oct-07		20:06:20		72.21		53		16-Oct-07		20:07:53		70.41		54.5		26-Nov-07		20:25:59		66.81		36

		16-Oct-07		22:07:10		74.6		47		16-Oct-07		22:06:20		72.21		51		16-Oct-07		22:07:53		69.8		54		26-Nov-07		22:25:59		66.2		35.5

		17-Oct-07		0:07:10		74.01		45		17-Oct-07		0:06:20		72.8		48.5		17-Oct-07		0:07:53		69.2		52.5		27-Nov-07		0:25:59		65.6		35.5

		17-Oct-07		2:07:10		73.4		43		17-Oct-07		2:06:20		71.6		45.5		17-Oct-07		2:07:53		68		51		27-Nov-07		2:25:59		65.6		34.5

		17-Oct-07		4:07:10		72.8		42.5		17-Oct-07		4:06:20		71		45		17-Oct-07		4:07:53		66.81		50.5		27-Nov-07		4:25:59		65.01		34

		17-Oct-07		6:07:10		72.8		43		17-Oct-07		6:06:20		70.41		44.5		17-Oct-07		6:07:53		68		49		27-Nov-07		6:25:59		66.2		32.5

		17-Oct-07		8:07:10		71.6		43.5		17-Oct-07		8:06:20		69.8		48		17-Oct-07		8:07:53		69.8		46		27-Nov-07		8:25:59		68.61		30.5

		17-Oct-07		10:07:10		72.8		43.5		17-Oct-07		10:06:20		71		52.5		17-Oct-07		10:07:53		71		46		27-Nov-07		10:25:59		70.41		32.5

		17-Oct-07		12:07:10		73.4		46		17-Oct-07		12:06:20		71		55.5		17-Oct-07		12:07:53		71.6		46		27-Nov-07		12:25:59		72.21		33.5

		17-Oct-07		14:07:10		73.4		47		17-Oct-07		14:06:20		71		41		17-Oct-07		14:07:53		71		52.5		27-Nov-07		14:25:59		72.8		34.5

		17-Oct-07		16:07:10		72.8		53		17-Oct-07		16:06:20		69.2		55.5		17-Oct-07		16:07:53		70.41		60.5		27-Nov-07		16:25:59		73.4		35.5

		17-Oct-07		18:07:10		72.8		52		17-Oct-07		18:06:20		69.2		60		17-Oct-07		18:07:53		69.8		55.5		27-Nov-07		18:25:59		72.8		37

		17-Oct-07		20:07:10		72.8		46.5		17-Oct-07		20:06:20		71		49.5		17-Oct-07		20:07:53		69.8		51.5		27-Nov-07		20:25:59		71		37

		17-Oct-07		22:07:10		72.21		44		17-Oct-07		22:06:20		71		46.5		17-Oct-07		22:07:53		68		49.5		27-Nov-07		22:25:59		69.8		36.5

		18-Oct-07		0:07:10		71		42		18-Oct-07		0:06:20		69.8		44		18-Oct-07		0:07:53		66.81		48.5		28-Nov-07		0:25:59		68.61		36.5

		18-Oct-07		2:07:10		70.41		41		18-Oct-07		2:06:20		69.2		43		18-Oct-07		2:07:53		66.2		47.5		28-Nov-07		2:25:59		67.4		36.5

		18-Oct-07		4:07:10		70.41		41.5		18-Oct-07		4:06:20		69.2		44		18-Oct-07		4:07:53		66.2		48.5		28-Nov-07		4:25:59		66.81		36.5

		18-Oct-07		6:07:10		71		43.5		18-Oct-07		6:06:20		69.8		46		18-Oct-07		6:07:53		68		48		28-Nov-07		6:25:59		67.4		36

		18-Oct-07		8:07:10		71.6		44.5		18-Oct-07		8:06:20		71		49.5		18-Oct-07		8:07:53		69.8		46		28-Nov-07		8:25:59		69.8		35

		18-Oct-07		10:07:10		74.01		45.5		18-Oct-07		10:06:20		74.01		41.5		18-Oct-07		10:07:53		71		51.5		28-Nov-07		10:25:59		73.4		36

		18-Oct-07		12:07:10		74.6		44		18-Oct-07		12:06:20		73.4		46.5		18-Oct-07		12:07:53		71.6		50.5		28-Nov-07		12:25:59		72.8		38.5

		18-Oct-07		14:07:10		75.2		41.5		18-Oct-07		14:06:20		74.6		37.5		18-Oct-07		14:07:53		71.6		45		28-Nov-07		14:25:59		73.4		35

		18-Oct-07		16:07:10		75.2		41		18-Oct-07		16:06:20		72.21		41.5		18-Oct-07		16:07:53		70.41		47		28-Nov-07		16:25:59		74.01		34

		18-Oct-07		18:07:10		74.6		41.5		18-Oct-07		18:06:20		71.6		42.5		18-Oct-07		18:07:53		70.41		48.5		28-Nov-07		18:25:59		74.01		35.5

		18-Oct-07		20:07:10		74.6		41		18-Oct-07		20:06:20		72.8		44		18-Oct-07		20:07:53		69.8		47		28-Nov-07		20:25:59		72.21		37

		18-Oct-07		22:07:10		73.4		40.5		18-Oct-07		22:06:20		72.21		43		18-Oct-07		22:07:53		68.61		47.5		28-Nov-07		22:25:59		71		37

		19-Oct-07		0:07:10		72.8		41		19-Oct-07		0:06:20		72.21		43.5		19-Oct-07		0:07:53		67.4		48.5		29-Nov-07		0:25:59		69.8		37

		19-Oct-07		2:07:10		72.21		41.5		19-Oct-07		2:06:20		71		43.5		19-Oct-07		2:07:53		66.81		49.5		29-Nov-07		2:25:59		68.61		37

		19-Oct-07		4:07:10		71.6		42.5		19-Oct-07		4:06:20		71		44.5		19-Oct-07		4:07:53		66.2		52		29-Nov-07		4:25:59		67.4		36.5

		19-Oct-07		6:07:10		71.6		43		19-Oct-07		6:06:20		71		45.5		19-Oct-07		6:07:53		68		49		29-Nov-07		6:25:59		67.4		34.5

		19-Oct-07		8:07:10		72.21		44		19-Oct-07		8:06:20		72.21		47		19-Oct-07		8:07:53		69.2		48		29-Nov-07		8:25:59		69.8		32

		19-Oct-07		10:07:10		72.8		43.5		19-Oct-07		10:06:20		72.21		40		19-Oct-07		10:07:53		71		49.5		29-Nov-07		10:25:59		72.21		33

		19-Oct-07		12:07:10		74.01		44.5		19-Oct-07		12:06:20		72.21		49.5		19-Oct-07		12:07:53		71.6		51		29-Nov-07		12:25:59		72.21		33

		19-Oct-07		14:07:10		75.2		47		19-Oct-07		14:06:20		72.8		47		19-Oct-07		14:07:53		71		54		29-Nov-07		14:25:59		73.4		32.5

		19-Oct-07		16:07:10		74.6		47		19-Oct-07		16:06:20		71.6		45.5		19-Oct-07		16:07:53		71		48		29-Nov-07		16:25:59		73.4		32

		19-Oct-07		18:07:10		74.6		51.5		19-Oct-07		18:06:20		71		56.5		19-Oct-07		18:07:53		70.41		58.5		29-Nov-07		18:25:59		72.8		30.5

		19-Oct-07		20:07:10		74.6		51.5		19-Oct-07		20:06:20		72.8		57		19-Oct-07		20:07:53		70.41		58		29-Nov-07		20:25:59		71		32

		19-Oct-07		22:07:10		74.01		52.5		19-Oct-07		22:06:20		73.4		56		19-Oct-07		22:07:53		70.41		59		29-Nov-07		22:25:59		69.8		32.5

		20-Oct-07		0:07:10		74.01		53		20-Oct-07		0:06:20		72.8		57.5		20-Oct-07		0:07:53		70.41		60.5		30-Nov-07		0:25:59		69.2		33

		20-Oct-07		2:07:10		73.4		55.5		20-Oct-07		2:06:20		72.8		59		20-Oct-07		2:07:53		69.8		61.5		30-Nov-07		2:25:59		68		32.5

		20-Oct-07		4:07:10		73.4		56		20-Oct-07		4:06:20		72.8		59.5		20-Oct-07		4:07:53		69.8		62		30-Nov-07		4:25:59		67.4		32.5

		20-Oct-07		6:07:10		74.01		56		20-Oct-07		6:06:20		72.8		59		20-Oct-07		6:07:53		70.41		65		30-Nov-07		6:25:59		67.4		31.5

		20-Oct-07		8:07:10		73.4		52.5		20-Oct-07		8:06:20		71		55		20-Oct-07		8:07:53		71		63.5		30-Nov-07		8:25:59		69.2		29.5

		20-Oct-07		10:07:10		73.4		54.5		20-Oct-07		10:06:20		71		54		20-Oct-07		10:07:53		71.6		63.5		30-Nov-07		10:25:59		72.21		31.5

		20-Oct-07		12:07:10		74.6		53		20-Oct-07		12:06:20		71		59.5		20-Oct-07		12:07:53		71.6		58		30-Nov-07		12:25:59		71.6		33

		20-Oct-07		14:07:10		75.2		54.5		20-Oct-07		14:06:20		71		48.5		20-Oct-07		14:07:53		71		62		30-Nov-07		14:25:59		74.01		31.5

		20-Oct-07		16:07:10		74.6		56.5		20-Oct-07		16:06:20		69.8		67		20-Oct-07		16:07:53		70.41		70		30-Nov-07		16:25:59		74.6		30.5

		20-Oct-07		18:07:10		73.4		57.5		20-Oct-07		18:06:20		69.2		61		20-Oct-07		18:07:53		70.41		59.5		30-Nov-07		18:25:59		74.01		29

		20-Oct-07		20:07:10		74.6		53.5		20-Oct-07		20:06:20		72.21		58		20-Oct-07		20:07:53		69.8		61.5		30-Nov-07		20:25:59		72.8		27.5

		20-Oct-07		22:07:10		74.01		49		20-Oct-07		22:06:20		72.21		51.5		20-Oct-07		22:07:53		69.2		56.5		30-Nov-07		22:25:59		71		30

		21-Oct-07		0:07:10		73.4		45		21-Oct-07		0:06:20		71.6		46.5		21-Oct-07		0:07:53		68		53		1-Dec-07		0:25:59		69.2		31

		21-Oct-07		2:07:10		72.21		44.5		21-Oct-07		2:06:20		71		47		21-Oct-07		2:07:53		66.81		53.5		1-Dec-07		2:25:59		68		31

		21-Oct-07		4:07:10		71.6		45		21-Oct-07		4:06:20		71		47		21-Oct-07		4:07:53		66.2		54		1-Dec-07		4:25:59		67.4		31

		21-Oct-07		6:07:10		71		43		21-Oct-07		6:06:20		70.41		45		21-Oct-07		6:07:53		65.6		52		1-Dec-07		6:25:59		68		29.5

		21-Oct-07		8:07:10		70.41		42		21-Oct-07		8:06:20		68.61		44		21-Oct-07		8:07:53		68		46		1-Dec-07		8:25:59		71		28

		21-Oct-07		10:07:10		70.41		45		21-Oct-07		10:06:20		69.2		50		21-Oct-07		10:07:53		67.4		52		1-Dec-07		10:25:59		72.8		28

		21-Oct-07		12:07:10		71		41.5		21-Oct-07		12:06:20		68.61		42.5		21-Oct-07		12:07:53		69.2		45		1-Dec-07		12:25:59		74.01		26.5

		21-Oct-07		14:07:10		71		37.5		21-Oct-07		14:06:20		69.2		37		21-Oct-07		14:07:53		69.2		40.5		1-Dec-07		14:25:59		74.01		27

		21-Oct-07		16:07:10		71		36		21-Oct-07		16:06:20		68.61		38		21-Oct-07		16:07:53		69.2		38		1-Dec-07		16:25:59		74.6		26

		21-Oct-07		18:07:10		71.6		35		21-Oct-07		18:06:20		68.61		37		21-Oct-07		18:07:53		69.8		37		1-Dec-07		18:25:59		75.2		26.5

		21-Oct-07		20:07:10		72.21		35.5		21-Oct-07		20:06:20		70.41		38		21-Oct-07		20:07:53		68.61		40		1-Dec-07		20:25:59		74.01		25

		21-Oct-07		22:07:10		72.21		36		21-Oct-07		22:06:20		71		38		21-Oct-07		22:07:53		67.4		42		1-Dec-07		22:25:59		70.41		27

		22-Oct-07		0:07:10		71.6		36		22-Oct-07		0:06:20		70.41		38		22-Oct-07		0:07:53		66.2		42.5		2-Dec-07		0:25:59		68.61		28

		22-Oct-07		2:07:10		71		35.5		22-Oct-07		2:06:20		69.8		37.5		22-Oct-07		2:07:53		65.01		43		2-Dec-07		2:25:59		67.4		27.5

		22-Oct-07		4:07:10		70.41		35.5		22-Oct-07		4:06:20		69.8		37		22-Oct-07		4:07:53		64.4		43		2-Dec-07		4:25:59		66.2		27.5

		22-Oct-07		6:07:10		69.8		34.5		22-Oct-07		6:06:20		69.2		36.5		22-Oct-07		6:07:53		63.8		42.5		2-Dec-07		6:25:59		66.2		27

		22-Oct-07		8:07:10		69.2		34.5		22-Oct-07		8:06:20		68.61		36.5		22-Oct-07		8:07:53		68		37.5		2-Dec-07		8:25:59		66.2		26

		22-Oct-07		10:07:10		69.8		33.5		22-Oct-07		10:06:20		68.61		35		22-Oct-07		10:07:53		67.4		37.5		2-Dec-07		10:25:59		66.2		26.5

		22-Oct-07		12:07:10		69.8		33		22-Oct-07		12:06:20		68.61		34		22-Oct-07		12:07:53		68.61		35.5		2-Dec-07		12:25:59		66.81		29

		22-Oct-07		14:07:10		71		31		22-Oct-07		14:06:20		68.61		32		22-Oct-07		14:07:53		69.8		34		2-Dec-07		14:25:59		67.4		29.5

		22-Oct-07		16:07:10		72.21		30.5		22-Oct-07		16:06:20		68.61		31		22-Oct-07		16:07:53		70.41		33.5		2-Dec-07		16:25:59		68		30

		22-Oct-07		18:07:10		72.21		30.5		22-Oct-07		18:06:20		69.2		32.5		22-Oct-07		18:07:53		70.41		33.5		2-Dec-07		18:25:59		67.4		30

		22-Oct-07		20:07:10		74.01		28		22-Oct-07		20:06:20		72.21		29.5		22-Oct-07		20:07:53		71.6		31		2-Dec-07		20:25:59		66.81		31

		22-Oct-07		22:07:10		74.01		32		22-Oct-07		22:06:20		72.8		35		22-Oct-07		22:07:53		71		36.5		2-Dec-07		22:25:59		66.2		31

		23-Oct-07		0:07:10		73.4		33		23-Oct-07		0:06:20		72.21		36		23-Oct-07		0:07:53		69.2		38		3-Dec-07		0:25:59		66.2		30.5

		23-Oct-07		2:07:10		72.8		33.5		23-Oct-07		2:06:20		71.6		36.5		23-Oct-07		2:07:53		68.61		39		3-Dec-07		2:25:59		66.2		31

		23-Oct-07		4:07:10		72.21		34		23-Oct-07		4:06:20		71		36.5		23-Oct-07		4:07:53		66.81		40		3-Dec-07		4:25:59		66.2		32.5

		23-Oct-07		6:07:10		71.6		34.5		23-Oct-07		6:06:20		69.8		36.5		23-Oct-07		6:07:53		68		39.5		3-Dec-07		6:25:59		66.2		34.5

		23-Oct-07		8:07:10		71.6		35.5		23-Oct-07		8:06:20		69.8		38.5		23-Oct-07		8:07:53		69.2		38		3-Dec-07		8:25:59		66.2		35.5

		23-Oct-07		10:07:10		72.21		37.5		23-Oct-07		10:06:20		70.41		43.5		23-Oct-07		10:07:53		70.41		42		3-Dec-07		10:25:59		66.81		35.5

		23-Oct-07		12:07:10		72.8		35		23-Oct-07		12:06:20		70.41		36.5		23-Oct-07		12:07:53		71.6		34.5		3-Dec-07		12:25:59		67.4		36.5

		23-Oct-07		14:07:10		74.6		38.5		23-Oct-07		14:06:20		69.8		45		23-Oct-07		14:07:53		71.6		41		3-Dec-07		14:25:59		67.4		37.5

		23-Oct-07		16:07:10		75.81		35		23-Oct-07		16:06:20		71		41.5		23-Oct-07		16:07:53		71.6		42.5		3-Dec-07		16:25:59		68		39

		23-Oct-07		18:07:10		75.2		34		23-Oct-07		18:06:20		71.6		36		23-Oct-07		18:07:53		71		36		3-Dec-07		18:25:59		68		39.5

		23-Oct-07		20:07:10		75.81		34.5		23-Oct-07		20:06:20		72.8		38		23-Oct-07		20:07:53		70.41		40.5		3-Dec-07		20:25:59		68		40

		23-Oct-07		22:07:10		75.2		36		23-Oct-07		22:06:20		72.21		40		23-Oct-07		22:07:53		71.6		40.5		3-Dec-07		22:25:59		68		42

		24-Oct-07		0:07:10		74.6		36.5		24-Oct-07		0:06:20		72.21		40.5		24-Oct-07		0:07:53		71		42		4-Dec-07		0:25:59		68		42

		24-Oct-07		2:07:10		74.01		36.5		24-Oct-07		2:06:20		72.21		40		24-Oct-07		2:07:53		69.2		42.5		4-Dec-07		2:25:59		68		41.5

		24-Oct-07		4:07:10		73.4		36.5		24-Oct-07		4:06:20		72.21		39		24-Oct-07		4:07:53		68.61		42.5		4-Dec-07		4:25:59		67.4		41.5

		24-Oct-07		6:07:10		73.4		35.5		24-Oct-07		6:06:20		72.21		38		24-Oct-07		6:07:53		68		42.5		4-Dec-07		6:25:59		68.61		41

		24-Oct-07		8:07:10		73.4		36		24-Oct-07		8:06:20		71.6		40		24-Oct-07		8:07:53		69.8		40		4-Dec-07		8:25:59		72.8		37

		24-Oct-07		10:07:10		75.2		39		24-Oct-07		10:06:20		72.21		40.5		24-Oct-07		10:07:53		71.6		46.5		4-Dec-07		10:25:59		74.6		38

		24-Oct-07		12:07:10		75.81		39.5		24-Oct-07		12:06:20		72.21		38		24-Oct-07		12:07:53		71.6		49		4-Dec-07		12:25:59		75.2		36

		24-Oct-07		14:07:10		75.81		39		24-Oct-07		14:06:20		72.8		46.5		24-Oct-07		14:07:53		71.6		49		4-Dec-07		14:25:59		74.6		37

		24-Oct-07		16:07:10		76.4		40		24-Oct-07		16:06:20		71.6		50		24-Oct-07		16:07:53		71.6		45		4-Dec-07		16:25:59		74.6		38

		24-Oct-07		18:07:10		74.6		41		24-Oct-07		18:06:20		69.8		42		24-Oct-07		18:07:53		71		53.5		4-Dec-07		18:25:59		74.6		39

		24-Oct-07		20:07:10		75.81		43.5		24-Oct-07		20:06:20		73.4		48.5		24-Oct-07		20:07:53		70.41		55.5		4-Dec-07		20:25:59		74.01		39.5

		24-Oct-07		22:07:10		75.81		43.5		24-Oct-07		22:06:20		72.8		48		24-Oct-07		22:07:53		72.8		48		4-Dec-07		22:25:59		72.8		41

		25-Oct-07		0:07:10		75.2		41.5		25-Oct-07		0:06:20		72.8		45.5		25-Oct-07		0:07:53		72.21		46		5-Dec-07		0:25:59		71.6		44.5

		25-Oct-07		2:07:10		74.6		40		25-Oct-07		2:06:20		72.8		43.5		25-Oct-07		2:07:53		71.6		45		5-Dec-07		2:25:59		70.41		45

		25-Oct-07		4:07:10		74.01		39		25-Oct-07		4:06:20		72.8		41.5		25-Oct-07		4:07:53		69.8		44		5-Dec-07		4:25:59		69.8		45.5

		25-Oct-07		6:07:10		73.4		39		25-Oct-07		6:06:20		71.6		42		25-Oct-07		6:07:53		69.2		45		5-Dec-07		6:25:59		70.41		50

		25-Oct-07		8:07:10		72.8		39.5		25-Oct-07		8:06:20		71		45.5		25-Oct-07		8:07:53		71		42.5		5-Dec-07		8:25:59		74.6		47

		25-Oct-07		10:07:10		72.8		43.5		25-Oct-07		10:06:20		70.41		52.5		25-Oct-07		10:07:53		71.6		49.5		5-Dec-07		10:25:59		75.81		48

		25-Oct-07		12:07:10		73.4		43.5		25-Oct-07		12:06:20		70.41		52		25-Oct-07		12:07:53		71.6		44		5-Dec-07		12:25:59		75.2		50

		25-Oct-07		14:07:10		74.01		42		25-Oct-07		14:06:20		71		39.5		25-Oct-07		14:07:53		71.6		47		5-Dec-07		14:25:59		74.6		51.5

		25-Oct-07		16:07:10		74.6		46		25-Oct-07		16:06:20		69.8		54		25-Oct-07		16:07:53		71.6		50.5		5-Dec-07		16:25:59		74.6		50

		25-Oct-07		18:07:10		74.6		47		25-Oct-07		18:06:20		69.2		56.5		25-Oct-07		18:07:53		71		48.5		5-Dec-07		18:25:59		74.6		49.5

		25-Oct-07		20:07:10		75.81		42		25-Oct-07		20:06:20		72.8		46.5		25-Oct-07		20:07:53		72.8		46.5		5-Dec-07		20:25:59		74.6		48.5

		25-Oct-07		22:07:10		75.2		40.5		25-Oct-07		22:06:20		72.8		43.5		25-Oct-07		22:07:53		72.8		44.5		5-Dec-07		22:25:59		72.8		50

		26-Oct-07		0:07:10		74.6		39.5		26-Oct-07		0:06:20		72.8		43.5		26-Oct-07		0:07:53		71.6		44		6-Dec-07		0:25:59		72.21		51.5

		26-Oct-07		2:07:10		74.01		39		26-Oct-07		2:06:20		72.21		42		26-Oct-07		2:07:53		69.8		44		6-Dec-07		2:25:59		71		51.5

		26-Oct-07		4:07:10		72.8		38		26-Oct-07		4:06:20		71		40.5		26-Oct-07		4:07:53		68.61		43.5		6-Dec-07		4:25:59		70.41		52

		26-Oct-07		6:07:10		72.8		37.5		26-Oct-07		6:06:20		70.41		39.5		26-Oct-07		6:07:53		68		43.5		6-Dec-07		6:25:59		70.41		52

		26-Oct-07		8:07:10		72.21		38		26-Oct-07		8:06:20		69.8		42.5		26-Oct-07		8:07:53		69.2		40.5		6-Dec-07		8:25:59		74.6		46.5

		26-Oct-07		10:07:10		72.8		38.5		26-Oct-07		10:06:20		71		40		26-Oct-07		10:07:53		71		47.5		6-Dec-07		10:25:59		75.81		45

		26-Oct-07		12:07:10		73.4		44.5		26-Oct-07		12:06:20		70.41		50.5		26-Oct-07		12:07:53		71.6		44.5		6-Dec-07		12:25:59		75.2		47

		26-Oct-07		14:07:10		74.6		40		26-Oct-07		14:06:20		71		39.5		26-Oct-07		14:07:53		71.6		48.5		6-Dec-07		14:25:59		74.6		49

		26-Oct-07		16:07:10		74.6		47		26-Oct-07		16:06:20		69.8		58.5		26-Oct-07		16:07:53		71		56		6-Dec-07		16:25:59		74.6		47

		26-Oct-07		18:07:10		74.01		47.5		26-Oct-07		18:06:20		69.2		56		26-Oct-07		18:07:53		70.41		52.5		6-Dec-07		18:25:59		74.6		40.5

		26-Oct-07		20:07:10		74.6		41.5		26-Oct-07		20:06:20		71		47.5		26-Oct-07		20:07:53		71		47.5		6-Dec-07		20:25:59		74.01		39.5

		26-Oct-07		22:07:10		74.01		40.5		26-Oct-07		22:06:20		71		40.5		26-Oct-07		22:07:53		70.41		45.5		6-Dec-07		22:25:59		72.21		42

		27-Oct-07		0:07:10		73.4		40.5		27-Oct-07		0:06:20		71.6		44.5		27-Oct-07		0:07:53		69.2		46		7-Dec-07		0:25:59		71		44

		27-Oct-07		2:07:10		72.8		41.5		27-Oct-07		2:06:20		70.41		46.5		27-Oct-07		2:07:53		68		48		7-Dec-07		2:25:59		70.41		43.5

		27-Oct-07		4:07:10		72.21		42		27-Oct-07		4:06:20		70.41		46		27-Oct-07		4:07:53		68		48.5		7-Dec-07		4:25:59		70.41		44

		27-Oct-07		6:07:10		72.8		42		27-Oct-07		6:06:20		71		45.5		27-Oct-07		6:07:53		68		49		7-Dec-07		6:25:59		70.41		44.5

		27-Oct-07		8:07:10		72.21		41		27-Oct-07		8:06:20		71		45.5		27-Oct-07		8:07:53		71		46.5		7-Dec-07		8:25:59		74.6		41

		27-Oct-07		10:07:10		72.8		45		27-Oct-07		10:06:20		71		45.5		27-Oct-07		10:07:53		71		37.5		7-Dec-07		10:25:59		74.6		42

		27-Oct-07		12:07:10		73.4		45		27-Oct-07		12:06:20		70.41		53.5		27-Oct-07		12:07:53		71		52.5		7-Dec-07		12:25:59		72.8		45.5

		27-Oct-07		14:07:10		73.4		42.5		27-Oct-07		14:06:20		71		47.5		27-Oct-07		14:07:53		71		51		7-Dec-07		14:25:59		72.8		46.5

		27-Oct-07		16:07:10		73.4		46		27-Oct-07		16:06:20		68.61		46		27-Oct-07		16:07:53		71		46.5		7-Dec-07		16:25:59		72.8		47.5

		27-Oct-07		18:07:10		73.4		44.5		27-Oct-07		18:06:20		68		46.5		27-Oct-07		18:07:53		69.8		49.5		7-Dec-07		18:25:59		72.8		46

		27-Oct-07		20:07:10		72.8		42		27-Oct-07		20:06:20		69.2		47.5		27-Oct-07		20:07:53		69.8		46.5		7-Dec-07		20:25:59		72.21		46

		27-Oct-07		22:07:10		72.21		41.5		27-Oct-07		22:06:20		69.2		46		27-Oct-07		22:07:53		68.61		46		7-Dec-07		22:25:59		69.8		47.5

		28-Oct-07		0:07:10		71.6		40		28-Oct-07		0:06:20		68.61		44.5		28-Oct-07		0:07:53		67.4		45		8-Dec-07		0:25:59		68.61		48

		28-Oct-07		2:07:10		71		39		28-Oct-07		2:06:20		68.61		43		28-Oct-07		2:07:53		66.2		45		8-Dec-07		2:25:59		68		47

		28-Oct-07		4:07:10		70.41		38.5		28-Oct-07		4:06:20		68.61		41.5		28-Oct-07		4:07:53		65.01		45.5		8-Dec-07		4:25:59		67.4		46.5

		28-Oct-07		6:07:10		69.8		38		28-Oct-07		6:06:20		68		41.5		28-Oct-07		6:07:53		63.8		46		8-Dec-07		6:25:59		68		45.5

		28-Oct-07		8:07:10		69.2		39.5		28-Oct-07		8:06:20		68		43.5		28-Oct-07		8:07:53		66.81		43.5		8-Dec-07		8:25:59		71.6		40

		28-Oct-07		10:07:10		69.2		42		28-Oct-07		10:06:20		68		47		28-Oct-07		10:07:53		66.81		46.5		8-Dec-07		10:25:59		72.21		39.5

		28-Oct-07		12:07:10		69.2		44.5		28-Oct-07		12:06:20		67.4		50		28-Oct-07		12:07:53		67.4		48		8-Dec-07		12:25:59		71.6		40

		28-Oct-07		14:07:10		69.8		47		28-Oct-07		14:06:20		67.4		53		28-Oct-07		14:07:53		68.61		50		8-Dec-07		14:25:59		72.21		39.5

		28-Oct-07		16:07:10		70.41		49.5		28-Oct-07		16:06:20		67.4		49		28-Oct-07		16:07:53		69.2		52		8-Dec-07		16:25:59		72.21		38

		28-Oct-07		18:07:10		71		43		28-Oct-07		18:06:20		68		46.5		28-Oct-07		18:07:53		69.2		47.5		8-Dec-07		18:25:59		71.6		37.5

		28-Oct-07		20:07:10		71		43.5		28-Oct-07		20:06:20		68.61		47		28-Oct-07		20:07:53		68.61		47		8-Dec-07		20:25:59		70.41		36.5

		28-Oct-07		22:07:10		71		41		28-Oct-07		22:06:20		69.2		44.5		28-Oct-07		22:07:53		67.4		46.5		8-Dec-07		22:25:59		69.8		36.5

		29-Oct-07		0:07:10		70.41		41.5		29-Oct-07		0:06:20		68.61		44.5		29-Oct-07		0:07:53		66.2		47		9-Dec-07		0:25:59		68		37

		29-Oct-07		2:07:10		70.41		41.5		29-Oct-07		2:06:20		68.61		44.5		29-Oct-07		2:07:53		65.6		48		9-Dec-07		2:25:59		66.81		37

		29-Oct-07		4:07:10		69.8		40.5		29-Oct-07		4:06:20		68		44		29-Oct-07		4:07:53		65.01		48		9-Dec-07		4:25:59		66.2		36.5

		29-Oct-07		6:07:10		69.8		40.5		29-Oct-07		6:06:20		68		43.5		29-Oct-07		6:07:53		64.4		48		9-Dec-07		6:25:59		66.2		36

		29-Oct-07		8:07:10		69.2		40		29-Oct-07		8:06:20		68		43		29-Oct-07		8:07:53		67.4		43.5		9-Dec-07		8:25:59		66.2		35.5

		29-Oct-07		10:07:10		69.2		43.5		29-Oct-07		10:06:20		68		49.5		29-Oct-07		10:07:53		67.4		48		9-Dec-07		10:25:59		66.2		34

		29-Oct-07		12:07:10		69.8		47.5		29-Oct-07		12:06:20		68		53.5		29-Oct-07		12:07:53		69.2		50		9-Dec-07		12:25:59		66.2		34

		29-Oct-07		14:07:10		71		48.5		29-Oct-07		14:06:20		68		48.5		29-Oct-07		14:07:53		69.8		54.5		9-Dec-07		14:25:59		66.81		33.5

		29-Oct-07		16:07:10		71.6		48.5		29-Oct-07		16:06:20		68.61		55		29-Oct-07		16:07:53		70.41		45.5		9-Dec-07		16:25:59		66.81		33

		29-Oct-07		18:07:10		72.21		50.5		29-Oct-07		18:06:20		68.61		62.5		29-Oct-07		18:07:53		70.41		55.5		9-Dec-07		18:25:59		66.81		31

		29-Oct-07		20:07:10		72.8		48.5		29-Oct-07		20:06:20		69.2		46		29-Oct-07		20:07:53		71.6		50		9-Dec-07		20:25:59		65.6		30.5

		29-Oct-07		22:07:10		72.21		46		29-Oct-07		22:06:20		69.2		51.5		29-Oct-07		22:07:53		70.41		48.5		9-Dec-07		22:25:59		65.01		31.5

		30-Oct-07		0:07:10		71.6		45		30-Oct-07		0:06:20		68.61		50.5		30-Oct-07		0:07:53		69.2		48		10-Dec-07		0:25:59		64.4		31

		30-Oct-07		2:07:10		71.6		44.5		30-Oct-07		2:06:20		68.61		46.5		30-Oct-07		2:07:53		68.61		48.5		10-Dec-07		2:25:59		63.8		31

		30-Oct-07		4:07:10		71		43.5		30-Oct-07		4:06:20		69.2		48		30-Oct-07		4:07:53		67.4		49		10-Dec-07		4:25:59		63.21		31

		30-Oct-07		6:07:10		71.6		43.5		30-Oct-07		6:06:20		69.2		46.5		30-Oct-07		6:07:53		68		49		10-Dec-07		6:25:59		62.6		31

		30-Oct-07		8:07:10		71		46		30-Oct-07		8:06:20		68.61		44.5		30-Oct-07		8:07:53		69.2		47.5		10-Dec-07		8:25:59		63.21		31

		30-Oct-07		10:07:10		72.21		46		30-Oct-07		10:06:20		69.2		55.5		30-Oct-07		10:07:53		71.6		47.5		10-Dec-07		10:25:59		64.4		31

		30-Oct-07		12:07:10		72.21		49		30-Oct-07		12:06:20		69.8		56		30-Oct-07		12:07:53		71		49		10-Dec-07		12:25:59		65.6		31.5

		30-Oct-07		14:07:10		73.4		47		30-Oct-07		14:06:20		70.41		53.5		30-Oct-07		14:07:53		71		55		10-Dec-07		14:25:59		66.2		32

		30-Oct-07		16:07:10		73.4		48.5		30-Oct-07		16:06:20		68.61		61.5		30-Oct-07		16:07:53		70.41		54		10-Dec-07		16:25:59		66.81		32.5

		30-Oct-07		18:07:10		72.8		45		30-Oct-07		18:06:20		69.2		54.5		30-Oct-07		18:07:53		70.41		51.5		10-Dec-07		18:25:59		66.81		33

		30-Oct-07		20:07:10		72.21		46		30-Oct-07		20:06:20		68.61		53		30-Oct-07		20:07:53		69.8		48.5		10-Dec-07		20:25:59		66.2		34

		30-Oct-07		22:07:10		71.6		45.5		30-Oct-07		22:06:20		68.61		51.5		30-Oct-07		22:07:53		69.2		49		10-Dec-07		22:25:59		65.01		35

		31-Oct-07		0:07:10		71.6		45		31-Oct-07		0:06:20		69.2		50		31-Oct-07		0:07:53		68.61		49.5		11-Dec-07		0:25:59		64.4		36.5

		31-Oct-07		2:07:10		71		46.5		31-Oct-07		2:06:20		68.61		52		31-Oct-07		2:07:53		68		51		11-Dec-07		2:25:59		63.21		36.5

		31-Oct-07		4:07:10		71		47		31-Oct-07		4:06:20		68.61		52		31-Oct-07		4:07:53		67.4		52.5		11-Dec-07		4:25:59		63.21		36

		31-Oct-07		6:07:10		71.6		47		31-Oct-07		6:06:20		68.61		52		31-Oct-07		6:07:53		72.21		48		11-Dec-07		6:25:59		64.4		34.5

		31-Oct-07		8:07:10		71.6		47.5		31-Oct-07		8:06:20		69.8		48.5		31-Oct-07		8:07:53		71		43.5		11-Dec-07		8:25:59		66.81		31.5

		31-Oct-07		10:07:10		72.21		48		31-Oct-07		10:06:20		69.8		51.5		31-Oct-07		10:07:53		71.6		49.5		11-Dec-07		10:25:59		69.8		31.5

		31-Oct-07		12:07:10		72.8		46.5		31-Oct-07		12:06:20		69.2		45.5		31-Oct-07		12:07:53		72.21		48		11-Dec-07		12:25:59		74.01		32

		31-Oct-07		14:07:10		72.8		46.5		31-Oct-07		14:06:20		70.41		45.5		31-Oct-07		14:07:53		71		52		11-Dec-07		14:25:59		71.6		33.5

		31-Oct-07		16:07:10		73.4		47		31-Oct-07		16:06:20		68		51		31-Oct-07		16:07:53		71		45.5		11-Dec-07		16:25:59		71.6		34.5

		31-Oct-07		18:07:10		72.8		47		31-Oct-07		18:06:20		68.61		48		31-Oct-07		18:07:53		70.41		51.5		11-Dec-07		18:25:59		71.6		33.5

		31-Oct-07		20:07:10		72.21		45		31-Oct-07		20:06:20		68.61		51.5		31-Oct-07		20:07:53		69.8		48		11-Dec-07		20:25:59		69.8		33.5

		31-Oct-07		22:07:10		72.21		44.5		31-Oct-07		22:06:20		69.2		49.5		31-Oct-07		22:07:53		68.61		49.5		11-Dec-07		22:25:59		67.4		33

		1-Nov-07		0:07:10		71.6		44.5		1-Nov-07		0:06:20		69.2		49.5		1-Nov-07		0:07:53		67.4		50		12-Dec-07		0:25:59		66.2		33.5

		1-Nov-07		2:07:10		71.6		45.5		1-Nov-07		2:06:20		69.2		50		1-Nov-07		2:07:53		66.81		51.5		12-Dec-07		2:25:59		65.01		31

		1-Nov-07		4:07:10		71		46.5		1-Nov-07		4:06:20		68.61		52		1-Nov-07		4:07:53		66.81		53		12-Dec-07		4:25:59		63.8		29

		1-Nov-07		6:07:10		71.6		47.5		1-Nov-07		6:06:20		69.2		53.5		1-Nov-07		6:07:53		68.61		51		12-Dec-07		6:25:59		65.6		24

		1-Nov-07		8:07:10		72.21		44.5		1-Nov-07		8:06:20		69.8		53.5		1-Nov-07		8:07:53		70.41		49		12-Dec-07		8:25:59		69.8		21.5

		1-Nov-07		10:07:10		72.21		47		1-Nov-07		10:06:20		68.61		51.5		1-Nov-07		10:07:53		71		48.5		12-Dec-07		10:25:59		72.21		23

		1-Nov-07		12:07:10		72.8		45.5		1-Nov-07		12:06:20		69.8		44		1-Nov-07		12:07:53		71.6		45.5		12-Dec-07		12:25:59		71.6		22

		1-Nov-07		14:07:10		72.8		46.5		1-Nov-07		14:06:20		68.61		47.5		1-Nov-07		14:07:53		71		51		12-Dec-07		14:25:59		72.21		21

		1-Nov-07		16:07:10		72.8		51.5		1-Nov-07		16:06:20		68.61		60.5		1-Nov-07		16:07:53		70.41		55.5		12-Dec-07		16:25:59		72.21		20.5

		1-Nov-07		18:07:10		72.8		50		1-Nov-07		18:06:20		68.61		59		1-Nov-07		18:07:53		69.8		54.5		12-Dec-07		18:25:59		71.6		23

		1-Nov-07		20:07:10		72.21		47.5		1-Nov-07		20:06:20		68.61		53.5		1-Nov-07		20:07:53		69.8		50.5		12-Dec-07		20:25:59		69.8		24

		1-Nov-07		22:07:10		71.6		47.5		1-Nov-07		22:06:20		69.2		52		1-Nov-07		22:07:53		69.2		51		12-Dec-07		22:25:59		68.61		25.5

		2-Nov-07		0:07:10		71		48		2-Nov-07		0:06:20		68.61		52.5		2-Nov-07		0:07:53		68.61		51.5		13-Dec-07		0:25:59		66.2		26.5

		2-Nov-07		2:07:10		71		48		2-Nov-07		2:06:20		68.61		52.5		2-Nov-07		2:07:53		68		52.5		13-Dec-07		2:25:59		64.4		27

		2-Nov-07		4:07:10		70.41		47.5		2-Nov-07		4:06:20		68.61		52		2-Nov-07		4:07:53		67.4		52.5		13-Dec-07		4:25:59		63.21		27.5

		2-Nov-07		6:07:10		71		46		2-Nov-07		6:06:20		69.2		49		2-Nov-07		6:07:53		68		51.5		13-Dec-07		6:25:59		64.4		28

		2-Nov-07		8:07:10		72.21		46.5		2-Nov-07		8:06:20		68.61		54.5		2-Nov-07		8:07:53		69.8		48		13-Dec-07		8:25:59		68		27.5

		2-Nov-07		10:07:10		73.4		46		2-Nov-07		10:06:20		69.2		53		2-Nov-07		10:07:53		71.6		46.5		13-Dec-07		10:25:59		70.41		28.5

		2-Nov-07		12:07:10		74.01		47		2-Nov-07		12:06:20		69.8		56.5		2-Nov-07		12:07:53		71.6		47.5		13-Dec-07		12:25:59		71.6		29

		2-Nov-07		14:07:10		74.01		44		2-Nov-07		14:06:20		71		48.5		2-Nov-07		14:07:53		71		44		13-Dec-07		14:25:59		71.6		26

		2-Nov-07		16:07:10		74.01		52.5		2-Nov-07		16:06:20		69.2		58		2-Nov-07		16:07:53		71		56.5		13-Dec-07		16:25:59		71.6		25.5

		2-Nov-07		18:07:10		74.01		49.5		2-Nov-07		18:06:20		69.2		49.5		2-Nov-07		18:07:53		70.41		50		13-Dec-07		18:25:59		71.6		26

		2-Nov-07		20:07:10		73.4		46.5		2-Nov-07		20:06:20		69.2		51.5		2-Nov-07		20:07:53		70.41		51		13-Dec-07		20:25:59		71		27.5

		2-Nov-07		22:07:10		72.8		42		2-Nov-07		22:06:20		69.8		47.5		2-Nov-07		22:07:53		69.8		47		13-Dec-07		22:25:59		68		28.5

		3-Nov-07		0:07:10		71.6		42		3-Nov-07		0:06:20		69.2		46		3-Nov-07		0:07:53		68		46.5		14-Dec-07		0:25:59		66.2		29.5

		3-Nov-07		2:07:10		71		40.5		3-Nov-07		2:06:20		69.2		43.5		3-Nov-07		2:07:53		66.81		46.5		14-Dec-07		2:25:59		64.4		29.5

		3-Nov-07		4:07:10		70.41		40		3-Nov-07		4:06:20		68		42.5		3-Nov-07		4:07:53		66.81		45		14-Dec-07		4:25:59		63.8		30

		3-Nov-07		6:07:10		70.41		38		3-Nov-07		6:06:20		67.4		40.5		3-Nov-07		6:07:53		67.4		42.5		14-Dec-07		6:25:59		65.01		29

		3-Nov-07		8:07:10		72.8		36.5		3-Nov-07		8:06:20		69.2		42		3-Nov-07		8:07:53		68.61		39		14-Dec-07		8:25:59		66.81		27

		3-Nov-07		10:07:10		74.01		39.5		3-Nov-07		10:06:20		71.6		46		3-Nov-07		10:07:53		70.41		47		14-Dec-07		10:25:59		70.41		28.5

		3-Nov-07		12:07:10		74.6		40		3-Nov-07		12:06:20		71.6		46.5		3-Nov-07		12:07:53		71.6		45.5		14-Dec-07		12:25:59		72.21		28.5

		3-Nov-07		14:07:10		74.6		42		3-Nov-07		14:06:20		70.41		50		3-Nov-07		14:07:53		71		52		14-Dec-07		14:25:59		72.21		29.5

		3-Nov-07		16:07:10		74.01		42.5		3-Nov-07		16:06:20		69.8		50.5		3-Nov-07		16:07:53		71		49.5		14-Dec-07		16:25:59		72.21		30.5

		3-Nov-07		18:07:10		74.01		47.5		3-Nov-07		18:06:20		69.2		59.5		3-Nov-07		18:07:53		71		47		14-Dec-07		18:25:59		72.8		31.5

		3-Nov-07		20:07:10		74.6		42		3-Nov-07		20:06:20		71		47.5		3-Nov-07		20:07:53		70.41		48.5		14-Dec-07		20:25:59		71		31.5

		3-Nov-07		22:07:10		74.01		40.5		3-Nov-07		22:06:20		71		45		3-Nov-07		22:07:53		69.8		45.5		14-Dec-07		22:25:59		68.61		31

		4-Nov-07		0:07:10		72.8		38.5		4-Nov-07		0:06:20		69.8		42		4-Nov-07		0:07:53		68		44.5		15-Dec-07		0:25:59		66.2		31.5

		4-Nov-07		2:07:10		71.6		37.5		4-Nov-07		2:06:20		69.8		40		4-Nov-07		2:07:53		66.81		44		15-Dec-07		2:25:59		64.4		31.5

		4-Nov-07		4:07:10		71		36.5		4-Nov-07		4:06:20		69.2		39		4-Nov-07		4:07:53		65.01		43.5		15-Dec-07		4:25:59		63.21		31

		4-Nov-07		6:07:10		69.8		35.5		4-Nov-07		6:06:20		68.61		38		4-Nov-07		6:07:53		63.8		43.5		15-Dec-07		6:25:59		64.4		30

		4-Nov-07		8:07:10		69.2		35		4-Nov-07		8:06:20		67.4		38		4-Nov-07		8:07:53		66.81		39		15-Dec-07		8:25:59		66.81		28.5

		4-Nov-07		10:07:10		69.8		37.5		4-Nov-07		10:06:20		68.61		40.5		4-Nov-07		10:07:53		67.4		41		15-Dec-07		10:25:59		69.2		30

		4-Nov-07		12:07:10		70.41		40.5		4-Nov-07		12:06:20		68.61		43		4-Nov-07		12:07:53		68.61		43.5		15-Dec-07		12:25:59		72.21		31

		4-Nov-07		14:07:10		71		41		4-Nov-07		14:06:20		69.2		39.5		4-Nov-07		14:07:53		70.41		41		15-Dec-07		14:25:59		71.6		32

		4-Nov-07		16:07:10		72.21		42.5		4-Nov-07		16:06:20		69.2		41.5		4-Nov-07		16:07:53		70.41		46.5		15-Dec-07		16:25:59		72.21		31.5

		4-Nov-07		18:07:10		72.8		38.5		4-Nov-07		18:06:20		69.2		41		4-Nov-07		18:07:53		69.8		44		15-Dec-07		18:25:59		71.6		34

		4-Nov-07		20:07:10		72.8		36		4-Nov-07		20:06:20		70.41		39		4-Nov-07		20:07:53		70.41		40		15-Dec-07		20:25:59		71		34.5

		4-Nov-07		22:07:10		72.8		35.5		4-Nov-07		22:06:20		70.41		39		4-Nov-07		22:07:53		69.2		40		15-Dec-07		22:25:59		68.61		34

		5-Nov-07		0:07:10		72.21		36.5		5-Nov-07		0:06:20		70.41		40		5-Nov-07		0:07:53		67.4		42		16-Dec-07		0:25:59		67.4		35

		5-Nov-07		2:07:10		71.6		36		5-Nov-07		2:06:20		70.41		38.5		5-Nov-07		2:07:53		65.6		42		16-Dec-07		2:25:59		66.81		35

		5-Nov-07		4:07:10		70.41		35.5		5-Nov-07		4:06:20		69.2		37.5		5-Nov-07		4:07:53		64.4		42.5		16-Dec-07		4:25:59		66.2		35.5

		5-Nov-07		6:07:10		69.8		34.5		5-Nov-07		6:06:20		68.61		37		5-Nov-07		6:07:53		64.4		41.5		16-Dec-07		6:25:59		66.2		35.5

		5-Nov-07		8:07:10		69.2		34		5-Nov-07		8:06:20		67.4		37		5-Nov-07		8:07:53		66.81		37.5		16-Dec-07		8:25:59		65.6		35.5

		5-Nov-07		10:07:10		69.2		37		5-Nov-07		10:06:20		68		40		5-Nov-07		10:07:53		67.4		40.5		16-Dec-07		10:25:59		65.6		36

		5-Nov-07		12:07:10		69.8		39		5-Nov-07		12:06:20		68.61		39		5-Nov-07		12:07:53		68		42		16-Dec-07		12:25:59		66.2		37.5

		5-Nov-07		14:07:10		71		40.5		5-Nov-07		14:06:20		68.61		43		5-Nov-07		14:07:53		69.8		42.5		16-Dec-07		14:25:59		66.2		38.5

		5-Nov-07		16:07:10		71.6		41.5		5-Nov-07		16:06:20		69.2		40.5		5-Nov-07		16:07:53		69.8		45		16-Dec-07		16:25:59		66.2		40

		5-Nov-07		18:07:10		72.21		40.5		5-Nov-07		18:06:20		68.61		45		5-Nov-07		18:07:53		70.41		43.5		16-Dec-07		18:25:59		65.6		41.5

		5-Nov-07		20:07:10		72.8		40		5-Nov-07		20:06:20		71		43		5-Nov-07		20:07:53		70.41		44.5		16-Dec-07		20:25:59		65.01		42

		5-Nov-07		22:07:10		72.21		40.5		5-Nov-07		22:06:20		70.41		44.5		5-Nov-07		22:07:53		69.2		44.5		16-Dec-07		22:25:59		65.01		42

		6-Nov-07		0:07:10		71.6		39		6-Nov-07		0:06:20		70.41		41.5		6-Nov-07		0:07:53		67.4		44		17-Dec-07		0:25:59		64.4		42.5

		6-Nov-07		2:07:10		71		38		6-Nov-07		2:06:20		69.8		40		6-Nov-07		2:07:53		66.2		44		17-Dec-07		2:25:59		63.8		43.5

		6-Nov-07		4:07:10		69.8		36		6-Nov-07		4:06:20		68.61		38		6-Nov-07		4:07:53		65.01		42.5		17-Dec-07		4:25:59		63.8		43.5

		6-Nov-07		6:07:10		69.2		35		6-Nov-07		6:06:20		67.4		37		6-Nov-07		6:07:53		67.4		38		17-Dec-07		6:25:59		63.21		43

		6-Nov-07		8:07:10		71.6		33.5		6-Nov-07		8:06:20		68		36		6-Nov-07		8:07:53		68		37		17-Dec-07		8:25:59		64.4		44

		6-Nov-07		10:07:10		72.8		35.5		6-Nov-07		10:06:20		70.41		42.5		6-Nov-07		10:07:53		70.41		35.5		17-Dec-07		10:25:59		65.6		43.5

		6-Nov-07		12:07:10		74.01		38.5		6-Nov-07		12:06:20		70.41		47.5		6-Nov-07		12:07:53		70.41		46.5		17-Dec-07		12:25:59		66.2		43.5

		6-Nov-07		14:07:10		74.01		37		6-Nov-07		14:06:20		71		39		6-Nov-07		14:07:53		70.41		49.5		17-Dec-07		14:25:59		66.2		42

		6-Nov-07		16:07:10		74.6		44		6-Nov-07		16:06:20		70.41		48.5		6-Nov-07		16:07:53		71		49		17-Dec-07		16:25:59		66.81		41.5

		6-Nov-07		18:07:10		74.6		41.5		6-Nov-07		18:06:20		69.2		43		6-Nov-07		18:07:53		70.41		46.5		17-Dec-07		18:25:59		66.81		41.5

		6-Nov-07		20:07:10		73.4		39.5		6-Nov-07		20:06:20		70.41		44.5		6-Nov-07		20:07:53		69.8		44.5		17-Dec-07		20:25:59		65.6		41.5

		6-Nov-07		22:07:10		72.8		40		6-Nov-07		22:06:20		70.41		44		6-Nov-07		22:07:53		68		46		17-Dec-07		22:25:59		65.01		43.5

		7-Nov-07		0:07:10		72.21		40.5		7-Nov-07		0:06:20		70.41		44.5		7-Nov-07		0:07:53		67.4		47		18-Dec-07		0:25:59		64.4		44.5

		7-Nov-07		2:07:10		71.6		41		7-Nov-07		2:06:20		70.41		44		7-Nov-07		2:07:53		66.2		48		18-Dec-07		2:25:59		63.8		45

		7-Nov-07		4:07:10		71		41		7-Nov-07		4:06:20		69.8		43.5		7-Nov-07		4:07:53		65.6		48.5		18-Dec-07		4:25:59		63.8		44

		7-Nov-07		6:07:10		70.41		41.5		7-Nov-07		6:06:20		69.8		43.5		7-Nov-07		6:07:53		67.4		45		18-Dec-07		6:25:59		65.6		46

		7-Nov-07		8:07:10		71.6		41.5		7-Nov-07		8:06:20		68.61		45		7-Nov-07		8:07:53		70.41		43.5		18-Dec-07		8:25:59		68		45

		7-Nov-07		10:07:10		72.8		41		7-Nov-07		10:06:20		70.41		47.5		7-Nov-07		10:07:53		71		44		18-Dec-07		10:25:59		71		45

		7-Nov-07		12:07:10		72.8		40		7-Nov-07		12:06:20		71		38.5		7-Nov-07		12:07:53		70.41		45.5		18-Dec-07		12:25:59		71.6		44

		7-Nov-07		14:07:10		73.4		42.5		7-Nov-07		14:06:20		71		50.5		7-Nov-07		14:07:53		70.41		45.5		18-Dec-07		14:25:59		71.6		45.5

		7-Nov-07		16:07:10		74.01		46		7-Nov-07		16:06:20		70.41		46		7-Nov-07		16:07:53		71		53		18-Dec-07		16:25:59		71.6		45

		7-Nov-07		18:07:10		74.01		43.5		7-Nov-07		18:06:20		69.2		51.5		7-Nov-07		18:07:53		69.8		50		18-Dec-07		18:25:59		72.21		44

		7-Nov-07		20:07:10		72.8		40.5		7-Nov-07		20:06:20		70.41		44		7-Nov-07		20:07:53		69.2		45.5		18-Dec-07		20:25:59		70.41		43

		7-Nov-07		22:07:10		72.21		39		7-Nov-07		22:06:20		70.41		41		7-Nov-07		22:07:53		68		44		18-Dec-07		22:25:59		68.61		44

		8-Nov-07		0:07:10		71.6		40		8-Nov-07		0:06:20		70.41		42.5		8-Nov-07		0:07:53		66.81		46.5		19-Dec-07		0:25:59		67.4		45

		8-Nov-07		2:07:10		71		40.5		8-Nov-07		2:06:20		70.41		42		8-Nov-07		2:07:53		65.6		47.5		19-Dec-07		2:25:59		66.2		46

		8-Nov-07		4:07:10		70.41		39.5		8-Nov-07		4:06:20		69.8		40.5		8-Nov-07		4:07:53		65.01		47		19-Dec-07		4:25:59		65.01		46.5

		8-Nov-07		6:07:10		69.8		39.5		8-Nov-07		6:06:20		69.8		40		8-Nov-07		6:07:53		67.4		43		19-Dec-07		6:25:59		65.6		49

		8-Nov-07		8:07:10		71.6		38.5		8-Nov-07		8:06:20		68.61		42.5		8-Nov-07		8:07:53		69.2		41.5		19-Dec-07		8:25:59		69.2		46.5

		8-Nov-07		10:07:10		71		40		8-Nov-07		10:06:20		67.4		47		8-Nov-07		10:07:53		71		41		19-Dec-07		10:25:59		71.6		47

		8-Nov-07		12:07:10		72.21		43		8-Nov-07		12:06:20		70.41		46.5		8-Nov-07		12:07:53		70.41		47		19-Dec-07		12:25:59		72.21		46.5

		8-Nov-07		14:07:10		71.6		41		8-Nov-07		14:06:20		68		43		8-Nov-07		14:07:53		71.6		45.5		19-Dec-07		14:25:59		72.21		49.5

		8-Nov-07		16:07:10		74.01		43.5		8-Nov-07		16:06:20		71.6		43		8-Nov-07		16:07:53		70.41		53		19-Dec-07		16:25:59		72.8		46.5

		8-Nov-07		18:07:10		73.4		43		8-Nov-07		18:06:20		71		47.5		8-Nov-07		18:07:53		69.8		48		19-Dec-07		18:25:59		72.21		44.5

		8-Nov-07		20:07:10		71.6		43		8-Nov-07		20:06:20		69.2		46.5		8-Nov-07		20:07:53		69.8		47		19-Dec-07		20:25:59		71.6		42

		8-Nov-07		22:07:10		71.6		44		8-Nov-07		22:06:20		68.61		48		8-Nov-07		22:07:53		68.61		48		19-Dec-07		22:25:59		69.2		43

		9-Nov-07		0:07:10		71		43		9-Nov-07		0:06:20		68.61		46.5		9-Nov-07		0:07:53		68		47		20-Dec-07		0:25:59		68		42.5

		9-Nov-07		2:07:10		70.41		44		9-Nov-07		2:06:20		68.61		47.5		9-Nov-07		2:07:53		67.4		48.5		20-Dec-07		2:25:59		67.4		42.5

		9-Nov-07		4:07:10		70.41		44.5		9-Nov-07		4:06:20		68.61		47.5		9-Nov-07		4:07:53		66.81		49.5		20-Dec-07		4:25:59		66.81		42.5

		9-Nov-07		6:07:10		69.8		44		9-Nov-07		6:06:20		68.61		46.5		9-Nov-07		6:07:53		68		47		20-Dec-07		6:25:59		67.4		42.5

		9-Nov-07		8:07:10		71.6		43		9-Nov-07		8:06:20		69.8		46		9-Nov-07		8:07:53		70.41		47		20-Dec-07		8:25:59		69.8		41.5

		9-Nov-07		10:07:10		71.6		44.5		9-Nov-07		10:06:20		71		48		9-Nov-07		10:07:53		71.6		47.5		20-Dec-07		10:25:59		71.6		41.5

		9-Nov-07		12:07:10		72.21		45		9-Nov-07		12:06:20		71		49		9-Nov-07		12:07:53		70.41		48		20-Dec-07		12:25:59		72.8		41

		9-Nov-07		14:07:10		74.01		42.5		9-Nov-07		14:06:20		71.6		44.5		9-Nov-07		14:07:53		71		49.5		20-Dec-07		14:25:59		72.8		42.5

		9-Nov-07		16:07:10		74.01		44		9-Nov-07		16:06:20		71.6		49		9-Nov-07		16:07:53		69.8		49.5		20-Dec-07		16:25:59		72.8		43.5

		9-Nov-07		18:07:10		72.8		42.5		9-Nov-07		18:06:20		70.41		46.5		9-Nov-07		18:07:53		69.8		50		20-Dec-07		18:25:59		72.8		43

		9-Nov-07		20:07:10		72.8		42.5		9-Nov-07		20:06:20		69.8		46		9-Nov-07		20:07:53		69.2		47		20-Dec-07		20:25:59		71.6		43

		9-Nov-07		22:07:10		71.6		43.5		9-Nov-07		22:06:20		69.2		47		9-Nov-07		22:07:53		69.2		47.5		20-Dec-07		22:25:59		70.41		45

		10-Nov-07		0:07:10		71		44.5		10-Nov-07		0:06:20		69.2		48.5		10-Nov-07		0:07:53		68.61		48.5		21-Dec-07		0:25:59		69.2		45.5

		10-Nov-07		2:07:10		71		45		10-Nov-07		2:06:20		68.61		49.5		10-Nov-07		2:07:53		68		49.5		21-Dec-07		2:25:59		68.61		46.5

		10-Nov-07		4:07:10		70.41		45		10-Nov-07		4:06:20		68.61		48		10-Nov-07		4:07:53		67.4		49.5		21-Dec-07		4:25:59		68.61		46.5

		10-Nov-07		6:07:10		69.8		42		10-Nov-07		6:06:20		68.61		45		10-Nov-07		6:07:53		66.81		47		21-Dec-07		6:25:59		68.61		46

		10-Nov-07		8:07:10		72.21		40		10-Nov-07		8:06:20		68.61		44		10-Nov-07		8:07:53		69.8		44		21-Dec-07		8:25:59		70.41		41

		10-Nov-07		10:07:10		74.01		39.5		10-Nov-07		10:06:20		71		42		10-Nov-07		10:07:53		70.41		47		21-Dec-07		10:25:59		72.8		40.5

		10-Nov-07		12:07:10		73.4		41		10-Nov-07		12:06:20		71		48.5		10-Nov-07		12:07:53		70.41		47		21-Dec-07		12:25:59		72.21		38.5

		10-Nov-07		14:07:10		73.4		40		10-Nov-07		14:06:20		71.6		41		10-Nov-07		14:07:53		71		51		21-Dec-07		14:25:59		72.8		37

		10-Nov-07		16:07:10		74.01		44		10-Nov-07		16:06:20		71		50		10-Nov-07		16:07:53		70.41		41.5		21-Dec-07		16:25:59		72.21		35.5

		10-Nov-07		18:07:10		73.4		44.5		10-Nov-07		18:06:20		69.8		51		10-Nov-07		18:07:53		70.41		52.5		21-Dec-07		18:25:59		71.6		34.5

		10-Nov-07		20:07:10		72.8		44		10-Nov-07		20:06:20		69.2		48.5		10-Nov-07		20:07:53		69.8		48.5		21-Dec-07		20:25:59		69.8		34.5

		10-Nov-07		22:07:10		71.6		42.5		10-Nov-07		22:06:20		68.61		46.5		10-Nov-07		22:07:53		69.2		46.5		21-Dec-07		22:25:59		68.61		35

		11-Nov-07		0:07:10		71		41		11-Nov-07		0:06:20		68.61		44.5		11-Nov-07		0:07:53		68		45		22-Dec-07		0:25:59		68		35

		11-Nov-07		2:07:10		70.41		40		11-Nov-07		2:06:20		68		43		11-Nov-07		2:07:53		66.2		45		22-Dec-07		2:25:59		67.4		34.5

		11-Nov-07		4:07:10		69.8		40		11-Nov-07		4:06:20		68		44		11-Nov-07		4:07:53		65.6		46.5		22-Dec-07		4:25:59		66.2		34

		11-Nov-07		6:07:10		69.8		41		11-Nov-07		6:06:20		68		45.5		11-Nov-07		6:07:53		65.01		48		22-Dec-07		6:25:59		66.81		33

		11-Nov-07		8:07:10		69.8		43		11-Nov-07		8:06:20		68		47.5		11-Nov-07		8:07:53		67.4		47		22-Dec-07		8:25:59		69.2		30.5

		11-Nov-07		10:07:10		69.8		46		11-Nov-07		10:06:20		68		51		11-Nov-07		10:07:53		68		48.5		22-Dec-07		10:25:59		70.41		31

		11-Nov-07		12:07:10		69.8		50		11-Nov-07		12:06:20		68		55		11-Nov-07		12:07:53		67.4		53.5		22-Dec-07		12:25:59		71		30

		11-Nov-07		14:07:10		70.41		52.5		11-Nov-07		14:06:20		68.61		57.5		11-Nov-07		14:07:53		68		54.5		22-Dec-07		14:25:59		70.41		30

		11-Nov-07		16:07:10		70.41		53.5		11-Nov-07		16:06:20		68.61		58.5		11-Nov-07		16:07:53		68		55.5		22-Dec-07		16:25:59		71.6		29.5

		11-Nov-07		18:07:10		70.41		54.5		11-Nov-07		18:06:20		68.61		59		11-Nov-07		18:07:53		68.61		56.5		22-Dec-07		18:25:59		70.41		30

		11-Nov-07		20:07:10		70.41		54.5		11-Nov-07		20:06:20		68.61		59		11-Nov-07		20:07:53		68.61		56		22-Dec-07		20:25:59		69.2		30.5

		11-Nov-07		22:07:10		70.41		55		11-Nov-07		22:06:20		68.61		59.5		11-Nov-07		22:07:53		68		56.5		22-Dec-07		22:25:59		66.81		31.5

		12-Nov-07		0:07:10		70.41		55		12-Nov-07		0:06:20		68.61		59		12-Nov-07		0:07:53		68		57		23-Dec-07		0:25:59		64.4		32

		12-Nov-07		2:07:10		70.41		55		12-Nov-07		2:06:20		68.61		59		12-Nov-07		2:07:53		68		57.5		23-Dec-07		2:25:59		63.21		32.5

		12-Nov-07		4:07:10		69.8		50.5		12-Nov-07		4:06:20		68.61		52		12-Nov-07		4:07:53		67.4		55.5		23-Dec-07		4:25:59		62.6		31.5

		12-Nov-07		6:07:10		69.8		45.5		12-Nov-07		6:06:20		68.61		46		12-Nov-07		6:07:53		66.2		51.5		23-Dec-07		6:25:59		62		31

		12-Nov-07		8:07:10		69.2		43.5		12-Nov-07		8:06:20		68		45.5		12-Nov-07		8:07:53		67.4		47		23-Dec-07		8:25:59		62.6		31

		12-Nov-07		10:07:10		69.2		44		12-Nov-07		10:06:20		68.61		46		12-Nov-07		10:07:53		68		47		23-Dec-07		10:25:59		62.6		32

		12-Nov-07		12:07:10		70.41		43		12-Nov-07		12:06:20		69.2		43.5		12-Nov-07		12:07:53		68		46.5		23-Dec-07		12:25:59		62.6		33.5

		12-Nov-07		14:07:10		71		39.5		12-Nov-07		14:06:20		69.2		39		12-Nov-07		14:07:53		69.2		43		23-Dec-07		14:25:59		65.01		35

		12-Nov-07		16:07:10		71		38.5		12-Nov-07		16:06:20		69.2		38.5		12-Nov-07		16:07:53		69.8		42.5		23-Dec-07		16:25:59		65.01		34

		12-Nov-07		18:07:10		71.6		39		12-Nov-07		18:06:20		69.8		38.5		12-Nov-07		18:07:53		69.8		42.5		23-Dec-07		18:25:59		64.4		34

		12-Nov-07		20:07:10		71		39.5		12-Nov-07		20:06:20		68.61		42		12-Nov-07		20:07:53		69.2		43		23-Dec-07		20:25:59		63.21		35.5

		12-Nov-07		22:07:10		70.41		39		12-Nov-07		22:06:20		68.61		41.5		12-Nov-07		22:07:53		67.4		43		23-Dec-07		22:25:59		62.6		35.5

		13-Nov-07		0:07:10		69.8		38.5		13-Nov-07		0:06:20		68		41		13-Nov-07		0:07:53		65.6		43.5		24-Dec-07		0:25:59		62.6		36

		13-Nov-07		2:07:10		69.2		38		13-Nov-07		2:06:20		68		40.5		13-Nov-07		2:07:53		64.4		44.5		24-Dec-07		2:25:59		62		36

		13-Nov-07		4:07:10		69.2		38		13-Nov-07		4:06:20		68		40.5		13-Nov-07		4:07:53		63.8		45		24-Dec-07		4:25:59		62		36

		13-Nov-07		6:07:10		68.61		39		13-Nov-07		6:06:20		68		41.5		13-Nov-07		6:07:53		66.81		43		24-Dec-07		6:25:59		62		36

		13-Nov-07		8:07:10		71.6		38		13-Nov-07		8:06:20		69.2		41		13-Nov-07		8:07:53		69.2		41.5		24-Dec-07		8:25:59		62		36

		13-Nov-07		10:07:10		72.8		38		13-Nov-07		10:06:20		70.41		42.5		13-Nov-07		10:07:53		71		41		24-Dec-07		10:25:59		62		36.5

		13-Nov-07		12:07:10		75.2		37.5		13-Nov-07		12:06:20		71		40		13-Nov-07		12:07:53		70.41		42.5		24-Dec-07		12:25:59		62		38

		13-Nov-07		14:07:10		74.6		35		13-Nov-07		14:06:20		71.6		38.5		13-Nov-07		14:07:53		71.6		42		24-Dec-07		14:25:59		63.21		41.5

		13-Nov-07		16:07:10		74.01		34.5		13-Nov-07		16:06:20		71.6		37.5		13-Nov-07		16:07:53		70.41		41		24-Dec-07		16:25:59		64.4		42.5

		13-Nov-07		18:07:10		74.01		32		13-Nov-07		18:06:20		69.8		31.5		13-Nov-07		18:07:53		70.41		38		24-Dec-07		18:25:59		65.6		43

		13-Nov-07		20:07:10		73.4		37		13-Nov-07		20:06:20		69.8		42		13-Nov-07		20:07:53		70.41		42		24-Dec-07		20:25:59		65.01		45.5

		13-Nov-07		22:07:10		72.8		40		13-Nov-07		22:06:20		69.8		45		13-Nov-07		22:07:53		69.8		44		24-Dec-07		22:25:59		64.4		44.5

		14-Nov-07		0:07:10		72.21		42		14-Nov-07		0:06:20		69.2		47.5		14-Nov-07		0:07:53		69.8		45		25-Dec-07		0:25:59		63.8		45

		14-Nov-07		2:07:10		72.21		43		14-Nov-07		2:06:20		69.8		48		14-Nov-07		2:07:53		69.2		47.5		25-Dec-07		2:25:59		63.8		45

		14-Nov-07		4:07:10		71.6		44.5		14-Nov-07		4:06:20		69.2		50		14-Nov-07		4:07:53		68.61		48.5		25-Dec-07		4:25:59		63.21		44.5

		14-Nov-07		6:07:10		71		46		14-Nov-07		6:06:20		69.2		51.5		14-Nov-07		6:07:53		68.61		50		25-Dec-07		6:25:59		64.4		44

		14-Nov-07		8:07:10		73.4		45		14-Nov-07		8:06:20		69.8		51.5		14-Nov-07		8:07:53		70.41		44		25-Dec-07		8:25:59		66.81		40.5

		14-Nov-07		10:07:10		74.01		46		14-Nov-07		10:06:20		71.6		54.5		14-Nov-07		10:07:53		70.41		53		25-Dec-07		10:25:59		69.2		36.5

		14-Nov-07		12:07:10		74.01		47.5		14-Nov-07		12:06:20		72.21		54		14-Nov-07		12:07:53		70.41		47		25-Dec-07		12:25:59		70.41		34.5

		14-Nov-07		14:07:10		74.01		48		14-Nov-07		14:06:20		72.21		45		14-Nov-07		14:07:53		70.41		47		25-Dec-07		14:25:59		71		33

		14-Nov-07		16:07:10		74.6		49.5		14-Nov-07		16:06:20		71.6		44.5		14-Nov-07		16:07:53		71		59.5		25-Dec-07		16:25:59		70.41		33.5

		14-Nov-07		18:07:10		74.6		49.5		14-Nov-07		18:06:20		71		49		14-Nov-07		18:07:53		71		53.5		25-Dec-07		18:25:59		68.61		33.5

		14-Nov-07		20:07:10		74.01		49		14-Nov-07		20:06:20		70.41		52.5		14-Nov-07		20:07:53		70.41		57.5		25-Dec-07		20:25:59		66.81		35

		14-Nov-07		22:07:10		73.4		52		14-Nov-07		22:06:20		69.8		61		14-Nov-07		22:07:53		71		55.5		25-Dec-07		22:25:59		64.4		35.5

		15-Nov-07		0:07:10		72.8		52		15-Nov-07		0:06:20		69.8		57		15-Nov-07		0:07:53		71		54		26-Dec-07		0:25:59		63.21		35

		15-Nov-07		2:07:10		72.21		50.5		15-Nov-07		2:06:20		69.8		56		15-Nov-07		2:07:53		70.41		53.5		26-Dec-07		2:25:59		62.6		34

		15-Nov-07		4:07:10		71.6		47		15-Nov-07		4:06:20		68.61		50.5		15-Nov-07		4:07:53		69.8		50.5		26-Dec-07		4:25:59		62		33.5

		15-Nov-07		6:07:10		71		45.5		15-Nov-07		6:06:20		68.61		49		15-Nov-07		6:07:53		68.61		49.5		26-Dec-07		6:25:59		62		33

		15-Nov-07		8:07:10		72.21		43.5		15-Nov-07		8:06:20		69.2		47		15-Nov-07		8:07:53		70.41		47.5		26-Dec-07		8:25:59		62.6		32.5

		15-Nov-07		10:07:10		74.01		44.5		15-Nov-07		10:06:20		71.6		56		15-Nov-07		10:07:53		71		46.5		26-Dec-07		10:25:59		62		32.5

		15-Nov-07		12:07:10		74.01		46.5		15-Nov-07		12:06:20		71.6		54		15-Nov-07		12:07:53		71.6		50.5		26-Dec-07		12:25:59		62		33.5

		15-Nov-07		14:07:10		74.01		47.5		15-Nov-07		14:06:20		71.6		56		15-Nov-07		14:07:53		71		52		26-Dec-07		14:25:59		62.6		34.5

		15-Nov-07		16:07:10		74.6		50		15-Nov-07		16:06:20		71.6		45.5		15-Nov-07		16:07:53		70.41		56		26-Dec-07		16:25:59		63.8		35.5

		15-Nov-07		18:07:10		74.01		51		15-Nov-07		18:06:20		70.41		51		15-Nov-07		18:07:53		70.41		56		26-Dec-07		18:25:59		63.8		37

		15-Nov-07		20:07:10		73.4		50		15-Nov-07		20:06:20		69.8		56.5		15-Nov-07		20:07:53		71		55.5		26-Dec-07		20:25:59		63.21		38

		15-Nov-07		22:07:10		73.4		48.5		15-Nov-07		22:06:20		69.8		54.5		15-Nov-07		22:07:53		71.6		51.5		26-Dec-07		22:25:59		62.6		37.5

		16-Nov-07		0:07:10		72.8		46.5		16-Nov-07		0:06:20		69.8		51		16-Nov-07		0:07:53		71		50		27-Dec-07		0:25:59		62		38.5

		16-Nov-07		2:07:10		71.6		45.5		16-Nov-07		2:06:20		68.61		49.5		16-Nov-07		2:07:53		69.2		49		27-Dec-07		2:25:59		62		39

		16-Nov-07		4:07:10		71		45.5		16-Nov-07		4:06:20		68.61		49.5		16-Nov-07		4:07:53		68.61		49.5		27-Dec-07		4:25:59		62		38

		16-Nov-07		6:07:10		70.41		44		16-Nov-07		6:06:20		68.61		47.5		16-Nov-07		6:07:53		67.4		49		27-Dec-07		6:25:59		62		37.5

		16-Nov-07		8:07:10		71.6		42.5		16-Nov-07		8:06:20		68.61		46		16-Nov-07		8:07:53		70.41		46		27-Dec-07		8:25:59		63.21		36.5

		16-Nov-07		10:07:10		72.8		44.5		16-Nov-07		10:06:20		71		49.5		16-Nov-07		10:07:53		72.21		47		27-Dec-07		10:25:59		67.4		35

		16-Nov-07		12:07:10		73.4		45		16-Nov-07		12:06:20		71.6		50.5		16-Nov-07		12:07:53		71		47		27-Dec-07		12:25:59		72.21		30.5

		16-Nov-07		14:07:10		74.01		46.5		16-Nov-07		14:06:20		71.6		53.5		16-Nov-07		14:07:53		71.6		51.5		27-Dec-07		14:25:59		71		28

		16-Nov-07		16:07:10		74.01		50		16-Nov-07		16:06:20		71.6		52		16-Nov-07		16:07:53		71		60.5		27-Dec-07		16:25:59		71		26

		16-Nov-07		18:07:10		74.01		49.5		16-Nov-07		18:06:20		70.41		62		16-Nov-07		18:07:53		70.41		53.5		27-Dec-07		18:25:59		70.41		26

		16-Nov-07		20:07:10		73.4		51		16-Nov-07		20:06:20		69.8		57.5		16-Nov-07		20:07:53		70.41		57		27-Dec-07		20:25:59		69.2		26.5

		16-Nov-07		22:07:10		72.8		51		16-Nov-07		22:06:20		69.8		56.5		16-Nov-07		22:07:53		70.41		55.5		27-Dec-07		22:25:59		66.2		31.5

		17-Nov-07		0:07:10		72.21		50.5		17-Nov-07		0:06:20		69.8		56		17-Nov-07		0:07:53		70.41		54		28-Dec-07		0:25:59		63.8		29.5

		17-Nov-07		2:07:10		71.6		50.5		17-Nov-07		2:06:20		69.2		56		17-Nov-07		2:07:53		69.8		53.5		28-Dec-07		2:25:59		62.6		29.5

		17-Nov-07		4:07:10		71.6		50.5		17-Nov-07		4:06:20		69.2		55.5		17-Nov-07		4:07:53		69.2		54		28-Dec-07		4:25:59		62.6		29.5

		17-Nov-07		6:07:10		71		49.5		17-Nov-07		6:06:20		68		54		17-Nov-07		6:07:53		68.61		53.5		28-Dec-07		6:25:59		62.6		29

		17-Nov-07		8:07:10		71.6		49.5		17-Nov-07		8:06:20		68		55		17-Nov-07		8:07:53		71		53		28-Dec-07		8:25:59		65.01		28.5

		17-Nov-07		10:07:10		72.21		47.5		17-Nov-07		10:06:20		71		51.5		17-Nov-07		10:07:53		71		49.5		28-Dec-07		10:25:59		68.61		28

		17-Nov-07		12:07:10		73.4		47.5		17-Nov-07		12:06:20		72.21		55		17-Nov-07		12:07:53		71.6		55.5		28-Dec-07		12:25:59		71.6		27

		17-Nov-07		14:07:10		74.01		49.5		17-Nov-07		14:06:20		71		46		17-Nov-07		14:07:53		71		57.5		28-Dec-07		14:25:59		71		28.5

		17-Nov-07		16:07:10		74.6		50		17-Nov-07		16:06:20		71.6		48		17-Nov-07		16:07:53		70.41		58		28-Dec-07		16:25:59		71		28.5

		17-Nov-07		18:07:10		74.6		48.5		17-Nov-07		18:06:20		69.8		55		17-Nov-07		18:07:53		70.41		50		28-Dec-07		18:25:59		72.21		29.5

		17-Nov-07		20:07:10		72.8		47.5		17-Nov-07		20:06:20		69.8		52		17-Nov-07		20:07:53		69.8		52		28-Dec-07		20:25:59		71		32

		17-Nov-07		22:07:10		71.6		48		17-Nov-07		22:06:20		69.2		53.5		17-Nov-07		22:07:53		69.2		51.5		28-Dec-07		22:25:59		68		34.5

		18-Nov-07		0:07:10		71.6		49.5		18-Nov-07		0:06:20		68.61		54		18-Nov-07		0:07:53		69.2		53		29-Dec-07		0:25:59		65.6		35

		18-Nov-07		2:07:10		71		49		18-Nov-07		2:06:20		68		54.5		18-Nov-07		2:07:53		68		53		29-Dec-07		2:25:59		64.4		36

		18-Nov-07		4:07:10		70.41		50		18-Nov-07		4:06:20		68		55		18-Nov-07		4:07:53		67.4		53.5		29-Dec-07		4:25:59		63.21		37

		18-Nov-07		6:07:10		69.8		49.5		18-Nov-07		6:06:20		67.4		54.5		18-Nov-07		6:07:53		66.81		54		29-Dec-07		6:25:59		64.4		37.5

		18-Nov-07		8:07:10		69.8		49.5		18-Nov-07		8:06:20		67.4		54.5		18-Nov-07		8:07:53		67.4		53		29-Dec-07		8:25:59		66.81		36.5

		18-Nov-07		10:07:10		69.2		49.5		18-Nov-07		10:06:20		67.4		54.5		18-Nov-07		10:07:53		67.4		53		29-Dec-07		10:25:59		69.8		36

		18-Nov-07		12:07:10		69.8		51.5		18-Nov-07		12:06:20		67.4		56.5		18-Nov-07		12:07:53		67.4		55.5		29-Dec-07		12:25:59		72.8		34

		18-Nov-07		14:07:10		70.41		52		18-Nov-07		14:06:20		68.61		55.5		18-Nov-07		14:07:53		68		55.5		29-Dec-07		14:25:59		72.8		34

		18-Nov-07		16:07:10		71		53.5		18-Nov-07		16:06:20		69.2		53.5		18-Nov-07		16:07:53		69.8		58		29-Dec-07		16:25:59		73.4		33

		18-Nov-07		18:07:10		71.6		55		18-Nov-07		18:06:20		69.2		56		18-Nov-07		18:07:53		69.8		58.5		29-Dec-07		18:25:59		72.21		33.5

		18-Nov-07		20:07:10		71		52		18-Nov-07		20:06:20		69.2		55.5		18-Nov-07		20:07:53		69.8		54.5		29-Dec-07		20:25:59		71		34

		18-Nov-07		22:07:10		70.41		52		18-Nov-07		22:06:20		68.61		56		18-Nov-07		22:07:53		68.61		55		29-Dec-07		22:25:59		67.4		36

		19-Nov-07		0:07:10		70.41		52		19-Nov-07		0:06:20		68		56		19-Nov-07		0:07:53		68.61		54.5		30-Dec-07		0:25:59		65.01		37.5

		19-Nov-07		2:07:10		69.8		51		19-Nov-07		2:06:20		67.4		56		19-Nov-07		2:07:53		68		55		30-Dec-07		2:25:59		63.8		38

		19-Nov-07		4:07:10		69.8		51		19-Nov-07		4:06:20		67.4		56.5		19-Nov-07		4:07:53		67.4		55.5		30-Dec-07		4:25:59		63.21		39

		19-Nov-07		6:07:10		69.8		51		19-Nov-07		6:06:20		67.4		55.5		19-Nov-07		6:07:53		66.81		56		30-Dec-07		6:25:59		62.6		39.5

		19-Nov-07		8:07:10		69.2		51		19-Nov-07		8:06:20		67.4		55.5		19-Nov-07		8:07:53		67.4		54		30-Dec-07		8:25:59		62.6		40.5

		19-Nov-07		10:07:10		69.2		52		19-Nov-07		10:06:20		67.4		56.5		19-Nov-07		10:07:53		67.4		55.5		30-Dec-07		10:25:59		63.21		42.5

		19-Nov-07		12:07:10		69.8		54.5		19-Nov-07		12:06:20		68		60		19-Nov-07		12:07:53		67.4		58		30-Dec-07		12:25:59		63.21		43.5

		19-Nov-07		14:07:10		70.41		56.5		19-Nov-07		14:06:20		68.61		60		19-Nov-07		14:07:53		68.61		59.5		30-Dec-07		14:25:59		63.8		44.5

		19-Nov-07		16:07:10		71		59		19-Nov-07		16:06:20		69.2		65		19-Nov-07		16:07:53		69.2		61.5		30-Dec-07		16:25:59		63.21		45

		19-Nov-07		18:07:10		71		55		19-Nov-07		18:06:20		69.8		54		19-Nov-07		18:07:53		69.8		59		30-Dec-07		18:25:59		63.21		46

		19-Nov-07		20:07:10		71.6		53		19-Nov-07		20:06:20		69.8		55		19-Nov-07		20:07:53		69.8		56		30-Dec-07		20:25:59		62.6		46.5

		19-Nov-07		22:07:10		71		52		19-Nov-07		22:06:20		69.2		54.5		19-Nov-07		22:07:53		69.2		54.5		30-Dec-07		22:25:59		62.6		47

		20-Nov-07		0:07:10		70.41		50		20-Nov-07		0:06:20		68		53.5		20-Nov-07		0:07:53		68.61		53		31-Dec-07		0:25:59		62.6		47.5

		20-Nov-07		2:07:10		69.8		48.5		20-Nov-07		2:06:20		68		52.5		20-Nov-07		2:07:53		67.4		52.5		31-Dec-07		2:25:59		62.6		48

		20-Nov-07		4:07:10		69.2		50		20-Nov-07		4:06:20		67.4		54.5		20-Nov-07		4:07:53		66.81		54		31-Dec-07		4:25:59		62.6		48.5

		20-Nov-07		6:07:10		69.2		52.5		20-Nov-07		6:06:20		67.4		58		20-Nov-07		6:07:53		67.4		54.5		31-Dec-07		6:25:59		62		48

		20-Nov-07		8:07:10		71		54.5		20-Nov-07		8:06:20		68.61		60		20-Nov-07		8:07:53		69.8		56.5		31-Dec-07		8:25:59		63.21		46

		20-Nov-07		10:07:10		72.8		56		20-Nov-07		10:06:20		70.41		58		20-Nov-07		10:07:53		71		50		31-Dec-07		10:25:59		63.8		44

		20-Nov-07		12:07:10		74.6		50.5		20-Nov-07		12:06:20		71		58.5		20-Nov-07		12:07:53		71.6		58		31-Dec-07		12:25:59		65.01		42.5

		20-Nov-07		14:07:10		74.6		45.5		20-Nov-07		14:06:20		71.6		52		20-Nov-07		14:07:53		71		52		31-Dec-07		14:25:59		65.6		41.5

		20-Nov-07		16:07:10		74.01		41		20-Nov-07		16:06:20		72.21		44		20-Nov-07		16:07:53		70.41		51.5		31-Dec-07		16:25:59		65.6		40.5

		20-Nov-07		18:07:10		73.4		40.5		20-Nov-07		18:06:20		69.8		42.5		20-Nov-07		18:07:53		70.41		48		31-Dec-07		18:25:59		65.6		39

		20-Nov-07		20:07:10		72.8		40		20-Nov-07		20:06:20		69.8		42		20-Nov-07		20:07:53		69.2		45.5		31-Dec-07		20:25:59		64.4		38.5

		20-Nov-07		22:07:10		71.6		39.5		20-Nov-07		22:06:20		68.61		42.5		20-Nov-07		22:07:53		68.61		44		31-Dec-07		22:25:59		62.6		38.5

		21-Nov-07		0:07:10		71		39		21-Nov-07		0:06:20		68.61		40.5		21-Nov-07		0:07:53		68		43		1-Jan-08		0:25:59		62.6		37

		21-Nov-07		2:07:10		70.41		38.5		21-Nov-07		2:06:20		68		40.5		21-Nov-07		2:07:53		66.2		43.5		1-Jan-08		2:25:59		62		36

		21-Nov-07		4:07:10		69.8		37		21-Nov-07		4:06:20		68		39.5		21-Nov-07		4:07:53		65.01		43.5		1-Jan-08		4:25:59		62		35

		21-Nov-07		6:07:10		69.2		36.5		21-Nov-07		6:06:20		68		38.5		21-Nov-07		6:07:53		67.4		39.5		1-Jan-08		6:25:59		62.6		33.5

		21-Nov-07		8:07:10		71		35.5		21-Nov-07		8:06:20		68		37		21-Nov-07		8:07:53		68.61		38		1-Jan-08		8:25:59		65.01		32.5

		21-Nov-07		10:07:10		71.6		35.5		21-Nov-07		10:06:20		69.8		34.5		21-Nov-07		10:07:53		71.6		37		1-Jan-08		10:25:59		68		31

		21-Nov-07		12:07:10		72.8		33.5		21-Nov-07		12:06:20		70.41		34.5		21-Nov-07		12:07:53		70.41		38.5		1-Jan-08		12:25:59		72.21		30.5

		21-Nov-07		14:07:10		73.4		33.5		21-Nov-07		14:06:20		71		35		21-Nov-07		14:07:53		71.6		34.5		1-Jan-08		14:25:59		71.6		31.5

		21-Nov-07		16:07:10		74.6		33.5		21-Nov-07		16:06:20		71		36		21-Nov-07		16:07:53		71		37.5		1-Jan-08		16:25:59		72.21		30.5

		21-Nov-07		18:07:10		74.01		35		21-Nov-07		18:06:20		69.8		37.5		21-Nov-07		18:07:53		70.41		38.5		1-Jan-08		18:25:59		71		31.5

		21-Nov-07		20:07:10		72.8		34		21-Nov-07		20:06:20		69.2		36		21-Nov-07		20:07:53		70.41		38		1-Jan-08		20:25:59		70.41		31.5

		21-Nov-07		22:07:10		71		34		21-Nov-07		22:06:20		68.61		36.5		21-Nov-07		22:07:53		68		37.5		1-Jan-08		22:25:59		66.2		32.5

		22-Nov-07		0:07:10		70.41		33.5		22-Nov-07		0:06:20		68		35.5		22-Nov-07		0:07:53		65.6		38		2-Jan-08		0:25:59		63.8		33

		22-Nov-07		2:07:10		69.8		32		22-Nov-07		2:06:20		68		34		22-Nov-07		2:07:53		64.4		38		2-Jan-08		2:25:59		62.6		33

		22-Nov-07		4:07:10		69.2		31		22-Nov-07		4:06:20		67.4		33		22-Nov-07		4:07:53		63.21		37.5		2-Jan-08		4:25:59		62		32.5

		22-Nov-07		6:07:10		68.61		31		22-Nov-07		6:06:20		68		32.5		22-Nov-07		6:07:53		66.81		33.5		2-Jan-08		6:25:59		62.6		31.5

		22-Nov-07		8:07:10		70.41		30.5		22-Nov-07		8:06:20		69.8		31.5		22-Nov-07		8:07:53		69.2		32		2-Jan-08		8:25:59		63.8		31

		22-Nov-07		10:07:10		71.6		31.5		22-Nov-07		10:06:20		70.41		33.5		22-Nov-07		10:07:53		71.6		33		2-Jan-08		10:25:59		64.4		31

		22-Nov-07		12:07:10		72.21		32.5		22-Nov-07		12:06:20		71		34		22-Nov-07		12:07:53		70.41		35.5		2-Jan-08		12:25:59		66.81		32.5

		22-Nov-07		14:07:10		73.4		31.5		22-Nov-07		14:06:20		71		32.5		22-Nov-07		14:07:53		71.6		33.5		2-Jan-08		14:25:59		68.61		34

		22-Nov-07		16:07:10		73.4		29		22-Nov-07		16:06:20		69.8		29		22-Nov-07		16:07:53		71.6		33		2-Jan-08		16:25:59		70.41		34.5

		22-Nov-07		18:07:10		74.01		31.5		22-Nov-07		18:06:20		69.8		34		22-Nov-07		18:07:53		70.41		36		2-Jan-08		18:25:59		71		33.5

		22-Nov-07		20:07:10		71.6		31		22-Nov-07		20:06:20		68.61		33		22-Nov-07		20:07:53		69.8		34.5		2-Jan-08		20:25:59		70.41		33

		22-Nov-07		22:07:10		70.41		31.5		22-Nov-07		22:06:20		66.81		34.5		22-Nov-07		22:07:53		66.81		35.5		2-Jan-08		22:25:59		66.2		34.5

		23-Nov-07		0:07:10		69.2		31.5		23-Nov-07		0:06:20		66.2		35		23-Nov-07		0:07:53		64.4		37		3-Jan-08		0:25:59		64.4		35.5

		23-Nov-07		2:07:10		68.61		31		23-Nov-07		2:06:20		66.2		34		23-Nov-07		2:07:53		63.21		37		3-Jan-08		2:25:59		62.6		35.5

		23-Nov-07		4:07:10		68		31		23-Nov-07		4:06:20		66.2		33.5		23-Nov-07		4:07:53		62		36.5		3-Jan-08		4:25:59		62		36

		23-Nov-07		6:07:10		67.4		30		23-Nov-07		6:06:20		66.2		31.5		23-Nov-07		6:07:53		66.2		32.5		3-Jan-08		6:25:59		63.8		36

		23-Nov-07		8:07:10		69.2		28.5		23-Nov-07		8:06:20		67.4		30		23-Nov-07		8:07:53		67.4		31		3-Jan-08		8:25:59		65.01		34.5

		23-Nov-07		10:07:10		69.8		30		23-Nov-07		10:06:20		68		33		23-Nov-07		10:07:53		68		32.5		3-Jan-08		10:25:59		67.4		35

		23-Nov-07		12:07:10		70.41		31.5		23-Nov-07		12:06:20		68.61		33		23-Nov-07		12:07:53		68.61		33.5		3-Jan-08		12:25:59		72.8		33.5

		23-Nov-07		14:07:10		71		31		23-Nov-07		14:06:20		69.2		32		23-Nov-07		14:07:53		69.2		34		3-Jan-08		14:25:59		73.4		33

		23-Nov-07		16:07:10		71.6		29.5		23-Nov-07		16:06:20		69.2		29		23-Nov-07		16:07:53		69.8		32.5		3-Jan-08		16:25:59		72.8		34

		23-Nov-07		18:07:10		71.6		31.5		23-Nov-07		18:06:20		69.8		31.5		23-Nov-07		18:07:53		69.8		34		3-Jan-08		18:25:59		72.8		34.5

		23-Nov-07		20:07:10		71.6		32		23-Nov-07		20:06:20		68.61		35		23-Nov-07		20:07:53		68.61		36		3-Jan-08		20:25:59		71.6		35

		23-Nov-07		22:07:10		69.8		32		23-Nov-07		22:06:20		67.4		35.5		23-Nov-07		22:07:53		66.81		36		3-Jan-08		22:25:59		68		36

		24-Nov-07		0:07:10		68.61		32		24-Nov-07		0:06:20		66.2		35.5		24-Nov-07		0:07:53		65.01		36.5		4-Jan-08		0:25:59		65.6		36.5

		24-Nov-07		2:07:10		68		31.5		24-Nov-07		2:06:20		66.2		33.5		24-Nov-07		2:07:53		63.8		36.5		4-Jan-08		2:25:59		64.4		38

		24-Nov-07		4:07:10		67.4		30.5		24-Nov-07		4:06:20		66.2		31.5		24-Nov-07		4:07:53		62.6		35.5		4-Jan-08		4:25:59		63.8		39

		24-Nov-07		6:07:10		67.4		30.5		24-Nov-07		6:06:20		66.2		32.5		24-Nov-07		6:07:53		66.81		32		4-Jan-08		6:25:59		65.01		41

		24-Nov-07		8:07:10		69.2		27		24-Nov-07		8:06:20		68		28		24-Nov-07		8:07:53		68		30		4-Jan-08		8:25:59		68.61		40

		24-Nov-07		10:07:10		70.41		23.5		24-Nov-07		10:06:20		69.2		22		24-Nov-07		10:07:53		68		26		4-Jan-08		10:25:59		71.6		41

		24-Nov-07		12:07:10		71		20.5		24-Nov-07		12:06:20		69.2		18.5		24-Nov-07		12:07:53		68.61		24		4-Jan-08		12:25:59		74.01		40.5

		24-Nov-07		14:07:10		71		19		24-Nov-07		14:06:20		69.2		16		24-Nov-07		14:07:53		69.2		23		4-Jan-08		14:25:59		73.4		42.5

		24-Nov-07		16:07:10		71.6		18.5		24-Nov-07		16:06:20		69.2		16.5		24-Nov-07		16:07:53		69.8		22		4-Jan-08		16:25:59		74.01		41.5

		24-Nov-07		18:07:10		71.6		18.5		24-Nov-07		18:06:20		69.2		17		24-Nov-07		18:07:53		70.41		22		4-Jan-08		18:25:59		73.4		42

		24-Nov-07		20:07:10		71.6		21		24-Nov-07		20:06:20		69.2		22		24-Nov-07		20:07:53		69.2		24.5		4-Jan-08		20:25:59		72.8		43

		24-Nov-07		22:07:10		69.8		24.5		24-Nov-07		22:06:20		67.4		28		24-Nov-07		22:07:53		67.4		28		4-Jan-08		22:25:59		69.8		44

		25-Nov-07		0:07:10		69.2		25.5		25-Nov-07		0:06:20		66.81		29		25-Nov-07		0:07:53		65.6		29.5		5-Jan-08		0:25:59		68		45

		25-Nov-07		2:07:10		68		25.5		25-Nov-07		2:06:20		66.2		28.5		25-Nov-07		2:07:53		63.8		30.5		5-Jan-08		2:25:59		67.4		45.5

		25-Nov-07		4:07:10		67.4		26		25-Nov-07		4:06:20		66.2		28.5		25-Nov-07		4:07:53		62.6		30.5		5-Jan-08		4:25:59		66.81		46

		25-Nov-07		6:07:10		66.81		25.5		25-Nov-07		6:06:20		66.2		28		25-Nov-07		6:07:53		62		31		5-Jan-08		6:25:59		67.4		49

		25-Nov-07		8:07:10		67.4		24.5		25-Nov-07		8:06:20		67.4		26		25-Nov-07		8:07:53		66.81		26.5		5-Jan-08		8:25:59		71.6		48.5

		25-Nov-07		10:07:10		68		26.5		25-Nov-07		10:06:20		68		29		25-Nov-07		10:07:53		67.4		28		5-Jan-08		10:25:59		73.4		48.5

		25-Nov-07		12:07:10		68.61		27.5		25-Nov-07		12:06:20		68		29		25-Nov-07		12:07:53		67.4		30		5-Jan-08		12:25:59		72.8		48.5

		25-Nov-07		14:07:10		69.2		26		25-Nov-07		14:06:20		69.2		26		25-Nov-07		14:07:53		68		29		5-Jan-08		14:25:59		72.21		46

		25-Nov-07		16:07:10		69.8		27.5		25-Nov-07		16:06:20		69.2		28.5		25-Nov-07		16:07:53		68.61		30.5		5-Jan-08		16:25:59		72.8		44.5

		25-Nov-07		18:07:10		70.41		29.5		25-Nov-07		18:06:20		69.2		30.5		25-Nov-07		18:07:53		68.61		31.5		5-Jan-08		18:25:59		73.4		42

		25-Nov-07		20:07:10		69.2		29.5		25-Nov-07		20:06:20		68		32		25-Nov-07		20:07:53		67.4		32.5		5-Jan-08		20:25:59		72.21		41.5

		25-Nov-07		22:07:10		68.61		32		25-Nov-07		22:06:20		66.81		35.5		25-Nov-07		22:07:53		66.2		35		5-Jan-08		22:25:59		68.61		43.5

		26-Nov-07		0:07:10		68		32		26-Nov-07		0:06:20		66.2		35.5		26-Nov-07		0:07:53		65.01		36		6-Jan-08		0:25:59		67.4		44

		26-Nov-07		2:07:10		68		32.5		26-Nov-07		2:06:20		66.2		35.5		26-Nov-07		2:07:53		63.8		37		6-Jan-08		2:25:59		66.2		43.5

		26-Nov-07		4:07:10		67.4		32.5		26-Nov-07		4:06:20		66.2		35.5		26-Nov-07		4:07:53		63.21		37.5		6-Jan-08		4:25:59		65.6		43.5

		26-Nov-07		6:07:10		67.4		33		26-Nov-07		6:06:20		66.2		35.5		26-Nov-07		6:07:53		62.6		38		6-Jan-08		6:25:59		65.01		43.5

		26-Nov-07		8:07:10		68		32.5		26-Nov-07		8:06:20		67.4		34.5		26-Nov-07		8:07:53		67.4		34		6-Jan-08		8:25:59		64.4		43.5

		26-Nov-07		10:07:10		68		34		26-Nov-07		10:06:20		67.4		36.5		26-Nov-07		10:07:53		67.4		36		6-Jan-08		10:25:59		64.4		44.5

		26-Nov-07		12:07:10		68.61		34.5		26-Nov-07		12:06:20		67.4		37		26-Nov-07		12:07:53		68		35.5		6-Jan-08		12:25:59		64.4		45.5

		26-Nov-07		14:07:10		68.61		32		26-Nov-07		14:06:20		68		32		26-Nov-07		14:07:53		68		34		6-Jan-08		14:25:59		64.4		47

		26-Nov-07		16:07:10		69.2		32		26-Nov-07		16:06:20		68.61		33		26-Nov-07		16:07:53		67.4		34.5		6-Jan-08		16:25:59		65.01		47.5

		26-Nov-07		18:07:10		69.2		33		26-Nov-07		18:06:20		68		35		26-Nov-07		18:07:53		68		35.5		6-Jan-08		18:25:59		64.4		47.5

		26-Nov-07		20:07:10		68.61		34		26-Nov-07		20:06:20		67.4		36.5		26-Nov-07		20:07:53		66.81		36.5		6-Jan-08		20:25:59		64.4		47.5

		26-Nov-07		22:07:10		68		33.5		26-Nov-07		22:06:20		66.2		36		26-Nov-07		22:07:53		64.4		37.5		6-Jan-08		22:25:59		64.4		46.5

		27-Nov-07		0:07:10		67.4		33		27-Nov-07		0:06:20		66.2		36		27-Nov-07		0:07:53		63.8		38		7-Jan-08		0:25:59		64.4		46

		27-Nov-07		2:07:10		66.81		32		27-Nov-07		2:06:20		66.2		34		27-Nov-07		2:07:53		62.6		36.5		7-Jan-08		2:25:59		63.8		45

		27-Nov-07		4:07:10		66.81		31.5		27-Nov-07		4:06:20		65.6		32.5		27-Nov-07		4:07:53		62		36.5		7-Jan-08		4:25:59		63.8		44.5

		27-Nov-07		6:07:10		66.81		30.5		27-Nov-07		6:06:20		65.6		32		27-Nov-07		6:07:53		66.81		32		7-Jan-08		6:25:59		63.21		43.5

		27-Nov-07		8:07:10		69.2		28.5		27-Nov-07		8:06:20		67.4		30.5		27-Nov-07		8:07:53		68.61		30.5		7-Jan-08		8:25:59		63.21		43

		27-Nov-07		10:07:10		69.8		31		27-Nov-07		10:06:20		69.8		32.5		27-Nov-07		10:07:53		69.2		32		7-Jan-08		10:25:59		63.8		42

		27-Nov-07		12:07:10		71		32.5		27-Nov-07		12:06:20		71.6		34		27-Nov-07		12:07:53		71		33.5		7-Jan-08		12:25:59		63.8		43

		27-Nov-07		14:07:10		71.6		34		27-Nov-07		14:06:20		71		35.5		27-Nov-07		14:07:53		71		34.5		7-Jan-08		14:25:59		65.01		44.5

		27-Nov-07		16:07:10		72.21		34		27-Nov-07		16:06:20		71.6		37.5		27-Nov-07		16:07:53		70.41		38		7-Jan-08		16:25:59		65.01		44.5

		27-Nov-07		18:07:10		72.21		36.5		27-Nov-07		18:06:20		69.8		39.5		27-Nov-07		18:07:53		69.8		39		7-Jan-08		18:25:59		65.6		44

		27-Nov-07		20:07:10		71.6		36.5		27-Nov-07		20:06:20		68.61		40		27-Nov-07		20:07:53		69.2		39.5		7-Jan-08		20:25:59		64.4		44.5

		27-Nov-07		22:07:10		69.8		35		27-Nov-07		22:06:20		67.4		38.5		27-Nov-07		22:07:53		67.4		38.5		7-Jan-08		22:25:59		63.8		45

		28-Nov-07		0:07:10		69.2		35		28-Nov-07		0:06:20		66.81		38.5		28-Nov-07		0:07:53		66.2		38.5		8-Jan-08		0:25:59		63.8		45.5

		28-Nov-07		2:07:10		68		34.5		28-Nov-07		2:06:20		66.2		38		28-Nov-07		2:07:53		65.01		39		8-Jan-08		2:25:59		63.8		45.5

		28-Nov-07		4:07:10		68		34		28-Nov-07		4:06:20		66.2		37		28-Nov-07		4:07:53		63.8		39		8-Jan-08		4:25:59		63.8		46

		28-Nov-07		6:07:10		67.4		34.5		28-Nov-07		6:06:20		66.2		37.5		28-Nov-07		6:07:53		67.4		35.5		8-Jan-08		6:25:59		65.01		45

		28-Nov-07		8:07:10		69.8		34		28-Nov-07		8:06:20		68		36.5		28-Nov-07		8:07:53		69.2		36.5		8-Jan-08		8:25:59		67.4		40.5

		28-Nov-07		10:07:10		71		34.5		28-Nov-07		10:06:20		70.41		36.5		28-Nov-07		10:07:53		71.6		36		8-Jan-08		10:25:59		69.8		39

		28-Nov-07		12:07:10		72.21		39		28-Nov-07		12:06:20		71		43.5		28-Nov-07		12:07:53		71		41		8-Jan-08		12:25:59		73.4		39

		28-Nov-07		14:07:10		72.8		34		28-Nov-07		14:06:20		71		34		28-Nov-07		14:07:53		71		39		8-Jan-08		14:25:59		72.8		37

		28-Nov-07		16:07:10		72.8		33.5		28-Nov-07		16:06:20		71.6		34.5		28-Nov-07		16:07:53		71		37.5		8-Jan-08		16:25:59		72.21		36

		28-Nov-07		18:07:10		72.8		35		28-Nov-07		18:06:20		70.41		37.5		28-Nov-07		18:07:53		71		37.5		8-Jan-08		18:25:59		72.21		35.5

		28-Nov-07		20:07:10		72.8		35		28-Nov-07		20:06:20		69.8		37.5		28-Nov-07		20:07:53		70.41		38.5		8-Jan-08		20:25:59		71.6		34.5

		28-Nov-07		22:07:10		71.6		35		28-Nov-07		22:06:20		68.61		38		28-Nov-07		22:07:53		69.2		38		8-Jan-08		22:25:59		68		37.5

		29-Nov-07		0:07:10		70.41		35.5		29-Nov-07		0:06:20		67.4		38.5		29-Nov-07		0:07:53		68		38		9-Jan-08		0:25:59		66.81		38

		29-Nov-07		2:07:10		69.2		34		29-Nov-07		2:06:20		66.81		37		29-Nov-07		2:07:53		66.2		38		9-Jan-08		2:25:59		65.6		39

		29-Nov-07		4:07:10		68.61		33		29-Nov-07		4:06:20		66.81		35.5		29-Nov-07		4:07:53		65.01		37.5		9-Jan-08		4:25:59		65.01		39.5

		29-Nov-07		6:07:10		68.61		32		29-Nov-07		6:06:20		66.2		33.5		29-Nov-07		6:07:53		66.81		34.5		9-Jan-08		6:25:59		65.6		39.5

		29-Nov-07		8:07:10		70.41		30.5		29-Nov-07		8:06:20		68		32		29-Nov-07		8:07:53		68		33.5		9-Jan-08		8:25:59		68.61		38

		29-Nov-07		10:07:10		71.6		32.5		29-Nov-07		10:06:20		71		34.5		29-Nov-07		10:07:53		70.41		34		9-Jan-08		10:25:59		71		40

		29-Nov-07		12:07:10		72.8		31		29-Nov-07		12:06:20		71.6		32.5		29-Nov-07		12:07:53		71		33		9-Jan-08		12:25:59		73.4		39

		29-Nov-07		14:07:10		72.8		31		29-Nov-07		14:06:20		71.6		32.5		29-Nov-07		14:07:53		71.6		31		9-Jan-08		14:25:59		74.01		40

		29-Nov-07		16:07:10		72.8		30.5		29-Nov-07		16:06:20		71.6		31.5		29-Nov-07		16:07:53		71		35		9-Jan-08		16:25:59		74.6		41

		29-Nov-07		18:07:10		72.8		28		29-Nov-07		18:06:20		69.2		29		29-Nov-07		18:07:53		71		32		9-Jan-08		18:25:59		75.2		41.5

		29-Nov-07		20:07:10		72.21		30		29-Nov-07		20:06:20		69.2		31		29-Nov-07		20:07:53		69.8		32.5		9-Jan-08		20:25:59		73.4		41.5

		29-Nov-07		22:07:10		70.41		31		29-Nov-07		22:06:20		67.4		34		29-Nov-07		22:07:53		68		34		9-Jan-08		22:25:59		69.8		42.5

		30-Nov-07		0:07:10		69.2		31		30-Nov-07		0:06:20		66.81		34		30-Nov-07		0:07:53		66.2		34.5		10-Jan-08		0:25:59		68		44

		30-Nov-07		2:07:10		68.61		30.5		30-Nov-07		2:06:20		66.2		33.5		30-Nov-07		2:07:53		65.01		35		10-Jan-08		2:25:59		66.81		44.5

		30-Nov-07		4:07:10		68		30		30-Nov-07		4:06:20		65.6		33		30-Nov-07		4:07:53		63.21		35		10-Jan-08		4:25:59		66.2		45

		30-Nov-07		6:07:10		67.4		30		30-Nov-07		6:06:20		66.2		32		30-Nov-07		6:07:53		67.4		31		10-Jan-08		6:25:59		68		45

		30-Nov-07		8:07:10		69.8		28		30-Nov-07		8:06:20		68.61		30.5		30-Nov-07		8:07:53		68		31		10-Jan-08		8:25:59		71.6		41.5

		30-Nov-07		10:07:10		71		30		30-Nov-07		10:06:20		70.41		33		30-Nov-07		10:07:53		70.41		32		10-Jan-08		10:25:59		73.4		40.5

		30-Nov-07		12:07:10		71.6		31.5		30-Nov-07		12:06:20		71		31		30-Nov-07		12:07:53		71.6		31.5		10-Jan-08		12:25:59		74.6		39.5

		30-Nov-07		14:07:10		72.8		30		30-Nov-07		14:06:20		71		31		30-Nov-07		14:07:53		71		35		10-Jan-08		14:25:59		74.6		39

		30-Nov-07		16:07:10		73.4		28		30-Nov-07		16:06:20		71		29		30-Nov-07		16:07:53		71		32.5		10-Jan-08		16:25:59		74.6		39

		30-Nov-07		18:07:10		73.4		26.5		30-Nov-07		18:06:20		69.8		26.5		30-Nov-07		18:07:53		69.8		31		10-Jan-08		18:25:59		73.4		39.5

		30-Nov-07		20:07:10		72.21		26		30-Nov-07		20:06:20		69.2		27.5		30-Nov-07		20:07:53		69.2		29		10-Jan-08		20:25:59		74.01		38.5

		30-Nov-07		22:07:10		71		27.5		30-Nov-07		22:06:20		68		30.5		30-Nov-07		22:07:53		68		31		10-Jan-08		22:25:59		70.41		43

		1-Dec-07		0:07:10		69.8		28.5		1-Dec-07		0:06:20		67.4		32		1-Dec-07		0:07:53		66.81		32.5		11-Jan-08		0:25:59		68.61		42.5

		1-Dec-07		2:07:10		69.2		28.5		1-Dec-07		2:06:20		66.81		31.5		1-Dec-07		2:07:53		65.01		33		11-Jan-08		2:25:59		67.4		43.5

		1-Dec-07		4:07:10		68.61		28		1-Dec-07		4:06:20		66.2		30.5		1-Dec-07		4:07:53		64.4		33		11-Jan-08		4:25:59		66.2		44

		1-Dec-07		6:07:10		68.61		28		1-Dec-07		6:06:20		66.2		30.5		1-Dec-07		6:07:53		66.81		30.5		11-Jan-08		6:25:59		68		44.5

		1-Dec-07		8:07:10		70.41		27		1-Dec-07		8:06:20		68		29		1-Dec-07		8:07:53		69.2		29.5		11-Jan-08		8:25:59		71.6		42

		1-Dec-07		10:07:10		71		27.5		1-Dec-07		10:06:20		70.41		29.5		1-Dec-07		10:07:53		71		29		11-Jan-08		10:25:59		74.01		41.5

		1-Dec-07		12:07:10		72.21		26.5		1-Dec-07		12:06:20		71.6		27		1-Dec-07		12:07:53		71		29.5		11-Jan-08		12:25:59		74.6		41

		1-Dec-07		14:07:10		72.8		24.5		1-Dec-07		14:06:20		71		26		1-Dec-07		14:07:53		70.41		29		11-Jan-08		14:25:59		74.01		43

		1-Dec-07		16:07:10		72.8		24.5		1-Dec-07		16:06:20		71		25.5		1-Dec-07		16:07:53		70.41		28		11-Jan-08		16:25:59		73.4		44.5

		1-Dec-07		18:07:10		72.8		26.5		1-Dec-07		18:06:20		69.8		28.5		1-Dec-07		18:07:53		70.41		30.5		11-Jan-08		18:25:59		71.6		45.5

		1-Dec-07		20:07:10		71.6		24.5		1-Dec-07		20:06:20		68		26		1-Dec-07		20:07:53		68.61		28		11-Jan-08		20:25:59		69.2		46.5

		1-Dec-07		22:07:10		69.8		24.5		1-Dec-07		22:06:20		66.81		27.5		1-Dec-07		22:07:53		66.2		28.5		11-Jan-08		22:25:59		68.61		47

		2-Dec-07		0:07:10		68.61		26		2-Dec-07		0:06:20		66.2		28		2-Dec-07		0:07:53		64.4		31.5		12-Jan-08		0:25:59		67.4		47.5

		2-Dec-07		2:07:10		68		25		2-Dec-07		2:06:20		65.6		28		2-Dec-07		2:07:53		63.21		30.5		12-Jan-08		2:25:59		66.81		48

		2-Dec-07		4:07:10		67.4		24.5		2-Dec-07		4:06:20		65.6		26.5		2-Dec-07		4:07:53		62		29.5		12-Jan-08		4:25:59		66.2		48

		2-Dec-07		6:07:10		66.81		24		2-Dec-07		6:06:20		65.6		26		2-Dec-07		6:07:53		61.41		29		12-Jan-08		6:25:59		66.2		49

		2-Dec-07		8:07:10		67.4		23		2-Dec-07		8:06:20		67.4		24.5		2-Dec-07		8:07:53		66.81		25.5		12-Jan-08		8:25:59		69.8		44.5

		2-Dec-07		10:07:10		67.4		24.5		2-Dec-07		10:06:20		67.4		26		2-Dec-07		10:07:53		68.61		25		12-Jan-08		10:25:59		71.6		43.5

		2-Dec-07		12:07:10		68		27		2-Dec-07		12:06:20		68		28.5		2-Dec-07		12:07:53		68.61		28		12-Jan-08		12:25:59		70.41		45

		2-Dec-07		14:07:10		68.61		27.5		2-Dec-07		14:06:20		68		28.5		2-Dec-07		14:07:53		69.2		29		12-Jan-08		14:25:59		71		44.5

		2-Dec-07		16:07:10		69.2		28		2-Dec-07		16:06:20		68		29.5		2-Dec-07		16:07:53		68		30		12-Jan-08		16:25:59		70.41		44

		2-Dec-07		18:07:10		69.2		28.5		2-Dec-07		18:06:20		68		30		2-Dec-07		18:07:53		67.4		31		12-Jan-08		18:25:59		69.8		44

		2-Dec-07		20:07:10		68		30		2-Dec-07		20:06:20		66.81		33		2-Dec-07		20:07:53		67.4		31		12-Jan-08		20:25:59		68.61		44.5

		2-Dec-07		22:07:10		67.4		29.5		2-Dec-07		22:06:20		66.2		32.5		2-Dec-07		22:07:53		63.8		33.5		12-Jan-08		22:25:59		67.4		46

		3-Dec-07		0:07:10		66.81		29.5		3-Dec-07		0:06:20		65.6		32		3-Dec-07		0:07:53		62.6		33.5		13-Jan-08		0:25:59		66.2		46.5

		3-Dec-07		2:07:10		66.81		30		3-Dec-07		2:06:20		66.2		33		3-Dec-07		2:07:53		62		34.5		13-Jan-08		2:25:59		66.2		47

		3-Dec-07		4:07:10		66.81		32.5		3-Dec-07		4:06:20		66.2		36		3-Dec-07		4:07:53		62.6		37.5		13-Jan-08		4:25:59		65.6		47

		3-Dec-07		6:07:10		66.81		35		3-Dec-07		6:06:20		66.2		39		3-Dec-07		6:07:53		62.6		40		13-Jan-08		6:25:59		65.01		47

		3-Dec-07		8:07:10		68		35.5		3-Dec-07		8:06:20		67.4		38		3-Dec-07		8:07:53		68.61		36		13-Jan-08		8:25:59		65.01		47.5

		3-Dec-07		10:07:10		68		35		3-Dec-07		10:06:20		67.4		37		3-Dec-07		10:07:53		68		36.5		13-Jan-08		10:25:59		65.01		48.5

		3-Dec-07		12:07:10		68		36		3-Dec-07		12:06:20		67.4		38		3-Dec-07		12:07:53		67.4		37.5		13-Jan-08		12:25:59		65.01		50

		3-Dec-07		14:07:10		68.61		36.5		3-Dec-07		14:06:20		68		39		3-Dec-07		14:07:53		68		38		13-Jan-08		14:25:59		65.6		51

		3-Dec-07		16:07:10		69.2		39		3-Dec-07		16:06:20		68		42.5		3-Dec-07		16:07:53		67.4		41		13-Jan-08		16:25:59		66.81		50

		3-Dec-07		18:07:10		69.2		39.5		3-Dec-07		18:06:20		68		42.5		3-Dec-07		18:07:53		67.4		42		13-Jan-08		18:25:59		67.4		49.5

		3-Dec-07		20:07:10		68.61		41		3-Dec-07		20:06:20		67.4		44.5		3-Dec-07		20:07:53		67.4		43		13-Jan-08		20:25:59		66.2		49.5

		3-Dec-07		22:07:10		68.61		44.5		3-Dec-07		22:06:20		66.81		50		3-Dec-07		22:07:53		66.2		47.5		13-Jan-08		22:25:59		65.6		49

		4-Dec-07		0:07:10		68.61		43		4-Dec-07		0:06:20		66.81		47		4-Dec-07		0:07:53		66.2		46.5		14-Jan-08		0:25:59		65.01		48

		4-Dec-07		2:07:10		68.61		42		4-Dec-07		2:06:20		66.81		45.5		4-Dec-07		2:07:53		66.2		45.5		14-Jan-08		2:25:59		64.4		48.5

		4-Dec-07		4:07:10		68.61		40.5		4-Dec-07		4:06:20		67.4		43		4-Dec-07		4:07:53		66.2		44.5		14-Jan-08		4:25:59		64.4		49

		4-Dec-07		6:07:10		68.61		40		4-Dec-07		6:06:20		67.4		42		4-Dec-07		6:07:53		66.2		44		14-Jan-08		6:25:59		64.4		49.5

		4-Dec-07		8:07:10		71.6		37		4-Dec-07		8:06:20		69.2		39		4-Dec-07		8:07:53		69.2		41		14-Jan-08		8:25:59		65.01		50.5

		4-Dec-07		10:07:10		72.8		39		4-Dec-07		10:06:20		71		42		4-Dec-07		10:07:53		70.41		43.5		14-Jan-08		10:25:59		65.6		49.5

		4-Dec-07		12:07:10		74.6		37.5		4-Dec-07		12:06:20		71.6		39		4-Dec-07		12:07:53		71		38.5		14-Jan-08		12:25:59		66.2		49

		4-Dec-07		14:07:10		73.4		38		4-Dec-07		14:06:20		71		42.5		4-Dec-07		14:07:53		71		39.5		14-Jan-08		14:25:59		66.81		48.5

		4-Dec-07		16:07:10		74.01		39.5		4-Dec-07		16:06:20		71.6		41.5		4-Dec-07		16:07:53		70.41		40		14-Jan-08		16:25:59		66.81		49

		4-Dec-07		18:07:10		74.01		40		4-Dec-07		18:06:20		70.41		42		4-Dec-07		18:07:53		71		45		14-Jan-08		18:25:59		66.81		49.5

		4-Dec-07		20:07:10		72.8		40.5		4-Dec-07		20:06:20		69.8		44		4-Dec-07		20:07:53		70.41		44		14-Jan-08		20:25:59		66.2		49

		4-Dec-07		22:07:10		72.21		44		4-Dec-07		22:06:20		69.8		50.5		4-Dec-07		22:07:53		69.8		46.5		14-Jan-08		22:25:59		65.01		49

		5-Dec-07		0:07:10		72.21		47		5-Dec-07		0:06:20		69.2		53.5		5-Dec-07		0:07:53		69.8		49.5		15-Jan-08		0:25:59		64.4		47.5

		5-Dec-07		2:07:10		71.6		48.5		5-Dec-07		2:06:20		69.2		54.5		5-Dec-07		2:07:53		69.2		51		15-Jan-08		2:25:59		63.8		47

		5-Dec-07		4:07:10		71		49.5		5-Dec-07		4:06:20		69.2		55		5-Dec-07		4:07:53		68.61		52.5		15-Jan-08		4:25:59		63.8		46.5

		5-Dec-07		6:07:10		71		50.5		5-Dec-07		6:06:20		68.61		56		5-Dec-07		6:07:53		68		53.5		15-Jan-08		6:25:59		64.4		46.5

		5-Dec-07		8:07:10		73.4		50		5-Dec-07		8:06:20		69.8		57.5		5-Dec-07		8:07:53		71		53		15-Jan-08		8:25:59		67.4		44

		5-Dec-07		10:07:10		74.01		49		5-Dec-07		10:06:20		71		44		5-Dec-07		10:07:53		71		57.5		15-Jan-08		10:25:59		71		43.5

		5-Dec-07		12:07:10		74.01		48		5-Dec-07		12:06:20		71.6		54		5-Dec-07		12:07:53		71		51		15-Jan-08		12:25:59		70.41		43

		5-Dec-07		14:07:10		74.01		49		5-Dec-07		14:06:20		71.6		54		5-Dec-07		14:07:53		71		48.5		15-Jan-08		14:25:59		69.8		44

		5-Dec-07		16:07:10		74.01		51		5-Dec-07		16:06:20		71.6		54		5-Dec-07		16:07:53		71		59.5		15-Jan-08		16:25:59		70.41		45

		5-Dec-07		18:07:10		73.4		50.5		5-Dec-07		18:06:20		69.8		57		5-Dec-07		18:07:53		71		47.5		15-Jan-08		18:25:59		71.6		43.5

		5-Dec-07		20:07:10		73.4		50		5-Dec-07		20:06:20		69.8		56		5-Dec-07		20:07:53		71		54.5		15-Jan-08		20:25:59		69.2		43

		5-Dec-07		22:07:10		72.8		50.5		5-Dec-07		22:06:20		69.8		56.5		5-Dec-07		22:07:53		70.41		55		15-Jan-08		22:25:59		66.81		43.5

		6-Dec-07		0:07:10		72.21		51.5		6-Dec-07		0:06:20		69.2		57		6-Dec-07		0:07:53		70.41		54.5		16-Jan-08		0:25:59		65.01		43.5

		6-Dec-07		2:07:10		71.6		51.5		6-Dec-07		2:06:20		69.2		57		6-Dec-07		2:07:53		69.8		54		16-Jan-08		2:25:59		64.4		43.5

		6-Dec-07		4:07:10		71.6		52		6-Dec-07		4:06:20		68.61		57.5		6-Dec-07		4:07:53		69.8		54		16-Jan-08		4:25:59		63.8		43.5

		6-Dec-07		6:07:10		71		50		6-Dec-07		6:06:20		68		54		6-Dec-07		6:07:53		69.2		53		16-Jan-08		6:25:59		64.4		42.5

		6-Dec-07		8:07:10		72.8		47.5		6-Dec-07		8:06:20		69.8		52		6-Dec-07		8:07:53		71		52		16-Jan-08		8:25:59		66.81		39.5

		6-Dec-07		10:07:10		74.01		45.5		6-Dec-07		10:06:20		71		45		6-Dec-07		10:07:53		71		50		16-Jan-08		10:25:59		70.41		38

		6-Dec-07		12:07:10		74.01		46		6-Dec-07		12:06:20		71		55		6-Dec-07		12:07:53		71		48		16-Jan-08		12:25:59		71		39.5

		6-Dec-07		14:07:10		74.01		46		6-Dec-07		14:06:20		71		57		6-Dec-07		14:07:53		71		54.5		16-Jan-08		14:25:59		72.21		40.5

		6-Dec-07		16:07:10		74.6		47.5		6-Dec-07		16:06:20		71		47.5		6-Dec-07		16:07:53		70.41		51.5		16-Jan-08		16:25:59		72.21		43

		6-Dec-07		18:07:10		74.01		39		6-Dec-07		18:06:20		69.8		41		6-Dec-07		18:07:53		69.8		45		16-Jan-08		18:25:59		72.8		41.5

		6-Dec-07		20:07:10		73.4		38		6-Dec-07		20:06:20		69.8		40		6-Dec-07		20:07:53		69.8		43.5		16-Jan-08		20:25:59		71		41.5

		6-Dec-07		22:07:10		72.21		40		6-Dec-07		22:06:20		69.2		44		6-Dec-07		22:07:53		70.41		44		16-Jan-08		22:25:59		68.61		41.5

		7-Dec-07		0:07:10		71.6		42		7-Dec-07		0:06:20		68		47		7-Dec-07		0:07:53		69.8		44.5		17-Jan-08		0:25:59		66.2		41.5

		7-Dec-07		2:07:10		70.41		42.5		7-Dec-07		2:06:20		67.4		48		7-Dec-07		2:07:53		69.2		45		17-Jan-08		2:25:59		65.01		41.5

		7-Dec-07		4:07:10		69.8		43		7-Dec-07		4:06:20		66.81		48.5		7-Dec-07		4:07:53		68.61		45.5		17-Jan-08		4:25:59		64.4		41.5

		7-Dec-07		6:07:10		69.8		43.5		7-Dec-07		6:06:20		66.81		49		7-Dec-07		6:07:53		68		46.5		17-Jan-08		6:25:59		65.01		39.5

		7-Dec-07		8:07:10		72.21		42		7-Dec-07		8:06:20		68.61		47.5		7-Dec-07		8:07:53		70.41		45		17-Jan-08		8:25:59		66.81		36.5

		7-Dec-07		10:07:10		73.4		42.5		7-Dec-07		10:06:20		71		49.5		7-Dec-07		10:07:53		71		48		17-Jan-08		10:25:59		71		33

		7-Dec-07		12:07:10		72.8		45		7-Dec-07		12:06:20		71		44.5		7-Dec-07		12:07:53		70.41		50.5		17-Jan-08		12:25:59		71.6		27

		7-Dec-07		14:07:10		72.21		47		7-Dec-07		14:06:20		71		47		7-Dec-07		14:07:53		71.6		52.5		17-Jan-08		14:25:59		72.8		25.5

		7-Dec-07		16:07:10		72.21		46		7-Dec-07		16:06:20		71		50		7-Dec-07		16:07:53		70.41		50		17-Jan-08		16:25:59		72.21		23.5

		7-Dec-07		18:07:10		72.21		45.5		7-Dec-07		18:06:20		69.2		50.5		7-Dec-07		18:07:53		70.41		51.5		17-Jan-08		18:25:59		72.21		23

		7-Dec-07		20:07:10		71		47		7-Dec-07		20:06:20		68.61		51		7-Dec-07		20:07:53		69.8		49		17-Jan-08		20:25:59		71.6		23

		7-Dec-07		22:07:10		69.8		47.5		7-Dec-07		22:06:20		67.4		52.5		7-Dec-07		22:07:53		69.8		48.5		17-Jan-08		22:25:59		69.2		24.5

		8-Dec-07		0:07:10		69.2		48		8-Dec-07		0:06:20		66.81		52.5		8-Dec-07		0:07:53		69.2		49		18-Jan-08		0:25:59		67.4		25.5

		8-Dec-07		2:07:10		68.61		44.5		8-Dec-07		2:06:20		66.81		47		8-Dec-07		2:07:53		68		46.5		18-Jan-08		2:25:59		66.2		26

		8-Dec-07		4:07:10		68.61		44		8-Dec-07		4:06:20		66.2		47		8-Dec-07		4:07:53		66.81		47		18-Jan-08		4:25:59		65.01		26

		8-Dec-07		6:07:10		68		43		8-Dec-07		6:06:20		66.2		45.5		8-Dec-07		6:07:53		67.4		45		18-Jan-08		6:25:59		66.2		26.5

		8-Dec-07		8:07:10		71		39		8-Dec-07		8:06:20		68		41		8-Dec-07		8:07:53		69.8		42		18-Jan-08		8:25:59		68.61		26

		8-Dec-07		10:07:10		72.21		37		8-Dec-07		10:06:20		69.8		40.5		8-Dec-07		10:07:53		71.6		40.5		18-Jan-08		10:25:59		72.21		27.5

		8-Dec-07		12:07:10		71.6		37.5		8-Dec-07		12:06:20		71		40.5		8-Dec-07		12:07:53		71		41		18-Jan-08		12:25:59		71.6		28

		8-Dec-07		14:07:10		71.6		36.5		8-Dec-07		14:06:20		71		40		8-Dec-07		14:07:53		71		35		18-Jan-08		14:25:59		72.21		29.5

		8-Dec-07		16:07:10		71.6		35.5		8-Dec-07		16:06:20		71		38		8-Dec-07		16:07:53		70.41		38.5		18-Jan-08		16:25:59		72.8		29

		8-Dec-07		18:07:10		71.6		35.5		8-Dec-07		18:06:20		69.8		35.5		8-Dec-07		18:07:53		69.8		37.5		18-Jan-08		18:25:59		72.21		30

		8-Dec-07		20:07:10		70.41		35		8-Dec-07		20:06:20		67.4		36.5		8-Dec-07		20:07:53		69.2		37		18-Jan-08		20:25:59		71.6		31.5

		8-Dec-07		22:07:10		69.2		33.5		8-Dec-07		22:06:20		66.81		36		8-Dec-07		22:07:53		67.4		37		18-Jan-08		22:25:59		68.61		32

		9-Dec-07		0:07:10		68.61		33.5		9-Dec-07		0:06:20		66.81		35.5		9-Dec-07		0:07:53		66.2		37		19-Jan-08		0:25:59		66.81		32.5

		9-Dec-07		2:07:10		68		33		9-Dec-07		2:06:20		66.2		35		9-Dec-07		2:07:53		65.6		37		19-Jan-08		2:25:59		65.01		33

		9-Dec-07		4:07:10		68		32.5		9-Dec-07		4:06:20		66.2		34		9-Dec-07		4:07:53		64.4		37		19-Jan-08		4:25:59		64.4		33

		9-Dec-07		6:07:10		67.4		32		9-Dec-07		6:06:20		66.2		33.5		9-Dec-07		6:07:53		63.8		36.5		19-Jan-08		6:25:59		66.2		32

		9-Dec-07		8:07:10		68		30.5		9-Dec-07		8:06:20		67.4		31.5		9-Dec-07		8:07:53		67.4		33		19-Jan-08		8:25:59		68.61		30

		9-Dec-07		10:07:10		68.61		30.5		9-Dec-07		10:06:20		68		31		9-Dec-07		10:07:53		68.61		31.5		19-Jan-08		10:25:59		70.41		31

		9-Dec-07		12:07:10		68.61		29.5		9-Dec-07		12:06:20		68.61		29		9-Dec-07		12:07:53		69.8		30		19-Jan-08		12:25:59		71		32.5

		9-Dec-07		14:07:10		68.61		28.5		9-Dec-07		14:06:20		68		28		9-Dec-07		14:07:53		70.41		30		19-Jan-08		14:25:59		71.6		33

		9-Dec-07		16:07:10		69.2		25		9-Dec-07		16:06:20		68		22.5		9-Dec-07		16:07:53		69.2		28.5		19-Jan-08		16:25:59		72.8		32.5

		9-Dec-07		18:07:10		69.2		24		9-Dec-07		18:06:20		68		23		9-Dec-07		18:07:53		68.61		27.5		19-Jan-08		18:25:59		72.8		33

		9-Dec-07		20:07:10		68.61		24		9-Dec-07		20:06:20		67.4		23.5		9-Dec-07		20:07:53		67.4		27		19-Jan-08		20:25:59		72.21		32

		9-Dec-07		22:07:10		68		24		9-Dec-07		22:06:20		66.81		24		9-Dec-07		22:07:53		66.2		27		19-Jan-08		22:25:59		68		34.5

		10-Dec-07		0:07:10		67.4		24		10-Dec-07		0:06:20		66.2		24.5		10-Dec-07		0:07:53		65.6		27.5		20-Jan-08		0:25:59		66.2		34.5

		10-Dec-07		2:07:10		67.4		24.5		10-Dec-07		2:06:20		66.2		25		10-Dec-07		2:07:53		64.4		28		20-Jan-08		2:25:59		65.01		34.5

		10-Dec-07		4:07:10		66.81		25		10-Dec-07		4:06:20		65.6		26.5		10-Dec-07		4:07:53		63.8		28.5		20-Jan-08		4:25:59		63.8		34

		10-Dec-07		6:07:10		66.2		26		10-Dec-07		6:06:20		65.6		28		10-Dec-07		6:07:53		63.21		29.5		20-Jan-08		6:25:59		63.21		33.5

		10-Dec-07		8:07:10		66.81		26		10-Dec-07		8:06:20		67.4		27		10-Dec-07		8:07:53		68.61		26.5		20-Jan-08		8:25:59		63.21		32.5

		10-Dec-07		10:07:10		67.4		26.5		10-Dec-07		10:06:20		67.4		27.5		10-Dec-07		10:07:53		67.4		27.5		20-Jan-08		10:25:59		63.21		33

		10-Dec-07		12:07:10		68		27.5		10-Dec-07		12:06:20		68		28		10-Dec-07		12:07:53		68		29		20-Jan-08		12:25:59		63.8		37

		10-Dec-07		14:07:10		68.61		28.5		10-Dec-07		14:06:20		68		29.5		10-Dec-07		14:07:53		68		30		20-Jan-08		14:25:59		65.01		39

		10-Dec-07		16:07:10		69.2		28.5		10-Dec-07		16:06:20		68.61		29		10-Dec-07		16:07:53		68		31.5		20-Jan-08		16:25:59		66.2		37.5

		10-Dec-07		18:07:10		69.2		30		10-Dec-07		18:06:20		68		31.5		10-Dec-07		18:07:53		67.4		32.5		20-Jan-08		18:25:59		66.81		37

		10-Dec-07		20:07:10		68.61		31		10-Dec-07		20:06:20		66.81		33.5		10-Dec-07		20:07:53		66.81		33.5		20-Jan-08		20:25:59		65.6		37

		10-Dec-07		22:07:10		68		32.5		10-Dec-07		22:06:20		66.2		35.5		10-Dec-07		22:07:53		65.6		35		20-Jan-08		22:25:59		65.01		37

		11-Dec-07		0:07:10		67.4		33.5		11-Dec-07		0:06:20		66.2		36.5		11-Dec-07		0:07:53		65.01		36.5		21-Jan-08		0:25:59		64.4		37

		11-Dec-07		2:07:10		66.81		32		11-Dec-07		2:06:20		66.2		34.5		11-Dec-07		2:07:53		64.4		36		21-Jan-08		2:25:59		63.8		38

		11-Dec-07		4:07:10		66.81		31.5		11-Dec-07		4:06:20		66.2		33		11-Dec-07		4:07:53		63.21		35.5		21-Jan-08		4:25:59		63.8		38.5

		11-Dec-07		6:07:10		66.81		30.5		11-Dec-07		6:06:20		66.2		32		11-Dec-07		6:07:53		67.4		31.5		21-Jan-08		6:25:59		63.21		38

		11-Dec-07		8:07:10		68.61		28.5		11-Dec-07		8:06:20		67.4		30		11-Dec-07		8:07:53		68		30.5		21-Jan-08		8:25:59		63.21		38

		11-Dec-07		10:07:10		69.2		30		11-Dec-07		10:06:20		69.8		31.5		11-Dec-07		10:07:53		69.2		31		21-Jan-08		10:25:59		63.8		38

		11-Dec-07		12:07:10		71.6		31.5		11-Dec-07		12:06:20		70.41		34		11-Dec-07		12:07:53		71.6		32.5		21-Jan-08		12:25:59		65.01		39

		11-Dec-07		14:07:10		71.6		32.5		11-Dec-07		14:06:20		70.41		34		11-Dec-07		14:07:53		71		35.5		21-Jan-08		14:25:59		65.6		36

		11-Dec-07		16:07:10		72.21		32.5		11-Dec-07		16:06:20		69.8		34.5		11-Dec-07		16:07:53		71		35		21-Jan-08		16:25:59		65.6		36

		11-Dec-07		18:07:10		72.21		31		11-Dec-07		18:06:20		69.8		31		11-Dec-07		18:07:53		71		34.5		21-Jan-08		18:25:59		65.6		35.5

		11-Dec-07		20:07:10		70.41		32.5		11-Dec-07		20:06:20		67.4		36		11-Dec-07		20:07:53		70.41		33.5		21-Jan-08		20:25:59		65.01		36

		11-Dec-07		22:07:10		69.2		27		11-Dec-07		22:06:20		66.81		26.5		11-Dec-07		22:07:53		68		31		21-Jan-08		22:25:59		63.8		36.5

		12-Dec-07		0:07:10		68.61		25		12-Dec-07		0:06:20		66.81		24		12-Dec-07		0:07:53		66.81		29		22-Jan-08		0:25:59		63.21		36

		12-Dec-07		2:07:10		68		22		12-Dec-07		2:06:20		66.81		20		12-Dec-07		2:07:53		66.2		26		22-Jan-08		2:25:59		63.21		35

		12-Dec-07		4:07:10		67.4		19.5		12-Dec-07		4:06:20		66.2		17		12-Dec-07		4:07:53		65.6		23.5		22-Jan-08		4:25:59		62.6		33.5

		12-Dec-07		6:07:10		67.4		18.5		12-Dec-07		6:06:20		66.2		16.5		12-Dec-07		6:07:53		65.01		22.5		22-Jan-08		6:25:59		64.4		32.5

		12-Dec-07		8:07:10		69.8		17.5		12-Dec-07		8:06:20		68		16		12-Dec-07		8:07:53		68		20.5		22-Jan-08		8:25:59		66.81		31

		12-Dec-07		10:07:10		71.6		19.5		12-Dec-07		10:06:20		70.41		20		12-Dec-07		10:07:53		71		22		22-Jan-08		10:25:59		69.8		31.5

		12-Dec-07		12:07:10		72.21		18.5		12-Dec-07		12:06:20		71		18		12-Dec-07		12:07:53		71		22.5		22-Jan-08		12:25:59		74.6		30.5

		12-Dec-07		14:07:10		72.21		17.5		12-Dec-07		14:06:20		71		18.5		12-Dec-07		14:07:53		71.6		23		22-Jan-08		14:25:59		72.8		34

		12-Dec-07		16:07:10		72.21		17		12-Dec-07		16:06:20		71		19		12-Dec-07		16:07:53		70.41		22		22-Jan-08		16:25:59		73.4		34.5

		12-Dec-07		18:07:10		72.21		19		12-Dec-07		18:06:20		69.2		19		12-Dec-07		18:07:53		70.41		23.5		22-Jan-08		18:25:59		73.4		33.5

		12-Dec-07		20:07:10		70.41		22		12-Dec-07		20:06:20		67.4		24		12-Dec-07		20:07:53		69.8		24		22-Jan-08		20:25:59		72.21		34

		12-Dec-07		22:07:10		69.2		22.5		12-Dec-07		22:06:20		66.81		26		12-Dec-07		22:07:53		68.61		25		22-Jan-08		22:25:59		67.4		36

		13-Dec-07		0:07:10		68.61		23		13-Dec-07		0:06:20		66.2		26		13-Dec-07		0:07:53		66.81		25.5		23-Jan-08		0:25:59		65.6		37.5

		13-Dec-07		2:07:10		67.4		23		13-Dec-07		2:06:20		66.2		26		13-Dec-07		2:07:53		65.01		26.5		23-Jan-08		2:25:59		64.4		38

		13-Dec-07		4:07:10		66.81		23.5		13-Dec-07		4:06:20		66.2		25.5		13-Dec-07		4:07:53		63.8		27.5		23-Jan-08		4:25:59		63.8		38

		13-Dec-07		6:07:10		67.4		24.5		13-Dec-07		6:06:20		66.2		27		13-Dec-07		6:07:53		67.4		25.5		23-Jan-08		6:25:59		66.2		37.5

		13-Dec-07		8:07:10		70.41		24.5		13-Dec-07		8:06:20		68		27		13-Dec-07		8:07:53		68.61		26.5		23-Jan-08		8:25:59		68.61		34.5

		13-Dec-07		10:07:10		71.6		25		13-Dec-07		10:06:20		70.41		27.5		13-Dec-07		10:07:53		70.41		27.5		23-Jan-08		10:25:59		72.21		33

		13-Dec-07		12:07:10		72.21		26.5		13-Dec-07		12:06:20		71		28.5		13-Dec-07		12:07:53		70.41		30		23-Jan-08		12:25:59		74.01		31.5

		13-Dec-07		14:07:10		72.21		25.5		13-Dec-07		14:06:20		71		27		13-Dec-07		14:07:53		70.41		30.5		23-Jan-08		14:25:59		72.8		31.5

		13-Dec-07		16:07:10		72.21		22.5		13-Dec-07		16:06:20		71		23.5		13-Dec-07		16:07:53		70.41		28		23-Jan-08		16:25:59		72.21		31.5

		13-Dec-07		18:07:10		72.8		23.5		13-Dec-07		18:06:20		69.8		24		13-Dec-07		18:07:53		69.8		27.5		23-Jan-08		18:25:59		72.8		30.5

		13-Dec-07		20:07:10		70.41		25.5		13-Dec-07		20:06:20		67.4		28.5		13-Dec-07		20:07:53		69.2		28		23-Jan-08		20:25:59		72.8		30

		13-Dec-07		22:07:10		69.2		25.5		13-Dec-07		22:06:20		66.81		29		13-Dec-07		22:07:53		68		28.5		23-Jan-08		22:25:59		68		32

		14-Dec-07		0:07:10		68		26		14-Dec-07		0:06:20		66.2		29		14-Dec-07		0:07:53		66.2		29		24-Jan-08		0:25:59		65.6		33

		14-Dec-07		2:07:10		67.4		26.5		14-Dec-07		2:06:20		66.2		29		14-Dec-07		2:07:53		64.4		30		24-Jan-08		2:25:59		64.4		34

		14-Dec-07		4:07:10		66.81		26		14-Dec-07		4:06:20		66.2		28.5		14-Dec-07		4:07:53		63.21		30.5		24-Jan-08		4:25:59		63.8		35

		14-Dec-07		6:07:10		66.81		25.5		14-Dec-07		6:06:20		66.2		27		14-Dec-07		6:07:53		66.2		27		24-Jan-08		6:25:59		65.6		36

		14-Dec-07		8:07:10		69.2		24		14-Dec-07		8:06:20		67.4		26		14-Dec-07		8:07:53		68.61		26.5		24-Jan-08		8:25:59		68		34.5

		14-Dec-07		10:07:10		69.8		26		14-Dec-07		10:06:20		69.8		28		14-Dec-07		10:07:53		69.8		27.5		24-Jan-08		10:25:59		71.6		34.5

		14-Dec-07		12:07:10		71		28		14-Dec-07		12:06:20		70.41		30.5		14-Dec-07		12:07:53		71.6		28.5		24-Jan-08		12:25:59		74.01		33.5

		14-Dec-07		14:07:10		71.6		28		14-Dec-07		14:06:20		71		29.5		14-Dec-07		14:07:53		71		28.5		24-Jan-08		14:25:59		71.6		35

		14-Dec-07		16:07:10		72.21		29		14-Dec-07		16:06:20		71.6		30		14-Dec-07		16:07:53		69.8		32		24-Jan-08		16:25:59		72.21		34.5

		14-Dec-07		18:07:10		73.4		30		14-Dec-07		18:06:20		69.8		33		14-Dec-07		18:07:53		70.41		33.5		24-Jan-08		18:25:59		72.21		33.5

		14-Dec-07		20:07:10		71		30.5		14-Dec-07		20:06:20		69.2		33		14-Dec-07		20:07:53		69.2		32		24-Jan-08		20:25:59		72.21		33.5

		14-Dec-07		22:07:10		69.2		29.5		14-Dec-07		22:06:20		66.81		32.5		14-Dec-07		22:07:53		68		31.5		24-Jan-08		22:25:59		68		36

		15-Dec-07		0:07:10		68		29		15-Dec-07		0:06:20		66.2		32		15-Dec-07		0:07:53		65.6		32		25-Jan-08		0:25:59		65.6		36.5

		15-Dec-07		2:07:10		67.4		28		15-Dec-07		2:06:20		66.2		30.5		15-Dec-07		2:07:53		63.8		32		25-Jan-08		2:25:59		65.01		37.5

		15-Dec-07		4:07:10		66.81		27		15-Dec-07		4:06:20		65.6		29		15-Dec-07		4:07:53		63.21		31.5		25-Jan-08		4:25:59		64.4		38.5

		15-Dec-07		6:07:10		66.81		27		15-Dec-07		6:06:20		66.2		28.5		15-Dec-07		6:07:53		67.4		27.5		25-Jan-08		6:25:59		66.2		38

		15-Dec-07		8:07:10		68.61		25		15-Dec-07		8:06:20		67.4		26		15-Dec-07		8:07:53		68.61		27		25-Jan-08		8:25:59		69.2		36

		15-Dec-07		10:07:10		70.41		27		15-Dec-07		10:06:20		69.8		28.5		15-Dec-07		10:07:53		70.41		28.5		25-Jan-08		10:25:59		72.8		36

		15-Dec-07		12:07:10		71.6		29.5		15-Dec-07		12:06:20		71		29.5		15-Dec-07		12:07:53		71.6		30		25-Jan-08		12:25:59		74.01		34.5

		15-Dec-07		14:07:10		71.6		30.5		15-Dec-07		14:06:20		71		31.5		15-Dec-07		14:07:53		70.41		30		25-Jan-08		14:25:59		73.4		35

		15-Dec-07		16:07:10		71.6		30.5		15-Dec-07		16:06:20		71		31.5		15-Dec-07		16:07:53		71		32.5		25-Jan-08		16:25:59		74.01		35.5

		15-Dec-07		18:07:10		72.8		33		15-Dec-07		18:06:20		69.8		37		15-Dec-07		18:07:53		70.41		35.5		25-Jan-08		18:25:59		72.8		35

		15-Dec-07		20:07:10		71		34.5		15-Dec-07		20:06:20		67.4		39		15-Dec-07		20:07:53		69.2		35.5		25-Jan-08		20:25:59		72.21		34

		15-Dec-07		22:07:10		69.2		33.5		15-Dec-07		22:06:20		66.81		37.5		15-Dec-07		22:07:53		67.4		35.5		25-Jan-08		22:25:59		69.2		36

		16-Dec-07		0:07:10		68.61		34		16-Dec-07		0:06:20		66.2		38		16-Dec-07		0:07:53		66.2		36.5		26-Jan-08		0:25:59		67.4		36.5

		16-Dec-07		2:07:10		68		34		16-Dec-07		2:06:20		66.2		38		16-Dec-07		2:07:53		65.6		37.5		26-Jan-08		2:25:59		66.2		37

		16-Dec-07		4:07:10		68		35		16-Dec-07		4:06:20		66.2		39		16-Dec-07		4:07:53		65.01		38.5		26-Jan-08		4:25:59		65.6		37

		16-Dec-07		6:07:10		67.4		35		16-Dec-07		6:06:20		66.2		38		16-Dec-07		6:07:53		64.4		39		26-Jan-08		6:25:59		66.81		37

		16-Dec-07		8:07:10		68		34		16-Dec-07		8:06:20		67.4		36.5		16-Dec-07		8:07:53		66.81		37		26-Jan-08		8:25:59		70.41		37

		16-Dec-07		10:07:10		68		34.5		16-Dec-07		10:06:20		67.4		36.5		16-Dec-07		10:07:53		66.81		36		26-Jan-08		10:25:59		73.4		38

		16-Dec-07		12:07:10		68		35		16-Dec-07		12:06:20		68		37		16-Dec-07		12:07:53		67.4		36.5		26-Jan-08		12:25:59		72.8		39

		16-Dec-07		14:07:10		68.61		37		16-Dec-07		14:06:20		68		39.5		16-Dec-07		14:07:53		66.81		39		26-Jan-08		14:25:59		73.4		39.5

		16-Dec-07		16:07:10		69.2		39		16-Dec-07		16:06:20		68		42.5		16-Dec-07		16:07:53		67.4		41.5		26-Jan-08		16:25:59		73.4		39.5

		16-Dec-07		18:07:10		69.2		40.5		16-Dec-07		18:06:20		68		44		16-Dec-07		18:07:53		68		42.5		26-Jan-08		18:25:59		73.4		40

		16-Dec-07		20:07:10		68.61		40.5		16-Dec-07		20:06:20		66.81		44		16-Dec-07		20:07:53		67.4		42		26-Jan-08		20:25:59		72.8		41

		16-Dec-07		22:07:10		68		40.5		16-Dec-07		22:06:20		66.81		44		16-Dec-07		22:07:53		66.2		43		26-Jan-08		22:25:59		69.8		43

		17-Dec-07		0:07:10		68		41		17-Dec-07		0:06:20		66.2		44.5		17-Dec-07		0:07:53		66.2		43.5		27-Jan-08		0:25:59		68		44

		17-Dec-07		2:07:10		67.4		41		17-Dec-07		2:06:20		66.2		44.5		17-Dec-07		2:07:53		65.6		44		27-Jan-08		2:25:59		67.4		45.5

		17-Dec-07		4:07:10		67.4		40.5		17-Dec-07		4:06:20		66.2		44.5		17-Dec-07		4:07:53		65.01		44		27-Jan-08		4:25:59		66.81		46.5

		17-Dec-07		6:07:10		66.81		40.5		17-Dec-07		6:06:20		66.2		43.5		17-Dec-07		6:07:53		65.01		43.5		27-Jan-08		6:25:59		66.2		47

		17-Dec-07		8:07:10		68		40		17-Dec-07		8:06:20		67.4		42.5		17-Dec-07		8:07:53		66.81		41.5		27-Jan-08		8:25:59		66.2		46.5

		17-Dec-07		10:07:10		68		40.5		17-Dec-07		10:06:20		67.4		43		17-Dec-07		10:07:53		67.4		42		27-Jan-08		10:25:59		66.2		45.5

		17-Dec-07		12:07:10		68		40.5		17-Dec-07		12:06:20		67.4		42.5		17-Dec-07		12:07:53		67.4		42.5		27-Jan-08		12:25:59		66.81		45

		17-Dec-07		14:07:10		68.61		37		17-Dec-07		14:06:20		68		37		17-Dec-07		14:07:53		67.4		40		27-Jan-08		14:25:59		67.4		46

		17-Dec-07		16:07:10		68.61		37.5		17-Dec-07		16:06:20		67.4		39.5		17-Dec-07		16:07:53		67.4		40.5		27-Jan-08		16:25:59		68		45.5

		17-Dec-07		18:07:10		68.61		38		17-Dec-07		18:06:20		68		39.5		17-Dec-07		18:07:53		67.4		40		27-Jan-08		18:25:59		67.4		44.5

		17-Dec-07		20:07:10		68		40		17-Dec-07		20:06:20		66.81		43.5		17-Dec-07		20:07:53		66.81		42		27-Jan-08		20:25:59		66.81		44

		17-Dec-07		22:07:10		68		42.5		17-Dec-07		22:06:20		66.2		47		17-Dec-07		22:07:53		65.6		45		27-Jan-08		22:25:59		66.2		44

		18-Dec-07		0:07:10		67.4		43.5		18-Dec-07		0:06:20		66.2		48.5		18-Dec-07		0:07:53		65.6		46.5		28-Jan-08		0:25:59		66.2		44.5

		18-Dec-07		2:07:10		67.4		43.5		18-Dec-07		2:06:20		66.81		46.5		18-Dec-07		2:07:53		65.6		46.5		28-Jan-08		2:25:59		66.2		46

		18-Dec-07		4:07:10		67.4		42		18-Dec-07		4:06:20		66.2		44.5		18-Dec-07		4:07:53		65.01		45.5		28-Jan-08		4:25:59		65.6		46.5

		18-Dec-07		6:07:10		67.4		43		18-Dec-07		6:06:20		66.2		46		18-Dec-07		6:07:53		66.81		43.5		28-Jan-08		6:25:59		65.6		47

		18-Dec-07		8:07:10		69.8		41		18-Dec-07		8:06:20		68		44.5		18-Dec-07		8:07:53		69.2		43		28-Jan-08		8:25:59		65.6		47.5

		18-Dec-07		10:07:10		71		42		18-Dec-07		10:06:20		71		39		18-Dec-07		10:07:53		71.6		41.5		28-Jan-08		10:25:59		66.81		47.5

		18-Dec-07		12:07:10		71.6		41		18-Dec-07		12:06:20		71.6		43.5		18-Dec-07		12:07:53		71.6		43.5		28-Jan-08		12:25:59		68		47

		18-Dec-07		14:07:10		71.6		41		18-Dec-07		14:06:20		71		45		18-Dec-07		14:07:53		71		45.5		28-Jan-08		14:25:59		68.61		46.5

		18-Dec-07		16:07:10		72.21		44		18-Dec-07		16:06:20		71		39.5		18-Dec-07		16:07:53		71		46		28-Jan-08		16:25:59		68.61		46.5

		18-Dec-07		18:07:10		72.21		42		18-Dec-07		18:06:20		69.2		45		18-Dec-07		18:07:53		71.6		40.5		28-Jan-08		18:25:59		69.2		46.5

		18-Dec-07		20:07:10		71		41.5		18-Dec-07		20:06:20		68		45		18-Dec-07		20:07:53		70.41		42.5		28-Jan-08		20:25:59		67.4		47.5

		18-Dec-07		22:07:10		69.8		43		18-Dec-07		22:06:20		66.81		48.5		18-Dec-07		22:07:53		68.61		44.5		28-Jan-08		22:25:59		66.2		46

		19-Dec-07		0:07:10		69.2		44		19-Dec-07		0:06:20		66.81		48.5		19-Dec-07		0:07:53		68		45.5		29-Jan-08		0:25:59		65.01		42.5

		19-Dec-07		2:07:10		68.61		44.5		19-Dec-07		2:06:20		66.81		49		19-Dec-07		2:07:53		67.4		46.5		29-Jan-08		2:25:59		64.4		41

		19-Dec-07		4:07:10		68.61		44.5		19-Dec-07		4:06:20		66.81		48.5		19-Dec-07		4:07:53		66.81		47.5		29-Jan-08		4:25:59		64.4		40.5

		19-Dec-07		6:07:10		68		45		19-Dec-07		6:06:20		66.81		48.5		19-Dec-07		6:07:53		68		46		29-Jan-08		6:25:59		66.2		39

		19-Dec-07		8:07:10		70.41		43		19-Dec-07		8:06:20		68.61		46		19-Dec-07		8:07:53		69.8		44.5		29-Jan-08		8:25:59		68.61		37

		19-Dec-07		10:07:10		71.6		42		19-Dec-07		10:06:20		71		48.5		19-Dec-07		10:07:53		71		43.5		29-Jan-08		10:25:59		73.4		35.5

		19-Dec-07		12:07:10		72.21		44		19-Dec-07		12:06:20		71.6		49.5		19-Dec-07		12:07:53		70.41		50		29-Jan-08		12:25:59		71		37

		19-Dec-07		14:07:10		72.21		45.5		19-Dec-07		14:06:20		71		53.5		19-Dec-07		14:07:53		69.8		49.5		29-Jan-08		14:25:59		71.6		36

		19-Dec-07		16:07:10		72.8		45.5		19-Dec-07		16:06:20		71		47		19-Dec-07		16:07:53		70.41		47		29-Jan-08		16:25:59		72.8		35.5

		19-Dec-07		18:07:10		72.21		41.5		19-Dec-07		18:06:20		69.2		44		19-Dec-07		18:07:53		69.8		44.5		29-Jan-08		18:25:59		72.21		35.5

		19-Dec-07		20:07:10		71		41		19-Dec-07		20:06:20		67.4		44.5		19-Dec-07		20:07:53		69.2		43		29-Jan-08		20:25:59		72.21		33.5

		19-Dec-07		22:07:10		69.8		39		19-Dec-07		22:06:20		66.81		42		19-Dec-07		22:07:53		68		42		29-Jan-08		22:25:59		68		36

		20-Dec-07		0:07:10		68.61		38.5		20-Dec-07		0:06:20		66.2		42		20-Dec-07		0:07:53		66.2		42		30-Jan-08		0:25:59		66.2		36

		20-Dec-07		2:07:10		68.61		39		20-Dec-07		2:06:20		66.2		43		20-Dec-07		2:07:53		65.6		43		30-Jan-08		2:25:59		65.01		36

		20-Dec-07		4:07:10		68		40		20-Dec-07		4:06:20		66.2		43.5		20-Dec-07		4:07:53		65.01		44		30-Jan-08		4:25:59		63.8		35

		20-Dec-07		6:07:10		68		40		20-Dec-07		6:06:20		66.2		43.5		20-Dec-07		6:07:53		67.4		41.5		30-Jan-08		6:25:59		66.2		34

		20-Dec-07		8:07:10		70.41		39		20-Dec-07		8:06:20		68		42.5		20-Dec-07		8:07:53		69.8		41		30-Jan-08		8:25:59		69.2		33

		20-Dec-07		10:07:10		72.21		39		20-Dec-07		10:06:20		70.41		42		20-Dec-07		10:07:53		71.6		39.5		30-Jan-08		10:25:59		72.8		33.5

		20-Dec-07		12:07:10		72.21		41		20-Dec-07		12:06:20		71		45.5		20-Dec-07		12:07:53		71.6		43		30-Jan-08		12:25:59		73.4		34

		20-Dec-07		14:07:10		72.8		39.5		20-Dec-07		14:06:20		70.41		47.5		20-Dec-07		14:07:53		71.6		42		30-Jan-08		14:25:59		72.8		37.5

		20-Dec-07		16:07:10		72.21		43		20-Dec-07		16:06:20		70.41		43		20-Dec-07		16:07:53		70.41		46		30-Jan-08		16:25:59		72.8		39.5

		20-Dec-07		18:07:10		72.8		41.5		20-Dec-07		18:06:20		69.2		45.5		20-Dec-07		18:07:53		70.41		44.5		30-Jan-08		18:25:59		72.21		37.5

		20-Dec-07		20:07:10		71.6		42.5		20-Dec-07		20:06:20		68.61		47.5		20-Dec-07		20:07:53		69.8		45		30-Jan-08		20:25:59		72.21		34.5

		20-Dec-07		22:07:10		70.41		44.5		20-Dec-07		22:06:20		68		49.5		20-Dec-07		22:07:53		69.2		46.5		30-Jan-08		22:25:59		69.2		36

		21-Dec-07		0:07:10		69.8		46		21-Dec-07		0:06:20		67.4		51.5		21-Dec-07		0:07:53		68		47.5		31-Jan-08		0:25:59		67.4		36.5

		21-Dec-07		2:07:10		69.2		46		21-Dec-07		2:06:20		67.4		51		21-Dec-07		2:07:53		68		49		31-Jan-08		2:25:59		66.2		36.5

		21-Dec-07		4:07:10		69.2		46.5		21-Dec-07		4:06:20		66.81		51.5		21-Dec-07		4:07:53		67.4		49		31-Jan-08		4:25:59		65.6		37

		21-Dec-07		6:07:10		68.61		44.5		21-Dec-07		6:06:20		66.81		47		21-Dec-07		6:07:53		67.4		47		31-Jan-08		6:25:59		66.81		36

		21-Dec-07		8:07:10		71		38.5		21-Dec-07		8:06:20		68		39		21-Dec-07		8:07:53		69.8		42		31-Jan-08		8:25:59		70.41		34.5

		21-Dec-07		10:07:10		71.6		38.5		21-Dec-07		10:06:20		69.8		38		21-Dec-07		10:07:53		71.6		39.5		31-Jan-08		10:25:59		74.01		34

		21-Dec-07		12:07:10		72.21		37		21-Dec-07		12:06:20		69.8		38.5		21-Dec-07		12:07:53		71		40		31-Jan-08		12:25:59		71		36

		21-Dec-07		14:07:10		72.21		35.5		21-Dec-07		14:06:20		70.41		35		21-Dec-07		14:07:53		71		40.5		31-Jan-08		14:25:59		72.21		35.5

		21-Dec-07		16:07:10		72.21		33		21-Dec-07		16:06:20		70.41		32.5		21-Dec-07		16:07:53		71		35.5		31-Jan-08		16:25:59		72.21		35

		21-Dec-07		18:07:10		71.6		31.5		21-Dec-07		18:06:20		69.2		30.5		21-Dec-07		18:07:53		70.41		34		31-Jan-08		18:25:59		72.21		35.5

		21-Dec-07		20:07:10		69.8		32		21-Dec-07		20:06:20		67.4		34		21-Dec-07		20:07:53		69.2		33.5		31-Jan-08		20:25:59		72.21		35.5

		21-Dec-07		22:07:10		69.2		32		21-Dec-07		22:06:20		66.81		34		21-Dec-07		22:07:53		67.4		34.5		31-Jan-08		22:25:59		69.2		38

		22-Dec-07		0:07:10		68.61		31.5		22-Dec-07		0:06:20		66.2		33.5		22-Dec-07		0:07:53		65.6		35		1-Feb-08		0:25:59		67.4		38.5

		22-Dec-07		2:07:10		68		31		22-Dec-07		2:06:20		66.2		33		22-Dec-07		2:07:53		64.4		35		1-Feb-08		2:25:59		66.2		39

		22-Dec-07		4:07:10		67.4		30		22-Dec-07		4:06:20		66.2		31.5		22-Dec-07		4:07:53		63.21		35		1-Feb-08		4:25:59		65.6		40

		22-Dec-07		6:07:10		67.4		29.5		22-Dec-07		6:06:20		66.2		30.5		22-Dec-07		6:07:53		66.2		31.5		1-Feb-08		6:25:59		66.81		40

		22-Dec-07		8:07:10		69.2		28		22-Dec-07		8:06:20		69.2		29		22-Dec-07		8:07:53		68.61		31.5		1-Feb-08		8:25:59		70.41		39

		22-Dec-07		10:07:10		71		28		22-Dec-07		10:06:20		70.41		30		22-Dec-07		10:07:53		70.41		31		1-Feb-08		10:25:59		73.4		40

		22-Dec-07		12:07:10		71		28.5		22-Dec-07		12:06:20		70.41		29.5		22-Dec-07		12:07:53		71.6		28.5		1-Feb-08		12:25:59		72.21		41

		22-Dec-07		14:07:10		71		26.5		22-Dec-07		14:06:20		69.2		26		22-Dec-07		14:07:53		69.8		30		1-Feb-08		14:25:59		72.8		42.5

		22-Dec-07		16:07:10		71		26.5		22-Dec-07		16:06:20		69.2		26		22-Dec-07		16:07:53		69.2		29.5		1-Feb-08		16:25:59		72.8		44

		22-Dec-07		18:07:10		70.41		26.5		22-Dec-07		18:06:20		69.2		26		22-Dec-07		18:07:53		69.2		29.5		1-Feb-08		18:25:59		72.21		45.5

		22-Dec-07		20:07:10		69.8		28		22-Dec-07		20:06:20		66.81		31		22-Dec-07		20:07:53		68		31.5		1-Feb-08		20:25:59		72.8		41

		22-Dec-07		22:07:10		68.61		28.5		22-Dec-07		22:06:20		66.2		31		22-Dec-07		22:07:53		66.2		31.5		1-Feb-08		22:25:59		69.8		42

		23-Dec-07		0:07:10		68		28		23-Dec-07		0:06:20		65.6		31		23-Dec-07		0:07:53		64.4		31.5		2-Feb-08		0:25:59		67.4		41.5

		23-Dec-07		2:07:10		66.81		27.5		23-Dec-07		2:06:20		65.6		30		23-Dec-07		2:07:53		63.21		32		2-Feb-08		2:25:59		65.6		40.5

		23-Dec-07		4:07:10		66.81		27		23-Dec-07		4:06:20		65.6		29.5		23-Dec-07		4:07:53		62		31.5		2-Feb-08		4:25:59		64.4		39.5

		23-Dec-07		6:07:10		66.2		26.5		23-Dec-07		6:06:20		65.6		28		23-Dec-07		6:07:53		61.41		31.5		2-Feb-08		6:25:59		65.6		37

		23-Dec-07		8:07:10		66.81		26.5		23-Dec-07		8:06:20		66.81		28		23-Dec-07		8:07:53		67.4		28		2-Feb-08		8:25:59		68		34.5

		23-Dec-07		10:07:10		67.4		28		23-Dec-07		10:06:20		67.4		29.5		23-Dec-07		10:07:53		68		28		2-Feb-08		10:25:59		71		38.5

		23-Dec-07		12:07:10		67.4		30		23-Dec-07		12:06:20		67.4		31.5		23-Dec-07		12:07:53		68		30.5		2-Feb-08		12:25:59		71.6		37

		23-Dec-07		14:07:10		68		29.5		23-Dec-07		14:06:20		67.4		30.5		23-Dec-07		14:07:53		68		31		2-Feb-08		14:25:59		71.6		39

		23-Dec-07		16:07:10		68		29.5		23-Dec-07		16:06:20		68		30.5		23-Dec-07		16:07:53		68		31.5		2-Feb-08		16:25:59		71.6		39

		23-Dec-07		18:07:10		68.61		29.5		23-Dec-07		18:06:20		67.4		30		23-Dec-07		18:07:53		68		31.5		2-Feb-08		18:25:59		71.6		39

		23-Dec-07		20:07:10		68		31.5		23-Dec-07		20:06:20		66.2		34		23-Dec-07		20:07:53		68.61		31.5		2-Feb-08		20:25:59		71.6		38.5

		23-Dec-07		22:07:10		67.4		32		23-Dec-07		22:06:20		66.2		34.5		23-Dec-07		22:07:53		68.61		32		2-Feb-08		22:25:59		68.61		39.5

		24-Dec-07		0:07:10		66.81		32		24-Dec-07		0:06:20		65.6		34.5		24-Dec-07		0:07:53		68.61		31.5		3-Feb-08		0:25:59		66.81		40.5

		24-Dec-07		2:07:10		66.81		31.5		24-Dec-07		2:06:20		66.2		33.5		24-Dec-07		2:07:53		68.61		31.5		3-Feb-08		2:25:59		66.2		41

		24-Dec-07		4:07:10		66.81		31.5		24-Dec-07		4:06:20		65.6		34		24-Dec-07		4:07:53		68.61		31.5		3-Feb-08		4:25:59		65.6		42

		24-Dec-07		6:07:10		66.81		31.5		24-Dec-07		6:06:20		65.6		33		24-Dec-07		6:07:53		68		31		3-Feb-08		6:25:59		65.01		42.5

		24-Dec-07		8:07:10		67.4		31		24-Dec-07		8:06:20		67.4		32		24-Dec-07		8:07:53		69.2		30.5		3-Feb-08		8:25:59		65.01		43

		24-Dec-07		10:07:10		67.4		32		24-Dec-07		10:06:20		67.4		33.5		24-Dec-07		10:07:53		69.2		31		3-Feb-08		10:25:59		66.2		43

		24-Dec-07		12:07:10		68		32.5		24-Dec-07		12:06:20		67.4		33.5		24-Dec-07		12:07:53		68.61		32		3-Feb-08		12:25:59		66.81		45

		24-Dec-07		14:07:10		68.61		36		24-Dec-07		14:06:20		68		38.5		24-Dec-07		14:07:53		69.2		35.5		3-Feb-08		14:25:59		67.4		46

		24-Dec-07		16:07:10		69.2		40		24-Dec-07		16:06:20		68.61		44		24-Dec-07		16:07:53		69.8		39.5		3-Feb-08		16:25:59		67.4		48.5

		24-Dec-07		18:07:10		69.8		43		24-Dec-07		18:06:20		68.61		48		24-Dec-07		18:07:53		69.8		43		3-Feb-08		18:25:59		66.81		50.5

		24-Dec-07		20:07:10		68.61		43		24-Dec-07		20:06:20		66.81		47.5		24-Dec-07		20:07:53		69.2		42.5		3-Feb-08		20:25:59		66.81		50

		24-Dec-07		22:07:10		68		41.5		24-Dec-07		22:06:20		66.2		46		24-Dec-07		22:07:53		69.8		40.5		3-Feb-08		22:25:59		66.2		51.5

		25-Dec-07		0:07:10		68		41.5		25-Dec-07		0:06:20		66.2		45		25-Dec-07		0:07:53		69.8		40		4-Feb-08		0:25:59		66.2		52.5

		25-Dec-07		2:07:10		67.4		40.5		25-Dec-07		2:06:20		66.2		44.5		25-Dec-07		2:07:53		69.8		39		4-Feb-08		2:25:59		66.2		51.5

		25-Dec-07		4:07:10		67.4		40.5		25-Dec-07		4:06:20		66.2		43.5		25-Dec-07		4:07:53		69.8		38		4-Feb-08		4:25:59		65.6		49.5

		25-Dec-07		6:07:10		67.4		39.5		25-Dec-07		6:06:20		66.2		42		25-Dec-07		6:07:53		69.8		37		4-Feb-08		6:25:59		65.6		48.5

		25-Dec-07		8:07:10		69.2		37.5		25-Dec-07		8:06:20		67.4		40		25-Dec-07		8:07:53		69.2		38		4-Feb-08		8:25:59		65.6		47

		25-Dec-07		10:07:10		69.8		33.5		25-Dec-07		10:06:20		68		34.5		25-Dec-07		10:07:53		68.61		35		4-Feb-08		10:25:59		66.2		46

		25-Dec-07		12:07:10		71		31.5		25-Dec-07		12:06:20		69.2		31		25-Dec-07		12:07:53		69.2		33.5		4-Feb-08		12:25:59		66.81		46.5

		25-Dec-07		14:07:10		70.41		30		25-Dec-07		14:06:20		69.2		28		25-Dec-07		14:07:53		69.8		31.5		4-Feb-08		14:25:59		67.4		46

		25-Dec-07		16:07:10		70.41		27.5		25-Dec-07		16:06:20		68.61		26		25-Dec-07		16:07:53		70.41		30.5		4-Feb-08		16:25:59		67.4		45.5

		25-Dec-07		18:07:10		70.41		29.5		25-Dec-07		18:06:20		68.61		29		25-Dec-07		18:07:53		70.41		30.5		4-Feb-08		18:25:59		67.4		45

		25-Dec-07		20:07:10		69.2		32		25-Dec-07		20:06:20		66.81		34.5		25-Dec-07		20:07:53		69.2		33		4-Feb-08		20:25:59		66.2		45

		25-Dec-07		22:07:10		68		30		25-Dec-07		22:06:20		66.2		31.5		25-Dec-07		22:07:53		67.4		32		4-Feb-08		22:25:59		65.6		45

		26-Dec-07		0:07:10		67.4		29.5		26-Dec-07		0:06:20		65.6		31		26-Dec-07		0:07:53		65.6		31.5		5-Feb-08		0:25:59		65.6		44.5

		26-Dec-07		2:07:10		66.81		28.5		26-Dec-07		2:06:20		65.6		30		26-Dec-07		2:07:53		64.4		31.5		5-Feb-08		2:25:59		65.01		44.5

		26-Dec-07		4:07:10		66.2		28		26-Dec-07		4:06:20		65.6		29.5		26-Dec-07		4:07:53		62.6		31		5-Feb-08		4:25:59		65.01		44

		26-Dec-07		6:07:10		66.2		27.5		26-Dec-07		6:06:20		65.6		29		26-Dec-07		6:07:53		66.81		28.5		5-Feb-08		6:25:59		66.2		42.5

		26-Dec-07		8:07:10		66.81		26.5		26-Dec-07		8:06:20		66.81		27		26-Dec-07		8:07:53		68		27.5		5-Feb-08		8:25:59		69.8		39.5

		26-Dec-07		10:07:10		67.4		26.5		26-Dec-07		10:06:20		67.4		27.5		26-Dec-07		10:07:53		68.61		27.5		5-Feb-08		10:25:59		72.8		37.5

		26-Dec-07		12:07:10		67.4		27.5		26-Dec-07		12:06:20		67.4		28		26-Dec-07		12:07:53		68.61		28.5		5-Feb-08		12:25:59		71.6		37.5

		26-Dec-07		14:07:10		68		28		26-Dec-07		14:06:20		68		28		26-Dec-07		14:07:53		68.61		29.5		5-Feb-08		14:25:59		71.6		36

		26-Dec-07		16:07:10		68.61		29.5		26-Dec-07		16:06:20		68		30.5		26-Dec-07		16:07:53		68.61		31		5-Feb-08		16:25:59		72.8		34.5

		26-Dec-07		18:07:10		68.61		32.5		26-Dec-07		18:06:20		68		35		26-Dec-07		18:07:53		68.61		34		5-Feb-08		18:25:59		72.8		34.5

		26-Dec-07		20:07:10		68		33.5		26-Dec-07		20:06:20		66.81		36		26-Dec-07		20:07:53		69.2		34		5-Feb-08		20:25:59		72.21		34

		26-Dec-07		22:07:10		67.4		34		26-Dec-07		22:06:20		66.2		36.5		26-Dec-07		22:07:53		67.4		34.5		5-Feb-08		22:25:59		69.2		36

		27-Dec-07		0:07:10		66.81		34.5		27-Dec-07		0:06:20		66.2		38		27-Dec-07		0:07:53		66.2		36		6-Feb-08		0:25:59		67.4		37

		27-Dec-07		2:07:10		66.81		34		27-Dec-07		2:06:20		66.2		36		27-Dec-07		2:07:53		65.01		36		6-Feb-08		2:25:59		66.2		38

		27-Dec-07		4:07:10		66.2		32.5		27-Dec-07		4:06:20		65.6		34		27-Dec-07		4:07:53		63.8		35		6-Feb-08		4:25:59		65.6		38

		27-Dec-07		6:07:10		66.2		31.5		27-Dec-07		6:06:20		65.6		32.5		27-Dec-07		6:07:53		68		31.5		6-Feb-08		6:25:59		66.81		39.5

		27-Dec-07		8:07:10		68		30		27-Dec-07		8:06:20		67.4		31		27-Dec-07		8:07:53		70.41		30.5		6-Feb-08		8:25:59		70.41		36.5

		27-Dec-07		10:07:10		69.2		30.5		27-Dec-07		10:06:20		69.8		31.5		27-Dec-07		10:07:53		71		30.5		6-Feb-08		10:25:59		72.8		35.5

		27-Dec-07		12:07:10		71		28.5		27-Dec-07		12:06:20		70.41		28.5		27-Dec-07		12:07:53		71		29		6-Feb-08		12:25:59		71		37

		27-Dec-07		14:07:10		70.41		25.5		27-Dec-07		14:06:20		70.41		24.5		27-Dec-07		14:07:53		71		25.5		6-Feb-08		14:25:59		72.21		37

		27-Dec-07		16:07:10		71		22.5		27-Dec-07		16:06:20		71		22		27-Dec-07		16:07:53		69.8		24		6-Feb-08		16:25:59		72.8		34.5

		27-Dec-07		18:07:10		70.41		23		27-Dec-07		18:06:20		68.61		23.5		27-Dec-07		18:07:53		69.2		24.5		6-Feb-08		18:25:59		72.8		35

		27-Dec-07		20:07:10		69.8		24		27-Dec-07		20:06:20		66.81		26		27-Dec-07		20:07:53		68		26		6-Feb-08		20:25:59		72.8		37

		27-Dec-07		22:07:10		68		24		27-Dec-07		22:06:20		66.2		26		27-Dec-07		22:07:53		66.2		27		6-Feb-08		22:25:59		69.8		38

		28-Dec-07		0:07:10		67.4		24.5		28-Dec-07		0:06:20		65.6		26		28-Dec-07		0:07:53		65.01		27.5		7-Feb-08		0:25:59		68		38.5

		28-Dec-07		2:07:10		66.81		24		28-Dec-07		2:06:20		65.6		26		28-Dec-07		2:07:53		63.21		28		7-Feb-08		2:25:59		66.81		38.5

		28-Dec-07		4:07:10		66.2		24		28-Dec-07		4:06:20		65.6		25.5		28-Dec-07		4:07:53		62.6		28		7-Feb-08		4:25:59		66.2		38.5

		28-Dec-07		6:07:10		66.2		24.5		28-Dec-07		6:06:20		65.6		25.5		28-Dec-07		6:07:53		66.2		26		7-Feb-08		6:25:59		67.4		38.5

		28-Dec-07		8:07:10		68		23.5		28-Dec-07		8:06:20		67.4		24.5		28-Dec-07		8:07:53		68		25.5		7-Feb-08		8:25:59		71.6		38

		28-Dec-07		10:07:10		69.2		24		28-Dec-07		10:06:20		69.2		25.5		28-Dec-07		10:07:53		69.8		25		7-Feb-08		10:25:59		72.21		37.5

		28-Dec-07		12:07:10		70.41		25		28-Dec-07		12:06:20		70.41		26		28-Dec-07		12:07:53		71		26		7-Feb-08		12:25:59		71.6		40.5

		28-Dec-07		14:07:10		70.41		25.5		28-Dec-07		14:06:20		70.41		26		28-Dec-07		14:07:53		71		27		7-Feb-08		14:25:59		71.6		40

		28-Dec-07		16:07:10		71		26.5		28-Dec-07		16:06:20		70.41		27.5		28-Dec-07		16:07:53		71		25		7-Feb-08		16:25:59		72.8		38

		28-Dec-07		18:07:10		71		28.5		28-Dec-07		18:06:20		68.61		31.5		28-Dec-07		18:07:53		71		29.5		7-Feb-08		18:25:59		72.8		37.5

		28-Dec-07		20:07:10		71		31.5		28-Dec-07		20:06:20		66.81		37		28-Dec-07		20:07:53		69.8		32.5		7-Feb-08		20:25:59		72.21		36

		28-Dec-07		22:07:10		69.8		33		28-Dec-07		22:06:20		66.2		38.5		28-Dec-07		22:07:53		68		34.5		7-Feb-08		22:25:59		69.2		37.5

		29-Dec-07		0:07:10		68.61		34		29-Dec-07		0:06:20		66.2		39		29-Dec-07		0:07:53		66.81		36		8-Feb-08		0:25:59		67.4		38.5

		29-Dec-07		2:07:10		68		34		29-Dec-07		2:06:20		66.2		37.5		29-Dec-07		2:07:53		66.2		36.5		8-Feb-08		2:25:59		66.81		39

		29-Dec-07		4:07:10		67.4		34		29-Dec-07		4:06:20		66.2		38		29-Dec-07		4:07:53		65.01		37		8-Feb-08		4:25:59		65.6		39.5

		29-Dec-07		6:07:10		68		33.5		29-Dec-07		6:06:20		65.6		36.5		29-Dec-07		6:07:53		66.81		35.5		8-Feb-08		6:25:59		67.4		39.5

		29-Dec-07		8:07:10		69.8		32		29-Dec-07		8:06:20		68		34.5		29-Dec-07		8:07:53		68.61		35.5		8-Feb-08		8:25:59		71		37.5

		29-Dec-07		10:07:10		70.41		32		29-Dec-07		10:06:20		69.8		33		29-Dec-07		10:07:53		70.41		33.5		8-Feb-08		10:25:59		71.6		38

		29-Dec-07		12:07:10		72.21		33		29-Dec-07		12:06:20		70.41		35		29-Dec-07		12:07:53		71.6		34		8-Feb-08		12:25:59		71		39

		29-Dec-07		14:07:10		72.8		32.5		29-Dec-07		14:06:20		71		34		29-Dec-07		14:07:53		71.6		34		8-Feb-08		14:25:59		72.21		40

		29-Dec-07		16:07:10		72.8		32		29-Dec-07		16:06:20		71		35		29-Dec-07		16:07:53		70.41		34.5		8-Feb-08		16:25:59		73.4		41

		29-Dec-07		18:07:10		72.21		32		29-Dec-07		18:06:20		69.2		35		29-Dec-07		18:07:53		69.2		35.5		8-Feb-08		18:25:59		74.01		40

		29-Dec-07		20:07:10		71		33		29-Dec-07		20:06:20		67.4		37.5		29-Dec-07		20:07:53		68		36.5		8-Feb-08		20:25:59		72.21		40.5

		29-Dec-07		22:07:10		69.2		34		29-Dec-07		22:06:20		66.81		38.5		29-Dec-07		22:07:53		66.2		37.5		8-Feb-08		22:25:59		70.41		41.5

		30-Dec-07		0:07:10		68		34.5		30-Dec-07		0:06:20		66.2		38.5		30-Dec-07		0:07:53		65.01		38.5		9-Feb-08		0:25:59		69.2		41.5

		30-Dec-07		2:07:10		67.4		35.5		30-Dec-07		2:06:20		65.6		39		30-Dec-07		2:07:53		63.8		40		9-Feb-08		2:25:59		68		41

		30-Dec-07		4:07:10		67.4		36		30-Dec-07		4:06:20		66.2		39.5		30-Dec-07		4:07:53		63.8		41		9-Feb-08		4:25:59		66.2		40.5

		30-Dec-07		6:07:10		66.81		37		30-Dec-07		6:06:20		65.6		40.5		30-Dec-07		6:07:53		63.21		42		9-Feb-08		6:25:59		67.4		39.5

		30-Dec-07		8:07:10		67.4		37		30-Dec-07		8:06:20		67.4		39		30-Dec-07		8:07:53		69.2		37		9-Feb-08		8:25:59		71		36.5

		30-Dec-07		10:07:10		68		37.5		30-Dec-07		10:06:20		67.4		40		30-Dec-07		10:07:53		67.4		39.5		9-Feb-08		10:25:59		71		37.5

		30-Dec-07		12:07:10		68		39		30-Dec-07		12:06:20		67.4		41.5		30-Dec-07		12:07:53		67.4		39.5		9-Feb-08		12:25:59		70.41		39

		30-Dec-07		14:07:10		68		40		30-Dec-07		14:06:20		67.4		42.5		30-Dec-07		14:07:53		67.4		40.5		9-Feb-08		14:25:59		71.6		37.5

		30-Dec-07		16:07:10		68		41		30-Dec-07		16:06:20		67.4		43.5		30-Dec-07		16:07:53		66.81		42.5		9-Feb-08		16:25:59		72.8		34

		30-Dec-07		18:07:10		68		41.5		30-Dec-07		18:06:20		67.4		44		30-Dec-07		18:07:53		66.81		43.5		9-Feb-08		18:25:59		73.4		33.5

		30-Dec-07		20:07:10		67.4		42.5		30-Dec-07		20:06:20		66.2		46		30-Dec-07		20:07:53		67.4		43		9-Feb-08		20:25:59		71.6		37.5

		30-Dec-07		22:07:10		66.81		43		30-Dec-07		22:06:20		66.2		46.5		30-Dec-07		22:07:53		65.01		45.5		9-Feb-08		22:25:59		69.8		38.5

		31-Dec-07		0:07:10		66.81		43.5		31-Dec-07		0:06:20		66.2		46.5		31-Dec-07		0:07:53		64.4		47		10-Feb-08		0:25:59		68		39

		31-Dec-07		2:07:10		66.81		44		31-Dec-07		2:06:20		66.2		47		31-Dec-07		2:07:53		63.8		48		10-Feb-08		2:25:59		66.2		39

		31-Dec-07		4:07:10		66.81		44		31-Dec-07		4:06:20		66.2		47		31-Dec-07		4:07:53		63.21		49		10-Feb-08		4:25:59		65.6		39.5

		31-Dec-07		6:07:10		66.81		42.5		31-Dec-07		6:06:20		65.6		44		31-Dec-07		6:07:53		63.21		48		10-Feb-08		6:25:59		64.4		40

		31-Dec-07		8:07:10		66.81		39.5		31-Dec-07		8:06:20		67.4		40		31-Dec-07		8:07:53		66.2		42		10-Feb-08		8:25:59		64.4		39.5

		31-Dec-07		10:07:10		67.4		38		31-Dec-07		10:06:20		67.4		38.5		31-Dec-07		10:07:53		68		38.5		10-Feb-08		10:25:59		65.01		40.5

		31-Dec-07		12:07:10		67.4		36.5		31-Dec-07		12:06:20		67.4		37		31-Dec-07		12:07:53		66.81		38		10-Feb-08		12:25:59		66.81		43

		31-Dec-07		14:07:10		68		34.5		31-Dec-07		14:06:20		68		34		31-Dec-07		14:07:53		67.4		36.5		10-Feb-08		14:25:59		68.61		44

		31-Dec-07		16:07:10		68		32		31-Dec-07		16:06:20		67.4		31.5		31-Dec-07		16:07:53		67.4		35		10-Feb-08		16:25:59		69.8		42

		31-Dec-07		18:07:10		68		30.5		31-Dec-07		18:06:20		68		30		31-Dec-07		18:07:53		67.4		33.5		10-Feb-08		18:25:59		71		42.5

		31-Dec-07		20:07:10		67.4		31		31-Dec-07		20:06:20		66.2		31.5		31-Dec-07		20:07:53		65.6		33.5		10-Feb-08		20:25:59		69.8		42.5

		31-Dec-07		22:07:10		66.81		31.5		31-Dec-07		22:06:20		65.6		33		31-Dec-07		22:07:53		63.8		35		10-Feb-08		22:25:59		68		43

		1-Jan-08		0:07:10		66.2		30.5		1-Jan-08		0:06:20		65.6		31.5		1-Jan-08		0:07:53		63.21		34.5		11-Feb-08		0:25:59		66.81		43

		1-Jan-08		2:07:10		66.2		29.5		1-Jan-08		2:06:20		65.6		30		1-Jan-08		2:07:53		62		33.5		11-Feb-08		2:25:59		65.6		43

		1-Jan-08		4:07:10		66.2		29		1-Jan-08		4:06:20		65.6		29.5		1-Jan-08		4:07:53		61.41		33.5		11-Feb-08		4:25:59		65.01		43

		1-Jan-08		6:07:10		66.2		28.5		1-Jan-08		6:06:20		65.6		29.5		1-Jan-08		6:07:53		67.4		29		11-Feb-08		6:25:59		64.4		42.5

		1-Jan-08		8:07:10		67.4		27		1-Jan-08		8:06:20		68.61		27.5		1-Jan-08		8:07:53		69.2		28.5		11-Feb-08		8:25:59		64.4		41.5

		1-Jan-08		10:07:10		68.61		27.5		1-Jan-08		10:06:20		69.2		28.5		1-Jan-08		10:07:53		69.8		29		11-Feb-08		10:25:59		65.6		41.5

		1-Jan-08		12:07:10		69.8		29		1-Jan-08		12:06:20		69.2		28.5		1-Jan-08		12:07:53		71.6		29		11-Feb-08		12:25:59		68		45

		1-Jan-08		14:07:10		71		29.5		1-Jan-08		14:06:20		70.41		30.5		1-Jan-08		14:07:53		71		31.5		11-Feb-08		14:25:59		69.2		45

		1-Jan-08		16:07:10		71.6		28.5		1-Jan-08		16:06:20		69.2		29		1-Jan-08		16:07:53		69.8		30.5		11-Feb-08		16:25:59		70.41		44.5

		1-Jan-08		18:07:10		71.6		29		1-Jan-08		18:06:20		69.2		30		1-Jan-08		18:07:53		69.8		31.5		11-Feb-08		18:25:59		71		45

		1-Jan-08		20:07:10		70.41		28.5		1-Jan-08		20:06:20		67.4		31		1-Jan-08		20:07:53		68.61		31.5		11-Feb-08		20:25:59		69.8		45

		1-Jan-08		22:07:10		68.61		28.5		1-Jan-08		22:06:20		66.81		31		1-Jan-08		22:07:53		66.2		31.5		11-Feb-08		22:25:59		68		45.5

		2-Jan-08		0:07:10		67.4		28.5		2-Jan-08		0:06:20		66.2		30.5		2-Jan-08		0:07:53		63.8		32		12-Feb-08		0:25:59		66.81		45.5

		2-Jan-08		2:07:10		66.81		29		2-Jan-08		2:06:20		65.6		31		2-Jan-08		2:07:53		62		33		12-Feb-08		2:25:59		65.6		45

		2-Jan-08		4:07:10		66.2		27.5		2-Jan-08		4:06:20		65.6		29.5		2-Jan-08		4:07:53		60.8		33		12-Feb-08		4:25:59		65.01		45

		2-Jan-08		6:07:10		66.81		27		2-Jan-08		6:06:20		65.6		29		2-Jan-08		6:07:53		66.81		28.5		12-Feb-08		6:25:59		66.2		44

		2-Jan-08		8:07:10		67.4		26		2-Jan-08		8:06:20		66.81		27.5		2-Jan-08		8:07:53		67.4		27.5		12-Feb-08		8:25:59		69.2		40.5

		2-Jan-08		10:07:10		68		26.5		2-Jan-08		10:06:20		67.4		28		2-Jan-08		10:07:53		67.4		28		12-Feb-08		10:25:59		72.8		40

		2-Jan-08		12:07:10		69.2		29.5		2-Jan-08		12:06:20		68		31.5		2-Jan-08		12:07:53		67.4		31		12-Feb-08		12:25:59		71.6		43

		2-Jan-08		14:07:10		70.41		31.5		2-Jan-08		14:06:20		68.61		33.5		2-Jan-08		14:07:53		68		33.5		12-Feb-08		14:25:59		72.8		43.5

		2-Jan-08		16:07:10		71.6		32		2-Jan-08		16:06:20		69.2		34		2-Jan-08		16:07:53		69.2		34.5		12-Feb-08		16:25:59		74.01		43.5

		2-Jan-08		18:07:10		72.21		31		2-Jan-08		18:06:20		69.2		33		2-Jan-08		18:07:53		68.61		34.5		12-Feb-08		18:25:59		74.01		44.5

		2-Jan-08		20:07:10		71.6		31		2-Jan-08		20:06:20		68		34		2-Jan-08		20:07:53		68		34.5		12-Feb-08		20:25:59		71.6		43.5

		2-Jan-08		22:07:10		69.2		31		2-Jan-08		22:06:20		66.81		35.5		2-Jan-08		22:07:53		66.81		34.5		12-Feb-08		22:25:59		70.41		44.5

		3-Jan-08		0:07:10		68		32		3-Jan-08		0:06:20		66.2		35.5		3-Jan-08		0:07:53		64.4		36		13-Feb-08		0:25:59		68.61		44.5

		3-Jan-08		2:07:10		66.81		31.5		3-Jan-08		2:06:20		66.2		34		3-Jan-08		2:07:53		63.21		36.5		13-Feb-08		2:25:59		67.4		44

		3-Jan-08		4:07:10		66.2		31.5		3-Jan-08		4:06:20		66.2		34		3-Jan-08		4:07:53		62		36.5		13-Feb-08		4:25:59		66.2		44

		3-Jan-08		6:07:10		66.81		31.5		3-Jan-08		6:06:20		65.6		34		3-Jan-08		6:07:53		66.81		33.5		13-Feb-08		6:25:59		66.81		43.5

		3-Jan-08		8:07:10		68.61		29.5		3-Jan-08		8:06:20		67.4		31.5		3-Jan-08		8:07:53		68		32.5		13-Feb-08		8:25:59		72.21		39.5

		3-Jan-08		10:07:10		69.2		30.5		3-Jan-08		10:06:20		69.8		32.5		3-Jan-08		10:07:53		69.8		32		13-Feb-08		10:25:59		71.6		40.5

		3-Jan-08		12:07:10		71.6		32		3-Jan-08		12:06:20		71		32.5		3-Jan-08		12:07:53		72.21		32.5		13-Feb-08		12:25:59		72.21		43

		3-Jan-08		14:07:10		72.8		31		3-Jan-08		14:06:20		71		30.5		3-Jan-08		14:07:53		71		35		13-Feb-08		14:25:59		74.01		43.5

		3-Jan-08		16:07:10		72.21		32.5		3-Jan-08		16:06:20		71		34.5		3-Jan-08		16:07:53		70.41		33.5		13-Feb-08		16:25:59		74.6		44.5

		3-Jan-08		18:07:10		72.21		32.5		3-Jan-08		18:06:20		69.2		35		3-Jan-08		18:07:53		70.41		35.5		13-Feb-08		18:25:59		74.01		44

		3-Jan-08		20:07:10		71.6		34		3-Jan-08		20:06:20		68		39		3-Jan-08		20:07:53		69.8		36.5		13-Feb-08		20:25:59		72.21		43.5

		3-Jan-08		22:07:10		70.41		33.5		3-Jan-08		22:06:20		66.81		37.5		3-Jan-08		22:07:53		68		36.5		13-Feb-08		22:25:59		71		43.5

		4-Jan-08		0:07:10		69.2		33		4-Jan-08		0:06:20		66.2		37		4-Jan-08		0:07:53		66.2		36.5		14-Feb-08		0:25:59		68.61		43.5

		4-Jan-08		2:07:10		68.61		34.5		4-Jan-08		2:06:20		66.2		39		4-Jan-08		2:07:53		65.01		38.5		14-Feb-08		2:25:59		67.4		43.5

		4-Jan-08		4:07:10		68		35		4-Jan-08		4:06:20		66.2		39.5		4-Jan-08		4:07:53		65.01		39.5		14-Feb-08		4:25:59		66.2		43.5

		4-Jan-08		6:07:10		68.61		36.5		4-Jan-08		6:06:20		66.2		41		4-Jan-08		6:07:53		66.81		40		14-Feb-08		6:25:59		66.81		44

		4-Jan-08		8:07:10		71		37.5		4-Jan-08		8:06:20		68.61		42		4-Jan-08		8:07:53		70.41		39.5		14-Feb-08		8:25:59		70.41		41

		4-Jan-08		10:07:10		72.21		39		4-Jan-08		10:06:20		70.41		40		4-Jan-08		10:07:53		71.6		40.5		14-Feb-08		10:25:59		71.6		37

		4-Jan-08		12:07:10		73.4		40		4-Jan-08		12:06:20		71		46.5		4-Jan-08		12:07:53		71		45.5		14-Feb-08		12:25:59		71.6		36.5

		4-Jan-08		14:07:10		72.8		42.5		4-Jan-08		14:06:20		71		47.5		4-Jan-08		14:07:53		71		45.5		14-Feb-08		14:25:59		72.8		36

		4-Jan-08		16:07:10		73.4		43.5		4-Jan-08		16:06:20		70.41		49		4-Jan-08		16:07:53		71.6		41.5		14-Feb-08		16:25:59		73.4		32

		4-Jan-08		18:07:10		72.8		42.5		4-Jan-08		18:06:20		69.8		47.5		4-Jan-08		18:07:53		71		42		14-Feb-08		18:25:59		73.4		29

		4-Jan-08		20:07:10		71.6		42.5		4-Jan-08		20:06:20		69.2		48		4-Jan-08		20:07:53		69.8		45.5		14-Feb-08		20:25:59		71.6		28

		4-Jan-08		22:07:10		71		43		4-Jan-08		22:06:20		68		49.5		4-Jan-08		22:07:53		69.2		46.5		14-Feb-08		22:25:59		70.41		31.5

		5-Jan-08		0:07:10		69.8		43.5		5-Jan-08		0:06:20		67.4		50.5		5-Jan-08		0:07:53		69.2		46.5		15-Feb-08		0:25:59		68.61		32.5

		5-Jan-08		2:07:10		69.2		44		5-Jan-08		2:06:20		67.4		51		5-Jan-08		2:07:53		68.61		47		15-Feb-08		2:25:59		67.4		33

		5-Jan-08		4:07:10		69.2		45		5-Jan-08		4:06:20		67.4		52.5		5-Jan-08		4:07:53		68.61		48		15-Feb-08		4:25:59		66.2		33.5

		5-Jan-08		6:07:10		68.61		46		5-Jan-08		6:06:20		67.4		53.5		5-Jan-08		6:07:53		68		49		15-Feb-08		6:25:59		66.81		33.5

		5-Jan-08		8:07:10		69.8		47		5-Jan-08		8:06:20		69.2		53.5		5-Jan-08		8:07:53		70.41		53		15-Feb-08		8:25:59		70.41		32

		5-Jan-08		10:07:10		71		49.5		5-Jan-08		10:06:20		70.41		56.5		5-Jan-08		10:07:53		71		49		15-Feb-08		10:25:59		71.6		30.5

		5-Jan-08		12:07:10		71		49.5		5-Jan-08		12:06:20		71		51		5-Jan-08		12:07:53		71		54.5		15-Feb-08		12:25:59		72.21		30

		5-Jan-08		14:07:10		70.41		46		5-Jan-08		14:06:20		70.41		47		5-Jan-08		14:07:53		72.21		45.5		15-Feb-08		14:25:59		72.8		30.5

		5-Jan-08		16:07:10		69.8		45.5		5-Jan-08		16:06:20		71		46		5-Jan-08		16:07:53		71		46		15-Feb-08		16:25:59		73.4		29.5

		5-Jan-08		18:07:10		73.4		41.5		5-Jan-08		18:06:20		74.01		42		5-Jan-08		18:07:53		74.01		42.5		15-Feb-08		18:25:59		74.01		30

		5-Jan-08		20:07:10		69.2		42.5		5-Jan-08		20:06:20		68		44.5		5-Jan-08		20:07:53		69.2		43.5		15-Feb-08		20:25:59		71		30

		5-Jan-08		22:07:10		68		41.5		5-Jan-08		22:06:20		66.81		43.5		5-Jan-08		22:07:53		68		44		15-Feb-08		22:25:59		69.2		31.5

		6-Jan-08		0:07:10		67.4		41		6-Jan-08		0:06:20		66.81		42.5		6-Jan-08		0:07:53		67.4		43.5		16-Feb-08		0:25:59		68		33

		6-Jan-08		2:07:10		66.81		39.5		6-Jan-08		2:06:20		66.81		39.5		6-Jan-08		2:07:53		66.2		42.5		16-Feb-08		2:25:59		66.2		34

		6-Jan-08		4:07:10		66.2		41		6-Jan-08		4:06:20		66.2		42		6-Jan-08		4:07:53		65.6		43		16-Feb-08		4:25:59		65.6		35

		6-Jan-08		6:07:10		65.6		41		6-Jan-08		6:06:20		66.2		41		6-Jan-08		6:07:53		65.01		43.5		16-Feb-08		6:25:59		66.2		36

		6-Jan-08		8:07:10		65.6		42		6-Jan-08		8:06:20		68		40		6-Jan-08		8:07:53		66.81		41		16-Feb-08		8:25:59		69.2		34

		6-Jan-08		10:07:10		65.6		43.5		6-Jan-08		10:06:20		68		42.5		6-Jan-08		10:07:53		66.81		42.5		16-Feb-08		10:25:59		71.6		34.5

		6-Jan-08		12:07:10		65.6		44.5		6-Jan-08		12:06:20		68		42.5		6-Jan-08		12:07:53		67.4		43		16-Feb-08		12:25:59		72.21		34

		6-Jan-08		14:07:10		65.6		45.5		6-Jan-08		14:06:20		68		44		6-Jan-08		14:07:53		67.4		45		16-Feb-08		14:25:59		72.8		34

		6-Jan-08		16:07:10		66.2		45		6-Jan-08		16:06:20		68		43.5		6-Jan-08		16:07:53		68		44.5		16-Feb-08		16:25:59		74.6		37

		6-Jan-08		18:07:10		66.2		45		6-Jan-08		18:06:20		68		44		6-Jan-08		18:07:53		67.4		45		16-Feb-08		18:25:59		74.01		37

		6-Jan-08		20:07:10		66.2		45		6-Jan-08		20:06:20		66.81		44.5		6-Jan-08		20:07:53		67.4		44		16-Feb-08		20:25:59		71.6		37.5

		6-Jan-08		22:07:10		65.6		43		6-Jan-08		22:06:20		66.81		42.5		6-Jan-08		22:07:53		66.2		43.5		16-Feb-08		22:25:59		69.2		38

		7-Jan-08		0:07:10		65.01		42.5		7-Jan-08		0:06:20		66.2		41.5		7-Jan-08		0:07:53		65.6		43		17-Feb-08		0:25:59		68		39

		7-Jan-08		2:07:10		65.01		42.5		7-Jan-08		2:06:20		66.2		41		7-Jan-08		2:07:53		65.6		43		17-Feb-08		2:25:59		67.4		39.5

		7-Jan-08		4:07:10		64.4		41.5		7-Jan-08		4:06:20		66.2		40		7-Jan-08		4:07:53		65.01		42		17-Feb-08		4:25:59		66.81		40.5

		7-Jan-08		6:07:10		64.4		40		7-Jan-08		6:06:20		66.2		38		7-Jan-08		6:07:53		64.4		41		17-Feb-08		6:25:59		66.81		41

		7-Jan-08		8:07:10		64.4		40.5		7-Jan-08		8:06:20		67.4		37		7-Jan-08		8:07:53		66.81		38.5		17-Feb-08		8:25:59		66.2		41

		7-Jan-08		10:07:10		64.4		39		7-Jan-08		10:06:20		67.4		35.5		7-Jan-08		10:07:53		67.4		36.5		17-Feb-08		10:25:59		66.2		41

		7-Jan-08		12:07:10		64.4		41		7-Jan-08		12:06:20		68		38.5		7-Jan-08		12:07:53		67.4		38.5		17-Feb-08		12:25:59		66.81		42

		7-Jan-08		14:07:10		65.01		43		7-Jan-08		14:06:20		68		41		7-Jan-08		14:07:53		67.4		41		17-Feb-08		14:25:59		67.4		43

		7-Jan-08		16:07:10		65.6		42.5		7-Jan-08		16:06:20		68		39.5		7-Jan-08		16:07:53		68		40.5		17-Feb-08		16:25:59		68.61		42

		7-Jan-08		18:07:10		65.6		41.5		7-Jan-08		18:06:20		68		39.5		7-Jan-08		18:07:53		68		40		17-Feb-08		18:25:59		69.2		41

		7-Jan-08		20:07:10		65.6		42		7-Jan-08		20:06:20		66.81		41.5		7-Jan-08		20:07:53		66.81		41		17-Feb-08		20:25:59		68		41.5

		7-Jan-08		22:07:10		65.01		43.5		7-Jan-08		22:06:20		66.81		42.5		7-Jan-08		22:07:53		65.6		43		17-Feb-08		22:25:59		67.4		42

		8-Jan-08		0:07:10		65.01		44.5		8-Jan-08		0:06:20		66.81		43		8-Jan-08		0:07:53		65.6		44		18-Feb-08		0:25:59		66.2		42

		8-Jan-08		2:07:10		64.4		44		8-Jan-08		2:06:20		66.81		42.5		8-Jan-08		2:07:53		65.01		44		18-Feb-08		2:25:59		65.6		42.5

		8-Jan-08		4:07:10		64.4		44.5		8-Jan-08		4:06:20		66.2		42.5		8-Jan-08		4:07:53		65.01		44		18-Feb-08		4:25:59		65.01		43.5

		8-Jan-08		6:07:10		64.4		44		8-Jan-08		6:06:20		66.2		41.5		8-Jan-08		6:07:53		66.81		41.5		18-Feb-08		6:25:59		65.01		44

		8-Jan-08		8:07:10		65.6		41		8-Jan-08		8:06:20		68		37.5		8-Jan-08		8:07:53		69.2		38.5		18-Feb-08		8:25:59		65.6		43

		8-Jan-08		10:07:10		66.2		39.5		8-Jan-08		10:06:20		69.8		35.5		8-Jan-08		10:07:53		71		36.5		18-Feb-08		10:25:59		66.2		42.5

		8-Jan-08		12:07:10		67.4		42		8-Jan-08		12:06:20		71.6		40.5		8-Jan-08		12:07:53		72.21		39		18-Feb-08		12:25:59		67.4		42

		8-Jan-08		14:07:10		68		38.5		8-Jan-08		14:06:20		71.6		35.5		8-Jan-08		14:07:53		70.41		40.5		18-Feb-08		14:25:59		68		42.5

		8-Jan-08		16:07:10		68.61		35.5		8-Jan-08		16:06:20		71		33.5		8-Jan-08		16:07:53		71		35.5		18-Feb-08		16:25:59		68		43.5

		8-Jan-08		18:07:10		68.61		34		8-Jan-08		18:06:20		69.2		34		8-Jan-08		18:07:53		70.41		36		18-Feb-08		18:25:59		68		43.5

		8-Jan-08		20:07:10		68		34.5		8-Jan-08		20:06:20		67.4		36		8-Jan-08		20:07:53		69.2		36		18-Feb-08		20:25:59		67.4		43.5

		8-Jan-08		22:07:10		67.4		35.5		8-Jan-08		22:06:20		66.81		36.5		8-Jan-08		22:07:53		67.4		38		18-Feb-08		22:25:59		66.2		43.5

		9-Jan-08		0:07:10		66.81		36.5		9-Jan-08		0:06:20		66.81		37		9-Jan-08		0:07:53		65.6		38.5		19-Feb-08		0:25:59		65.6		44.5

		9-Jan-08		2:07:10		65.6		37.5		9-Jan-08		2:06:20		66.81		37.5		9-Jan-08		2:07:53		64.4		39.5		19-Feb-08		2:25:59		65.6		45

		9-Jan-08		4:07:10		65.01		38		9-Jan-08		4:06:20		66.2		38		9-Jan-08		4:07:53		63.21		41		19-Feb-08		4:25:59		65.01		45.5

		9-Jan-08		6:07:10		65.01		39		9-Jan-08		6:06:20		66.2		38.5		9-Jan-08		6:07:53		67.4		38		19-Feb-08		6:25:59		66.2		45

		9-Jan-08		8:07:10		65.6		39		9-Jan-08		8:06:20		68		37.5		9-Jan-08		8:07:53		68.61		39		19-Feb-08		8:25:59		69.8		42.5

		9-Jan-08		10:07:10		66.81		41		9-Jan-08		10:06:20		71		37.5		9-Jan-08		10:07:53		70.41		39.5		19-Feb-08		10:25:59		72.21		40.5

		9-Jan-08		12:07:10		67.4		42.5		9-Jan-08		12:06:20		71		42		9-Jan-08		12:07:53		71		41.5		19-Feb-08		12:25:59		71.6		40.5

		9-Jan-08		14:07:10		68.61		44.5		9-Jan-08		14:06:20		72.8		43.5		9-Jan-08		14:07:53		71.6		42.5		19-Feb-08		14:25:59		71.6		40.5

		9-Jan-08		16:07:10		69.2		46		9-Jan-08		16:06:20		74.01		42.5		9-Jan-08		16:07:53		71		44		19-Feb-08		16:25:59		72.21		40.5

		9-Jan-08		18:07:10		69.8		46		9-Jan-08		18:06:20		71		46		9-Jan-08		18:07:53		71.6		38.5		19-Feb-08		18:25:59		71.6		41

		9-Jan-08		20:07:10		70.41		45		9-Jan-08		20:06:20		69.8		45		9-Jan-08		20:07:53		70.41		44.5		19-Feb-08		20:25:59		71.6		41

		9-Jan-08		22:07:10		69.2		42.5		9-Jan-08		22:06:20		68		44.5		9-Jan-08		22:07:53		68.61		43.5		19-Feb-08		22:25:59		69.2		41.5

		10-Jan-08		0:07:10		68		44		10-Jan-08		0:06:20		66.81		46.5		10-Jan-08		0:07:53		67.4		45		20-Feb-08		0:25:59		67.4		42

		10-Jan-08		2:07:10		67.4		45		10-Jan-08		2:06:20		66.81		47		10-Jan-08		2:07:53		66.2		46.5		20-Feb-08		2:25:59		66.81		42.5

		10-Jan-08		4:07:10		66.81		45.5		10-Jan-08		4:06:20		66.81		46		10-Jan-08		4:07:53		65.6		47		20-Feb-08		4:25:59		66.2		43.5

		10-Jan-08		6:07:10		66.2		46		10-Jan-08		6:06:20		67.4		45.5		10-Jan-08		6:07:53		66.81		45.5		20-Feb-08		6:25:59		66.81		43.5

		10-Jan-08		8:07:10		66.81		45		10-Jan-08		8:06:20		69.8		41.5		10-Jan-08		8:07:53		70.41		43		20-Feb-08		8:25:59		71.6		42

		10-Jan-08		10:07:10		68		44.5		10-Jan-08		10:06:20		70.41		41		10-Jan-08		10:07:53		72.21		41.5		20-Feb-08		10:25:59		72.8		41

		10-Jan-08		12:07:10		68.61		43.5		10-Jan-08		12:06:20		70.41		39		10-Jan-08		12:07:53		71.6		42		20-Feb-08		12:25:59		72.8		41.5

		10-Jan-08		14:07:10		69.2		43.5		10-Jan-08		14:06:20		70.41		45		10-Jan-08		14:07:53		71.6		44		20-Feb-08		14:25:59		72.21		43.5

		10-Jan-08		16:07:10		69.2		43		10-Jan-08		16:06:20		70.41		39.5		10-Jan-08		16:07:53		71		43		20-Feb-08		16:25:59		72.21		45.5

		10-Jan-08		18:07:10		69.2		43		10-Jan-08		18:06:20		68.61		44		10-Jan-08		18:07:53		70.41		43.5		20-Feb-08		18:25:59		71.6		45.5

		10-Jan-08		20:07:10		69.2		42.5		10-Jan-08		20:06:20		68		44.5		10-Jan-08		20:07:53		69.2		42.5		20-Feb-08		20:25:59		71.6		45.5

		10-Jan-08		22:07:10		68.61		43		10-Jan-08		22:06:20		67.4		45		10-Jan-08		22:07:53		68		44		20-Feb-08		22:25:59		70.41		45.5

		11-Jan-08		0:07:10		68		43.5		11-Jan-08		0:06:20		67.4		44.5		11-Jan-08		0:07:53		67.4		44.5		21-Feb-08		0:25:59		68.61		46

		11-Jan-08		2:07:10		67.4		44		11-Jan-08		2:06:20		67.4		45.5		11-Jan-08		2:07:53		66.81		45.5		21-Feb-08		2:25:59		68		46

		11-Jan-08		4:07:10		67.4		44		11-Jan-08		4:06:20		67.4		45		11-Jan-08		4:07:53		65.6		46.5		21-Feb-08		4:25:59		66.81		46.5

		11-Jan-08		6:07:10		66.81		44.5		11-Jan-08		6:06:20		67.4		45		11-Jan-08		6:07:53		68		45		21-Feb-08		6:25:59		66.81		47

		11-Jan-08		8:07:10		67.4		45		11-Jan-08		8:06:20		67.4		45		11-Jan-08		8:07:53		69.8		44		21-Feb-08		8:25:59		71		44.5

		11-Jan-08		10:07:10		68		46		11-Jan-08		10:06:20		72.21		42.5		11-Jan-08		10:07:53		71.6		43		21-Feb-08		10:25:59		72.21		44

		11-Jan-08		12:07:10		69.2		46.5		11-Jan-08		12:06:20		72.8		44		11-Jan-08		12:07:53		71.6		47		21-Feb-08		12:25:59		72.8		43.5

		11-Jan-08		14:07:10		70.41		47.5		11-Jan-08		14:06:20		72.8		46		11-Jan-08		14:07:53		71		41.5		21-Feb-08		14:25:59		73.4		42

		11-Jan-08		16:07:10		70.41		47		11-Jan-08		16:06:20		73.4		40		11-Jan-08		16:07:53		71		48.5		21-Feb-08		16:25:59		74.01		40.5

		11-Jan-08		18:07:10		70.41		47		11-Jan-08		18:06:20		71		46.5		11-Jan-08		18:07:53		70.41		44.5		21-Feb-08		18:25:59		73.4		41

		11-Jan-08		20:07:10		69.8		46		11-Jan-08		20:06:20		69.2		48		11-Jan-08		20:07:53		70.41		44.5		21-Feb-08		20:25:59		72.21		40.5

		11-Jan-08		22:07:10		68.61		47		11-Jan-08		22:06:20		68		49.5		11-Jan-08		22:07:53		69.2		47		21-Feb-08		22:25:59		71		41

		12-Jan-08		0:07:10		68		48		12-Jan-08		0:06:20		68		49.5		12-Jan-08		0:07:53		68		48		22-Feb-08		0:25:59		69.8		41

		12-Jan-08		2:07:10		67.4		49		12-Jan-08		2:06:20		68		50		12-Jan-08		2:07:53		67.4		49		22-Feb-08		2:25:59		68.61		42

		12-Jan-08		4:07:10		66.81		48.5		12-Jan-08		4:06:20		67.4		48.5		12-Jan-08		4:07:53		66.81		49		22-Feb-08		4:25:59		67.4		43

		12-Jan-08		6:07:10		66.81		47.5		12-Jan-08		6:06:20		67.4		46.5		12-Jan-08		6:07:53		67.4		47.5		22-Feb-08		6:25:59		67.4		43.5

		12-Jan-08		8:07:10		66.81		46		12-Jan-08		8:06:20		69.2		43		12-Jan-08		8:07:53		69.8		45		22-Feb-08		8:25:59		71.6		42

		12-Jan-08		10:07:10		68		45.5		12-Jan-08		10:06:20		72.8		38		12-Jan-08		10:07:53		71.6		43		22-Feb-08		10:25:59		72.8		41

		12-Jan-08		12:07:10		68		45.5		12-Jan-08		12:06:20		71		45		12-Jan-08		12:07:53		71		41		22-Feb-08		12:25:59		72.8		42.5

		12-Jan-08		14:07:10		68		44.5		12-Jan-08		14:06:20		70.41		42		12-Jan-08		14:07:53		69.8		44		22-Feb-08		14:25:59		72.21		42

		12-Jan-08		16:07:10		68		45		12-Jan-08		16:06:20		68.61		44		12-Jan-08		16:07:53		70.41		43.5		22-Feb-08		16:25:59		72.21		43.5

		12-Jan-08		18:07:10		67.4		45		12-Jan-08		18:06:20		68.61		44.5		12-Jan-08		18:07:53		69.8		43.5		22-Feb-08		18:25:59		72.21		44

		12-Jan-08		20:07:10		67.4		45.5		12-Jan-08		20:06:20		68		45.5		12-Jan-08		20:07:53		69.2		44		22-Feb-08		20:25:59		72.21		43.5

		12-Jan-08		22:07:10		66.81		45.5		12-Jan-08		22:06:20		66.81		46.5		12-Jan-08		22:07:53		69.2		44.5		22-Feb-08		22:25:59		70.41		44.5

		13-Jan-08		0:07:10		65.6		47		13-Jan-08		0:06:20		66.2		48		13-Jan-08		0:07:53		69.2		43.5		23-Feb-08		0:25:59		68.61		45

		13-Jan-08		2:07:10		65.01		47.5		13-Jan-08		2:06:20		66.2		47.5		13-Jan-08		2:07:53		69.2		43		23-Feb-08		2:25:59		68		45.5

		13-Jan-08		4:07:10		65.01		48		13-Jan-08		4:06:20		66.2		47		13-Jan-08		4:07:53		69.8		42.5		23-Feb-08		4:25:59		67.4		45.5

		13-Jan-08		6:07:10		64.4		49		13-Jan-08		6:06:20		66.2		48		13-Jan-08		6:07:53		69.8		43		23-Feb-08		6:25:59		67.4		45

		13-Jan-08		8:07:10		64.4		49		13-Jan-08		8:06:20		67.4		45.5		13-Jan-08		8:07:53		69.8		42.5		23-Feb-08		8:25:59		72.8		42.5

		13-Jan-08		10:07:10		64.4		49.5		13-Jan-08		10:06:20		68		45.5		13-Jan-08		10:07:53		69.8		42.5		23-Feb-08		10:25:59		72.8		42.5

		13-Jan-08		12:07:10		65.01		50		13-Jan-08		12:06:20		68		47		13-Jan-08		12:07:53		69.8		45		23-Feb-08		12:25:59		71.6		42.5

		13-Jan-08		14:07:10		65.6		49.5		13-Jan-08		14:06:20		68.61		46		13-Jan-08		14:07:53		69.8		44		23-Feb-08		14:25:59		71.6		43

		13-Jan-08		16:07:10		66.2		49.5		13-Jan-08		16:06:20		69.2		46		13-Jan-08		16:07:53		69.8		45.5		23-Feb-08		16:25:59		72.8		41

		13-Jan-08		18:07:10		66.81		49.5		13-Jan-08		18:06:20		69.2		45		13-Jan-08		18:07:53		69.8		46.5		23-Feb-08		18:25:59		72.8		38.5

		13-Jan-08		20:07:10		66.81		48.5		13-Jan-08		20:06:20		68		47.5		13-Jan-08		20:07:53		69.2		45.5		23-Feb-08		20:25:59		71.6		38

		13-Jan-08		22:07:10		66.2		47		13-Jan-08		22:06:20		66.2		46		13-Jan-08		22:07:53		69.2		43		23-Feb-08		22:25:59		69.2		38.5

		14-Jan-08		0:07:10		65.01		46.5		14-Jan-08		0:06:20		65.6		45.5		14-Jan-08		0:07:53		69.2		41		24-Feb-08		0:25:59		66.81		39.5

		14-Jan-08		2:07:10		64.4		48		14-Jan-08		2:06:20		65.6		47		14-Jan-08		2:07:53		69.8		41.5		24-Feb-08		2:25:59		65.6		40

		14-Jan-08		4:07:10		64.4		49.5		14-Jan-08		4:06:20		65.6		48		14-Jan-08		4:07:53		69.8		42		24-Feb-08		4:25:59		64.4		40

		14-Jan-08		6:07:10		64.4		50.5		14-Jan-08		6:06:20		66.2		49		14-Jan-08		6:07:53		69.8		42.5		24-Feb-08		6:25:59		64.4		40.5

		14-Jan-08		8:07:10		64.4		51.5		14-Jan-08		8:06:20		68		47		14-Jan-08		8:07:53		69.8		43		24-Feb-08		8:25:59		65.01		40.5

		14-Jan-08		10:07:10		64.4		50		14-Jan-08		10:06:20		68		45.5		14-Jan-08		10:07:53		69.8		42		24-Feb-08		10:25:59		65.01		41.5

		14-Jan-08		12:07:10		65.01		49		14-Jan-08		12:06:20		68		44.5		14-Jan-08		12:07:53		70.41		39.5		24-Feb-08		12:25:59		65.6		42.5

		14-Jan-08		14:07:10		65.01		49		14-Jan-08		14:06:20		68		45		14-Jan-08		14:07:53		69.8		38.5		24-Feb-08		14:25:59		66.2		43.5

		14-Jan-08		16:07:10		65.6		49.5		14-Jan-08		16:06:20		68.61		46.5		14-Jan-08		16:07:53		69.8		42.5		24-Feb-08		16:25:59		65.6		43.5

		14-Jan-08		18:07:10		66.2		49.5		14-Jan-08		18:06:20		68.61		47		14-Jan-08		18:07:53		69.8		45		24-Feb-08		18:25:59		65.01		44

		14-Jan-08		20:07:10		66.2		48.5		14-Jan-08		20:06:20		67.4		47		14-Jan-08		20:07:53		69.8		44		24-Feb-08		20:25:59		64.4		45

		14-Jan-08		22:07:10		65.6		47		14-Jan-08		22:06:20		66.2		46		14-Jan-08		22:07:53		69.8		41.5		24-Feb-08		22:25:59		64.4		46

		15-Jan-08		0:07:10		64.4		44		15-Jan-08		0:06:20		65.6		42		15-Jan-08		0:07:53		69.2		39		25-Feb-08		0:25:59		64.4		47.5

		15-Jan-08		2:07:10		63.8		45		15-Jan-08		2:06:20		65.6		43		15-Jan-08		2:07:53		69.8		38.5		25-Feb-08		2:25:59		64.4		48

		15-Jan-08		4:07:10		63.8		45		15-Jan-08		4:06:20		65.6		42.5		15-Jan-08		4:07:53		69.8		38		25-Feb-08		4:25:59		64.4		49

		15-Jan-08		6:07:10		63.21		46		15-Jan-08		6:06:20		65.6		44		15-Jan-08		6:07:53		69.8		38.5		25-Feb-08		6:25:59		64.4		49.5

		15-Jan-08		8:07:10		63.8		47		15-Jan-08		8:06:20		67.4		42.5		15-Jan-08		8:07:53		71		39.5		25-Feb-08		8:25:59		65.01		49.5

		15-Jan-08		10:07:10		65.01		47.5		15-Jan-08		10:06:20		70.41		41.5		15-Jan-08		10:07:53		71		37		25-Feb-08		10:25:59		66.2		49.5

		15-Jan-08		12:07:10		65.6		47.5		15-Jan-08		12:06:20		70.41		43		15-Jan-08		12:07:53		71		43.5		25-Feb-08		12:25:59		66.81		49.5

		15-Jan-08		14:07:10		66.2		48		15-Jan-08		14:06:20		70.41		46.5		15-Jan-08		14:07:53		71		43.5		25-Feb-08		14:25:59		67.4		50

		15-Jan-08		16:07:10		66.81		49.5		15-Jan-08		16:06:20		71		44		15-Jan-08		16:07:53		70.41		45		25-Feb-08		16:25:59		67.4		50

		15-Jan-08		18:07:10		66.81		48		15-Jan-08		18:06:20		69.2		44		15-Jan-08		18:07:53		70.41		43.5		25-Feb-08		18:25:59		67.4		49.5

		15-Jan-08		20:07:10		66.81		45.5		15-Jan-08		20:06:20		67.4		44		15-Jan-08		20:07:53		69.8		41.5		25-Feb-08		20:25:59		66.81		49

		15-Jan-08		22:07:10		65.6		43.5		15-Jan-08		22:06:20		65.6		42.5		15-Jan-08		22:07:53		68.61		41		25-Feb-08		22:25:59		66.2		49

		16-Jan-08		0:07:10		65.01		43		16-Jan-08		0:06:20		65.6		41		16-Jan-08		0:07:53		66.81		40		26-Feb-08		0:25:59		65.6		49.5

		16-Jan-08		2:07:10		64.4		42.5		16-Jan-08		2:06:20		65.01		41.5		16-Jan-08		2:07:53		65.6		41		26-Feb-08		2:25:59		65.01		50

		16-Jan-08		4:07:10		63.8		42.5		16-Jan-08		4:06:20		65.6		40		16-Jan-08		4:07:53		64.4		41		26-Feb-08		4:25:59		64.4		49.5

		16-Jan-08		6:07:10		63.21		42		16-Jan-08		6:06:20		65.01		40		16-Jan-08		6:07:53		67.4		38		26-Feb-08		6:25:59		66.2		48

		16-Jan-08		8:07:10		63.8		41		16-Jan-08		8:06:20		67.4		37		16-Jan-08		8:07:53		69.2		36.5		26-Feb-08		8:25:59		69.8		45

		16-Jan-08		10:07:10		65.01		41		16-Jan-08		10:06:20		70.41		36		16-Jan-08		10:07:53		71		36		26-Feb-08		10:25:59		72.21		44

		16-Jan-08		12:07:10		65.6		42.5		16-Jan-08		12:06:20		71		35		16-Jan-08		12:07:53		71.6		36		26-Feb-08		12:25:59		72.21		43.5

		16-Jan-08		14:07:10		66.81		44.5		16-Jan-08		14:06:20		71		39		16-Jan-08		14:07:53		70.41		43.5		26-Feb-08		14:25:59		72.8		43

		16-Jan-08		16:07:10		68		46		16-Jan-08		16:06:20		71.6		40.5		16-Jan-08		16:07:53		69.8		44.5		26-Feb-08		16:25:59		73.4		42

		16-Jan-08		18:07:10		68		44.5		16-Jan-08		18:06:20		69.8		42		16-Jan-08		18:07:53		69.8		43.5		26-Feb-08		18:25:59		73.4		42.5

		16-Jan-08		20:07:10		68		44		16-Jan-08		20:06:20		68.61		43.5		16-Jan-08		20:07:53		69.2		43		26-Feb-08		20:25:59		72.21		42.5

		16-Jan-08		22:07:10		67.4		42		16-Jan-08		22:06:20		66.81		43		16-Jan-08		22:07:53		68.61		40.5		26-Feb-08		22:25:59		70.41		43.5

		17-Jan-08		0:07:10		66.2		40.5		17-Jan-08		0:06:20		65.6		41		17-Jan-08		0:07:53		66.81		39.5		27-Feb-08		0:25:59		68		43.5

		17-Jan-08		2:07:10		65.01		40.5		17-Jan-08		2:06:20		65.6		39		17-Jan-08		2:07:53		65.6		39.5		27-Feb-08		2:25:59		66.81		43.5

		17-Jan-08		4:07:10		63.8		40		17-Jan-08		4:06:20		65.6		38.5		17-Jan-08		4:07:53		64.4		39.5		27-Feb-08		4:25:59		65.6		43.5

		17-Jan-08		6:07:10		63.8		39.5		17-Jan-08		6:06:20		65.6		37		17-Jan-08		6:07:53		66.2		37		27-Feb-08		6:25:59		66.81		43.5

		17-Jan-08		8:07:10		64.4		38.5		17-Jan-08		8:06:20		68		34.5		17-Jan-08		8:07:53		69.2		35.5		27-Feb-08		8:25:59		71.6		41

		17-Jan-08		10:07:10		65.01		35		17-Jan-08		10:06:20		70.41		29.5		17-Jan-08		10:07:53		71.6		31		27-Feb-08		10:25:59		72.21		41

		17-Jan-08		12:07:10		66.2		29		17-Jan-08		12:06:20		71		21.5		17-Jan-08		12:07:53		69.8		23.5		27-Feb-08		12:25:59		72.21		42.5

		17-Jan-08		14:07:10		67.4		27		17-Jan-08		14:06:20		71		22.5		17-Jan-08		14:07:53		71		23.5		27-Feb-08		14:25:59		74.01		40

		17-Jan-08		16:07:10		68		25		17-Jan-08		16:06:20		70.41		21.5		17-Jan-08		16:07:53		70.41		24.5		27-Feb-08		16:25:59		74.01		40

		17-Jan-08		18:07:10		68.61		24		17-Jan-08		18:06:20		69.8		19		17-Jan-08		18:07:53		69.8		22.5		27-Feb-08		18:25:59		74.01		41.5

		17-Jan-08		20:07:10		68.61		22		17-Jan-08		20:06:20		69.8		18		17-Jan-08		20:07:53		70.41		23		27-Feb-08		20:25:59		72.8		42.5

		17-Jan-08		22:07:10		68.61		20.5		17-Jan-08		22:06:20		69.2		17.5		17-Jan-08		22:07:53		70.41		24		27-Feb-08		22:25:59		71.6		43

		18-Jan-08		0:07:10		68		20		18-Jan-08		0:06:20		68		18		18-Jan-08		0:07:53		69.2		23		28-Feb-08		0:25:59		69.8		43

		18-Jan-08		2:07:10		67.4		21.5		18-Jan-08		2:06:20		66.2		22		18-Jan-08		2:07:53		68		24		28-Feb-08		2:25:59		68.61		44

		18-Jan-08		4:07:10		66.2		21		18-Jan-08		4:06:20		66.2		20		18-Jan-08		4:07:53		66.81		23.5		28-Feb-08		4:25:59		67.4		44

		18-Jan-08		6:07:10		65.6		24.5		18-Jan-08		6:06:20		65.6		26		18-Jan-08		6:07:53		65.6		26		28-Feb-08		6:25:59		67.4		43.5

		18-Jan-08		8:07:10		65.6		26.5		18-Jan-08		8:06:20		67.4		26		18-Jan-08		8:07:53		69.8		26		28-Feb-08		8:25:59		71		41

		18-Jan-08		10:07:10		66.81		29		18-Jan-08		10:06:20		70.41		27.5		18-Jan-08		10:07:53		71.6		27		28-Feb-08		10:25:59		72.21		41

		18-Jan-08		12:07:10		67.4		28.5		18-Jan-08		12:06:20		71		26.5		18-Jan-08		12:07:53		71		28		28-Feb-08		12:25:59		72.8		42.5

		18-Jan-08		14:07:10		68		29		18-Jan-08		14:06:20		71		28		18-Jan-08		14:07:53		71		29		28-Feb-08		14:25:59		74.01		42.5

		18-Jan-08		16:07:10		68.61		29		18-Jan-08		16:06:20		70.41		29.5		18-Jan-08		16:07:53		71		31.5		28-Feb-08		16:25:59		75.2		43.5

		18-Jan-08		18:07:10		69.2		30		18-Jan-08		18:06:20		69.8		29.5		18-Jan-08		18:07:53		70.41		31.5		28-Feb-08		18:25:59		74.6		43.5

		18-Jan-08		20:07:10		69.2		32		18-Jan-08		20:06:20		68.61		34		18-Jan-08		20:07:53		71		32.5		28-Feb-08		20:25:59		72.21		44

		18-Jan-08		22:07:10		68		32		18-Jan-08		22:06:20		66.81		34.5		18-Jan-08		22:07:53		69.8		32		28-Feb-08		22:25:59		71.6		44.5

		19-Jan-08		0:07:10		66.81		32.5		19-Jan-08		0:06:20		66.2		34		19-Jan-08		0:07:53		68		32.5		29-Feb-08		0:25:59		69.2		44

		19-Jan-08		2:07:10		66.2		32.5		19-Jan-08		2:06:20		65.6		33		19-Jan-08		2:07:53		66.2		32.5		29-Feb-08		2:25:59		68		43.5

		19-Jan-08		4:07:10		65.01		32.5		19-Jan-08		4:06:20		65.6		32.5		19-Jan-08		4:07:53		65.01		32.5		29-Feb-08		4:25:59		66.81		43

		19-Jan-08		6:07:10		64.4		32.5		19-Jan-08		6:06:20		65.6		32		19-Jan-08		6:07:53		67.4		30		29-Feb-08		6:25:59		67.4		42.5

		19-Jan-08		8:07:10		65.01		32		19-Jan-08		8:06:20		68		29.5		19-Jan-08		8:07:53		69.2		31		29-Feb-08		8:25:59		70.41		40

		19-Jan-08		10:07:10		65.6		33		19-Jan-08		10:06:20		68.61		31		19-Jan-08		10:07:53		71.6		30		29-Feb-08		10:25:59		72.21		40.5

		19-Jan-08		12:07:10		65.6		35.5		19-Jan-08		12:06:20		70.41		33.5		19-Jan-08		12:07:53		71		30.5		29-Feb-08		12:25:59		73.4		42

		19-Jan-08		14:07:10		66.2		35.5		19-Jan-08		14:06:20		70.41		33.5		19-Jan-08		14:07:53		71		34.5		29-Feb-08		14:25:59		74.6		41.5

		19-Jan-08		16:07:10		67.4		35		19-Jan-08		16:06:20		71		32		19-Jan-08		16:07:53		71		34.5		29-Feb-08		16:25:59		74.6		41.5

		19-Jan-08		18:07:10		68		35.5		19-Jan-08		18:06:20		69.8		34		19-Jan-08		18:07:53		70.41		35		29-Feb-08		18:25:59		74.01		43.5

		19-Jan-08		20:07:10		68		34		19-Jan-08		20:06:20		68		34.5		19-Jan-08		20:07:53		69.8		34		29-Feb-08		20:25:59		72.21		42.5

		19-Jan-08		22:07:10		67.4		34.5		19-Jan-08		22:06:20		66.2		36.5		19-Jan-08		22:07:53		68.61		35		29-Feb-08		22:25:59		71		43.5

		20-Jan-08		0:07:10		66.2		34		20-Jan-08		0:06:20		65.6		35		20-Jan-08		0:07:53		67.4		34		1-Mar-08		0:25:59		69.8		43

		20-Jan-08		2:07:10		65.6		34		20-Jan-08		2:06:20		65.6		34		20-Jan-08		2:07:53		65.6		34		1-Mar-08		2:25:59		68.61		43.5

		20-Jan-08		4:07:10		64.4		33		20-Jan-08		4:06:20		65.6		33		20-Jan-08		4:07:53		64.4		33.5		1-Mar-08		4:25:59		68		44

		20-Jan-08		6:07:10		63.8		32.5		20-Jan-08		6:06:20		65.6		31		20-Jan-08		6:07:53		63.21		33.5		1-Mar-08		6:25:59		68		44.5

		20-Jan-08		8:07:10		63.8		31.5		20-Jan-08		8:06:20		67.4		28		20-Jan-08		8:07:53		67.4		29		1-Mar-08		8:25:59		71.6		42

		20-Jan-08		10:07:10		63.8		32		20-Jan-08		10:06:20		68		30		20-Jan-08		10:07:53		66.81		29.5		1-Mar-08		10:25:59		72.8		41.5

		20-Jan-08		12:07:10		64.4		36.5		20-Jan-08		12:06:20		68.61		35		20-Jan-08		12:07:53		67.4		33		1-Mar-08		12:25:59		72.21		43

		20-Jan-08		14:07:10		65.01		37		20-Jan-08		14:06:20		68.61		35		20-Jan-08		14:07:53		67.4		35.5		1-Mar-08		14:25:59		72.8		44

		20-Jan-08		16:07:10		66.2		36.5		20-Jan-08		16:06:20		69.8		33.5		20-Jan-08		16:07:53		68.61		35.5		1-Mar-08		16:25:59		74.01		45

		20-Jan-08		18:07:10		66.81		36.5		20-Jan-08		18:06:20		69.2		34.5		20-Jan-08		18:07:53		69.8		35.5		1-Mar-08		18:25:59		73.4		43.5

		20-Jan-08		20:07:10		66.81		34.5		20-Jan-08		20:06:20		68		33.5		20-Jan-08		20:07:53		69.2		34		1-Mar-08		20:25:59		72.21		43

		20-Jan-08		22:07:10		66.2		35		20-Jan-08		22:06:20		66.2		35.5		20-Jan-08		22:07:53		67.4		34.5		1-Mar-08		22:25:59		71		43

		21-Jan-08		0:07:10		65.01		35		21-Jan-08		0:06:20		65.6		35		21-Jan-08		0:07:53		65.6		34.5		2-Mar-08		0:25:59		69.2		43

		21-Jan-08		2:07:10		64.4		38.5		21-Jan-08		2:06:20		65.6		39		21-Jan-08		2:07:53		65.01		37		2-Mar-08		2:25:59		68.61		44

		21-Jan-08		4:07:10		64.4		38.5		21-Jan-08		4:06:20		65.6		38		21-Jan-08		4:07:53		64.4		38		2-Mar-08		4:25:59		67.4		44.5

		21-Jan-08		6:07:10		63.8		37		21-Jan-08		6:06:20		65.6		36		21-Jan-08		6:07:53		63.8		37.5		2-Mar-08		6:25:59		67.4		44.5

		21-Jan-08		8:07:10		63.8		38		21-Jan-08		8:06:20		67.4		35		21-Jan-08		8:07:53		66.81		34.5		2-Mar-08		8:25:59		67.4		44

		21-Jan-08		10:07:10		63.8		38.5		21-Jan-08		10:06:20		68		35		21-Jan-08		10:07:53		66.81		35.5		2-Mar-08		10:25:59		68		43.5

		21-Jan-08		12:07:10		64.4		40		21-Jan-08		12:06:20		68		36.5		21-Jan-08		12:07:53		67.4		36		2-Mar-08		12:25:59		69.2		42

		21-Jan-08		14:07:10		64.4		35		21-Jan-08		14:06:20		68		31		21-Jan-08		14:07:53		67.4		33.5		2-Mar-08		14:25:59		70.41		40.5

		21-Jan-08		16:07:10		65.01		34.5		21-Jan-08		16:06:20		68		32		21-Jan-08		16:07:53		67.4		34		2-Mar-08		16:25:59		69.8		39

		21-Jan-08		18:07:10		65.6		33.5		21-Jan-08		18:06:20		68		31		21-Jan-08		18:07:53		67.4		33.5		2-Mar-08		18:25:59		69.8		38

		21-Jan-08		20:07:10		65.6		34.5		21-Jan-08		20:06:20		66.2		34		21-Jan-08		20:07:53		66.81		34		2-Mar-08		20:25:59		68.61		39

		21-Jan-08		22:07:10		65.01		34.5		21-Jan-08		22:06:20		65.6		34		21-Jan-08		22:07:53		65.01		34.5		2-Mar-08		22:25:59		67.4		39.5

		22-Jan-08		0:07:10		64.4		34.5		22-Jan-08		0:06:20		65.6		33.5		22-Jan-08		0:07:53		63.8		35		3-Mar-08		0:25:59		66.81		40

		22-Jan-08		2:07:10		63.8		34		22-Jan-08		2:06:20		65.01		32		22-Jan-08		2:07:53		62.6		34		3-Mar-08		2:25:59		65.6		40

		22-Jan-08		4:07:10		63.21		32.5		22-Jan-08		4:06:20		65.01		30.5		22-Jan-08		4:07:53		61.41		33.5		3-Mar-08		4:25:59		65.01		39.5

		22-Jan-08		6:07:10		62.6		31.5		22-Jan-08		6:06:20		65.01		30		22-Jan-08		6:07:53		66.81		29.5		3-Mar-08		6:25:59		64.4		39.5

		22-Jan-08		8:07:10		63.21		32		22-Jan-08		8:06:20		67.4		28.5		22-Jan-08		8:07:53		68		30		3-Mar-08		8:25:59		65.01		38.5

		22-Jan-08		10:07:10		64.4		33.5		22-Jan-08		10:06:20		69.2		30		22-Jan-08		10:07:53		70.41		30.5		3-Mar-08		10:25:59		66.2		38

		22-Jan-08		12:07:10		65.01		36		22-Jan-08		12:06:20		70.41		32.5		22-Jan-08		12:07:53		71.6		31		3-Mar-08		12:25:59		66.81		38

		22-Jan-08		14:07:10		66.2		37.5		22-Jan-08		14:06:20		71		35.5		22-Jan-08		14:07:53		71		36		3-Mar-08		14:25:59		67.4		35.5

		22-Jan-08		16:07:10		66.81		39		22-Jan-08		16:06:20		71		34.5		22-Jan-08		16:07:53		70.41		37		3-Mar-08		16:25:59		68.61		33.5

		22-Jan-08		18:07:10		67.4		37		22-Jan-08		18:06:20		68.61		36		22-Jan-08		18:07:53		69.8		36		3-Mar-08		18:25:59		68.61		31.5

		22-Jan-08		20:07:10		67.4		36.5		22-Jan-08		20:06:20		68		36.5		22-Jan-08		20:07:53		69.8		35		3-Mar-08		20:25:59		68.61		31

		22-Jan-08		22:07:10		66.81		37		22-Jan-08		22:06:20		67.4		36.5		22-Jan-08		22:07:53		67.4		36		3-Mar-08		22:25:59		68		33

		23-Jan-08		0:07:10		65.6		37.5		23-Jan-08		0:06:20		67.4		36.5		23-Jan-08		0:07:53		65.6		37.5		4-Mar-08		0:25:59		66.81		35

		23-Jan-08		2:07:10		65.01		37		23-Jan-08		2:06:20		67.4		35.5		23-Jan-08		2:07:53		65.01		38		4-Mar-08		2:25:59		66.2		37

		23-Jan-08		4:07:10		64.4		37.5		23-Jan-08		4:06:20		66.81		35.5		23-Jan-08		4:07:53		63.8		38.5		4-Mar-08		4:25:59		65.6		37.5

		23-Jan-08		6:07:10		64.4		37		23-Jan-08		6:06:20		66.81		35		23-Jan-08		6:07:53		67.4		35.5		4-Mar-08		6:25:59		66.2		37.5

		23-Jan-08		8:07:10		65.01		36		23-Jan-08		8:06:20		68		33		23-Jan-08		8:07:53		69.2		34		4-Mar-08		8:25:59		69.2		35.5

		23-Jan-08		10:07:10		65.6		36.5		23-Jan-08		10:06:20		69.2		34		23-Jan-08		10:07:53		71		35		4-Mar-08		10:25:59		71.6		36.5

		23-Jan-08		12:07:10		66.2		36		23-Jan-08		12:06:20		69.8		33		23-Jan-08		12:07:53		71		34		4-Mar-08		12:25:59		72.21		36.5

		23-Jan-08		14:07:10		66.81		34.5		23-Jan-08		14:06:20		70.41		32		23-Jan-08		14:07:53		70.41		35		4-Mar-08		14:25:59		73.4		33.5

		23-Jan-08		16:07:10		66.81		33.5		23-Jan-08		16:06:20		69.8		31.5		23-Jan-08		16:07:53		70.41		32		4-Mar-08		16:25:59		74.01		33.5

		23-Jan-08		18:07:10		66.81		33		23-Jan-08		18:06:20		69.2		31		23-Jan-08		18:07:53		69.2		32		4-Mar-08		18:25:59		74.01		33

		23-Jan-08		20:07:10		66.81		32.5		23-Jan-08		20:06:20		68		31		23-Jan-08		20:07:53		68		32.5		4-Mar-08		20:25:59		72.21		32

		23-Jan-08		22:07:10		66.2		32.5		23-Jan-08		22:06:20		67.4		32		23-Jan-08		22:07:53		68		32.5		4-Mar-08		22:25:59		71		33.5

		24-Jan-08		0:07:10		65.6		33.5		24-Jan-08		0:06:20		66.81		32.5		24-Jan-08		0:07:53		66.2		33		5-Mar-08		0:25:59		69.2		34.5

		24-Jan-08		2:07:10		65.01		34		24-Jan-08		2:06:20		67.4		32.5		24-Jan-08		2:07:53		64.4		34.5		5-Mar-08		2:25:59		68		35.5

		24-Jan-08		4:07:10		64.4		35.5		24-Jan-08		4:06:20		67.4		34		24-Jan-08		4:07:53		63.8		36		5-Mar-08		4:25:59		66.81		36

		24-Jan-08		6:07:10		64.4		37		24-Jan-08		6:06:20		66.81		35		24-Jan-08		6:07:53		68		34		5-Mar-08		6:25:59		66.81		36.5

		24-Jan-08		8:07:10		65.01		37		24-Jan-08		8:06:20		68		35		24-Jan-08		8:07:53		69.2		35.5		5-Mar-08		8:25:59		69.8		34

		24-Jan-08		10:07:10		65.6		38		24-Jan-08		10:06:20		71		33.5		24-Jan-08		10:07:53		71		35		5-Mar-08		10:25:59		72.21		36

		24-Jan-08		12:07:10		66.81		39		24-Jan-08		12:06:20		71		36		24-Jan-08		12:07:53		71		37		5-Mar-08		12:25:59		72.8		36.5

		24-Jan-08		14:07:10		68		38		24-Jan-08		14:06:20		71		37		24-Jan-08		14:07:53		71		38.5		5-Mar-08		14:25:59		74.01		36.5

		24-Jan-08		16:07:10		68		36		24-Jan-08		16:06:20		71		34		24-Jan-08		16:07:53		71.6		35		5-Mar-08		16:25:59		74.6		35.5

		24-Jan-08		18:07:10		68.61		34.5		24-Jan-08		18:06:20		68.61		33.5		24-Jan-08		18:07:53		71		34		5-Mar-08		18:25:59		74.6		36.5

		24-Jan-08		20:07:10		68		35.5		24-Jan-08		20:06:20		68		36.5		24-Jan-08		20:07:53		69.8		35		5-Mar-08		20:25:59		72.8		37

		24-Jan-08		22:07:10		67.4		36.5		24-Jan-08		22:06:20		67.4		37		24-Jan-08		22:07:53		68		36		5-Mar-08		22:25:59		71		37

		25-Jan-08		0:07:10		66.2		36.5		25-Jan-08		0:06:20		67.4		36		25-Jan-08		0:07:53		66.2		37		6-Mar-08		0:25:59		69.2		37

		25-Jan-08		2:07:10		65.6		37.5		25-Jan-08		2:06:20		66.81		37		25-Jan-08		2:07:53		65.01		38		6-Mar-08		2:25:59		68		37.5

		25-Jan-08		4:07:10		65.01		39		25-Jan-08		4:06:20		67.4		37.5		25-Jan-08		4:07:53		64.4		39.5		6-Mar-08		4:25:59		66.81		38

		25-Jan-08		6:07:10		64.4		39.5		25-Jan-08		6:06:20		67.4		38		25-Jan-08		6:07:53		66.81		38		6-Mar-08		6:25:59		66.81		37.5

		25-Jan-08		8:07:10		65.01		39		25-Jan-08		8:06:20		68		36.5		25-Jan-08		8:07:53		69.2		36		6-Mar-08		8:25:59		70.41		35.5

		25-Jan-08		10:07:10		65.6		40.5		25-Jan-08		10:06:20		69.8		37		25-Jan-08		10:07:53		71.6		36		6-Mar-08		10:25:59		71.6		36.5

		25-Jan-08		12:07:10		66.81		39.5		25-Jan-08		12:06:20		69.8		37.5		25-Jan-08		12:07:53		72.21		36		6-Mar-08		12:25:59		72.8		35.5

		25-Jan-08		14:07:10		67.4		38		25-Jan-08		14:06:20		69.8		37.5		25-Jan-08		14:07:53		71		37.5		6-Mar-08		14:25:59		74.01		32.5

		25-Jan-08		16:07:10		68.61		37.5		25-Jan-08		16:06:20		70.41		37		25-Jan-08		16:07:53		70.41		38		6-Mar-08		16:25:59		74.6		31

		25-Jan-08		18:07:10		68.61		36		25-Jan-08		18:06:20		68		36.5		25-Jan-08		18:07:53		69.8		36		6-Mar-08		18:25:59		68.61		44.5

		25-Jan-08		20:07:10		68.61		35		25-Jan-08		20:06:20		67.4		37		25-Jan-08		20:07:53		68.61		36		6-Mar-08		20:25:59		68.61		44

		25-Jan-08		22:07:10		68		35.5		25-Jan-08		22:06:20		66.81		37		25-Jan-08		22:07:53		67.4		37.5		6-Mar-08		22:25:59		68.61		42.5

		26-Jan-08		0:07:10		67.4		35.5		26-Jan-08		0:06:20		66.81		36		26-Jan-08		0:07:53		66.81		37.5		7-Mar-08		0:25:59		68.61		44

		26-Jan-08		2:07:10		66.81		36		26-Jan-08		2:06:20		66.81		36.5		26-Jan-08		2:07:53		65.6		37.5		7-Mar-08		2:25:59		68		43

		26-Jan-08		4:07:10		66.2		35		26-Jan-08		4:06:20		66.81		35		26-Jan-08		4:07:53		65.6		37.5		7-Mar-08		4:25:59		69.2		44

		26-Jan-08		6:07:10		65.6		37.5		26-Jan-08		6:06:20		66.81		38		26-Jan-08		6:07:53		68.61		36.5		7-Mar-08		6:25:59		68.61		43.5

		26-Jan-08		8:07:10		66.2		39.5		26-Jan-08		8:06:20		67.4		40		26-Jan-08		8:07:53		69.2		38.5		7-Mar-08		8:25:59		68.61		44.5

		26-Jan-08		10:07:10		67.4		42		26-Jan-08		10:06:20		69.8		42		26-Jan-08		10:07:53		71.6		40.5		7-Mar-08		10:25:59		68.61		44.5

		26-Jan-08		12:07:10		68.61		41		26-Jan-08		12:06:20		69.2		42.5		26-Jan-08		12:07:53		71		43		7-Mar-08		12:25:59		68.61		45

		26-Jan-08		14:07:10		69.8		42		26-Jan-08		14:06:20		71		44		26-Jan-08		14:07:53		71		38.5		7-Mar-08		14:25:59		68.61		45

		26-Jan-08		16:07:10		70.41		43.5		26-Jan-08		16:06:20		70.41		46.5		26-Jan-08		16:07:53		70.41		44.5		7-Mar-08		16:25:59		68.61		44

		26-Jan-08		18:07:10		69.8		42.5		26-Jan-08		18:06:20		68.61		45.5		26-Jan-08		18:07:53		69.2		44		7-Mar-08		18:25:59		68.61		44.5

		26-Jan-08		20:07:10		69.2		44.5		26-Jan-08		20:06:20		68		48		26-Jan-08		20:07:53		68.61		45.5		7-Mar-08		20:25:59		68.61		46.5

		26-Jan-08		22:07:10		68.61		46.5		26-Jan-08		22:06:20		68		49.5		26-Jan-08		22:07:53		68		47.5		7-Mar-08		22:25:59		68.61		45.5

		27-Jan-08		0:07:10		68.61		47.5		27-Jan-08		0:06:20		67.4		51		27-Jan-08		0:07:53		67.4		48		8-Mar-08		0:25:59		68.61		44.5

		27-Jan-08		2:07:10		68		48.5		27-Jan-08		2:06:20		67.4		51.5		27-Jan-08		2:07:53		67.4		48.5		8-Mar-08		2:25:59		68		45

		27-Jan-08		4:07:10		68		49		27-Jan-08		4:06:20		67.4		51		27-Jan-08		4:07:53		67.4		49		8-Mar-08		4:25:59		68		44

		27-Jan-08		6:07:10		67.4		48		27-Jan-08		6:06:20		67.4		49		27-Jan-08		6:07:53		66.81		49		8-Mar-08		6:25:59		68		45

		27-Jan-08		8:07:10		67.4		44.5		27-Jan-08		8:06:20		68		43.5		27-Jan-08		8:07:53		68		45.5		8-Mar-08		8:25:59		68.61		45

		27-Jan-08		10:07:10		67.4		40.5		27-Jan-08		10:06:20		67.4		39.5		27-Jan-08		10:07:53		68		43		8-Mar-08		10:25:59		68.61		45

		27-Jan-08		12:07:10		67.4		39.5		27-Jan-08		12:06:20		67.4		39		27-Jan-08		12:07:53		67.4		42		8-Mar-08		12:25:59		68.61		45

		27-Jan-08		14:07:10		67.4		39		27-Jan-08		14:06:20		68		38.5		27-Jan-08		14:07:53		68		42		8-Mar-08		14:25:59		68.61		45

		27-Jan-08		16:07:10		67.4		39.5		27-Jan-08		16:06:20		68		39		27-Jan-08		16:07:53		68		41		8-Mar-08		16:25:59		68.61		45

		27-Jan-08		18:07:10		68		40		27-Jan-08		18:06:20		68.61		40.5		27-Jan-08		18:07:53		68.61		41.5		8-Mar-08		18:25:59		68.61		44.5

		27-Jan-08		20:07:10		68		39.5		27-Jan-08		20:06:20		67.4		40.5		27-Jan-08		20:07:53		68		42		8-Mar-08		20:25:59		68.61		45.5

		27-Jan-08		22:07:10		67.4		41		27-Jan-08		22:06:20		67.4		42		27-Jan-08		22:07:53		67.4		42.5		8-Mar-08		22:25:59		68.61		45

		28-Jan-08		0:07:10		67.4		43.5		28-Jan-08		0:06:20		67.4		46.5		28-Jan-08		0:07:53		67.4		44		9-Mar-08		0:25:59		68		45

		28-Jan-08		2:07:10		66.81		47.5		28-Jan-08		2:06:20		67.4		49		28-Jan-08		2:07:53		66.81		46.5		9-Mar-08		2:25:59		68		45

		28-Jan-08		4:07:10		66.81		46.5		28-Jan-08		4:06:20		67.4		47		28-Jan-08		4:07:53		66.81		46.5		9-Mar-08		4:25:59		68.61		45

		28-Jan-08		6:07:10		66.81		47.5		28-Jan-08		6:06:20		67.4		48.5		28-Jan-08		6:07:53		66.81		47.5		9-Mar-08		6:25:59		68.61		44.5

		28-Jan-08		8:07:10		66.81		48.5		28-Jan-08		8:06:20		68		48.5		28-Jan-08		8:07:53		67.4		47		9-Mar-08		8:25:59		68.61		45.5

		28-Jan-08		10:07:10		66.81		49.5		28-Jan-08		10:06:20		68		49		28-Jan-08		10:07:53		67.4		47.5		9-Mar-08		10:25:59		68.61		45

		28-Jan-08		12:07:10		66.81		48		28-Jan-08		12:06:20		68		47.5		28-Jan-08		12:07:53		68		47.5		9-Mar-08		12:25:59		68.61		45.5

		28-Jan-08		14:07:10		66.81		45.5		28-Jan-08		14:06:20		68		45		28-Jan-08		14:07:53		68		46		9-Mar-08		14:25:59		68.61		45

		28-Jan-08		16:07:10		67.4		47.5		28-Jan-08		16:06:20		68		49		28-Jan-08		16:07:53		68		47.5		9-Mar-08		16:25:59		68.61		45

		28-Jan-08		18:07:10		68		48.5		28-Jan-08		18:06:20		68		49		28-Jan-08		18:07:53		67.4		48.5		9-Mar-08		18:25:59		68.61		45

		28-Jan-08		20:07:10		68		49		28-Jan-08		20:06:20		67.4		50.5		28-Jan-08		20:07:53		67.4		49		9-Mar-08		20:25:59		68.61		46

		28-Jan-08		22:07:10		67.4		40.5		28-Jan-08		22:06:20		66.81		37.5		28-Jan-08		22:07:53		66.2		41.5		9-Mar-08		22:25:59		68.61		45

		29-Jan-08		0:07:10		66.2		36.5		29-Jan-08		0:06:20		66.2		35		29-Jan-08		0:07:53		63.8		38		10-Mar-08		0:25:59		68		45

		29-Jan-08		2:07:10		65.6		36.5		29-Jan-08		2:06:20		66.81		35.5		29-Jan-08		2:07:53		63.21		39		10-Mar-08		2:25:59		68.61		45

		29-Jan-08		4:07:10		65.6		36.5		29-Jan-08		4:06:20		66.81		35		29-Jan-08		4:07:53		62.6		39.5		10-Mar-08		4:25:59		68.61		45.5

		29-Jan-08		6:07:10		65.6		36		29-Jan-08		6:06:20		66.81		35		29-Jan-08		6:07:53		66.81		36.5		10-Mar-08		6:25:59		68.61		45.5

		29-Jan-08		8:07:10		65.6		36		29-Jan-08		8:06:20		67.4		34.5		29-Jan-08		8:07:53		69.2		35		10-Mar-08		8:25:59		68		45.5

		29-Jan-08		10:07:10		66.2		37.5		29-Jan-08		10:06:20		69.8		34.5		29-Jan-08		10:07:53		70.41		36.5		10-Mar-08		10:25:59		68		45.5

		29-Jan-08		12:07:10		67.4		37.5		29-Jan-08		12:06:20		70.41		35.5		29-Jan-08		12:07:53		71		37		10-Mar-08		12:25:59		68.61		45.5

		29-Jan-08		14:07:10		68.61		35		29-Jan-08		14:06:20		71		31		29-Jan-08		14:07:53		70.41		38		10-Mar-08		14:25:59		68.61		45

		29-Jan-08		16:07:10		69.2		34.5		29-Jan-08		16:06:20		69.8		34		29-Jan-08		16:07:53		70.41		35.5		10-Mar-08		16:25:59		68.61		45.5

		29-Jan-08		18:07:10		69.8		33.5		29-Jan-08		18:06:20		69.2		34		29-Jan-08		18:07:53		69.8		35		10-Mar-08		18:25:59		68.61		45

		29-Jan-08		20:07:10		69.2		32.5		29-Jan-08		20:06:20		67.4		33.5		29-Jan-08		20:07:53		68		35		10-Mar-08		20:25:59		68.61		45

		29-Jan-08		22:07:10		68.61		32.5		29-Jan-08		22:06:20		67.4		33.5		29-Jan-08		22:07:53		66.2		35.5		10-Mar-08		22:25:59		68		45

		30-Jan-08		0:07:10		68		31.5		30-Jan-08		0:06:20		66.81		32.5		30-Jan-08		0:07:53		65.01		35.5		11-Mar-08		0:25:59		68.61		45

		30-Jan-08		2:07:10		67.4		30.5		30-Jan-08		2:06:20		66.81		30.5		30-Jan-08		2:07:53		63.21		34.5		11-Mar-08		2:25:59		68.61		45

		30-Jan-08		4:07:10		66.81		30		30-Jan-08		4:06:20		66.81		30		30-Jan-08		4:07:53		62		34		11-Mar-08		4:25:59		68.61		46

		30-Jan-08		6:07:10		66.81		31		30-Jan-08		6:06:20		66.81		31		30-Jan-08		6:07:53		67.4		31.5		11-Mar-08		6:25:59		68.61		45.5

		30-Jan-08		8:07:10		66.81		31.5		30-Jan-08		8:06:20		67.4		31.5		30-Jan-08		8:07:53		69.2		33		11-Mar-08		8:25:59		68.61		44.5

		30-Jan-08		10:07:10		67.4		33.5		30-Jan-08		10:06:20		69.8		32.5		30-Jan-08		10:07:53		70.41		35		11-Mar-08		10:25:59		68		45

		30-Jan-08		12:07:10		68.61		36		30-Jan-08		12:06:20		71		36		30-Jan-08		12:07:53		71		37.5		11-Mar-08		12:25:59		68.61		46

		30-Jan-08		14:07:10		69.8		39		30-Jan-08		14:06:20		71.6		40.5		30-Jan-08		14:07:53		71		42		11-Mar-08		14:25:59		68		49.5

		30-Jan-08		16:07:10		71.6		40.5		30-Jan-08		16:06:20		71.6		43		30-Jan-08		16:07:53		71		42		11-Mar-08		16:25:59		68.61		46

		30-Jan-08		18:07:10		71		36		30-Jan-08		18:06:20		68.61		36.5		30-Jan-08		18:07:53		69.8		38		11-Mar-08		18:25:59		68		45

		30-Jan-08		20:07:10		70.41		33		30-Jan-08		20:06:20		68		34		30-Jan-08		20:07:53		68.61		36.5		11-Mar-08		20:25:59		68.61		45

		30-Jan-08		22:07:10		69.8		31.5		30-Jan-08		22:06:20		68		32.5		30-Jan-08		22:07:53		67.4		36		11-Mar-08		22:25:59		68.61		45.5

		31-Jan-08		0:07:10		69.2		32		31-Jan-08		0:06:20		68		33.5		31-Jan-08		0:07:53		65.6		36.5		12-Mar-08		0:25:59		68.61		45

		31-Jan-08		2:07:10		68.61		33		31-Jan-08		2:06:20		68		34		31-Jan-08		2:07:53		65.01		37		12-Mar-08		2:25:59		68		45

		31-Jan-08		4:07:10		68.61		33.5		31-Jan-08		4:06:20		68		34.5		31-Jan-08		4:07:53		64.4		38		12-Mar-08		4:25:59		68		46

		31-Jan-08		6:07:10		68		33.5		31-Jan-08		6:06:20		68		34.5		31-Jan-08		6:07:53		66.81		36		12-Mar-08		6:25:59		68		45

		31-Jan-08		8:07:10		69.8		32.5		31-Jan-08		8:06:20		68		34		31-Jan-08		8:07:53		68.61		35.5		12-Mar-08		8:25:59		68.61		46

		31-Jan-08		10:07:10		71.6		33		31-Jan-08		10:06:20		71		34.5		31-Jan-08		10:07:53		71.6		36.5		12-Mar-08		10:25:59		68.61		45.5

		31-Jan-08		12:07:10		71.6		33.5		31-Jan-08		12:06:20		71		33.5		31-Jan-08		12:07:53		70.41		38		12-Mar-08		12:25:59		68		46

		31-Jan-08		14:07:10		71.6		33.5		31-Jan-08		14:06:20		71		36		31-Jan-08		14:07:53		71.6		36		12-Mar-08		14:25:59		68		46.5

		31-Jan-08		16:07:10		71.6		33.5		31-Jan-08		16:06:20		71		35.5		31-Jan-08		16:07:53		69.8		37		12-Mar-08		16:25:59		68.61		48.5

		31-Jan-08		18:07:10		71		34		31-Jan-08		18:06:20		68.61		37		31-Jan-08		18:07:53		71		36.5		12-Mar-08		18:25:59		68.61		47.5

		31-Jan-08		20:07:10		69.2		36		31-Jan-08		20:06:20		68.61		38		31-Jan-08		20:07:53		70.41		37.5		12-Mar-08		20:25:59		68.61		45.5

		31-Jan-08		22:07:10		67.4		37.5		31-Jan-08		22:06:20		68		38		31-Jan-08		22:07:53		69.2		38.5		12-Mar-08		22:25:59		68.61		45.5

		1-Feb-08		0:07:10		66.2		39		1-Feb-08		0:06:20		68		38		1-Feb-08		0:07:53		67.4		39		13-Mar-08		0:25:59		68		46

		1-Feb-08		2:07:10		65.01		40.5		1-Feb-08		2:06:20		68		38		1-Feb-08		2:07:53		66.2		40		13-Mar-08		2:25:59		68		45

		1-Feb-08		4:07:10		64.4		42		1-Feb-08		4:06:20		68		39		1-Feb-08		4:07:53		65.6		41		13-Mar-08		4:25:59		68.61		45

		1-Feb-08		6:07:10		63.8		43		1-Feb-08		6:06:20		68		39		1-Feb-08		6:07:53		66.81		40.5		13-Mar-08		6:25:59		68.61		45

		1-Feb-08		8:07:10		66.2		42		1-Feb-08		8:06:20		68		40.5		1-Feb-08		8:07:53		69.8		40		13-Mar-08		8:25:59		68.61		45.5

		1-Feb-08		10:07:10		68.61		42		1-Feb-08		10:06:20		71		41.5		1-Feb-08		10:07:53		71.6		42		13-Mar-08		10:25:59		68		45.5

		1-Feb-08		12:07:10		69.2		43		1-Feb-08		12:06:20		71		43		1-Feb-08		12:07:53		71		46		13-Mar-08		12:25:59		68.61		45

		1-Feb-08		14:07:10		69.8		45		1-Feb-08		14:06:20		71		44		1-Feb-08		14:07:53		71		40		13-Mar-08		14:25:59		68.61		47

		1-Feb-08		16:07:10		70.41		46.5		1-Feb-08		16:06:20		71		45		1-Feb-08		16:07:53		70.41		48		13-Mar-08		16:25:59		68.61		47

		1-Feb-08		18:07:10		69.2		48.5		1-Feb-08		18:06:20		69.2		50		1-Feb-08		18:07:53		70.41		48		13-Mar-08		18:25:59		68		45.5

		1-Feb-08		20:07:10		68		44.5		1-Feb-08		20:06:20		68.61		43.5		1-Feb-08		20:07:53		70.41		43.5		13-Mar-08		20:25:59		68.61		45

		1-Feb-08		22:07:10		66.81		41.5		1-Feb-08		22:06:20		68		39.5		1-Feb-08		22:07:53		69.2		41		13-Mar-08		22:25:59		68.61		45.5

		2-Feb-08		0:07:10		65.6		40		2-Feb-08		0:06:20		68		37.5		2-Feb-08		0:07:53		66.81		40		14-Mar-08		0:25:59		68.61		47.5

		2-Feb-08		2:07:10		64.4		38		2-Feb-08		2:06:20		68		34		2-Feb-08		2:07:53		64.4		39		14-Mar-08		2:25:59		68		46

		2-Feb-08		4:07:10		63.21		37.5		2-Feb-08		4:06:20		68		33		2-Feb-08		4:07:53		62.6		38		14-Mar-08		4:25:59		68		47

		2-Feb-08		6:07:10		62.6		36.5		2-Feb-08		6:06:20		68		32		2-Feb-08		6:07:53		67.4		33.5		14-Mar-08		6:25:59		68		46.5

		2-Feb-08		8:07:10		63.8		35		2-Feb-08		8:06:20		67.4		31.5		2-Feb-08		8:07:53		68		33.5		14-Mar-08		8:25:59		68.61		47.5

		2-Feb-08		10:07:10		66.2		36		2-Feb-08		10:06:20		71		33		2-Feb-08		10:07:53		70.41		35.5		14-Mar-08		10:25:59		68		48

		2-Feb-08		12:07:10		68.61		38		2-Feb-08		12:06:20		72.8		36		2-Feb-08		12:07:53		71		39.5		14-Mar-08		12:25:59		68.61		45.5

		2-Feb-08		14:07:10		69.2		38		2-Feb-08		14:06:20		71.6		36.5		2-Feb-08		14:07:53		69.8		39.5		14-Mar-08		14:25:59		68.61		45

		2-Feb-08		16:07:10		68.61		38		2-Feb-08		16:06:20		71		36.5		2-Feb-08		16:07:53		69.8		39		14-Mar-08		16:25:59		68.61		45

		2-Feb-08		18:07:10		68		37.5		2-Feb-08		18:06:20		71		35.5		2-Feb-08		18:07:53		71		39		14-Mar-08		18:25:59		68.61		45

		2-Feb-08		20:07:10		67.4		37		2-Feb-08		20:06:20		68.61		35.5		2-Feb-08		20:07:53		69.2		40		14-Mar-08		20:25:59		68.61		45

		2-Feb-08		22:07:10		66.81		36.5		2-Feb-08		22:06:20		68		34		2-Feb-08		22:07:53		67.4		44		14-Mar-08		22:25:59		68.61		45

		3-Feb-08		0:07:10		66.81		35.5		3-Feb-08		0:06:20		68		33		3-Feb-08		0:07:53		66.81		41		15-Mar-08		0:25:59		68.61		45.5

		3-Feb-08		2:07:10		66.2		35		3-Feb-08		2:06:20		68		33		3-Feb-08		2:07:53		65.6		42		15-Mar-08		2:25:59		68.61		46

		3-Feb-08		4:07:10		66.2		34.5		3-Feb-08		4:06:20		68		33		3-Feb-08		4:07:53		65.01		43		15-Mar-08		4:25:59		68.61		45.5

		3-Feb-08		6:07:10		66.2		34.5		3-Feb-08		6:06:20		68		33.5		3-Feb-08		6:07:53		64.4		44		15-Mar-08		6:25:59		68.61		46

		3-Feb-08		8:07:10		66.2		35.5		3-Feb-08		8:06:20		69.8		33		3-Feb-08		8:07:53		67.4		41.5		15-Mar-08		8:25:59		68.61		45.5

		3-Feb-08		10:07:10		66.2		36.5		3-Feb-08		10:06:20		66.81		36.5		3-Feb-08		10:07:53		67.4		42		15-Mar-08		10:25:59		68.61		45

		3-Feb-08		12:07:10		66.81		40		3-Feb-08		12:06:20		65.6		44.5		3-Feb-08		12:07:53		68		47.5		15-Mar-08		12:25:59		68.61		45

		3-Feb-08		14:07:10		66.2		43.5		3-Feb-08		14:06:20		66.2		47.5		3-Feb-08		14:07:53		67.4		49		15-Mar-08		14:25:59		68.61		44.5

		3-Feb-08		16:07:10		66.2		46		3-Feb-08		16:06:20		66.2		49		3-Feb-08		16:07:53		68		49		15-Mar-08		16:25:59		68		44.5

		3-Feb-08		18:07:10		66.2		47.5		3-Feb-08		18:06:20		66.2		50		3-Feb-08		18:07:53		68.61		51		15-Mar-08		18:25:59		68		44.5

		3-Feb-08		20:07:10		66.2		49.5		3-Feb-08		20:06:20		66.81		52		3-Feb-08		20:07:53		67.4		51.5		15-Mar-08		20:25:59		68.61		45

		3-Feb-08		22:07:10		66.2		51.5		3-Feb-08		22:06:20		66.81		53.5		3-Feb-08		22:07:53		68		54		15-Mar-08		22:25:59		68		45

		4-Feb-08		0:07:10		66.2		51.5		4-Feb-08		0:06:20		67.4		52.5		4-Feb-08		0:07:53		68		54		16-Mar-08		0:25:59		68		44.5

		4-Feb-08		2:07:10		66.2		49		4-Feb-08		2:06:20		66.81		48		4-Feb-08		2:07:53		67.4		50.5		16-Mar-08		2:25:59		68.61		44.5

		4-Feb-08		4:07:10		66.2		45		4-Feb-08		4:06:20		65.6		45		4-Feb-08		4:07:53		66.81		47.5		16-Mar-08		4:25:59		68		46

		4-Feb-08		6:07:10		65.6		43		4-Feb-08		6:06:20		65.6		44		4-Feb-08		6:07:53		66.81		47.5		16-Mar-08		6:25:59		68		39

		4-Feb-08		8:07:10		65.6		40.5		4-Feb-08		8:06:20		65.01		41		4-Feb-08		8:07:53		68		45.5		16-Mar-08		8:25:59		68.61		45.5

		4-Feb-08		10:07:10		65.6		41		4-Feb-08		10:06:20		65.6		42.5		4-Feb-08		10:07:53		68.61		45		16-Mar-08		10:25:59		68.61		45.5

		4-Feb-08		12:07:10		65.6		41.5		4-Feb-08		12:06:20		66.2		41		4-Feb-08		12:07:53		68		46		16-Mar-08		12:25:59		68.61		45.5

		4-Feb-08		14:07:10		65.6		40.5		4-Feb-08		14:06:20		66.81		38		4-Feb-08		14:07:53		68		46		16-Mar-08		14:25:59		68.61		35

		4-Feb-08		16:07:10		66.2		39		4-Feb-08		16:06:20		66.81		38		4-Feb-08		16:07:53		68		45		16-Mar-08		16:25:59		68.61		45

		4-Feb-08		18:07:10		66.2		38.5		4-Feb-08		18:06:20		66.81		36.5		4-Feb-08		18:07:53		68		45		16-Mar-08		18:25:59		68.61		45

		4-Feb-08		20:07:10		66.2		37.5		4-Feb-08		20:06:20		65.6		38		4-Feb-08		20:07:53		68		45.5		16-Mar-08		20:25:59		68.61		45

		4-Feb-08		22:07:10		65.6		37.5		4-Feb-08		22:06:20		65.6		38.5		4-Feb-08		22:07:53		67.4		46		16-Mar-08		22:25:59		68		46

		5-Feb-08		0:07:10		65.6		37		5-Feb-08		0:06:20		65.01		38		5-Feb-08		0:07:53		66.81		46.5		17-Mar-08		0:25:59		68.61		44

		5-Feb-08		2:07:10		65.6		36		5-Feb-08		2:06:20		65.6		35.5		5-Feb-08		2:07:53		66.81		46		17-Mar-08		2:25:59		68.61		44

		5-Feb-08		4:07:10		65.6		34.5		5-Feb-08		4:06:20		65.01		35		5-Feb-08		4:07:53		66.2		46		17-Mar-08		4:25:59		68.61		45

		5-Feb-08		6:07:10		65.6		33.5		5-Feb-08		6:06:20		65.01		33		5-Feb-08		6:07:53		66.81		46		17-Mar-08		6:25:59		68		43.5

		5-Feb-08		8:07:10		65.6		33		5-Feb-08		8:06:20		65.01		33.5		5-Feb-08		8:07:53		70.41		39.5		17-Mar-08		8:25:59		68.61		44

		5-Feb-08		10:07:10		65.6		34.5		5-Feb-08		10:06:20		68.61		32.5		5-Feb-08		10:07:53		71		41.5		17-Mar-08		10:25:59		68.61		43

		5-Feb-08		12:07:10		66.2		34.5		5-Feb-08		12:06:20		71		30.5		5-Feb-08		12:07:53		70.41		42.5		17-Mar-08		12:25:59		68		35.5

		5-Feb-08		14:07:10		66.81		32		5-Feb-08		14:06:20		70.41		29.5		5-Feb-08		14:07:53		71		39.5		17-Mar-08		14:25:59		68.61		27.5

		5-Feb-08		16:07:10		67.4		31		5-Feb-08		16:06:20		70.41		28.5		5-Feb-08		16:07:53		71		34.5		17-Mar-08		16:25:59		68.61		26

		5-Feb-08		18:07:10		68		34		5-Feb-08		18:06:20		69.8		29		5-Feb-08		18:07:53		70.41		37.5		17-Mar-08		18:25:59		68		34

		5-Feb-08		20:07:10		67.4		41.5		5-Feb-08		20:06:20		68		32		5-Feb-08		20:07:53		71		36		17-Mar-08		20:25:59		68		44

		5-Feb-08		22:07:10		66.81		35.5		5-Feb-08		22:06:20		67.4		33		5-Feb-08		22:07:53		69.8		39		17-Mar-08		22:25:59		68.61		44

		6-Feb-08		0:07:10		66.81		34.5		6-Feb-08		0:06:20		67.4		33.5		6-Feb-08		0:07:53		68		36.5		18-Mar-08		0:25:59		68.61		37.5

		6-Feb-08		2:07:10		66.81		34		6-Feb-08		2:06:20		67.4		33		6-Feb-08		2:07:53		66.81		36.5		18-Mar-08		2:25:59		68.61		36.5

		6-Feb-08		4:07:10		66.2		34		6-Feb-08		4:06:20		67.4		32.5		6-Feb-08		4:07:53		66.2		37		18-Mar-08		4:25:59		68		44.5

		6-Feb-08		6:07:10		66.2		33		6-Feb-08		6:06:20		68		31.5		6-Feb-08		6:07:53		67.4		36		18-Mar-08		6:25:59		68		42

		6-Feb-08		8:07:10		66.2		32		6-Feb-08		8:06:20		68		30.5		6-Feb-08		8:07:53		68		35		18-Mar-08		8:25:59		68.61		43.5

		6-Feb-08		10:07:10		66.81		34		6-Feb-08		10:06:20		69.8		31.5		6-Feb-08		10:07:53		70.41		36.5		18-Mar-08		10:25:59		68		39.5

		6-Feb-08		12:07:10		67.4		34.5		6-Feb-08		12:06:20		71		31.5		6-Feb-08		12:07:53		69.8		39.5		18-Mar-08		12:25:59		68.61		43.5

		6-Feb-08		14:07:10		67.4		34.5		6-Feb-08		14:06:20		69.2		34.5		6-Feb-08		14:07:53		71		36		18-Mar-08		14:25:59		68		40

		6-Feb-08		16:07:10		68.61		33		6-Feb-08		16:06:20		71		31		6-Feb-08		16:07:53		71		35		18-Mar-08		16:25:59		68.61		46

		6-Feb-08		18:07:10		68		37		6-Feb-08		18:06:20		69.8		33		6-Feb-08		18:07:53		71		38		18-Mar-08		18:25:59		68.61		44.5

		6-Feb-08		20:07:10		66.81		41		6-Feb-08		20:06:20		68		37.5		6-Feb-08		20:07:53		70.41		39		18-Mar-08		20:25:59		68.61		44.5

		6-Feb-08		22:07:10		66.2		44		6-Feb-08		22:06:20		67.4		38		6-Feb-08		22:07:53		69.8		39		18-Mar-08		22:25:59		68.61		44.5

		7-Feb-08		0:07:10		66.2		45		7-Feb-08		0:06:20		68		36		7-Feb-08		0:07:53		68.61		39.5		19-Mar-08		0:25:59		68		41

		7-Feb-08		2:07:10		65.6		46		7-Feb-08		2:06:20		67.4		35.5		7-Feb-08		2:07:53		67.4		40		19-Mar-08		2:25:59		68		45

		7-Feb-08		4:07:10		65.6		46		7-Feb-08		4:06:20		68		34		7-Feb-08		4:07:53		66.81		40		19-Mar-08		4:25:59		68		45

		7-Feb-08		6:07:10		65.6		46.5		7-Feb-08		6:06:20		68		33		7-Feb-08		6:07:53		66.81		39.5		19-Mar-08		6:25:59		68.61		44.5

		7-Feb-08		8:07:10		65.6		47		7-Feb-08		8:06:20		67.4		33		7-Feb-08		8:07:53		69.8		38		19-Mar-08		8:25:59		68.61		44.5

		7-Feb-08		10:07:10		65.6		46.5		7-Feb-08		10:06:20		72.21		33.5		7-Feb-08		10:07:53		71.6		37.5		19-Mar-08		10:25:59		68.61		46.5

		7-Feb-08		12:07:10		66.81		46		7-Feb-08		12:06:20		74.01		36.5		7-Feb-08		12:07:53		69.8		44.5		19-Mar-08		12:25:59		68.61		47.5

		7-Feb-08		14:07:10		67.4		46		7-Feb-08		14:06:20		71.6		34		7-Feb-08		14:07:53		71		47		19-Mar-08		14:25:59		68.61		45

		7-Feb-08		16:07:10		67.4		46		7-Feb-08		16:06:20		69.8		37		7-Feb-08		16:07:53		70.41		43.5		19-Mar-08		16:25:59		68.61		44.5

		7-Feb-08		18:07:10		67.4		46		7-Feb-08		18:06:20		69.2		34		7-Feb-08		18:07:53		70.41		41		19-Mar-08		18:25:59		68.61		47.5

		7-Feb-08		20:07:10		66.2		46.5		7-Feb-08		20:06:20		69.2		34		7-Feb-08		20:07:53		69.8		39		19-Mar-08		20:25:59		68		48

		7-Feb-08		22:07:10		66.2		47		7-Feb-08		22:06:20		66.81		36		7-Feb-08		22:07:53		69.8		38		19-Mar-08		22:25:59		68.61		45

		8-Feb-08		0:07:10		65.6		48		8-Feb-08		0:06:20		65.6		37.5		8-Feb-08		0:07:53		68.61		38.5		20-Mar-08		0:25:59		68.61		45

		8-Feb-08		2:07:10		65.01		48.5		8-Feb-08		2:06:20		65.6		37.5		8-Feb-08		2:07:53		67.4		39		20-Mar-08		2:25:59		68		40

		8-Feb-08		4:07:10		65.01		49		8-Feb-08		4:06:20		65.6		36.5		8-Feb-08		4:07:53		66.81		39.5		20-Mar-08		4:25:59		68		39

		8-Feb-08		6:07:10		65.01		49		8-Feb-08		6:06:20		65.6		36		8-Feb-08		6:07:53		66.81		39		20-Mar-08		6:25:59		68.61		38.5

		8-Feb-08		8:07:10		65.01		48.5		8-Feb-08		8:06:20		68		33.5		8-Feb-08		8:07:53		69.8		37		20-Mar-08		8:25:59		68		44.5

		8-Feb-08		10:07:10		65.01		49		8-Feb-08		10:06:20		70.41		35		8-Feb-08		10:07:53		71.6		38		20-Mar-08		10:25:59		68.61		45

		8-Feb-08		12:07:10		66.2		48		8-Feb-08		12:06:20		70.41		35.5		8-Feb-08		12:07:53		70.41		39		20-Mar-08		12:25:59		68.61		45.5

		8-Feb-08		14:07:10		66.81		48.5		8-Feb-08		14:06:20		71		38.5		8-Feb-08		14:07:53		71.6		46.5		20-Mar-08		14:25:59		68.61		46

		8-Feb-08		16:07:10		68.61		49.5		8-Feb-08		16:06:20		71		39		8-Feb-08		16:07:53		69.8		49		20-Mar-08		16:25:59		68		47

		8-Feb-08		18:07:10		68.61		44.5		8-Feb-08		18:06:20		69.8		41		8-Feb-08		18:07:53		71		47		20-Mar-08		18:25:59		68.61		45

		8-Feb-08		20:07:10		68.61		42.5		8-Feb-08		20:06:20		69.8		40.5		8-Feb-08		20:07:53		69.8		44.5		20-Mar-08		20:25:59		68.61		45

		8-Feb-08		22:07:10		68		45		8-Feb-08		22:06:20		68		44		8-Feb-08		22:07:53		70.41		42.5		20-Mar-08		22:25:59		68.61		44.5

		9-Feb-08		0:07:10		66.81		44		9-Feb-08		0:06:20		66.2		44		9-Feb-08		0:07:53		69.8		41		21-Mar-08		0:25:59		68.61		45

		9-Feb-08		2:07:10		66.2		44		9-Feb-08		2:06:20		66.2		40.5		9-Feb-08		2:07:53		68.61		40		21-Mar-08		2:25:59		68		45.5

		9-Feb-08		4:07:10		66.2		42		9-Feb-08		4:06:20		66.2		37		9-Feb-08		4:07:53		67.4		38.5		21-Mar-08		4:25:59		68		36.5

		9-Feb-08		6:07:10		65.6		40.5		9-Feb-08		6:06:20		66.2		36		9-Feb-08		6:07:53		67.4		37.5		21-Mar-08		6:25:59		68		45.5

		9-Feb-08		8:07:10		65.6		39.5		9-Feb-08		8:06:20		68		32		9-Feb-08		8:07:53		69.2		36		21-Mar-08		8:25:59		68		36

		9-Feb-08		10:07:10		66.2		40		9-Feb-08		10:06:20		71		35		9-Feb-08		10:07:53		71.6		35.5		21-Mar-08		10:25:59		67.4		46.5

		9-Feb-08		12:07:10		67.4		46.5		9-Feb-08		12:06:20		69.2		33.5		9-Feb-08		12:07:53		71		38.5		21-Mar-08		12:25:59		68.61		42

		9-Feb-08		14:07:10		69.8		47.5		9-Feb-08		14:06:20		68.61		33		9-Feb-08		14:07:53		71		34.5		21-Mar-08		14:25:59		68.61		32.5

		9-Feb-08		16:07:10		72.8		42		9-Feb-08		16:06:20		68.61		28.5		9-Feb-08		16:07:53		71		38.5		21-Mar-08		16:25:59		68		32.5

		9-Feb-08		18:07:10		71		48		9-Feb-08		18:06:20		68		29		9-Feb-08		18:07:53		70.41		35.5		21-Mar-08		18:25:59		68		42.5

		9-Feb-08		20:07:10		67.4		48.5		9-Feb-08		20:06:20		68.61		38.5		9-Feb-08		20:07:53		69.8		39.5		21-Mar-08		20:25:59		68.61		37

		9-Feb-08		22:07:10		65.6		51		9-Feb-08		22:06:20		67.4		38.5		9-Feb-08		22:07:53		69.8		38.5		21-Mar-08		22:25:59		68.61		36.5

		10-Feb-08		0:07:10		65.01		49.5		10-Feb-08		0:06:20		66.2		39		10-Feb-08		0:07:53		69.2		37.5		22-Mar-08		0:25:59		68		34.5

		10-Feb-08		2:07:10		65.01		49		10-Feb-08		2:06:20		65.6		38		10-Feb-08		2:07:53		68		37.5		22-Mar-08		2:25:59		68		42.5

		10-Feb-08		4:07:10		65.01		50		10-Feb-08		4:06:20		65.6		36.5		10-Feb-08		4:07:53		66.81		37.5		22-Mar-08		4:25:59		68		38

		10-Feb-08		6:07:10		65.01		51		10-Feb-08		6:06:20		65.6		35.5		10-Feb-08		6:07:53		66.2		38		22-Mar-08		6:25:59		68		35

		10-Feb-08		8:07:10		65.01		50		10-Feb-08		8:06:20		66.2		34		10-Feb-08		8:07:53		66.81		37		22-Mar-08		8:25:59		68		43.5

		10-Feb-08		10:07:10		65.01		49.5		10-Feb-08		10:06:20		67.4		36		10-Feb-08		10:07:53		68		37		22-Mar-08		10:25:59		68		41

		10-Feb-08		12:07:10		66.2		51		10-Feb-08		12:06:20		67.4		40.5		10-Feb-08		12:07:53		69.8		38.5		22-Mar-08		12:25:59		68.61		43.5

		10-Feb-08		14:07:10		68.61		49.5		10-Feb-08		14:06:20		68		41.5		10-Feb-08		14:07:53		70.41		41		22-Mar-08		14:25:59		68		37

		10-Feb-08		16:07:10		69.8		49		10-Feb-08		16:06:20		68		44		10-Feb-08		16:07:53		70.41		45		22-Mar-08		16:25:59		68.61		45

		10-Feb-08		18:07:10		69.8		49.5		10-Feb-08		18:06:20		68		39.5		10-Feb-08		18:07:53		70.41		42		22-Mar-08		18:25:59		68		44.5

		10-Feb-08		20:07:10		67.4		47.5		10-Feb-08		20:06:20		68.61		39.5		10-Feb-08		20:07:53		69.8		46.5		22-Mar-08		20:25:59		68		38.5

		10-Feb-08		22:07:10		66.2		49.5		10-Feb-08		22:06:20		68		39.5		10-Feb-08		22:07:53		70.41		42		22-Mar-08		22:25:59		68		38.5

		11-Feb-08		0:07:10		65.6		49.5		11-Feb-08		0:06:20		66.2		42		11-Feb-08		0:07:53		69.8		41.5		23-Mar-08		0:25:59		68		39

		11-Feb-08		2:07:10		65.01		50		11-Feb-08		2:06:20		66.2		42		11-Feb-08		2:07:53		68.61		42		23-Mar-08		2:25:59		68.61		36.5

		11-Feb-08		4:07:10		65.01		50		11-Feb-08		4:06:20		65.6		40		11-Feb-08		4:07:53		68		41.5		23-Mar-08		4:25:59		68		35.5

		11-Feb-08		6:07:10		65.01		50.5		11-Feb-08		6:06:20		65.6		38		11-Feb-08		6:07:53		67.4		42.5		23-Mar-08		6:25:59		68.61		43.5

		11-Feb-08		8:07:10		65.01		50		11-Feb-08		8:06:20		66.2		36.5		11-Feb-08		8:07:53		68		41.5		23-Mar-08		8:25:59		68		36

		11-Feb-08		10:07:10		65.01		51		11-Feb-08		10:06:20		66.81		39		11-Feb-08		10:07:53		68		42.5		23-Mar-08		10:25:59		68.61		44

		11-Feb-08		12:07:10		66.2		51.5		11-Feb-08		12:06:20		68		41.5		11-Feb-08		12:07:53		69.8		41.5		23-Mar-08		12:25:59		68		40

		11-Feb-08		14:07:10		68		51		11-Feb-08		14:06:20		67.4		43.5		11-Feb-08		14:07:53		69.8		44		23-Mar-08		14:25:59		68.61		44.5

		11-Feb-08		16:07:10		70.41		51		11-Feb-08		16:06:20		68		42		11-Feb-08		16:07:53		70.41		46.5		23-Mar-08		16:25:59		68.61		33

		11-Feb-08		18:07:10		69.8		50.5		11-Feb-08		18:06:20		68		48.5		11-Feb-08		18:07:53		70.41		46		23-Mar-08		18:25:59		68.61		44.5

		11-Feb-08		20:07:10		66.2		52		11-Feb-08		20:06:20		68.61		45.5		11-Feb-08		20:07:53		70.41		46		23-Mar-08		20:25:59		68.61		43.5

		11-Feb-08		22:07:10		65.6		52		11-Feb-08		22:06:20		67.4		44.5		11-Feb-08		22:07:53		70.41		43.5		23-Mar-08		22:25:59		68		45

		12-Feb-08		0:07:10		65.6		51.5		12-Feb-08		0:06:20		66.2		44.5		12-Feb-08		0:07:53		69.2		41.5		24-Mar-08		0:25:59		68		38.5

		12-Feb-08		2:07:10		65.01		50		12-Feb-08		2:06:20		66.2		42		12-Feb-08		2:07:53		68.61		41		24-Mar-08		2:25:59		68.61		39.5

		12-Feb-08		4:07:10		65.01		52		12-Feb-08		4:06:20		65.6		41.5		12-Feb-08		4:07:53		68		41		24-Mar-08		4:25:59		68.61		36

		12-Feb-08		6:07:10		65.01		50		12-Feb-08		6:06:20		65.6		40.5		12-Feb-08		6:07:53		67.4		41		24-Mar-08		6:25:59		68		35.5

		12-Feb-08		8:07:10		65.01		51		12-Feb-08		8:06:20		66.81		37.5		12-Feb-08		8:07:53		69.8		38		24-Mar-08		8:25:59		68.61		33.5

		12-Feb-08		10:07:10		65.6		49.5		12-Feb-08		10:06:20		71		39		12-Feb-08		10:07:53		71		41.5		24-Mar-08		10:25:59		68		37.5

		12-Feb-08		12:07:10		67.4		49.5		12-Feb-08		12:06:20		72.21		42.5		12-Feb-08		12:07:53		70.41		39.5		24-Mar-08		12:25:59		68.61		37.5

		12-Feb-08		14:07:10		70.41		50		12-Feb-08		14:06:20		72.8		41.5		12-Feb-08		14:07:53		71		44		24-Mar-08		14:25:59		68.61		38.5

		12-Feb-08		16:07:10		72.8		49.5		12-Feb-08		16:06:20		71.6		38.5		12-Feb-08		16:07:53		70.41		47.5		24-Mar-08		16:25:59		68		45

		12-Feb-08		18:07:10		71.6		49.5		12-Feb-08		18:06:20		70.41		48.5		12-Feb-08		18:07:53		70.41		50.5		24-Mar-08		18:25:59		68		42.5

		12-Feb-08		20:07:10		67.4		51		12-Feb-08		20:06:20		69.8		43.5		12-Feb-08		20:07:53		69.8		49		24-Mar-08		20:25:59		68		44.5

		12-Feb-08		22:07:10		66.2		52		12-Feb-08		22:06:20		69.2		43.5		12-Feb-08		22:07:53		70.41		45.5		24-Mar-08		22:25:59		68.61		40

		13-Feb-08		0:07:10		66.2		48.5		13-Feb-08		0:06:20		68.61		42.5		13-Feb-08		0:07:53		69.8		42.5		25-Mar-08		0:25:59		68.61		44

		13-Feb-08		2:07:10		65.6		49		13-Feb-08		2:06:20		68.61		40.5		13-Feb-08		2:07:53		69.2		41.5		25-Mar-08		2:25:59		68		38

		13-Feb-08		4:07:10		65.6		48.5		13-Feb-08		4:06:20		68.61		38		13-Feb-08		4:07:53		68.61		40.5		25-Mar-08		4:25:59		68.61		44.5

		13-Feb-08		6:07:10		65.6		50.5		13-Feb-08		6:06:20		68.61		36.5		13-Feb-08		6:07:53		67.4		41		25-Mar-08		6:25:59		68		37.5

		13-Feb-08		8:07:10		65.6		50		13-Feb-08		8:06:20		69.2		36.5		13-Feb-08		8:07:53		69.8		40		25-Mar-08		8:25:59		68		38

		13-Feb-08		10:07:10		66.2		50.5		13-Feb-08		10:06:20		70.41		37.5		13-Feb-08		10:07:53		71.6		42		25-Mar-08		10:25:59		67.4		42.5

		13-Feb-08		12:07:10		67.4		50.5		13-Feb-08		12:06:20		71		43		13-Feb-08		12:07:53		71		47		25-Mar-08		12:25:59		68		44.5

		13-Feb-08		14:07:10		73.4		46		13-Feb-08		14:06:20		71.6		43.5		13-Feb-08		14:07:53		71		52.5		25-Mar-08		14:25:59		68		46

		13-Feb-08		16:07:10		73.4		48.5		13-Feb-08		16:06:20		71.6		40		13-Feb-08		16:07:53		71		50.5		25-Mar-08		16:25:59		68		45.5

		13-Feb-08		18:07:10		71		48		13-Feb-08		18:06:20		70.41		45		13-Feb-08		18:07:53		70.41		47		25-Mar-08		18:25:59		68		44

		13-Feb-08		20:07:10		66.2		53		13-Feb-08		20:06:20		69.8		44		13-Feb-08		20:07:53		70.41		42.5		25-Mar-08		20:25:59		68		42.5

		13-Feb-08		22:07:10		65.6		53		13-Feb-08		22:06:20		69.2		43.5		13-Feb-08		22:07:53		70.41		44		25-Mar-08		22:25:59		68.61		41.5

		14-Feb-08		0:07:10		65.6		50.5		14-Feb-08		0:06:20		68.61		41		14-Feb-08		0:07:53		70.41		42		26-Mar-08		0:25:59		68.61		40.5

		14-Feb-08		2:07:10		65.01		51		14-Feb-08		2:06:20		68.61		39		14-Feb-08		2:07:53		69.2		40		26-Mar-08		2:25:59		68.61		40

		14-Feb-08		4:07:10		65.01		49		14-Feb-08		4:06:20		68.61		39		14-Feb-08		4:07:53		68.61		40.5		26-Mar-08		4:25:59		68.61		39

		14-Feb-08		6:07:10		65.01		51		14-Feb-08		6:06:20		68.61		38.5		14-Feb-08		6:07:53		68		40.5		26-Mar-08		6:25:59		68.61		40

		14-Feb-08		8:07:10		65.6		49.5		14-Feb-08		8:06:20		68.61		37		14-Feb-08		8:07:53		71		40		26-Mar-08		8:25:59		68		41.5

		14-Feb-08		10:07:10		67.4		46.5		14-Feb-08		10:06:20		69.8		30		14-Feb-08		10:07:53		70.41		39		26-Mar-08		10:25:59		68		42.5

		14-Feb-08		12:07:10		68		46.5		14-Feb-08		12:06:20		70.41		30.5		14-Feb-08		12:07:53		71		33		26-Mar-08		12:25:59		68.61		43.5

		14-Feb-08		14:07:10		66.2		46.5		14-Feb-08		14:06:20		72.21		28.5		14-Feb-08		14:07:53		71		38.5		26-Mar-08		14:25:59		68		43

		14-Feb-08		16:07:10		65.6		47		14-Feb-08		16:06:20		72.8		24		14-Feb-08		16:07:53		71		37.5		26-Mar-08		16:25:59		68		42

		14-Feb-08		18:07:10		65.01		49		14-Feb-08		18:06:20		71.6		16.5		14-Feb-08		18:07:53		71		30.5		26-Mar-08		18:25:59		68		40.5

		14-Feb-08		20:07:10		64.4		47		14-Feb-08		20:06:20		71		17		14-Feb-08		20:07:53		70.41		30		26-Mar-08		20:25:59		68.61		38

		14-Feb-08		22:07:10		64.4		49		14-Feb-08		22:06:20		70.41		27.5		14-Feb-08		22:07:53		71		32		26-Mar-08		22:25:59		68		37.5

		15-Feb-08		0:07:10		64.4		49		15-Feb-08		0:06:20		70.41		26		15-Feb-08		0:07:53		70.41		32		27-Mar-08		0:25:59		68		38

		15-Feb-08		2:07:10		64.4		46.5		15-Feb-08		2:06:20		70.41		23.5		15-Feb-08		2:07:53		69.2		31		27-Mar-08		2:25:59		67.4		37.5

		15-Feb-08		4:07:10		64.4		50.5		15-Feb-08		4:06:20		70.41		21		15-Feb-08		4:07:53		68.61		31		27-Mar-08		4:25:59		67.4		36.5

		15-Feb-08		6:07:10		64.4		49		15-Feb-08		6:06:20		70.41		19.5		15-Feb-08		6:07:53		68		30.5		27-Mar-08		6:25:59		67.4		35

		15-Feb-08		8:07:10		64.4		50.5		15-Feb-08		8:06:20		70.41		19.5		15-Feb-08		8:07:53		70.41		31		27-Mar-08		8:25:59		68		35.5

		15-Feb-08		10:07:10		65.01		33.5		15-Feb-08		10:06:20		72.21		19.5		15-Feb-08		10:07:53		71		30.5		27-Mar-08		10:25:59		67.4		37

		15-Feb-08		12:07:10		65.6		48		15-Feb-08		12:06:20		72.8		19		15-Feb-08		12:07:53		71		29.5		27-Mar-08		12:25:59		68		36.5

		15-Feb-08		14:07:10		65.6		49		15-Feb-08		14:06:20		72.8		19.5		15-Feb-08		14:07:53		71		34.5		27-Mar-08		14:25:59		68		39

		15-Feb-08		16:07:10		65.6		48.5		15-Feb-08		16:06:20		73.4		19		15-Feb-08		16:07:53		71		34		27-Mar-08		16:25:59		68		39.5

		15-Feb-08		18:07:10		65.6		49.5		15-Feb-08		18:06:20		71.6		20.5		15-Feb-08		18:07:53		70.41		32		27-Mar-08		18:25:59		68.61		37.5

		15-Feb-08		20:07:10		65.01		43.5		15-Feb-08		20:06:20		71		24.5		15-Feb-08		20:07:53		70.41		31.5		27-Mar-08		20:25:59		68.61		37

		15-Feb-08		22:07:10		65.01		49		15-Feb-08		22:06:20		70.41		26.5		15-Feb-08		22:07:53		69.8		31.5		27-Mar-08		22:25:59		68.61		34.5

		16-Feb-08		0:07:10		65.6		50		16-Feb-08		0:06:20		70.41		26.5		16-Feb-08		0:07:53		69.2		32		28-Mar-08		0:25:59		68		34.5

		16-Feb-08		2:07:10		65.01		50		16-Feb-08		2:06:20		70.41		26.5		16-Feb-08		2:07:53		68.61		33		28-Mar-08		2:25:59		67.4		33

		16-Feb-08		4:07:10		65.01		51		16-Feb-08		4:06:20		70.41		27		16-Feb-08		4:07:53		68		33.5		28-Mar-08		4:25:59		66.81		31.5

		16-Feb-08		6:07:10		65.01		50		16-Feb-08		6:06:20		70.41		26.5		16-Feb-08		6:07:53		66.81		34		28-Mar-08		6:25:59		67.4		31.5

		16-Feb-08		8:07:10		65.01		51		16-Feb-08		8:06:20		70.41		27		16-Feb-08		8:07:53		69.2		33		28-Mar-08		8:25:59		68		30.5

		16-Feb-08		10:07:10		65.6		51		16-Feb-08		10:06:20		71.6		27.5		16-Feb-08		10:07:53		71.6		33.5		28-Mar-08		10:25:59		68		29

		16-Feb-08		12:07:10		65.01		50		16-Feb-08		12:06:20		73.4		28		16-Feb-08		12:07:53		70.41		39		28-Mar-08		12:25:59		68		26

		16-Feb-08		14:07:10		65.6		50		16-Feb-08		14:06:20		73.4		27		16-Feb-08		14:07:53		71		33		28-Mar-08		14:25:59		68.61		25.5

		16-Feb-08		16:07:10		65.6		51.5		16-Feb-08		16:06:20		73.4		37.5		16-Feb-08		16:07:53		71.6		36.5		28-Mar-08		16:25:59		68		23.5

		16-Feb-08		18:07:10		65.01		51		16-Feb-08		18:06:20		67.4		41		16-Feb-08		18:07:53		70.41		40		28-Mar-08		18:25:59		68.61		23.5

		16-Feb-08		20:07:10		65.01		50.5		16-Feb-08		20:06:20		66.2		43		16-Feb-08		20:07:53		71		39.5		28-Mar-08		20:25:59		68		26.5

		16-Feb-08		22:07:10		65.01		52		16-Feb-08		22:06:20		66.81		41		16-Feb-08		22:07:53		70.41		39		28-Mar-08		22:25:59		68		32.5

		17-Feb-08		0:07:10		65.01		52		17-Feb-08		0:06:20		66.2		40		17-Feb-08		0:07:53		69.8		38		29-Mar-08		0:25:59		67.4		33.5

		17-Feb-08		2:07:10		65.01		52.5		17-Feb-08		2:06:20		66.2		40.5		17-Feb-08		2:07:53		69.2		39.5		29-Mar-08		2:25:59		67.4		34

		17-Feb-08		4:07:10		65.01		53		17-Feb-08		4:06:20		66.2		41.5		17-Feb-08		4:07:53		68.61		39.5		29-Mar-08		4:25:59		66.81		34

		17-Feb-08		6:07:10		65.01		53		17-Feb-08		6:06:20		66.2		41		17-Feb-08		6:07:53		68.61		40		29-Mar-08		6:25:59		67.4		33.5

		17-Feb-08		8:07:10		65.01		52		17-Feb-08		8:06:20		65.6		40		17-Feb-08		8:07:53		70.41		39		29-Mar-08		8:25:59		68		34

		17-Feb-08		10:07:10		65.01		52		17-Feb-08		10:06:20		65.6		40.5		17-Feb-08		10:07:53		71		37.5		29-Mar-08		10:25:59		67.4		30.5

		17-Feb-08		12:07:10		65.01		52.5		17-Feb-08		12:06:20		66.81		40.5		17-Feb-08		12:07:53		71		38.5		29-Mar-08		12:25:59		68		37

		17-Feb-08		14:07:10		65.01		52		17-Feb-08		14:06:20		67.4		40.5		17-Feb-08		14:07:53		70.41		41.5		29-Mar-08		14:25:59		68		39.5

		17-Feb-08		16:07:10		65.01		53		17-Feb-08		16:06:20		68		38		17-Feb-08		16:07:53		71		43.5		29-Mar-08		16:25:59		68		42

		17-Feb-08		18:07:10		65.01		52.5		17-Feb-08		18:06:20		66.81		42.5		17-Feb-08		18:07:53		70.41		41.5		29-Mar-08		18:25:59		68		42.5

		17-Feb-08		20:07:10		65.01		52.5		17-Feb-08		20:06:20		66.81		42.5		17-Feb-08		20:07:53		69.8		40.5		29-Mar-08		20:25:59		68		43

		17-Feb-08		22:07:10		65.01		53		17-Feb-08		22:06:20		66.81		40.5		17-Feb-08		22:07:53		69.8		39		29-Mar-08		22:25:59		68		43.5

		18-Feb-08		0:07:10		65.01		52		18-Feb-08		0:06:20		66.2		39.5		18-Feb-08		0:07:53		69.2		38.5		30-Mar-08		0:25:59		68		43.5

		18-Feb-08		2:07:10		65.01		52.5		18-Feb-08		2:06:20		66.2		42.5		18-Feb-08		2:07:53		68.61		40		30-Mar-08		2:25:59		68.61		42.5

		18-Feb-08		4:07:10		65.01		52		18-Feb-08		4:06:20		65.6		41.5		18-Feb-08		4:07:53		68		40.5		30-Mar-08		4:25:59		68.61		41.5

		18-Feb-08		6:07:10		65.01		51.5		18-Feb-08		6:06:20		65.6		41.5		18-Feb-08		6:07:53		68		40.5		30-Mar-08		6:25:59		68.61		40

		18-Feb-08		8:07:10		65.01		52		18-Feb-08		8:06:20		65.6		40		18-Feb-08		8:07:53		67.4		40.5		30-Mar-08		8:25:59		68.61		39

		18-Feb-08		10:07:10		65.01		51.5		18-Feb-08		10:06:20		65.6		41		18-Feb-08		10:07:53		67.4		40.5		30-Mar-08		10:25:59		68.61		39

		18-Feb-08		12:07:10		65.01		52		18-Feb-08		12:06:20		66.2		41.5		18-Feb-08		12:07:53		67.4		41		30-Mar-08		12:25:59		68.61		40

		18-Feb-08		14:07:10		65.01		52.5		18-Feb-08		14:06:20		67.4		42		18-Feb-08		14:07:53		68.61		41.5		30-Mar-08		14:25:59		68.61		40.5

		18-Feb-08		16:07:10		65.01		53.5		18-Feb-08		16:06:20		66.81		45.5		18-Feb-08		16:07:53		69.8		42		30-Mar-08		16:25:59		68.61		40

		18-Feb-08		18:07:10		65.01		54		18-Feb-08		18:06:20		66.2		45		18-Feb-08		18:07:53		69.8		42.5		30-Mar-08		18:25:59		68.61		38.5

		18-Feb-08		20:07:10		65.01		52.5		18-Feb-08		20:06:20		66.81		41.5		18-Feb-08		20:07:53		69.2		41		30-Mar-08		20:25:59		68.61		37

		18-Feb-08		22:07:10		65.01		53		18-Feb-08		22:06:20		66.2		42.5		18-Feb-08		22:07:53		68.61		40.5		30-Mar-08		22:25:59		68.61		32.5

		19-Feb-08		0:07:10		65.01		51		19-Feb-08		0:06:20		66.2		41.5		19-Feb-08		0:07:53		68.61		41		31-Mar-08		0:25:59		68.61		32

		19-Feb-08		2:07:10		65.01		52.5		19-Feb-08		2:06:20		66.2		42.5		19-Feb-08		2:07:53		68		41.5		31-Mar-08		2:25:59		67.4		33

		19-Feb-08		4:07:10		65.01		51		19-Feb-08		4:06:20		66.2		43		19-Feb-08		4:07:53		68		41.5		31-Mar-08		4:25:59		66.81		33.5

		19-Feb-08		6:07:10		65.01		53		19-Feb-08		6:06:20		66.2		43		19-Feb-08		6:07:53		68		42		31-Mar-08		6:25:59		67.4		32.5

		19-Feb-08		8:07:10		65.01		52		19-Feb-08		8:06:20		66.81		42.5		19-Feb-08		8:07:53		68		42.5		31-Mar-08		8:25:59		68		32

		19-Feb-08		10:07:10		65.01		52.5		19-Feb-08		10:06:20		66.2		43.5		19-Feb-08		10:07:53		68.61		42.5		31-Mar-08		10:25:59		68.61		28.5

		19-Feb-08		12:07:10		65.01		52.5		19-Feb-08		12:06:20		66.2		43.5		19-Feb-08		12:07:53		69.2		42.5		31-Mar-08		12:25:59		67.4		25.5

		19-Feb-08		14:07:10		65.01		52		19-Feb-08		14:06:20		66.81		43		19-Feb-08		14:07:53		69.8		42		31-Mar-08		14:25:59		68		24

		19-Feb-08		16:07:10		65.01		52.5		19-Feb-08		16:06:20		66.2		44.5		19-Feb-08		16:07:53		69.8		42.5		31-Mar-08		16:25:59		68.61		24.5

		19-Feb-08		18:07:10		65.01		51.5		19-Feb-08		18:06:20		66.81		43		19-Feb-08		18:07:53		69.8		42		31-Mar-08		18:25:59		68		27.5

		19-Feb-08		20:07:10		65.01		52		19-Feb-08		20:06:20		66.2		43		19-Feb-08		20:07:53		69.8		41.5		31-Mar-08		20:25:59		68		27

		19-Feb-08		22:07:10		65.01		52		19-Feb-08		22:06:20		66.2		42		19-Feb-08		22:07:53		69.8		40.5		31-Mar-08		22:25:59		68		27.5

		20-Feb-08		0:07:10		65.01		52.5		20-Feb-08		0:06:20		66.81		39.5		20-Feb-08		0:07:53		69.8		40		1-Apr-08		0:25:59		67.4		29

		20-Feb-08		2:07:10		65.01		52		20-Feb-08		2:06:20		66.81		40.5		20-Feb-08		2:07:53		69.2		40		1-Apr-08		2:25:59		67.4		29

		20-Feb-08		4:07:10		65.01		52		20-Feb-08		4:06:20		66.81		40.5		20-Feb-08		4:07:53		69.2		40		1-Apr-08		4:25:59		68		28

		20-Feb-08		6:07:10		65.01		52.5		20-Feb-08		6:06:20		66.81		41		20-Feb-08		6:07:53		69.2		40.5		1-Apr-08		6:25:59		68.61		28.5

		20-Feb-08		8:07:10		65.6		51.5		20-Feb-08		8:06:20		67.4		41		20-Feb-08		8:07:53		71		41		1-Apr-08		8:25:59		68		30

		20-Feb-08		10:07:10		65.6		51.5		20-Feb-08		10:06:20		66.81		42		20-Feb-08		10:07:53		71		39.5		1-Apr-08		10:25:59		67.4		31

		20-Feb-08		12:07:10		66.2		51		20-Feb-08		12:06:20		66.81		48.5		20-Feb-08		12:07:53		71		42.5		1-Apr-08		12:25:59		68		25

		20-Feb-08		14:07:10		65.6		52.5		20-Feb-08		14:06:20		66.81		51.5		20-Feb-08		14:07:53		71		39		1-Apr-08		14:25:59		68		29.5

		20-Feb-08		16:07:10		66.81		52.5		20-Feb-08		16:06:20		67.4		48.5		20-Feb-08		16:07:53		70.41		43.5		1-Apr-08		16:25:59		68		31

		20-Feb-08		18:07:10		66.2		52		20-Feb-08		18:06:20		67.4		51.5		20-Feb-08		18:07:53		70.41		48		1-Apr-08		18:25:59		68		29.5

		20-Feb-08		20:07:10		66.2		51		20-Feb-08		20:06:20		66.2		55		20-Feb-08		20:07:53		70.41		47		1-Apr-08		20:25:59		67.4		30.5

		20-Feb-08		22:07:10		66.2		52.5		20-Feb-08		22:06:20		67.4		51.5		20-Feb-08		22:07:53		71		45.5		1-Apr-08		22:25:59		68		29.5

		21-Feb-08		0:07:10		66.2		52.5		21-Feb-08		0:06:20		67.4		50.5		21-Feb-08		0:07:53		70.41		45.5		2-Apr-08		0:25:59		68		32.5

		21-Feb-08		2:07:10		65.6		52.5		21-Feb-08		2:06:20		66.81		47		21-Feb-08		2:07:53		69.8		44		2-Apr-08		2:25:59		68		33.5

		21-Feb-08		4:07:10		65.6		52		21-Feb-08		4:06:20		66.81		47.5		21-Feb-08		4:07:53		69.2		44		2-Apr-08		4:25:59		68		33

		21-Feb-08		6:07:10		65.6		52.5		21-Feb-08		6:06:20		66.81		47		21-Feb-08		6:07:53		68.61		44.5		2-Apr-08		6:25:59		68		31

		21-Feb-08		8:07:10		66.2		52		21-Feb-08		8:06:20		67.4		47		21-Feb-08		8:07:53		71		41.5		2-Apr-08		8:25:59		68		33.5

		21-Feb-08		10:07:10		66.2		52		21-Feb-08		10:06:20		67.4		48.5		21-Feb-08		10:07:53		72.21		44.5		2-Apr-08		10:25:59		68		33

		21-Feb-08		12:07:10		65.6		51.5		21-Feb-08		12:06:20		66.81		49.5		21-Feb-08		12:07:53		70.41		48		2-Apr-08		12:25:59		68.61		33

		21-Feb-08		14:07:10		65.6		51		21-Feb-08		14:06:20		68		41		21-Feb-08		14:07:53		71.6		48.5		2-Apr-08		14:25:59		68		36.5

		21-Feb-08		16:07:10		66.81		50.5		21-Feb-08		16:06:20		68		40.5		21-Feb-08		16:07:53		71		47.5		2-Apr-08		16:25:59		68		34

		21-Feb-08		18:07:10		66.2		52		21-Feb-08		18:06:20		67.4		42.5		21-Feb-08		18:07:53		70.41		45.5		2-Apr-08		18:25:59		68		34

		21-Feb-08		20:07:10		66.2		52.5		21-Feb-08		20:06:20		66.81		44.5		21-Feb-08		20:07:53		70.41		43.5		2-Apr-08		20:25:59		68		37

		21-Feb-08		22:07:10		66.2		51.5		21-Feb-08		22:06:20		67.4		45		21-Feb-08		22:07:53		71		42.5		2-Apr-08		22:25:59		68.61		36.5

		22-Feb-08		0:07:10		66.2		49.5		22-Feb-08		0:06:20		66.81		43		22-Feb-08		0:07:53		70.41		41.5		3-Apr-08		0:25:59		68.61		36.5

		22-Feb-08		2:07:10		65.6		51.5		22-Feb-08		2:06:20		66.81		43.5		22-Feb-08		2:07:53		69.8		41		3-Apr-08		2:25:59		68		36

		22-Feb-08		4:07:10		65.6		52		22-Feb-08		4:06:20		66.81		43.5		22-Feb-08		4:07:53		69.2		41.5		3-Apr-08		4:25:59		67.4		35

		22-Feb-08		6:07:10		66.2		51.5		22-Feb-08		6:06:20		66.81		44		22-Feb-08		6:07:53		69.2		42		3-Apr-08		6:25:59		69.2		34

		22-Feb-08		8:07:10		66.2		51		22-Feb-08		8:06:20		66.2		46		22-Feb-08		8:07:53		71		44		3-Apr-08		8:25:59		67.4		36.5

		22-Feb-08		10:07:10		66.81		48		22-Feb-08		10:06:20		66.2		48		22-Feb-08		10:07:53		71.6		43		3-Apr-08		10:25:59		68		36.5

		22-Feb-08		12:07:10		66.81		48.5		22-Feb-08		12:06:20		67.4		43.5		22-Feb-08		12:07:53		71		39		3-Apr-08		12:25:59		68		37.5

		22-Feb-08		14:07:10		66.81		49		22-Feb-08		14:06:20		68		44.5		22-Feb-08		14:07:53		71		44		3-Apr-08		14:25:59		68		39

		22-Feb-08		16:07:10		66.2		50		22-Feb-08		16:06:20		68		48		22-Feb-08		16:07:53		71		40		3-Apr-08		16:25:59		68		37.5

		22-Feb-08		18:07:10		66.2		51.5		22-Feb-08		18:06:20		66.81		48		22-Feb-08		18:07:53		71		46.5		3-Apr-08		18:25:59		68.61		35

		22-Feb-08		20:07:10		66.2		49		22-Feb-08		20:06:20		67.4		49.5		22-Feb-08		20:07:53		70.41		42		3-Apr-08		20:25:59		68		35.5

		22-Feb-08		22:07:10		66.2		51		22-Feb-08		22:06:20		66.81		51.5		22-Feb-08		22:07:53		70.41		45.5		3-Apr-08		22:25:59		68.61		34

		23-Feb-08		0:07:10		65.6		50.5		23-Feb-08		0:06:20		66.81		49.5		23-Feb-08		0:07:53		70.41		44.5		4-Apr-08		0:25:59		68		34

		23-Feb-08		2:07:10		65.6		49		23-Feb-08		2:06:20		67.4		48		23-Feb-08		2:07:53		69.8		43.5		4-Apr-08		2:25:59		68		33.5

		23-Feb-08		4:07:10		65.6		49		23-Feb-08		4:06:20		67.4		46		23-Feb-08		4:07:53		69.8		43		4-Apr-08		4:25:59		68		35

		23-Feb-08		6:07:10		65.6		46.5		23-Feb-08		6:06:20		66.81		47		23-Feb-08		6:07:53		69.2		43		4-Apr-08		6:25:59		68.61		36.5

		23-Feb-08		8:07:10		66.2		48.5		23-Feb-08		8:06:20		66.2		48		23-Feb-08		8:07:53		71		40.5		4-Apr-08		8:25:59		68		38

		23-Feb-08		10:07:10		66.2		49.5		23-Feb-08		10:06:20		67.4		48		23-Feb-08		10:07:53		71.6		48.5		4-Apr-08		10:25:59		67.4		39

		23-Feb-08		12:07:10		66.81		48.5		23-Feb-08		12:06:20		67.4		47.5		23-Feb-08		12:07:53		71		49.5		4-Apr-08		12:25:59		73.4		36.5

		23-Feb-08		14:07:10		66.81		48.5		23-Feb-08		14:06:20		67.4		47		23-Feb-08		14:07:53		71		45.5		4-Apr-08		14:25:59		74.01		36

		23-Feb-08		16:07:10		66.81		44		23-Feb-08		16:06:20		68		41.5		23-Feb-08		16:07:53		71.6		45.5		4-Apr-08		16:25:59		74.6		37.5

		23-Feb-08		18:07:10		66.2		48		23-Feb-08		18:06:20		67.4		39.5		23-Feb-08		18:07:53		71		42.5		4-Apr-08		18:25:59		74.01		36.5

		23-Feb-08		20:07:10		66.2		48		23-Feb-08		20:06:20		66.81		38		23-Feb-08		20:07:53		70.41		40		4-Apr-08		20:25:59		73.4		36.5

		23-Feb-08		22:07:10		66.2		48.5		23-Feb-08		22:06:20		66.2		38.5		23-Feb-08		22:07:53		69.8		40.5		4-Apr-08		22:25:59		71.6		37

		24-Feb-08		0:07:10		65.6		49.5		24-Feb-08		0:06:20		65.01		38		24-Feb-08		0:07:53		69.2		38		5-Apr-08		0:25:59		70.41		36.5

		24-Feb-08		2:07:10		65.6		41.5		24-Feb-08		2:06:20		64.4		38		24-Feb-08		2:07:53		68		38		5-Apr-08		2:25:59		69.2		36.5

		24-Feb-08		4:07:10		65.6		48		24-Feb-08		4:06:20		63.8		37		24-Feb-08		4:07:53		66.81		37.5		5-Apr-08		4:25:59		68.61		38

		24-Feb-08		6:07:10		65.6		48		24-Feb-08		6:06:20		63.8		38		24-Feb-08		6:07:53		66.2		38.5		5-Apr-08		6:25:59		69.2		37.5

		24-Feb-08		8:07:10		66.2		48		24-Feb-08		8:06:20		64.4		38.5		24-Feb-08		8:07:53		68		38		5-Apr-08		8:25:59		70.41		38.5

		24-Feb-08		10:07:10		66.81		43		24-Feb-08		10:06:20		65.01		42		24-Feb-08		10:07:53		67.4		39.5		5-Apr-08		10:25:59		71.6		38.5

		24-Feb-08		12:07:10		66.81		47		24-Feb-08		12:06:20		66.2		42		24-Feb-08		12:07:53		68		40		5-Apr-08		12:25:59		72.8		38.5

		24-Feb-08		14:07:10		66.2		48		24-Feb-08		14:06:20		66.2		42.5		24-Feb-08		14:07:53		68		41		5-Apr-08		14:25:59		73.4		38.5

		24-Feb-08		16:07:10		66.2		48		24-Feb-08		16:06:20		65.6		44.5		24-Feb-08		16:07:53		68		42		5-Apr-08		16:25:59		74.01		38.5

		24-Feb-08		18:07:10		66.2		49		24-Feb-08		18:06:20		65.01		41.5		24-Feb-08		18:07:53		67.4		41.5		5-Apr-08		18:25:59		73.4		37.5

		24-Feb-08		20:07:10		65.6		45		24-Feb-08		20:06:20		65.6		44		24-Feb-08		20:07:53		66.81		42.5		5-Apr-08		20:25:59		72.8		37

		24-Feb-08		22:07:10		66.2		49		24-Feb-08		22:06:20		65.6		48		24-Feb-08		22:07:53		66.81		44.5		5-Apr-08		22:25:59		71.6		36.5

		25-Feb-08		0:07:10		66.2		49		25-Feb-08		0:06:20		66.2		47.5		25-Feb-08		0:07:53		67.4		45		6-Apr-08		0:25:59		69.8		36

		25-Feb-08		2:07:10		66.2		49		25-Feb-08		2:06:20		66.81		48		25-Feb-08		2:07:53		67.4		45.5		6-Apr-08		2:25:59		68		36.5

		25-Feb-08		4:07:10		66.2		49.5		25-Feb-08		4:06:20		66.81		49		25-Feb-08		4:07:53		67.4		46		6-Apr-08		4:25:59		67.4		37

		25-Feb-08		6:07:10		66.2		48		25-Feb-08		6:06:20		66.81		50		25-Feb-08		6:07:53		67.4		47		6-Apr-08		6:25:59		66.81		36.5

		25-Feb-08		8:07:10		66.2		49.5		25-Feb-08		8:06:20		66.81		51		25-Feb-08		8:07:53		67.4		48		6-Apr-08		8:25:59		66.81		36.5

		25-Feb-08		10:07:10		66.2		51.5		25-Feb-08		10:06:20		67.4		51.5		25-Feb-08		10:07:53		67.4		49.5		6-Apr-08		10:25:59		68.61		38

		25-Feb-08		12:07:10		66.2		52		25-Feb-08		12:06:20		66.81		52.5		25-Feb-08		12:07:53		68		49		6-Apr-08		12:25:59		70.41		38.5

		25-Feb-08		14:07:10		66.2		53		25-Feb-08		14:06:20		67.4		52		25-Feb-08		14:07:53		68		49.5		6-Apr-08		14:25:59		71.6		37.5

		25-Feb-08		16:07:10		66.2		49.5		25-Feb-08		16:06:20		66.2		52.5		25-Feb-08		16:07:53		68		49		6-Apr-08		16:25:59		72.21		37

		25-Feb-08		18:07:10		66.2		50.5		25-Feb-08		18:06:20		67.4		49.5		25-Feb-08		18:07:53		68		48		6-Apr-08		18:25:59		72.8		36.5

		25-Feb-08		20:07:10		66.2		50		25-Feb-08		20:06:20		67.4		47.5		25-Feb-08		20:07:53		68		47.5		6-Apr-08		20:25:59		72.21		36.5

		25-Feb-08		22:07:10		66.2		50		25-Feb-08		22:06:20		66.81		48		25-Feb-08		22:07:53		68		47		6-Apr-08		22:25:59		71		37

		26-Feb-08		0:07:10		66.2		49.5		26-Feb-08		0:06:20		66.81		49.5		26-Feb-08		0:07:53		68		47		7-Apr-08		0:25:59		69.2		37

		26-Feb-08		2:07:10		65.6		50.5		26-Feb-08		2:06:20		66.2		49		26-Feb-08		2:07:53		67.4		47		7-Apr-08		2:25:59		68.61		37.5

		26-Feb-08		4:07:10		65.6		49		26-Feb-08		4:06:20		65.6		47		26-Feb-08		4:07:53		67.4		45.5		7-Apr-08		4:25:59		67.4		37.5

		26-Feb-08		6:07:10		65.6		49		26-Feb-08		6:06:20		65.6		48		26-Feb-08		6:07:53		66.81		45.5		7-Apr-08		6:25:59		66.81		38

		26-Feb-08		8:07:10		66.2		49		26-Feb-08		8:06:20		66.2		46.5		26-Feb-08		8:07:53		69.8		44		7-Apr-08		8:25:59		66.81		38.5

		26-Feb-08		10:07:10		66.81		49		26-Feb-08		10:06:20		66.81		48.5		26-Feb-08		10:07:53		71.6		42		7-Apr-08		10:25:59		68		39.5

		26-Feb-08		12:07:10		66.81		49.5		26-Feb-08		12:06:20		67.4		46.5		26-Feb-08		12:07:53		70.41		49.5		7-Apr-08		12:25:59		68.61		40

		26-Feb-08		14:07:10		66.81		48		26-Feb-08		14:06:20		67.4		45.5		26-Feb-08		14:07:53		71.6		51		7-Apr-08		14:25:59		69.8		39

		26-Feb-08		16:07:10		66.81		47.5		26-Feb-08		16:06:20		67.4		44.5		26-Feb-08		16:07:53		71		50.5		7-Apr-08		16:25:59		70.41		37.5

		26-Feb-08		18:07:10		66.2		49		26-Feb-08		18:06:20		67.4		47		26-Feb-08		18:07:53		71		50.5		7-Apr-08		18:25:59		71		36

		26-Feb-08		20:07:10		66.2		48.5		26-Feb-08		20:06:20		66.2		48.5		26-Feb-08		20:07:53		70.41		46		7-Apr-08		20:25:59		69.8		35

		26-Feb-08		22:07:10		65.6		50		26-Feb-08		22:06:20		66.81		46		26-Feb-08		22:07:53		70.41		44.5		7-Apr-08		22:25:59		68.61		35

		27-Feb-08		0:07:10		65.6		47.5		27-Feb-08		0:06:20		66.2		45		27-Feb-08		0:07:53		69.8		41.5		8-Apr-08		0:25:59		68		35.5

		27-Feb-08		2:07:10		65.6		49		27-Feb-08		2:06:20		65.01		43.5		27-Feb-08		2:07:53		68.61		41		8-Apr-08		2:25:59		66.81		36.5

		27-Feb-08		4:07:10		66.2		49		27-Feb-08		4:06:20		65.01		43.5		27-Feb-08		4:07:53		68		41		8-Apr-08		4:25:59		66.2		37

		27-Feb-08		6:07:10		66.2		48		27-Feb-08		6:06:20		65.01		44		27-Feb-08		6:07:53		67.4		41.5		8-Apr-08		6:25:59		67.4		36

		27-Feb-08		8:07:10		66.2		47.5		27-Feb-08		8:06:20		65.6		41		27-Feb-08		8:07:53		69.8		40		8-Apr-08		8:25:59		68.61		35.5

		27-Feb-08		10:07:10		66.2		47		27-Feb-08		10:06:20		66.81		44.5		27-Feb-08		10:07:53		71.6		38		8-Apr-08		10:25:59		71.6		36

		27-Feb-08		12:07:10		66.81		48.5		27-Feb-08		12:06:20		68		44.5		27-Feb-08		12:07:53		71		40.5		8-Apr-08		12:25:59		72.8		35

		27-Feb-08		14:07:10		66.81		46.5		27-Feb-08		14:06:20		67.4		44		27-Feb-08		14:07:53		70.41		39.5		8-Apr-08		14:25:59		74.01		33.5

		27-Feb-08		16:07:10		66.81		47		27-Feb-08		16:06:20		68.61		42		27-Feb-08		16:07:53		70.41		49.5		8-Apr-08		16:25:59		74.01		35.5

		27-Feb-08		18:07:10		66.2		50		27-Feb-08		18:06:20		68		48.5		27-Feb-08		18:07:53		70.41		42.5		8-Apr-08		18:25:59		73.4		34.5

		27-Feb-08		20:07:10		66.2		49.5		27-Feb-08		20:06:20		66.81		51.5		27-Feb-08		20:07:53		70.41		42.5		8-Apr-08		20:25:59		72.8		34.5

		27-Feb-08		22:07:10		66.2		49.5		27-Feb-08		22:06:20		66.81		50		27-Feb-08		22:07:53		71		46		8-Apr-08		22:25:59		72.21		34

		28-Feb-08		0:07:10		66.2		48.5		28-Feb-08		0:06:20		66.2		49.5		28-Feb-08		0:07:53		71		43		9-Apr-08		0:25:59		70.41		35

		28-Feb-08		2:07:10		66.2		49		28-Feb-08		2:06:20		66.81		47.5		28-Feb-08		2:07:53		70.41		42.5		9-Apr-08		2:25:59		69.2		35

		28-Feb-08		4:07:10		65.6		49		28-Feb-08		4:06:20		66.2		46.5		28-Feb-08		4:07:53		69.8		41.5		9-Apr-08		4:25:59		68.61		35.5

		28-Feb-08		6:07:10		65.6		50		28-Feb-08		6:06:20		65.6		45		28-Feb-08		6:07:53		69.2		41		9-Apr-08		6:25:59		69.2		36

		28-Feb-08		8:07:10		66.2		48		28-Feb-08		8:06:20		65.6		42.5		28-Feb-08		8:07:53		70.41		41.5		9-Apr-08		8:25:59		70.41		36.5

		28-Feb-08		10:07:10		66.2		47.5		28-Feb-08		10:06:20		67.4		46		28-Feb-08		10:07:53		71		39		9-Apr-08		10:25:59		72.8		35.5

		28-Feb-08		12:07:10		66.81		49		28-Feb-08		12:06:20		68		48		28-Feb-08		12:07:53		71		41		9-Apr-08		12:25:59		74.01		35

		28-Feb-08		14:07:10		66.81		49.5		28-Feb-08		14:06:20		68.61		47		28-Feb-08		14:07:53		71		40		9-Apr-08		14:25:59		74.01		34

		28-Feb-08		16:07:10		66.81		51.5		28-Feb-08		16:06:20		67.4		56		28-Feb-08		16:07:53		71		51.5		9-Apr-08		16:25:59		74.01		34.5

		28-Feb-08		18:07:10		66.2		51.5		28-Feb-08		18:06:20		68		49.5		28-Feb-08		18:07:53		71		52		9-Apr-08		18:25:59		74.01		34.5

		28-Feb-08		20:07:10		66.2		48.5		28-Feb-08		20:06:20		66.81		53		28-Feb-08		20:07:53		71.6		47		9-Apr-08		20:25:59		72.8		33.5

		28-Feb-08		22:07:10		66.2		50		28-Feb-08		22:06:20		67.4		49.5		28-Feb-08		22:07:53		72.21		44		9-Apr-08		22:25:59		71		33.5

		29-Feb-08		0:07:10		65.6		49		29-Feb-08		0:06:20		66.81		48		29-Feb-08		0:07:53		71.6		42.5		10-Apr-08		0:25:59		69.2		33.5

		29-Feb-08		2:07:10		65.6		49		29-Feb-08		2:06:20		66.2		46		29-Feb-08		2:07:53		70.41		41.5		10-Apr-08		2:25:59		68		34.5

		29-Feb-08		4:07:10		66.2		49		29-Feb-08		4:06:20		65.01		44.5		29-Feb-08		4:07:53		69.2		40.5		10-Apr-08		4:25:59		66.81		35

		29-Feb-08		6:07:10		65.6		48.5		29-Feb-08		6:06:20		65.01		42		29-Feb-08		6:07:53		68.61		39.5		10-Apr-08		6:25:59		68		34.5

		29-Feb-08		8:07:10		66.2		48		29-Feb-08		8:06:20		65.01		40		29-Feb-08		8:07:53		71		38		10-Apr-08		8:25:59		69.2		35

		29-Feb-08		10:07:10		66.2		48		29-Feb-08		10:06:20		66.81		45.5		29-Feb-08		10:07:53		72.21		42.5		10-Apr-08		10:25:59		72.21		36

		29-Feb-08		12:07:10		66.81		48.5		29-Feb-08		12:06:20		66.81		47.5		29-Feb-08		12:07:53		71.6		47		10-Apr-08		12:25:59		74.01		35.5

		29-Feb-08		14:07:10		66.81		50.5		29-Feb-08		14:06:20		68.61		47.5		29-Feb-08		14:07:53		71		45		10-Apr-08		14:25:59		74.6		36.5

		29-Feb-08		16:07:10		66.81		51.5		29-Feb-08		16:06:20		68		45.5		29-Feb-08		16:07:53		70.41		44		10-Apr-08		16:25:59		74.01		37

		29-Feb-08		18:07:10		66.2		52		29-Feb-08		18:06:20		67.4		54		29-Feb-08		18:07:53		71		52		10-Apr-08		18:25:59		73.4		34.5

		29-Feb-08		20:07:10		66.2		49		29-Feb-08		20:06:20		67.4		48.5		29-Feb-08		20:07:53		69.8		50		10-Apr-08		20:25:59		72.8		35

		29-Feb-08		22:07:10		65.6		50		29-Feb-08		22:06:20		66.81		49.5		29-Feb-08		22:07:53		71.6		44.5		10-Apr-08		22:25:59		71.6		35

		1-Mar-08		0:07:10		65.6		48.5		1-Mar-08		0:06:20		66.81		47		1-Mar-08		0:07:53		71.6		42		11-Apr-08		0:25:59		70.41		35.5

		1-Mar-08		2:07:10		65.6		48.5		1-Mar-08		2:06:20		66.2		49		1-Mar-08		2:07:53		71		42		11-Apr-08		2:25:59		69.2		35

		1-Mar-08		4:07:10		65.6		49.5		1-Mar-08		4:06:20		66.2		48.5		1-Mar-08		4:07:53		70.41		42.5		11-Apr-08		4:25:59		68.61		35.5

		1-Mar-08		6:07:10		65.6		49		1-Mar-08		6:06:20		65.6		48		1-Mar-08		6:07:53		70.41		42.5		11-Apr-08		6:25:59		69.2		35.5

		1-Mar-08		8:07:10		66.2		48.5		1-Mar-08		8:06:20		66.2		46.5		1-Mar-08		8:07:53		71		43.5		11-Apr-08		8:25:59		71		36

		1-Mar-08		10:07:10		66.2		48.5		1-Mar-08		10:06:20		67.4		45		1-Mar-08		10:07:53		71		46		11-Apr-08		10:25:59		72.8		36.5

		1-Mar-08		12:07:10		66.81		49.5		1-Mar-08		12:06:20		66.81		49.5		1-Mar-08		12:07:53		71		48		11-Apr-08		12:25:59		74.6		36.5

		1-Mar-08		14:07:10		66.81		49		1-Mar-08		14:06:20		68		51.5		1-Mar-08		14:07:53		71		40		11-Apr-08		14:25:59		74.6		36

		1-Mar-08		16:07:10		66.81		51.5		1-Mar-08		16:06:20		68		56		1-Mar-08		16:07:53		71		51.5		11-Apr-08		16:25:59		74.6		36.5

		1-Mar-08		18:07:10		66.2		49		1-Mar-08		18:06:20		66.81		50.5		1-Mar-08		18:07:53		70.41		48.5		11-Apr-08		18:25:59		74.01		36

		1-Mar-08		20:07:10		65.6		49.5		1-Mar-08		20:06:20		66.81		49		1-Mar-08		20:07:53		69.8		46.5		11-Apr-08		20:25:59		74.01		36

		1-Mar-08		22:07:10		65.6		49		1-Mar-08		22:06:20		66.81		47		1-Mar-08		22:07:53		69.8		44		11-Apr-08		22:25:59		72.8		36.5

		2-Mar-08		0:07:10		65.6		49		2-Mar-08		0:06:20		66.81		48.5		2-Mar-08		0:07:53		69.8		43.5		12-Apr-08		0:25:59		71.6		37

		2-Mar-08		2:07:10		65.6		49		2-Mar-08		2:06:20		66.81		48.5		2-Mar-08		2:07:53		69.8		43.5		12-Apr-08		2:25:59		69.8		37

		2-Mar-08		4:07:10		65.6		49		2-Mar-08		4:06:20		66.2		48.5		2-Mar-08		4:07:53		69.2		43.5		12-Apr-08		4:25:59		69.2		37.5

		2-Mar-08		6:07:10		65.6		49		2-Mar-08		6:06:20		66.2		48		2-Mar-08		6:07:53		69.2		43.5		12-Apr-08		6:25:59		69.8		37

		2-Mar-08		8:07:10		65.6		49		2-Mar-08		8:06:20		66.81		45		2-Mar-08		8:07:53		71.6		41		12-Apr-08		8:25:59		71		37

		2-Mar-08		10:07:10		66.2		48.5		2-Mar-08		10:06:20		68		42		2-Mar-08		10:07:53		71		36.5		12-Apr-08		10:25:59		73.4		39

		2-Mar-08		12:07:10		66.2		49		2-Mar-08		12:06:20		67.4		35.5		2-Mar-08		12:07:53		70.41		40.5		12-Apr-08		12:25:59		74.6		38.5

		2-Mar-08		14:07:10		65.6		48		2-Mar-08		14:06:20		66.81		34.5		2-Mar-08		14:07:53		71		36.5		12-Apr-08		14:25:59		75.2		36.5

		2-Mar-08		16:07:10		65.6		47		2-Mar-08		16:06:20		67.4		35.5		2-Mar-08		16:07:53		70.41		35		12-Apr-08		16:25:59		74.6		36

		2-Mar-08		18:07:10		65.6		48.5		2-Mar-08		18:06:20		66.2		34.5		2-Mar-08		18:07:53		69.8		34.5		12-Apr-08		18:25:59		74.01		35

		2-Mar-08		20:07:10		65.6		47.5		2-Mar-08		20:06:20		66.2		36.5		2-Mar-08		20:07:53		69.8		35.5		12-Apr-08		20:25:59		73.4		33

		2-Mar-08		22:07:10		65.6		48		2-Mar-08		22:06:20		66.81		37.5		2-Mar-08		22:07:53		69.2		36.5		12-Apr-08		22:25:59		72.8		34.5

		3-Mar-08		0:07:10		65.6		47		3-Mar-08		0:06:20		66.2		37		3-Mar-08		0:07:53		68.61		36.5		13-Apr-08		0:25:59		71.6		35.5

		3-Mar-08		2:07:10		65.6		46.5		3-Mar-08		2:06:20		65.6		35		3-Mar-08		2:07:53		68		36.5		13-Apr-08		2:25:59		70.41		36.5

		3-Mar-08		4:07:10		65.6		49.5		3-Mar-08		4:06:20		65.01		34.5		3-Mar-08		4:07:53		67.4		36		13-Apr-08		4:25:59		69.8		36.5

		3-Mar-08		6:07:10		65.6		48.5		3-Mar-08		6:06:20		65.01		33		3-Mar-08		6:07:53		66.81		36		13-Apr-08		6:25:59		69.8		36.5

		3-Mar-08		8:07:10		66.2		47.5		3-Mar-08		8:06:20		65.01		32.5		3-Mar-08		8:07:53		67.4		34.5		13-Apr-08		8:25:59		69.8		36.5

		3-Mar-08		10:07:10		65.01		47		3-Mar-08		10:06:20		66.2		30.5		3-Mar-08		10:07:53		68		34		13-Apr-08		10:25:59		71.6		38.5

		3-Mar-08		12:07:10		65.6		48		3-Mar-08		12:06:20		67.4		27.5		3-Mar-08		12:07:53		69.2		31.5		13-Apr-08		12:25:59		74.01		37.5

		3-Mar-08		14:07:10		66.2		44.5		3-Mar-08		14:06:20		68		21.5		3-Mar-08		14:07:53		69.8		29		13-Apr-08		14:25:59		74.01		37.5

		3-Mar-08		16:07:10		66.2		44.5		3-Mar-08		16:06:20		68		19		3-Mar-08		16:07:53		69.8		29		13-Apr-08		16:25:59		72.8		38

		3-Mar-08		18:07:10		66.2		45		3-Mar-08		18:06:20		67.4		19		3-Mar-08		18:07:53		69.2		29.5		13-Apr-08		18:25:59		72.8		37.5

		3-Mar-08		20:07:10		65.6		46		3-Mar-08		20:06:20		66.81		19.5		3-Mar-08		20:07:53		70.41		28		13-Apr-08		20:25:59		72.8		37

		3-Mar-08		22:07:10		65.6		47.5		3-Mar-08		22:06:20		67.4		26		3-Mar-08		22:07:53		70.41		29.5		13-Apr-08		22:25:59		72.8		39.5

		4-Mar-08		0:07:10		65.6		48		4-Mar-08		0:06:20		66.2		34		4-Mar-08		0:07:53		69.8		32		14-Apr-08		0:25:59		71.6		39.5

		4-Mar-08		2:07:10		65.6		48.5		4-Mar-08		2:06:20		65.6		35.5		4-Mar-08		2:07:53		69.2		33.5		14-Apr-08		2:25:59		71		39

		4-Mar-08		4:07:10		65.6		46.5		4-Mar-08		4:06:20		65.01		35.5		4-Mar-08		4:07:53		68		34		14-Apr-08		4:25:59		69.8		38.5

		4-Mar-08		6:07:10		66.2		47.5		4-Mar-08		6:06:20		64.4		35		4-Mar-08		6:07:53		67.4		34.5		14-Apr-08		6:25:59		69.2		38.5

		4-Mar-08		8:07:10		66.2		47.5		4-Mar-08		8:06:20		65.01		34		4-Mar-08		8:07:53		69.2		34		14-Apr-08		8:25:59		68.61		39

		4-Mar-08		10:07:10		66.2		46		4-Mar-08		10:06:20		67.4		35.5		4-Mar-08		10:07:53		72.21		36		14-Apr-08		10:25:59		71		40.5

		4-Mar-08		12:07:10		66.81		47		4-Mar-08		12:06:20		68		34.5		4-Mar-08		12:07:53		71		40.5		14-Apr-08		12:25:59		72.8		40

		4-Mar-08		14:07:10		66.81		46		4-Mar-08		14:06:20		68		29		4-Mar-08		14:07:53		71		40		14-Apr-08		14:25:59		74.01		39

		4-Mar-08		16:07:10		66.81		47		4-Mar-08		16:06:20		68.61		31		4-Mar-08		16:07:53		70.41		37		14-Apr-08		16:25:59		74.01		39

		4-Mar-08		18:07:10		66.2		47.5		4-Mar-08		18:06:20		68		30		4-Mar-08		18:07:53		70.41		34.5		14-Apr-08		18:25:59		72.8		39.5

		4-Mar-08		20:07:10		66.2		45.5		4-Mar-08		20:06:20		67.4		30		4-Mar-08		20:07:53		69.8		34		14-Apr-08		20:25:59		72.8		40

		4-Mar-08		22:07:10		65.6		48		4-Mar-08		22:06:20		66.2		32		4-Mar-08		22:07:53		70.41		34		14-Apr-08		22:25:59		71.6		39.5

		5-Mar-08		0:07:10		65.6		47		5-Mar-08		0:06:20		67.4		33		5-Mar-08		0:07:53		71		33.5		15-Apr-08		0:25:59		71		39.5

		5-Mar-08		2:07:10		65.6		47.5		5-Mar-08		2:06:20		65.6		34.5		5-Mar-08		2:07:53		69.8		33.5		15-Apr-08		2:25:59		69.8		39

		5-Mar-08		4:07:10		65.6		48.5		5-Mar-08		4:06:20		65.01		35.5		5-Mar-08		4:07:53		68.61		33.5		15-Apr-08		4:25:59		68.61		39

		5-Mar-08		6:07:10		66.2		49		5-Mar-08		6:06:20		64.4		35		5-Mar-08		6:07:53		67.4		34		15-Apr-08		6:25:59		69.2		39

		5-Mar-08		8:07:10		66.2		47		5-Mar-08		8:06:20		65.01		34.5		5-Mar-08		8:07:53		69.8		33		15-Apr-08		8:25:59		70.41		39.5

		5-Mar-08		10:07:10		66.2		46		5-Mar-08		10:06:20		66.81		37.5		5-Mar-08		10:07:53		72.21		34.5		15-Apr-08		10:25:59		72.8		40.5

		5-Mar-08		12:07:10		66.81		46.5		5-Mar-08		12:06:20		68		38		5-Mar-08		12:07:53		71		42.5		15-Apr-08		12:25:59		74.6		38.5

		5-Mar-08		14:07:10		66.81		47		5-Mar-08		14:06:20		68		38		5-Mar-08		14:07:53		71		36.5		15-Apr-08		14:25:59		74.6		37

		5-Mar-08		16:07:10		66.81		45.5		5-Mar-08		16:06:20		68		35.5		5-Mar-08		16:07:53		70.41		37		15-Apr-08		16:25:59		74.01		36.5

		5-Mar-08		18:07:10		66.81		47.5		5-Mar-08		18:06:20		68		38.5		5-Mar-08		18:07:53		69.8		43		15-Apr-08		18:25:59		73.4		35

		5-Mar-08		20:07:10		66.2		48		5-Mar-08		20:06:20		67.4		42		5-Mar-08		20:07:53		70.41		41.5		15-Apr-08		20:25:59		72.21		34

		5-Mar-08		22:07:10		66.2		48		5-Mar-08		22:06:20		67.4		36.5		5-Mar-08		22:07:53		70.41		39		15-Apr-08		22:25:59		71		33.5

		6-Mar-08		0:07:10		65.6		48.5		6-Mar-08		0:06:20		66.2		38		6-Mar-08		0:07:53		70.41		36.5		16-Apr-08		0:25:59		69.2		33.5

		6-Mar-08		2:07:10		65.6		48.5		6-Mar-08		2:06:20		65.6		38		6-Mar-08		2:07:53		69.8		36		16-Apr-08		2:25:59		68		34

		6-Mar-08		4:07:10		65.6		48.5		6-Mar-08		4:06:20		65.01		37.5		6-Mar-08		4:07:53		68.61		36		16-Apr-08		4:25:59		67.4		35

		6-Mar-08		6:07:10		66.2		48.5		6-Mar-08		6:06:20		65.01		36		6-Mar-08		6:07:53		67.4		36		16-Apr-08		6:25:59		68		34

		6-Mar-08		8:07:10		66.2		47.5		6-Mar-08		8:06:20		65.01		35		6-Mar-08		8:07:53		70.41		34.5		16-Apr-08		8:25:59		70.41		34.5

		6-Mar-08		10:07:10		66.81		46		6-Mar-08		10:06:20		67.4		36.5		6-Mar-08		10:07:53		71.6		35		16-Apr-08		10:25:59		72.8		35

		6-Mar-08		12:07:10		66.81		46.5		6-Mar-08		12:06:20		68		34.5		6-Mar-08		12:07:53		70.41		44.5		16-Apr-08		12:25:59		74.6		34.5

		6-Mar-08		14:07:10		66.81		46.5		6-Mar-08		14:06:20		68.61		28		6-Mar-08		14:07:53		70.41		41		16-Apr-08		14:25:59		74.6		33.5

		6-Mar-08		16:07:10		66.81		43.5		6-Mar-08		16:06:20		68.61		25		6-Mar-08		16:07:53		70.41		39		16-Apr-08		16:25:59		74.01		33.5

		6-Mar-08		18:07:10		66.2		41.5		6-Mar-08		18:06:20		68		29.5		6-Mar-08		18:07:53		69.8		38.5		16-Apr-08		18:25:59		73.4		33

		6-Mar-08		20:07:10		66.2		48.5		6-Mar-08		20:06:20		66.81		37.5		6-Mar-08		20:07:53		71		37.5		16-Apr-08		20:25:59		72.8		32

		6-Mar-08		22:07:10		65.6		47		6-Mar-08		22:06:20		66.81		40		6-Mar-08		22:07:53		71.6		37		16-Apr-08		22:25:59		71.6		32

		7-Mar-08		0:07:10		65.6		48.5		7-Mar-08		0:06:20		66.2		39		7-Mar-08		0:07:53		70.41		36.5		17-Apr-08		0:25:59		69.8		32.5

		7-Mar-08		2:07:10		65.6		48.5		7-Mar-08		2:06:20		65.01		38		7-Mar-08		2:07:53		69.2		36		17-Apr-08		2:25:59		68.61		34

		7-Mar-08		4:07:10		65.6		42.5		7-Mar-08		4:06:20		64.4		37.5		7-Mar-08		4:07:53		68.61		36		17-Apr-08		4:25:59		68		34.5

		7-Mar-08		6:07:10		65.6		47		7-Mar-08		6:06:20		63.8		36.5		7-Mar-08		6:07:53		67.4		36		17-Apr-08		6:25:59		69.2		34

		7-Mar-08		8:07:10		66.2		48		7-Mar-08		8:06:20		65.01		35.5		7-Mar-08		8:07:53		70.41		35		17-Apr-08		8:25:59		71		34.5

		7-Mar-08		10:07:10		65.6		46.5		7-Mar-08		10:06:20		66.81		37.5		7-Mar-08		10:07:53		71.6		33.5		17-Apr-08		10:25:59		74.01		35

		7-Mar-08		12:07:10		66.2		48		7-Mar-08		12:06:20		67.4		39.5		7-Mar-08		12:07:53		71		39.5		17-Apr-08		12:25:59		75.2		34.5

		7-Mar-08		14:07:10		66.2		43.5		7-Mar-08		14:06:20		68		39		7-Mar-08		14:07:53		71.6		38.5		17-Apr-08		14:25:59		75.2		34.5

		7-Mar-08		16:07:10		66.81		47.5		7-Mar-08		16:06:20		68		40		7-Mar-08		16:07:53		70.41		36.5		17-Apr-08		16:25:59		74.6		34.5

		7-Mar-08		18:07:10		66.2		48		7-Mar-08		18:06:20		68		36.5		7-Mar-08		18:07:53		70.41		35		17-Apr-08		18:25:59		74.01		34

		7-Mar-08		20:07:10		66.2		48		7-Mar-08		20:06:20		66.81		40.5		7-Mar-08		20:07:53		69.8		36		17-Apr-08		20:25:59		74.01		35

		7-Mar-08		22:07:10		65.6		48.5		7-Mar-08		22:06:20		66.81		39		7-Mar-08		22:07:53		70.41		38		17-Apr-08		22:25:59		73.4		35

		8-Mar-08		0:07:10		65.6		43		8-Mar-08		0:06:20		66.2		40.5		8-Mar-08		0:07:53		69.8		37		18-Apr-08		0:25:59		71.6		35

		8-Mar-08		2:07:10		65.6		48.5		8-Mar-08		2:06:20		65.01		41.5		8-Mar-08		2:07:53		69.2		37		18-Apr-08		2:25:59		70.41		36

		8-Mar-08		4:07:10		65.6		48		8-Mar-08		4:06:20		64.4		39.5		8-Mar-08		4:07:53		68		37		18-Apr-08		4:25:59		69.2		36

		8-Mar-08		6:07:10		65.6		48.5		8-Mar-08		6:06:20		63.8		38.5		8-Mar-08		6:07:53		67.4		36.5		18-Apr-08		6:25:59		69.8		36

		8-Mar-08		8:07:10		66.2		47.5		8-Mar-08		8:06:20		65.6		37		8-Mar-08		8:07:53		69.2		36		18-Apr-08		8:25:59		71.6		36

		8-Mar-08		10:07:10		66.2		42		8-Mar-08		10:06:20		67.4		39.5		8-Mar-08		10:07:53		71		38.5		18-Apr-08		10:25:59		74.01		37.5

		8-Mar-08		12:07:10		66.2		48		8-Mar-08		12:06:20		68		38.5		8-Mar-08		12:07:53		70.41		43		18-Apr-08		12:25:59		75.2		39

		8-Mar-08		14:07:10		66.2		47		8-Mar-08		14:06:20		67.4		38.5		8-Mar-08		14:07:53		71		36		18-Apr-08		14:25:59		75.2		38

		8-Mar-08		16:07:10		66.2		48		8-Mar-08		16:06:20		67.4		40		8-Mar-08		16:07:53		70.41		42		18-Apr-08		16:25:59		75.2		38

		8-Mar-08		18:07:10		66.2		49		8-Mar-08		18:06:20		67.4		44		8-Mar-08		18:07:53		70.41		42		18-Apr-08		18:25:59		74.6		37

		8-Mar-08		20:07:10		65.6		43.5		8-Mar-08		20:06:20		66.81		41.5		8-Mar-08		20:07:53		69.8		40		18-Apr-08		20:25:59		74.6		38

		8-Mar-08		22:07:10		65.6		48.5		8-Mar-08		22:06:20		66.2		45.5		8-Mar-08		22:07:53		70.41		40.5		18-Apr-08		22:25:59		73.4		37.5

		9-Mar-08		0:07:10		65.6		48.5		9-Mar-08		0:06:20		66.81		44.5		9-Mar-08		0:07:53		70.41		40		19-Apr-08		0:25:59		71.6		37.5

		9-Mar-08		2:07:10		65.6		47		9-Mar-08		2:06:20		66.2		43.5		9-Mar-08		2:07:53		69.8		39		19-Apr-08		2:25:59		71		38.5

		9-Mar-08		4:07:10		65.6		48		9-Mar-08		4:06:20		65.01		42.5		9-Mar-08		4:07:53		69.2		38.5		19-Apr-08		4:25:59		70.41		39.5

		9-Mar-08		6:07:10		65.6		42		9-Mar-08		6:06:20		64.4		42		9-Mar-08		6:07:53		68.61		38.5		19-Apr-08		6:25:59		71.6		39.5

		9-Mar-08		8:07:10		65.6		48		9-Mar-08		8:06:20		65.01		39		9-Mar-08		8:07:53		71		37		19-Apr-08		8:25:59		72.21		39

		9-Mar-08		10:07:10		66.2		48.5		9-Mar-08		10:06:20		66.81		43.5		9-Mar-08		10:07:53		71		34.5		19-Apr-08		10:25:59		73.4		40

		9-Mar-08		12:07:10		66.2		48.5		9-Mar-08		12:06:20		67.4		43		9-Mar-08		12:07:53		71.6		46		19-Apr-08		12:25:59		74.01		40.5

		9-Mar-08		14:07:10		66.2		47.5		9-Mar-08		14:06:20		68		35		9-Mar-08		14:07:53		71		43		19-Apr-08		14:25:59		75.2		41

		9-Mar-08		16:07:10		66.2		44		9-Mar-08		16:06:20		67.4		37.5		9-Mar-08		16:07:53		71		36.5		19-Apr-08		16:25:59		74.6		39.5

		9-Mar-08		18:07:10		66.2		47.5		9-Mar-08		18:06:20		67.4		31.5		9-Mar-08		18:07:53		69.8		36		19-Apr-08		18:25:59		74.01		38.5

		9-Mar-08		20:07:10		66.2		47.5		9-Mar-08		20:06:20		67.4		44.5		9-Mar-08		20:07:53		69.8		42		19-Apr-08		20:25:59		74.01		38.5

		9-Mar-08		22:07:10		65.6		48.5		9-Mar-08		22:06:20		66.2		47.5		9-Mar-08		22:07:53		71.6		40		19-Apr-08		22:25:59		72.8		37.5

		10-Mar-08		0:07:10		65.6		48.5		10-Mar-08		0:06:20		66.81		44.5		10-Mar-08		0:07:53		71		39.5		20-Apr-08		0:25:59		71		38

		10-Mar-08		2:07:10		65.6		48		10-Mar-08		2:06:20		66.2		44.5		10-Mar-08		2:07:53		70.41		39		20-Apr-08		2:25:59		69.8		38

		10-Mar-08		4:07:10		65.6		49		10-Mar-08		4:06:20		65.01		44		10-Mar-08		4:07:53		69.8		38.5		20-Apr-08		4:25:59		68.61		37.5

		10-Mar-08		6:07:10		65.6		49.5		10-Mar-08		6:06:20		64.4		42		10-Mar-08		6:07:53		68.61		38.5		20-Apr-08		6:25:59		68		37.5

		10-Mar-08		8:07:10		65.6		48		10-Mar-08		8:06:20		63.8		40.5		10-Mar-08		8:07:53		68		38		20-Apr-08		8:25:59		67.4		36.5

		10-Mar-08		10:07:10		65.6		48		10-Mar-08		10:06:20		66.2		41.5		10-Mar-08		10:07:53		69.2		39		20-Apr-08		10:25:59		68		37.5

		10-Mar-08		12:07:10		65.6		49		10-Mar-08		12:06:20		66.81		41		10-Mar-08		12:07:53		69.8		40		20-Apr-08		12:25:59		69.2		36.5

		10-Mar-08		14:07:10		66.2		47.5		10-Mar-08		14:06:20		68		37.5		10-Mar-08		14:07:53		70.41		41		20-Apr-08		14:25:59		70.41		33.5

		10-Mar-08		16:07:10		66.2		48		10-Mar-08		16:06:20		68		34.5		10-Mar-08		16:07:53		69.8		41.5		20-Apr-08		16:25:59		70.41		33

		10-Mar-08		18:07:10		66.2		48		10-Mar-08		18:06:20		68		33.5		10-Mar-08		18:07:53		70.41		39.5		20-Apr-08		18:25:59		70.41		32

		10-Mar-08		20:07:10		66.2		48		10-Mar-08		20:06:20		67.4		43		10-Mar-08		20:07:53		71		42		20-Apr-08		20:25:59		69.8		32

		10-Mar-08		22:07:10		65.6		49		10-Mar-08		22:06:20		66.2		45		10-Mar-08		22:07:53		71.6		40.5		20-Apr-08		22:25:59		68.61		33

		11-Mar-08		0:07:10		65.6		49		11-Mar-08		0:06:20		66.81		44.5		11-Mar-08		0:07:53		71		39.5		21-Apr-08		0:25:59		67.4		33.5

		11-Mar-08		2:07:10		65.6		49		11-Mar-08		2:06:20		66.2		45		11-Mar-08		2:07:53		70.41		39.5		21-Apr-08		2:25:59		66.81		34

		11-Mar-08		4:07:10		65.6		48.5		11-Mar-08		4:06:20		65.6		45		11-Mar-08		4:07:53		69.8		39		21-Apr-08		4:25:59		65.6		35

		11-Mar-08		6:07:10		65.6		48		11-Mar-08		6:06:20		65.01		45		11-Mar-08		6:07:53		71		39.5		21-Apr-08		6:25:59		65.01		35.5

		11-Mar-08		8:07:10		66.2		48		11-Mar-08		8:06:20		66.81		43		11-Mar-08		8:07:53		71.6		35.5		21-Apr-08		8:25:59		64.4		36.5

		11-Mar-08		10:07:10		66.81		47.5		11-Mar-08		10:06:20		67.4		43.5		11-Mar-08		10:07:53		71		37		21-Apr-08		10:25:59		65.6		37.5

		11-Mar-08		12:07:10		66.2		48		11-Mar-08		12:06:20		67.4		44		11-Mar-08		12:07:53		71		43		21-Apr-08		12:25:59		66.81		36

		11-Mar-08		14:07:10		66.81		52.5		11-Mar-08		14:06:20		68.61		52		11-Mar-08		14:07:53		70.41		48.5		21-Apr-08		14:25:59		68.61		36

		11-Mar-08		16:07:10		66.2		49.5		11-Mar-08		16:06:20		67.4		49		11-Mar-08		16:07:53		70.41		53		21-Apr-08		16:25:59		69.8		34.5

		11-Mar-08		18:07:10		66.2		49		11-Mar-08		18:06:20		68		45		11-Mar-08		18:07:53		71		42		21-Apr-08		18:25:59		69.8		33

		11-Mar-08		20:07:10		65.6		48.5		11-Mar-08		20:06:20		66.81		46		11-Mar-08		20:07:53		70.41		43		21-Apr-08		20:25:59		69.2		33

		11-Mar-08		22:07:10		65.6		48.5		11-Mar-08		22:06:20		67.4		45.5		11-Mar-08		22:07:53		71		42		21-Apr-08		22:25:59		68.61		34.5

		12-Mar-08		0:07:10		65.6		49		12-Mar-08		0:06:20		66.81		45.5		12-Mar-08		0:07:53		71.6		40.5		22-Apr-08		0:25:59		67.4		34.5

		12-Mar-08		2:07:10		65.6		49		12-Mar-08		2:06:20		66.81		45		12-Mar-08		2:07:53		70.41		40.5		22-Apr-08		2:25:59		66.2		35

		12-Mar-08		4:07:10		65.6		49		12-Mar-08		4:06:20		65.6		44.5		12-Mar-08		4:07:53		69.8		39.5		22-Apr-08		4:25:59		65.6		36

		12-Mar-08		6:07:10		65.6		49		12-Mar-08		6:06:20		65.01		44		12-Mar-08		6:07:53		70.41		39.5		22-Apr-08		6:25:59		66.81		34

		12-Mar-08		8:07:10		66.2		48		12-Mar-08		8:06:20		66.2		42.5		12-Mar-08		8:07:53		71		40.5		22-Apr-08		8:25:59		68		34.5

		12-Mar-08		10:07:10		66.2		49		12-Mar-08		10:06:20		66.81		50		12-Mar-08		10:07:53		70.41		45		22-Apr-08		10:25:59		72.21		36

		12-Mar-08		12:07:10		66.2		50		12-Mar-08		12:06:20		66.81		48		12-Mar-08		12:07:53		71.6		50		22-Apr-08		12:25:59		73.4		35.5

		12-Mar-08		14:07:10		66.2		49.5		12-Mar-08		14:06:20		68		50.5		12-Mar-08		14:07:53		71		41.5		22-Apr-08		14:25:59		73.4		35.5

		12-Mar-08		16:07:10		66.2		51.5		12-Mar-08		16:06:20		66.81		59.5		12-Mar-08		16:07:53		71		50.5		22-Apr-08		16:25:59		73.4		35.5

		12-Mar-08		18:07:10		66.2		51.5		12-Mar-08		18:06:20		67.4		48.5		12-Mar-08		18:07:53		70.41		50		22-Apr-08		18:25:59		72.8		35

		12-Mar-08		20:07:10		65.6		50		12-Mar-08		20:06:20		67.4		51.5		12-Mar-08		20:07:53		70.41		48		22-Apr-08		20:25:59		72.21		34.5

		12-Mar-08		22:07:10		65.6		49		12-Mar-08		22:06:20		67.4		49		12-Mar-08		22:07:53		70.41		44.5		22-Apr-08		22:25:59		71		34

		13-Mar-08		0:07:10		65.6		49		13-Mar-08		0:06:20		66.81		47.5		13-Mar-08		0:07:53		70.41		42		23-Apr-08		0:25:59		69.8		34

		13-Mar-08		2:07:10		65.6		49		13-Mar-08		2:06:20		65.6		46		13-Mar-08		2:07:53		70.41		41		23-Apr-08		2:25:59		68.61		34.5

		13-Mar-08		4:07:10		65.6		49.5		13-Mar-08		4:06:20		65.01		47		13-Mar-08		4:07:53		69.2		41		23-Apr-08		4:25:59		67.4		35

		13-Mar-08		6:07:10		65.6		49		13-Mar-08		6:06:20		65.6		48.5		13-Mar-08		6:07:53		70.41		42.5		23-Apr-08		6:25:59		68.61		34.5

		13-Mar-08		8:07:10		66.2		48		13-Mar-08		8:06:20		67.4		46.5		13-Mar-08		8:07:53		71		44		23-Apr-08		8:25:59		70.41		34.5

		13-Mar-08		10:07:10		66.2		48		13-Mar-08		10:06:20		66.81		46.5		13-Mar-08		10:07:53		71.6		41.5		23-Apr-08		10:25:59		71.6		35.5

		13-Mar-08		12:07:10		66.2		48.5		13-Mar-08		12:06:20		66.81		47.5		13-Mar-08		12:07:53		71		43		23-Apr-08		12:25:59		72.21		37.5

		13-Mar-08		14:07:10		66.81		49		13-Mar-08		14:06:20		67.4		46.5		13-Mar-08		14:07:53		71		46.5		23-Apr-08		14:25:59		72.8		39

		13-Mar-08		16:07:10		66.81		49.5		13-Mar-08		16:06:20		67.4		52		13-Mar-08		16:07:53		70.41		41.5		23-Apr-08		16:25:59		73.4		40.5

		13-Mar-08		18:07:10		66.2		49		13-Mar-08		18:06:20		66.81		49		13-Mar-08		18:07:53		71		44.5		23-Apr-08		18:25:59		73.4		40.5

		13-Mar-08		20:07:10		66.2		48.5		13-Mar-08		20:06:20		66.2		48		13-Mar-08		20:07:53		71		43.5		23-Apr-08		20:25:59		72.8		41.5

		13-Mar-08		22:07:10		66.2		49		13-Mar-08		22:06:20		67.4		46.5		13-Mar-08		22:07:53		72.21		41.5		23-Apr-08		22:25:59		71.6		41.5

		14-Mar-08		0:07:10		66.2		49.5		14-Mar-08		0:06:20		67.4		51		14-Mar-08		0:07:53		71.6		42		24-Apr-08		0:25:59		70.41		42

		14-Mar-08		2:07:10		65.6		50.5		14-Mar-08		2:06:20		67.4		52		14-Mar-08		2:07:53		71.6		43		24-Apr-08		2:25:59		69.2		42

		14-Mar-08		4:07:10		65.6		50.5		14-Mar-08		4:06:20		66.81		53		14-Mar-08		4:07:53		71.6		43.5		24-Apr-08		4:25:59		68.61		42.5

		14-Mar-08		6:07:10		66.2		50.5		14-Mar-08		6:06:20		67.4		53.5		14-Mar-08		6:07:53		71		40.5		24-Apr-08		6:25:59		69.2		42

		14-Mar-08		8:07:10		66.2		49.5		14-Mar-08		8:06:20		66.81		52		14-Mar-08		8:07:53		70.41		50		24-Apr-08		8:25:59		71		42

		14-Mar-08		10:07:10		66.2		51		14-Mar-08		10:06:20		67.4		52.5		14-Mar-08		10:07:53		71		51.5		24-Apr-08		10:25:59		72.8		43

		14-Mar-08		12:07:10		66.2		49.5		14-Mar-08		12:06:20		68		48		14-Mar-08		12:07:53		71		50.5		24-Apr-08		12:25:59		74.01		43

		14-Mar-08		14:07:10		66.81		48.5		14-Mar-08		14:06:20		68.61		47.5		14-Mar-08		14:07:53		71		52.5		24-Apr-08		14:25:59		74.01		40.5

		14-Mar-08		16:07:10		66.2		48		14-Mar-08		16:06:20		68		45.5		14-Mar-08		16:07:53		70.41		44		24-Apr-08		16:25:59		74.01		38.5

		14-Mar-08		18:07:10		65.6		48.5		14-Mar-08		18:06:20		66.81		46		14-Mar-08		18:07:53		70.41		43		24-Apr-08		18:25:59		72.8		36.5

		14-Mar-08		20:07:10		65.6		48.5		14-Mar-08		20:06:20		67.4		45		14-Mar-08		20:07:53		69.8		43		24-Apr-08		20:25:59		72.8		36.5

		14-Mar-08		22:07:10		65.6		48.5		14-Mar-08		22:06:20		67.4		45.5		14-Mar-08		22:07:53		71		41		24-Apr-08		22:25:59		71.6		35

		15-Mar-08		0:07:10		65.6		49		15-Mar-08		0:06:20		66.2		45		15-Mar-08		0:07:53		70.41		40.5		25-Apr-08		0:25:59		69.8		35

		15-Mar-08		2:07:10		65.6		49		15-Mar-08		2:06:20		65.6		44		15-Mar-08		2:07:53		69.8		39.5		25-Apr-08		2:25:59		68		35.5

		15-Mar-08		4:07:10		65.6		49		15-Mar-08		4:06:20		65.01		42.5		15-Mar-08		4:07:53		69.2		39		25-Apr-08		4:25:59		66.81		37

		15-Mar-08		6:07:10		66.2		48.5		15-Mar-08		6:06:20		65.6		44.5		15-Mar-08		6:07:53		69.2		42		25-Apr-08		6:25:59		68		36.5

		15-Mar-08		8:07:10		66.2		47.5		15-Mar-08		8:06:20		66.2		44		15-Mar-08		8:07:53		71		42		25-Apr-08		8:25:59		69.2		36.5

		15-Mar-08		10:07:10		66.81		48		15-Mar-08		10:06:20		67.4		46.5		15-Mar-08		10:07:53		71		47		25-Apr-08		10:25:59		72.8		38.5

		15-Mar-08		12:07:10		66.2		48		15-Mar-08		12:06:20		67.4		46.5		15-Mar-08		12:07:53		71		46.5		25-Apr-08		12:25:59		74.01		37

		15-Mar-08		14:07:10		66.2		48		15-Mar-08		14:06:20		67.4		41		15-Mar-08		14:07:53		71.6		44		25-Apr-08		14:25:59		74.6		36.5

		15-Mar-08		16:07:10		66.2		47.5		15-Mar-08		16:06:20		66.81		38		15-Mar-08		16:07:53		70.41		39.5		25-Apr-08		16:25:59		74.6		37.5

		15-Mar-08		18:07:10		65.6		48		15-Mar-08		18:06:20		66.81		40		15-Mar-08		18:07:53		69.8		38.5		25-Apr-08		18:25:59		74.01		35.5

		15-Mar-08		20:07:10		65.6		42.5		15-Mar-08		20:06:20		65.6		41		15-Mar-08		20:07:53		69.8		37.5		25-Apr-08		20:25:59		74.6		35.5

		15-Mar-08		22:07:10		65.6		49		15-Mar-08		22:06:20		65.01		41.5		15-Mar-08		22:07:53		69.2		37		25-Apr-08		22:25:59		74.01		35.5

		16-Mar-08		0:07:10		65.01		49		16-Mar-08		0:06:20		64.4		42		16-Mar-08		0:07:53		68.61		38		26-Apr-08		0:25:59		72.8		35

		16-Mar-08		2:07:10		65.01		50		16-Mar-08		2:06:20		63.8		43.5		16-Mar-08		2:07:53		68		38.5		26-Apr-08		2:25:59		71		36

		16-Mar-08		4:07:10		65.01		49		16-Mar-08		4:06:20		63.21		44		16-Mar-08		4:07:53		67.4		39		26-Apr-08		4:25:59		69.8		36.5

		16-Mar-08		6:07:10		65.01		49.5		16-Mar-08		6:06:20		63.21		43		16-Mar-08		6:07:53		68		39		26-Apr-08		6:25:59		70.41		37.5

		16-Mar-08		8:07:10		65.6		48		16-Mar-08		8:06:20		62		41.5		16-Mar-08		8:07:53		70.41		36.5		26-Apr-08		8:25:59		72.21		37

		16-Mar-08		10:07:10		65.6		49		16-Mar-08		10:06:20		64.4		44		16-Mar-08		10:07:53		71.6		38.5		26-Apr-08		10:25:59		74.01		38

		16-Mar-08		12:07:10		65.6		44		16-Mar-08		12:06:20		65.6		38		16-Mar-08		12:07:53		71		34		26-Apr-08		12:25:59		75.2		37.5

		16-Mar-08		14:07:10		65.6		38		16-Mar-08		14:06:20		66.2		34.5		16-Mar-08		14:07:53		70.41		33.5		26-Apr-08		14:25:59		73.4		34

		16-Mar-08		16:07:10		65.6		46		16-Mar-08		16:06:20		67.4		33		16-Mar-08		16:07:53		69.8		31.5		26-Apr-08		16:25:59		73.4		35.5

		16-Mar-08		18:07:10		65.6		41		16-Mar-08		18:06:20		66.2		36		16-Mar-08		18:07:53		69.2		34.5		26-Apr-08		18:25:59		73.4		37

		16-Mar-08		20:07:10		65.6		44		16-Mar-08		20:06:20		65.6		40		16-Mar-08		20:07:53		69.2		37		26-Apr-08		20:25:59		73.4		37

		16-Mar-08		22:07:10		65.6		48.5		16-Mar-08		22:06:20		65.6		37.5		16-Mar-08		22:07:53		68.61		36.5		26-Apr-08		22:25:59		72.8		36.5

		17-Mar-08		0:07:10		65.6		47.5		17-Mar-08		0:06:20		65.01		36		17-Mar-08		0:07:53		68		36		27-Apr-08		0:25:59		72.21		36.5

		17-Mar-08		2:07:10		65.6		47		17-Mar-08		2:06:20		64.4		34.5		17-Mar-08		2:07:53		67.4		35		27-Apr-08		2:25:59		71		36

		17-Mar-08		4:07:10		65.6		47.5		17-Mar-08		4:06:20		64.4		34		17-Mar-08		4:07:53		66.81		35		27-Apr-08		4:25:59		70.41		36.5

		17-Mar-08		6:07:10		65.01		38		17-Mar-08		6:06:20		64.4		34.5		17-Mar-08		6:07:53		66.2		35		27-Apr-08		6:25:59		69.8		36

		17-Mar-08		8:07:10		65.01		46.5		17-Mar-08		8:06:20		63.8		34.5		17-Mar-08		8:07:53		67.4		34.5		27-Apr-08		8:25:59		69.8		37.5

		17-Mar-08		10:07:10		65.6		38.5		17-Mar-08		10:06:20		65.01		34		17-Mar-08		10:07:53		68.61		33.5		27-Apr-08		10:25:59		71		40

		17-Mar-08		12:07:10		65.6		33.5		17-Mar-08		12:06:20		67.4		30		17-Mar-08		12:07:53		69.8		31.5		27-Apr-08		12:25:59		72.8		39.5

		17-Mar-08		14:07:10		65.6		42		17-Mar-08		14:06:20		66.81		23		17-Mar-08		14:07:53		69.8		30		27-Apr-08		14:25:59		74.01		38.5

		17-Mar-08		16:07:10		65.6		40		17-Mar-08		16:06:20		66.81		22		17-Mar-08		16:07:53		69.8		29		27-Apr-08		16:25:59		73.4		40.5

		17-Mar-08		18:07:10		65.6		36.5		17-Mar-08		18:06:20		66.2		31.5		17-Mar-08		18:07:53		69.8		31		27-Apr-08		18:25:59		73.4		40.5

		17-Mar-08		20:07:10		65.6		47.5		17-Mar-08		20:06:20		66.2		34.5		17-Mar-08		20:07:53		69.8		33		27-Apr-08		20:25:59		73.4		40.5

		17-Mar-08		22:07:10		65.6		47.5		17-Mar-08		22:06:20		66.81		35		17-Mar-08		22:07:53		70.41		34		27-Apr-08		22:25:59		73.4		38.5

		18-Mar-08		0:07:10		65.6		48		18-Mar-08		0:06:20		66.2		36		18-Mar-08		0:07:53		69.8		33.5		28-Apr-08		0:25:59		72.8		37.5

		18-Mar-08		2:07:10		65.6		39		18-Mar-08		2:06:20		65.01		37		18-Mar-08		2:07:53		68.61		34		28-Apr-08		2:25:59		72.21		39.5

		18-Mar-08		4:07:10		65.6		48		18-Mar-08		4:06:20		65.01		37.5		18-Mar-08		4:07:53		68		35		28-Apr-08		4:25:59		71.6		39.5

		18-Mar-08		6:07:10		66.2		47		18-Mar-08		6:06:20		65.01		37.5		18-Mar-08		6:07:53		69.2		34.5		28-Apr-08		6:25:59		70.41		39.5

		18-Mar-08		8:07:10		66.81		42		18-Mar-08		8:06:20		66.2		36.5		18-Mar-08		8:07:53		71.6		34.5		28-Apr-08		8:25:59		69.8		39.5

		18-Mar-08		10:07:10		66.2		38.5		18-Mar-08		10:06:20		67.4		35.5		18-Mar-08		10:07:53		71.6		39.5		28-Apr-08		10:25:59		71.6		41.5

		18-Mar-08		12:07:10		66.2		42		18-Mar-08		12:06:20		66.81		34.5		18-Mar-08		12:07:53		71.6		37		28-Apr-08		12:25:59		74.01		40

		18-Mar-08		14:07:10		66.81		46		18-Mar-08		14:06:20		66.2		39		18-Mar-08		14:07:53		71.6		34.5		28-Apr-08		14:25:59		74.01		39.5

		18-Mar-08		16:07:10		66.81		47.5		18-Mar-08		16:06:20		65.6		45		18-Mar-08		16:07:53		71.6		40		28-Apr-08		16:25:59		73.4		41.5

		18-Mar-08		18:07:10		66.81		46.5		18-Mar-08		18:06:20		65.6		45.5		18-Mar-08		18:07:53		70.41		37.5		28-Apr-08		18:25:59		73.4		41

		18-Mar-08		20:07:10		66.2		47		18-Mar-08		20:06:20		65.6		47		18-Mar-08		20:07:53		70.41		42.5		28-Apr-08		20:25:59		73.4		40.5

		18-Mar-08		22:07:10		66.2		47.5		18-Mar-08		22:06:20		65.01		47		18-Mar-08		22:07:53		71.6		40.5		28-Apr-08		22:25:59		73.4		39.5

		19-Mar-08		0:07:10		65.6		48		19-Mar-08		0:06:20		65.6		44.5		19-Mar-08		0:07:53		72.21		39		29-Apr-08		0:25:59		72.8		38.5

		19-Mar-08		2:07:10		65.6		48.5		19-Mar-08		2:06:20		64.4		49.5		19-Mar-08		2:07:53		71.6		39		29-Apr-08		2:25:59		71.6		38.5

		19-Mar-08		4:07:10		65.6		48		19-Mar-08		4:06:20		65.6		46.5		19-Mar-08		4:07:53		71		39		29-Apr-08		4:25:59		70.41		38.5

		19-Mar-08		6:07:10		66.2		47		19-Mar-08		6:06:20		65.6		45.5		19-Mar-08		6:07:53		71.6		39.5		29-Apr-08		6:25:59		70.41		38

		19-Mar-08		8:07:10		66.2		47		19-Mar-08		8:06:20		65.01		47		19-Mar-08		8:07:53		70.41		38		29-Apr-08		8:25:59		69.8		39.5

		19-Mar-08		10:07:10		66.2		47		19-Mar-08		10:06:20		66.2		47		19-Mar-08		10:07:53		70.41		37.5		29-Apr-08		10:25:59		72.8		40.5

		19-Mar-08		12:07:10		66.81		48.5		19-Mar-08		12:06:20		66.2		48		19-Mar-08		12:07:53		71.6		50.5		29-Apr-08		12:25:59		73.4		42.5

		19-Mar-08		14:07:10		66.81		49		19-Mar-08		14:06:20		66.2		51		19-Mar-08		14:07:53		71		41		29-Apr-08		14:25:59		73.4		43

		19-Mar-08		16:07:10		66.81		46.5		19-Mar-08		16:06:20		66.2		44		19-Mar-08		16:07:53		71.6		42.5		29-Apr-08		16:25:59		74.01		42.5

		19-Mar-08		18:07:10		66.2		47.5		19-Mar-08		18:06:20		66.2		45		19-Mar-08		18:07:53		70.41		40		29-Apr-08		18:25:59		74.01		41

		19-Mar-08		20:07:10		66.2		49		19-Mar-08		20:06:20		65.01		51.5		19-Mar-08		20:07:53		70.41		45		29-Apr-08		20:25:59		74.6		41

		19-Mar-08		22:07:10		65.6		48		19-Mar-08		22:06:20		65.6		52.5		19-Mar-08		22:07:53		71		44.5		29-Apr-08		22:25:59		74.01		40

		20-Mar-08		0:07:10		65.6		47		20-Mar-08		0:06:20		65.01		50.5		20-Mar-08		0:07:53		71		41.5		30-Apr-08		0:25:59		72.8		36.5

		20-Mar-08		2:07:10		65.6		48.5		20-Mar-08		2:06:20		65.6		47.5		20-Mar-08		2:07:53		71		40		30-Apr-08		2:25:59		71		36

		20-Mar-08		4:07:10		65.6		48.5		20-Mar-08		4:06:20		65.01		44.5		20-Mar-08		4:07:53		70.41		39		30-Apr-08		4:25:59		70.41		36

		20-Mar-08		6:07:10		65.6		41		20-Mar-08		6:06:20		64.4		43.5		20-Mar-08		6:07:53		70.41		38.5		30-Apr-08		6:25:59		70.41		36

		20-Mar-08		8:07:10		66.2		47		20-Mar-08		8:06:20		65.6		45		20-Mar-08		8:07:53		71.6		41		30-Apr-08		8:25:59		71		36

		20-Mar-08		10:07:10		66.2		45		20-Mar-08		10:06:20		65.6		49		20-Mar-08		10:07:53		71		45.5		30-Apr-08		10:25:59		72.8		36

		20-Mar-08		12:07:10		66.2		48		20-Mar-08		12:06:20		65.01		51.5		20-Mar-08		12:07:53		69.8		47		30-Apr-08		12:25:59		72.8		34.5

		20-Mar-08		14:07:10		66.81		47.5		20-Mar-08		14:06:20		65.6		53.5		20-Mar-08		14:07:53		71		51.5		30-Apr-08		14:25:59		73.4		33.5

		20-Mar-08		16:07:10		66.2		50		20-Mar-08		16:06:20		65.6		55.5		20-Mar-08		16:07:53		69.8		50.5		30-Apr-08		16:25:59		73.4		34

		20-Mar-08		18:07:10		66.2		48.5		20-Mar-08		18:06:20		65.6		56		20-Mar-08		18:07:53		69.8		48.5		30-Apr-08		18:25:59		72.8		32

		20-Mar-08		20:07:10		65.6		48.5		20-Mar-08		20:06:20		66.2		46		20-Mar-08		20:07:53		70.41		44		30-Apr-08		20:25:59		73.4		32

		20-Mar-08		22:07:10		65.6		48.5		20-Mar-08		22:06:20		65.6		47.5		20-Mar-08		22:07:53		71		41.5		30-Apr-08		22:25:59		72.21		31

		21-Mar-08		0:07:10		65.6		43		21-Mar-08		0:06:20		65.01		44		21-Mar-08		0:07:53		70.41		40		1-May-08		0:25:59		70.41		31.5

		21-Mar-08		2:07:10		65.6		49		21-Mar-08		2:06:20		65.01		41		21-Mar-08		2:07:53		69.8		38		1-May-08		2:25:59		69.2		31

		21-Mar-08		4:07:10		65.01		39.5		21-Mar-08		4:06:20		64.4		40		21-Mar-08		4:07:53		68.61		37.5		1-May-08		4:25:59		68		31

		21-Mar-08		6:07:10		65.6		48.5		21-Mar-08		6:06:20		64.4		39		21-Mar-08		6:07:53		69.2		37		1-May-08		6:25:59		70.41		30.5

		21-Mar-08		8:07:10		65.6		37.5		21-Mar-08		8:06:20		65.01		37.5		21-Mar-08		8:07:53		71		33		1-May-08		8:25:59		69.2		30

		21-Mar-08		10:07:10		66.2		47		21-Mar-08		10:06:20		66.2		39		21-Mar-08		10:07:53		71		40		1-May-08		10:25:59		71		30

		21-Mar-08		12:07:10		66.2		42.5		21-Mar-08		12:06:20		66.2		32		21-Mar-08		12:07:53		71		37		1-May-08		12:25:59		72.8		29

		21-Mar-08		14:07:10		66.2		46		21-Mar-08		14:06:20		66.81		30.5		21-Mar-08		14:07:53		70.41		31.5		1-May-08		14:25:59		73.4		28

		21-Mar-08		16:07:10		66.2		34.5		21-Mar-08		16:06:20		66.81		33		21-Mar-08		16:07:53		70.41		35.5		1-May-08		16:25:59		72.8		28

		21-Mar-08		18:07:10		66.2		46.5		21-Mar-08		18:06:20		66.2		36		21-Mar-08		18:07:53		70.41		33.5		1-May-08		18:25:59		73.4		29

		21-Mar-08		20:07:10		65.6		40		21-Mar-08		20:06:20		65.6		37		21-Mar-08		20:07:53		70.41		36.5		1-May-08		20:25:59		73.4		29.5

		21-Mar-08		22:07:10		65.6		39		21-Mar-08		22:06:20		65.01		37.5		21-Mar-08		22:07:53		70.41		35		1-May-08		22:25:59		72.8		29.5

		22-Mar-08		0:07:10		65.6		37		22-Mar-08		0:06:20		65.6		35		22-Mar-08		0:07:53		69.8		33.5		2-May-08		0:25:59		71.6		29.5

		22-Mar-08		2:07:10		65.01		36.5		22-Mar-08		2:06:20		65.6		35.5		22-Mar-08		2:07:53		69.2		33.5		2-May-08		2:25:59		70.41		30

		22-Mar-08		4:07:10		65.01		47		22-Mar-08		4:06:20		65.6		35		22-Mar-08		4:07:53		68.61		34		2-May-08		4:25:59		69.2		30

		22-Mar-08		6:07:10		65.6		46		22-Mar-08		6:06:20		65.6		34.5		22-Mar-08		6:07:53		69.2		33.5		2-May-08		6:25:59		71		30.5

		22-Mar-08		8:07:10		65.6		36		22-Mar-08		8:06:20		65.6		34.5		22-Mar-08		8:07:53		71		32.5		2-May-08		8:25:59		69.8		31.5

		22-Mar-08		10:07:10		66.2		41.5		22-Mar-08		10:06:20		65.6		37		22-Mar-08		10:07:53		70.41		34		2-May-08		10:25:59		72.21		32

		22-Mar-08		12:07:10		66.2		42		22-Mar-08		12:06:20		66.81		33.5		22-Mar-08		12:07:53		70.41		32.5		2-May-08		12:25:59		72.8		30.5

		22-Mar-08		14:07:10		66.81		45		22-Mar-08		14:06:20		66.2		33		22-Mar-08		14:07:53		71		33		2-May-08		14:25:59		73.4		28

		22-Mar-08		16:07:10		66.2		41.5		22-Mar-08		16:06:20		65.6		40		22-Mar-08		16:07:53		71		33		2-May-08		16:25:59		74.01		30

		22-Mar-08		18:07:10		66.2		47		22-Mar-08		18:06:20		65.01		40		22-Mar-08		18:07:53		70.41		34.5		2-May-08		18:25:59		72.8		31

		22-Mar-08		20:07:10		65.6		47		22-Mar-08		20:06:20		66.2		43		22-Mar-08		20:07:53		69.8		39.5		2-May-08		20:25:59		74.01		31.5

		22-Mar-08		22:07:10		65.6		47.5		22-Mar-08		22:06:20		65.01		42.5		22-Mar-08		22:07:53		70.41		38.5		2-May-08		22:25:59		74.01		30.5

		23-Mar-08		0:07:10		65.6		47.5		23-Mar-08		0:06:20		65.6		42		23-Mar-08		0:07:53		71		37		3-May-08		0:25:59		73.4		29.5

		23-Mar-08		2:07:10		65.6		40.5		23-Mar-08		2:06:20		65.01		40		23-Mar-08		2:07:53		70.41		36.5		3-May-08		2:25:59		72.21		30.5

		23-Mar-08		4:07:10		65.6		49		23-Mar-08		4:06:20		65.01		38.5		23-Mar-08		4:07:53		69.2		35		3-May-08		4:25:59		70.41		31.5

		23-Mar-08		6:07:10		65.01		38.5		23-Mar-08		6:06:20		65.6		38		23-Mar-08		6:07:53		69.8		35.5		3-May-08		6:25:59		70.41		32

		23-Mar-08		8:07:10		65.6		46		23-Mar-08		8:06:20		65.01		37.5		23-Mar-08		8:07:53		71		34.5		3-May-08		8:25:59		70.41		33.5

		23-Mar-08		10:07:10		65.6		41.5		23-Mar-08		10:06:20		66.2		40.5		23-Mar-08		10:07:53		70.41		34.5		3-May-08		10:25:59		72.8		34.5

		23-Mar-08		12:07:10		66.2		47		23-Mar-08		12:06:20		66.2		42.5		23-Mar-08		12:07:53		69.8		34.5		3-May-08		12:25:59		73.4		34

		23-Mar-08		14:07:10		66.2		42.5		23-Mar-08		14:06:20		65.6		43		23-Mar-08		14:07:53		70.41		43.5		3-May-08		14:25:59		73.4		35.5

		23-Mar-08		16:07:10		66.2		36		23-Mar-08		16:06:20		65.6		36		23-Mar-08		16:07:53		71		38.5		3-May-08		16:25:59		74.01		35

		23-Mar-08		18:07:10		66.2		43.5		23-Mar-08		18:06:20		66.2		42		23-Mar-08		18:07:53		70.41		40		3-May-08		18:25:59		73.4		36.5

		23-Mar-08		20:07:10		65.6		44		23-Mar-08		20:06:20		65.6		45.5		23-Mar-08		20:07:53		69.8		41.5		3-May-08		20:25:59		74.01		36.5

		23-Mar-08		22:07:10		65.6		48		23-Mar-08		22:06:20		65.01		46.5		23-Mar-08		22:07:53		71		39.5		3-May-08		22:25:59		74.01		35

		24-Mar-08		0:07:10		65.6		47.5		24-Mar-08		0:06:20		65.01		44.5		24-Mar-08		0:07:53		71		37.5		4-May-08		0:25:59		72.21		34.5

		24-Mar-08		2:07:10		65.6		43		24-Mar-08		2:06:20		65.6		41		24-Mar-08		2:07:53		69.8		36		4-May-08		2:25:59		70.41		35

		24-Mar-08		4:07:10		65.6		47.5		24-Mar-08		4:06:20		65.01		39.5		24-Mar-08		4:07:53		68.61		36		4-May-08		4:25:59		69.2		34.5

		24-Mar-08		6:07:10		65.01		47.5		24-Mar-08		6:06:20		64.4		38.5		24-Mar-08		6:07:53		68		35.5		4-May-08		6:25:59		69.2		34.5

		24-Mar-08		8:07:10		65.01		36		24-Mar-08		8:06:20		63.8		36.5		24-Mar-08		8:07:53		66.81		35		4-May-08		8:25:59		69.8		35

		24-Mar-08		10:07:10		65.6		47.5		24-Mar-08		10:06:20		65.6		39		24-Mar-08		10:07:53		69.8		35		4-May-08		10:25:59		71.6		37

		24-Mar-08		12:07:10		65.6		39.5		24-Mar-08		12:06:20		66.2		38		24-Mar-08		12:07:53		70.41		36.5		4-May-08		12:25:59		73.4		37

		24-Mar-08		14:07:10		66.2		43.5		24-Mar-08		14:06:20		65.6		39		24-Mar-08		14:07:53		69.8		39		4-May-08		14:25:59		74.6		38

		24-Mar-08		16:07:10		66.2		47.5		24-Mar-08		16:06:20		65.6		45.5		24-Mar-08		16:07:53		70.41		42		4-May-08		16:25:59		74.01		38

		24-Mar-08		18:07:10		66.2		45.5		24-Mar-08		18:06:20		66.2		50		24-Mar-08		18:07:53		69.8		45		4-May-08		18:25:59		73.4		40.5

		24-Mar-08		20:07:10		65.6		47.5		24-Mar-08		20:06:20		66.2		45.5		24-Mar-08		20:07:53		71		42.5		4-May-08		20:25:59		73.4		40

		24-Mar-08		22:07:10		65.6		43		24-Mar-08		22:06:20		65.6		45		24-Mar-08		22:07:53		71.6		39.5		4-May-08		22:25:59		72.8		39

		25-Mar-08		0:07:10		65.6		42.5		25-Mar-08		0:06:20		65.01		46		25-Mar-08		0:07:53		71		38.5		5-May-08		0:25:59		71.6		38.5

		25-Mar-08		2:07:10		65.6		41		25-Mar-08		2:06:20		65.6		42		25-Mar-08		2:07:53		69.8		37.5		5-May-08		2:25:59		71		38

		25-Mar-08		4:07:10		65.6		46		25-Mar-08		4:06:20		65.6		42.5		25-Mar-08		4:07:53		69.2		37		5-May-08		4:25:59		69.8		37.5

		25-Mar-08		6:07:10		65.6		39.5		25-Mar-08		6:06:20		65.6		41		25-Mar-08		6:07:53		69.8		37.5		5-May-08		6:25:59		68.61		37.5

		25-Mar-08		8:07:10		65.6		40		25-Mar-08		8:06:20		65.6		41.5		25-Mar-08		8:07:53		71.6		37		5-May-08		8:25:59		68.61		38

		25-Mar-08		10:07:10		66.2		44.5		25-Mar-08		10:06:20		66.2		49		25-Mar-08		10:07:53		70.41		44.5		5-May-08		10:25:59		69.8		40.5

		25-Mar-08		12:07:10		66.81		46.5		25-Mar-08		12:06:20		66.2		53.5		25-Mar-08		12:07:53		71.6		38.5		5-May-08		12:25:59		71.6		41.5

		25-Mar-08		14:07:10		66.81		47.5		25-Mar-08		14:06:20		66.2		59.5		25-Mar-08		14:07:53		71		46		5-May-08		14:25:59		72.8		41.5

		25-Mar-08		16:07:10		66.81		48.5		25-Mar-08		16:06:20		65.6		53.5		25-Mar-08		16:07:53		71		49		5-May-08		16:25:59		73.4		40.5

		25-Mar-08		18:07:10		66.2		47		25-Mar-08		18:06:20		65.6		57.5		25-Mar-08		18:07:53		70.41		50.5		5-May-08		18:25:59		73.4		39.5

		25-Mar-08		20:07:10		66.2		45.5		25-Mar-08		20:06:20		65.6		55		25-Mar-08		20:07:53		70.41		51		5-May-08		20:25:59		72.8		39

		25-Mar-08		22:07:10		65.6		45		25-Mar-08		22:06:20		65.6		51		25-Mar-08		22:07:53		70.41		46		5-May-08		22:25:59		72.21		38

		26-Mar-08		0:07:10		65.6		44		26-Mar-08		0:06:20		65.6		49		26-Mar-08		0:07:53		69.8		42.5		6-May-08		0:25:59		71.6		37.5

		26-Mar-08		2:07:10		65.6		43		26-Mar-08		2:06:20		65.6		47.5		26-Mar-08		2:07:53		69.8		40.5		6-May-08		2:25:59		70.41		38

		26-Mar-08		4:07:10		65.6		42		26-Mar-08		4:06:20		65.6		45.5		26-Mar-08		4:07:53		69.8		39		6-May-08		4:25:59		69.2		37.5

		26-Mar-08		6:07:10		65.6		43		26-Mar-08		6:06:20		64.4		49.5		26-Mar-08		6:07:53		70.41		40.5		6-May-08		6:25:59		69.8		37.5

		26-Mar-08		8:07:10		66.2		44		26-Mar-08		8:06:20		65.6		50.5		26-Mar-08		8:07:53		71.6		41.5		6-May-08		8:25:59		69.8		40

		26-Mar-08		10:07:10		66.2		45		26-Mar-08		10:06:20		65.01		53		26-Mar-08		10:07:53		71		45.5		6-May-08		10:25:59		72.21		41.5

		26-Mar-08		12:07:10		66.2		46		26-Mar-08		12:06:20		65.6		53.5		26-Mar-08		12:07:53		71		49		6-May-08		12:25:59		73.4		43.5

		26-Mar-08		14:07:10		66.81		45.5		26-Mar-08		14:06:20		65.6		53.5		26-Mar-08		14:07:53		71		48.5		6-May-08		14:25:59		73.4		43

		26-Mar-08		16:07:10		66.2		44		26-Mar-08		16:06:20		66.2		50.5		26-Mar-08		16:07:53		70.41		39.5		6-May-08		16:25:59		74.01		43

		26-Mar-08		18:07:10		65.6		43		26-Mar-08		18:06:20		66.2		45		26-Mar-08		18:07:53		70.41		48		6-May-08		18:25:59		74.01		40

		26-Mar-08		20:07:10		65.6		41		26-Mar-08		20:06:20		65.6		41.5		26-Mar-08		20:07:53		70.41		43.5		6-May-08		20:25:59		73.4		40

		26-Mar-08		22:07:10		65.6		40.5		26-Mar-08		22:06:20		64.4		44		26-Mar-08		22:07:53		72.21		37.5		6-May-08		22:25:59		72.21		39.5

		27-Mar-08		0:07:10		65.6		41		27-Mar-08		0:06:20		65.6		43		27-Mar-08		0:07:53		71.6		36.5		7-May-08		0:25:59		71.6		40

		27-Mar-08		2:07:10		65.01		39.5		27-Mar-08		2:06:20		64.4		42.5		27-Mar-08		2:07:53		70.41		36		7-May-08		2:25:59		71		40

		27-Mar-08		4:07:10		65.01		38		27-Mar-08		4:06:20		63.8		41.5		27-Mar-08		4:07:53		69.8		35		7-May-08		4:25:59		69.8		40

		27-Mar-08		6:07:10		65.01		37		27-Mar-08		6:06:20		63.8		40.5		27-Mar-08		6:07:53		70.41		35		7-May-08		6:25:59		71		40.5

		27-Mar-08		8:07:10		65.6		37		27-Mar-08		8:06:20		63.8		39		27-Mar-08		8:07:53		71.6		34.5		7-May-08		8:25:59		71.6		41.5

		27-Mar-08		10:07:10		65.6		40		27-Mar-08		10:06:20		66.2		41		27-Mar-08		10:07:53		71.6		35		7-May-08		10:25:59		73.4		41

		27-Mar-08		12:07:10		65.6		39		27-Mar-08		12:06:20		69.2		36.5		27-Mar-08		12:07:53		71		42		7-May-08		12:25:59		73.4		43

		27-Mar-08		14:07:10		66.2		40		27-Mar-08		14:06:20		69.2		37		27-Mar-08		14:07:53		71		35.5		7-May-08		14:25:59		73.4		45.5

		27-Mar-08		16:07:10		65.6		43		27-Mar-08		16:06:20		68.61		41.5		27-Mar-08		16:07:53		70.41		37		7-May-08		16:25:59		73.4		44.5

		27-Mar-08		18:07:10		65.6		41		27-Mar-08		18:06:20		68.61		38		27-Mar-08		18:07:53		70.41		42		7-May-08		18:25:59		73.4		43

		27-Mar-08		20:07:10		65.6		40		27-Mar-08		20:06:20		68		38.5		27-Mar-08		20:07:53		72.8		36		7-May-08		20:25:59		74.01		42

		27-Mar-08		22:07:10		65.6		37.5		27-Mar-08		22:06:20		66.81		36		27-Mar-08		22:07:53		74.6		32		7-May-08		22:25:59		74.01		37.5

		28-Mar-08		0:07:10		65.01		36.5		28-Mar-08		0:06:20		65.6		36.5		28-Mar-08		0:07:53		71.6		32.5		8-May-08		0:25:59		73.4		37

		28-Mar-08		2:07:10		65.01		35		28-Mar-08		2:06:20		64.4		35.5		28-Mar-08		2:07:53		69.8		32		8-May-08		2:25:59		71.6		37

		28-Mar-08		4:07:10		65.01		33.5		28-Mar-08		4:06:20		63.8		35		28-Mar-08		4:07:53		68.61		31.5		8-May-08		4:25:59		70.41		37.5

		28-Mar-08		6:07:10		65.01		33		28-Mar-08		6:06:20		63.21		35		28-Mar-08		6:07:53		69.2		32		8-May-08		6:25:59		73.4		35.5

		28-Mar-08		8:07:10		65.6		32		28-Mar-08		8:06:20		64.4		34		28-Mar-08		8:07:53		70.41		32		8-May-08		8:25:59		72.8		35.5

		28-Mar-08		10:07:10		65.6		30.5		28-Mar-08		10:06:20		66.2		31		28-Mar-08		10:07:53		71		33		8-May-08		10:25:59		72.8		37.5

		28-Mar-08		12:07:10		65.6		28		28-Mar-08		12:06:20		68.61		27		28-Mar-08		12:07:53		71		29.5		8-May-08		12:25:59		72.8		38.5

		28-Mar-08		14:07:10		66.2		28		28-Mar-08		14:06:20		69.2		25.5		28-Mar-08		14:07:53		70.41		32.5		8-May-08		14:25:59		73.4		39.5

		28-Mar-08		16:07:10		66.2		23.5		28-Mar-08		16:06:20		69.2		22		28-Mar-08		16:07:53		70.41		28.5		8-May-08		16:25:59		74.01		39.5

		28-Mar-08		18:07:10		65.6		24.5		28-Mar-08		18:06:20		69.2		21		28-Mar-08		18:07:53		71		26.5		8-May-08		18:25:59		73.4		39

		28-Mar-08		20:07:10		65.6		26		28-Mar-08		20:06:20		68.61		23.5		28-Mar-08		20:07:53		71.6		26.5		8-May-08		20:25:59		74.01		39.5

		28-Mar-08		22:07:10		65.01		35		28-Mar-08		22:06:20		67.4		34		28-Mar-08		22:07:53		74.6		28.5		8-May-08		22:25:59		74.01		37.5

		29-Mar-08		0:07:10		65.01		35		29-Mar-08		0:06:20		65.6		35.5		29-Mar-08		0:07:53		72.8		29.5		9-May-08		0:25:59		72.8		37

		29-Mar-08		2:07:10		65.01		36		29-Mar-08		2:06:20		65.01		37.5		29-Mar-08		2:07:53		71		30.5		9-May-08		2:25:59		71		36.5

		29-Mar-08		4:07:10		65.01		35.5		29-Mar-08		4:06:20		64.4		37.5		29-Mar-08		4:07:53		69.8		31		9-May-08		4:25:59		69.2		36.5

		29-Mar-08		6:07:10		65.6		34.5		29-Mar-08		6:06:20		64.4		37		29-Mar-08		6:07:53		70.41		33		9-May-08		6:25:59		72.8		35.5

		29-Mar-08		8:07:10		65.01		36.5		29-Mar-08		8:06:20		65.6		37.5		29-Mar-08		8:07:53		70.41		35		9-May-08		8:25:59		73.4		36.5

		29-Mar-08		10:07:10		65.6		32		29-Mar-08		10:06:20		68		32.5		29-Mar-08		10:07:53		70.41		35.5		9-May-08		10:25:59		73.4		38.5

		29-Mar-08		12:07:10		64.4		39		29-Mar-08		12:06:20		69.2		32		29-Mar-08		12:07:53		71		36.5		9-May-08		12:25:59		72.21		41

		29-Mar-08		14:07:10		66.81		38.5		29-Mar-08		14:06:20		68		38		29-Mar-08		14:07:53		71		44		9-May-08		14:25:59		72.21		41.5

		29-Mar-08		16:07:10		66.81		43		29-Mar-08		16:06:20		65.6		51		29-Mar-08		16:07:53		71		43		9-May-08		16:25:59		73.4		39.5

		29-Mar-08		18:07:10		66.81		44.5		29-Mar-08		18:06:20		64.4		55.5		29-Mar-08		18:07:53		72.21		42.5		9-May-08		18:25:59		72.8		39

		29-Mar-08		20:07:10		66.81		44.5		29-Mar-08		20:06:20		65.01		55		29-Mar-08		20:07:53		71		45.5		9-May-08		20:25:59		73.4		38.5

		29-Mar-08		22:07:10		66.81		45		29-Mar-08		22:06:20		64.4		57		29-Mar-08		22:07:53		70.41		44		9-May-08		22:25:59		72.8		37.5

		30-Mar-08		0:07:10		66.81		45		30-Mar-08		0:06:20		65.01		56		30-Mar-08		0:07:53		70.41		42.5		10-May-08		0:25:59		72.21		36

		30-Mar-08		2:07:10		66.81		44.5		30-Mar-08		2:06:20		65.01		54.5		30-Mar-08		2:07:53		69.8		43		10-May-08		2:25:59		72.21		35

		30-Mar-08		4:07:10		66.81		43.5		30-Mar-08		4:06:20		64.4		53.5		30-Mar-08		4:07:53		69.8		42		10-May-08		4:25:59		72.21		35

		30-Mar-08		6:07:10		66.81		41.5		30-Mar-08		6:06:20		65.01		50		30-Mar-08		6:07:53		69.8		41.5		10-May-08		6:25:59		72.21		34

		30-Mar-08		8:07:10		67.4		40.5		30-Mar-08		8:06:20		65.01		47.5		30-Mar-08		8:07:53		69.8		40		10-May-08		8:25:59		71		36

		30-Mar-08		10:07:10		67.4		39.5		30-Mar-08		10:06:20		64.4		47.5		30-Mar-08		10:07:53		69.8		39.5		10-May-08		10:25:59		73.4		36

		30-Mar-08		12:07:10		68		40.5		30-Mar-08		12:06:20		64.4		48		30-Mar-08		12:07:53		69.8		41		10-May-08		12:25:59		74.6		34.5

		30-Mar-08		14:07:10		67.4		42		30-Mar-08		14:06:20		65.01		51		30-Mar-08		14:07:53		70.41		37.5		10-May-08		14:25:59		75.2		33.5

		30-Mar-08		16:07:10		67.4		40.5		30-Mar-08		16:06:20		65.01		46.5		30-Mar-08		16:07:53		70.41		39		10-May-08		16:25:59		75.2		35.5

		30-Mar-08		18:07:10		67.4		39.5		30-Mar-08		18:06:20		65.01		45.5		30-Mar-08		18:07:53		69.8		43		10-May-08		18:25:59		75.2		35.5

		30-Mar-08		20:07:10		68		37		30-Mar-08		20:06:20		64.4		43		30-Mar-08		20:07:53		70.41		39.5		10-May-08		20:25:59		74.6		36

		30-Mar-08		22:07:10		68		33		30-Mar-08		22:06:20		64.4		37		30-Mar-08		22:07:53		71		35.5		10-May-08		22:25:59		74.6		34.5

		31-Mar-08		0:07:10		68		32		31-Mar-08		0:06:20		65.01		35		31-Mar-08		0:07:53		69.8		33		11-May-08		0:25:59		74.01		34

		31-Mar-08		2:07:10		67.4		32		31-Mar-08		2:06:20		64.4		35.5		31-Mar-08		2:07:53		69.8		32.5		11-May-08		2:25:59		72.21		34

		31-Mar-08		4:07:10		67.4		32.5		31-Mar-08		4:06:20		63.8		37		31-Mar-08		4:07:53		68.61		32.5		11-May-08		4:25:59		71.6		34

		31-Mar-08		6:07:10		68		32.5		31-Mar-08		6:06:20		63.21		38.5		31-Mar-08		6:07:53		68		33		11-May-08		6:25:59		72.21		34

		31-Mar-08		8:07:10		67.4		31		31-Mar-08		8:06:20		63.8		36		31-Mar-08		8:07:53		68		32.5		11-May-08		8:25:59		72.21		34.5

		31-Mar-08		10:07:10		67.4		28.5		31-Mar-08		10:06:20		64.4		32		31-Mar-08		10:07:53		69.2		31		11-May-08		10:25:59		72.8		35

		31-Mar-08		12:07:10		67.4		25.5		31-Mar-08		12:06:20		64.4		29.5		31-Mar-08		12:07:53		69.8		29.5		11-May-08		12:25:59		74.01		35

		31-Mar-08		14:07:10		68		23.5		31-Mar-08		14:06:20		65.01		25.5		31-Mar-08		14:07:53		69.8		27.5		11-May-08		14:25:59		75.81		35.5

		31-Mar-08		16:07:10		67.4		24		31-Mar-08		16:06:20		65.01		26		31-Mar-08		16:07:53		69.2		28		11-May-08		16:25:59		77		34.5

		31-Mar-08		18:07:10		67.4		26.5		31-Mar-08		18:06:20		65.01		29.5		31-Mar-08		18:07:53		69.8		28.5		11-May-08		18:25:59		78.2		35

		31-Mar-08		20:07:10		68		26.5		31-Mar-08		20:06:20		64.4		30		31-Mar-08		20:07:53		71		28.5		11-May-08		20:25:59		77.61		36

		31-Mar-08		22:07:10		67.4		27		31-Mar-08		22:06:20		64.4		30.5		31-Mar-08		22:07:53		70.41		27.5		11-May-08		22:25:59		75.81		37

		1-Apr-08		0:07:10		67.4		27.5		1-Apr-08		0:06:20		64.4		31.5		1-Apr-08		0:07:53		69.2		27.5		12-May-08		0:25:59		74.01		37.5

		1-Apr-08		2:07:10		67.4		28		1-Apr-08		2:06:20		63.8		32.5		1-Apr-08		2:07:53		68.61		28		12-May-08		2:25:59		72.8		38

		1-Apr-08		4:07:10		67.4		28		1-Apr-08		4:06:20		62.6		32.5		1-Apr-08		4:07:53		67.4		28.5		12-May-08		4:25:59		72.21		38

		1-Apr-08		6:07:10		67.4		28.5		1-Apr-08		6:06:20		62		34		1-Apr-08		6:07:53		66.81		29.5		12-May-08		6:25:59		72.21		37.5

		1-Apr-08		8:07:10		68		28.5		1-Apr-08		8:06:20		63.21		34		1-Apr-08		8:07:53		69.8		29.5		12-May-08		8:25:59		72.21		38.5

		1-Apr-08		10:07:10		67.4		30.5		1-Apr-08		10:06:20		65.01		34.5		1-Apr-08		10:07:53		71		31.5		12-May-08		10:25:59		71.6		40

		1-Apr-08		12:07:10		66.81		27		1-Apr-08		12:06:20		65.6		30		1-Apr-08		12:07:53		71		34		12-May-08		12:25:59		72.8		41

		1-Apr-08		14:07:10		66.81		30		1-Apr-08		14:06:20		66.2		31		1-Apr-08		14:07:53		71		35		12-May-08		14:25:59		74.01		36

		1-Apr-08		16:07:10		66.81		31		1-Apr-08		16:06:20		65.6		34		1-Apr-08		16:07:53		71		36.5		12-May-08		16:25:59		74.6		32

		1-Apr-08		18:07:10		66.81		29.5		1-Apr-08		18:06:20		65.01		32.5		1-Apr-08		18:07:53		71		33.5		12-May-08		18:25:59		76.4		31

		1-Apr-08		20:07:10		67.4		30.5		1-Apr-08		20:06:20		65.01		32.5		1-Apr-08		20:07:53		70.41		32		12-May-08		20:25:59		75.81		31.5

		1-Apr-08		22:07:10		67.4		29		1-Apr-08		22:06:20		64.4		32		1-Apr-08		22:07:53		70.41		32		12-May-08		22:25:59		74.01		31

		2-Apr-08		0:07:10		66.81		33		2-Apr-08		0:06:20		65.01		37		2-Apr-08		0:07:53		70.41		31		13-May-08		0:25:59		72.8		31

		2-Apr-08		2:07:10		66.81		34		2-Apr-08		2:06:20		64.4		38.5		2-Apr-08		2:07:53		70.41		31		13-May-08		2:25:59		71.6		31

		2-Apr-08		4:07:10		66.81		33		2-Apr-08		4:06:20		64.4		38		2-Apr-08		4:07:53		70.41		32		13-May-08		4:25:59		71.6		31

		2-Apr-08		6:07:10		66.81		31.5		2-Apr-08		6:06:20		65.01		35		2-Apr-08		6:07:53		71		32		13-May-08		6:25:59		71.6		30

		2-Apr-08		8:07:10		66.81		33.5		2-Apr-08		8:06:20		65.01		37.5		2-Apr-08		8:07:53		71.6		33.5		13-May-08		8:25:59		71.6		30

		2-Apr-08		10:07:10		66.81		33.5		2-Apr-08		10:06:20		66.2		35.5		2-Apr-08		10:07:53		70.41		35		13-May-08		10:25:59		74.01		29.5

		2-Apr-08		12:07:10		66.81		33		2-Apr-08		12:06:20		66.81		33		2-Apr-08		12:07:53		71		36		13-May-08		12:25:59		74.01		29.5

		2-Apr-08		14:07:10		66.81		39		2-Apr-08		14:06:20		67.4		42.5		2-Apr-08		14:07:53		71.6		34.5		13-May-08		14:25:59		75.2		29.5

		2-Apr-08		16:07:10		67.4		34		2-Apr-08		16:06:20		67.4		31.5		2-Apr-08		16:07:53		71.6		36.5		13-May-08		16:25:59		75.2		30

		2-Apr-08		18:07:10		66.81		35		2-Apr-08		18:06:20		66.2		36		2-Apr-08		18:07:53		71		32.5		13-May-08		18:25:59		75.2		30

		2-Apr-08		20:07:10		67.4		36.5		2-Apr-08		20:06:20		66.81		37		2-Apr-08		20:07:53		71		37		13-May-08		20:25:59		74.6		30.5

		2-Apr-08		22:07:10		66.81		37.5		2-Apr-08		22:06:20		65.6		41.5		2-Apr-08		22:07:53		75.2		33		13-May-08		22:25:59		74.01		29.5

		3-Apr-08		0:07:10		66.81		37.5		3-Apr-08		0:06:20		66.2		42		3-Apr-08		0:07:53		71.6		34		14-May-08		0:25:59		73.4		29.5

		3-Apr-08		2:07:10		66.81		36.5		3-Apr-08		2:06:20		65.6		40.5		3-Apr-08		2:07:53		70.41		34.5		14-May-08		2:25:59		72.21		30

		3-Apr-08		4:07:10		67.4		34.5		3-Apr-08		4:06:20		64.4		38.5		3-Apr-08		4:07:53		69.2		33.5		14-May-08		4:25:59		71.6		30.5

		3-Apr-08		6:07:10		67.4		35.5		3-Apr-08		6:06:20		64.4		38		3-Apr-08		6:07:53		69.2		33		14-May-08		6:25:59		72.21		31

		3-Apr-08		8:07:10		67.4		35.5		3-Apr-08		8:06:20		65.01		38.5		3-Apr-08		8:07:53		71		31		14-May-08		8:25:59		71.6		32.5

		3-Apr-08		10:07:10		65.01		39		3-Apr-08		10:06:20		66.2		41		3-Apr-08		10:07:53		71.6		34.5		14-May-08		10:25:59		74.6		33

		3-Apr-08		12:07:10		66.81		38		3-Apr-08		12:06:20		66.81		39		3-Apr-08		12:07:53		71		34.5		14-May-08		12:25:59		74.01		32

		3-Apr-08		14:07:10		66.81		40		3-Apr-08		14:06:20		67.4		41.5		3-Apr-08		14:07:53		71		38		14-May-08		14:25:59		74.01		30.5

		3-Apr-08		16:07:10		66.81		38		3-Apr-08		16:06:20		66.2		40		3-Apr-08		16:07:53		71.6		42.5		14-May-08		16:25:59		74.6		29

		3-Apr-08		18:07:10		66.81		35.5		3-Apr-08		18:06:20		66.81		36		3-Apr-08		18:07:53		71		32		14-May-08		18:25:59		74.01		29

		3-Apr-08		20:07:10		67.4		35.5		3-Apr-08		20:06:20		66.2		37.5		3-Apr-08		20:07:53		71		32.5		14-May-08		20:25:59		74.6		33

		3-Apr-08		22:07:10		67.4		34.5		3-Apr-08		22:06:20		65.6		37		3-Apr-08		22:07:53		72.21		34		14-May-08		22:25:59		75.2		33

		4-Apr-08		0:07:10		67.4		34.5		4-Apr-08		0:06:20		66.2		37.5		4-Apr-08		0:07:53		72.21		33.5		15-May-08		0:25:59		74.6		33.5

		4-Apr-08		2:07:10		66.81		34		4-Apr-08		2:06:20		65.6		36.5		4-Apr-08		2:07:53		70.41		32.5		15-May-08		2:25:59		74.01		34

		4-Apr-08		4:07:10		66.81		35		4-Apr-08		4:06:20		65.01		38		4-Apr-08		4:07:53		69.8		32		15-May-08		4:25:59		73.4		35

		4-Apr-08		6:07:10		66.81		37		4-Apr-08		6:06:20		65.6		40.5		4-Apr-08		6:07:53		69.8		34		15-May-08		6:25:59		73.4		36.5

		4-Apr-08		8:07:10		67.4		37.5		4-Apr-08		8:06:20		66.81		42		4-Apr-08		8:07:53		72.21		33.5		15-May-08		8:25:59		73.4		39

		4-Apr-08		10:07:10		68		38.5		4-Apr-08		10:06:20		66.81		42		4-Apr-08		10:07:53		71.6		36		15-May-08		10:25:59		74.6		40

		4-Apr-08		12:07:10		74.6		35		4-Apr-08		12:06:20		74.6		35.5		4-Apr-08		12:07:53		71.6		42.5		15-May-08		12:25:59		74.01		41.5

		4-Apr-08		14:07:10		66.81		38.5		4-Apr-08		14:06:20		67.4		38.5		4-Apr-08		14:07:53		71.6		45		15-May-08		14:25:59		74.01		38.5

		4-Apr-08		16:07:10		66.81		42		4-Apr-08		16:06:20		66.81		45		4-Apr-08		16:07:53		71		45		15-May-08		16:25:59		74.01		38.5

		4-Apr-08		18:07:10		66.81		40.5		4-Apr-08		18:06:20		66.81		43.5		4-Apr-08		18:07:53		71.6		44		15-May-08		18:25:59		73.4		38.5

		4-Apr-08		20:07:10		66.81		45.5		4-Apr-08		20:06:20		65.6		44		4-Apr-08		20:07:53		71.6		43		15-May-08		20:25:59		75.2		38.5

		4-Apr-08		22:07:10		66.81		45.5		4-Apr-08		22:06:20		66.2		43		4-Apr-08		22:07:53		71.6		35.5		15-May-08		22:25:59		76.4		36

		5-Apr-08		0:07:10		67.4		45		5-Apr-08		0:06:20		65.6		42		5-Apr-08		0:07:53		71		39.5		16-May-08		0:25:59		76.4		35.5

		5-Apr-08		2:07:10		66.81		46.5		5-Apr-08		2:06:20		65.01		43.5		5-Apr-08		2:07:53		70.41		37.5		16-May-08		2:25:59		75.81		35.5

		5-Apr-08		4:07:10		66.81		46.5		5-Apr-08		4:06:20		65.01		44.5		5-Apr-08		4:07:53		69.8		38		16-May-08		4:25:59		75.2		35.5

		5-Apr-08		6:07:10		66.81		46		5-Apr-08		6:06:20		65.01		43		5-Apr-08		6:07:53		70.41		39		16-May-08		6:25:59		75.2		35

		5-Apr-08		8:07:10		68		43.5		5-Apr-08		8:06:20		65.6		43.5		5-Apr-08		8:07:53		71		41		16-May-08		8:25:59		74.6		36.5

		5-Apr-08		10:07:10		67.4		47		5-Apr-08		10:06:20		67.4		40		5-Apr-08		10:07:53		70.41		39		16-May-08		10:25:59		74.01		38.5

		5-Apr-08		12:07:10		67.4		45.5		5-Apr-08		12:06:20		67.4		38.5		5-Apr-08		12:07:53		71		44		16-May-08		12:25:59		73.4		40.5

		5-Apr-08		14:07:10		66.81		47		5-Apr-08		14:06:20		68.61		40.5		5-Apr-08		14:07:53		74.6		35.5		16-May-08		14:25:59		72.8		40.5

		5-Apr-08		16:07:10		66.81		46		5-Apr-08		16:06:20		67.4		43		5-Apr-08		16:07:53		71.6		45.5		16-May-08		16:25:59		73.4		40.5

		5-Apr-08		18:07:10		66.81		46.5		5-Apr-08		18:06:20		66.81		40		5-Apr-08		18:07:53		73.4		40		16-May-08		18:25:59		74.01		40.5

		5-Apr-08		20:07:10		67.4		46.5		5-Apr-08		20:06:20		67.4		40.5		5-Apr-08		20:07:53		75.2		37		16-May-08		20:25:59		75.2		40.5

		5-Apr-08		22:07:10		66.81		46		5-Apr-08		22:06:20		67.4		36.5		5-Apr-08		22:07:53		73.4		36.5		16-May-08		22:25:59		77		40

		6-Apr-08		0:07:10		66.81		46		6-Apr-08		0:06:20		66.81		37		6-Apr-08		0:07:53		71		36		17-May-08		0:25:59		76.4		39

		6-Apr-08		2:07:10		66.81		46.5		6-Apr-08		2:06:20		65.6		37.5		6-Apr-08		2:07:53		69.8		35.5		17-May-08		2:25:59		75.2		39

		6-Apr-08		4:07:10		66.81		47		6-Apr-08		4:06:20		65.01		38		6-Apr-08		4:07:53		68.61		36		17-May-08		4:25:59		74.6		39

		6-Apr-08		6:07:10		67.4		46		6-Apr-08		6:06:20		65.01		37.5		6-Apr-08		6:07:53		67.4		36.5		17-May-08		6:25:59		74.6		40

		6-Apr-08		8:07:10		67.4		47		6-Apr-08		8:06:20		65.01		37.5		6-Apr-08		8:07:53		67.4		36.5		17-May-08		8:25:59		74.6		41.5

		6-Apr-08		10:07:10		67.4		45		6-Apr-08		10:06:20		66.81		37		6-Apr-08		10:07:53		69.2		36.5		17-May-08		10:25:59		74.01		43

		6-Apr-08		12:07:10		67.4		46		6-Apr-08		12:06:20		68		35.5		6-Apr-08		12:07:53		70.41		36.5		17-May-08		12:25:59		73.4		46.5

		6-Apr-08		14:07:10		67.4		46		6-Apr-08		14:06:20		68		37		6-Apr-08		14:07:53		70.41		39		17-May-08		14:25:59		74.01		45.5

		6-Apr-08		16:07:10		68		45.5		6-Apr-08		16:06:20		68		39		6-Apr-08		16:07:53		70.41		40.5		17-May-08		16:25:59		74.01		45

		6-Apr-08		18:07:10		67.4		46.5		6-Apr-08		18:06:20		67.4		38.5		6-Apr-08		18:07:53		71		40		17-May-08		18:25:59		73.4		42.5

		6-Apr-08		20:07:10		68		45.5		6-Apr-08		20:06:20		67.4		39.5		6-Apr-08		20:07:53		72.21		38		17-May-08		20:25:59		75.2		42.5

		6-Apr-08		22:07:10		67.4		43.5		6-Apr-08		22:06:20		67.4		39.5		6-Apr-08		22:07:53		71.6		37		17-May-08		22:25:59		75.81		40

		7-Apr-08		0:07:10		67.4		44		7-Apr-08		0:06:20		66.81		39		7-Apr-08		0:07:53		71		36.5		18-May-08		0:25:59		75.2		39.5

		7-Apr-08		2:07:10		68		46		7-Apr-08		2:06:20		66.2		37.5		7-Apr-08		2:07:53		69.8		36		18-May-08		2:25:59		74.6		40

		7-Apr-08		4:07:10		67.4		45		7-Apr-08		4:06:20		65.6		38		7-Apr-08		4:07:53		69.2		36.5		18-May-08		4:25:59		73.4		40

		7-Apr-08		6:07:10		67.4		45.5		7-Apr-08		6:06:20		65.6		38		7-Apr-08		6:07:53		68.61		37		18-May-08		6:25:59		73.4		39.5

		7-Apr-08		8:07:10		67.4		46.5		7-Apr-08		8:06:20		65.6		39		7-Apr-08		8:07:53		68		37		18-May-08		8:25:59		74.01		40.5

		7-Apr-08		10:07:10		67.4		46		7-Apr-08		10:06:20		66.81		40		7-Apr-08		10:07:53		69.8		37.5		18-May-08		10:25:59		75.81		41.5

		7-Apr-08		12:07:10		68		45		7-Apr-08		12:06:20		66.81		44		7-Apr-08		12:07:53		69.8		39		18-May-08		12:25:59		77.61		42

		7-Apr-08		14:07:10		67.4		45		7-Apr-08		14:06:20		67.4		36		7-Apr-08		14:07:53		71		37		18-May-08		14:25:59		79.41		43

		7-Apr-08		16:07:10		67.4		45.5		7-Apr-08		16:06:20		66.81		35.5		7-Apr-08		16:07:53		71.6		35.5		18-May-08		16:25:59		79.41		41.5

		7-Apr-08		18:07:10		67.4		45.5		7-Apr-08		18:06:20		67.4		33		7-Apr-08		18:07:53		72.21		34.5		18-May-08		18:25:59		78.2		41.5

		7-Apr-08		20:07:10		67.4		44.5		7-Apr-08		20:06:20		66.81		31.5		7-Apr-08		20:07:53		71.6		33		18-May-08		20:25:59		77.61		41

		7-Apr-08		22:07:10		68		46		7-Apr-08		22:06:20		67.4		32.5		7-Apr-08		22:07:53		71		33		18-May-08		22:25:59		76.4		40

		8-Apr-08		0:07:10		67.4		44.5		8-Apr-08		0:06:20		66.81		34		8-Apr-08		0:07:53		69.8		33		19-May-08		0:25:59		74.6		39.5

		8-Apr-08		2:07:10		67.4		46.5		8-Apr-08		2:06:20		66.2		35.5		8-Apr-08		2:07:53		69.2		34		19-May-08		2:25:59		73.4		39

		8-Apr-08		4:07:10		67.4		45.5		8-Apr-08		4:06:20		65.6		35.5		8-Apr-08		4:07:53		68		34.5		19-May-08		4:25:59		72.21		39

		8-Apr-08		6:07:10		67.4		46		8-Apr-08		6:06:20		65.01		35		8-Apr-08		6:07:53		68		35		19-May-08		6:25:59		72.21		39.5

		8-Apr-08		8:07:10		67.4		46.5		8-Apr-08		8:06:20		66.2		35		8-Apr-08		8:07:53		71.6		35		19-May-08		8:25:59		72.21		40

		8-Apr-08		10:07:10		67.4		45		8-Apr-08		10:06:20		68		31.5		8-Apr-08		10:07:53		71.6		33.5		19-May-08		10:25:59		72.8		41.5

		8-Apr-08		12:07:10		66.81		46.5		8-Apr-08		12:06:20		68		29.5		8-Apr-08		12:07:53		71.6		34.5		19-May-08		12:25:59		74.6		41.5

		8-Apr-08		14:07:10		66.81		47		8-Apr-08		14:06:20		67.4		28.5		8-Apr-08		14:07:53		71		34.5		19-May-08		14:25:59		75.81		42

		8-Apr-08		16:07:10		66.81		46.5		8-Apr-08		16:06:20		67.4		35		8-Apr-08		16:07:53		71		37		19-May-08		16:25:59		77		41.5

		8-Apr-08		18:07:10		66.81		46		8-Apr-08		18:06:20		66.81		33		8-Apr-08		18:07:53		71.6		35		19-May-08		18:25:59		77.61		40

		8-Apr-08		20:07:10		66.81		46.5		8-Apr-08		20:06:20		66.81		38.5		8-Apr-08		20:07:53		71		34.5		19-May-08		20:25:59		77		39.5

		8-Apr-08		22:07:10		67.4		47		8-Apr-08		22:06:20		66.2		34		8-Apr-08		22:07:53		71.6		37.5		19-May-08		22:25:59		74.6		39.5

		9-Apr-08		0:07:10		66.81		45.5		9-Apr-08		0:06:20		66.2		38		9-Apr-08		0:07:53		71		35.5		20-May-08		0:25:59		73.4		40

		9-Apr-08		2:07:10		66.81		48		9-Apr-08		2:06:20		66.2		35.5		9-Apr-08		2:07:53		70.41		35		20-May-08		2:25:59		72.21		40

		9-Apr-08		4:07:10		66.81		47.5		9-Apr-08		4:06:20		66.2		36		9-Apr-08		4:07:53		69.8		34.5		20-May-08		4:25:59		72.21		40

		9-Apr-08		6:07:10		66.81		44		9-Apr-08		6:06:20		66.2		37		9-Apr-08		6:07:53		69.8		35.5		20-May-08		6:25:59		72.21		40.5

		9-Apr-08		8:07:10		66.81		47.5		9-Apr-08		8:06:20		66.81		37		9-Apr-08		8:07:53		71		38		20-May-08		8:25:59		71.6		42

		9-Apr-08		10:07:10		66.81		46		9-Apr-08		10:06:20		67.4		34		9-Apr-08		10:07:53		71		34.5		20-May-08		10:25:59		73.4		42.5

		9-Apr-08		12:07:10		66.81		45		9-Apr-08		12:06:20		68		32		9-Apr-08		12:07:53		71		38.5		20-May-08		12:25:59		74.01		43.5

		9-Apr-08		14:07:10		66.81		45		9-Apr-08		14:06:20		68.61		29.5		9-Apr-08		14:07:53		70.41		38.5		20-May-08		14:25:59		74.01		44.5

		9-Apr-08		16:07:10		66.81		47		9-Apr-08		16:06:20		67.4		36		9-Apr-08		16:07:53		71		41.5		20-May-08		16:25:59		74.6		44

		9-Apr-08		18:07:10		66.81		46.5		9-Apr-08		18:06:20		68		34		9-Apr-08		18:07:53		71.6		39.5		20-May-08		18:25:59		74.01		43.5

		9-Apr-08		20:07:10		67.4		47		9-Apr-08		20:06:20		67.4		33.5		9-Apr-08		20:07:53		75.2		35		20-May-08		20:25:59		74.6		43

		9-Apr-08		22:07:10		66.81		47		9-Apr-08		22:06:20		66.81		34.5		9-Apr-08		22:07:53		72.8		34.5		20-May-08		22:25:59		74.01		41

		10-Apr-08		0:07:10		66.81		47.5		10-Apr-08		0:06:20		66.2		33.5		10-Apr-08		0:07:53		70.41		33.5		21-May-08		0:25:59		72.8		41

		10-Apr-08		2:07:10		66.81		47		10-Apr-08		2:06:20		65.6		34.5		10-Apr-08		2:07:53		69.8		33		21-May-08		2:25:59		72.21		41

		10-Apr-08		4:07:10		66.81		47		10-Apr-08		4:06:20		65.01		34.5		10-Apr-08		4:07:53		69.2		33.5		21-May-08		4:25:59		72.21		41

		10-Apr-08		6:07:10		67.4		46		10-Apr-08		6:06:20		65.6		34.5		10-Apr-08		6:07:53		68.61		34.5		21-May-08		6:25:59		72.21		40.5

		10-Apr-08		8:07:10		66.81		47		10-Apr-08		8:06:20		66.2		34.5		10-Apr-08		8:07:53		69.8		35		21-May-08		8:25:59		72.21		42

		10-Apr-08		10:07:10		66.81		47.5		10-Apr-08		10:06:20		68		34		10-Apr-08		10:07:53		70.41		38		21-May-08		10:25:59		73.4		42.5

		10-Apr-08		12:07:10		66.81		47		10-Apr-08		12:06:20		69.2		34		10-Apr-08		12:07:53		70.41		35		21-May-08		12:25:59		73.4		43

		10-Apr-08		14:07:10		66.81		47.5		10-Apr-08		14:06:20		69.8		36		10-Apr-08		14:07:53		71		42.5		21-May-08		14:25:59		74.01		44

		10-Apr-08		16:07:10		66.81		46.5		10-Apr-08		16:06:20		69.2		39.5		10-Apr-08		16:07:53		70.41		47		21-May-08		16:25:59		74.01		41

		10-Apr-08		18:07:10		66.81		47.5		10-Apr-08		18:06:20		68		32		10-Apr-08		18:07:53		69.8		35.5		21-May-08		18:25:59		74.01		35

		10-Apr-08		20:07:10		66.81		46.5		10-Apr-08		20:06:20		67.4		37		10-Apr-08		20:07:53		70.41		41.5		21-May-08		20:25:59		73.4		34.5

		10-Apr-08		22:07:10		66.81		47		10-Apr-08		22:06:20		67.4		37		10-Apr-08		22:07:53		71		37.5		21-May-08		22:25:59		74.01		35

		11-Apr-08		0:07:10		66.81		47.5		11-Apr-08		0:06:20		68		36.5		11-Apr-08		0:07:53		69.2		38		22-May-08		0:25:59		73.4		34.5

		11-Apr-08		2:07:10		66.81		46.5		11-Apr-08		2:06:20		66.81		36.5		11-Apr-08		2:07:53		69.8		36.5		22-May-08		2:25:59		72.21		34.5

		11-Apr-08		4:07:10		66.81		46.5		11-Apr-08		4:06:20		66.2		37.5		11-Apr-08		4:07:53		69.8		35.5		22-May-08		4:25:59		71.6		34

		11-Apr-08		6:07:10		66.81		46.5		11-Apr-08		6:06:20		65.6		37.5		11-Apr-08		6:07:53		69.2		36.5		22-May-08		6:25:59		72.21		32.5

		11-Apr-08		8:07:10		66.81		47.5		11-Apr-08		8:06:20		66.81		38		11-Apr-08		8:07:53		70.41		38.5		22-May-08		8:25:59		71.6		33.5

		11-Apr-08		10:07:10		66.81		48		11-Apr-08		10:06:20		68		36.5		11-Apr-08		10:07:53		70.41		36		22-May-08		10:25:59		73.4		34

		11-Apr-08		12:07:10		66.2		48.5		11-Apr-08		12:06:20		68.61		35		11-Apr-08		12:07:53		71		39.5		22-May-08		12:25:59		73.4		35

		11-Apr-08		14:07:10		66.81		48		11-Apr-08		14:06:20		68.61		34.5		11-Apr-08		14:07:53		70.41		45.5		22-May-08		14:25:59		74.01		35

		11-Apr-08		16:07:10		66.2		45.5		11-Apr-08		16:06:20		68.61		40		11-Apr-08		16:07:53		70.41		47.5		22-May-08		16:25:59		74.01		35

		11-Apr-08		18:07:10		66.81		48		11-Apr-08		18:06:20		68.61		37.5		11-Apr-08		18:07:53		71		45.5		22-May-08		18:25:59		74.01		34.5

		11-Apr-08		20:07:10		66.81		47.5		11-Apr-08		20:06:20		68.61		39.5		11-Apr-08		20:07:53		70.41		42		22-May-08		20:25:59		73.4		34.5

		11-Apr-08		22:07:10		66.81		47		11-Apr-08		22:06:20		67.4		42.5		11-Apr-08		22:07:53		70.41		43		22-May-08		22:25:59		72.8		33.5

		12-Apr-08		0:07:10		66.81		48		12-Apr-08		0:06:20		68		41.5		12-Apr-08		0:07:53		69.8		41.5		23-May-08		0:25:59		72.21		33

		12-Apr-08		2:07:10		66.81		47		12-Apr-08		2:06:20		66.81		42		12-Apr-08		2:07:53		69.8		39		23-May-08		2:25:59		71		32.5

		12-Apr-08		4:07:10		66.81		47.5		12-Apr-08		4:06:20		66.2		41		12-Apr-08		4:07:53		70.41		38.5		23-May-08		4:25:59		71.6		31.5

		12-Apr-08		6:07:10		66.81		47.5		12-Apr-08		6:06:20		66.2		40.5		12-Apr-08		6:07:53		70.41		38		23-May-08		6:25:59		71.6		30.5

		12-Apr-08		8:07:10		66.81		48.5		12-Apr-08		8:06:20		68		39.5		12-Apr-08		8:07:53		69.8		36		23-May-08		8:25:59		71		31.5

		12-Apr-08		10:07:10		66.81		47.5		12-Apr-08		10:06:20		68.61		43		12-Apr-08		10:07:53		70.41		43		23-May-08		10:25:59		73.4		31

		12-Apr-08		12:07:10		66.81		47		12-Apr-08		12:06:20		68		39		12-Apr-08		12:07:53		69.8		47.5		23-May-08		12:25:59		73.4		29.5

		12-Apr-08		14:07:10		67.4		46.5		12-Apr-08		14:06:20		68.61		33.5		12-Apr-08		14:07:53		70.41		40.5		23-May-08		14:25:59		74.01		29

		12-Apr-08		16:07:10		67.4		48		12-Apr-08		16:06:20		67.4		35		12-Apr-08		16:07:53		72.21		40		23-May-08		16:25:59		74.6		30

		12-Apr-08		18:07:10		67.4		45.5		12-Apr-08		18:06:20		67.4		34		12-Apr-08		18:07:53		68		45		23-May-08		18:25:59		74.01		31

		12-Apr-08		20:07:10		67.4		46.5		12-Apr-08		20:06:20		66.81		32.5		12-Apr-08		20:07:53		68		45		23-May-08		20:25:59		74.01		32

		12-Apr-08		22:07:10		67.4		46.5		12-Apr-08		22:06:20		66.2		38.5		12-Apr-08		22:07:53		68		44		23-May-08		22:25:59		74.6		31.5

		13-Apr-08		0:07:10		67.4		46		13-Apr-08		0:06:20		66.81		41		13-Apr-08		0:07:53		66.81		46		24-May-08		0:25:59		73.4		31.5

		13-Apr-08		2:07:10		67.4		46		13-Apr-08		2:06:20		65.6		42		13-Apr-08		2:07:53		66.81		45.5		24-May-08		2:25:59		72.21		32

		13-Apr-08		4:07:10		68		45.5		13-Apr-08		4:06:20		65.6		41		13-Apr-08		4:07:53		66.2		46.5		24-May-08		4:25:59		71.6		32

		13-Apr-08		6:07:10		68		46.5		13-Apr-08		6:06:20		66.81		40		13-Apr-08		6:07:53		66.2		47		24-May-08		6:25:59		72.21		31.5

		13-Apr-08		8:07:10		67.4		46.5		13-Apr-08		8:06:20		66.2		40.5		13-Apr-08		8:07:53		66.2		47.5		24-May-08		8:25:59		71.6		33

		13-Apr-08		10:07:10		68		47		13-Apr-08		10:06:20		66.81		42		13-Apr-08		10:07:53		66.81		47		24-May-08		10:25:59		74.01		33.5

		13-Apr-08		12:07:10		67.4		46		13-Apr-08		12:06:20		67.4		41.5		13-Apr-08		12:07:53		67.4		45.5		24-May-08		12:25:59		73.4		35

		13-Apr-08		14:07:10		67.4		46.5		13-Apr-08		14:06:20		67.4		43		13-Apr-08		14:07:53		67.4		46		24-May-08		14:25:59		74.01		35

		13-Apr-08		16:07:10		67.4		46		13-Apr-08		16:06:20		66.81		40		13-Apr-08		16:07:53		68		45.5		24-May-08		16:25:59		74.01		34.5

		13-Apr-08		18:07:10		67.4		46.5		13-Apr-08		18:06:20		66.81		38.5		13-Apr-08		18:07:53		67.4		45.5		24-May-08		18:25:59		74.01		34.5

		13-Apr-08		20:07:10		68		46		13-Apr-08		20:06:20		66.2		43.5		13-Apr-08		20:07:53		67.4		46		24-May-08		20:25:59		74.01		35.5

		13-Apr-08		22:07:10		67.4		47.5		13-Apr-08		22:06:20		66.2		53.5		13-Apr-08		22:07:53		67.4		46.5		24-May-08		22:25:59		74.01		35

		14-Apr-08		0:07:10		67.4		46		14-Apr-08		0:06:20		66.2		48.5		14-Apr-08		0:07:53		66.81		47		25-May-08		0:25:59		72.8		35.5

		14-Apr-08		2:07:10		67.4		46		14-Apr-08		2:06:20		66.2		46		14-Apr-08		2:07:53		66.81		47		25-May-08		2:25:59		72.21		36

		14-Apr-08		4:07:10		67.4		46		14-Apr-08		4:06:20		65.6		45.5		14-Apr-08		4:07:53		66.2		47.5		25-May-08		4:25:59		71.6		36.5

		14-Apr-08		6:07:10		68.61		46		14-Apr-08		6:06:20		65.6		44		14-Apr-08		6:07:53		66.2		48		25-May-08		6:25:59		71.6		37

		14-Apr-08		8:07:10		67.4		46		14-Apr-08		8:06:20		66.2		41.5		14-Apr-08		8:07:53		66.2		47		25-May-08		8:25:59		71.6		37.5

		14-Apr-08		10:07:10		68		46		14-Apr-08		10:06:20		66.2		43		14-Apr-08		10:07:53		66.2		48		25-May-08		10:25:59		71.6		38.5

		14-Apr-08		12:07:10		67.4		46		14-Apr-08		12:06:20		67.4		43		14-Apr-08		12:07:53		66.81		47		25-May-08		12:25:59		71.6		40

		14-Apr-08		14:07:10		67.4		48		14-Apr-08		14:06:20		67.4		45.5		14-Apr-08		14:07:53		67.4		48.5		25-May-08		14:25:59		71.6		40.5

		14-Apr-08		16:07:10		67.4		46		14-Apr-08		16:06:20		66.81		43		14-Apr-08		16:07:53		66.81		47		25-May-08		16:25:59		71.6		40

		14-Apr-08		18:07:10		67.4		47		14-Apr-08		18:06:20		66.81		46.5		14-Apr-08		18:07:53		66.81		48		25-May-08		18:25:59		71.6		41

		14-Apr-08		20:07:10		67.4		47		14-Apr-08		20:06:20		66.2		50		14-Apr-08		20:07:53		66.2		48		25-May-08		20:25:59		71.6		41

		14-Apr-08		22:07:10		68		45.5		14-Apr-08		22:06:20		66.2		46		14-Apr-08		22:07:53		66.2		48		25-May-08		22:25:59		71.6		41

		15-Apr-08		0:07:10		67.4		46		15-Apr-08		0:06:20		65.6		49		15-Apr-08		0:07:53		66.81		47		26-May-08		0:25:59		71.6		40

		15-Apr-08		2:07:10		67.4		47		15-Apr-08		2:06:20		66.2		46		15-Apr-08		2:07:53		66.81		47.5		26-May-08		2:25:59		71.6		38.5

		15-Apr-08		4:07:10		67.4		44		15-Apr-08		4:06:20		65.6		45		15-Apr-08		4:07:53		66.81		47.5		26-May-08		4:25:59		71.6		37.5

		15-Apr-08		6:07:10		68		46		15-Apr-08		6:06:20		65.01		45		15-Apr-08		6:07:53		66.2		48		26-May-08		6:25:59		71.6		37

		15-Apr-08		8:07:10		67.4		45.5		15-Apr-08		8:06:20		67.4		45		15-Apr-08		8:07:53		65.6		49.5		26-May-08		8:25:59		71.6		37.5

		15-Apr-08		10:07:10		67.4		47		15-Apr-08		10:06:20		69.2		44		15-Apr-08		10:07:53		65.01		49		26-May-08		10:25:59		71.6		39.5

		15-Apr-08		12:07:10		67.4		47		15-Apr-08		12:06:20		69.8		37.5		15-Apr-08		12:07:53		65.6		49		26-May-08		12:25:59		72.21		38.5

		15-Apr-08		14:07:10		67.4		41		15-Apr-08		14:06:20		71		33.5		15-Apr-08		14:07:53		66.2		47.5		26-May-08		14:25:59		72.8		38

		15-Apr-08		16:07:10		67.4		45.5		15-Apr-08		16:06:20		70.41		32.5		15-Apr-08		16:07:53		66.81		47		26-May-08		16:25:59		73.4		36.5

		15-Apr-08		18:07:10		67.4		45.5		15-Apr-08		18:06:20		69.2		31.5		15-Apr-08		18:07:53		68		45.5		26-May-08		18:25:59		74.01		36

		15-Apr-08		20:07:10		67.4		45		15-Apr-08		20:06:20		69.2		29		15-Apr-08		20:07:53		67.4		45		26-May-08		20:25:59		74.01		35.5

		15-Apr-08		22:07:10		68		45.5		15-Apr-08		22:06:20		68		31.5		15-Apr-08		22:07:53		67.4		45		26-May-08		22:25:59		72.21		37

		16-Apr-08		0:07:10		67.4		37		16-Apr-08		0:06:20		66.81		34.5		16-Apr-08		0:07:53		67.4		45.5		27-May-08		0:25:59		72.21		37.5

		16-Apr-08		2:07:10		67.4		46.5		16-Apr-08		2:06:20		65.6		33		16-Apr-08		2:07:53		68		44.5		27-May-08		2:25:59		71.6		37.5

		16-Apr-08		4:07:10		67.4		45		16-Apr-08		4:06:20		65.01		33		16-Apr-08		4:07:53		68		45		27-May-08		4:25:59		71.6		37.5

		16-Apr-08		6:07:10		67.4		45.5		16-Apr-08		6:06:20		65.01		33.5		16-Apr-08		6:07:53		68		44.5		27-May-08		6:25:59		72.21		37.5

		16-Apr-08		8:07:10		67.4		46		16-Apr-08		8:06:20		68		32.5		16-Apr-08		8:07:53		67.4		44		27-May-08		8:25:59		71		39

		16-Apr-08		10:07:10		69.2		34		16-Apr-08		10:06:20		70.41		30		16-Apr-08		10:07:53		66.2		47.5		27-May-08		10:25:59		71		39.5

		16-Apr-08		12:07:10		69.8		44		16-Apr-08		12:06:20		68.61		27.5		16-Apr-08		12:07:53		66.2		48		27-May-08		12:25:59		72.21		40.5

		16-Apr-08		14:07:10		70.41		43		16-Apr-08		14:06:20		69.8		26		16-Apr-08		14:07:53		66.2		49.5		27-May-08		14:25:59		72.8		40

		16-Apr-08		16:07:10		70.41		46		16-Apr-08		16:06:20		69.2		28		16-Apr-08		16:07:53		67.4		47		27-May-08		16:25:59		72.8		39.5

		16-Apr-08		18:07:10		70.41		45.5		16-Apr-08		18:06:20		68.61		31		16-Apr-08		18:07:53		68		48		27-May-08		18:25:59		72.8		41

		16-Apr-08		20:07:10		69.2		44.5		16-Apr-08		20:06:20		68		30		16-Apr-08		20:07:53		67.4		44.5		27-May-08		20:25:59		72.8		40.5

		16-Apr-08		22:07:10		69.2		44.5		16-Apr-08		22:06:20		68		30		16-Apr-08		22:07:53		68		45		27-May-08		22:25:59		72.21		39.5

		17-Apr-08		0:07:10		70.41		46		17-Apr-08		0:06:20		67.4		31.5		17-Apr-08		0:07:53		68		41		28-May-08		0:25:59		72.21		39.5

		17-Apr-08		2:07:10		70.41		43.5		17-Apr-08		2:06:20		66.2		33		17-Apr-08		2:07:53		68		48.5		28-May-08		2:25:59		72.21		40

		17-Apr-08		4:07:10		69.8		46		17-Apr-08		4:06:20		65.6		34		17-Apr-08		4:07:53		68		46.5		28-May-08		4:25:59		71.6		40

		17-Apr-08		6:07:10		69.8		46		17-Apr-08		6:06:20		65.6		34.5		17-Apr-08		6:07:53		68		47		28-May-08		6:25:59		72.21		40.5

		17-Apr-08		8:07:10		71		44.5		17-Apr-08		8:06:20		69.2		33		17-Apr-08		8:07:53		67.4		48		28-May-08		8:25:59		71.6		42.5

		17-Apr-08		10:07:10		70.41		44.5		17-Apr-08		10:06:20		70.41		31.5		17-Apr-08		10:07:53		66.81		45.5		28-May-08		10:25:59		73.4		42

		17-Apr-08		12:07:10		71		45.5		17-Apr-08		12:06:20		71		29		17-Apr-08		12:07:53		68		48.5		28-May-08		12:25:59		74.01		41

		17-Apr-08		14:07:10		71		45.5		17-Apr-08		14:06:20		69.2		29.5		17-Apr-08		14:07:53		67.4		49.5		28-May-08		14:25:59		74.01		41.5

		17-Apr-08		16:07:10		71		45.5		17-Apr-08		16:06:20		68.61		31.5		17-Apr-08		16:07:53		68		48		28-May-08		16:25:59		74.6		39.5

		17-Apr-08		18:07:10		71		46.5		17-Apr-08		18:06:20		70.41		31		17-Apr-08		18:07:53		68.61		48		28-May-08		18:25:59		75.2		38

		17-Apr-08		20:07:10		71		44.5		17-Apr-08		20:06:20		69.8		34.5		17-Apr-08		20:07:53		67.4		46.5		28-May-08		20:25:59		74.6		39.5

		17-Apr-08		22:07:10		69.8		42.5		17-Apr-08		22:06:20		69.8		36.5		17-Apr-08		22:07:53		67.4		46		28-May-08		22:25:59		74.01		38

		18-Apr-08		0:07:10		70.41		45.5		18-Apr-08		0:06:20		68.61		38		18-Apr-08		0:07:53		68		48.5		29-May-08		0:25:59		72.8		38

		18-Apr-08		2:07:10		70.41		42.5		18-Apr-08		2:06:20		67.4		39		18-Apr-08		2:07:53		68		47.5		29-May-08		2:25:59		72.21		38

		18-Apr-08		4:07:10		69.8		46.5		18-Apr-08		4:06:20		66.2		39.5		18-Apr-08		4:07:53		68		47.5		29-May-08		4:25:59		72.21		38.5

		18-Apr-08		6:07:10		69.8		46		18-Apr-08		6:06:20		65.6		40		18-Apr-08		6:07:53		68		42		29-May-08		6:25:59		72.8		38.5

		18-Apr-08		8:07:10		70.41		46.5		18-Apr-08		8:06:20		68.61		39		18-Apr-08		8:07:53		67.4		49		29-May-08		8:25:59		72.8		40

		18-Apr-08		10:07:10		70.41		46		18-Apr-08		10:06:20		71		37.5		18-Apr-08		10:07:53		67.4		47.5		29-May-08		10:25:59		74.01		39

		18-Apr-08		12:07:10		71		44		18-Apr-08		12:06:20		72.21		36.5		18-Apr-08		12:07:53		68		49		29-May-08		12:25:59		74.6		39.5

		18-Apr-08		14:07:10		70.41		44.5		18-Apr-08		14:06:20		71		34.5		18-Apr-08		14:07:53		66.81		49.5		29-May-08		14:25:59		75.2		39

		18-Apr-08		16:07:10		70.41		42.5		18-Apr-08		16:06:20		71		39		18-Apr-08		16:07:53		67.4		49		29-May-08		16:25:59		74.6		39

		18-Apr-08		18:07:10		70.41		45		18-Apr-08		18:06:20		70.41		38		18-Apr-08		18:07:53		68		47.5		29-May-08		18:25:59		74.6		38

		18-Apr-08		20:07:10		70.41		44.5		18-Apr-08		20:06:20		69.8		41		18-Apr-08		20:07:53		67.4		48.5		29-May-08		20:25:59		74.6		39.5

		18-Apr-08		22:07:10		70.41		45.5		18-Apr-08		22:06:20		69.2		41		18-Apr-08		22:07:53		68		48.5		29-May-08		22:25:59		74.6		38.5

		19-Apr-08		0:07:10		69.8		44.5		19-Apr-08		0:06:20		68		42.5		19-Apr-08		0:07:53		67.4		49		30-May-08		0:25:59		74.01		38.5

		19-Apr-08		2:07:10		69.8		45		19-Apr-08		2:06:20		67.4		45		19-Apr-08		2:07:53		67.4		49		30-May-08		2:25:59		72.8		38.5

		19-Apr-08		4:07:10		69.8		40		19-Apr-08		4:06:20		66.81		45		19-Apr-08		4:07:53		68		46.5		30-May-08		4:25:59		72.21		39

		19-Apr-08		6:07:10		69.8		45.5		19-Apr-08		6:06:20		66.81		45		19-Apr-08		6:07:53		68		49		30-May-08		6:25:59		72.21		39.5

		19-Apr-08		8:07:10		69.8		45		19-Apr-08		8:06:20		71		41		19-Apr-08		8:07:53		66.81		50		30-May-08		8:25:59		72.21		41.5

		19-Apr-08		10:07:10		69.8		45		19-Apr-08		10:06:20		71.6		40.5		19-Apr-08		10:07:53		66.81		50		30-May-08		10:25:59		74.6		41.5

		19-Apr-08		12:07:10		70.41		44.5		19-Apr-08		12:06:20		71.6		39		19-Apr-08		12:07:53		66.81		50		30-May-08		12:25:59		74.6		41.5

		19-Apr-08		14:07:10		70.41		42		19-Apr-08		14:06:20		72.8		41		19-Apr-08		14:07:53		66.81		48		30-May-08		14:25:59		74.6		41.5

		19-Apr-08		16:07:10		70.41		45		19-Apr-08		16:06:20		69.8		42.5		19-Apr-08		16:07:53		67.4		48		30-May-08		16:25:59		75.2		40.5

		19-Apr-08		18:07:10		69.8		45		19-Apr-08		18:06:20		69.8		43.5		19-Apr-08		18:07:53		67.4		49.5		30-May-08		18:25:59		74.6		39

		19-Apr-08		20:07:10		69.8		42		19-Apr-08		20:06:20		68.61		41		19-Apr-08		20:07:53		67.4		46		30-May-08		20:25:59		74.6		41

		19-Apr-08		22:07:10		69.8		44.5		19-Apr-08		22:06:20		68.61		39		19-Apr-08		22:07:53		67.4		49.5		30-May-08		22:25:59		74.6		39.5

		20-Apr-08		0:07:10		69.2		44		20-Apr-08		0:06:20		67.4		40		20-Apr-08		0:07:53		67.4		49.5		31-May-08		0:25:59		74.01		39

		20-Apr-08		2:07:10		69.2		44.5		20-Apr-08		2:06:20		66.2		40		20-Apr-08		2:07:53		67.4		48		31-May-08		2:25:59		72.8		39.5

		20-Apr-08		4:07:10		68.61		45.5		20-Apr-08		4:06:20		65.01		38.5		20-Apr-08		4:07:53		66.81		48.5		31-May-08		4:25:59		72.21		40

		20-Apr-08		6:07:10		68.61		46.5		20-Apr-08		6:06:20		65.01		36		20-Apr-08		6:07:53		67.4		48.5		31-May-08		6:25:59		71.6		41

		20-Apr-08		8:07:10		68.61		47		20-Apr-08		8:06:20		65.01		33.5		20-Apr-08		8:07:53		67.4		47.5		31-May-08		8:25:59		71.6		42

		20-Apr-08		10:07:10		68.61		46		20-Apr-08		10:06:20		67.4		30		20-Apr-08		10:07:53		68		47.5		31-May-08		10:25:59		73.4		42.5

		20-Apr-08		12:07:10		69.2		43.5		20-Apr-08		12:06:20		69.2		26		20-Apr-08		12:07:53		67.4		44.5		31-May-08		12:25:59		74.6		42

		20-Apr-08		14:07:10		69.2		43.5		20-Apr-08		14:06:20		69.2		23		20-Apr-08		14:07:53		66.81		36.5		31-May-08		14:25:59		75.2		43.5

		20-Apr-08		16:07:10		69.2		45		20-Apr-08		16:06:20		69.2		23.5		20-Apr-08		16:07:53		67.4		47.5		31-May-08		16:25:59		74.6		43

		20-Apr-08		18:07:10		69.2		44		20-Apr-08		18:06:20		69.8		23		20-Apr-08		18:07:53		67.4		44.5		31-May-08		18:25:59		74.6		44.5

		20-Apr-08		20:07:10		69.2		45.5		20-Apr-08		20:06:20		68		25.5		20-Apr-08		20:07:53		67.4		47		31-May-08		20:25:59		74.6		43

		20-Apr-08		22:07:10		68.61		45		20-Apr-08		22:06:20		66.81		27.5		20-Apr-08		22:07:53		67.4		47.5		31-May-08		22:25:59		74.01		41

		21-Apr-08		0:07:10		68.61		46.5		21-Apr-08		0:06:20		65.6		29		21-Apr-08		0:07:53		67.4		48.5		1-Jun-08		0:25:59		72.8		41

		21-Apr-08		2:07:10		68		44.5		21-Apr-08		2:06:20		65.01		30.5		21-Apr-08		2:07:53		66.81		37.5		1-Jun-08		2:25:59		72.21		40.5

		21-Apr-08		4:07:10		68		46.5		21-Apr-08		4:06:20		63.8		31.5		21-Apr-08		4:07:53		66.81		47.5		1-Jun-08		4:25:59		71.6		40.5

		21-Apr-08		6:07:10		68		47.5		21-Apr-08		6:06:20		63.21		33		21-Apr-08		6:07:53		67.4		47.5		1-Jun-08		6:25:59		72.21		40.5

		21-Apr-08		8:07:10		68		44		21-Apr-08		8:06:20		63.21		33		21-Apr-08		8:07:53		67.4		47.5		1-Jun-08		8:25:59		72.21		40.5

		21-Apr-08		10:07:10		68		47.5		21-Apr-08		10:06:20		65.01		29		21-Apr-08		10:07:53		67.4		47.5		1-Jun-08		10:25:59		72.21		40.5

		21-Apr-08		12:07:10		68		42.5		21-Apr-08		12:06:20		67.4		24.5		21-Apr-08		12:07:53		67.4		42		1-Jun-08		12:25:59		73.4		41

		21-Apr-08		14:07:10		68.61		45.5		21-Apr-08		14:06:20		69.2		27.5		21-Apr-08		14:07:53		67.4		48		1-Jun-08		14:25:59		74.6		41.5

		21-Apr-08		16:07:10		68.61		45		21-Apr-08		16:06:20		69.2		29.5		21-Apr-08		16:07:53		67.4		48		1-Jun-08		16:25:59		75.81		41

		21-Apr-08		18:07:10		68.61		45		21-Apr-08		18:06:20		69.2		27		21-Apr-08		18:07:53		66.81		46.5		1-Jun-08		18:25:59		77		39.5

		21-Apr-08		20:07:10		69.2		45		21-Apr-08		20:06:20		68		30		21-Apr-08		20:07:53		67.4		48		1-Jun-08		20:25:59		76.4		39.5

		21-Apr-08		22:07:10		68.61		46.5		21-Apr-08		22:06:20		66.2		32		21-Apr-08		22:07:53		67.4		48.5		1-Jun-08		22:25:59		74.6		39

		22-Apr-08		0:07:10		68.61		45		22-Apr-08		0:06:20		65.01		30		22-Apr-08		0:07:53		67.4		48		2-Jun-08		0:25:59		72.8		39

		22-Apr-08		2:07:10		68		47		22-Apr-08		2:06:20		64.4		32		22-Apr-08		2:07:53		67.4		48		2-Jun-08		2:25:59		72.21		38.5

		22-Apr-08		4:07:10		67.4		47		22-Apr-08		4:06:20		63.8		32.5		22-Apr-08		4:07:53		66.81		41		2-Jun-08		4:25:59		72.21		38

		22-Apr-08		6:07:10		68		46.5		22-Apr-08		6:06:20		63.21		34		22-Apr-08		6:07:53		67.4		48		2-Jun-08		6:25:59		71.6		37.5

		22-Apr-08		8:07:10		68.61		47		22-Apr-08		8:06:20		66.81		33.5		22-Apr-08		8:07:53		66.81		49		2-Jun-08		8:25:59		71.6		38

		22-Apr-08		10:07:10		69.2		44.5		22-Apr-08		10:06:20		71		29.5		22-Apr-08		10:07:53		66.2		49.5		2-Jun-08		10:25:59		72.21		39

		22-Apr-08		12:07:10		69.8		44		22-Apr-08		12:06:20		71		27.5		22-Apr-08		12:07:53		66.81		48		2-Jun-08		12:25:59		73.4		38.5

		22-Apr-08		14:07:10		69.8		46		22-Apr-08		14:06:20		71		31		22-Apr-08		14:07:53		66.2		49.5		2-Jun-08		14:25:59		75.2		38

		22-Apr-08		16:07:10		69.2		44.5		22-Apr-08		16:06:20		69.8		32.5		22-Apr-08		16:07:53		67.4		47.5		2-Jun-08		16:25:59		75.81		38

		22-Apr-08		18:07:10		69.2		45		22-Apr-08		18:06:20		69.8		32		22-Apr-08		18:07:53		68		46.5		2-Jun-08		18:25:59		76.4		37

		22-Apr-08		20:07:10		69.8		45		22-Apr-08		20:06:20		69.2		31.5		22-Apr-08		20:07:53		68		46.5		2-Jun-08		20:25:59		75.81		37

		22-Apr-08		22:07:10		69.8		43.5		22-Apr-08		22:06:20		68		32		22-Apr-08		22:07:53		68		47		2-Jun-08		22:25:59		74.01		37.5

		23-Apr-08		0:07:10		69.2		45		23-Apr-08		0:06:20		66.81		32		23-Apr-08		0:07:53		67.4		47.5		3-Jun-08		0:25:59		72.21		37

		23-Apr-08		2:07:10		68.61		45		23-Apr-08		2:06:20		65.6		33		23-Apr-08		2:07:53		67.4		47		3-Jun-08		2:25:59		72.21		36.5

		23-Apr-08		4:07:10		68.61		46.5		23-Apr-08		4:06:20		65.01		34.5		23-Apr-08		4:07:53		67.4		47.5		3-Jun-08		4:25:59		71.6		36

		23-Apr-08		6:07:10		68.61		43.5		23-Apr-08		6:06:20		64.4		35.5		23-Apr-08		6:07:53		67.4		47.5		3-Jun-08		6:25:59		72.21		35.5

		23-Apr-08		8:07:10		69.2		42.5		23-Apr-08		8:06:20		66.81		35.5		23-Apr-08		8:07:53		67.4		48		3-Jun-08		8:25:59		71.6		37.5

		23-Apr-08		10:07:10		69.8		46		23-Apr-08		10:06:20		70.41		32.5		23-Apr-08		10:07:53		67.4		48		3-Jun-08		10:25:59		74.01		38

		23-Apr-08		12:07:10		69.2		45.5		23-Apr-08		12:06:20		71		35.5		23-Apr-08		12:07:53		66.81		49.5		3-Jun-08		12:25:59		74.01		39

		23-Apr-08		14:07:10		69.8		45		23-Apr-08		14:06:20		71.6		41		23-Apr-08		14:07:53		66.2		50.5		3-Jun-08		14:25:59		74.6		39.5

		23-Apr-08		16:07:10		70.41		47		23-Apr-08		16:06:20		69.8		49		23-Apr-08		16:07:53		67.4		50.5		3-Jun-08		16:25:59		74.6		39

		23-Apr-08		18:07:10		70.41		44.5		23-Apr-08		18:06:20		69.2		47.5		23-Apr-08		18:07:53		68		50		3-Jun-08		18:25:59		74.6		38.5

		23-Apr-08		20:07:10		70.41		46		23-Apr-08		20:06:20		69.8		49.5		23-Apr-08		20:07:53		68		50		3-Jun-08		20:25:59		74.6		34.5

		23-Apr-08		22:07:10		70.41		46.5		23-Apr-08		22:06:20		69.2		48.5		23-Apr-08		22:07:53		68		50		3-Jun-08		22:25:59		74.6		31.5

		24-Apr-08		0:07:10		70.41		47		24-Apr-08		0:06:20		68		47		24-Apr-08		0:07:53		68		49.5		4-Jun-08		0:25:59		73.4		32.5

		24-Apr-08		2:07:10		69.8		44.5		24-Apr-08		2:06:20		66.81		47.5		24-Apr-08		2:07:53		68		49.5		4-Jun-08		2:25:59		72.8		33.5

		24-Apr-08		4:07:10		69.8		46.5		24-Apr-08		4:06:20		66.2		46		24-Apr-08		4:07:53		68		48.5		4-Jun-08		4:25:59		72.21		34

		24-Apr-08		6:07:10		69.8		46.5		24-Apr-08		6:06:20		65.6		44.5		24-Apr-08		6:07:53		68		49		4-Jun-08		6:25:59		72.21		33.5

		24-Apr-08		8:07:10		70.41		47		24-Apr-08		8:06:20		68		44		24-Apr-08		8:07:53		67.4		50		4-Jun-08		8:25:59		72.21		37

		24-Apr-08		10:07:10		70.41		46		24-Apr-08		10:06:20		70.41		46		24-Apr-08		10:07:53		68		49.5		4-Jun-08		10:25:59		74.01		41.5

		24-Apr-08		12:07:10		70.41		46.5		24-Apr-08		12:06:20		69.8		44.5		24-Apr-08		12:07:53		68		50		4-Jun-08		12:25:59		74.01		44

		24-Apr-08		14:07:10		70.41		46		24-Apr-08		14:06:20		71		36		24-Apr-08		14:07:53		68		49		4-Jun-08		14:25:59		74.01		44.5

		24-Apr-08		16:07:10		70.41		44.5		24-Apr-08		16:06:20		69.8		32		24-Apr-08		16:07:53		68		48		4-Jun-08		16:25:59		73.4		42

		24-Apr-08		18:07:10		69.8		44		24-Apr-08		18:06:20		70.41		31		24-Apr-08		18:07:53		68		45		4-Jun-08		18:25:59		73.4		39

		24-Apr-08		20:07:10		70.41		46		24-Apr-08		20:06:20		69.8		30.5		24-Apr-08		20:07:53		69.2		46.5		4-Jun-08		20:25:59		74.6		39.5

		24-Apr-08		22:07:10		70.41		46		24-Apr-08		22:06:20		68		33		24-Apr-08		22:07:53		68		48.5		4-Jun-08		22:25:59		74.6		38

		25-Apr-08		0:07:10		69.8		45		25-Apr-08		0:06:20		66.2		34		25-Apr-08		0:07:53		68		48.5		5-Jun-08		0:25:59		74.01		37.5

		25-Apr-08		2:07:10		69.2		46		25-Apr-08		2:06:20		65.01		35.5		25-Apr-08		2:07:53		68.61		46		5-Jun-08		2:25:59		72.8		36.5

		25-Apr-08		4:07:10		69.2		45		25-Apr-08		4:06:20		63.8		36		25-Apr-08		4:07:53		68		47.5		5-Jun-08		4:25:59		72.21		36

		25-Apr-08		6:07:10		69.8		45		25-Apr-08		6:06:20		63.21		36		25-Apr-08		6:07:53		68.61		47.5		5-Jun-08		6:25:59		72.21		35.5

		25-Apr-08		8:07:10		69.8		46		25-Apr-08		8:06:20		66.81		35.5		25-Apr-08		8:07:53		68.61		47.5		5-Jun-08		8:25:59		72.21		35.5

		25-Apr-08		10:07:10		69.8		45		25-Apr-08		10:06:20		70.41		32.5		25-Apr-08		10:07:53		67.4		49.5		5-Jun-08		10:25:59		74.01		35.5

		25-Apr-08		12:07:10		70.41		42.5		25-Apr-08		12:06:20		71		28.5		25-Apr-08		12:07:53		68.61		48		5-Jun-08		12:25:59		73.4		35

		25-Apr-08		14:07:10		70.41		45.5		25-Apr-08		14:06:20		71		28		25-Apr-08		14:07:53		68		47.5		5-Jun-08		14:25:59		73.4		34

		25-Apr-08		16:07:10		70.41		46		25-Apr-08		16:06:20		71.6		32.5		25-Apr-08		16:07:53		68.61		48.5		5-Jun-08		16:25:59		74.01		34.5

		25-Apr-08		18:07:10		70.41		45.5		25-Apr-08		18:06:20		70.41		31		25-Apr-08		18:07:53		68		40.5		5-Jun-08		18:25:59		73.4		35

		25-Apr-08		20:07:10		70.41		41.5		25-Apr-08		20:06:20		71		32.5		25-Apr-08		20:07:53		68		48		5-Jun-08		20:25:59		74.01		35.5

		25-Apr-08		22:07:10		69.8		45		25-Apr-08		22:06:20		70.41		35.5		25-Apr-08		22:07:53		68		46		5-Jun-08		22:25:59		74.6		34

		26-Apr-08		0:07:10		70.41		46		26-Apr-08		0:06:20		69.2		36.5		26-Apr-08		0:07:53		68		49		6-Jun-08		0:25:59		74.01		34.5

		26-Apr-08		2:07:10		69.8		45.5		26-Apr-08		2:06:20		67.4		38.5		26-Apr-08		2:07:53		68.61		48		6-Jun-08		2:25:59		72.21		35

		26-Apr-08		4:07:10		69.8		44.5		26-Apr-08		4:06:20		66.2		39		26-Apr-08		4:07:53		68		48		6-Jun-08		4:25:59		71.6		35

		26-Apr-08		6:07:10		69.8		46		26-Apr-08		6:06:20		65.6		38.5		26-Apr-08		6:07:53		68.61		48		6-Jun-08		6:25:59		71.6		35

		26-Apr-08		8:07:10		70.41		46.5		26-Apr-08		8:06:20		68.61		37.5		26-Apr-08		8:07:53		68.61		48.5		6-Jun-08		8:25:59		72.21		37

		26-Apr-08		10:07:10		70.41		45.5		26-Apr-08		10:06:20		71		35.5		26-Apr-08		10:07:53		68		46.5		6-Jun-08		10:25:59		73.4		37.5

		26-Apr-08		12:07:10		71		46.5		26-Apr-08		12:06:20		71		32.5		26-Apr-08		12:07:53		68.61		49		6-Jun-08		12:25:59		73.4		35.5

		26-Apr-08		14:07:10		71		32		26-Apr-08		14:06:20		69.2		31		26-Apr-08		14:07:53		67.4		36		6-Jun-08		14:25:59		74.01		37.5

		26-Apr-08		16:07:10		71		35		26-Apr-08		16:06:20		68.61		36		26-Apr-08		16:07:53		67.4		39.5		6-Jun-08		16:25:59		74.01		38.5

		26-Apr-08		18:07:10		71		39.5		26-Apr-08		18:06:20		69.2		39.5		26-Apr-08		18:07:53		68.61		42.5		6-Jun-08		18:25:59		73.4		38.5

		26-Apr-08		20:07:10		70.41		38		26-Apr-08		20:06:20		69.2		41		26-Apr-08		20:07:53		68.61		41		6-Jun-08		20:25:59		74.01		41

		26-Apr-08		22:07:10		69.8		38		26-Apr-08		22:06:20		68		42		26-Apr-08		22:07:53		68.61		40.5		6-Jun-08		22:25:59		74.6		39

		27-Apr-08		0:07:10		69.8		36.5		27-Apr-08		0:06:20		68		39.5		27-Apr-08		0:07:53		68.61		39.5		7-Jun-08		0:25:59		74.01		38.5

		27-Apr-08		2:07:10		70.41		36.5		27-Apr-08		2:06:20		68		39.5		27-Apr-08		2:07:53		68.61		39.5		7-Jun-08		2:25:59		72.8		39

		27-Apr-08		4:07:10		70.41		37.5		27-Apr-08		4:06:20		66.81		42.5		27-Apr-08		4:07:53		68.61		39.5		7-Jun-08		4:25:59		71.6		38.5

		27-Apr-08		6:07:10		69.8		36		27-Apr-08		6:06:20		67.4		40.5		27-Apr-08		6:07:53		68		39		7-Jun-08		6:25:59		72.21		37.5

		27-Apr-08		8:07:10		69.8		37.5		27-Apr-08		8:06:20		68		42		27-Apr-08		8:07:53		68.61		40.5		7-Jun-08		8:25:59		72.21		38

		27-Apr-08		10:07:10		70.41		40		27-Apr-08		10:06:20		69.2		43		27-Apr-08		10:07:53		68.61		42.5		7-Jun-08		10:25:59		73.4		37.5

		27-Apr-08		12:07:10		71		40		27-Apr-08		12:06:20		69.2		42.5		27-Apr-08		12:07:53		68		44		7-Jun-08		12:25:59		73.4		36

		27-Apr-08		14:07:10		71		40		27-Apr-08		14:06:20		69.2		40.5		27-Apr-08		14:07:53		69.2		42.5		7-Jun-08		14:25:59		73.4		34

		27-Apr-08		16:07:10		71		43		27-Apr-08		16:06:20		69.2		47		27-Apr-08		16:07:53		69.2		46		7-Jun-08		16:25:59		73.4		33.5

		27-Apr-08		18:07:10		71		42.5		27-Apr-08		18:06:20		69.2		43.5		27-Apr-08		18:07:53		69.2		44		7-Jun-08		18:25:59		73.4		34

		27-Apr-08		20:07:10		71.6		38		27-Apr-08		20:06:20		68		43.5		27-Apr-08		20:07:53		68.61		42.5		7-Jun-08		20:25:59		74.01		35

		27-Apr-08		22:07:10		71		37.5		27-Apr-08		22:06:20		68		42.5		27-Apr-08		22:07:53		68.61		41		7-Jun-08		22:25:59		74.01		33.5

		28-Apr-08		0:07:10		70.41		38.5		28-Apr-08		0:06:20		68		40		28-Apr-08		0:07:53		68.61		40		8-Jun-08		0:25:59		73.4		33

		28-Apr-08		2:07:10		69.8		39.5		28-Apr-08		2:06:20		68		45		28-Apr-08		2:07:53		68.61		42		8-Jun-08		2:25:59		72.21		33

		28-Apr-08		4:07:10		69.2		39.5		28-Apr-08		4:06:20		67.4		47.5		28-Apr-08		4:07:53		68		41.5		8-Jun-08		4:25:59		71.6		33

		28-Apr-08		6:07:10		69.2		39.5		28-Apr-08		6:06:20		67.4		45		28-Apr-08		6:07:53		68		41.5		8-Jun-08		6:25:59		71.6		33

		28-Apr-08		8:07:10		70.41		40		28-Apr-08		8:06:20		68		47		28-Apr-08		8:07:53		68.61		42.5		8-Jun-08		8:25:59		71.6		33

		28-Apr-08		10:07:10		70.41		40.5		28-Apr-08		10:06:20		68		47.5		28-Apr-08		10:07:53		68.61		43		8-Jun-08		10:25:59		72.21		34

		28-Apr-08		12:07:10		71		40		28-Apr-08		12:06:20		68.61		44		28-Apr-08		12:07:53		69.2		43		8-Jun-08		12:25:59		74.6		33

		28-Apr-08		14:07:10		71		43		28-Apr-08		14:06:20		69.2		43		28-Apr-08		14:07:53		69.2		45.5		8-Jun-08		14:25:59		75.81		31.5

		28-Apr-08		16:07:10		71		44		28-Apr-08		16:06:20		68.61		52		28-Apr-08		16:07:53		69.2		47		8-Jun-08		16:25:59		77		30.5

		28-Apr-08		18:07:10		71		41.5		28-Apr-08		18:06:20		69.2		46		28-Apr-08		18:07:53		68.61		45		8-Jun-08		18:25:59		77		31.5

		28-Apr-08		20:07:10		71		39		28-Apr-08		20:06:20		68.61		45		28-Apr-08		20:07:53		68.61		43		8-Jun-08		20:25:59		77		33.5

		28-Apr-08		22:07:10		71		38.5		28-Apr-08		22:06:20		68.61		43.5		28-Apr-08		22:07:53		68.61		41.5		8-Jun-08		22:25:59		75.81		34.5

		29-Apr-08		0:07:10		69.2		38.5		29-Apr-08		0:06:20		68		45		29-Apr-08		0:07:53		68		41		9-Jun-08		0:25:59		74.6		34

		29-Apr-08		2:07:10		69.8		38		29-Apr-08		2:06:20		67.4		44.5		29-Apr-08		2:07:53		68.61		40.5		9-Jun-08		2:25:59		74.01		34.5

		29-Apr-08		4:07:10		69.8		37.5		29-Apr-08		4:06:20		66.81		44		29-Apr-08		4:07:53		68.61		40		9-Jun-08		4:25:59		72.8		35

		29-Apr-08		6:07:10		69.2		36.5		29-Apr-08		6:06:20		66.2		44		29-Apr-08		6:07:53		68.61		39		9-Jun-08		6:25:59		72.21		35.5

		29-Apr-08		8:07:10		69.8		38.5		29-Apr-08		8:06:20		68		44.5		29-Apr-08		8:07:53		68		41		9-Jun-08		8:25:59		72.21		36.5

		29-Apr-08		10:07:10		70.41		39.5		29-Apr-08		10:06:20		69.8		45		29-Apr-08		10:07:53		68		43		9-Jun-08		10:25:59		74.01		37

		29-Apr-08		12:07:10		71		42		29-Apr-08		12:06:20		70.41		48.5		29-Apr-08		12:07:53		69.2		44.5		9-Jun-08		12:25:59		76.4		36

		29-Apr-08		14:07:10		71		42.5		29-Apr-08		14:06:20		70.41		48		29-Apr-08		14:07:53		68.61		46.5		9-Jun-08		14:25:59		77.61		35

		29-Apr-08		16:07:10		71		43		29-Apr-08		16:06:20		69.8		49		29-Apr-08		16:07:53		68.61		47		9-Jun-08		16:25:59		78.8		34.5

		29-Apr-08		18:07:10		71.6		41.5		29-Apr-08		18:06:20		69.2		48.5		29-Apr-08		18:07:53		68.61		45.5		9-Jun-08		18:25:59		78.2		35.5

		29-Apr-08		20:07:10		71		40		29-Apr-08		20:06:20		69.2		46.5		29-Apr-08		20:07:53		68.61		43.5		9-Jun-08		20:25:59		78.2		35.5

		29-Apr-08		22:07:10		71		39		29-Apr-08		22:06:20		69.2		47.5		29-Apr-08		22:07:53		68.61		42.5		9-Jun-08		22:25:59		76.4		35.5

		30-Apr-08		0:07:10		69.2		33		30-Apr-08		0:06:20		68		34		30-Apr-08		0:07:53		68		35.5		10-Jun-08		0:25:59		74.6		35.5

		30-Apr-08		2:07:10		69.2		35.5		30-Apr-08		2:06:20		68.61		37.5		30-Apr-08		2:07:53		68.61		37.5		10-Jun-08		2:25:59		73.4		36

		30-Apr-08		4:07:10		69.8		35		30-Apr-08		4:06:20		67.4		38.5		30-Apr-08		4:07:53		68.61		37		10-Jun-08		4:25:59		72.8		36

		30-Apr-08		6:07:10		70.41		35		30-Apr-08		6:06:20		69.2		39		30-Apr-08		6:07:53		68.61		38		10-Jun-08		6:25:59		72.21		37

		30-Apr-08		8:07:10		70.41		34		30-Apr-08		8:06:20		69.8		34		30-Apr-08		8:07:53		68		36.5		10-Jun-08		8:25:59		72.8		39

		30-Apr-08		10:07:10		69.2		34		30-Apr-08		10:06:20		69.8		35		30-Apr-08		10:07:53		67.4		37.5		10-Jun-08		10:25:59		73.4		38.5

		30-Apr-08		12:07:10		69.8		32.5		30-Apr-08		12:06:20		69.8		35		30-Apr-08		12:07:53		68		36		10-Jun-08		12:25:59		72.8		39

		30-Apr-08		14:07:10		69.8		33.5		30-Apr-08		14:06:20		69.2		34		30-Apr-08		14:07:53		68.61		36		10-Jun-08		14:25:59		72.8		39

		30-Apr-08		16:07:10		69.8		34		30-Apr-08		16:06:20		69.2		35		30-Apr-08		16:07:53		68.61		36.5		10-Jun-08		16:25:59		72.21		40

		30-Apr-08		18:07:10		69.8		31		30-Apr-08		18:06:20		69.2		32		30-Apr-08		18:07:53		68		33.5		10-Jun-08		18:25:59		72.8		42.5

		30-Apr-08		20:07:10		68.61		31.5		30-Apr-08		20:06:20		68.61		31.5		30-Apr-08		20:07:53		68		33.5		10-Jun-08		20:25:59		74.6		43

		30-Apr-08		22:07:10		69.2		31		30-Apr-08		22:06:20		68.61		32.5		30-Apr-08		22:07:53		68.61		33.5		10-Jun-08		22:25:59		76.4		40.5

		1-May-08		0:07:10		68.61		31.5		1-May-08		0:06:20		67.4		34		1-May-08		0:07:53		68		34		11-Jun-08		0:25:59		75.81		40.5

		1-May-08		2:07:10		68.61		30.5		1-May-08		2:06:20		66.2		33		1-May-08		2:07:53		68		32.5		11-Jun-08		2:25:59		75.2		39

		1-May-08		4:07:10		68		29.5		1-May-08		4:06:20		65.6		32		1-May-08		4:07:53		68		31		11-Jun-08		4:25:59		74.01		38

		1-May-08		6:07:10		68.61		29		1-May-08		6:06:20		65.6		31.5		1-May-08		6:07:53		68		30.5		11-Jun-08		6:25:59		72.8		37.5

		1-May-08		8:07:10		69.2		28		1-May-08		8:06:20		69.2		30		1-May-08		8:07:53		68.61		30.5		11-Jun-08		8:25:59		72.21		37

		1-May-08		10:07:10		69.8		26		1-May-08		10:06:20		70.41		27.5		1-May-08		10:07:53		68.61		29		11-Jun-08		10:25:59		72.8		33

		1-May-08		12:07:10		69.8		24		1-May-08		12:06:20		70.41		24.5		1-May-08		12:07:53		68.61		27		11-Jun-08		12:25:59		72.8		30.5

		1-May-08		14:07:10		70.41		25		1-May-08		14:06:20		71		26		1-May-08		14:07:53		69.8		27		11-Jun-08		14:25:59		74.01		30.5

		1-May-08		16:07:10		71		25.5		1-May-08		16:06:20		69.8		27.5		1-May-08		16:07:53		69.2		27.5		11-Jun-08		16:25:59		74.01		30.5

		1-May-08		18:07:10		70.41		29		1-May-08		18:06:20		70.41		29.5		1-May-08		18:07:53		69.8		30		11-Jun-08		18:25:59		73.4		32

		1-May-08		20:07:10		69.2		29.5		1-May-08		20:06:20		69.2		30		1-May-08		20:07:53		69.2		31		11-Jun-08		20:25:59		74.6		32.5

		1-May-08		22:07:10		69.2		30.5		1-May-08		22:06:20		69.8		30.5		1-May-08		22:07:53		69.2		32		11-Jun-08		22:25:59		75.2		32

		2-May-08		0:07:10		69.8		30.5		2-May-08		0:06:20		68		33		2-May-08		0:07:53		69.2		32.5		12-Jun-08		0:25:59		74.6		32

		2-May-08		2:07:10		69.8		30.5		2-May-08		2:06:20		67.4		33.5		2-May-08		2:07:53		69.2		32		12-Jun-08		2:25:59		73.4		32.5

		2-May-08		4:07:10		69.2		30.5		2-May-08		4:06:20		66.81		34		2-May-08		4:07:53		69.2		31.5		12-Jun-08		4:25:59		72.21		32.5

		2-May-08		6:07:10		69.2		30		2-May-08		6:06:20		66.81		34		2-May-08		6:07:53		69.2		32		12-Jun-08		6:25:59		71.6		32.5

		2-May-08		8:07:10		69.8		30.5		2-May-08		8:06:20		69.2		33		2-May-08		8:07:53		69.8		32		12-Jun-08		8:25:59		72.21		34.5

		2-May-08		10:07:10		69.8		30		2-May-08		10:06:20		69.8		31.5		2-May-08		10:07:53		69.8		31.5		12-Jun-08		10:25:59		73.4		34.5

		2-May-08		12:07:10		70.41		27		2-May-08		12:06:20		69.8		28		2-May-08		12:07:53		70.41		29.5		12-Jun-08		12:25:59		73.4		32.5

		2-May-08		14:07:10		71		23.5		2-May-08		14:06:20		71		25.5		2-May-08		14:07:53		69.8		26		12-Jun-08		14:25:59		72.8		29

		2-May-08		16:07:10		70.41		29.5		2-May-08		16:06:20		69.8		31		2-May-08		16:07:53		69.2		31		12-Jun-08		16:25:59		73.4		27.5

		2-May-08		18:07:10		70.41		30.5		2-May-08		18:06:20		70.41		31.5		2-May-08		18:07:53		69.8		32		12-Jun-08		18:25:59		73.4		29

		2-May-08		20:07:10		71		34		2-May-08		20:06:20		70.41		34		2-May-08		20:07:53		69.8		34		12-Jun-08		20:25:59		74.6		31.5

		2-May-08		22:07:10		70.41		29		2-May-08		22:06:20		70.41		30		2-May-08		22:07:53		70.41		31		12-Jun-08		22:25:59		75.2		32.5

		3-May-08		0:07:10		69.2		30		3-May-08		0:06:20		69.2		31		3-May-08		0:07:53		69.8		31.5		13-Jun-08		0:25:59		74.6		33

		3-May-08		2:07:10		70.41		33		3-May-08		2:06:20		68.61		36		3-May-08		2:07:53		69.8		34		13-Jun-08		2:25:59		73.4		33.5

		3-May-08		4:07:10		70.41		32.5		3-May-08		4:06:20		67.4		36		3-May-08		4:07:53		69.8		33.5		13-Jun-08		4:25:59		72.8		34

		3-May-08		6:07:10		70.41		32		3-May-08		6:06:20		66.81		36.5		3-May-08		6:07:53		69.8		33.5		13-Jun-08		6:25:59		71.6		35

		3-May-08		8:07:10		70.41		33.5		3-May-08		8:06:20		69.8		35.5		3-May-08		8:07:53		69.2		35		13-Jun-08		8:25:59		72.21		37

		3-May-08		10:07:10		70.41		34		3-May-08		10:06:20		70.41		35.5		3-May-08		10:07:53		69.8		35.5		13-Jun-08		10:25:59		72.21		37

		3-May-08		12:07:10		71		33.5		3-May-08		12:06:20		71		34		3-May-08		12:07:53		69.8		34.5		13-Jun-08		12:25:59		72.21		30.5

		3-May-08		14:07:10		71		36.5		3-May-08		14:06:20		71.6		35		3-May-08		14:07:53		69.8		36.5		13-Jun-08		14:25:59		73.4		27.5

		3-May-08		16:07:10		71		34		3-May-08		16:06:20		70.41		35.5		3-May-08		16:07:53		69.8		36.5		13-Jun-08		16:25:59		73.4		30.5

		3-May-08		18:07:10		71		37.5		3-May-08		18:06:20		71		40		3-May-08		18:07:53		69.8		39		13-Jun-08		18:25:59		73.4		28.5

		3-May-08		20:07:10		71		36.5		3-May-08		20:06:20		70.41		40		3-May-08		20:07:53		69.8		38		13-Jun-08		20:25:59		74.6		29

		3-May-08		22:07:10		71		35.5		3-May-08		22:06:20		69.8		39		3-May-08		22:07:53		69.8		37		13-Jun-08		22:25:59		75.81		29.5

		4-May-08		0:07:10		71		35		4-May-08		0:06:20		68		40		4-May-08		0:07:53		69.2		37		14-Jun-08		0:25:59		75.2		30.5

		4-May-08		2:07:10		70.41		35		4-May-08		2:06:20		66.81		41		4-May-08		2:07:53		69.8		36.5		14-Jun-08		2:25:59		74.01		31.5

		4-May-08		4:07:10		70.41		34.5		4-May-08		4:06:20		66.2		41		4-May-08		4:07:53		69.2		35.5		14-Jun-08		4:25:59		72.8		32

		4-May-08		6:07:10		69.8		33.5		4-May-08		6:06:20		65.6		40		4-May-08		6:07:53		69.8		35		14-Jun-08		6:25:59		72.21		33.5

		4-May-08		8:07:10		70.41		35.5		4-May-08		8:06:20		66.81		41.5		4-May-08		8:07:53		70.41		36		14-Jun-08		8:25:59		72.21		35.5

		4-May-08		10:07:10		70.41		36		4-May-08		10:06:20		69.8		39		4-May-08		10:07:53		70.41		37.5		14-Jun-08		10:25:59		72.8		37

		4-May-08		12:07:10		71		37		4-May-08		12:06:20		71		39.5		4-May-08		12:07:53		70.41		39		14-Jun-08		12:25:59		72.8		39.5

		4-May-08		14:07:10		71		39.5		4-May-08		14:06:20		70.41		45.5		4-May-08		14:07:53		68.61		42.5		14-Jun-08		14:25:59		73.4		38

		4-May-08		16:07:10		71		39.5		4-May-08		16:06:20		70.41		44.5		4-May-08		16:07:53		68.61		43.5		14-Jun-08		16:25:59		72.8		38.5

		4-May-08		18:07:10		71		40		4-May-08		18:06:20		69.8		48		4-May-08		18:07:53		69.2		43		14-Jun-08		18:25:59		73.4		38.5

		4-May-08		20:07:10		71		38.5		4-May-08		20:06:20		69.2		47		4-May-08		20:07:53		68.61		42		14-Jun-08		20:25:59		74.01		37

		4-May-08		22:07:10		71		38		4-May-08		22:06:20		69.8		44		4-May-08		22:07:53		68.61		40.5		14-Jun-08		22:25:59		74.01		37.5

		5-May-08		0:07:10		71		37.5		5-May-08		0:06:20		68.61		44		5-May-08		0:07:53		70.41		39.5		15-Jun-08		0:25:59		72.8		37

		5-May-08		2:07:10		71		37		5-May-08		2:06:20		68		44.5		5-May-08		2:07:53		70.41		38.5		15-Jun-08		2:25:59		72.21		37.5

		5-May-08		4:07:10		70.41		36.5		5-May-08		4:06:20		66.81		44.5		5-May-08		4:07:53		69.8		37.5		15-Jun-08		4:25:59		71.6		37.5

		5-May-08		6:07:10		69.8		35		5-May-08		6:06:20		66.2		43		5-May-08		6:07:53		69.8		37		15-Jun-08		6:25:59		71.6		37.5

		5-May-08		8:07:10		69.8		37		5-May-08		8:06:20		66.2		44.5		5-May-08		8:07:53		69.8		37.5		15-Jun-08		8:25:59		72.21		38

		5-May-08		10:07:10		69.8		38		5-May-08		10:06:20		68.61		44		5-May-08		10:07:53		69.8		39		15-Jun-08		10:25:59		72.21		39

		5-May-08		12:07:10		70.41		40		5-May-08		12:06:20		70.41		45		5-May-08		12:07:53		71		40.5		15-Jun-08		12:25:59		73.4		40

		5-May-08		14:07:10		71		40		5-May-08		14:06:20		71		44.5		5-May-08		14:07:53		71		41.5		15-Jun-08		14:25:59		74.6		41

		5-May-08		16:07:10		71		38		5-May-08		16:06:20		69.8		42		5-May-08		16:07:53		70.41		40		15-Jun-08		16:25:59		75.2		41.5

		5-May-08		18:07:10		71		37.5		5-May-08		18:06:20		70.41		41.5		5-May-08		18:07:53		70.41		39		15-Jun-08		18:25:59		75.81		41

		5-May-08		20:07:10		71		37		5-May-08		20:06:20		70.41		41.5		5-May-08		20:07:53		69.8		38.5		15-Jun-08		20:25:59		75.2		40

		5-May-08		22:07:10		70.41		37		5-May-08		22:06:20		69.8		41		5-May-08		22:07:53		69.8		38.5		15-Jun-08		22:25:59		74.01		39.5

		6-May-08		0:07:10		71		36.5		6-May-08		0:06:20		69.2		42		6-May-08		0:07:53		70.41		38		16-Jun-08		0:25:59		72.8		39

		6-May-08		2:07:10		71		36.5		6-May-08		2:06:20		67.4		43		6-May-08		2:07:53		70.41		37.5		16-Jun-08		2:25:59		72.21		39

		6-May-08		4:07:10		70.41		36		6-May-08		4:06:20		66.81		43		6-May-08		4:07:53		69.8		37		16-Jun-08		4:25:59		71.6		39

		6-May-08		6:07:10		69.8		35.5		6-May-08		6:06:20		65.6		43		6-May-08		6:07:53		69.2		37		16-Jun-08		6:25:59		71		39

		6-May-08		8:07:10		70.41		38		6-May-08		8:06:20		68		43.5		6-May-08		8:07:53		68.61		42		16-Jun-08		8:25:59		70.41		39.5

		6-May-08		10:07:10		70.41		39		6-May-08		10:06:20		71		44		6-May-08		10:07:53		67.4		41.5		16-Jun-08		10:25:59		70.41		40.5

		6-May-08		12:07:10		70.41		40.5		6-May-08		12:06:20		71.6		45		6-May-08		12:07:53		67.4		44		16-Jun-08		12:25:59		72.21		41.5

		6-May-08		14:07:10		71		40.5		6-May-08		14:06:20		71		44.5		6-May-08		14:07:53		67.4		44.5		16-Jun-08		14:25:59		73.4		42.5

		6-May-08		16:07:10		71		40		6-May-08		16:06:20		70.41		46.5		6-May-08		16:07:53		68.61		43.5		16-Jun-08		16:25:59		74.6		41

		6-May-08		18:07:10		70.41		39		6-May-08		18:06:20		69.2		45.5		6-May-08		18:07:53		68.61		41		16-Jun-08		18:25:59		75.2		40

		6-May-08		20:07:10		70.41		39.5		6-May-08		20:06:20		68.61		45		6-May-08		20:07:53		68.61		41.5		16-Jun-08		20:25:59		75.2		39

		6-May-08		22:07:10		70.41		38		6-May-08		22:06:20		69.2		44		6-May-08		22:07:53		68.61		41		16-Jun-08		22:25:59		74.01		38.5

		7-May-08		0:07:10		70.41		38.5		7-May-08		0:06:20		68.61		45		7-May-08		0:07:53		68.61		41		17-Jun-08		0:25:59		72.21		38

		7-May-08		2:07:10		70.41		38.5		7-May-08		2:06:20		68		46.5		7-May-08		2:07:53		68		41.5		17-Jun-08		2:25:59		71		37.5

		7-May-08		4:07:10		69.8		38		7-May-08		4:06:20		67.4		47		7-May-08		4:07:53		68.61		40.5		17-Jun-08		4:25:59		70.41		38.5

		7-May-08		6:07:10		70.41		39		7-May-08		6:06:20		66.81		47.5		7-May-08		6:07:53		68		42		17-Jun-08		6:25:59		70.41		39.5

		7-May-08		8:07:10		70.41		39		7-May-08		8:06:20		69.8		45		7-May-08		8:07:53		68.61		41.5		17-Jun-08		8:25:59		70.41		41.5

		7-May-08		10:07:10		71		38.5		7-May-08		10:06:20		70.41		45		7-May-08		10:07:53		68		42		17-Jun-08		10:25:59		71.6		42.5

		7-May-08		12:07:10		71		40.5		7-May-08		12:06:20		70.41		47		7-May-08		12:07:53		68		43.5		17-Jun-08		12:25:59		73.4		42.5

		7-May-08		14:07:10		71		43.5		7-May-08		14:06:20		69.8		51		7-May-08		14:07:53		68.61		46.5		17-Jun-08		14:25:59		74.01		43.5

		7-May-08		16:07:10		71		43		7-May-08		16:06:20		70.41		56		7-May-08		16:07:53		68.61		46.5		17-Jun-08		16:25:59		74.6		41

		7-May-08		18:07:10		70.41		43.5		7-May-08		18:06:20		71		50		7-May-08		18:07:53		68		46.5		17-Jun-08		18:25:59		74.01		40

		7-May-08		20:07:10		71		36.5		7-May-08		20:06:20		70.41		39		7-May-08		20:07:53		68		41		17-Jun-08		20:25:59		74.01		39.5

		7-May-08		22:07:10		71		34.5		7-May-08		22:06:20		69.8		36		7-May-08		22:07:53		68		38		17-Jun-08		22:25:59		74.01		38.5

		8-May-08		0:07:10		69.8		37		8-May-08		0:06:20		69.8		40.5		8-May-08		0:07:53		68		40		18-Jun-08		0:25:59		72.8		38

		8-May-08		2:07:10		70.41		37		8-May-08		2:06:20		68.61		41		8-May-08		2:07:53		69.2		39		18-Jun-08		2:25:59		71.6		37.5

		8-May-08		4:07:10		70.41		36		8-May-08		4:06:20		68		41.5		8-May-08		4:07:53		69.8		37.5		18-Jun-08		4:25:59		70.41		38.5

		8-May-08		6:07:10		71		34.5		8-May-08		6:06:20		68		39.5		8-May-08		6:07:53		68.61		38		18-Jun-08		6:25:59		70.41		39.5

		8-May-08		8:07:10		71		34.5		8-May-08		8:06:20		69.8		37		8-May-08		8:07:53		68.61		38		18-Jun-08		8:25:59		70.41		41.5

		8-May-08		10:07:10		70.41		36		8-May-08		10:06:20		70.41		38.5		8-May-08		10:07:53		68.61		38		18-Jun-08		10:25:59		72.8		42

		8-May-08		12:07:10		70.41		37		8-May-08		12:06:20		71		38.5		8-May-08		12:07:53		67.4		40.5		18-Jun-08		12:25:59		72.8		41.5

		8-May-08		14:07:10		70.41		39		8-May-08		14:06:20		71		41		8-May-08		14:07:53		67.4		43		18-Jun-08		14:25:59		72.8		42.5

		8-May-08		16:07:10		71		38.5		8-May-08		16:06:20		70.41		43		8-May-08		16:07:53		68		41.5		18-Jun-08		16:25:59		73.4		43

		8-May-08		18:07:10		71		39		8-May-08		18:06:20		71		41.5		8-May-08		18:07:53		68.61		42		18-Jun-08		18:25:59		74.01		34.5

		8-May-08		20:07:10		71		38		8-May-08		20:06:20		70.41		43.5		8-May-08		20:07:53		68		41.5		18-Jun-08		20:25:59		74.6		32

		8-May-08		22:07:10		70.41		37		8-May-08		22:06:20		69.8		41		8-May-08		22:07:53		68		40		18-Jun-08		22:25:59		74.6		30.5

		9-May-08		0:07:10		70.41		37		9-May-08		0:06:20		68.61		41.5		9-May-08		0:07:53		68		40		19-Jun-08		0:25:59		74.01		30.5

		9-May-08		2:07:10		70.41		36.5		9-May-08		2:06:20		67.4		42		9-May-08		2:07:53		68.61		39		19-Jun-08		2:25:59		73.4		31.5

		9-May-08		4:07:10		69.8		35.5		9-May-08		4:06:20		66.81		42.5		9-May-08		4:07:53		69.2		38		19-Jun-08		4:25:59		72.21		33

		9-May-08		6:07:10		71		35.5		9-May-08		6:06:20		66.81		41.5		9-May-08		6:07:53		69.2		37.5		19-Jun-08		6:25:59		71		33.5

		9-May-08		8:07:10		71		37		9-May-08		8:06:20		69.8		42		9-May-08		8:07:53		69.2		39		19-Jun-08		8:25:59		71		35.5

		9-May-08		10:07:10		70.41		38		9-May-08		10:06:20		71		40.5		9-May-08		10:07:53		68.61		40		19-Jun-08		10:25:59		72.8		35.5

		9-May-08		12:07:10		70.41		40		9-May-08		12:06:20		71.6		43		9-May-08		12:07:53		69.2		41.5		19-Jun-08		12:25:59		73.4		33.5

		9-May-08		14:07:10		70.41		39		9-May-08		14:06:20		69.8		45.5		9-May-08		14:07:53		68		42.5		19-Jun-08		14:25:59		72.21		35.5

		9-May-08		16:07:10		70.41		38		9-May-08		16:06:20		69.2		43		9-May-08		16:07:53		67.4		42.5		19-Jun-08		16:25:59		72.21		33.5

		9-May-08		18:07:10		70.41		38.5		9-May-08		18:06:20		68.61		42.5		9-May-08		18:07:53		68.61		41.5		19-Jun-08		18:25:59		74.01		28.5

		9-May-08		20:07:10		70.41		37		9-May-08		20:06:20		68.61		42		9-May-08		20:07:53		68		40		19-Jun-08		20:25:59		74.6		29

		9-May-08		22:07:10		69.8		36.5		9-May-08		22:06:20		68		41.5		9-May-08		22:07:53		68.61		39		19-Jun-08		22:25:59		75.2		27.5

		10-May-08		0:07:10		69.8		35.5		10-May-08		0:06:20		68		40.5		10-May-08		0:07:53		68		39		20-Jun-08		0:25:59		74.6		30

		10-May-08		2:07:10		69.8		34.5		10-May-08		2:06:20		66.81		40.5		10-May-08		2:07:53		68		37.5		20-Jun-08		2:25:59		73.4		31

		10-May-08		4:07:10		69.8		34		10-May-08		4:06:20		66.2		40.5		10-May-08		4:07:53		68.61		37		20-Jun-08		4:25:59		72.8		31.5

		10-May-08		6:07:10		70.41		33.5		10-May-08		6:06:20		65.6		39.5		10-May-08		6:07:53		68.61		35.5		20-Jun-08		6:25:59		71.6		32.5

		10-May-08		8:07:10		70.41		35.5		10-May-08		8:06:20		68		41.5		10-May-08		8:07:53		67.4		38.5		20-Jun-08		8:25:59		72.21		35

		10-May-08		10:07:10		69.8		34		10-May-08		10:06:20		70.41		35		10-May-08		10:07:53		68		37.5		20-Jun-08		10:25:59		73.4		36.5

		10-May-08		12:07:10		71		33.5		10-May-08		12:06:20		71		34.5		10-May-08		12:07:53		68.61		36.5		20-Jun-08		12:25:59		72.8		35

		10-May-08		14:07:10		71.6		32		10-May-08		14:06:20		70.41		34.5		10-May-08		14:07:53		68		35.5		20-Jun-08		14:25:59		72.8		33.5

		10-May-08		16:07:10		71.6		35		10-May-08		16:06:20		69.8		38.5		10-May-08		16:07:53		67.4		40.5		20-Jun-08		16:25:59		72.8		34

		10-May-08		18:07:10		71.6		36		10-May-08		18:06:20		69.2		39.5		10-May-08		18:07:53		67.4		41.5		20-Jun-08		18:25:59		72.8		31

		10-May-08		20:07:10		71		35.5		10-May-08		20:06:20		68.61		40.5		10-May-08		20:07:53		68		39.5		20-Jun-08		20:25:59		74.6		31.5

		10-May-08		22:07:10		70.41		35.5		10-May-08		22:06:20		68.61		39.5		10-May-08		22:07:53		68		38.5		20-Jun-08		22:25:59		75.81		30.5

		11-May-08		0:07:10		70.41		35.5		11-May-08		0:06:20		68.61		39.5		11-May-08		0:07:53		68		38.5		21-Jun-08		0:25:59		75.2		31.5

		11-May-08		2:07:10		70.41		35		11-May-08		2:06:20		67.4		40		11-May-08		2:07:53		68		38		21-Jun-08		2:25:59		74.01		32

		11-May-08		4:07:10		69.8		34		11-May-08		4:06:20		66.81		40.5		11-May-08		4:07:53		68.61		37		21-Jun-08		4:25:59		73.4		32.5

		11-May-08		6:07:10		70.41		34.5		11-May-08		6:06:20		68		39		11-May-08		6:07:53		68.61		36.5		21-Jun-08		6:25:59		72.21		34

		11-May-08		8:07:10		70.41		35.5		11-May-08		8:06:20		69.8		39		11-May-08		8:07:53		68		38.5		21-Jun-08		8:25:59		72.8		35.5

		11-May-08		10:07:10		70.41		35		11-May-08		10:06:20		69.8		36.5		11-May-08		10:07:53		68.61		37.5		21-Jun-08		10:25:59		72.8		35.5

		11-May-08		12:07:10		71		35.5		11-May-08		12:06:20		70.41		38		11-May-08		12:07:53		68.61		39		21-Jun-08		12:25:59		72.8		33.5

		11-May-08		14:07:10		71.6		38		11-May-08		14:06:20		69.2		41		11-May-08		14:07:53		68.61		41.5		21-Jun-08		14:25:59		72.8		32

		11-May-08		16:07:10		71.6		37.5		11-May-08		16:06:20		68.61		40		11-May-08		16:07:53		68.61		40.5		21-Jun-08		16:25:59		73.4		30

		11-May-08		18:07:10		71.6		38.5		11-May-08		18:06:20		69.2		44		11-May-08		18:07:53		68.61		42.5		21-Jun-08		18:25:59		71.6		27

		11-May-08		20:07:10		71.6		39		11-May-08		20:06:20		69.2		50		11-May-08		20:07:53		68.61		43.5		21-Jun-08		20:25:59		74.01		26.5

		11-May-08		22:07:10		71		38.5		11-May-08		22:06:20		68.61		46.5		11-May-08		22:07:53		69.2		41.5		21-Jun-08		22:25:59		75.81		25.5

		12-May-08		0:07:10		69.8		38.5		12-May-08		0:06:20		68.61		47.5		12-May-08		0:07:53		69.2		41		22-Jun-08		0:25:59		75.81		27.5

		12-May-08		2:07:10		70.41		39		12-May-08		2:06:20		68.61		47.5		12-May-08		2:07:53		69.8		41		22-Jun-08		2:25:59		75.2		29

		12-May-08		4:07:10		70.41		38		12-May-08		4:06:20		68		47		12-May-08		4:07:53		69.8		40		22-Jun-08		4:25:59		74.01		29.5

		12-May-08		6:07:10		71		38		12-May-08		6:06:20		67.4		47		12-May-08		6:07:53		69.8		40		22-Jun-08		6:25:59		74.6		30

		12-May-08		8:07:10		71		38.5		12-May-08		8:06:20		67.4		47.5		12-May-08		8:07:53		69.8		40.5		22-Jun-08		8:25:59		75.2		30.5

		12-May-08		10:07:10		70.41		39		12-May-08		10:06:20		68.61		45		12-May-08		10:07:53		69.8		40.5		22-Jun-08		10:25:59		77		31

		12-May-08		12:07:10		70.41		40		12-May-08		12:06:20		69.2		44.5		12-May-08		12:07:53		69.8		41.5		22-Jun-08		12:25:59		78.2		29.5

		12-May-08		14:07:10		71		33		12-May-08		14:06:20		69.2		32		12-May-08		14:07:53		69.8		34.5		22-Jun-08		14:25:59		79.41		28.5

		12-May-08		16:07:10		71		29.5		12-May-08		16:06:20		69.8		29.5		12-May-08		16:07:53		69.8		31		22-Jun-08		16:25:59		79.41		27

		12-May-08		18:07:10		71.6		31.5		12-May-08		18:06:20		69.8		33		12-May-08		18:07:53		69.8		33		22-Jun-08		18:25:59		78.8		25

		12-May-08		20:07:10		71.6		30.5		12-May-08		20:06:20		69.2		33		12-May-08		20:07:53		69.8		33		22-Jun-08		20:25:59		78.8		25

		12-May-08		22:07:10		70.41		30.5		12-May-08		22:06:20		68		33		12-May-08		22:07:53		69.8		32.5		22-Jun-08		22:25:59		77.61		27

		13-May-08		0:07:10		68.61		31		13-May-08		0:06:20		68.61		32.5		13-May-08		0:07:53		68.61		32.5		23-Jun-08		0:25:59		76.4		29

		13-May-08		2:07:10		68		32		13-May-08		2:06:20		68		33		13-May-08		2:07:53		68		33		23-Jun-08		2:25:59		75.2		31

		13-May-08		4:07:10		68		31.5		13-May-08		4:06:20		68.61		32		13-May-08		4:07:53		68		32.5		23-Jun-08		4:25:59		74.01		32

		13-May-08		6:07:10		68		30.5		13-May-08		6:06:20		68.61		31		13-May-08		6:07:53		68		32		23-Jun-08		6:25:59		73.4		32.5

		13-May-08		8:07:10		68.61		29		13-May-08		8:06:20		69.2		31		13-May-08		8:07:53		68.61		31.5		23-Jun-08		8:25:59		72.8		34

		13-May-08		10:07:10		69.8		28		13-May-08		10:06:20		70.41		29.5		13-May-08		10:07:53		68.61		30.5		23-Jun-08		10:25:59		74.01		35.5

		13-May-08		12:07:10		71		27.5		13-May-08		12:06:20		71.6		29		13-May-08		12:07:53		68.61		30.5		23-Jun-08		12:25:59		75.2		35.5

		13-May-08		14:07:10		71.6		28.5		13-May-08		14:06:20		71		30		13-May-08		14:07:53		68.61		31.5		23-Jun-08		14:25:59		76.4		36

		13-May-08		16:07:10		71.6		29.5		13-May-08		16:06:20		69.2		32.5		13-May-08		16:07:53		68.61		33		23-Jun-08		16:25:59		77		36

		13-May-08		18:07:10		71.6		30.5		13-May-08		18:06:20		70.41		33		13-May-08		18:07:53		68.61		34.5		23-Jun-08		18:25:59		77.61		35.5

		13-May-08		20:07:10		71		30		13-May-08		20:06:20		69.8		31.5		13-May-08		20:07:53		68		33.5		23-Jun-08		20:25:59		77.61		34.5

		13-May-08		22:07:10		70.41		30.5		13-May-08		22:06:20		70.41		31.5		13-May-08		22:07:53		68.61		33		23-Jun-08		22:25:59		75.81		34.5

		14-May-08		0:07:10		69.2		31		14-May-08		0:06:20		69.8		32		14-May-08		0:07:53		68		33.5		24-Jun-08		0:25:59		74.6		34.5

		14-May-08		2:07:10		68		32.5		14-May-08		2:06:20		69.2		33.5		14-May-08		2:07:53		68		34.5		24-Jun-08		2:25:59		73.4		34.5

		14-May-08		4:07:10		68		33		14-May-08		4:06:20		69.2		34		14-May-08		4:07:53		68		34.5		24-Jun-08		4:25:59		72.21		34.5

		14-May-08		6:07:10		68.61		33		14-May-08		6:06:20		69.2		34		14-May-08		6:07:53		68		35		24-Jun-08		6:25:59		71		36.5

		14-May-08		8:07:10		69.2		34		14-May-08		8:06:20		70.41		36.5		14-May-08		8:07:53		68		36		24-Jun-08		8:25:59		71		39

		14-May-08		10:07:10		71		34		14-May-08		10:06:20		71		36		14-May-08		10:07:53		67.4		38		24-Jun-08		10:25:59		72.21		40.5

		14-May-08		12:07:10		71.6		28.5		14-May-08		12:06:20		70.41		31.5		14-May-08		12:07:53		68		33		24-Jun-08		12:25:59		72.21		41.5

		14-May-08		14:07:10		71.6		29.5		14-May-08		14:06:20		70.41		32		14-May-08		14:07:53		68		34		24-Jun-08		14:25:59		73.4		39.5

		14-May-08		16:07:10		71.6		26.5		14-May-08		16:06:20		71		28		14-May-08		16:07:53		68		30		24-Jun-08		16:25:59		74.01		39

		14-May-08		18:07:10		71.6		27.5		14-May-08		18:06:20		71		28		14-May-08		18:07:53		68		30.5		24-Jun-08		18:25:59		74.01		38.5

		14-May-08		20:07:10		71.6		35		14-May-08		20:06:20		70.41		39.5		14-May-08		20:07:53		68		39.5		24-Jun-08		20:25:59		74.01		39.5

		14-May-08		22:07:10		71		36		14-May-08		22:06:20		69.8		41		14-May-08		22:07:53		68		40		24-Jun-08		22:25:59		75.2		37

		15-May-08		0:07:10		70.41		36.5		15-May-08		0:06:20		69.8		41		15-May-08		0:07:53		68.61		39.5		25-Jun-08		0:25:59		73.4		37

		15-May-08		2:07:10		69.8		37		15-May-08		2:06:20		69.2		42		15-May-08		2:07:53		68.61		39.5		25-Jun-08		2:25:59		72.21		37

		15-May-08		4:07:10		69.8		38		15-May-08		4:06:20		69.8		42.5		15-May-08		4:07:53		69.2		40.5		25-Jun-08		4:25:59		71		37

		15-May-08		6:07:10		70.41		39		15-May-08		6:06:20		69.8		42.5		15-May-08		6:07:53		68.61		41		25-Jun-08		6:25:59		70.41		38

		15-May-08		8:07:10		71		40		15-May-08		8:06:20		70.41		48.5		15-May-08		8:07:53		68		43.5		25-Jun-08		8:25:59		70.41		40.5

		15-May-08		10:07:10		71.6		40.5		15-May-08		10:06:20		71		46		15-May-08		10:07:53		67.4		46.5		25-Jun-08		10:25:59		72.8		41.5

		15-May-08		12:07:10		71.6		40.5		15-May-08		12:06:20		70.41		46.5		15-May-08		12:07:53		68		46.5		25-Jun-08		12:25:59		73.4		41

		15-May-08		14:07:10		71.6		38		15-May-08		14:06:20		69.8		41		15-May-08		14:07:53		68		43		25-Jun-08		14:25:59		72.8		42

		15-May-08		16:07:10		71.6		37.5		15-May-08		16:06:20		69.8		40.5		15-May-08		16:07:53		68		42.5		25-Jun-08		16:25:59		72.8		41.5

		15-May-08		18:07:10		71.6		39		15-May-08		18:06:20		68.61		42.5		15-May-08		18:07:53		69.2		43		25-Jun-08		18:25:59		74.01		39.5

		15-May-08		20:07:10		71.6		39		15-May-08		20:06:20		68.61		44		15-May-08		20:07:53		68.61		43.5		25-Jun-08		20:25:59		74.01		41

		15-May-08		22:07:10		71.6		37.5		15-May-08		22:06:20		68		44		15-May-08		22:07:53		68.61		42		25-Jun-08		22:25:59		74.6		38.5

		16-May-08		0:07:10		72.21		37		16-May-08		0:06:20		68		42.5		16-May-08		0:07:53		68.61		41.5		26-Jun-08		0:25:59		74.01		37.5

		16-May-08		2:07:10		71.6		37		16-May-08		2:06:20		68		43		16-May-08		2:07:53		69.2		40.5		26-Jun-08		2:25:59		72.8		37.5

		16-May-08		4:07:10		71.6		36.5		16-May-08		4:06:20		68		43		16-May-08		4:07:53		69.2		40.5		26-Jun-08		4:25:59		71.6		38

		16-May-08		6:07:10		71.6		36		16-May-08		6:06:20		68.61		42		16-May-08		6:07:53		69.2		39.5		26-Jun-08		6:25:59		71		38.5

		16-May-08		8:07:10		72.21		36.5		16-May-08		8:06:20		69.8		42		16-May-08		8:07:53		68.61		41		26-Jun-08		8:25:59		71		40.5

		16-May-08		10:07:10		71.6		38		16-May-08		10:06:20		69.2		43		16-May-08		10:07:53		68		43		26-Jun-08		10:25:59		73.4		40.5

		16-May-08		12:07:10		71.6		39.5		16-May-08		12:06:20		70.41		43.5		16-May-08		12:07:53		68		44		26-Jun-08		12:25:59		72.21		43

		16-May-08		14:07:10		71.6		39		16-May-08		14:06:20		70.41		43		16-May-08		14:07:53		68		44		26-Jun-08		14:25:59		72.21		44

		16-May-08		16:07:10		71.6		40		16-May-08		16:06:20		69.2		46		16-May-08		16:07:53		68.61		45		26-Jun-08		16:25:59		72.21		43.5

		16-May-08		18:07:10		71.6		40.5		16-May-08		18:06:20		69.2		45		16-May-08		18:07:53		68.61		45		26-Jun-08		18:25:59		71.6		43

		16-May-08		20:07:10		71.6		42		16-May-08		20:06:20		69.2		48.5		16-May-08		20:07:53		69.2		46.5		26-Jun-08		20:25:59		72.8		40.5

		16-May-08		22:07:10		72.21		41		16-May-08		22:06:20		68.61		54.5		16-May-08		22:07:53		68		46.5		26-Jun-08		22:25:59		73.4		40.5

		17-May-08		0:07:10		72.21		39.5		17-May-08		0:06:20		68.61		50		17-May-08		0:07:53		68.61		44.5		27-Jun-08		0:25:59		72.8		39.5

		17-May-08		2:07:10		72.21		39		17-May-08		2:06:20		68.61		47		17-May-08		2:07:53		68.61		43.5		27-Jun-08		2:25:59		71.6		39

		17-May-08		4:07:10		71.6		39		17-May-08		4:06:20		68		51		17-May-08		4:07:53		68.61		43		27-Jun-08		4:25:59		71		39

		17-May-08		6:07:10		71.6		39		17-May-08		6:06:20		68.61		53		17-May-08		6:07:53		69.2		43		27-Jun-08		6:25:59		70.41		39.5

		17-May-08		8:07:10		72.21		40		17-May-08		8:06:20		69.8		55.5		17-May-08		8:07:53		68		45.5		27-Jun-08		8:25:59		70.41		41

		17-May-08		10:07:10		72.21		40.5		17-May-08		10:06:20		69.8		53.5		17-May-08		10:07:53		68		46		27-Jun-08		10:25:59		72.8		42.5

		17-May-08		12:07:10		71		44.5		17-May-08		12:06:20		69.8		50		17-May-08		12:07:53		68.61		49.5		27-Jun-08		12:25:59		72.21		43

		17-May-08		14:07:10		71.6		45		17-May-08		14:06:20		70.41		52.5		17-May-08		14:07:53		68		51		27-Jun-08		14:25:59		72.21		44.5

		17-May-08		16:07:10		71.6		44.5		17-May-08		16:06:20		69.8		51		17-May-08		16:07:53		68.61		49.5		27-Jun-08		16:25:59		72.8		44

		17-May-08		18:07:10		71.6		41.5		17-May-08		18:06:20		69.2		45.5		17-May-08		18:07:53		68.61		45.5		27-Jun-08		18:25:59		72.8		41

		17-May-08		20:07:10		71.6		41.5		17-May-08		20:06:20		68.61		49		17-May-08		20:07:53		68.61		46		27-Jun-08		20:25:59		73.4		41.5

		17-May-08		22:07:10		72.21		39.5		17-May-08		22:06:20		69.2		48		17-May-08		22:07:53		68		44.5		27-Jun-08		22:25:59		74.01		40

		18-May-08		0:07:10		72.21		39		18-May-08		0:06:20		68		50.5		18-May-08		0:07:53		68.61		43.5		28-Jun-08		0:25:59		73.4		39.5

		18-May-08		2:07:10		71.6		40		18-May-08		2:06:20		68		52		18-May-08		2:07:53		68.61		43.5		28-Jun-08		2:25:59		72.21		39.5

		18-May-08		4:07:10		71		40		18-May-08		4:06:20		68		52.5		18-May-08		4:07:53		69.2		43		28-Jun-08		4:25:59		71.6		39.5

		18-May-08		6:07:10		70.41		39.5		18-May-08		6:06:20		68		50.5		18-May-08		6:07:53		69.2		42		28-Jun-08		6:25:59		71		40

		18-May-08		8:07:10		71		40.5		18-May-08		8:06:20		68.61		53.5		18-May-08		8:07:53		68.61		44		28-Jun-08		8:25:59		71		42

		18-May-08		10:07:10		71.6		42.5		18-May-08		10:06:20		69.2		56.5		18-May-08		10:07:53		68.61		46.5		28-Jun-08		10:25:59		73.4		43

		18-May-08		12:07:10		71.6		44.5		18-May-08		12:06:20		69.2		53.5		18-May-08		12:07:53		68.61		49.5		28-Jun-08		12:25:59		72.8		44

		18-May-08		14:07:10		72.21		48.5		18-May-08		14:06:20		69.2		58.5		18-May-08		14:07:53		68.61		54		28-Jun-08		14:25:59		72.21		45

		18-May-08		16:07:10		72.21		45		18-May-08		16:06:20		68.61		63.5		18-May-08		16:07:53		68.61		51.5		28-Jun-08		16:25:59		72.8		45.5

		18-May-08		18:07:10		72.21		43		18-May-08		18:06:20		68.61		60.5		18-May-08		18:07:53		68.61		49.5		28-Jun-08		18:25:59		72.8		43.5

		18-May-08		20:07:10		72.21		40.5		18-May-08		20:06:20		68.61		52.5		18-May-08		20:07:53		68		46		28-Jun-08		20:25:59		72.8		43.5

		18-May-08		22:07:10		72.21		39		18-May-08		22:06:20		68		51.5		18-May-08		22:07:53		68.61		43.5		28-Jun-08		22:25:59		72.8		42.5

		19-May-08		0:07:10		71		39		19-May-08		0:06:20		68		49.5		19-May-08		0:07:53		69.2		42		29-Jun-08		0:25:59		72.21		42.5

		19-May-08		2:07:10		70.41		39.5		19-May-08		2:06:20		68		49		19-May-08		2:07:53		69.2		42		29-Jun-08		2:25:59		71.6		42.5

		19-May-08		4:07:10		70.41		39		19-May-08		4:06:20		67.4		48		19-May-08		4:07:53		69.2		41.5		29-Jun-08		4:25:59		71		43

		19-May-08		6:07:10		71		39		19-May-08		6:06:20		67.4		49		19-May-08		6:07:53		69.2		41.5		29-Jun-08		6:25:59		71		43.5

		19-May-08		8:07:10		71		39.5		19-May-08		8:06:20		68		49		19-May-08		8:07:53		69.2		42		29-Jun-08		8:25:59		71		44

		19-May-08		10:07:10		70.41		40.5		19-May-08		10:06:20		68		48.5		19-May-08		10:07:53		69.2		43		29-Jun-08		10:25:59		71.6		44.5

		19-May-08		12:07:10		71		41.5		19-May-08		12:06:20		68.61		51		19-May-08		12:07:53		69.2		44.5		29-Jun-08		12:25:59		72.21		45.5

		19-May-08		14:07:10		71.6		41.5		19-May-08		14:06:20		68		54.5		19-May-08		14:07:53		69.8		45		29-Jun-08		14:25:59		74.01		45.5

		19-May-08		16:07:10		72.21		42		19-May-08		16:06:20		68.61		51.5		19-May-08		16:07:53		69.2		46		29-Jun-08		16:25:59		75.2		44.5

		19-May-08		18:07:10		72.21		40		19-May-08		18:06:20		68		55		19-May-08		18:07:53		69.2		44.5		29-Jun-08		18:25:59		75.81		43.5

		19-May-08		20:07:10		72.21		39		19-May-08		20:06:20		68.61		50.5		19-May-08		20:07:53		69.2		43		29-Jun-08		20:25:59		75.2		43

		19-May-08		22:07:10		71		39		19-May-08		22:06:20		67.4		52.5		19-May-08		22:07:53		69.2		42		29-Jun-08		22:25:59		74.01		42.5

		20-May-08		0:07:10		71		39.5		20-May-08		0:06:20		67.4		51		20-May-08		0:07:53		69.2		42		30-Jun-08		0:25:59		72.21		42.5

		20-May-08		2:07:10		71		39.5		20-May-08		2:06:20		68		50		20-May-08		2:07:53		69.2		42		30-Jun-08		2:25:59		71.6		42.5

		20-May-08		4:07:10		70.41		39.5		20-May-08		4:06:20		67.4		49.5		20-May-08		4:07:53		69.2		41.5		30-Jun-08		4:25:59		71		42.5

		20-May-08		6:07:10		71		39.5		20-May-08		6:06:20		68		49.5		20-May-08		6:07:53		69.2		41.5		30-Jun-08		6:25:59		70.41		43

		20-May-08		8:07:10		71		39		20-May-08		8:06:20		68.61		50.5		20-May-08		8:07:53		68.61		44		30-Jun-08		8:25:59		70.41		43.5

		20-May-08		10:07:10		71		39		20-May-08		10:06:20		71		44.5		20-May-08		10:07:53		68.61		43		30-Jun-08		10:25:59		70.41		44

		20-May-08		12:07:10		71		41		20-May-08		12:06:20		71		49.5		20-May-08		12:07:53		68		45		30-Jun-08		12:25:59		72.21		44.5

		20-May-08		14:07:10		71		43		20-May-08		14:06:20		71		55.5		20-May-08		14:07:53		68		48		30-Jun-08		14:25:59		73.4		44.5

		20-May-08		16:07:10		71.6		42		20-May-08		16:06:20		70.41		49.5		20-May-08		16:07:53		68.61		46.5		30-Jun-08		16:25:59		74.6		44.5

		20-May-08		18:07:10		71.6		41		20-May-08		18:06:20		69.8		51		20-May-08		18:07:53		69.2		44.5		30-Jun-08		18:25:59		75.2		43

		20-May-08		20:07:10		71		39		20-May-08		20:06:20		69.8		48.5		20-May-08		20:07:53		69.2		42.5		30-Jun-08		20:25:59		75.2		42.5

		20-May-08		22:07:10		71		39.5		20-May-08		22:06:20		69.8		48		20-May-08		22:07:53		69.8		41.5		30-Jun-08		22:25:59		73.4		42

		21-May-08		0:07:10		70.41		40		21-May-08		0:06:20		69.2		48.5		21-May-08		0:07:53		69.2		42		1-Jul-08		0:25:59		72.21		42

		21-May-08		2:07:10		70.41		40		21-May-08		2:06:20		68.61		48.5		21-May-08		2:07:53		69.8		42		1-Jul-08		2:25:59		71.6		42

		21-May-08		4:07:10		71		39.5		21-May-08		4:06:20		68.61		48		21-May-08		4:07:53		69.2		41.5		1-Jul-08		4:25:59		71		42

		21-May-08		6:07:10		71		39.5		21-May-08		6:06:20		68		48.5		21-May-08		6:07:53		69.8		41		1-Jul-08		6:25:59		71		43

		21-May-08		8:07:10		71		39.5		21-May-08		8:06:20		70.41		48.5		21-May-08		8:07:53		68.61		42		1-Jul-08		8:25:59		70.41		45

		21-May-08		10:07:10		71		40		21-May-08		10:06:20		71		47		21-May-08		10:07:53		68		43		1-Jul-08		10:25:59		72.21		45

		21-May-08		12:07:10		71		41		21-May-08		12:06:20		71		51		21-May-08		12:07:53		68.61		44.5		1-Jul-08		12:25:59		72.21		45

		21-May-08		14:07:10		71		44		21-May-08		14:06:20		71.6		54		21-May-08		14:07:53		68		48.5		1-Jul-08		14:25:59		72.8		46.5

		21-May-08		16:07:10		71		39.5		21-May-08		16:06:20		71		45		21-May-08		16:07:53		69.2		43.5		1-Jul-08		16:25:59		72.8		46.5

		21-May-08		18:07:10		71.6		32		21-May-08		18:06:20		71		34		21-May-08		18:07:53		69.2		36.5		1-Jul-08		18:25:59		72.8		44.5

		21-May-08		20:07:10		71		30		21-May-08		20:06:20		70.41		30		21-May-08		20:07:53		69.8		31.5		1-Jul-08		20:25:59		74.01		42

		21-May-08		22:07:10		70.41		36		21-May-08		22:06:20		70.41		39		21-May-08		22:07:53		69.8		38		1-Jul-08		22:25:59		74.01		43.5

		22-May-08		0:07:10		69.2		35		22-May-08		0:06:20		69.2		37.5		22-May-08		0:07:53		68.61		37		2-Jul-08		0:25:59		73.4		43

		22-May-08		2:07:10		68.61		34.5		22-May-08		2:06:20		69.2		35.5		22-May-08		2:07:53		68.61		36.5		2-Jul-08		2:25:59		72.21		43

		22-May-08		4:07:10		68.61		34		22-May-08		4:06:20		69.2		35		22-May-08		4:07:53		68.61		35		2-Jul-08		4:25:59		72.21		43.5

		22-May-08		6:07:10		69.8		32.5		22-May-08		6:06:20		69.2		34.5		22-May-08		6:07:53		69.2		34.5		2-Jul-08		6:25:59		71.6		44.5

		22-May-08		8:07:10		69.8		32.5		22-May-08		8:06:20		71		34.5		22-May-08		8:07:53		68.61		35		2-Jul-08		8:25:59		71		46.5

		22-May-08		10:07:10		70.41		33.5		22-May-08		10:06:20		71.6		34		22-May-08		10:07:53		68.61		35.5		2-Jul-08		10:25:59		72.21		47.5

		22-May-08		12:07:10		71		33.5		22-May-08		12:06:20		70.41		35.5		22-May-08		12:07:53		69.2		36		2-Jul-08		12:25:59		72.21		46.5

		22-May-08		14:07:10		71		34.5		22-May-08		14:06:20		69.8		37		22-May-08		14:07:53		68.61		38		2-Jul-08		14:25:59		72.21		47.5

		22-May-08		16:07:10		71		35		22-May-08		16:06:20		69.2		38		22-May-08		16:07:53		68.61		38.5		2-Jul-08		16:25:59		72.8		45.5

		22-May-08		18:07:10		71		35		22-May-08		18:06:20		68.61		37.5		22-May-08		18:07:53		68		38		2-Jul-08		18:25:59		72.8		44.5

		22-May-08		20:07:10		70.41		34.5		22-May-08		20:06:20		68.61		37		22-May-08		20:07:53		68		37		2-Jul-08		20:25:59		73.4		42.5

		22-May-08		22:07:10		69.2		33.5		22-May-08		22:06:20		68		36.5		22-May-08		22:07:53		68.61		36		2-Jul-08		22:25:59		74.01		43

		23-May-08		0:07:10		68.61		33.5		23-May-08		0:06:20		68		36		23-May-08		0:07:53		68		35.5		3-Jul-08		0:25:59		72.8		42.5

		23-May-08		2:07:10		68		32.5		23-May-08		2:06:20		68		34.5		23-May-08		2:07:53		68		34.5		3-Jul-08		2:25:59		71.6		42

		23-May-08		4:07:10		68.61		31		23-May-08		4:06:20		68		32.5		23-May-08		4:07:53		68.61		33		3-Jul-08		4:25:59		71		42.5

		23-May-08		6:07:10		69.8		30		23-May-08		6:06:20		68		32		23-May-08		6:07:53		69.2		32		3-Jul-08		6:25:59		70.41		43

		23-May-08		8:07:10		69.8		30		23-May-08		8:06:20		68.61		33		23-May-08		8:07:53		69.2		32		3-Jul-08		8:25:59		71		44.5

		23-May-08		10:07:10		70.41		30		23-May-08		10:06:20		68.61		32.5		23-May-08		10:07:53		68		32		3-Jul-08		10:25:59		72.21		45

		23-May-08		12:07:10		71		25		23-May-08		12:06:20		69.2		27.5		23-May-08		12:07:53		68		28.5		3-Jul-08		12:25:59		71.6		46.5

		23-May-08		14:07:10		71		28.5		23-May-08		14:06:20		68.61		30		23-May-08		14:07:53		67.4		31		3-Jul-08		14:25:59		72.21		46

		23-May-08		16:07:10		71		29.5		23-May-08		16:06:20		68		33		23-May-08		16:07:53		68.61		32.5		3-Jul-08		16:25:59		72.21		45.5

		23-May-08		18:07:10		71		32		23-May-08		18:06:20		68.61		34.5		23-May-08		18:07:53		68.61		35		3-Jul-08		18:25:59		73.4		44

		23-May-08		20:07:10		71		33.5		23-May-08		20:06:20		69.2		36		23-May-08		20:07:53		68.61		36		3-Jul-08		20:25:59		74.01		42

		23-May-08		22:07:10		70.41		33		23-May-08		22:06:20		68.61		37		23-May-08		22:07:53		68.61		36		3-Jul-08		22:25:59		74.6		42

		24-May-08		0:07:10		69.2		33.5		24-May-08		0:06:20		68		37		24-May-08		0:07:53		68.61		36		4-Jul-08		0:25:59		73.4		41.5

		24-May-08		2:07:10		68.61		33.5		24-May-08		2:06:20		68		37		24-May-08		2:07:53		68		36		4-Jul-08		2:25:59		72.21		41.5

		24-May-08		4:07:10		69.2		33		24-May-08		4:06:20		67.4		37		24-May-08		4:07:53		68.61		35		4-Jul-08		4:25:59		71.6		41.5

		24-May-08		6:07:10		70.41		32.5		24-May-08		6:06:20		68		36		24-May-08		6:07:53		69.2		34.5		4-Jul-08		6:25:59		71		42

		24-May-08		8:07:10		70.41		32.5		24-May-08		8:06:20		67.4		38.5		24-May-08		8:07:53		68.61		35.5		4-Jul-08		8:25:59		71		44.5

		24-May-08		10:07:10		70.41		34		24-May-08		10:06:20		70.41		36		24-May-08		10:07:53		68.61		36.5		4-Jul-08		10:25:59		71.6		45

		24-May-08		12:07:10		71		35		24-May-08		12:06:20		71		36		24-May-08		12:07:53		69.2		36.5		4-Jul-08		12:25:59		72.21		48.5

		24-May-08		14:07:10		71		34		24-May-08		14:06:20		71		37		24-May-08		14:07:53		68		37.5		4-Jul-08		14:25:59		73.4		50

		24-May-08		16:07:10		71		34.5		24-May-08		16:06:20		69.8		37		24-May-08		16:07:53		69.2		37		4-Jul-08		16:25:59		72.8		49

		24-May-08		18:07:10		70.41		35.5		24-May-08		18:06:20		70.41		39		24-May-08		18:07:53		69.2		38		4-Jul-08		18:25:59		73.4		48.5

		24-May-08		20:07:10		70.41		36.5		24-May-08		20:06:20		69.8		41		24-May-08		20:07:53		68.61		39		4-Jul-08		20:25:59		74.01		46

		24-May-08		22:07:10		71		36.5		24-May-08		22:06:20		69.2		42.5		24-May-08		22:07:53		68.61		39.5		4-Jul-08		22:25:59		74.01		47

		25-May-08		0:07:10		70.41		37		25-May-08		0:06:20		69.2		42.5		25-May-08		0:07:53		69.2		39.5		5-Jul-08		0:25:59		73.4		46.5

		25-May-08		2:07:10		70.41		37		25-May-08		2:06:20		68.61		42.5		25-May-08		2:07:53		69.2		39		5-Jul-08		2:25:59		72.21		46

		25-May-08		4:07:10		70.41		37.5		25-May-08		4:06:20		68.61		43		25-May-08		4:07:53		69.2		39		5-Jul-08		4:25:59		71.6		45.5

		25-May-08		6:07:10		70.41		37.5		25-May-08		6:06:20		68.61		45		25-May-08		6:07:53		69.2		39.5		5-Jul-08		6:25:59		71		46.5

		25-May-08		8:07:10		70.41		38		25-May-08		8:06:20		68.61		45		25-May-08		8:07:53		69.2		39.5		5-Jul-08		8:25:59		71		48

		25-May-08		10:07:10		70.41		39.5		25-May-08		10:06:20		68.61		48		25-May-08		10:07:53		69.2		41.5		5-Jul-08		10:25:59		72.21		48

		25-May-08		12:07:10		70.41		40		25-May-08		12:06:20		69.2		50		25-May-08		12:07:53		69.8		42		5-Jul-08		12:25:59		72.21		48.5

		25-May-08		14:07:10		69.8		37.5		25-May-08		14:06:20		68.61		46		25-May-08		14:07:53		69.8		40		5-Jul-08		14:25:59		73.4		48

		25-May-08		16:07:10		69.8		38.5		25-May-08		16:06:20		68.61		44.5		25-May-08		16:07:53		69.2		39.5		5-Jul-08		16:25:59		73.4		47.5

		25-May-08		18:07:10		69.8		39.5		25-May-08		18:06:20		69.2		48.5		25-May-08		18:07:53		69.8		41		5-Jul-08		18:25:59		73.4		46.5

		25-May-08		20:07:10		70.41		40		25-May-08		20:06:20		69.2		50		25-May-08		20:07:53		69.2		41.5		5-Jul-08		20:25:59		72.8		45.5

		25-May-08		22:07:10		70.41		40		25-May-08		22:06:20		68.61		48		25-May-08		22:07:53		69.2		41		5-Jul-08		22:25:59		72.8		47

		26-May-08		0:07:10		70.41		39		26-May-08		0:06:20		68		47		26-May-08		0:07:53		69.2		40.5		6-Jul-08		0:25:59		72.21		46

		26-May-08		2:07:10		70.41		37.5		26-May-08		2:06:20		67.4		45		26-May-08		2:07:53		69.2		39		6-Jul-08		2:25:59		72.21		45.5

		26-May-08		4:07:10		70.41		36.5		26-May-08		4:06:20		66.81		44		26-May-08		4:07:53		69.2		38		6-Jul-08		4:25:59		71		45.5

		26-May-08		6:07:10		70.41		36.5		26-May-08		6:06:20		66.81		44.5		26-May-08		6:07:53		69.8		38		6-Jul-08		6:25:59		71		45

		26-May-08		8:07:10		70.41		38.5		26-May-08		8:06:20		67.4		45.5		26-May-08		8:07:53		69.8		39		6-Jul-08		8:25:59		70.41		45.5

		26-May-08		10:07:10		69.8		37		26-May-08		10:06:20		69.2		43		26-May-08		10:07:53		69.2		39.5		6-Jul-08		10:25:59		71.6		47.5

		26-May-08		12:07:10		69.8		37		26-May-08		12:06:20		69.2		40.5		26-May-08		12:07:53		69.2		38.5		6-Jul-08		12:25:59		73.4		48.5

		26-May-08		14:07:10		70.41		37		26-May-08		14:06:20		69.2		40		26-May-08		14:07:53		69.8		38.5		6-Jul-08		14:25:59		75.2		49

		26-May-08		16:07:10		70.41		36		26-May-08		16:06:20		69.2		39		26-May-08		16:07:53		69.2		38		6-Jul-08		16:25:59		77		47.5

		26-May-08		18:07:10		70.41		35.5		26-May-08		18:06:20		68.61		38.5		26-May-08		18:07:53		69.2		37		6-Jul-08		18:25:59		77.61		45.5

		26-May-08		20:07:10		70.41		36		26-May-08		20:06:20		69.2		38.5		26-May-08		20:07:53		69.8		37.5		6-Jul-08		20:25:59		78.2		45

		26-May-08		22:07:10		69.8		37.5		26-May-08		22:06:20		69.2		44		26-May-08		22:07:53		69.2		39.5		6-Jul-08		22:25:59		77		45.5

		27-May-08		0:07:10		70.41		38		27-May-08		0:06:20		68.61		44.5		27-May-08		0:07:53		69.8		39.5		7-Jul-08		0:25:59		75.81		45.5

		27-May-08		2:07:10		70.41		37.5		27-May-08		2:06:20		68		45		27-May-08		2:07:53		69.8		39		7-Jul-08		2:25:59		74.6		44.5

		27-May-08		4:07:10		70.41		37.5		27-May-08		4:06:20		67.4		45.5		27-May-08		4:07:53		69.8		39		7-Jul-08		4:25:59		74.01		44.5

		27-May-08		6:07:10		70.41		37		27-May-08		6:06:20		67.4		45		27-May-08		6:07:53		69.2		38.5		7-Jul-08		6:25:59		72.8		44

		27-May-08		8:07:10		70.41		38		27-May-08		8:06:20		68		45		27-May-08		8:07:53		69.2		39.5		7-Jul-08		8:25:59		72.21		44.5

		27-May-08		10:07:10		69.8		37.5		27-May-08		10:06:20		69.2		42.5		27-May-08		10:07:53		69.2		39		7-Jul-08		10:25:59		73.4		46.5

		27-May-08		12:07:10		70.41		39		27-May-08		12:06:20		69.2		45		27-May-08		12:07:53		69.2		40		7-Jul-08		12:25:59		74.6		48

		27-May-08		14:07:10		70.41		38.5		27-May-08		14:06:20		68.61		45		27-May-08		14:07:53		69.2		40.5		7-Jul-08		14:25:59		76.4		49

		27-May-08		16:07:10		70.41		39		27-May-08		16:06:20		69.2		45.5		27-May-08		16:07:53		69.2		40.5		7-Jul-08		16:25:59		77.61		47.5

		27-May-08		18:07:10		70.41		39		27-May-08		18:06:20		69.2		46		27-May-08		18:07:53		69.2		40.5		7-Jul-08		18:25:59		78.2		46

		27-May-08		20:07:10		70.41		38.5		27-May-08		20:06:20		69.2		46		27-May-08		20:07:53		69.8		40		7-Jul-08		20:25:59		78.2		44.5

		27-May-08		22:07:10		70.41		39		27-May-08		22:06:20		69.2		45		27-May-08		22:07:53		69.8		40		7-Jul-08		22:25:59		76.4		43.5

		28-May-08		0:07:10		70.41		38.5		28-May-08		0:06:20		69.2		46		28-May-08		0:07:53		69.8		40		8-Jul-08		0:25:59		75.2		42.5

		28-May-08		2:07:10		70.41		39		28-May-08		2:06:20		69.2		46.5		28-May-08		2:07:53		69.2		40.5		8-Jul-08		2:25:59		74.01		42.5

		28-May-08		4:07:10		70.41		39		28-May-08		4:06:20		68.61		47		28-May-08		4:07:53		69.8		40.5		8-Jul-08		4:25:59		72.8		42

		28-May-08		6:07:10		70.41		39.5		28-May-08		6:06:20		69.2		47.5		28-May-08		6:07:53		69.2		41		8-Jul-08		6:25:59		72.21		41.5

		28-May-08		8:07:10		70.41		39		28-May-08		8:06:20		69.2		50		28-May-08		8:07:53		69.2		41.5		8-Jul-08		8:25:59		71.6		46

		28-May-08		10:07:10		71		38.5		28-May-08		10:06:20		69.8		45		28-May-08		10:07:53		68.61		41		8-Jul-08		10:25:59		72.8		47

		28-May-08		12:07:10		71		38.5		28-May-08		12:06:20		69.8		44		28-May-08		12:07:53		69.2		41.5		8-Jul-08		12:25:59		72.8		49

		28-May-08		14:07:10		71		39		28-May-08		14:06:20		69.2		43.5		28-May-08		14:07:53		68.61		42.5		8-Jul-08		14:25:59		72.8		49

		28-May-08		16:07:10		71		38		28-May-08		16:06:20		69.8		45.5		28-May-08		16:07:53		68.61		41.5		8-Jul-08		16:25:59		73.4		48.5

		28-May-08		18:07:10		71		37.5		28-May-08		18:06:20		71		41.5		28-May-08		18:07:53		69.2		40.5		8-Jul-08		18:25:59		73.4		47

		28-May-08		20:07:10		71		37.5		28-May-08		20:06:20		70.41		42.5		28-May-08		20:07:53		69.2		40		8-Jul-08		20:25:59		74.6		45.5

		28-May-08		22:07:10		70.41		37.5		28-May-08		22:06:20		71		41.5		28-May-08		22:07:53		69.2		39		8-Jul-08		22:25:59		75.2		45

		29-May-08		0:07:10		70.41		37.5		29-May-08		0:06:20		69.8		43		29-May-08		0:07:53		69.2		39.5		9-Jul-08		0:25:59		75.2		44

		29-May-08		2:07:10		70.41		38		29-May-08		2:06:20		69.2		44		29-May-08		2:07:53		69.8		39.5		9-Jul-08		2:25:59		74.6		44

		29-May-08		4:07:10		70.41		38		29-May-08		4:06:20		68.61		45		29-May-08		4:07:53		69.8		39.5		9-Jul-08		4:25:59		74.01		43.5

		29-May-08		6:07:10		70.41		38.5		29-May-08		6:06:20		68.61		45.5		29-May-08		6:07:53		69.8		40		9-Jul-08		6:25:59		73.4		42

		29-May-08		8:07:10		71		38.5		29-May-08		8:06:20		69.8		46.5		29-May-08		8:07:53		69.2		40.5		9-Jul-08		8:25:59		72.21		45.5

		29-May-08		10:07:10		71		36.5		29-May-08		10:06:20		69.2		41.5		29-May-08		10:07:53		68.61		39.5		9-Jul-08		10:25:59		72.8		50

		29-May-08		12:07:10		71		37.5		29-May-08		12:06:20		69.8		43		29-May-08		12:07:53		69.2		40		9-Jul-08		12:25:59		72.8		50.5

		29-May-08		14:07:10		71		37.5		29-May-08		14:06:20		69.2		41.5		29-May-08		14:07:53		68.61		40.5		9-Jul-08		14:25:59		72.21		49.5

		29-May-08		16:07:10		71		37		29-May-08		16:06:20		69.8		41		29-May-08		16:07:53		68.61		40.5		9-Jul-08		16:25:59		72.8		48.5

		29-May-08		18:07:10		71		38		29-May-08		18:06:20		70.41		42.5		29-May-08		18:07:53		68.61		41		9-Jul-08		18:25:59		73.4		47.5

		29-May-08		20:07:10		71		38		29-May-08		20:06:20		70.41		44.5		29-May-08		20:07:53		69.2		40.5		9-Jul-08		20:25:59		74.01		45

		29-May-08		22:07:10		71		38		29-May-08		22:06:20		70.41		43.5		29-May-08		22:07:53		69.8		40		9-Jul-08		22:25:59		75.81		44

		30-May-08		0:07:10		69.8		38.5		30-May-08		0:06:20		69.2		47		30-May-08		0:07:53		67.4		42.5		10-Jul-08		0:25:59		75.2		44

		30-May-08		2:07:10		70.41		39		30-May-08		2:06:20		68.61		46.5		30-May-08		2:07:53		69.2		41		10-Jul-08		2:25:59		74.6		44

		30-May-08		4:07:10		71		39		30-May-08		4:06:20		68.61		47.5		30-May-08		4:07:53		69.8		40.5		10-Jul-08		4:25:59		74.01		44.5

		30-May-08		6:07:10		71		38.5		30-May-08		6:06:20		68		47.5		30-May-08		6:07:53		69.8		40.5		10-Jul-08		6:25:59		73.4		43

		30-May-08		8:07:10		70.41		39.5		30-May-08		8:06:20		70.41		48.5		30-May-08		8:07:53		68.61		42		10-Jul-08		8:25:59		73.4		46

		30-May-08		10:07:10		71		39		30-May-08		10:06:20		71		44.5		30-May-08		10:07:53		68.61		41.5		10-Jul-08		10:25:59		74.01		47.5

		30-May-08		12:07:10		71.6		39		30-May-08		12:06:20		69.2		49		30-May-08		12:07:53		69.2		41.5		10-Jul-08		12:25:59		72.8		49.5

		30-May-08		14:07:10		71		39.5		30-May-08		14:06:20		69.2		45.5		30-May-08		14:07:53		69.2		42.5		10-Jul-08		14:25:59		72.21		51

		30-May-08		16:07:10		71		39.5		30-May-08		16:06:20		69.2		49		30-May-08		16:07:53		68		44		10-Jul-08		16:25:59		72.8		50.5

		30-May-08		18:07:10		71		39		30-May-08		18:06:20		69.2		47.5		30-May-08		18:07:53		68.61		42		10-Jul-08		18:25:59		73.4		49

		30-May-08		20:07:10		71		38.5		30-May-08		20:06:20		69.2		44		30-May-08		20:07:53		69.2		41		10-Jul-08		20:25:59		74.6		46

		30-May-08		22:07:10		70.41		38.5		30-May-08		22:06:20		68.61		45		30-May-08		22:07:53		69.2		41		10-Jul-08		22:25:59		75.81		47

		31-May-08		0:07:10		71		39.5		31-May-08		0:06:20		68		49.5		31-May-08		0:07:53		69.2		42		11-Jul-08		0:25:59		75.81		46

		31-May-08		2:07:10		70.41		39		31-May-08		2:06:20		68		49.5		31-May-08		2:07:53		69.2		41		11-Jul-08		2:25:59		74.6		46.5

		31-May-08		4:07:10		70.41		39		31-May-08		4:06:20		68		49		31-May-08		4:07:53		69.8		40.5		11-Jul-08		4:25:59		74.01		46.5

		31-May-08		6:07:10		70.41		39		31-May-08		6:06:20		68		51.5		31-May-08		6:07:53		68.61		41.5		11-Jul-08		6:25:59		73.4		44.5

		31-May-08		8:07:10		71		39		31-May-08		8:06:20		68		45.5		31-May-08		8:07:53		68		42.5		11-Jul-08		8:25:59		72.21		47.5

		31-May-08		10:07:10		70.41		39.5		31-May-08		10:06:20		69.2		51		31-May-08		10:07:53		68		42.5		11-Jul-08		10:25:59		73.4		50.5

		31-May-08		12:07:10		71		40		31-May-08		12:06:20		69.2		49		31-May-08		12:07:53		68		44		11-Jul-08		12:25:59		72.8		51

		31-May-08		14:07:10		71		42		31-May-08		14:06:20		69.2		48		31-May-08		14:07:53		68.61		45.5		11-Jul-08		14:25:59		72.8		51.5

		31-May-08		16:07:10		71		40.5		31-May-08		16:06:20		69.2		51		31-May-08		16:07:53		68.61		45		11-Jul-08		16:25:59		72.8		49

		31-May-08		18:07:10		71		40.5		31-May-08		18:06:20		68.61		52.5		31-May-08		18:07:53		68		45		11-Jul-08		18:25:59		73.4		47.5

		31-May-08		20:07:10		71		39.5		31-May-08		20:06:20		68.61		52		31-May-08		20:07:53		68.61		43		11-Jul-08		20:25:59		74.01		46.5

		31-May-08		22:07:10		70.41		39		31-May-08		22:06:20		69.2		48		31-May-08		22:07:53		69.8		41		11-Jul-08		22:25:59		75.2		45

		1-Jun-08		0:07:10		70.41		39.5		1-Jun-08		0:06:20		68.61		47.5		1-Jun-08		0:07:53		68.61		41.5		12-Jul-08		0:25:59		74.6		43.5

		1-Jun-08		2:07:10		70.41		39		1-Jun-08		2:06:20		68.61		47.5		1-Jun-08		2:07:53		69.2		41		12-Jul-08		2:25:59		73.4		44

		1-Jun-08		4:07:10		70.41		39		1-Jun-08		4:06:20		68.61		47.5		1-Jun-08		4:07:53		69.2		41.5		12-Jul-08		4:25:59		72.21		44.5

		1-Jun-08		6:07:10		70.41		39		1-Jun-08		6:06:20		67.4		50.5		1-Jun-08		6:07:53		69.8		41		12-Jul-08		6:25:59		72.21		44

		1-Jun-08		8:07:10		70.41		39.5		1-Jun-08		8:06:20		67.4		51		1-Jun-08		8:07:53		69.2		41.5		12-Jul-08		8:25:59		71.6		46.5

		1-Jun-08		10:07:10		70.41		39.5		1-Jun-08		10:06:20		67.4		50		1-Jun-08		10:07:53		69.8		41		12-Jul-08		10:25:59		72.8		48

		1-Jun-08		12:07:10		70.41		39.5		1-Jun-08		12:06:20		67.4		50.5		1-Jun-08		12:07:53		69.2		42		12-Jul-08		12:25:59		74.6		46.5

		1-Jun-08		14:07:10		71		41		1-Jun-08		14:06:20		68.61		52		1-Jun-08		14:07:53		69.2		43.5		12-Jul-08		14:25:59		74.6		46.5

		1-Jun-08		16:07:10		71		40		1-Jun-08		16:06:20		69.2		50		1-Jun-08		16:07:53		69.2		43.5		12-Jul-08		16:25:59		75.81		45

		1-Jun-08		18:07:10		71.6		39.5		1-Jun-08		18:06:20		69.2		47.5		1-Jun-08		18:07:53		69.2		43		12-Jul-08		18:25:59		75.2		44.5

		1-Jun-08		20:07:10		71.6		38.5		1-Jun-08		20:06:20		68.61		47		1-Jun-08		20:07:53		69.2		42		12-Jul-08		20:25:59		75.81		41.5

		1-Jun-08		22:07:10		70.41		38.5		1-Jun-08		22:06:20		68		47.5		1-Jun-08		22:07:53		68.61		41		12-Jul-08		22:25:59		76.4		43

		2-Jun-08		0:07:10		70.41		38.5		2-Jun-08		0:06:20		68.61		46		2-Jun-08		0:07:53		68.61		41		13-Jul-08		0:25:59		76.4		43

		2-Jun-08		2:07:10		70.41		38		2-Jun-08		2:06:20		68		46		2-Jun-08		2:07:53		68.61		40.5		13-Jul-08		2:25:59		75.81		44

		2-Jun-08		4:07:10		70.41		37		2-Jun-08		4:06:20		67.4		45		2-Jun-08		4:07:53		68.61		39.5		13-Jul-08		4:25:59		75.81		44

		2-Jun-08		6:07:10		69.8		36		2-Jun-08		6:06:20		66.2		44		2-Jun-08		6:07:53		68.61		38.5		13-Jul-08		6:25:59		75.81		44.5

		2-Jun-08		8:07:10		70.41		38		2-Jun-08		8:06:20		66.81		46		2-Jun-08		8:07:53		69.2		40		13-Jul-08		8:25:59		75.81		44.5

		2-Jun-08		10:07:10		69.8		37		2-Jun-08		10:06:20		68.61		40.5		2-Jun-08		10:07:53		68.61		39.5		13-Jul-08		10:25:59		75.81		44.5

		2-Jun-08		12:07:10		70.41		38		2-Jun-08		12:06:20		69.2		41		2-Jun-08		12:07:53		69.2		39.5		13-Jul-08		12:25:59		76.4		44

		2-Jun-08		14:07:10		71		39		2-Jun-08		14:06:20		69.8		42		2-Jun-08		14:07:53		69.2		41.5		13-Jul-08		14:25:59		77.61		44.5

		2-Jun-08		16:07:10		71		38.5		2-Jun-08		16:06:20		69.2		45.5		2-Jun-08		16:07:53		65.01		46		13-Jul-08		16:25:59		78.8		43.5

		2-Jun-08		18:07:10		71		38.5		2-Jun-08		18:06:20		68.61		45		2-Jun-08		18:07:53		67.4		43		13-Jul-08		18:25:59		78.8		43

		2-Jun-08		20:07:10		71		37.5		2-Jun-08		20:06:20		67.4		47		2-Jun-08		20:07:53		66.81		43.5		13-Jul-08		20:25:59		78.8		43.5

		2-Jun-08		22:07:10		69.8		37		2-Jun-08		22:06:20		68		45		2-Jun-08		22:07:53		67.4		42		13-Jul-08		22:25:59		77.61		42.5

		3-Jun-08		0:07:10		69.8		37		3-Jun-08		0:06:20		67.4		44		3-Jun-08		0:07:53		67.4		41		14-Jul-08		0:25:59		77		42.5

		3-Jun-08		2:07:10		70.41		36.5		3-Jun-08		2:06:20		66.81		43.5		3-Jun-08		2:07:53		66.81		40.5		14-Jul-08		2:25:59		76.4		42.5

		3-Jun-08		4:07:10		69.8		35		3-Jun-08		4:06:20		66.2		43		3-Jun-08		4:07:53		67.4		39.5		14-Jul-08		4:25:59		75.81		42.5

		3-Jun-08		6:07:10		70.41		35.5		3-Jun-08		6:06:20		66.2		42.5		3-Jun-08		6:07:53		67.4		38.5		14-Jul-08		6:25:59		75.2		42

		3-Jun-08		8:07:10		70.41		37		3-Jun-08		8:06:20		68		42		3-Jun-08		8:07:53		68.61		39.5		14-Jul-08		8:25:59		74.6		42.5

		3-Jun-08		10:07:10		71		37		3-Jun-08		10:06:20		68		44.5		3-Jun-08		10:07:53		67.4		41.5		14-Jul-08		10:25:59		75.2		42.5

		3-Jun-08		12:07:10		71		37.5		3-Jun-08		12:06:20		71		41		3-Jun-08		12:07:53		68		41.5		14-Jul-08		12:25:59		76.4		43

		3-Jun-08		14:07:10		71		39.5		3-Jun-08		14:06:20		70.41		45.5		3-Jun-08		14:07:53		66.81		45		14-Jul-08		14:25:59		77		43.5

		3-Jun-08		16:07:10		71		39.5		3-Jun-08		16:06:20		69.2		44.5		3-Jun-08		16:07:53		67.4		44.5		14-Jul-08		16:25:59		78.2		43.5

		3-Jun-08		18:07:10		71		39.5		3-Jun-08		18:06:20		69.2		45		3-Jun-08		18:07:53		67.4		44.5		14-Jul-08		18:25:59		78.8		43

		3-Jun-08		20:07:10		71		30.5		3-Jun-08		20:06:20		69.2		31.5		3-Jun-08		20:07:53		67.4		34.5		14-Jul-08		20:25:59		78.8		42.5

		3-Jun-08		22:07:10		70.41		27		3-Jun-08		22:06:20		68.61		29.5		3-Jun-08		22:07:53		68		31		14-Jul-08		22:25:59		77.61		41.5

		4-Jun-08		0:07:10		69.2		34		4-Jun-08		0:06:20		68.61		37		4-Jun-08		0:07:53		68		37		15-Jul-08		0:25:59		77		41

		4-Jun-08		2:07:10		69.2		35.5		4-Jun-08		2:06:20		68		40		4-Jun-08		2:07:53		68		38		15-Jul-08		2:25:59		76.4		41

		4-Jun-08		4:07:10		68.61		35		4-Jun-08		4:06:20		67.4		39.5		4-Jun-08		4:07:53		68		37.5		15-Jul-08		4:25:59		75.81		41.5

		4-Jun-08		6:07:10		69.8		34.5		4-Jun-08		6:06:20		68		39		4-Jun-08		6:07:53		68.61		37		15-Jul-08		6:25:59		75.2		41

		4-Jun-08		8:07:10		69.8		38.5		4-Jun-08		8:06:20		68		46		4-Jun-08		8:07:53		68		40.5		15-Jul-08		8:25:59		74.01		43.5

		4-Jun-08		10:07:10		70.41		41		4-Jun-08		10:06:20		69.8		53		4-Jun-08		10:07:53		68		45		15-Jul-08		10:25:59		74.6		45

		4-Jun-08		12:07:10		71		42.5		4-Jun-08		12:06:20		69.8		50		4-Jun-08		12:07:53		68		46.5		15-Jul-08		12:25:59		75.2		44.5

		4-Jun-08		14:07:10		70.41		41.5		4-Jun-08		14:06:20		69.2		53		4-Jun-08		14:07:53		66.81		47		15-Jul-08		14:25:59		75.81		45

		4-Jun-08		16:07:10		70.41		40		4-Jun-08		16:06:20		70.41		44.5		4-Jun-08		16:07:53		67.4		44.5		15-Jul-08		16:25:59		75.81		44

		4-Jun-08		18:07:10		71		38		4-Jun-08		18:06:20		70.41		38.5		4-Jun-08		18:07:53		67.4		42		15-Jul-08		18:25:59		76.4		42.5

		4-Jun-08		20:07:10		71		38		4-Jun-08		20:06:20		70.41		42		4-Jun-08		20:07:53		67.4		43		15-Jul-08		20:25:59		77		39.5

		4-Jun-08		22:07:10		71		37.5		4-Jun-08		22:06:20		69.8		43		4-Jun-08		22:07:53		67.4		42.5		15-Jul-08		22:25:59		77		41

		5-Jun-08		0:07:10		70.41		38		5-Jun-08		0:06:20		69.2		44		5-Jun-08		0:07:53		68		41.5		16-Jul-08		0:25:59		76.4		41.5

		5-Jun-08		2:07:10		69.8		36		5-Jun-08		2:06:20		69.8		38.5		5-Jun-08		2:07:53		68.61		39		16-Jul-08		2:25:59		75.81		41.5

		5-Jun-08		4:07:10		68.61		36		5-Jun-08		4:06:20		69.2		38.5		5-Jun-08		4:07:53		68		38.5		16-Jul-08		4:25:59		75.81		42

		5-Jun-08		6:07:10		68.61		36		5-Jun-08		6:06:20		68.61		38.5		5-Jun-08		6:07:53		68		38		16-Jul-08		6:25:59		75.2		41

		5-Jun-08		8:07:10		69.2		35		5-Jun-08		8:06:20		69.2		39.5		5-Jun-08		8:07:53		68		38		16-Jul-08		8:25:59		74.6		43.5

		5-Jun-08		10:07:10		70.41		35		5-Jun-08		10:06:20		71		36.5		5-Jun-08		10:07:53		68		38.5		16-Jul-08		10:25:59		75.2		44.5

		5-Jun-08		12:07:10		70.41		34.5		5-Jun-08		12:06:20		69.8		35		5-Jun-08		12:07:53		68.61		37		16-Jul-08		12:25:59		75.2		43.5

		5-Jun-08		14:07:10		70.41		32		5-Jun-08		14:06:20		69.2		34.5		5-Jun-08		14:07:53		68.61		35		16-Jul-08		14:25:59		75.81		45

		5-Jun-08		16:07:10		70.41		34.5		5-Jun-08		16:06:20		70.41		36.5		5-Jun-08		16:07:53		68.61		37.5		16-Jul-08		16:25:59		75.2		43.5

		5-Jun-08		18:07:10		71		35		5-Jun-08		18:06:20		69.8		36		5-Jun-08		18:07:53		68.61		37.5

		5-Jun-08		20:07:10		71		35.5		5-Jun-08		20:06:20		69.2		38.5		5-Jun-08		20:07:53		69.2		38

		5-Jun-08		22:07:10		71		35		5-Jun-08		22:06:20		68.61		39		5-Jun-08		22:07:53		69.2		37.5

		6-Jun-08		0:07:10		69.8		35.5		6-Jun-08		0:06:20		68		41		6-Jun-08		0:07:53		68.61		38.5

		6-Jun-08		2:07:10		69.2		36		6-Jun-08		2:06:20		67.4		41		6-Jun-08		2:07:53		68.61		38

		6-Jun-08		4:07:10		69.2		36		6-Jun-08		4:06:20		67.4		41.5		6-Jun-08		4:07:53		68.61		38.5

		6-Jun-08		6:07:10		69.2		36		6-Jun-08		6:06:20		67.4		41.5		6-Jun-08		6:07:53		68		38.5

		6-Jun-08		8:07:10		69.8		36.5		6-Jun-08		8:06:20		68		42		6-Jun-08		8:07:53		68.61		39.5

		6-Jun-08		10:07:10		70.41		36		6-Jun-08		10:06:20		68		42		6-Jun-08		10:07:53		68		40

		6-Jun-08		12:07:10		70.41		33		6-Jun-08		12:06:20		69.8		36		6-Jun-08		12:07:53		68		37.5

		6-Jun-08		14:07:10		70.41		38.5		6-Jun-08		14:06:20		69.2		40.5		6-Jun-08		14:07:53		67.4		42

		6-Jun-08		16:07:10		70.41		39.5		6-Jun-08		16:06:20		69.8		43		6-Jun-08		16:07:53		68		43

		6-Jun-08		18:07:10		71		38.5		6-Jun-08		18:06:20		69.2		44.5		6-Jun-08		18:07:53		68		42.5

		6-Jun-08		20:07:10		71		39.5		6-Jun-08		20:06:20		69.2		47		6-Jun-08		20:07:53		68.61		43

		6-Jun-08		22:07:10		71		39		6-Jun-08		22:06:20		68.61		51.5		6-Jun-08		22:07:53		68.61		43

		7-Jun-08		0:07:10		70.41		38.5		7-Jun-08		0:06:20		68.61		45		7-Jun-08		0:07:53		69.2		41

		7-Jun-08		2:07:10		69.8		38		7-Jun-08		2:06:20		68		48.5		7-Jun-08		2:07:53		69.2		40.5

		7-Jun-08		4:07:10		69.2		38		7-Jun-08		4:06:20		67.4		45.5		7-Jun-08		4:07:53		68.61		40

		7-Jun-08		6:07:10		69.2		37.5		7-Jun-08		6:06:20		67.4		43.5		7-Jun-08		6:07:53		68.61		39.5

		7-Jun-08		8:07:10		69.8		37.5		7-Jun-08		8:06:20		68.61		44		7-Jun-08		8:07:53		68.61		39.5

		7-Jun-08		10:07:10		70.41		36		7-Jun-08		10:06:20		68.61		40		7-Jun-08		10:07:53		68		39.5

		7-Jun-08		12:07:10		70.41		34.5		7-Jun-08		12:06:20		70.41		36.5		7-Jun-08		12:07:53		69.2		37

		7-Jun-08		14:07:10		70.41		31.5		7-Jun-08		14:06:20		69.8		32.5		7-Jun-08		14:07:53		68.61		33.5

		7-Jun-08		16:07:10		71		32		7-Jun-08		16:06:20		68.61		34.5		7-Jun-08		16:07:53		68		35

		7-Jun-08		18:07:10		70.41		34.5		7-Jun-08		18:06:20		68.61		36.5		7-Jun-08		18:07:53		68.61		36.5

		7-Jun-08		20:07:10		71		34.5		7-Jun-08		20:06:20		69.2		38		7-Jun-08		20:07:53		69.2		37

		7-Jun-08		22:07:10		70.41		34		7-Jun-08		22:06:20		68.61		38		7-Jun-08		22:07:53		68.61		36.5

		8-Jun-08		0:07:10		69.8		34		8-Jun-08		0:06:20		68		38		8-Jun-08		0:07:53		68.61		36.5

		8-Jun-08		2:07:10		69.2		34		8-Jun-08		2:06:20		68		37.5		8-Jun-08		2:07:53		68.61		36

		8-Jun-08		4:07:10		69.2		34		8-Jun-08		4:06:20		68		37		8-Jun-08		4:07:53		68.61		35.5

		8-Jun-08		6:07:10		69.8		33		8-Jun-08		6:06:20		67.4		37		8-Jun-08		6:07:53		68.61		35.5

		8-Jun-08		8:07:10		69.8		33.5		8-Jun-08		8:06:20		68		36.5		8-Jun-08		8:07:53		68.61		35.5

		8-Jun-08		10:07:10		70.41		34.5		8-Jun-08		10:06:20		68		37		8-Jun-08		10:07:53		69.2		35.5

		8-Jun-08		12:07:10		71		33		8-Jun-08		12:06:20		68.61		34.5		8-Jun-08		12:07:53		69.2		35

		8-Jun-08		14:07:10		71		30.5		8-Jun-08		14:06:20		68.61		32		8-Jun-08		14:07:53		69.2		33

		8-Jun-08		16:07:10		71.6		31		8-Jun-08		16:06:20		69.2		33.5		8-Jun-08		16:07:53		68.61		34.5

		8-Jun-08		18:07:10		71.6		34.5		8-Jun-08		18:06:20		68.61		37.5		8-Jun-08		18:07:53		68.61		38

		8-Jun-08		20:07:10		71.6		36.5		8-Jun-08		20:06:20		68.61		45		8-Jun-08		20:07:53		68.61		40.5

		8-Jun-08		22:07:10		71		37		8-Jun-08		22:06:20		68.61		44		8-Jun-08		22:07:53		68.61		40

		9-Jun-08		0:07:10		71		36		9-Jun-08		0:06:20		68.61		40.5		9-Jun-08		0:07:53		69.2		38.5

		9-Jun-08		2:07:10		70.41		36.5		9-Jun-08		2:06:20		68		43		9-Jun-08		2:07:53		69.2		38

		9-Jun-08		4:07:10		69.8		36.5		9-Jun-08		4:06:20		68		43		9-Jun-08		4:07:53		69.2		38.5

		9-Jun-08		6:07:10		69.2		37		9-Jun-08		6:06:20		67.4		43.5		9-Jun-08		6:07:53		69.2		39

		9-Jun-08		8:07:10		69.8		38		9-Jun-08		8:06:20		67.4		45		9-Jun-08		8:07:53		69.2		39

		9-Jun-08		10:07:10		70.41		38.5		9-Jun-08		10:06:20		68.61		43.5		9-Jun-08		10:07:53		69.2		40

		9-Jun-08		12:07:10		71		38		9-Jun-08		12:06:20		68.61		42.5		9-Jun-08		12:07:53		69.8		40.5

		9-Jun-08		14:07:10		71		38		9-Jun-08		14:06:20		68.61		41.5		9-Jun-08		14:07:53		69.2		40.5

		9-Jun-08		16:07:10		72.21		38.5		9-Jun-08		16:06:20		68.61		44.5		9-Jun-08		16:07:53		69.8		42

		9-Jun-08		18:07:10		71.6		39		9-Jun-08		18:06:20		68.61		46.5		9-Jun-08		18:07:53		69.2		43

		9-Jun-08		20:07:10		71.6		38		9-Jun-08		20:06:20		68		48		9-Jun-08		20:07:53		69.2		41.5

		9-Jun-08		22:07:10		71		37.5		9-Jun-08		22:06:20		68		47		9-Jun-08		22:07:53		69.2		40

		10-Jun-08		0:07:10		70.41		37.5		10-Jun-08		0:06:20		68		45.5		10-Jun-08		0:07:53		69.2		39.5

		10-Jun-08		2:07:10		69.8		37		10-Jun-08		2:06:20		67.4		46		10-Jun-08		2:07:53		69.2		39.5

		10-Jun-08		4:07:10		69.8		38		10-Jun-08		4:06:20		68		47		10-Jun-08		4:07:53		69.2		39.5

		10-Jun-08		6:07:10		69.8		38		10-Jun-08		6:06:20		68		44.5		10-Jun-08		6:07:53		69.8		39.5

		10-Jun-08		8:07:10		71		38.5		10-Jun-08		8:06:20		68.61		48		10-Jun-08		8:07:53		69.2		41

		10-Jun-08		10:07:10		71		37.5		10-Jun-08		10:06:20		69.2		43		10-Jun-08		10:07:53		69.2		40.5

		10-Jun-08		12:07:10		71		38		10-Jun-08		12:06:20		70.41		40		10-Jun-08		12:07:53		69.2		40.5

		10-Jun-08		14:07:10		71		37.5		10-Jun-08		14:06:20		71.6		37.5		10-Jun-08		14:07:53		68.61		39.5

		10-Jun-08		16:07:10		70.41		40		10-Jun-08		16:06:20		70.41		41		10-Jun-08		16:07:53		68.61		42

		10-Jun-08		18:07:10		70.41		44		10-Jun-08		18:06:20		71.6		47.5		10-Jun-08		18:07:53		69.2		46.5

		10-Jun-08		20:07:10		71		42		10-Jun-08		20:06:20		71		47		10-Jun-08		20:07:53		68.61		46

		10-Jun-08		22:07:10		71.6		41		10-Jun-08		22:06:20		71		51		10-Jun-08		22:07:53		69.2		44.5

		11-Jun-08		0:07:10		71.6		40.5		11-Jun-08		0:06:20		71		47.5		11-Jun-08		0:07:53		68.61		45

		11-Jun-08		2:07:10		71.6		36.5		11-Jun-08		2:06:20		71		40.5		11-Jun-08		2:07:53		69.2		40

		11-Jun-08		4:07:10		71		37.5		11-Jun-08		4:06:20		69.8		44		11-Jun-08		4:07:53		69.2		40.5

		11-Jun-08		6:07:10		70.41		36.5		11-Jun-08		6:06:20		69.8		41		11-Jun-08		6:07:53		69.2		39

		11-Jun-08		8:07:10		71		35.5		11-Jun-08		8:06:20		70.41		39		11-Jun-08		8:07:53		68		39

		11-Jun-08		10:07:10		71		27.5		11-Jun-08		10:06:20		70.41		29.5		11-Jun-08		10:07:53		67.4		31.5

		11-Jun-08		12:07:10		71		24		11-Jun-08		12:06:20		69.8		24.5		11-Jun-08		12:07:53		68.61		27

		11-Jun-08		14:07:10		71.6		27.5		11-Jun-08		14:06:20		70.41		30.5		11-Jun-08		14:07:53		68		31.5

		11-Jun-08		16:07:10		71		28.5		11-Jun-08		16:06:20		69.8		30		11-Jun-08		16:07:53		68.61		31.5

		11-Jun-08		18:07:10		71		31.5		11-Jun-08		18:06:20		69.8		33		11-Jun-08		18:07:53		68.61		34

		11-Jun-08		20:07:10		71		33.5		11-Jun-08		20:06:20		69.8		35		11-Jun-08		20:07:53		68.61		36

		11-Jun-08		22:07:10		71.6		33.5		11-Jun-08		22:06:20		69.2		37		11-Jun-08		22:07:53		68.61		37

		12-Jun-08		0:07:10		70.41		34		12-Jun-08		0:06:20		69.2		36.5		12-Jun-08		0:07:53		68.61		36.5

		12-Jun-08		2:07:10		69.8		33.5		12-Jun-08		2:06:20		68.61		36.5		12-Jun-08		2:07:53		68.61		36

		12-Jun-08		4:07:10		69.2		34		12-Jun-08		4:06:20		68.61		37		12-Jun-08		4:07:53		68.61		36

		12-Jun-08		6:07:10		68.61		34.5		12-Jun-08		6:06:20		68		37		12-Jun-08		6:07:53		68		36.5

		12-Jun-08		8:07:10		69.8		34.5		12-Jun-08		8:06:20		69.2		37.5		12-Jun-08		8:07:53		68.61		36.5

		12-Jun-08		10:07:10		71		34		12-Jun-08		10:06:20		71		36		12-Jun-08		10:07:53		68.61		37

		12-Jun-08		12:07:10		71		29.5		12-Jun-08		12:06:20		71.6		30		12-Jun-08		12:07:53		69.8		32

		12-Jun-08		14:07:10		71		24.5		12-Jun-08		14:06:20		72.8		26		12-Jun-08		14:07:53		69.8		28.5

		12-Jun-08		16:07:10		71		26.5		12-Jun-08		16:06:20		71.6		20.5		12-Jun-08		16:07:53		69.2		28

		12-Jun-08		18:07:10		70.41		27.5		12-Jun-08		18:06:20		71		27.5		12-Jun-08		18:07:53		69.2		29.5

		12-Jun-08		20:07:10		70.41		35.5		12-Jun-08		20:06:20		71		38.5		12-Jun-08		20:07:53		69.2		38

		12-Jun-08		22:07:10		71		35.5		12-Jun-08		22:06:20		70.41		40		12-Jun-08		22:07:53		69.2		38

		13-Jun-08		0:07:10		70.41		36		13-Jun-08		0:06:20		70.41		39.5		13-Jun-08		0:07:53		69.2		37.5

		13-Jun-08		2:07:10		69.8		36		13-Jun-08		2:06:20		69.8		39.5		13-Jun-08		2:07:53		69.2		37.5

		13-Jun-08		4:07:10		69.8		36.5		13-Jun-08		4:06:20		69.8		40.5		13-Jun-08		4:07:53		69.2		38

		13-Jun-08		6:07:10		69.2		36.5		13-Jun-08		6:06:20		69.8		39.5		13-Jun-08		6:07:53		69.2		37.5

		13-Jun-08		8:07:10		70.41		37		13-Jun-08		8:06:20		70.41		39.5		13-Jun-08		8:07:53		69.2		39

		13-Jun-08		10:07:10		71		36.5		13-Jun-08		10:06:20		70.41		38.5		13-Jun-08		10:07:53		69.2		38.5

		13-Jun-08		12:07:10		71		24		13-Jun-08		12:06:20		71.6		25		13-Jun-08		12:07:53		69.8		28

		13-Jun-08		14:07:10		71		22.5		13-Jun-08		14:06:20		71.6		23.5		13-Jun-08		14:07:53		69.2		25

		13-Jun-08		16:07:10		70.41		29		13-Jun-08		16:06:20		72.21		30		13-Jun-08		16:07:53		69.8		31.5

		13-Jun-08		18:07:10		71		26.5		13-Jun-08		18:06:20		71		27		13-Jun-08		18:07:53		69.8		29

		13-Jun-08		20:07:10		71		29		13-Jun-08		20:06:20		71.6		27.5		13-Jun-08		20:07:53		68.61		29.5

		13-Jun-08		22:07:10		71.6		32.5		13-Jun-08		22:06:20		71		33.5		13-Jun-08		22:07:53		69.2		34.5

		14-Jun-08		0:07:10		71		33		14-Jun-08		0:06:20		70.41		35.5		14-Jun-08		0:07:53		69.2		35.5

		14-Jun-08		2:07:10		70.41		34.5		14-Jun-08		2:06:20		70.41		37		14-Jun-08		2:07:53		69.2		36

		14-Jun-08		4:07:10		69.8		34.5		14-Jun-08		4:06:20		69.8		38.5		14-Jun-08		4:07:53		69.2		36.5

		14-Jun-08		6:07:10		69.8		35.5		14-Jun-08		6:06:20		69.8		38.5		14-Jun-08		6:07:53		68.61		37

		14-Jun-08		8:07:10		70.41		36		14-Jun-08		8:06:20		71		38.5		14-Jun-08		8:07:53		69.2		38

		14-Jun-08		10:07:10		71		36.5		14-Jun-08		10:06:20		71		39.5		14-Jun-08		10:07:53		68.61		39.5

		14-Jun-08		12:07:10		70.41		39		14-Jun-08		12:06:20		71.6		42		14-Jun-08		12:07:53		69.2		41.5

		14-Jun-08		14:07:10		71		37.5		14-Jun-08		14:06:20		72.8		37		14-Jun-08		14:07:53		69.2		39.5

		14-Jun-08		16:07:10		70.41		39		14-Jun-08		16:06:20		71		41		14-Jun-08		16:07:53		69.8		41

		14-Jun-08		18:07:10		70.41		39		14-Jun-08		18:06:20		71		42.5		14-Jun-08		18:07:53		68.61		42

		14-Jun-08		20:07:10		70.41		38		14-Jun-08		20:06:20		70.41		45		14-Jun-08		20:07:53		68.61		41.5

		14-Jun-08		22:07:10		70.41		38		14-Jun-08		22:06:20		71		45		14-Jun-08		22:07:53		68.61		40.5

		15-Jun-08		0:07:10		70.41		38.5		15-Jun-08		0:06:20		69.8		43.5		15-Jun-08		0:07:53		68.61		40.5

		15-Jun-08		2:07:10		70.41		38		15-Jun-08		2:06:20		69.8		44		15-Jun-08		2:07:53		68.61		40.5

		15-Jun-08		4:07:10		69.8		37.5		15-Jun-08		4:06:20		69.2		44		15-Jun-08		4:07:53		68.61		40

		15-Jun-08		6:07:10		69.8		38		15-Jun-08		6:06:20		69.2		45		15-Jun-08		6:07:53		68.61		40.5

		15-Jun-08		8:07:10		70.41		39		15-Jun-08		8:06:20		69.2		45.5		15-Jun-08		8:07:53		68.61		41

		15-Jun-08		10:07:10		70.41		39		15-Jun-08		10:06:20		69.8		45		15-Jun-08		10:07:53		68.61		41

		15-Jun-08		12:07:10		70.41		40		15-Jun-08		12:06:20		70.41		46.5		15-Jun-08		12:07:53		69.2		42

		15-Jun-08		14:07:10		71		41.5		15-Jun-08		14:06:20		71		47.5		15-Jun-08		14:07:53		69.2		44

		15-Jun-08		16:07:10		71		41.5		15-Jun-08		16:06:20		70.41		51.5		15-Jun-08		16:07:53		69.2		44.5

		15-Jun-08		18:07:10		71		40.5		15-Jun-08		18:06:20		70.41		50		15-Jun-08		18:07:53		69.2		43.5

		15-Jun-08		20:07:10		71		38.5		15-Jun-08		20:06:20		69.8		47		15-Jun-08		20:07:53		69.2		41.5

		15-Jun-08		22:07:10		71		38.5		15-Jun-08		22:06:20		70.41		45.5		15-Jun-08		22:07:53		69.2		41

		16-Jun-08		0:07:10		70.41		38.5		16-Jun-08		0:06:20		69.8		44.5		16-Jun-08		0:07:53		69.2		40.5

		16-Jun-08		2:07:10		70.41		38		16-Jun-08		2:06:20		69.2		44.5		16-Jun-08		2:07:53		69.2		40

		16-Jun-08		4:07:10		70.41		38		16-Jun-08		4:06:20		68.61		45		16-Jun-08		4:07:53		69.2		40

		16-Jun-08		6:07:10		69.8		37.5		16-Jun-08		6:06:20		68.61		44.5		16-Jun-08		6:07:53		69.2		39.5

		16-Jun-08		8:07:10		69.8		38		16-Jun-08		8:06:20		68.61		44.5		16-Jun-08		8:07:53		69.2		40

		16-Jun-08		10:07:10		69.8		38.5		16-Jun-08		10:06:20		69.8		44.5		16-Jun-08		10:07:53		69.2		40

		16-Jun-08		12:07:10		70.41		40.5		16-Jun-08		12:06:20		69.8		47		16-Jun-08		12:07:53		69.2		41.5

		16-Jun-08		14:07:10		70.41		42		16-Jun-08		14:06:20		70.41		49.5		16-Jun-08		14:07:53		69.2		43.5

		16-Jun-08		16:07:10		71		40.5		16-Jun-08		16:06:20		71		46		16-Jun-08		16:07:53		69.2		43

		16-Jun-08		18:07:10		71		39.5		16-Jun-08		18:06:20		71		43.5		16-Jun-08		18:07:53		69.2		42.5

		16-Jun-08		20:07:10		71		38		16-Jun-08		20:06:20		70.41		44.5		16-Jun-08		20:07:53		69.2		41

		16-Jun-08		22:07:10		70.41		38		16-Jun-08		22:06:20		70.41		43		16-Jun-08		22:07:53		69.2		40

		17-Jun-08		0:07:10		70.41		37.5		17-Jun-08		0:06:20		69.8		42		17-Jun-08		0:07:53		69.2		39.5

		17-Jun-08		2:07:10		69.8		36.5		17-Jun-08		2:06:20		68.61		43		17-Jun-08		2:07:53		69.2		39

		17-Jun-08		4:07:10		69.8		38		17-Jun-08		4:06:20		68		45.5		17-Jun-08		4:07:53		69.2		40

		17-Jun-08		6:07:10		69.8		38		17-Jun-08		6:06:20		68		45.5		17-Jun-08		6:07:53		69.2		40

		17-Jun-08		8:07:10		70.41		38.5		17-Jun-08		8:06:20		70.41		45		17-Jun-08		8:07:53		68.61		41

		17-Jun-08		10:07:10		70.41		39		17-Jun-08		10:06:20		71		44		17-Jun-08		10:07:53		68.61		41

		17-Jun-08		12:07:10		71		39.5		17-Jun-08		12:06:20		69.8		45.5		17-Jun-08		12:07:53		69.2		42

		17-Jun-08		14:07:10		71		41.5		17-Jun-08		14:06:20		70.41		48.5		17-Jun-08		14:07:53		68		45

		17-Jun-08		16:07:10		71		40		17-Jun-08		16:06:20		70.41		45		17-Jun-08		16:07:53		69.2		43.5

		17-Jun-08		18:07:10		71		39.5		17-Jun-08		18:06:20		70.41		46		17-Jun-08		18:07:53		69.8		41.5

		17-Jun-08		20:07:10		70.41		38.5		17-Jun-08		20:06:20		69.8		44.5		17-Jun-08		20:07:53		69.8		40

		17-Jun-08		22:07:10		70.41		38		17-Jun-08		22:06:20		69.8		43		17-Jun-08		22:07:53		69.8		39.5

		18-Jun-08		0:07:10		70.41		37.5		18-Jun-08		0:06:20		69.2		43		18-Jun-08		0:07:53		69.8		39

		18-Jun-08		2:07:10		70.41		37.5		18-Jun-08		2:06:20		68		43.5		18-Jun-08		2:07:53		69.8		38.5

		18-Jun-08		4:07:10		70.41		38		18-Jun-08		4:06:20		67.4		46		18-Jun-08		4:07:53		69.8		39

		18-Jun-08		6:07:10		70.41		38		18-Jun-08		6:06:20		66.81		46.5		18-Jun-08		6:07:53		69.8		39

		18-Jun-08		8:07:10		70.41		39		18-Jun-08		8:06:20		70.41		43.5		18-Jun-08		8:07:53		69.2		40.5

		18-Jun-08		10:07:10		71		38.5		18-Jun-08		10:06:20		70.41		44.5		18-Jun-08		10:07:53		68.61		41

		18-Jun-08		12:07:10		71		39		18-Jun-08		12:06:20		69.8		44.5		18-Jun-08		12:07:53		69.8		41

		18-Jun-08		14:07:10		71		42		18-Jun-08		14:06:20		69.8		46.5		18-Jun-08		14:07:53		69.2		44.5

		18-Jun-08		16:07:10		71		43.5		18-Jun-08		16:06:20		69.8		51.5		18-Jun-08		16:07:53		69.2		46

		18-Jun-08		18:07:10		71		29		18-Jun-08		18:06:20		69.2		31		18-Jun-08		18:07:53		69.2		32

		18-Jun-08		20:07:10		71		28		18-Jun-08		20:06:20		68.61		29		18-Jun-08		20:07:53		69.2		30

		18-Jun-08		22:07:10		71		29.5		18-Jun-08		22:06:20		68.61		31		18-Jun-08		22:07:53		69.2		31.5

		19-Jun-08		0:07:10		70.41		29		19-Jun-08		0:06:20		68.61		31.5		19-Jun-08		0:07:53		69.2		31

		19-Jun-08		2:07:10		69.8		34		19-Jun-08		2:06:20		68		37		19-Jun-08		2:07:53		69.2		35.5

		19-Jun-08		4:07:10		69.2		35		19-Jun-08		4:06:20		67.4		39.5		19-Jun-08		4:07:53		68.61		36.5

		19-Jun-08		6:07:10		69.8		34		19-Jun-08		6:06:20		67.4		39		19-Jun-08		6:07:53		69.2		35.5

		19-Jun-08		8:07:10		69.8		35.5		19-Jun-08		8:06:20		68		41.5		19-Jun-08		8:07:53		69.2		37.5

		19-Jun-08		10:07:10		71		33.5		19-Jun-08		10:06:20		70.41		36.5		19-Jun-08		10:07:53		69.2		36.5

		19-Jun-08		12:07:10		71		31		19-Jun-08		12:06:20		70.41		33		19-Jun-08		12:07:53		69.8		33

		19-Jun-08		14:07:10		70.41		34.5		19-Jun-08		14:06:20		71		36		19-Jun-08		14:07:53		69.8		36

		19-Jun-08		16:07:10		70.41		31		19-Jun-08		16:06:20		69.2		32.5		19-Jun-08		16:07:53		69.8		32.5

		19-Jun-08		18:07:10		71		25		19-Jun-08		18:06:20		69.2		26		19-Jun-08		18:07:53		69.2		27

		19-Jun-08		20:07:10		71		26		19-Jun-08		20:06:20		69.2		27		19-Jun-08		20:07:53		69.2		27.5

		19-Jun-08		22:07:10		71		30.5		19-Jun-08		22:06:20		68.61		31.5		19-Jun-08		22:07:53		69.2		31.5

		20-Jun-08		0:07:10		71		33		20-Jun-08		0:06:20		68		37		20-Jun-08		0:07:53		68.61		35.5

		20-Jun-08		2:07:10		70.41		33.5		20-Jun-08		2:06:20		68		37.5		20-Jun-08		2:07:53		68.61		35.5

		20-Jun-08		4:07:10		69.8		33.5		20-Jun-08		4:06:20		68		38		20-Jun-08		4:07:53		68.61		36

		20-Jun-08		6:07:10		69.2		34.5		20-Jun-08		6:06:20		67.4		39		20-Jun-08		6:07:53		68		36.5

		20-Jun-08		8:07:10		69.8		35.5		20-Jun-08		8:06:20		68.61		39		20-Jun-08		8:07:53		68.61		37.5

		20-Jun-08		10:07:10		71		35.5		20-Jun-08		10:06:20		70.41		38		20-Jun-08		10:07:53		68.61		38

		20-Jun-08		12:07:10		70.41		34		20-Jun-08		12:06:20		72.21		34.5		20-Jun-08		12:07:53		68.61		36.5

		20-Jun-08		14:07:10		70.41		31		20-Jun-08		14:06:20		69.8		32		20-Jun-08		14:07:53		68		33.5

		20-Jun-08		16:07:10		70.41		32.5		20-Jun-08		16:06:20		71		34.5		20-Jun-08		16:07:53		68.61		35.5

		20-Jun-08		18:07:10		70.41		29		20-Jun-08		18:06:20		69.2		30		20-Jun-08		18:07:53		68.61		31

		20-Jun-08		20:07:10		71		31.5		20-Jun-08		20:06:20		68		34.5		20-Jun-08		20:07:53		68.61		34.5

		20-Jun-08		22:07:10		71		32.5		20-Jun-08		22:06:20		68		36		20-Jun-08		22:07:53		68.61		35

		21-Jun-08		0:07:10		71		34.5		21-Jun-08		0:06:20		68.61		38.5		21-Jun-08		0:07:53		68.61		37

		21-Jun-08		2:07:10		70.41		35		21-Jun-08		2:06:20		67.4		41		21-Jun-08		2:07:53		68.61		37

		21-Jun-08		4:07:10		70.41		36		21-Jun-08		4:06:20		67.4		41		21-Jun-08		4:07:53		69.2		37.5

		21-Jun-08		6:07:10		69.8		36		21-Jun-08		6:06:20		68		43		21-Jun-08		6:07:53		68.61		38.5

		21-Jun-08		8:07:10		71		36		21-Jun-08		8:06:20		68.61		43		21-Jun-08		8:07:53		68.61		39

		21-Jun-08		10:07:10		71		35		21-Jun-08		10:06:20		69.2		37		21-Jun-08		10:07:53		69.2		37

		21-Jun-08		12:07:10		70.41		30.5		21-Jun-08		12:06:20		71		31.5		21-Jun-08		12:07:53		69.2		33

		21-Jun-08		14:07:10		71		30		21-Jun-08		14:06:20		70.41		30.5		21-Jun-08		14:07:53		69.2		31.5

		21-Jun-08		16:07:10		71		26.5		21-Jun-08		16:06:20		71.6		26.5		21-Jun-08		16:07:53		68.61		29

		21-Jun-08		18:07:10		70.41		23		21-Jun-08		18:06:20		70.41		24		21-Jun-08		18:07:53		69.2		26

		21-Jun-08		20:07:10		71		22.5		21-Jun-08		20:06:20		71		22.5		21-Jun-08		20:07:53		69.2		24.5

		21-Jun-08		22:07:10		71		27.5		21-Jun-08		22:06:20		70.41		29		21-Jun-08		22:07:53		69.2		30

		22-Jun-08		0:07:10		71		31		22-Jun-08		0:06:20		70.41		34		22-Jun-08		0:07:53		68.61		34.5

		22-Jun-08		2:07:10		71		31.5		22-Jun-08		2:06:20		69.8		35		22-Jun-08		2:07:53		68.61		35.5

		22-Jun-08		4:07:10		71		32.5		22-Jun-08		4:06:20		69.8		34.5		22-Jun-08		4:07:53		68.61		35.5

		22-Jun-08		6:07:10		70.41		33		22-Jun-08		6:06:20		69.2		35.5		22-Jun-08		6:07:53		68.61		35.5

		22-Jun-08		8:07:10		71		33.5		22-Jun-08		8:06:20		69.2		36.5		22-Jun-08		8:07:53		69.8		35.5

		22-Jun-08		10:07:10		71		34.5		22-Jun-08		10:06:20		70.41		37		22-Jun-08		10:07:53		69.8		37

		22-Jun-08		12:07:10		71.6		32		22-Jun-08		12:06:20		71		34.5		22-Jun-08		12:07:53		69.2		36

		22-Jun-08		14:07:10		71.6		29.5		22-Jun-08		14:06:20		71		32.5		22-Jun-08		14:07:53		69.8		33.5

		22-Jun-08		16:07:10		72.21		26		22-Jun-08		16:06:20		70.41		29		22-Jun-08		16:07:53		69.2		30.5

		22-Jun-08		18:07:10		72.21		22.5		22-Jun-08		18:06:20		70.41		25.5		22-Jun-08		18:07:53		69.2		26.5

		22-Jun-08		20:07:10		72.21		30.5		22-Jun-08		20:06:20		70.41		31.5		22-Jun-08		20:07:53		69.8		31.5

		22-Jun-08		22:07:10		71.6		31		22-Jun-08		22:06:20		70.41		34.5		22-Jun-08		22:07:53		69.2		34

		23-Jun-08		0:07:10		71		34.5		23-Jun-08		0:06:20		69.2		39		23-Jun-08		0:07:53		69.2		36.5

		23-Jun-08		2:07:10		70.41		35.5		23-Jun-08		2:06:20		69.8		41.5		23-Jun-08		2:07:53		69.2		38

		23-Jun-08		4:07:10		70.41		36		23-Jun-08		4:06:20		69.2		42		23-Jun-08		4:07:53		69.8		38

		23-Jun-08		6:07:10		70.41		35.5		23-Jun-08		6:06:20		68.61		42		23-Jun-08		6:07:53		69.8		37.5

		23-Jun-08		8:07:10		70.41		37		23-Jun-08		8:06:20		69.2		44		23-Jun-08		8:07:53		69.8		38.5

		23-Jun-08		10:07:10		71		38		23-Jun-08		10:06:20		69.2		45		23-Jun-08		10:07:53		69.8		39.5

		23-Jun-08		12:07:10		71		38.5		23-Jun-08		12:06:20		69.8		42.5		23-Jun-08		12:07:53		69.8		39.5

		23-Jun-08		14:07:10		71		39		23-Jun-08		14:06:20		70.41		44.5		23-Jun-08		14:07:53		69.8		41

		23-Jun-08		16:07:10		71.6		39.5		23-Jun-08		16:06:20		69.8		46.5		23-Jun-08		16:07:53		69.8		42

		23-Jun-08		18:07:10		71.6		38		23-Jun-08		18:06:20		70.41		42.5		23-Jun-08		18:07:53		69.2		41

		23-Jun-08		20:07:10		71.6		37		23-Jun-08		20:06:20		69.8		43		23-Jun-08		20:07:53		69.8		39.5

		23-Jun-08		22:07:10		71		36		23-Jun-08		22:06:20		69.2		42.5		23-Jun-08		22:07:53		69.8		38.5

		24-Jun-08		0:07:10		69.8		36.5		24-Jun-08		0:06:20		69.2		42		24-Jun-08		0:07:53		69.2		38.5

		24-Jun-08		2:07:10		70.41		36.5		24-Jun-08		2:06:20		68.61		42		24-Jun-08		2:07:53		69.8		38

		24-Jun-08		4:07:10		70.41		36		24-Jun-08		4:06:20		68		42.5		24-Jun-08		4:07:53		69.8		37.5

		24-Jun-08		6:07:10		70.41		37.5		24-Jun-08		6:06:20		67.4		45.5		24-Jun-08		6:07:53		69.8		38.5

		24-Jun-08		8:07:10		70.41		38.5		24-Jun-08		8:06:20		69.8		44.5		24-Jun-08		8:07:53		69.8		40

		24-Jun-08		10:07:10		70.41		38		24-Jun-08		10:06:20		71		44		24-Jun-08		10:07:53		69.2		40.5

		24-Jun-08		12:07:10		70.41		39.5		24-Jun-08		12:06:20		71.6		42.5		24-Jun-08		12:07:53		69.8		41

		24-Jun-08		14:07:10		70.41		38.5		24-Jun-08		14:06:20		71		42.5		24-Jun-08		14:07:53		68		42.5

		24-Jun-08		16:07:10		71		39		24-Jun-08		16:06:20		69.2		47		24-Jun-08		16:07:53		68		42.5

		24-Jun-08		18:07:10		71		38.5		24-Jun-08		18:06:20		69.2		45.5		24-Jun-08		18:07:53		69.2		41.5

		24-Jun-08		20:07:10		70.41		38.5		24-Jun-08		20:06:20		68.61		47		24-Jun-08		20:07:53		69.2		40.5

		24-Jun-08		22:07:10		70.41		38		24-Jun-08		22:06:20		68.61		44		24-Jun-08		22:07:53		69.2		39.5

		25-Jun-08		0:07:10		70.41		38.5		25-Jun-08		0:06:20		68		43.5		25-Jun-08		0:07:53		69.2		40

		25-Jun-08		2:07:10		70.41		37.5		25-Jun-08		2:06:20		67.4		46.5		25-Jun-08		2:07:53		69.8		39

		25-Jun-08		4:07:10		70.41		37.5		25-Jun-08		4:06:20		67.4		45		25-Jun-08		4:07:53		69.8		39

		25-Jun-08		6:07:10		70.41		37		25-Jun-08		6:06:20		66.81		45		25-Jun-08		6:07:53		69.8		38.5

		25-Jun-08		8:07:10		69.8		38.5		25-Jun-08		8:06:20		68		44		25-Jun-08		8:07:53		68.61		40.5

		25-Jun-08		10:07:10		70.41		39		25-Jun-08		10:06:20		69.8		46.5		25-Jun-08		10:07:53		68.61		42

		25-Jun-08		12:07:10		70.41		40.5		25-Jun-08		12:06:20		69.8		44		25-Jun-08		12:07:53		68		43.5

		25-Jun-08		14:07:10		70.41		42		25-Jun-08		14:06:20		69.8		47		25-Jun-08		14:07:53		67.4		46.5

		25-Jun-08		16:07:10		70.41		41.5		25-Jun-08		16:06:20		69.8		50		25-Jun-08		16:07:53		68.61		45

		25-Jun-08		18:07:10		71		39.5		25-Jun-08		18:06:20		69.2		48		25-Jun-08		18:07:53		68.61		43.5

		25-Jun-08		20:07:10		71		38.5		25-Jun-08		20:06:20		69.2		44		25-Jun-08		20:07:53		69.2		42

		25-Jun-08		22:07:10		71		38		25-Jun-08		22:06:20		69.8		43.5		25-Jun-08		22:07:53		69.2		40.5

		26-Jun-08		0:07:10		70.41		38		26-Jun-08		0:06:20		68.61		46		26-Jun-08		0:07:53		69.2		40

		26-Jun-08		2:07:10		69.8		38		26-Jun-08		2:06:20		68.61		44.5		26-Jun-08		2:07:53		68.61		39.5

		26-Jun-08		4:07:10		70.41		38		26-Jun-08		4:06:20		68.61		44		26-Jun-08		4:07:53		69.2		39.5

		26-Jun-08		6:07:10		70.41		37.5		26-Jun-08		6:06:20		68		44.5		26-Jun-08		6:07:53		69.8		39

		26-Jun-08		8:07:10		70.41		39		26-Jun-08		8:06:20		69.2		44		26-Jun-08		8:07:53		68		41.5

		26-Jun-08		10:07:10		70.41		39		26-Jun-08		10:06:20		69.2		45		26-Jun-08		10:07:53		68.61		41.5

		26-Jun-08		12:07:10		70.41		40.5		26-Jun-08		12:06:20		71		43.5		26-Jun-08		12:07:53		68.61		43

		26-Jun-08		14:07:10		70.41		42.5		26-Jun-08		14:06:20		70.41		47.5		26-Jun-08		14:07:53		68		46

		26-Jun-08		16:07:10		70.41		42.5		26-Jun-08		16:06:20		68.61		49.5		26-Jun-08		16:07:53		68.61		45.5

		26-Jun-08		18:07:10		70.41		41.5		26-Jun-08		18:06:20		69.2		47		26-Jun-08		18:07:53		69.2		43.5

		26-Jun-08		20:07:10		70.41		40		26-Jun-08		20:06:20		69.2		47.5		26-Jun-08		20:07:53		69.2		42

		26-Jun-08		22:07:10		70.41		39		26-Jun-08		22:06:20		69.2		46.5		26-Jun-08		22:07:53		69.2		41

		27-Jun-08		0:07:10		69.8		38		27-Jun-08		0:06:20		68		47.5		27-Jun-08		0:07:53		68.61		40.5

		27-Jun-08		2:07:10		69.8		38		27-Jun-08		2:06:20		67.4		46		27-Jun-08		2:07:53		69.2		40

		27-Jun-08		4:07:10		70.41		38		27-Jun-08		4:06:20		68		45		27-Jun-08		4:07:53		69.8		39

		27-Jun-08		6:07:10		69.8		37.5		27-Jun-08		6:06:20		67.4		45		27-Jun-08		6:07:53		69.8		39

		27-Jun-08		8:07:10		70.41		39		27-Jun-08		8:06:20		68.61		49.5		27-Jun-08		8:07:53		69.2		40.5

		27-Jun-08		10:07:10		70.41		39.5		27-Jun-08		10:06:20		69.8		44.5		27-Jun-08		10:07:53		68.61		42

		27-Jun-08		12:07:10		70.41		41		27-Jun-08		12:06:20		70.41		50.5		27-Jun-08		12:07:53		69.2		43

		27-Jun-08		14:07:10		70.41		43		27-Jun-08		14:06:20		71		48.5		27-Jun-08		14:07:53		68		46

		27-Jun-08		16:07:10		70.41		42.5		27-Jun-08		16:06:20		70.41		48.5		27-Jun-08		16:07:53		68		46

		27-Jun-08		18:07:10		70.41		40		27-Jun-08		18:06:20		70.41		44		27-Jun-08		18:07:53		68.61		43

		27-Jun-08		20:07:10		70.41		39		27-Jun-08		20:06:20		70.41		44.5		27-Jun-08		20:07:53		68.61		42

		27-Jun-08		22:07:10		70.41		38.5		27-Jun-08		22:06:20		70.41		45		27-Jun-08		22:07:53		69.2		41

		28-Jun-08		0:07:10		69.8		38.5		28-Jun-08		0:06:20		69.2		46		28-Jun-08		0:07:53		68.61		41

		28-Jun-08		2:07:10		69.8		38.5		28-Jun-08		2:06:20		69.2		45		28-Jun-08		2:07:53		68.61		40.5

		28-Jun-08		4:07:10		69.2		38.5		28-Jun-08		4:06:20		69.2		44.5		28-Jun-08		4:07:53		68.61		40

		28-Jun-08		6:07:10		69.2		39.5		28-Jun-08		6:06:20		69.2		45.5		28-Jun-08		6:07:53		68.61		40.5

		28-Jun-08		8:07:10		69.8		39.5		28-Jun-08		8:06:20		70.41		44		28-Jun-08		8:07:53		68.61		41.5

		28-Jun-08		10:07:10		71		40.5		28-Jun-08		10:06:20		71		50.5		28-Jun-08		10:07:53		68.61		43

		28-Jun-08		12:07:10		70.41		42.5		28-Jun-08		12:06:20		71.6		48		28-Jun-08		12:07:53		69.8		44

		28-Jun-08		14:07:10		70.41		43.5		28-Jun-08		14:06:20		71.6		53.5		28-Jun-08		14:07:53		68.61		46

		28-Jun-08		16:07:10		70.41		44		28-Jun-08		16:06:20		71		50		28-Jun-08		16:07:53		69.2		46.5

		28-Jun-08		18:07:10		71		40.5		28-Jun-08		18:06:20		70.41		51		28-Jun-08		18:07:53		69.2		43.5

		28-Jun-08		20:07:10		71		39.5		28-Jun-08		20:06:20		70.41		49.5		28-Jun-08		20:07:53		69.2		42

		28-Jun-08		22:07:10		70.41		39.5		28-Jun-08		22:06:20		69.8		49		28-Jun-08		22:07:53		69.8		41

		29-Jun-08		0:07:10		69.8		39.5		29-Jun-08		0:06:20		69.8		49.5		29-Jun-08		0:07:53		69.2		41.5

		29-Jun-08		2:07:10		69.8		40		29-Jun-08		2:06:20		69.2		49		29-Jun-08		2:07:53		69.2		41.5

		29-Jun-08		4:07:10		69.8		40		29-Jun-08		4:06:20		69.2		50		29-Jun-08		4:07:53		69.8		41.5

		29-Jun-08		6:07:10		69.8		40		29-Jun-08		6:06:20		69.2		50.5		29-Jun-08		6:07:53		69.8		41

		29-Jun-08		8:07:10		69.8		40		29-Jun-08		8:06:20		69.8		50.5		29-Jun-08		8:07:53		69.8		41.5

		29-Jun-08		10:07:10		70.41		40.5		29-Jun-08		10:06:20		69.2		47		29-Jun-08		10:07:53		69.8		41.5

		29-Jun-08		12:07:10		70.41		41.5		29-Jun-08		12:06:20		69.2		53.5		29-Jun-08		12:07:53		69.8		42.5

		29-Jun-08		14:07:10		70.41		42.5		29-Jun-08		14:06:20		69.8		48		29-Jun-08		14:07:53		70.41		44

		29-Jun-08		16:07:10		71		43		29-Jun-08		16:06:20		69.8		52.5		29-Jun-08		16:07:53		70.41		44.5

		29-Jun-08		18:07:10		71		42		29-Jun-08		18:06:20		70.41		53		29-Jun-08		18:07:53		70.41		44

		29-Jun-08		20:07:10		71		40		29-Jun-08		20:06:20		69.2		52		29-Jun-08		20:07:53		69.8		42

		29-Jun-08		22:07:10		70.41		39.5		29-Jun-08		22:06:20		69.2		50		29-Jun-08		22:07:53		69.8		41

		30-Jun-08		0:07:10		69.2		40		30-Jun-08		0:06:20		69.2		48.5		30-Jun-08		0:07:53		69.2		41

		30-Jun-08		2:07:10		69.2		40		30-Jun-08		2:06:20		69.2		48.5		30-Jun-08		2:07:53		69.8		41

		30-Jun-08		4:07:10		69.2		40		30-Jun-08		4:06:20		69.2		49		30-Jun-08		4:07:53		69.2		41

		30-Jun-08		6:07:10		69.2		40		30-Jun-08		6:06:20		69.2		49		30-Jun-08		6:07:53		69.2		41

		30-Jun-08		8:07:10		69.2		40		30-Jun-08		8:06:20		69.2		49		30-Jun-08		8:07:53		69.8		41

		30-Jun-08		10:07:10		69.2		40		30-Jun-08		10:06:20		69.8		47.5		30-Jun-08		10:07:53		69.8		41

		30-Jun-08		12:07:10		70.41		41.5		30-Jun-08		12:06:20		69.8		49.5		30-Jun-08		12:07:53		70.41		42

		30-Jun-08		14:07:10		70.41		43		30-Jun-08		14:06:20		70.41		48		30-Jun-08		14:07:53		70.41		43.5

		30-Jun-08		16:07:10		71		43		30-Jun-08		16:06:20		70.41		50.5		30-Jun-08		16:07:53		70.41		44.5

		30-Jun-08		18:07:10		71		41.5		30-Jun-08		18:06:20		69.8		50		30-Jun-08		18:07:53		70.41		43.5

		30-Jun-08		20:07:10		71		40		30-Jun-08		20:06:20		69.8		50		30-Jun-08		20:07:53		70.41		42

		30-Jun-08		22:07:10		69.8		39.5		30-Jun-08		22:06:20		69.8		48.5		30-Jun-08		22:07:53		69.8		40.5

		1-Jul-08		0:07:10		69.8		40		1-Jul-08		0:06:20		69.2		48.5		1-Jul-08		0:07:53		69.2		41

		1-Jul-08		2:07:10		69.2		40		1-Jul-08		2:06:20		69.2		48.5		1-Jul-08		2:07:53		69.2		41

		1-Jul-08		4:07:10		69.8		40.5		1-Jul-08		4:06:20		68.61		49		1-Jul-08		4:07:53		69.8		41

		1-Jul-08		6:07:10		69.8		40		1-Jul-08		6:06:20		68.61		49.5		1-Jul-08		6:07:53		69.8		41

		1-Jul-08		8:07:10		70.41		40.5		1-Jul-08		8:06:20		71		48.5		1-Jul-08		8:07:53		69.8		41

		1-Jul-08		10:07:10		70.41		40		1-Jul-08		10:06:20		71		47.5		1-Jul-08		10:07:53		69.8		41.5

		1-Jul-08		12:07:10		70.41		42		1-Jul-08		12:06:20		70.41		46		1-Jul-08		12:07:53		70.41		43.5

		1-Jul-08		14:07:10		71		44		1-Jul-08		14:06:20		70.41		48		1-Jul-08		14:07:53		69.8		45

		1-Jul-08		16:07:10		70.41		44.5		1-Jul-08		16:06:20		70.41		57.5		1-Jul-08		16:07:53		69.2		47

		1-Jul-08		18:07:10		71		43		1-Jul-08		18:06:20		70.41		53		1-Jul-08		18:07:53		69.2		45.5

		1-Jul-08		20:07:10		71		41		1-Jul-08		20:06:20		70.41		53.5		1-Jul-08		20:07:53		69.2		44

		1-Jul-08		22:07:10		71		40		1-Jul-08		22:06:20		69.8		52		1-Jul-08		22:07:53		69.8		42

		2-Jul-08		0:07:10		70.41		40		2-Jul-08		0:06:20		69.2		52		2-Jul-08		0:07:53		69.2		41.5

		2-Jul-08		2:07:10		69.8		40		2-Jul-08		2:06:20		69.2		52		2-Jul-08		2:07:53		69.2		42

		2-Jul-08		4:07:10		69.8		40		2-Jul-08		4:06:20		69.8		51.5		2-Jul-08		4:07:53		69.8		41.5

		2-Jul-08		6:07:10		69.8		40.5		2-Jul-08		6:06:20		69.2		53		2-Jul-08		6:07:53		69.2		42

		2-Jul-08		8:07:10		70.41		41		2-Jul-08		8:06:20		70.41		49		2-Jul-08		8:07:53		69.2		42.5

		2-Jul-08		10:07:10		70.41		40.5		2-Jul-08		10:06:20		69.8		46.5		2-Jul-08		10:07:53		69.8		42

		2-Jul-08		12:07:10		71		42.5		2-Jul-08		12:06:20		70.41		54		2-Jul-08		12:07:53		69.8		43.5

		2-Jul-08		14:07:10		70.41		44.5		2-Jul-08		14:06:20		70.41		50.5		2-Jul-08		14:07:53		69.2		46.5

		2-Jul-08		16:07:10		71		44.5		2-Jul-08		16:06:20		70.41		57.5		2-Jul-08		16:07:53		69.2		47

		2-Jul-08		18:07:10		71		43		2-Jul-08		18:06:20		69.8		49		2-Jul-08		18:07:53		69.8		45

		2-Jul-08		20:07:10		71		41		2-Jul-08		20:06:20		69.8		52		2-Jul-08		20:07:53		69.8		43

		2-Jul-08		22:07:10		70.41		40		2-Jul-08		22:06:20		69.8		49.5		2-Jul-08		22:07:53		69.8		41.5

		3-Jul-08		0:07:10		69.2		40		3-Jul-08		0:06:20		69.8		49		3-Jul-08		0:07:53		69.2		41.5

		3-Jul-08		2:07:10		70.41		40		3-Jul-08		2:06:20		69.2		48		3-Jul-08		2:07:53		69.8		41

		3-Jul-08		4:07:10		70.41		40		3-Jul-08		4:06:20		68.61		49		3-Jul-08		4:07:53		69.8		41

		3-Jul-08		6:07:10		69.8		40		3-Jul-08		6:06:20		68		49.5		3-Jul-08		6:07:53		69.8		41

		3-Jul-08		8:07:10		70.41		40.5		3-Jul-08		8:06:20		69.8		49		3-Jul-08		8:07:53		69.8		41.5

		3-Jul-08		10:07:10		70.41		41		3-Jul-08		10:06:20		70.41		45		3-Jul-08		10:07:53		69.8		41.5

		3-Jul-08		12:07:10		70.41		43		3-Jul-08		12:06:20		71		45.5		3-Jul-08		12:07:53		69.8		43.5

		3-Jul-08		14:07:10		70.41		44.5		3-Jul-08		14:06:20		71		47		3-Jul-08		14:07:53		69.2		46

		3-Jul-08		16:07:10		70.41		44		3-Jul-08		16:06:20		69.8		53		3-Jul-08		16:07:53		69.2		46

		3-Jul-08		18:07:10		70.41		43		3-Jul-08		18:06:20		70.41		49		3-Jul-08		18:07:53		69.8		44.5

		3-Jul-08		20:07:10		70.41		41.5		3-Jul-08		20:06:20		70.41		51.5		3-Jul-08		20:07:53		69.8		43.5

		3-Jul-08		22:07:10		71		40		3-Jul-08		22:06:20		69.2		51		3-Jul-08		22:07:53		69.8		42

		4-Jul-08		0:07:10		69.8		39.5		4-Jul-08		0:06:20		69.2		49.5		4-Jul-08		0:07:53		69.2		41.5

		4-Jul-08		2:07:10		69.2		40.5		4-Jul-08		2:06:20		69.2		47.5		4-Jul-08		2:07:53		69.2		41.5

		4-Jul-08		4:07:10		69.8		40		4-Jul-08		4:06:20		68.61		48		4-Jul-08		4:07:53		69.2		41.5

		4-Jul-08		6:07:10		69.8		39.5		4-Jul-08		6:06:20		69.8		44		4-Jul-08		6:07:53		69.2		41.5

		4-Jul-08		8:07:10		69.8		40		4-Jul-08		8:06:20		69.8		50.5		4-Jul-08		8:07:53		69.2		41.5

		4-Jul-08		10:07:10		71		42		4-Jul-08		10:06:20		69.8		50.5		4-Jul-08		10:07:53		69.2		43

		4-Jul-08		12:07:10		70.41		47		4-Jul-08		12:06:20		71.6		55		4-Jul-08		12:07:53		69.2		48

		4-Jul-08		14:07:10		71		47.5		4-Jul-08		14:06:20		71		55		4-Jul-08		14:07:53		69.2		50

		4-Jul-08		16:07:10		71		48		4-Jul-08		16:06:20		71.6		57		4-Jul-08		16:07:53		69.2		50

		4-Jul-08		18:07:10		71.6		46		4-Jul-08		18:06:20		71.6		54		4-Jul-08		18:07:53		69.2		49.5

		4-Jul-08		20:07:10		71.6		43.5		4-Jul-08		20:06:20		71.6		59		4-Jul-08		20:07:53		69.2		46.5

		4-Jul-08		22:07:10		71		41.5		4-Jul-08		22:06:20		69.8		56.5		4-Jul-08		22:07:53		69.2		45

		5-Jul-08		0:07:10		70.41		42		5-Jul-08		0:06:20		69.8		56.5		5-Jul-08		0:07:53		68.61		44.5

		5-Jul-08		2:07:10		69.8		41		5-Jul-08		2:06:20		69.8		54.5		5-Jul-08		2:07:53		69.2		43.5

		5-Jul-08		4:07:10		69.8		41		5-Jul-08		4:06:20		69.2		53		5-Jul-08		4:07:53		69.2		42.5

		5-Jul-08		6:07:10		69.2		41.5		5-Jul-08		6:06:20		68.61		54.5		5-Jul-08		6:07:53		68.61		43

		5-Jul-08		8:07:10		69.8		42		5-Jul-08		8:06:20		69.2		55		5-Jul-08		8:07:53		69.2		44

		5-Jul-08		10:07:10		71		43		5-Jul-08		10:06:20		69.8		51.5		5-Jul-08		10:07:53		69.2		45

		5-Jul-08		12:07:10		71		45		5-Jul-08		12:06:20		69.8		53.5		5-Jul-08		12:07:53		69.2		47.5

		5-Jul-08		14:07:10		71.6		45.5		5-Jul-08		14:06:20		70.41		55		5-Jul-08		14:07:53		69.2		48.5

		5-Jul-08		16:07:10		71.6		46		5-Jul-08		16:06:20		70.41		55.5		5-Jul-08		16:07:53		69.2		49.5

		5-Jul-08		18:07:10		71.6		45		5-Jul-08		18:06:20		70.41		59.5		5-Jul-08		18:07:53		68.61		48.5

		5-Jul-08		20:07:10		71		42.5		5-Jul-08		20:06:20		69.8		58		5-Jul-08		20:07:53		69.2		46

		5-Jul-08		22:07:10		71		41.5		5-Jul-08		22:06:20		69.2		57.5		5-Jul-08		22:07:53		69.2		45

		6-Jul-08		0:07:10		70.41		41		6-Jul-08		0:06:20		69.2		56		6-Jul-08		0:07:53		69.2		43.5

		6-Jul-08		2:07:10		69.8		40.5		6-Jul-08		2:06:20		68.61		54.5		6-Jul-08		2:07:53		68.61		43

		6-Jul-08		4:07:10		69.8		40.5		6-Jul-08		4:06:20		69.2		52.5		6-Jul-08		4:07:53		68.61		42.5

		6-Jul-08		6:07:10		69.2		41.5		6-Jul-08		6:06:20		69.2		51.5		6-Jul-08		6:07:53		68.61		42.5

		6-Jul-08		8:07:10		69.8		41.5		6-Jul-08		8:06:20		69.2		53		6-Jul-08		8:07:53		68.61		43.5

		6-Jul-08		10:07:10		71		43		6-Jul-08		10:06:20		69.8		55.5		6-Jul-08		10:07:53		69.2		45

		6-Jul-08		12:07:10		71		47		6-Jul-08		12:06:20		70.41		58.5		6-Jul-08		12:07:53		69.2		49

		6-Jul-08		14:07:10		71.6		49		6-Jul-08		14:06:20		70.41		57.5		6-Jul-08		14:07:53		69.2		52

		6-Jul-08		16:07:10		72.21		46		6-Jul-08		16:06:20		70.41		54		6-Jul-08		16:07:53		69.2		51

		6-Jul-08		18:07:10		72.21		47		6-Jul-08		18:06:20		69.8		61		6-Jul-08		18:07:53		69.2		51

		6-Jul-08		20:07:10		72.21		45		6-Jul-08		20:06:20		70.41		54.5		6-Jul-08		20:07:53		69.2		50

		6-Jul-08		22:07:10		72.21		43		6-Jul-08		22:06:20		69.8		62		6-Jul-08		22:07:53		68.61		48

		7-Jul-08		0:07:10		71.6		41.5		7-Jul-08		0:06:20		69.8		57		7-Jul-08		0:07:53		69.2		45

		7-Jul-08		2:07:10		71		41		7-Jul-08		2:06:20		69.8		52		7-Jul-08		2:07:53		69.2		44.5

		7-Jul-08		4:07:10		70.41		41		7-Jul-08		4:06:20		69.2		54		7-Jul-08		4:07:53		69.2		43.5

		7-Jul-08		6:07:10		69.8		40.5		7-Jul-08		6:06:20		69.2		52.5		7-Jul-08		6:07:53		68.61		43

		7-Jul-08		8:07:10		70.41		41.5		7-Jul-08		8:06:20		69.2		53.5		7-Jul-08		8:07:53		69.2		43.5

		7-Jul-08		10:07:10		71		44		7-Jul-08		10:06:20		69.2		58		7-Jul-08		10:07:53		69.2		46

		7-Jul-08		12:07:10		71.6		47.5		7-Jul-08		12:06:20		69.8		62		7-Jul-08		12:07:53		69.2		50

		7-Jul-08		14:07:10		71.6		50.5		7-Jul-08		14:06:20		70.41		59.5		7-Jul-08		14:07:53		69.2		54

		7-Jul-08		16:07:10		72.21		48.5		7-Jul-08		16:06:20		69.8		62		7-Jul-08		16:07:53		69.8		52.5

		7-Jul-08		18:07:10		72.21		46.5		7-Jul-08		18:06:20		70.41		59.5		7-Jul-08		18:07:53		69.2		52

		7-Jul-08		20:07:10		72.21		42.5		7-Jul-08		20:06:20		69.8		55		7-Jul-08		20:07:53		68.61		47.5

		7-Jul-08		22:07:10		72.21		40.5		7-Jul-08		22:06:20		69.8		50		7-Jul-08		22:07:53		69.2		44.5

		8-Jul-08		0:07:10		71		40		8-Jul-08		0:06:20		69.2		52		8-Jul-08		0:07:53		69.2		43.5

		8-Jul-08		2:07:10		70.41		40.5		8-Jul-08		2:06:20		69.2		51		8-Jul-08		2:07:53		69.2		42.5

		8-Jul-08		4:07:10		69.8		40.5		8-Jul-08		4:06:20		68.61		51.5		8-Jul-08		4:07:53		68.61		42.5

		8-Jul-08		6:07:10		69.2		40.5		8-Jul-08		6:06:20		69.2		51.5		8-Jul-08		6:07:53		68.61		42.5

		8-Jul-08		8:07:10		70.41		41.5		8-Jul-08		8:06:20		69.8		53.5		8-Jul-08		8:07:53		68.61		44

		8-Jul-08		10:07:10		71.6		44		8-Jul-08		10:06:20		69.8		50.5		8-Jul-08		10:07:53		68.61		47.5

		8-Jul-08		12:07:10		71		49		8-Jul-08		12:06:20		69.8		54		8-Jul-08		12:07:53		69.2		51

		8-Jul-08		14:07:10		71		49.5		8-Jul-08		14:06:20		70.41		55.5		8-Jul-08		14:07:53		69.2		53.5

		8-Jul-08		16:07:10		71		50		8-Jul-08		16:06:20		70.41		58.5		8-Jul-08		16:07:53		68.61		53.5

		8-Jul-08		18:07:10		71		49		8-Jul-08		18:06:20		70.41		55.5		8-Jul-08		18:07:53		68.61		52.5

		8-Jul-08		20:07:10		71		45		8-Jul-08		20:06:20		71		57.5		8-Jul-08		20:07:53		68		50

		8-Jul-08		22:07:10		71.6		43		8-Jul-08		22:06:20		70.41		53		8-Jul-08		22:07:53		68.61		47.5

		9-Jul-08		0:07:10		71.6		42		9-Jul-08		0:06:20		70.41		52		9-Jul-08		0:07:53		69.2		46

		9-Jul-08		2:07:10		71		41.5		9-Jul-08		2:06:20		69.8		50		9-Jul-08		2:07:53		69.2		44.5

		9-Jul-08		4:07:10		71		41.5		9-Jul-08		4:06:20		69.2		53.5		9-Jul-08		4:07:53		69.2		44

		9-Jul-08		6:07:10		70.41		41		9-Jul-08		6:06:20		69.2		52.5		9-Jul-08		6:07:53		69.2		43.5

		9-Jul-08		8:07:10		71		42.5		9-Jul-08		8:06:20		70.41		56.5		9-Jul-08		8:07:53		68.61		45

		9-Jul-08		10:07:10		71		45.5		9-Jul-08		10:06:20		71		53		9-Jul-08		10:07:53		69.2		48.5

		9-Jul-08		12:07:10		71		49		9-Jul-08		12:06:20		71.6		51		9-Jul-08		12:07:53		69.8		50.5

		9-Jul-08		14:07:10		70.41		47.5		9-Jul-08		14:06:20		71.6		51		9-Jul-08		14:07:53		68.61		51

		9-Jul-08		16:07:10		70.41		49		9-Jul-08		16:06:20		71.6		52.5		9-Jul-08		16:07:53		69.8		50

		9-Jul-08		18:07:10		70.41		48.5		9-Jul-08		18:06:20		70.41		53		9-Jul-08		18:07:53		69.8		50

		9-Jul-08		20:07:10		71		44		9-Jul-08		20:06:20		71		53		9-Jul-08		20:07:53		69.2		47.5

		9-Jul-08		22:07:10		71.6		43		9-Jul-08		22:06:20		70.41		54		9-Jul-08		22:07:53		69.8		46

		10-Jul-08		0:07:10		71.6		42		10-Jul-08		0:06:20		69.8		54.5		10-Jul-08		0:07:53		69.2		45

		10-Jul-08		2:07:10		71.6		41.5		10-Jul-08		2:06:20		69.8		54		10-Jul-08		2:07:53		69.8		44

		10-Jul-08		4:07:10		71		42		10-Jul-08		4:06:20		69.2		58		10-Jul-08		4:07:53		69.8		44

		10-Jul-08		6:07:10		71		41.5		10-Jul-08		6:06:20		69.8		55.5		10-Jul-08		6:07:53		69.8		43.5

		10-Jul-08		8:07:10		71		42.5		10-Jul-08		8:06:20		69.8		58.5		10-Jul-08		8:07:53		69.8		45

		10-Jul-08		10:07:10		71		44.5		10-Jul-08		10:06:20		69.8		58.5		10-Jul-08		10:07:53		68		48.5

		10-Jul-08		12:07:10		70.41		49		10-Jul-08		12:06:20		69.8		56.5		10-Jul-08		12:07:53		69.2		50.5

		10-Jul-08		14:07:10		70.41		52.5		10-Jul-08		14:06:20		71.6		54		10-Jul-08		14:07:53		69.2		54.5

		10-Jul-08		16:07:10		70.41		51		10-Jul-08		16:06:20		71.6		60		10-Jul-08		16:07:53		68.61		54

		10-Jul-08		18:07:10		70.41		49.5		10-Jul-08		18:06:20		70.41		63		10-Jul-08		18:07:53		69.8		51

		10-Jul-08		20:07:10		71		46		10-Jul-08		20:06:20		70.41		58.5		10-Jul-08		20:07:53		69.8		48.5

		10-Jul-08		22:07:10		71.6		43.5		10-Jul-08		22:06:20		70.41		57		10-Jul-08		22:07:53		69.8		47

		11-Jul-08		0:07:10		71.6		42.5		11-Jul-08		0:06:20		69.8		61		11-Jul-08		0:07:53		69.2		46.5

		11-Jul-08		2:07:10		71.6		42.5		11-Jul-08		2:06:20		69.8		53.5		11-Jul-08		2:07:53		69.8		45.5

		11-Jul-08		4:07:10		71		42		11-Jul-08		4:06:20		69.8		53.5		11-Jul-08		4:07:53		69.2		44.5

		11-Jul-08		6:07:10		71		41.5		11-Jul-08		6:06:20		69.8		57		11-Jul-08		6:07:53		69.2		44.5

		11-Jul-08		8:07:10		71		42.5		11-Jul-08		8:06:20		71.6		49		11-Jul-08		8:07:53		69.8		45

		11-Jul-08		10:07:10		71		45.5		11-Jul-08		10:06:20		72.21		56.5		11-Jul-08		10:07:53		68.61		48

		11-Jul-08		12:07:10		71		48.5		11-Jul-08		12:06:20		69.8		63		11-Jul-08		12:07:53		69.2		50.5

		11-Jul-08		14:07:10		71		49.5		11-Jul-08		14:06:20		70.41		55.5		11-Jul-08		14:07:53		69.2		52.5

		11-Jul-08		16:07:10		71		47		11-Jul-08		16:06:20		69.8		63.5		11-Jul-08		16:07:53		69.2		49.5

		11-Jul-08		18:07:10		71		45		11-Jul-08		18:06:20		70.41		54		11-Jul-08		18:07:53		69.2		47.5

		11-Jul-08		20:07:10		71		42.5		11-Jul-08		20:06:20		70.41		53		11-Jul-08		20:07:53		69.2		45.5

		11-Jul-08		22:07:10		71		40.5		11-Jul-08		22:06:20		70.41		52.5		11-Jul-08		22:07:53		69.8		43.5

		12-Jul-08		0:07:10		70.41		41		12-Jul-08		0:06:20		69.2		53		12-Jul-08		0:07:53		69.2		43

		12-Jul-08		2:07:10		70.41		41		12-Jul-08		2:06:20		69.2		52.5		12-Jul-08		2:07:53		69.8		42.5

		12-Jul-08		4:07:10		69.8		40.5		12-Jul-08		4:06:20		69.2		52.5		12-Jul-08		4:07:53		69.2		42.5

		12-Jul-08		6:07:10		69.8		40.5		12-Jul-08		6:06:20		69.2		52.5		12-Jul-08		6:07:53		69.2		42.5

		12-Jul-08		8:07:10		70.41		41.5		12-Jul-08		8:06:20		69.2		55		12-Jul-08		8:07:53		69.2		43

		12-Jul-08		10:07:10		71		42.5		12-Jul-08		10:06:20		69.2		57.5		12-Jul-08		10:07:53		69.2		44.5

		12-Jul-08		12:07:10		71		45.5		12-Jul-08		12:06:20		68.61		53.5		12-Jul-08		12:07:53		69.8		46.5

		12-Jul-08		14:07:10		70.41		45.5		12-Jul-08		14:06:20		69.2		52.5		12-Jul-08		14:07:53		69.8		47.5

		12-Jul-08		16:07:10		70.41		45.5		12-Jul-08		16:06:20		69.2		63.5		12-Jul-08		16:07:53		69.8		47.5

		12-Jul-08		18:07:10		70.41		44.5		12-Jul-08		18:06:20		69.8		54		12-Jul-08		18:07:53		70.41		46.5

		12-Jul-08		20:07:10		71		42.5		12-Jul-08		20:06:20		70.41		54		12-Jul-08		20:07:53		70.41		45

		12-Jul-08		22:07:10		71		42.5		12-Jul-08		22:06:20		69.8		59.5		12-Jul-08		22:07:53		70.41		44.5

		13-Jul-08		0:07:10		71		42.5		13-Jul-08		0:06:20		69.8		60		13-Jul-08		0:07:53		69.8		44

		13-Jul-08		2:07:10		71		42.5		13-Jul-08		2:06:20		69.2		60.5		13-Jul-08		2:07:53		70.41		44.5

		13-Jul-08		4:07:10		71		42.5		13-Jul-08		4:06:20		69.2		60		13-Jul-08		4:07:53		70.41		44.5

		13-Jul-08		6:07:10		71		42.5		13-Jul-08		6:06:20		69.2		61		13-Jul-08		6:07:53		70.41		44.5

		13-Jul-08		8:07:10		71		42.5		13-Jul-08		8:06:20		68.61		59		13-Jul-08		8:07:53		69.8		44

		13-Jul-08		10:07:10		71		43		13-Jul-08		10:06:20		69.2		59.5		13-Jul-08		10:07:53		70.41		44.5

		13-Jul-08		12:07:10		71		45		13-Jul-08		12:06:20		69.2		59		13-Jul-08		12:07:53		69.8		46

		13-Jul-08		14:07:10		71		45		13-Jul-08		14:06:20		70.41		54		13-Jul-08		14:07:53		69.8		47

		13-Jul-08		16:07:10		71.6		44.5		13-Jul-08		16:06:20		69.8		55.5		13-Jul-08		16:07:53		69.8		47

		13-Jul-08		18:07:10		71.6		44		13-Jul-08		18:06:20		69.2		58.5		13-Jul-08		18:07:53		69.2		47

		13-Jul-08		20:07:10		71.6		43		13-Jul-08		20:06:20		69.2		57.5		13-Jul-08		20:07:53		69.8		46.5

		13-Jul-08		22:07:10		71		42.5		13-Jul-08		22:06:20		69.2		60.5		13-Jul-08		22:07:53		70.41		45.5

		14-Jul-08		0:07:10		71		42.5		14-Jul-08		0:06:20		69.2		58		14-Jul-08		0:07:53		70.41		44.5

		14-Jul-08		2:07:10		70.41		42		14-Jul-08		2:06:20		69.2		52		14-Jul-08		2:07:53		70.41		43.5

		14-Jul-08		4:07:10		70.41		42		14-Jul-08		4:06:20		69.2		57.5		14-Jul-08		4:07:53		69.8		43

		14-Jul-08		6:07:10		69.8		41		14-Jul-08		6:06:20		69.2		55.5		14-Jul-08		6:07:53		69.8		42.5

		14-Jul-08		8:07:10		69.8		42		14-Jul-08		8:06:20		69.2		56.5		14-Jul-08		8:07:53		69.8		43

		14-Jul-08		10:07:10		70.41		44		14-Jul-08		10:06:20		69.2		53.5		14-Jul-08		10:07:53		70.41		44.5

		14-Jul-08		12:07:10		70.41		47		14-Jul-08		12:06:20		69.8		62		14-Jul-08		12:07:53		70.41		47

		14-Jul-08		14:07:10		71		47		14-Jul-08		14:06:20		69.8		59.5		14-Jul-08		14:07:53		70.41		48

		14-Jul-08		16:07:10		71		47		14-Jul-08		16:06:20		69.8		60.5		14-Jul-08		16:07:53		70.41		48.5

		14-Jul-08		18:07:10		71		45		14-Jul-08		18:06:20		70.41		57		14-Jul-08		18:07:53		70.41		47

		14-Jul-08		20:07:10		71		43.5		14-Jul-08		20:06:20		69.8		59.5		14-Jul-08		20:07:53		70.41		46

		14-Jul-08		22:07:10		71		42.5		14-Jul-08		22:06:20		69.2		59.5		14-Jul-08		22:07:53		70.41		44.5

		15-Jul-08		0:07:10		70.41		42		15-Jul-08		0:06:20		69.2		57		15-Jul-08		0:07:53		70.41		43.5

		15-Jul-08		2:07:10		70.41		42		15-Jul-08		2:06:20		68.61		56		15-Jul-08		2:07:53		70.41		43.5

		15-Jul-08		4:07:10		69.8		41.5		15-Jul-08		4:06:20		68.61		59		15-Jul-08		4:07:53		69.8		43

		15-Jul-08		6:07:10		69.8		42		15-Jul-08		6:06:20		69.2		56.5		15-Jul-08		6:07:53		69.8		43

		15-Jul-08		8:07:10		70.41		42		15-Jul-08		8:06:20		68		53.5		15-Jul-08		8:07:53		69.8		43.5

		15-Jul-08		10:07:10		71		42		15-Jul-08		10:06:20		69.2		54.5		15-Jul-08		10:07:53		69.8		44

		15-Jul-08		12:07:10		71		44.5		15-Jul-08		12:06:20		69.2		60		15-Jul-08		12:07:53		69.8		45

		15-Jul-08		14:07:10		71		46.5		15-Jul-08		14:06:20		69.2		62		15-Jul-08		14:07:53		69.2		48.5

		15-Jul-08		16:07:10		70.41		45.5		15-Jul-08		16:06:20		69.2		57.5		15-Jul-08		16:07:53		69.8		47.5

		15-Jul-08		18:07:10		70.41		44.5		15-Jul-08		18:06:20		69.8		54.5		15-Jul-08		18:07:53		69.8		46

		15-Jul-08		20:07:10		71		42.5		15-Jul-08		20:06:20		70.41		53.5		15-Jul-08		20:07:53		69.8		44.5

		15-Jul-08		22:07:10		71		41.5		15-Jul-08		22:06:20		69.2		54.5		15-Jul-08		22:07:53		69.8		43.5

		16-Jul-08		0:07:10		70.41		41.5		16-Jul-08		0:06:20		69.2		57		16-Jul-08		0:07:53		69.2		43

		16-Jul-08		2:07:10		69.8		41.5		16-Jul-08		2:06:20		69.8		55.5		16-Jul-08		2:07:53		69.2		43.5

		16-Jul-08		4:07:10		69.8		41.5		16-Jul-08		4:06:20		68.61		56.5		16-Jul-08		4:07:53		69.2		43

		16-Jul-08		6:07:10		69.8		41		16-Jul-08		6:06:20		69.2		56		16-Jul-08		6:07:53		69.2		43

		16-Jul-08		8:07:10		70.41		41.5		16-Jul-08		8:06:20		68.61		58.5		16-Jul-08		8:07:53		69.2		43

		16-Jul-08		10:07:10		70.41		42		16-Jul-08		10:06:20		69.8		55		16-Jul-08		10:07:53		68.61		44.5

		16-Jul-08		12:07:10		71		42.5		16-Jul-08		12:06:20		69.8		51		16-Jul-08		12:07:53		69.2		44.5

		16-Jul-08		14:07:10		71		44.5		16-Jul-08		14:06:20		69.8		51		16-Jul-08		14:07:53		68.61		47.5

		16-Jul-08		16:07:10		71		45		16-Jul-08		16:06:20		70.41		57		16-Jul-08		16:07:53		68.61		48





		



CER 1 Temperature(°F)

CER 2 Temperature(°F)

CER 3 Temperature(°F)

Date

Temperature (Deg. F)

Figure 9.  CER Temperature



		



CER 1 Humidity(%)

CER 3 Humidity(%)

QA Humidity(%)

CER 2 Humidity(%)

Date

Humidity (%)

Figure 10.  CER Relative Humidity



		






_1294659857.xls
Airstrip Count

		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148

		39206		39206		39206		39148		39148

		39230		39230		39230		39167		39167

		39267		39267		39267		39206		39206

		39297		39297		39297		39230		39230

		39349		39349		39349		39267		39267

		39392		39392		39392		39297		39297

		39427		39427		39427		39349		39349

		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713



CER 1

CER 2

CER3

Alert Level

Action Level

Date

Average CER Count

Figure 1.  Average Airstrip Count

3.625

6

29

10

15

5.375

7.5

28

10

15

13.125

13.25

28.75

10

15

13.25

11

27.75

10

15

4.25

5.25

24.5

10

15

4

1.75

11.75

10

15

4.25

9.25

10

15

19.5

5.5

22.5

10

15

5.75

4.25

13

10

15

3.25

1

4.75

10

15

11.625

8

18.25

10

15

3.875

1.75

10.5

10

15

4.125

2

10

35

45

1.125

0.5

3.5

35

45

3

1.25

6.5

35

45

3.25

0.75

5.25

35

45

2

0.75

2.75

35

45

6.375

1.75

8.25

35

45

13.5

1.25

10.25

35

45

2.6666666667

2.6666666667

11.25

35

45

6.2

4

3.75

35

45

6.2666666667

2

3.75

35

45

7.6666666667

3

7.5

35

45

9.4

2.8888888889

9

35

45

8.4

3.4444444444

6.5

35

45

6.5333333333

2.3333333333

8.5

35

45



Contact Plate Count

		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148

		39206		39206		39206		39148		39148

		39230		39230		39230		39167		39167

		39267		39267		39267		39206		39206

		39297		39297		39297		39230		39230

		39349		39349		39349		39267		39267

		39392		39392		39392		39297		39297

		39427		39427		39427		39392		39392

		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

Alert Level

Action Level

Date

Contact Plate Count

Figure 2. Average Contact Plate Count

1.4285714286

0.25

2.5

10

15

3.7142857143

2.75

4

10

15

1.1428571429

1.75

0.8333333333

10

15

2.4285714286

3

2.5

10

15

2.4285714286

0.75

3.1666666667

10

15

5.5714285714

3.25

5

10

15

5.2857142857

5.2

10

15

2.7142857143

1.5

2

10

15

1.1428571429

0

2

10

15

3.1428571429

1

3.25

10

15

3.4285714286

3.25

2.25

10

15

1.5714285714

0.75

1.5

10

15

1.7142857143

1

2.25

6

7

0.5714285714

0.5

2.25

6

7

1.5714285714

0.5

3

6

7

2

0.75

2.5

6

7

0.7142857143

0.25

1.75

6

7

3.4285714286

1.25

3.25

6

7

4

1

3.75

6

7

1.5333333333

1

3

6

7

2

1

2.25

6

7

1.7333333333

0.6666666667

1.5

6

7

0.9333333333

0.4444444444

1.5

6

7

0.9333333333

0.7777777778

2.5

6

7

1.1333333333

0.6666666667

1.75

6

7

0.9333333333

0.6666666667

1.5

6

7



0.5micron Count

		38776		38776		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126		39126		39126

		39148		39167		39167		39148		39148		39148		39148

		39148		39206		39206		39148		39148		39148		39148

		39167		39230		39230		39167		39167		39167		39167

		39206		39267		39267		39206		39206		39206		39206

		39230		39297		39297		39230		39230		39297		39297

		39267		39349		39349		39267		39267		39349		39349

		39297		39392		39392		39297		39297		39392		39392

		39392		39427		39427		39392		39392		39427		39427

		39545		39545		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

CER 1,3 Alert Level

CER 1,3 Action Level

CER 2 Alert Level

CER 2 Action Level

Date

0.5um/cu ft Count

Figure 3.  Average 0.5mm/cu ft Count

194

383

3263.8

5000

10000

5000

10000

339.5

338.3333333333

1210.4

5000

10000

5000

10000

362.75

719.3333333333

2800.4

5000

10000

5000

10000

688.125

416.3333333333

1999.6

5000

10000

5000

10000

618.75

336.6666666667

2033

5000

10000

5000

10000

692.625

1000

1857.4

5000

10000

5000

10000

401.375

1423.2

5000

10000

5000

10000

523.125

842

2313.2

5000

10000

5000

10000

273

292.3333333333

624.4

5000

10000

5000

10000

588.875

620

1580.4

5000

10000

5000

10000

714

474.6666666667

1255.6

5000

10000

5000

10000

755.625

587.3333333333

1139.8

5000

10000

5000

10000

772.875

643

1484

3800

4500

1250

1500

244

896.6666666667

1571.2

3800

4500

1250

1500

551.75

704.3333333333

2714

3800

4500

1250

1500

678.625

553

1781.8

3800

4500

1250

1500

369.625

300

731.6

3800

4500

1250

1500

664

478

1178.6

3800

4500

1250

1500

835.625

525

1260.6

3800

4500

1250

1500

699

83.7777777778

1354.8

3800

4500

1250

1500

635

204.4444444444

620.8

3800

4500

1250

1500

606

181.3333333333

750.8

3800

4500

1250

1500

606

109.5555555556

474.6

3800

4500

1250

1500

612.0666666667

156.7777777778

659.8

3800

4500

1250

1500

285.1333333333

190.5555555556

945.2

3800

4500

1250

1500

474

216.3333333333

768.6

3800

4500

1250

1500



5.0micron Count

		38776		38776		38776		38776		38776		38776		38776

		38806		38806		38806		38806		38806		38806		38806

		38835		38835		38835		38835		38835		38835		38835

		38867		38867		38867		38867		38867		38867		38867

		38905		38905		38905		38905		38905		38905		38905

		38965		38965		38965		38965		38965		38965		38965

		38995		38995		38995		38995		38995		38995		38995

		39035		39035		39035		39035		39035		39035		39035

		39071		39071		39071		39071		39071		39071		39071

		39098		39098		39098		39098		39098		39098		39098

		39126		39126		39126		39126		39126		39126		39126

		39167		39167		39167		39148		39148		39148		39148

		39206		39206		39206		39148		39148		39148		39148

		39230		39230		39230		39167		39167		39167		39167

		39267		39267		39267		39206		39206		39267		39267

		39297		39297		39297		39230		39230		39297		39297

		39349		39349		39349		39267		39267		39349		39349

		39392		39392		39392		39297		39297		39392		39392

		39427		39427		39427		39392		39392		39427		39427

		39545		39545		39545		39545		39545		39545		39545

		39575		39575		39575		39575		39575		39575		39575

		39602		39602		39602		39602		39602		39602		39602

		39630		39630		39630		39630		39630		39630		39630

		39650		39650		39650		39650		39650		39650		39650

		39695		39695		39695		39695		39695		39695		39695

		39713		39713		39713		39713		39713		39713		39713



CER 1

CER 2

CER 3

CER 1,3 Alert Level

CER 1,3 Action Level

CER 2 Alert Level

CER 2 Action Level

Date

5.0um/cu ft Count

Figure 4.  Average 5.0mm/cu ft Count

14.125

48.6666666667

226.8

30

50

30

50

33.625

49.3333333333

104.4

30

50

30

50

36.25

49

211.4

30

50

30

50

126.75

76.6666666667

305.2

30

50

30

50

67.875

37.3333333333

344.6

30

50

30

50

71.75

72.3333333333

166.4

30

50

30

50

43.5

235

30

50

30

50

65.125

37.3333333333

219.4

30

50

30

50

33.125

31.3333333333

50.6

30

50

30

50

47.75

50.6666666667

99.4

30

50

30

50

43.875

32.3333333333

79.2

30

50

30

50

47.125

44.3333333333

92.8

30

50

30

50

49

43.3333333333

92.2

410

500

90

105

30.75

75.6666666667

129.2

410

500

90

105

78.875

89

258.4

410

500

90

105

60

44

147

410

500

90

105

28.375

22.6666666667

53

410

500

90

105

26.125

20.3333333333

58

410

500

90

105

45.125

24.3333333333

80.8

410

500

90

105

37.3333333333

10

69.2

410

500

90

105

34.6

12.5555555556

33.2

410

500

90

105

29

9.3333333333

34

410

500

90

105

29

7.1111111111

33

410

500

90

105

30.0666666667

8.8888888889

27.6

410

500

78

83

18.7333333333

11.5555555556

43.4

410

500

78

83

24.3333333333

9.8888888889

37.6

410

500

78

83



CER 1

				AIRSTRIPS:																																																																																																		CONTACT PLATES:																																																																																																		PARTICLE COUNTS

				A						B						C						D						E						F						G						H						I						J						K						L						M						N						O						Average								A						B						C						D						E						F						G						H						I						J						K						L						M						N						O						Average								A				B				C				D				E				F				G				H				I				J				K				L				M				N				O				Average

		Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 1		Date		Alert Level		Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 1		Date		Alert Level		Action Level		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		0.5um/ cu ft		5.0um/cu ft		CER 1 0.5um/ cu ft		Date		CER 1,3 Alert Level		CER 1,3 Action Level		CER 1 5.0um/cu ft		Date		CER 1,3 Alert Level		CER 1,3 Action Level

		2/28/06		2		0		2		4		0		4		5		0		5		4		0		4		8		0		8		0		0		0		3		0		3		3		0		3																																												4		2/28/06		10		15		0		0		0		0		0		0		1		0		1		0		0		0		2		0		2		0		0		0		3		0		3		4		0		4						0						0						0						0						0						0						0		1		2/28/06		10		15		207		8		291		16		133		12		278		21		134		13		25		5		262		22		222		16																														194		02/28/06		5000		10000		14		2/28/06		30		50

		3/30/06		4		0		4		4		0		4		7		0		7		6		0		6		10		0		10		2		0		2		6		0		6		4		0		4																																												5		3/30/06		10		15		1		0		1		3		0		3		6		0		6		3		0		3		2		0		2		5		0		5		3		0		3		3		0		3						0						0						0						0						0						0						0		4		3/30/06		10		15		310		48		483		69		134		18		263		24		444		31		679		40		199		8		204		31																														340		03/30/06		5000		10000		34		3/30/06		30		50

		4/28/06		4		0		4		12		0		12		12		0		12		15		0		15		17		0		17		6		4		10		12		0		12		23		0		23																																												13		4/28/06		10		15		0		0		0		2		0		2		2		0		2		0		0		0		0		0		0		0		0		0		4		0		4		0		0		0						0						0						0						0						0						0						0		1		4/28/06		10		15		487		81		221		21		261		19		390		32		480		60		287		23		321		19		455		35																														363		04/28/06		5000		10000		36		4/28/06		30		50

		5/30/06		6		0		6		10		0		10		12		0		12		17		0		17		19		0		19		9		0		9		12		0		12		21		0		21																																												13		5/30/06		10		15		1		0		1		4		0		4		3		0		3		0		0		0		1		0		1		0		0		0		7		0		7		1		0		1						0						0						0						0						0						0						0		2		5/30/06		10		15		678		124		1084		137		214		36		113		21		1478		449		220		32		1009		120		709		95																														688		05/30/06		5000		10000		127		5/30/06		30		50

		7/7/06		4		0		4		2		0		2		6		0		6		4		0		4		8		0		8		1		0		1		4		0		4		5		0		5																																												4		7/7/06		10		15		1		0		1		2		0		2		1		0		1		2		0		2		2		0		2		1		0		1		4		0		4		4		0		4						0						0						0						0						0						0						0		2		7/7/06		10		15		631		86		779		72		1234		81		282		38		464		75		694		93		564		65		302		33																														619		07/07/06		5000		10000		68		7/7/06		30		50

		9/5/06		4		0		4		4		0		4		6		0		6		5		0		5		2		0		2		2		0		2		4		0		4		5		0		5																																												4		9/5/06		10		15		4		0		4		6		0		6		4		0		4		3		0		3		6		0		6		5		0		5		5		0		5		6		0		6						0						0						0						0						0						0						0		6		9/5/06		10		15		1056		113		622		73		227		35		828		84		603		57		875		95		545		56		785		61																														693		09/05/06		5000		10000		72		9/5/06		30		50

		10/5/06		5		0		5		4		0		4		4		0		4		5		0		5		6		0		6		4		0		4		3		0		3		3		0		3																																												4		10/5/06		10		15		5		0		5		6		0		6		4		0		4		4		0		4		5		0		5		3		0		3		6		0		6		4		0		4						0						0						0						0						0						0						0		5		10/5/06		10		15		122		14		263		18		352		48		540		69		361		38		421		63		389		41		763		57																														401		10/05/06		5000		10000		44		10/5/06		30		50

		11/14/06		11		0		11		27		0		27		10		0		10		24		0		24		26		0		26		32		0		32		12		0		12		14		0		14																																												20		11/14/06		10		15		1		0		1		1		0		1		0		0		0		0		0		0		5		0		5		1		0		1		2		0		2		9		0		9						0						0						0						0						0						0						0		3		11/14/06		10		15		596		71		455		67		641		77		585		62		991		81		357		52		62		60		498		51																														523		11/14/06		5000		10000		65		11/14/06		30		50

		12/20/06		2		0		2		1		0		1		5		0		5		1		0		1		13		0		13		7		0		7		13		0		13		4		0		4																																												6		12/20/06		10		15		1		0		1		2		0		2		0		0		0		1		0		1		3		0		3		1		0		1		0		0		0		0		0		0						0						0						0						0						0						0						0		1		12/20/06		10		15		367		35		390		46		168		18		321		30		343		32		191		14		90		25		314		65																														273		12/20/06		5000		10000		33		12/20/06		30		50

		1/16/07		3		0		3		2		0		2		4		0		4		6		0		6		2		0		2		2		0		2		3		0		3		4		0		4																																												3		1/16/07		10		15		2		0		2		2		0		2		1		0		1		3		0		3		4		0		4		2		0		2		4		0		4		4		0		4						0						0						0						0						0						0						0		3		1/16/07		10		15		361		21		449		56		304		35		265		31		761		42		804		62		901		64		866		71																														589		01/16/07		5000		10000		48		1/16/07		30		50

		2/13/07		11		0		11		5		0		5		10		0		10		6		0		6		24		0		24		6		0		6		10		0		10		21		0		21																																												12		2/13/07		10		15		1		0		1		8		0		8		3		0		3		2		0		2		0		0		0		4		0		4		2		0		2		4		0		4						0						0						0						0						0						0						0		3		2/13/07		10		15		611		41		862		50		841		42		942		61		744		40		622		33		402		24		688		60																														714		02/13/07		5000		10000		44		2/13/07		30		50

		3/26/07		3		0		3		4		0		4		4		0		4		6		0		6		2		0		2		4		0		4		6		0		6		2		0		2																																												4		3/7/07		10		15		1		0		1		1		0		1		2		0		2		0		0		0		1		0		1		2		0		2		2		0		2		2		0		2						0						0						0						0						0						0						0		2		3/7/07		10		15		721		51		640		42		871		48		901		52		844		48		408		36		799		49		861		51																														756		03/07/07		5000		10000		47		3/7/07		30		50

		5/4/07		4		0		4		4		0		4		3		0		3		4		0		4		6		0		6		2		0		2		6		0		6		4		0		4																																												4		3/7/07		35		45		2		0		2		1		0		1		2		0		2		1		0		1		0		0		0		1		0		1		2		0		2		3		0		3						0						0						0						0						0						0						0		2		3/7/07		6		7		641		41		722		52		699		47		944		61		872		45		698		41		662		37		945		68																														773		03/07/07		3800		4500		49		3/7/07		410		500

		5/28/07		1		0		1		1		0		1		2		0		2		0		0		0		2		0		2		1		0		1		1		0		1		1		0		1																																												1		3/26/07		35		45		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1						0						0						0						0						0						0						0		1		3/26/07		6		7		161		17		200		21		251		36		275		28		320		53		101		15		460		55		184		21																														244		03/26/07		3800		4500		31		3/26/07		410		500

		7/4/07		2		0		2		3		0		3		3		0		3		3		0		3		2		0		2		4		0		4		4		0		4		3		0		3																																												3		5/4/07		35		45		2		0		2		2		0		2		1		0		1		0		0		0		1		0		1		1		0		1		2		0		2		2		0		2						0						0						0						0						0						0						0		2		5/4/07		6		7		346		64		339		37		537		77		301		55		492		86		292		31		896		120		1211		161																														552		05/04/07		3800		4500		79		5/4/07		410		500

		8/3/07		4		0		4		2		0		2		3		0		3		2		0		2		2		0		2		4		0		4		4		0		4		5		0		5																																												3		5/28/07		35		45		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		3		0		3		3		0		3		2		0		2						0						0						0						0						0						0						0		2		5/28/07		6		7		221		20		107		19		647		49		587		37		744		87		907		78		1241		101		975		89																														679		05/28/07		3800		4500		60		5/28/07		410		500

		9/24/07		2		0		2		1		0		1		1		0		1		2		0		2		3		0		3		3		0		3		2		0		2		2		0		2																																												2		7/4/07		35		45		0		0		0		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		2		0		2		2		0		2						0						0						0						0						0						0						0		1		7/4/07		6		7		310		27		488		31		210		20		401		29		121		18		404		31		601		41		422		30																														370		07/04/07		3800		4500		28		7/4/07		410		500

		11/6/07		6		0		6		4		0		4		4		0		4		4		0		4		8		0		8		7		0		7		8		0		8		10		0		10																																												6		8/3/07		35		45		2		0		2		2		0		2		3		0		3		1		0		1		3		0		3		5		0		5		4		0		4		4		0		4						0						0						0						0						0						0						0		3		8/3/07		6		7		523		33		678		25		498		14		671		22		687		23		721		33		856		34		678		25																														664		08/03/07		3800		4500		26		8/3/07		410		500

		12/11/07		10		0		10		9		0		9		11		0		11		12		0		12		12		0		12		15		0		15		21		0		21		18		0		18																																												14		9/24/07		35		45		2		0		2		1		0		1		3		0		3		4		0		4		4		0		4		4		0		4		3		0		3		7		0		7						0						0						0						0						0						0						0		4		11/6/07		6		7		678		36		761		31		734		34		891		44		851		33		781		33		1011		81		978		69																														836		11/06/07		3800		4500		45		11/6/07		410		500

		4/7/08		6		0		6		5		0		5		7		0		7		6		0		6		0		0		0		0		0		0		2		0		2		4		0		4		4		0		4		3		0		3		2		0		2		0		0		0		0		0		0		0		0		0		1		0		1		3		4/7/08		35		45		2		0		2		1		0		1		3		0		3		3		0		3		2		0		2		1		0		1		1		0		1		0		0		0		2		0		2		0		0		0		2		0		2		1		0		1		1		0		1		2		0		2		2		0		2		2		4/7/08		6		7		989		45		1045		58		1349		61		1305		60		689		46		430		30		1027		60		899		42		621		24		318		19		501		24		313		33		295		13		303		21		401		24		699		04/07/08		3800		4500		37		4/7/08		410		500

		5/7/08		9		0		9		8		0		8		7		0		7		8		0		8		3		0		3		3		0		3		3		0		3		7		0		7		7		0		7		4		0		4		8		0		8		4		0		4		8		0		8		9		0		9		5		0		5		6		5/7/08		35		45		3		0		3		2		0		2		2		0		2		2		0		2		3		0		3		3		0		3		2		0		2		1		0		1		1		0		1		1		0		1		2		0		2		2		0		2		2		0		2		2		0		2		2		0		2		2		5/7/08		6		7		782		44		671		39		724		41		454		22		576		33		430		30		671		32		572		28		781		37		671		32		677		33		476		41		672		31		781		43		587		33		635		05/07/08		3800		4500		35		5/7/08		410		500

		6/3/08		8		0		8		8		0		8		4		0		4		5		0		5		6		0		6		6		0		6		5		0		5		5		0		5		5		0		5		4		0		4		7		0		7		8		0		8		8		0		8		9		0		9		6		0		6		6		6/3/08		35		45		3		0		3		1		0		1		1		0		1		2		0		2		1		0		1		3		0		3		1		0		1		2		0		2		2		0		2		0		0		0		2		0		2		1		0		1		2		0		2		2		0		2		3		0		3		2		6/3/08		6		7		621		33		393		22		891		31		671		25		1192		44		671		19		781		22		245		19		1325		44		601		41		418		31		351		29		301		21		290		23		339		31		606		06/03/08		3800		4500		29		6/3/08		410		500

		7/1/08		9		0		9		9		0		9		7		0		7		9		0		9		8		0		8		5		0		5		8		0		8		8		0		8		8		0		8		6		0		6		11		0		11		6		0		6		9		0		9		9		0		9		3		0		3		8		7/1/08		35		45		1		0		1		2		0		2		0		0		0		1		0		1		1		0		1		1		0		1		0		0		0		0		0		0		2		0		2		1		0		1		1		0		1		2		0		2		0		0		0		1		0		1		1		0		1		1		7/1/08		6		7		621		33		393		22		891		31		671		25		1192		44		671		19		781		22		245		19		1325		44		601		41		418		31		351		29		301		21		290		23		339		31		606		07/01/08		3800		4500		29		7/1/08		410		500

		7/21/08		11		0		11		11		0		11		5		0		5		5		0		5		12		0		12		11		0		11		12		0		12		6		0		6		6		0		6		9		0		9		14		0		14		15		0		15		11		0		11		6		0		6		7		0		7		9		7/21/08		35		45		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		7/21/08		6		7		232		23		452		26		337		27		671		33		476		27		501		28		488		28		782		37		561		27		442		28		891		38		590		29		876		31		991		42		891		27		612		07/21/08		3800		4500		30		7/21/08		410		500

		9/4/08		10		0		10		9		0		9		6		0		6		7		0		7		7		0		7		9		0		9		6		0		6		9		0		9		11		0		11		12		0		12		10		0		10		9		0		9		6		0		6		6		0		6		9		0		9		8		9/4/08		35		45		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		0		1		1		0		1		2		0		2		1		0		1		1		9/4/08		6		7		219		19		140		14		275		16		101		9		244		16		301		21		189		19		181		17		176		17		215		21		414		24		409		21		357		21		454		19		602		27		285		09/04/08		3800		4500		19		9/4/08		410		500

		9/22/08		5		0		5		5		0		5		9		0		9		5		0		5		5		0		5		9		0		9		11		0		11		4		0		4		11		0		11		5		0		5		5		0		5		6		0		6		6		0		6		8		0		8		4		0		4		7		9/22/08		35		45		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		0		0		0		2		0		2		1		0		1		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		9/22/08		6		7		332		21		254		19		354		21		548		31		369		22		584		26		651		22		448		26		296		19		489		29		336		21		754		32		565		26		665		29		465		21		474		09/22/08		3800		4500		24		9/22/08		410		500

		11/6/08		3		0		3		3		0		3		5		0		5		4		0		4		4		0		4		3		0		3		4		0		4		4		0		4		4		0		4		5		0		5		5		0		5		3		0		3		3		0		3		3		0		3		4		0		4		4		11/6/08		35		45		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		1		0		1		0		11/6/08		6		7		721		31		867		39		253		12		458		22		357		20		445		28		432		22		685		31		591		28		241		9		219		8		473		19		501		21		765		33		801		36		521		11/06/08		3800		4500		24		11/6/08		410		500

		12/1/08		2		0		2		0		0		0		0		0		0		2		0		2		2		0		2		3		0		3		0		0		0		1		0		1		4		0		4		3		0		3		2		0		2		1		0		1		0		0		0		2		0		2		3		0		3		2		12/1/08		35		45		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		1		12/1/08		6		7		110		9		89		9		122		13		25		6		59		8		131		18		40		7		274		19		157		12		88		6		150		9		114		8		517		32		180		15		234		21		153		12/01/08		3800		4500		13		12/1/08		410		500

		12/16/08		3		0		3		2		0		2		3		0		3		2		0		2		2		0		2		3		0		3		4		0		4		3		0		3		5		0		5		4		0		4		4		0		4		3		0		3		3		0		3		3		0		3		3		0		3		3		12/16/08		35		45		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		0		1		0		0		0		1		0		1		1		12/16/08		6		7		291		18		178		11		271		19		189		14		177		14		276		18		198		11		187		14		278		17		91		7		87		6		287		16		376		21		301		17		227		19		228		12/16/08		3800		4500		15		12/16/08		410		500



&L&"Arial Narrow,Bold"&14CER 1&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER 2

										AIRSTRIPS:																																																												CONTACT PLATES:																																																						PARTICLE COUNTS

				A						B						C						D						E						F						G						H						I						Average						A						B						C						D						E						F						G						H						I						Average						A				B				C				D				E				F				G				H				I				Average

		Sample Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 2		Alert Level		Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 2		Total Alert Level		Total Action Level		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		CER 2 0.5um/cu ft		Date		CER 2 Alert Level		CER 2 Action Level		CER 2 5.0um/cu ft		Date		CER 2 Alert Level		CER 2 Action Level

		2/28/06								6		0		6		0		0		0		9		0		9		9		0		9																										6		10		15								0		0		0		0		0		0		1		0		1		0		0		0																										0		10		15		297		39		288		43		0		0		564		64																						383		2/28/06		5000		10000		49		02/28/06		30		50

		3/30/06								9		0		9		1		0		1		8		0		8		12		0		12																										8		10		15								2		0		2		0		0		0		6		0		6		3		0		3																										3		10		15		460		68		264		39		0		0		291		41																						338		3/30/06		5000		10000		49		03/30/06		30		50

		4/28/06								29		0		29		0		0		0		22		0		22		2		0		2																										13		10		15								2		0		2		2		0		2		0		0		0		3		0		3																										2		10		15		1084		67		543		41		0		0		531		39																						719		4/28/06		5000		10000		49		04/28/06		30		50

		5/30/06								21		0		21		0		0		0		19		0		19		4		0		4																										11		10		15								4		0		4		2		0		2		1		0		1		5		0		5																										3		10		15		435		87		354		66		0		0		460		77																						416		5/30/06		5000		10000		77		05/30/06		30		50

		7/7/06								5		0		5		0		0		0		8		0		8		8		0		8																										5		10		15								0		0		0		0		0		0		2		0		2		1		0		1																										1		10		15		232		33		299		39		0		0		479		40																						337		7/7/06		5000		10000		37		07/07/06		30		50

		9/5/06								3		0		3		0		0		0		2		0		2		2		0		2																										2		10		15								4		0		4		0		0		0		4		0		4		5		0		5																										3		10		15		1289		79		289		30		0		0		1422		108																						1000		9/5/06		5000		10000		72		09/05/06		30		50

		10/5/06																																																																																																																																																																10/5/06		5000		10000				10/05/06		30		50

		11/14/06								16		0		16		0		0		0		4		0		4		2		0		2																										6		10		15								1		0		1		0		0		0		4		0		4		1		0		1																										2		10		15		961		41		877		40		0		0		688		31																						842		11/14/06		5000		10000		37		11/14/06		30		50

		12/20/06								5		0		5		4		0		4		6		0		6		2		0		2																										4		10		15								0		0		0		0		0		0		0		0		0		0		0		0																										0		10		15		463		36		141		17		0		0		273		41																						292		12/20/06		5000		10000		31		12/20/06		30		50

		1/16/07								2		0		2		0		0		0		1		0		1		1		0		1																										1		10		15								1		0		1		0		0		0		1		0		1		2		0		2																										1		10		15		781		62		451		32		0		0		628		58																						620		1/16/07		5000		10000		51		01/16/07		30		50

		2/13/07								12		0		12		0		0		0		10		0		10		10		0		10																										8		10		15								4		0		4		0		0		0		4		0		4		4		1		5																										3		10		15		640		31		285		44		0		0		499		22																						475		2/13/07		5000		10000		32		02/13/07		30		50

		3/26/07								2		0		2		0		0		0		2		0		2		3		0		3																										2		35		45								1		0		1		0		0		0		1		0		1		1		0		1																										1		6		7		490		40		684		51		0		0		588		42																						587		3/7/07		5000		10000		44		03/07/07		30		50

		5/4/07								2		0		2		0		0		0		3		0		3		3		0		3																										2		35		45								1		0		1		0		0		0		1		0		1		2		0		2																										1		6		7		640		41		585		37		0		0		704		52																						643		3/7/07		1250		1500		43		03/07/07		90		105

		5/28/07								0		0		0		0		0		0		1		0		1		1		0		1																										1		35		45								1		0		1		0		0		0		0		0		0		1		0		1																										1		6		7		1104		101		944		81		0		0		642		45																						897		3/26/07		1250		1500		76		03/26/07		90		105

		7/4/07								1		0		1		0		0		0		2		0		2		2		0		2																										1		35		45								0		0		0		0		0		0		1		0		1		1		0		1																										1		6		7		10		0		962		123		0		0		1141		132																						704		5/4/07		1250		1500		89		07/04/07		90		105

		8/3/07								0		0		0		0		0		0		1		0		1		2		0		2																										1		35		45								1		0		1		0		0		0		1		0		1		1		0		1																										1		6		7		0		0		784		61		0		0		875		71																						553		8/3/07		1250		1500		44		08/03/07		90		105

		9/24/07								1		0		1		0		0		0		1		0		1		1		0		1																										1		35		45								0		0		0		0		0		0		0		0		0		1		0		1																										0		6		7		0		0		199		19		0		0		701		49																						300		9/24/07		1250		1500		23		09/24/07		90		105

		11/6/07								1		0		1		0		0		0		3		0		3		3		0		3																										2		35		45								1		0		1		0		0		0		2		0		2		2		0		2																										1		6		7		4		0		563		22		0		0		867		39																						478		11/6/07		1250		1500		20		11/06/07		90		105

		12/11/07								0		0		0		0		0		0		2		0		2		3		0		3																										1		35		45								0		0		0		0		0		0		3		0		3		1		0		1																										1		6		7		2		0		672		36		0		0		901		37																						525		12/11/07		1250		1500		24		12/11/07		90		105

		4/7/08		0		0		0		4		0		4		7		0		7		0		0		0		4		0		4		0		0		0		6		0		6		3		0		3		0		0		0		3		35		45		0		0		0		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		2		0		2		2		0		2		0		0		0		1		6		7		0		0		162		23		208		25		0		0		93		19		0		0		90		6		201		17		0		0		84		4/7/08		1250		1500		10		04/07/08		90		105

		5/7/08		0		0		0		3		0		3		9		0		9		0		0		0		8		0		8		0		0		0		8		0		8		8		0		8		0		0		0		4		35		45		0		0		0		2		0		2		3		0		3		0		0		0		2		0		2		0		0		0		1		0		1		1		0		1		0		0		0		1		6		7		0		0		401		24		489		25		0		0		281		22		0		0		187		18		482		24		0		0		204		5/7/08		1250		1500		13		05/07/08		90		105

		6/3/08		0		0		0		3		0		3		3		0		3		0		0		0		5		0		5		0		0		0		5		0		5		2		0		2		0		0		0		2		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		0		1		0		0		0		1		6		7		0		0		267		10		498		22		0		0		268		22		0		0		301		19		298		11		0		0		181		6/3/08		1250		1500		9		06/03/08		90		105

		7/1/08		0		0		0		8		0		8		0		0		0		8		0		8		6		0		6		0		0		0		3		0		3		2		0		2		0		0		0		3		35		45		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		0		0		0		0		6		7		0		0		403		22		0		0		153		11		287		19		1		0		21		1		121		11		0		0		110		7/1/08		1250		1500		7		07/01/08		90		105

		7/21/08		0		0		0		6		0		6		0		0		0		7		0		7		7		0		7		0		0		0		4		0		4		2		0		2		0		0		0		3		35		45		0		0		0		2		0		2		0		0		0		2		0		2		2		0		2		0		0		0		1		0		1		0		0		0		0		0		0		1		6		7		0		0		376		19		0		0		298		17		337		21		0		0		109		8		291		15		0		0		157		7/21/08		1250		1500		9		07/21/08		78		83

		9/4/08		0		0		0		7		0		7		9		0		9		0		0		0		4		0		4		0		0		0		4		0		4		4		0		4		3		0		3		3		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		6		7		0		0		210		19		175		11		0		0		361		18		0		0		101		7		162		9		706		40		191		9/4/08		1250		1500		12		09/04/08		78		83

		9/22/08		0		0		0		5		0		5		4		0		4		0		0		0		4		0		4		0		0		0		2		0		2		4		0		4		2		0		2		2		35		45		0		0		0		2		0		2		0		0		0		0		0		0		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		1		6		7		0		0		332		21		296		15		0		0		194		9		0		0		265		11		295		11		565		22		216		9/22/08		1250		1500		10		09/22/08		78		83

		11/6/08		0		0		0		2		0		2		3		0		3		0		0		0		2		0		2		0		0		0		3		0		3		3		0		3		2		0		2		2		35		45		0		0		0		1		0		1		0		0		0		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		6		7		0		0		776		22		409		19		0		0		292		8		0		0		301		16		228		11		220		9		247		11/6/08		1250		1500		9		11/06/08		78		83

		12/1/08		0		0		0		3		0		3		2		0		2		0		0		0		3		0		3		0		0		0		2		0		2		0		0		0		1		0		1		1		35		45		0		0		0		1		0		1		2		0		2		0		0		0		1		0		1		0		0		0		1		0		1		0		0		0		2		0		2		1		6		7		0		0		290		12		203		11		0		0		221		12		0		0		313		21		19		3		148		10		133		12/1/08		1250		1500		8		12/01/08		78		83

		12/16/08		0		0		0		4		0		4		3		0		3		0		0		0		3		0		3		0		0		0		3		0		3		0		0		0		1		0		1		2		35		45		0		0		0		1		0		1		1		0		1		0		0		0		1		0		1		0		0		0		1		0		1		1		0		1		1		0		1		1		6		7		0		0		199		9		289		16		0		0		167		7		0		0		267		17		89		6		177		11		132		12/16/08		1250		1500		7		12/16/08		78		83



&L&"Arial Narrow,Bold"&14CER 2&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER 3

				AIRSTRIPS:																														CONTACT PLATES:																																				PARTICLE COUNTS

				A						B						D						E						Average						A						B						C						D						E						Average						A				B				C				D				E				Average

		Sample Date		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER3		Total Alert Level		Total Action Level		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		Bacterial		Fungal		Total		CER 3		Total Alert Level		Total Action Level		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		0.5um/cu ft		5.0um/cu ft		CER 3 0.5um/cu ft		0.5um/cu ft Alert Level		0.5um/cu ft Action Level		CER 3 5.0um/cu ft		5.0um/cu ft Alert Level		5.0um/cu ft Action Level

		2/28/06		29		1		30		21		0		21		28		0		28		37		0		37		29		10		15		3		0		3		3		0		3		3		0		3		2		0		2		4		0		4		3		10		15		4411		344		3943		271		3664		229		3068		212		1233		78		3264		5000		10000		227		30		50

		3/30/06		32		1		33		26		0		26		21		0		21		32		0		32		28		10		15		5		0		5		4		0		4		6		0		6		4		0		4		5		0		5		4		10		15		1261		119		979		81		1461		101		1721		120		630		101		1210		5000		10000		104		30		50

		4/28/06		29		2		31		32		0		32		23		0		23		29		0		29		29		10		15		2		0		2		3		0		3		0		0		0		0		0		0		0		0		0		1		10		15		4536		307		3293		245		2424		222		2637		211		1112		72		2800		5000		10000		211		30		50

		5/30/06		31		0		31		29		0		29		21		1		22		29		0		29		28		10		15		4		0		4		5		0		5		2		0		2		1		0		1		3		0		3		3		10		15		1914		327		2122		327		2561		413		1572		207		1829		252		2000		5000		10000		305		30		50

		7/7/06		26		0		26		19		0		19		22		0		22		31		0		31		25		10		15		4		0		4		5		0		5		3		0		3		2		0		2		5		0		5		3		10		15		2150		382		2668		423		2561		401		2022		399		764		118		2033		5000		10000		345		30		50

		9/5/06		10		0		10		12		0		12		11		0		11		14		0		14		12		10		15		6		0		6		4		0		4		4		0		4		6		0		6		5		0		5		5		10		15		2286		180		2142		171		1829		162		1749		171		1281		148		1857		5000		10000		166		30		50

		10/5/06		9		0		9		10		0		10		10		0		10		8		0		8		9		10		15		7		0		7		5		0		5		6		0		6		4		0		4		4		0		4		5		10		15		1679		346		793		137		1841		241		1429		248		1374		203		1423		5000		10000		235		30		50

		11/14/06		19		2		21		26		0		26		26		0		26		17		0		17		23		10		15		2		0		2		1		0		1		0		0		0		1		0		1		6		0		6		2		10		15		2241		243		2301		231		1974		198		2475		224		2575		201		2313		5000		10000		219		30		50

		12/20/06		10		0		10		13		0		13		13		0		13		16		0		16		13		10		15		5		0		5		1		0		1		0		0		0		3		0		3		1		0		1		2		10		15		406		33		727		46		923		94		604		41		462		39		624		5000		10000		51		30		50

		1/16/07		4		0		4		5		0		5		7		0		7		3		0		3		5		10		15		3		0		3		2		0		2		3		0		3		4		0		4		4		0		4		3		10		15		485		41		1785		101		1986		128		1785		109		1861		118		1580		5000		10000		99		30		50

		2/13/07		12		0		12		22		0		22		18		0		18		21		0		21		18		10		15		2		0		2		4		0		4		2		0		2		1		0		1		2		0		2		2		10		15		1261		87		1641		98		901		62		988		61		1487		88		1256		5000		10000		79		30		50

		3/26/07		11		0		11		12		0		12		10		0		10		9		0		9		11		35		45		2		0		2		1		0		1		2		0		2		1		0		1		2		0		2		2		6		7		1421		109		1221		101		866		71		949		82		1242		101		1140		3800		4500		93		410		500

		5/4/07		10		0		10		10		0		10		9		0		9		11		0		11		10		35		45		2		0		2		3		0		3		1		0		1		2		0		2		2		0		2		2		6		7		1741		110		1444		91		1235		81		1479		87		1521		92		1484		3800		4500		92		410		500

		5/28/07		6		0		6		4		0		4		2		0		2		2		0		2		4		35		45		4		0		4		2		0		2		1		0		1		1		0		1		2		0		2		2		6		7		1421		102		1387		100		1842		169		1785		154		1421		121		1571		3800		4500		129		410		500

		7/4/07		7		0		7		6		0		6		6		0		6		7		0		7		7		35		45		4		0		4		3		0		3		2		0		2		1		0		1		4		0		4		3		6		7		3950		375		2745		292		1658		177		2431		201		2786		247		2714		3800		4500		258		410		500

		8/3/07		6		0		6		6		0		6		4		0		4		5		0		5		5		35		45		3		0		3		3		0		3		2		0		2		2		0		2		2		0		2		3		6		7		1672		145		1897		152		1866		149		1987		151		1487		138		1782		3800		4500		147		410		500

		9/24/07		4		0		4		3		0		3		2		0		2		2		0		2		3		35		45		2		0		2		2		0		2		2		0		2		1		0		1		2		0		2		2		6		7		781		61		1011		72		689		49		768		52		409		31		732		3800		4500		53		410		500

		11/6/07		7		0		7		9		0		9		8		0		8		9		0		9		8		35		45		3		0		3		3		0		3		5		0		5		1		0		1		6		0		6		3		6		7		1276		78		1454		65		1109		55		987		45		1067		47		1179		3800		4500		58		410		500

		12/11/07		9		0		9		12		0		12		9		0		9		11		0		11		10		35		45		2		0		2		4		0		4		4		0		4		5		0		5		4		0		4		4		6		7		1853		101		1321		99		901		45		1241		87		987		72		1261		3800		4500		81		410		500

		4/7/08		8		0		8		15		0		15		12		0		12		10		0		10		11		35		45		2		0		2		3		0		3		2		0		2		3		0		3		4		0		4		3		6		7		1047		69		1642		79		1421		67		1677		71		987		60		1355		3800		4500		69		410		500

		5/7/08		3		0		3		4		0		4		4		0		4		4		0		4		4		35		45		4		0		4		3		0		3		4		0		4		1		0		1		1		0		1		2		6		7		561		31		761		44		660		39		451		21		671		31		621		3800		4500		33		410		500

		6/3/08		3		0		3		4		0		4		4		0		4		4		0		4		4		35		45		2		0		2		2		0		2		2		0		2		1		0		1		1		0		1		2		6		7		409		26		391		33		782		34		891		33		1281		44		751		3800		4500		34		410		500

		7/1/08		7		0		7		7		0		7		8		0		8		8		0		8		8		35		45		2		0		2		2		0		2		1		0		1		1		0		1		1		0		1		2		6		7		1121		81		677		42		339		22		125		11		111		9		475		3800		4500		33		410		500

		7/21/08		9		0		9		8		0		8		8		0		8		11		0		11		9		35		45		3		0		3		3		0		3		2		0		2		2		0		2		2		0		2		3		6		7		891		41		781		33		789		31		499		21		339		12		660		3800		4500		28		410		500

		9/4/08		6		0		6		9		0		9		4		0		4		7		0		7		7		35		45		2		0		2		2		0		2		1		0		1		2		0		2		1		0		1		2		6		7		793		37		1044		44		977		39		1011		57		901		40		945		3800		4500		43		410		500

		9/22/08		9		0		9		9		0		9		9		0		9		7		0		7		9		35		45		1		0		1		2		0		2		2		0		2		2		0		2		1		0		1		2		6		7		984		44		564		31		965		33		698		41		632		39		769		3800		4500		38		410		500

		11/6/08		6		0		6		6		0		6		4		0		4		3		0		3		5		35		45		1		0		1		1		0		1		1		0		1		1		0		1		1		0		1		1		6		7		1198		81		901		67		789		43		761		41		904		61		911		3800		4500		59		410		500

		12/1/08		7		0		7		7		0		7		6		0		6		7		0		7		7		35		45		2		0		2		1		0		1		2		0		2		1		0		1		1		0		1		1		6		7		1198		81		901		67		789		43		761		41		904		61		911		3800		4500		59		410		500

		12/16/08		8		0		8		8		0		8		6		0		6		9		0		9		8		35		45		1		0		1		2		0		2		1		0		1		1		0		1		1		0		1		1		6		7		892		41		1098		69		892		34		901		44		1167		72		990		3800		4500		52		410		500



&L&"Arial Narrow,Bold"&14CER 3&C&"Arial Narrow,Italic"&14Environmental Monitoring Log



CER Pressure

		Daily				Monthly				Daily				Monthly				Daily																		Monthly																		Daily								Monthly								Specs

		Date		CER1		Month		CER1		Date		CER Change Room		Month		CER Change Room		Date		CER2		Temp (F)		Relative Humidity (%)		R&D Bio-Safety Cabinet North (left axis)		R&D Bio-Safety Cabinet South (left axis)		Mfg Bio-Safety Cabinet North (left axis)		Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)		Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)		Month		CER 2		Temp (F)		Relative Humidity (%)		R&D Bio-Safety Cabinet North (left axis)		R&D Bio-Safety Cabinet South (left axis)		Mfg Bio-Safety Cabinet North (left axis)		Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)		Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)		Date		CER3		Temp (ºF)		Humidity (%RH)		Month		CER 3		Temp (ºF)		Humidity (%RH)		Date		CER Alert Level		CER Action Level		Bio-Safety Cabinet Alert Level (left axis)		Bio-Safety Cabinet Action  Level (left axis)		Mfg Bio-Safety Cabinet South Alert Level (right axis)		Mfg Bio-Safety Cabinet South Alarm Level (right axis)

		4/24/06		0.05		April-06		0.045		3/31/06		0.05		March-06		0.055		3/31/06		0.09																March-06		0.090																6/19/06		0.05						June-06		0.051						4/30/06		0.05		0.03

		4/24/06		0.05		May-06		0.022		3/31/06		0.06		April-06		0.053		3/31/06		0.09																April-06		0.089																6/19/06		0.06						July-06		0.061						5/31/06		0.05		0.03

		4/25/06		0.05		June-06		0.013		4/4/06		0.05		May-06		0.050		4/4/06		0.09																July-06		0.076																6/28/06		0.03						August-06		0.055						6/30/06		0.05		0.03

		4/25/06		0.04		July-06		0.041		4/4/06		0.05		June-06		0.046		4/4/06		0.09																August-06		0.068																6/28/06		0.06						September-06		0.052						7/31/06		0.05		0.03

		4/26/06		0.06		August-06		0.033		4/5/06		0.05		July-06		0.048		4/5/06		0.09																September-06		0.062																6/29/06		0.03						October-06		0.051						8/31/06		0.05		0.03

		4/26/06		0.04		September-06		0.027		4/5/06		0.06		August-06		0.050		4/5/06		0.09																October-06		0.034																6/29/06		0.06						November-06		0.053						9/30/06		0.05		0.03

		4/27/06		0.04		October-06		0.033		4/6/06		0.05		September-06		0.048		4/6/06		0.09																November-06		0.020																6/30/06		0.06						December-06		0.051						10/31/06		0.05		0.03

		4/27/06		0.045		November-06		0.028		4/6/06		0.06		October-06		0.053		4/6/06		0.09																December-06		0.012																6/30/06		0.06						February-07		0.040						11/30/06		0.05		0.03

		4/28/06		0.05		December-06		0.030		4/7/06		0.055		November-06		0.035		4/7/06		0.09																January-07		0.011																7/5/06		0.03						March-07		0.037						12/31/06		0.05		0.03

		4/28/06		0.04		January-07		0.030		4/7/06		0.05		December-06		0.031		4/7/06		0.09																February-07		0.013																7/5/06		0.03						April-07		0.038						1/31/07		0.05		0.03

		4/29/06		0.035		February-07		0.038		4/10/06		0.055		January-07		0.031		4/10/06		0.095																March-07		0.031																7/6/06		0.06						May-07		0.038						1/28/07		0.05		0.03

		4/29/06		0.035		March-07		0.037		4/10/06		0.055		February-07		0.035		4/10/06		0.09																April-07		0.033																7/6/06		0.06						June-07		0.040						3/7/07		0.05		0.03

		5/1/06		0.025		April-07		0.031		4/11/06		0.055		March-07		0.036		4/11/06		0.095																May-07		0.044																7/7/06		0.06						July-07		0.057						3/7/07		0.03		0.005

		5/1/06		0.03		May-07		0.027		4/11/06		0.055		April-07		0.035		4/11/06		0.095																June-07		0.048																7/7/06		0.06						August-07		0.053						4/30/07		0.03		0.005

		5/2/06		0.025		June-07		0.027		4/12/06		0.055		May-07		0.032		4/12/06		0.09																July-07		0.050																7/10/06		0.06						September-07		0.050						5/16/07		0.03		0.005

		5/2/06		0.03		July-07		0.035		4/12/06		0.055		June-07		0.028		4/12/06		0.09																August-07		0.042																7/10/06		0.06						October-07		0.049						5/16/07		0.015		0.005

		5/3/06		0.015		August-07		0.032		4/13/06		0.055		July-07		0.030		4/13/06		0.09																September-07		0.046						0.610		0.408								7/11/06		0.06						November-07		0.047						5/31/07		0.015		0.005

		5/4/06		0.03		September-07		0.030		4/13/06		0.055		August-07		0.032		4/13/06		0.095																October-07		0.041						0.620		0.420								7/11/06		0.06						December-07		0.043						6/30/07		0.015		0.005

		5/5/06		0.03		October-07		0.030		4/17/06		0.06		September-07		0.029		4/17/06		0.095																November-07		0.035						0.632		0.424								7/12/06		0.06						January-08		0.040						7/31/07		0.015		0.005

		5/5/06		0.03		November-07		0.065		4/17/06		0.055		October-07		0.027		4/17/06		0.09																December-07		0.030						0.643		0.426								7/12/06		0.06						February-08		0.040						8/31/07		0.015		0.005

		5/6/06		0.03		December-07		0.077		4/18/06		0.055		November-07		0.044		4/18/06		0.095																January-08																		7/13/06		0.06						March-08		0.040						9/5/07		0.015		0.005		0.25		0.1

		5/6/06		0.025		January-08		0.088		4/18/06		0.06		December-07		0.043		4/18/06		0.09																February-08		0.049		69.778		46.100		0.281		0.309		0.428		62.091		1180.364		7/13/06		0.06						April-08		0.048		70.864		42.636		9/30/07		0.015		0.005		0.25		0.1

		5/7/06		0.03		February-08		0.035		4/19/06		0.045		January-08		0.032		4/19/06		0.085																March-08		0.063		70.000		39.750		0.272		0.318		0.441		63.000		1193.000		7/14/06		0.06						May-08		0.040		72.696		37.435		10/31/07		0.015		0.005		0.25		0.1

		5/8/06		0.03		March-08		0.041		4/19/06		0.05		February-08		0.035		4/19/06		0.09																April-08		0.053		71.045		41.000		0.276		0.320		0.454		62.333		1196.333		7/14/06		0.06						June-08		0.025		72.136		33.909		11/30/07		0.015		0.005		0.25		0.1

		5/8/06		0.03		April-08		0.043		4/20/06		0.055		March-08		0.039		4/20/06		0.079																May-08		0.043		72.304		35.913		0.282		0.320		0.449		60.652		1194.957		7/17/06		0.06						July-08		0.059		71.920		39.400		12/31/07		0.015		0.005		0.25		0.1

		5/9/06		0.025		May-08		0.041		4/20/06		0.05		April-08		0.040		4/20/06		0.08																June-08		0.043		71.826		33.522		0.288		0.318		0.447		57.913		790.783		7/17/06		0.06						August-08		0.057		71.600		40.040		1/31/08		0.015		0.005		0.25		0.1

		5/9/06		0.025		June-08		0.039		4/24/06		0.06		May-08		0.040		4/21/06		0.085																July-08		0.077		71.800		38.360		0.285		0.320		0.447		59.789		882.526		7/18/06		0.06						September-08		0.059		71.240		38.000		2/29/08		0.015		0.005		0.25		0.1

		5/10/06		0.025		July-08		0.027		4/24/06		0.06		June-08		0.037		4/21/06		0.085																August-08		0.061		71.440		38.480		0.272		0.318		0.448		0.000		0.000		7/18/06		0.06														3/31/08		0.015		0.005		0.25		0.1

		5/10/06		0.025		August-08		0.031		4/25/06		0.06		July-08		0.040		4/25/06		0.086																September-08		0.059		70.640		38.280		0.259		0.319		0.439		0.000		0.000		7/19/06		0.06														4/1/31		0.015		0.005		0.25		0.1

		5/11/06		0.015		September-08		0.030		4/25/06		0.06		August-08		0.041		4/25/06		0.085																																		7/19/06		0.06														5/31/08		0.015		0.005		0.25		0.1

		5/11/06		0.025						4/26/06		0.05		September-08		0.041		4/26/06		0.085																																		7/20/06		0.07														6/30/08		0.015		0.005		0.25		0.1

		5/12/06		0.025						4/26/06		0.02						4/26/06		0.087																																		7/20/06		0.07														7/31/08		0.015		0.005		0.25		0.1

		5/12/06		0.02						4/27/06		0.06						4/27/06		0.085																																		7/21/06		0.07														8/30/08		0.015		0.005		0.25		0.1

		5/15/06		0.02						4/27/06		0.055						4/27/06		0.085																																		7/21/06		0.07														9/30/08		0.015		0.005		0.25		0.1

		5/15/06		0.025						4/28/06		0.04						4/28/06		0.09																																		7/22/06		0.07

		5/16/06		0.01						4/28/06		0.055						4/28/06		0.08																																		7/22/06		0.07

		5/16/06		0.01						4/29/06		0.05						7/25/06		0.085																																		7/24/06		0.07

		5/17/06		0.01						4/29/06		0.05						7/25/06		0.085																																		7/24/06		0.07

		5/17/06		0.025						5/1/06		0.05						7/26/06		0.085																																		7/25/06		0.06

		5/18/06		0.02						5/1/06		0.055						7/26/06		0.075																																		7/25/06		0.06

		5/18/06		0.02						5/2/06		0.05						7/27/06		0.08																																		7/26/06		0.06

		5/19/06		0.03						5/2/06		0.055						7/27/06		0.08																																		7/26/06		0.06

		5/19/06		0.02						5/3/06		0.05						7/28/06		0.075																																		7/27/06		0.06

		5/20/06		0.01						5/4/06		0.045						7/28/06		0.079																																		7/27/06		0.06

		5/20/06		0.02						5/5/06		0.055						7/29/06		0.069																																		8/1/06		0.06

		5/22/06		0.015						5/5/06		0.05						7/29/06		0.07																																		8/1/06		0.06

		5/22/06		0.015						5/6/06		0.065						7/30/06		0.069																																		8/2/06		0.06

		5/23/06		0.015						5/6/06		0.055						7/30/06		0.069																																		8/2/06		0.06

		5/23/06		0.015						5/7/06		0.05						7/31/06		0.075																																		8/3/06		0.06

		5/24/06		0.015						5/8/06		0.05						7/31/06		0.073																																		8/3/06		0.06

		5/24/06		0.015						5/8/06		0.05						8/1/06		0.07																																		8/4/06		0.06

		5/25/06		0.015						5/9/06		0.05						8/1/06		0.075																																		8/4/06		0.06

		5/25/06		0.03						5/9/06		0.055						8/2/06		0.07																																		8/7/06		0.055

		5/30/06		0.015						5/10/06		0.045						8/2/06		0.07																																		8/7/06		0.06

		5/30/06		0.02						5/10/06		0.04						8/3/06		0.07																																		8/8/06		0.06

		6/1/06		0.01						5/11/06		0.045						8/3/06		0.074																																		8/8/06		0.06

		6/1/06		0.01						5/11/06		0.055						8/4/06		0.074																																		8/9/06		0.06

		6/2/06		0.015						5/12/06		0.05						8/4/06		0.074																																		8/9/06		0.06

		6/5/06		0.01						5/12/06		0.06						8/7/06		0.073																																		8/10/06		0.055

		6/5/06		0.013						5/15/06		0.045						8/7/06		0.073																																		8/10/06		0.055

		6/6/06		0.01						5/15/06		0.055						8/8/06		0.073																																		8/11/06		0.055

		6/6/06		0.01						5/16/06		0.05						8/8/06		0.073																																		8/11/06		0.055

		6/7/06		0.01						5/16/06		0.055						8/10/06		0.074																																		8/14/06		0.055

		6/7/06		0.01						5/17/06		0.04						8/10/06		0.071																																		8/14/06		0.055

		6/8/06		0.01						5/17/06		0.045						8/14/06		0.07																																		8/15/06		0.055

		6/8/06		0.01						5/18/06		0.05						8/15/06		0.069																																		8/15/06		0.055

		6/9/06		0.01						5/18/06		0.055						8/16/06		0.069																																		8/16/06		0.055

		6/9/06		0.01						5/19/06		0.04						8/16/06		0.07																																		8/16/06		0.055

		6/12/06		0.03						5/19/06		0.045						8/17/06		0.069																																		8/17/06		0.055

		6/12/06		0.01						5/20/06		0.04						8/17/06		0.069																																		8/17/06		0.06

		6/13/06		0.03						5/20/06		0.043						8/18/06		0.07																																		8/18/06		0.05

		6/13/06		0.01						5/22/06		0.05						8/18/06		0.068																																		8/18/06		0.065

		6/16/06		0.01						5/22/06		0.05						8/21/06		0.065																																		8/19/06		0.05

		6/16/06		0.01						5/23/06		0.05						8/22/06		0.06																																		8/19/06		0.055

		7/6/06		0.05						5/23/06		0.05						8/22/06		0.065																																		8/21/06		0.055

		7/6/06		0.04						5/24/06		0.045						8/23/06		0.065																																		8/21/06		0.05

		7/7/06		0.04						5/24/06		0.05						8/23/06		0.068																																		8/22/06		0.05

		7/8/06		0.04						5/25/06		0.05						8/24/06		0.065																																		8/22/06		0.056

		7/10/06		0.05						5/25/06		0.05						8/24/06		0.055																																		8/23/06		0.055

		7/11/06		0.04						5/30/06		0.045						8/25/06		0.065																																		8/23/06		0.055

		7/12/06		0.05						5/30/06		0.05						8/25/06		0.065																																		8/24/06		0.05

		7/13/06		0.05						6/1/06		0.045						8/28/06		0.065																																		8/24/06		0.05

		7/17/06		0.06						6/1/06		0.05						8/28/06		0.065																																		8/25/06		0.05

		7/18/06		0.04						6/2/06		0.04						8/30/06		0.065																																		8/25/06		0.055

		7/19/06		0.04						6/5/06		0.05						8/30/06		0.063																																		8/26/06		0.05

		7/20/06		0.04						6/5/06		0.055						8/31/06		0.065																																		8/26/06		0.05

		7/21/06		0.033						6/6/06		0.055						8/31/06		0.065																																		8/28/06		0.05

		7/22/06		0.04						6/6/06		0.05						9/1/06		0.06																																		8/28/06		0.05

		7/23/06		0.04						6/7/06		0.055						9/1/06		0.065																																		8/29/06		0.05

		7/24/06		0.04						6/7/06		0.05						9/5/06		0.065																																		8/29/06		0.05

		7/25/06		0.04						6/8/06		0.05						9/5/06		0.065																																		8/30/06		0.05

		7/26/06		0.035						6/8/06		0.05						9/6/06		0.055																																		8/30/06		0.05

		7/26/06		0.04						6/9/06		0.045						9/6/06		0.065																																		8/31/06		0.05

		7/27/06		0.03						6/9/06		0.05						9/7/06		0.055																																		8/31/06		0.05

		7/27/06		0.04						6/12/06		0.01						9/7/06		0.063																																		9/1/06		0.055

		7/28/06		0.04						6/12/06		0.05						9/8/06		0.06																																		9/6/06		0.05

		7/31/06		0.03						6/13/06		0.01						9/8/06		0.063																																		9/6/06		0.05

		8/1/06		0.035						6/13/06		0.05						9/11/06		0.06																																		9/7/06		0.05

		8/2/06		0.03						6/14/06		0.05						9/11/06		0.065																																		9/7/06		0.05

		8/3/06		0.03						6/14/06		0.055						9/12/06		0.06																																		9/8/06		0.05

		8/4/06		0.03						6/15/06		0.055						9/12/06		0.065																																		9/8/06		0.05

		8/7/06		0.03						6/15/06		0.06						9/13/06		0.06																																		9/11/06		0.05

		8/8/06		0.03						6/16/06		0.05						9/13/06		0.065																																		9/11/06		0.05

		8/10/06		0.03						6/16/06		0.04						9/14/06		0.06																																		9/12/06		0.05

		8/10/06		0.05						6/17/06		0.045						9/14/06		0.065																																		9/12/06		0.06

		8/11/06		0.03						6/17/06		0.05						9/15/06		0.06																																		9/13/06		0.05

		8/11/06		0.05						6/19/06		0.05						9/15/06		0.065																																		9/13/06		0.055

		8/14/06		0.03						6/19/06		0.05						9/18/06		0.06																																		9/14/06		0.05

		8/15/06		0.03						6/20/06		0.05						9/18/06		0.063																																		9/14/06		0.04

		8/16/06		0.05						6/20/06		0.05						9/19/06		0.065																																		9/15/06		0.05

		8/16/06		0.03						6/21/06		0.04						9/19/06		0.055																																		9/15/06		0.05

		8/17/06		0.035						6/21/06		0.05						9/20/06		0.065																																		9/18/06		0.055

		8/17/06		0.03						6/22/06		0.04						9/20/06		0.06																																		9/18/06		0.06

		8/18/06		0.03						6/22/06		0.045						9/21/06		0.065																																		9/19/06		0.05

		8/18/06		0.03						6/26/06		0.04						9/21/06		0.062																																		9/19/06		0.055

		8/19/06		0.035						6/27/06		0.04						9/23/06		0.065																																		9/20/06		0.05

		8/19/06		0.03						6/28/06		0.04						9/23/06		0.062																																		9/20/06		0.05

		8/20/06		0.035						6/29/06		0.04						9/25/06		0.059																																		9/21/06		0.055

		8/21/06		0.03						7/5/06		0.04						9/25/06		0.06																																		9/21/06		0.055

		8/21/06		0.03						7/6/06		0.04						10/2/06		0.06																																		9/22/06		0.05

		8/22/06		0.025						7/7/06		0.05						10/2/06		0.05																																		9/22/06		0.055

		8/22/06		0.035						7/8/06		0.05						10/3/06		0.048																																		9/23/06		0.06

		8/23/06		0.035						7/10/06		0.03						10/3/06		0.042																																		9/23/06		0.06

		8/23/06		0.035						7/11/06		0.05						10/4/06		0.048																																		9/25/06		0.05

		8/24/06		0.035						7/12/06		0.04						10/6/06		0.038																																		9/25/06		0.055

		8/24/06		0.035						7/13/06		0.0425						10/9/06		0.055																																		9/26/06		0.05

		8/25/06		0.035						7/17/06		0.04						10/9/06		0.036																																		9/26/06		0.05

		8/25/06		0.035						7/18/06		0.05						10/10/06		0.037																																		9/27/06		0.05

		8/26/06		0.03						7/19/06		0.05						10/10/06		0.032																																		9/27/06		0.05

		8/26/06		0.035						7/20/06		0.05						10/11/06		0.032																																		9/28/06		0.05

		8/28/06		0.03						7/21/06		0.055						10/11/06		0.032																																		9/28/06		0.05

		8/28/06		0.03						7/22/06		0.055						10/12/06		0.033																																		9/29/06		0.05

		8/29/06		0.03						7/23/06		0.055						10/12/06		0.03																																		9/29/06		0.05

		8/29/06		0.03						7/24/06		0.055						10/13/06		0.031																																		10/2/06		0.055

		8/30/06		0.03						7/25/06		0.05						10/13/06		0.03																																		10/2/06		0.06

		8/30/06		0.035						7/26/06		0.055						10/16/06		0.033																																		10/3/06		0.05

		8/31/06		0.03						7/26/06		0.05						10/16/06		0.032																																		10/3/06		0.05

		8/31/06		0.03						7/27/06		0.05						10/17/06		0.032																																		10/4/06		0.055

		9/1/06		0.03						7/27/06		0.05						10/17/06		0.03																																		10/4/06		0.05

		9/5/06		0.03						7/28/06		0.05						10/18/06		0.033																																		10/5/06		0.05

		9/5/06		0.03						7/31/06		0.05						10/18/06		0.03																																		10/5/06		0.05

		9/6/06		0.02						8/1/06		0.05						10/19/06		0.025																																		10/9/06		0.05

		9/7/06		0.02						8/2/06		0.05						10/19/06		0.03																																		10/9/06		0.05

		9/8/06		0.03						8/3/06		0.05						10/20/06		0.03																																		10/10/06		0.05

		9/11/06		0.03						8/4/06		0.05						10/20/06		0.035																																		10/10/06		0.05

		9/11/06		0.03						8/7/06		0.05						10/23/06		0.032																																		10/11/06		0.05

		9/12/06		0.03						8/8/06		0.05						10/23/06		0.026																																		10/11/06		0.05

		9/12/06		0.03						8/11/06		0.03						10/24/06		0.029																																		10/12/06		0.05

		9/13/06		0.025						8/11/06		0.05						10/24/06		0.029																																		10/12/06		0.05

		9/13/06		0.03						8/14/06		0.05						10/26/06		0.03																																		10/13/06		0.05

		9/14/06		0.03						8/15/06		0.035						10/26/06		0.03																																		10/13/06		0.05

		9/15/06		0.03						8/16/06		0.05						10/30/06		0.025																																		10/14/06		0.05

		9/18/06		0.03						8/17/06		0.05						10/30/06		0.023																																		10/14/06		0.05

		9/19/06		0.03						8/17/06		0.05						10/31/06		0.025																																		10/16/06		0.05

		9/19/06		0.03						8/18/06		0.05						10/31/06		0.015																																		10/16/06		0.05

		9/20/06		0.03						8/18/06		0.05						11/1/06		0.026																																		10/17/06		0.05

		9/20/06		0.03						8/19/06		0.05						11/1/06		0.022																																		10/17/06		0.05

		9/21/06		0.02						8/19/06		0.05						11/2/06		0.025																																		10/18/06		0.05

		9/21/06		0.02						8/20/06		0.05						11/2/06		0.015																																		10/18/06		0.05

		9/22/06		0.02						8/21/06		0.05						11/3/06		0.025																																		10/19/06		0.05

		9/22/06		0.02						8/21/06		0.05						11/3/06		0.015																																		10/19/06		0.05

		9/23/06		0.02						8/22/06		0.045						11/6/06		0.025																																		10/20/06		0.05

		9/23/06		0.03						8/22/06		0.05						11/6/06		0.023																																		10/20/06		0.05

		9/25/06		0.02						8/23/06		0.05						11/7/06		0.02																																		10/23/06		0.05

		9/25/06		0.02						8/23/06		0.055						11/7/06		0.018																																		10/23/06		0.055

		9/26/06		0.02						8/24/06		0.05						11/8/06		0.04																																		10/24/06		0.05

		9/26/06		0.02						8/24/06		0.055						11/8/06		0.018																																		10/24/06		0.05

		9/27/06		0.02						8/25/06		0.05						11/9/06		0.02																																		10/25/06		0.05

		9/27/06		0.05						8/25/06		0.055						11/9/06		0.019																																		10/25/06		0.05

		9/28/06		0.03						8/26/06		0.05						11/10/06		0.02																																		10/26/06		0.05

		9/28/06		0.03						8/26/06		0.05						11/10/06		0.015																																		10/26/06		0.05

		9/29/06		0.02						8/28/06		0.05						11/13/06		0.02																																		10/27/06		0.05

		9/29/06		0.03						8/28/06		0.055						11/13/06		0.02																																		10/27/06		0.05

		10/2/06		0.04						8/29/06		0.05						11/14/06		0.02																																		10/28/06		0.05

		10/3/06		0.03						8/29/06		0.05						11/14/06		0.02																																		10/28/06		0.05

		10/3/06		0.03						8/30/06		0.05						11/15/06		0.02																																		10/30/06		0.05

		10/4/06		0.03						8/30/06		0.05						11/15/06		0.02																																		10/30/06		0.05

		10/4/06		0.03						8/31/06		0.05						11/16/06		0.02																																		10/31/06		0.05

		10/5/06		0.04						8/31/06		0.055						11/17/06		0.02																																		10/31/06		0.05

		10/5/06		0.03						9/1/06		0.05						11/17/06		0.018																																		11/1/06		0.05

		10/6/06		0.02						9/5/06		0.045						11/20/06		0.02																																		11/1/06		0.05

		10/7/06		0.05						9/5/06		0.05						11/20/06		0.015																																		11/2/06		0.05

		10/7/06		0.05						9/6/06		0.045						11/21/06		0.02																																		11/2/06		0.055

		10/9/06		0.04						9/7/06		0.05						11/21/06		0.012																																		11/3/06		0.045

		10/9/06		0.04						9/8/06		0.05						11/22/06		0.02																																		11/3/06		0.05

		10/10/06		0.02						9/11/06		0.05						11/22/06		0.02																																		11/6/06		0.05

		10/10/06		0.02						9/11/06		0.05						11/27/06		0.02																																		11/6/06		0.05

		10/11/06		0.03						9/12/06		0.05						11/27/06		0.04																																		11/7/06		0.05

		10/11/06		0.04						9/12/06		0.05						11/28/06		0.02																																		11/7/06		0.055

		10/12/06		0.035						9/13/06		0.05						11/28/06		0.01																																		11/8/06		0.05

		10/12/06		0.035						9/13/06		0.05						11/29/06		0.02																																		11/8/06		0.06

		10/13/06		0.04						9/14/06		0.05						11/29/06		0.015																																		11/9/06		0.05

		10/13/06		0.04						9/15/06		0.05						11/30/06		0.02																																		11/9/06		0.05

		10/14/06		0.04						9/18/06		0.05						11/30/06		0.015																																		11/10/06		0.05

		10/14/06		0.035						9/19/06		0.05						12/1/06		0.01																																		11/10/06		0.05

		10/16/06		0.04						9/19/06		0.05						12/1/06		0.012																																		11/13/06		0.05

		10/16/06		0.035						9/20/06		0.05						12/4/06		0.01																																		11/13/06		0.06

		10/17/06		0.03						9/20/06		0.05						12/4/06		0.015																																		11/14/06		0.06

		10/17/06		0.04						9/21/06		0.05						12/5/06		0.01																																		11/14/06		0.05

		10/18/06		0.03						9/21/06		0.05						12/5/06		0.015																																		11/15/06		0.055

		10/18/06		0.03						9/22/06		0.05						12/6/06		0.01																																		11/15/06		0.05

		10/19/06		0.025						9/22/06		0.05						12/6/06		0.01																																		11/16/06		0.055

		10/19/06		0.02						9/23/06		0.05						12/7/06		0.02																																		11/16/06		0.055

		10/20/06		0.035						9/23/06		0.05						12/7/06		0.01																																		11/17/06		0.05

		10/20/06		0.05						9/25/06		0.05						12/8/06		0.01																																		11/17/06		0.055

		10/21/06		0.04						9/25/06		0.05						12/8/06		0.01																																		11/18/06		0.05

		10/21/06		0.03						9/26/06		0.05						12/11/06		0.01																																		11/18/06		0.065

		10/23/06		0.035						9/26/06		0.05						12/11/06		0.015																																		11/20/06		0.05

		10/23/06		0.04						9/27/06		0.05						12/12/06		0.01																																		11/20/06		0.06

		10/24/06		0.02						9/27/06		0.02						12/12/06		0.015																																		11/21/06		0.05

		10/24/06		0.02						9/28/06		0.03						12/13/06		0.01																																		11/21/06		0.06

		10/25/06		0.035						9/28/06		0.03						12/13/06		0.015																																		11/22/06		0.05

		10/25/06		0.035						9/29/06		0.05						12/14/06		0.02																																		11/22/06		0.05

		10/26/06		0.025						9/29/06		0.05						12/18/06		0.01																																		11/27/06		0.05

		10/26/06		0.045						10/2/06		0.04						12/18/06		0.01																																		11/27/06		0.05

		10/27/06		0.03						10/3/06		0.05						12/19/06		0.01																																		11/28/06		0.055

		10/27/06		0.03						10/3/06		0.05						12/19/06		0.009																																		11/28/06		0.06

		10/28/06		0.03						10/4/06		0.05						12/20/06		0.01																																		11/29/06		0.05

		10/28/06		0.025						10/4/06		0.05						12/20/06		0.01																																		11/29/06		0.055

		10/30/06		0.035						10/5/06		0.04						12/21/06		0.01																																		11/30/06		0.05

		10/30/06		0.035						10/5/06		0.04						12/21/06		0.008																																		11/30/06		0.05

		10/31/06		0.03						10/6/06		0.03						12/22/06		0.01																																		12/1/06		0.05

		11/1/06		0.025						10/7/06		0.03						12/27/06		0.03																																		12/1/06		0.065

		11/2/06		0.035						10/7/06		0.03						12/28/06		0.01																																		12/2/06		0.05

		11/2/06		0.03						10/9/06		0.03						12/28/06		0.01																																		12/2/06		0.065

		11/3/06		0.02						10/9/06		0.03						12/29/06		0.01																																		12/4/06		0.045

		11/6/06		0.015						10/10/06		0.05						12/29/06		0.01																																		12/4/06		0.05

		11/7/06		0.02						10/10/06		0.05						1/2/07		0.01																																		12/5/06		0.045

		11/8/06		0.025						10/11/06		0.03						1/2/07		0.01																																		12/5/06		0.05

		11/9/06		0.03						10/11/06		0.04						1/3/07		0.01																																		12/6/06		0.05

		11/10/06		0.025						10/12/06		0.035						1/3/07		0.01																																		12/6/06		0.05

		11/11/06		0.035						10/12/06		0.035						1/4/07		0.01																																		12/7/06		0.05

		11/13/06		0.035						10/13/06		0.03						1/4/07		0.01																																		12/7/06		0.05

		11/13/06		0.02						10/13/06		0.04						1/5/07		0.01																																		12/8/06		0.05

		11/14/06		0.02						10/14/06		0.03						1/5/07		0.01																																		12/8/06		0.05

		11/14/06		0.02						10/14/06		0.035						1/8/07		0.01																																		12/9/06		0.05

		11/15/06		0.03						10/16/06		0.04						1/8/07		0.01																																		12/9/06		0.05

		11/15/06		0.035						10/16/06		0.04						1/9/07		0.01																																		12/11/06		0.05

		11/16/06		0.035						10/17/06		0.04						1/9/07		0.01																																		12/11/06		0.05

		11/17/06		0.03						10/17/06		0.04						1/10/07		0.01																																		12/12/06		0.05

		11/17/06		0.035						10/18/06		0.04						1/10/07		0.01																																		12/12/06		0.05

		11/18/06		0.03						10/18/06		0.04						1/11/07		0.02																																		12/13/06		0.055

		11/18/06		0.03						10/19/06		0.04						1/11/07		0.01																																		12/13/06		0.055

		11/20/06		0.045						10/19/06		0.04						1/12/07		0.01																																		12/14/06		0.04

		11/21/06		0.035						10/20/06		0.04						1/12/07		0.01																																		12/14/06		0.05

		11/22/06		0.025						10/20/06		0.04						1/15/07		0.02																																		12/15/06		0.05

		11/22/06		0.035						10/21/06		0.03						1/15/07		0.01																																		12/15/06		0.05

		11/27/06		0.03						10/21/06		0.04						1/16/07		0.01																																		2/28/07		0.04

		11/27/06		0.035						10/23/06		0.035						1/16/07		0.015																																		2/28/07		0.04

		11/28/06		0.015						10/23/06		0.04						1/17/07		0.01																																		3/1/07		0.04

		11/29/06		0.015						10/24/06		0.035						1/17/07		0.01																																		3/2/07		0.04

		11/30/06		0.025						10/24/06		0.035						1/18/07		0.01																																		3/3/07		0.04

		12/1/06		0.025						10/25/06		0.03						1/18/07		0.01																																		3/5/07		0.04

		12/2/06		0.025						10/25/06		0.045						1/19/07		0.01																																		3/6/07		0.04

		12/4/06		0.025						10/26/06		0.045						1/19/07		0.01																																		3/7/07		0.04

		12/5/06		0.03						10/26/06		0.04						1/22/07		0.01																																		3/8/07		0.04

		12/6/06		0.03						10/27/06		0.035						1/22/07		0.02																																		3/9/07		0.04

		12/6/06		0.03						10/27/06		0.03						1/23/07		0.01																																		3/12/07		0.045

		12/7/06		0.03						10/28/06		0.03						1/23/07		0.01																																		3/13/07		0.04

		12/7/06		0.035						10/28/06		0.05						1/24/07		0.01																																		3/14/07		0.04

		12/8/06		0.03						10/30/06		0.035						1/24/07		0.005																																		3/15/07		0.03

		12/8/06		0.03						10/30/06		0.035						1/25/07		0.01																																		3/16/07		0.04

		12/9/06		0.03						10/31/06		0.035						1/25/07		0.01																																		3/17/07		0.04

		12/11/06		0.03						11/1/06		0.035						1/26/07		0.01																																		3/19/07		0.03

		12/11/06		0.03						11/2/06		0.035						1/26/07		0.01																																		3/20/07		0.04

		12/12/06		0.03						11/2/06		0.04						1/29/07		0.01																																		3/21/07		0.04

		12/12/06		0.035						11/3/06		0.035						1/29/07		0.01																																		3/22/07		0.03

		12/13/06		0.03						11/6/06		0.05						1/30/07		0.01																																		3/23/07		0.03

		12/13/06		0.03						11/7/06		0.035						1/30/07		0.01																																		3/26/07		0.04

		12/14/06		0.03						11/8/06		0.04						1/31/07		0.01																																		3/27/07		0.03

		12/14/06		0.03						11/9/06		0.035						1/31/07		0.01																																		3/28/07		0.04

		12/15/06		0.03						11/10/06		0.045						2/1/07		0.01																																		3/29/07		0.03

		12/15/06		0.03						11/11/06		0.04						2/1/07		0.005																																		3/30/07		0.04

		12/18/06		0.03						11/13/06		0.04						2/2/07		0.01																																		3/31/07		0.03

		12/18/06		0.03						11/13/06		0.05						2/2/07		0.005																																		4/2/07		0.03

		12/19/06		0.03						11/14/06		0.04						2/5/07		0.01																																		4/3/07		0.045

		12/19/06		0.03						11/14/06		0.04						2/5/07		0.005																																		4/4/07		0.04

		12/20/06		0.03						11/15/06		0.03						2/6/07		0.01																																		4/5/07		0.04

		12/21/06		0.03						11/15/06		0.03						2/6/07		0.005																																		4/6/07		0.04

		12/21/06		0.03						11/16/06		0.03						2/7/07		0.01																																		4/9/07		0.04

		12/22/06		0.02						11/17/06		0.03						2/7/07		0.005																																		4/10/07		0.03

		12/22/06		0.035						11/17/06		0.035						2/8/07		0.01																																		4/11/07		0.04

		12/27/06		0.03						11/18/06		0.03						2/8/07		0.015																																		4/12/07		0.04

		12/27/06		0.03						11/18/06		0.03						2/9/07		0.01																																		4/13/07		0.035

		12/28/06		0.03						11/20/06		0.015						2/9/07		0.018																																		4/16/07		0.035

		12/28/06		0.03						11/21/06		0.03						2/12/07		0.01																																		4/17/07		0.04

		12/29/06		0.03						11/22/06		0.035						2/12/07		0.012																																		4/18/07		0.035

		12/29/06		0.035						11/22/06		0.035						2/13/07		0.01																																		4/19/07		0.04

		1/2/07		0.03						11/27/06		0.035						2/13/07		0.02																																		4/20/07		0.04

		1/2/07		0.03						11/27/06		0.03						2/14/07		0.02																																		4/23/07		0.03

		1/3/07		0.03						11/28/06		0.035						2/14/07		0.015																																		4/24/07		0.04

		1/3/07		0.03						11/29/06		0.035						2/15/07		0.02																																		4/25/07		0.035

		1/4/07		0.03						11/30/06		0.035						2/16/07		0.01																																		4/26/07		0.035

		1/5/07		0.03						12/1/06		0.03						2/20/07		0.015																																		4/27/07		0.035

		1/5/07		0.03						12/2/06		0.03						2/20/07		0.015																																		4/28/07		0.045

		1/8/07		0.03						12/4/06		0.03						2/21/07		0.02																																		4/30/07		0.04

		1/8/07		0.03						12/5/06		0.03						2/21/07		0.015																																		5/1/07		0.04

		1/9/07		0.03						12/6/06		0.03						2/22/07		0.02																																		5/2/07		0.04

		1/9/07		0.03						12/6/06		0.035						2/22/07		0.018																																		5/3/07		0.04

		1/10/07		0.03						12/7/06		0.03						2/23/07		0.02																																		5/4/07		0.04

		1/10/07		0.03						12/7/06		0.03						2/23/07		0.016																																		5/5/07		0.04

		1/11/07		0.03						12/8/06		0.03						2/26/07		0.015																																		5/7/07		0.035

		1/11/07		0.03						12/8/06		0.035						2/26/07		0.014																																		5/8/07		0.04

		1/12/07		0.03						12/9/06		0.03						2/27/07		0.015																																		5/9/07		0.045

		1/13/07		0.03						12/11/06		0.03						2/27/07		0.014																																		5/10/07		0.04

		1/13/07		0.03						12/11/06		0.03						2/28/07		0.01																																		5/11/07		0.035

		1/15/07		0.03						12/12/06		0.03						3/1/07		0.015																																		5/14/07		0.03

		1/15/07		0.03						12/12/06		0.03						3/2/07		0.015																																		5/15/07		0.035

		1/16/07		0.03						12/13/06		0.03						3/5/07		0.01																																		5/16/07		0.045

		1/16/07		0.025						12/13/06		0.03						3/6/07		0.01																																		5/17/07		0.035

		1/17/07		0.02						12/14/06		0.03						3/7/07		0.04																																		5/18/07		0.04

		1/18/07		0.02						12/14/06		0.035						3/8/07		0.04																																		5/19/07		0.04

		1/19/07		0.03						12/15/06		0.03						3/9/07		0.04																																		5/21/07		0.04

		1/19/07		0.03						12/15/06		0.035						3/12/07		0.04																																		5/22/07		0.04

		1/20/07		0.03						12/18/06		0.03						3/13/07		0.04																																		5/23/07		0.045

		1/22/07		0.03						12/18/06		0.03						3/14/07		0.04																																		5/24/07		0.04

		1/23/07		0.03						12/19/06		0.03						3/15/07		0.035																																		5/29/07		0.03

		1/24/07		0.03						12/19/06		0.03						3/16/07		0.04																																		5/30/07		0.03

		1/24/07		0.03						12/20/06		0.03						3/19/07		0.035																																		5/31/07		0.035

		1/25/07		0.03						12/21/06		0.03						3/20/07		0.035																																		6/1/07		0.035

		1/25/07		0.03						12/21/06		0.035						3/21/07		0.035																																		6/2/07		0.05

		1/26/07		0.03						12/22/06		0.03						3/22/07		0.032																																		6/4/07		0.035

		1/26/07		0.035						12/22/06		0.03						3/23/07		0.03																																		6/5/07		0.04

		1/29/07		0.03						12/27/06		0.03						3/26/07		0.03																																		6/6/07		0.04

		1/29/07		0.035						12/27/06		0.03						3/27/07		0.03																																		6/7/07		0.04

		1/30/07		0.035						12/28/06		0.03						3/28/07		0.035																																		6/8/07		0.045

		1/30/07		0.035						12/28/06		0.035						3/29/07		0.035																																		6/9/07		0.04

		1/31/07		0.03						12/29/06		0.03						3/30/07		0.03																																		6/11/07		0.04

		1/31/07		0.035						12/29/06		0.035						4/2/07		0.03																																		6/12/07		0.04

		2/1/07		0.03						1/2/07		0.03						4/3/07		0.025																																		6/13/07		0.04

		2/1/07		0.03						1/2/07		0.03						4/4/07		0.03																																		6/14/07		0.035

		2/2/07		0.03						1/3/07		0.03						4/5/07		0.025																																		6/15/07		0.045

		2/2/07		0.03						1/3/07		0.03						4/6/07		0.03																																		6/16/07		0.05

		2/3/07		0.03						1/4/07		0.03						4/9/07		0.025																																		6/19/07		0.04

		2/3/07		0.035						1/5/07		0.03						4/10/07		0.03																																		6/20/07		0.04

		2/5/07		0.03						1/5/07		0.03						4/11/07		0.03																																		6/21/07		0.035

		2/5/07		0.03						1/8/07		0.03						4/12/07		0.03																																		6/22/07		0.04

		2/6/07		0.03						1/8/07		0.03						4/13/07		0.028																																		6/23/07		0.04

		2/6/07		0.03						1/9/07		0.03						4/16/07		0.032																																		6/25/07		0.04

		2/7/07		0.05						1/9/07		0.03						4/17/07		0.03																																		6/26/07		0.04

		2/7/07		0.04						1/10/07		0.03						4/18/07		0.025																																		6/27/07		0.04

		2/8/07		0.04						1/10/07		0.035						4/19/07		0.025																																		6/28/07		0.04

		2/8/07		0.03						1/11/07		0.03						4/23/07		0.04																																		6/29/07		0.04

		2/10/07		0.03						1/11/07		0.03						4/24/07		0.044																																		7/2/07		0.04

		2/10/07		0.05						1/12/07		0.03						4/25/07		0.049																																		7/3/07		0.045

		2/12/07		0.03						1/13/07		0.03						4/26/07		0.049																																		7/5/07		0.05

		2/13/07		0.035						1/13/07		0.03						4/27/07		0.045																																		7/6/07		0.05

		2/13/07		0.04						1/15/07		0.03						4/30/07		0.045																																		7/9/07		0.045

		2/14/07		0.04						1/15/07		0.03						5/1/07		0.042																																		7/10/07		0.07

		2/14/07		0.04						1/16/07		0.03						5/2/07		0.045																																		7/11/07		0.045

		2/15/07		0.05						1/16/07		0.03						5/3/07		0.042																																		7/12/07		0.055

		2/15/07		0.04						1/17/07		0.03						5/4/07		0.045																																		7/13/07		0.05

		2/16/07		0.04						1/18/07		0.03						5/7/07		0.045																																		7/14/07		0.05

		2/16/07		0.04						1/19/07		0.035						5/8/07		0.045																																		7/16/07		0.055

		2/20/07		0.05						1/19/07		0.03						5/9/07		0.045																																		7/17/07		0.05

		2/20/07		0.05						1/20/07		0.03						5/10/07		0.045																																		7/18/07		0.075

		2/21/07		0.04						1/22/07		0.03						5/11/07		0.045																																		7/19/07		0.07

		2/21/07		0.055						1/23/07		0.03						5/14/07		0.046																																		7/20/07		0.07

		2/22/07		0.04						1/24/07		0.03						5/15/07		0.05																																		7/23/07		0.07

		2/22/07		0.05						1/24/07		0.03						5/16/07		0.055																																		7/24/07		0.07

		2/23/07		0.03						1/25/07		0.03						5/17/07		0.045																																		7/25/07		0.065

		2/23/07		0.05						1/25/07		0.03						5/18/07		0.04																																		7/26/07		0.055

		2/26/07		0.05						1/26/07		0.03						5/21/07		0.044																																		7/27/07		0.06

		2/26/07		0.04						1/26/07		0.035						5/22/07		0.045																																		7/28/07		0.065

		2/27/07		0.03						1/29/07		0.035						5/23/07		0.045																																		7/30/07		0.05

		2/27/07		0.04						1/29/07		0.035						5/24/07		0.04																																		7/31/07		0.06

		2/28/07		0.03						1/30/07		0.03						5/24/07		0.04																																		8/1/07		0.06

		2/28/07		0.03						1/30/07		0.03						5/29/07		0.025																																		8/2/07		0.06

		3/1/07		0.04						1/31/07		0.03						5/30/07		0.045																																		8/3/07		0.06

		3/2/07		0.04						1/31/07		0.035						5/31/07		0.05																																		8/6/07		0.06

		3/5/07		0.04						2/1/07		0.035						6/1/07		0.051																																		8/7/07		0.06

		3/6/07		0.04						2/1/07		0.03						6/4/07		0.044																																		8/8/07		0.05

		3/7/07		0.04						2/2/07		0.03						6/5/07		0.047																																		8/9/07		0.05

		3/8/07		0.04						2/2/07		0.03						6/6/07		0.046																																		8/10/07		0.05

		3/9/07		0.04						2/3/07		0.03						6/7/07		0.05																																		8/11/07		0.05

		3/12/07		0.04						2/3/07		0.03						6/8/07		0.048																																		8/13/07		0.06

		3/13/07		0.03						2/5/07		0.03						6/9/07		0.049																																		8/14/07		0.05

		3/14/07		0.03						2/5/07		0.03						6/11/07		0.049																																		8/15/07		0.05

		3/15/07		0.04						2/6/07		0.03						6/12/07		0.05																																		8/16/07		0.055

		3/16/07		0.04						2/6/07		0.035						6/13/07		0.045																																		8/17/07		0.055

		3/19/07		0.03						2/7/07		0.03						6/14/07		0.048																																		8/20/07		0.05

		3/20/07		0.04						2/7/07		0.03						6/15/07		0.045																																		8/21/07		0.05

		3/21/07		0.035						2/8/07		0.03						6/18/07		0.045																																		8/22/07		0.05

		3/22/07		0.04						2/8/07		0.03						6/19/07		0.045																																		8/23/07		0.05

		3/23/07		0.04						2/10/07		0.03						6/20/07		0.045																																		8/24/07		0.05

		3/26/07		0.035						2/10/07		0.04						6/21/07		0.045																																		8/27/07		0.05

		3/27/07		0.04						2/12/07		0.03						6/25/07		0.042																																		8/28/07		0.05

		3/28/07		0.035						2/13/07		0.035						6/26/07		0.045																																		8/29/07		0.05

		3/29/07		0.035						2/13/07		0.05						6/27/07		0.04																																		8/30/07		0.05

		3/30/07		0.03						2/14/07		0.04						6/28/07		0.063																																		8/31/07		0.05

		3/31/07		0.035						2/14/07		0.04						6/29/07		0.061																																		9/4/07		0.05

		4/2/07		0.04						2/15/07		0.05						7/2/07		0.06																																		9/5/07		0.05

		4/3/07		0.035						2/15/07		0.04						7/3/07		0.062																																		9/6/07		0.05

		4/4/07		0.035						2/16/07		0.04						7/5/07		0.06																																		9/7/07		0.055

		4/5/07		0.035						2/16/07		0.04						7/6/07		0.058																																		9/10/07		0.045

		4/6/07		0.035						2/20/07		0.05						7/9/07		0.06																																		9/11/07		0.05

		4/9/07		0.035						2/20/07		0.05						7/10/07		0.06																																		9/12/07		0.05

		4/10/07		0.03						2/21/07		0.04						7/11/07		0.055																																		9/13/07		0.045

		4/11/07		0.03						2/21/07		0.035						7/12/07		0.056																																		9/14/07		0.05

		4/12/07		0.03						2/22/07		0.04						7/13/07		0.056																																		9/17/07		0.05

		4/13/07		0.03						2/22/07		0.04						7/16/07		0.055																																		9/18/07		0.045

		4/14/07		0.03						2/23/07		0.03						7/17/07		0.05																																		9/19/07		0.05

		4/16/07		0.03						2/23/07		0.04						7/18/07		0.045																																		9/20/07		0.05

		4/17/07		0.03						2/26/07		0.03						7/19/07		0.045																																		9/21/07		0.05

		4/18/07		0.025						2/26/07		0.035						7/20/07		0.04																																		9/22/07		0.05

		4/19/07		0.03						2/27/07		0.03						7/23/07		0.04																																		9/24/07		0.05

		4/20/07		0.035						2/27/07		0.03						7/24/07		0.04																																		9/25/07		0.05

		4/21/07		0.035						2/28/07		0.03						7/25/07		0.04																																		9/26/07		0.05

		4/23/07		0.025						3/1/07		0.03						7/26/07		0.04																																		9/27/07		0.05

		4/24/07		0.02						3/2/07		0.03						7/28/07		0.04																																		9/28/07		0.05

		4/25/07		0.03						3/5/07		0.03						7/30/07		0.044																																		10/1/07		0.05

		4/26/07		0.04						3/6/07		0.03						7/31/07		0.044																																		10/2/07		0.06

		4/27/07		0.025						3/7/07		0.04						8/1/07		0.04																																		10/3/07		0.05

		4/30/07		0.025						3/8/07		0.04						8/2/07		0.04																																		10/4/07		0.05

		5/1/07		0.03						3/9/07		0.04						8/3/07		0.04																																		10/5/07		0.045

		5/2/07		0.02						3/12/07		0.04						8/4/07		0.042																																		10/8/07		0.05

		5/3/07		0.02						3/13/07		0.04						8/6/07		0.04																																		10/9/07		0.05

		5/4/07		0.02						3/14/07		0.03						8/7/07		0.04																																		10/10/07		0.05

		5/5/07		0.02						3/15/07		0.035						8/8/07		0.034																																		10/11/07		0.05

		5/7/07		0.02						3/16/07		0.035						8/9/07		0.032																																		10/12/07		0.05

		5/8/07		0.025						3/19/07		0.035						8/10/07		0.043																																		10/15/07		0.05

		5/9/07		0.03						3/20/07		0.04						8/13/07		0.045																																		10/16/07		0.045

		5/10/07		0.025						3/21/07		0.04						8/14/07		0.045																																		10/17/07		0.05

		5/11/07		0.005						3/22/07		0.04						8/15/07		0.043																																		10/18/07		0.05

		5/14/07		0.035						3/23/07		0.035						8/16/07		0.04																																		10/19/07		0.045

		5/15/07		0.035						3/26/07		0.035						8/17/07		0.04																																		10/22/07		0.05

		5/16/07		0.03						3/27/07		0.04						8/20/07		0.04																																		10/23/07		0.05

		5/17/07		0.03						3/28/07		0.04						8/21/07		0.03																																		10/24/07		0.045

		5/18/07		0.03						3/29/07		0.035						8/22/07		0.04																																		10/25/07		0.045

		5/19/07		0.03						3/30/07		0.03						8/23/07		0.04																																		10/26/07		0.05

		5/21/07		0.025						3/31/07		0.035						8/24/07		0.04																																		10/29/07		0.05

		5/22/07		0.025						4/2/07		0.035						8/27/07		0.045																																		10/30/07		0.045

		5/23/07		0.025						4/3/07		0.035						8/28/07		0.04																																		10/31/07		0.05

		5/24/07		0.02						4/4/07		0.04						8/29/07		0.055																																		11/1/07		0.045

		5/25/07		0.025						4/5/07		0.04						8/30/07		0.055																																		11/2/07		0.05

		5/29/07		0.025						4/6/07		0.04						8/31/07		0.05																																		11/5/07		0.05

		5/30/07		0.048						4/9/07		0.035						9/4/07		0.05																																		11/6/07		0.045

		5/31/07		0.04						4/10/07		0.035						9/5/07		0.04						0.61		0.4																										11/7/07		0.05

		6/1/07		0.025						4/11/07		0.04						9/6/07		0.05						0.61		0.41																										11/8/07		0.05

		6/2/07		0.03						4/12/07		0.035						9/7/07		0.045						0.6		0.41																										11/9/07		0.05

		6/4/07		0.03						4/13/07		0.035						9/8/07		0.04						0.6		0.41																										11/12/07		0.045

		6/5/07		0.0175						4/14/07		0.03						9/10/07		0.055						0.61		0.41																										11/13/07		0.05

		6/6/07		0.03						4/16/07		0.035						9/11/07		0.05						0.61		0.41																										11/14/07		0.045

		6/7/07		0.04						4/17/07		0.035						9/12/07		0.05						0.61		0.41																										11/15/07		0.045

		6/8/07		0.025						4/18/07		0.04						9/13/07		0.05						0.61		0.41																										11/16/07		0.045

		6/9/07		0.02						4/19/07		0.035						9/14/07		0.05						0.6		0.42																										11/19/07		0.045

		6/11/07		0.04						4/20/07		0.04						9/15/07		0.05						0.6		0.4																										11/20/07		0.045

		6/12/07		0.02						4/21/07		0.035						9/17/07		0.054						0.6		0.41																										11/21/07		0.045

		6/13/07		0.03						4/23/07		0.035						9/18/07		0.054						0.61		0.41																										11/26/07		0.045

		6/14/07		0.025						4/24/07		0.02						9/19/07		0.045						0.65		0.4																										11/27/07		0.045

		6/15/07		0.02						4/25/07		0.04						9/20/07		0.045						0.61		0.41																										11/28/07		0.045

		6/18/07		0.025						4/26/07		0.035						9/21/07		0.04						0.6		0.4																										11/29/07		0.045

		6/19/07		0.02						4/27/07		0.04						9/24/07		0.035						0.6		0.4																										11/30/07		0.045

		6/20/07		0.03						4/30/07		0.025						9/25/07		0.04						0.62		0.4																										12/1/07		0.045

		6/21/07		0.016						5/1/07		0.03						9/26/07		0.04						0.62		0.42																										12/3/07		0.045

		6/22/07		0.025						5/2/07		0.03						9/27/07		0.04						0.62		0.42																										12/4/07		0.045

		6/25/07		0.02						5/3/07		0.03						9/28/07		0.05						0.6		0.4																										12/5/07		0.045

		6/26/07		0.025						5/4/07		0.035						10/1/07		0.04						0.62		0.42																										12/6/07		0.045

		6/27/07		0.03						5/5/07		0.035						10/2/07		0.045						0.62		0.42																										12/7/07		0.045

		6/28/07		0.045						5/7/07		0.04						10/3/07		0.045						0.62		0.42																										12/8/07		0.045

		6/29/07		0.025						5/8/07		0.045						10/4/07		0.05						0.61		0.42																										12/10/07		0.045

		7/2/07		0.04						5/9/07		0.03						10/5/07		0.05						0.62		0.42																										12/11/07		0.04

		7/3/07		0.04						5/10/07		0.04						10/8/07		0.05						0.62		0.42																										12/12/07		0.04

		7/5/07		0.04						5/11/07		0.03						10/9/07		0.04						0.62		0.42																										12/13/07		0.04

		7/6/07		0.04						5/14/07		0.03						10/10/07		0.04						0.62		0.42																										12/14/07		0.04

		7/9/07		0.04						5/15/07		0.03						10/11/07		0.05						0.62		0.42																										12/17/07		0.04

		7/10/07		0.03						5/16/07		0.03						10/12/07		0.045						0.62		0.42																										12/18/07		0.045

		7/11/07		0.035						5/17/07		0.03						10/13/07		0.04						0.62		0.42																										12/19/07		0.04

		7/12/07		0.035						5/18/07		0.03						10/15/07		0.04						0.61		0.41																										12/20/07		0.04

		7/13/07		0.03						5/19/07		0.03						10/16/07		0.04						0.62		0.42																										12/26/07		0.04

		7/16/07		0.03						5/21/07		0.03						10/17/07		0.04						0.61		0.41																										12/27/07		0.04

		7/17/07		0.035						5/22/07		0.03						10/18/07		0.04						0.62		0.42																										12/28/07		0.04

		7/18/07		0.03						5/23/07		0.03						10/19/07		0.04						0.62		0.42																										12/31/07		0.05

		7/19/07		0.03						5/24/07		0.03						10/22/07		0.045						0.62		0.42																										1/2/08		0.04

		7/20/07		0.03						5/25/07		0.03						10/23/07		0.05						0.64		0.44																										1/3/08		0.04

		7/23/07		0.04						5/29/07		0.035						10/24/07		0.045						0.62		0.42																										1/4/08		0.04

		7/24/07		0.035						5/30/07		0.02						10/25/07		0.03						0.62		0.42																										1/7/08		0.04

		7/25/07		0.035						5/31/07		0.03						10/26/07		0.035						0.62		0.42																										1/8/08		0.04

		7/26/07		0.04						6/1/07		0.03						10/29/07		0.03						0.62		0.42																										1/9/08		0.04

		7/27/07		0.04						6/2/07		0.03						10/30/07		0.025						0.62		0.42																										1/10/08		0.04

		7/30/07		0.035						6/4/07		0.03						10/31/07		0.03						0.62		0.42																										1/11/08		0.04

		7/31/07		0.035						6/5/07		0.04						11/1/07		0.035						0.62		0.42																										1/14/08		0.04

		8/1/07		0.03						6/6/07		0.025						11/2/07		0.035						0.62		0.42																										1/15/08		0.04

		8/2/07		0.035						6/7/07		0.03						11/5/07		0.025						0.62		0.4																										1/16/08		0.04

		8/3/07		0.04						6/8/07		0.03						11/6/07		0.04						0.62		0.41																										1/17/08		0.04

		8/4/07		0.03						6/9/07		0.025						11/7/07		0.02						0.62		0.42																										1/18/08		0.04

		8/6/07		0.03						6/11/07		0.03						11/8/07		0.03						0.62		0.42																										1/21/08		0.04

		8/7/07		0.035						6/12/07		0.02						11/9/07		0.02						0.62		0.42																										1/22/08		0.04

		8/8/07		0.03						6/13/07		0.03						11/12/07		0.035						0.62		0.42																										1/23/08		0.04

		8/9/07		0.03						6/14/07		0.025						11/13/07		0.04						0.62		0.4																										1/24/08		0.04

		8/10/07		0.04						6/15/07		0.025						11/14/07		0.04						0.62		0.42																										1/25/08		0.045

		8/13/07		0.03						6/18/07		0.03						11/15/07		0.04						0.62		0.42																										1/28/08		0.04

		8/14/07		0.03						6/19/07		0.025						11/16/07		0.035						0.62		0.42																										1/29/08		0.04

		8/15/07		0.03						6/20/07		0.03						11/19/07		0.045						0.66		0.44																										1/30/08		0.04

		8/17/07		0.03						6/21/07		0.03						11/20/07		0.04						0.64		0.42																										1/31/08		0.04

		8/20/07		0.03						6/22/07		0.02						11/21/07		0.04						0.64		0.42																										2/1/08		0.04

		8/21/07		0.03						6/25/07		0.02						11/26/07		0.04						0.66		0.44																										2/4/08		0.04

		8/22/07		0.03						6/26/07		0.02						11/27/07		0.042						0.66		0.44																										2/5/08		0.04

		8/23/07		0.03						6/27/07		0.03						11/28/07		0.04						0.66		0.44																										2/6/08		0.04

		8/24/07		0.03						6/28/07		0.03						11/29/07		0.03						0.64		0.44																										2/7/08		0.04

		8/25/07		0.02						6/29/07		0.04						11/30/07		0.03						0.64		0.44																										2/8/08		0.04

		8/27/07		0.04						7/2/07		0.03						12/3/07		0.04						0.64		0.44																										2/11/08		0.04

		8/28/07		0.035						7/3/07		0.025						12/4/07		0.03						0.64		0.42																										2/12/08		0.04

		8/29/07		0.04						7/5/07		0.03						12/5/07		0.03						0.64		0.44																										2/13/08		0.04

		8/30/07		0.03						7/6/07		0.025						12/6/07		0.03						0.64		0.42																										2/14/08		0.04

		8/31/07		0.03						7/9/07		0.025						12/7/07		0.03						0.64		0.44																										2/15/08		0.04

		9/4/07		0.03						7/10/07		0.03						12/10/07		0.03						0.64		0.44																										2/16/08		0.04

		9/5/07		0.03						7/11/07		0.035						12/11/07		0.03						0.66		0.42																										2/19/08		0.04

		9/6/07		0.035						7/12/07		0.035						12/12/07		0.03						0.6		0.42																										2/20/08		0.045

		9/7/07		0.02						7/13/07		0.03						12/13/07		0.045						0.66		0.42																										2/21/08		0.04

		9/8/07		0.04						7/16/07		0.03						12/14/07		0.03						0.66		0.42																										2/22/08		0.04

		9/10/07		0.025						7/17/07		0.03						12/17/07		0.03						0.64		0.42																										2/25/08		0.04

		9/11/07		0.035						7/18/07		0.025						12/18/07		0.03						0.66		0.4																										2/26/08		0.04

		9/12/07		0.035						7/19/07		0.025						12/19/07		0.02						0.66		0.42																										2/27/08		0.04

		9/13/07		0.03						7/20/07		0.035						12/20/07		0.03						0.64		0.42																										2/28/08		0.04

		9/14/07		0.03						7/23/07		0.03						12/21/07		0.04						0.66		0.42																										2/29/08		0.04

		9/17/07		0.03						7/24/07		0.025						12/26/07		0.03						0.64		0.42																										3/1/08		0.04

		9/18/07		0.025						7/25/07		0.035						12/27/07		0.025						0.62		0.44																										3/2/08		0.04

		9/19/07		0.04						7/26/07		0.03						12/28/07		0.025						0.64		0.44																										3/3/08		0.04

		9/20/07		0.04						7/27/07		0.03						12/31/07		0.02						0.64		0.44																										3/4/08		0.04

		9/21/07		0.03						7/30/07		0.035																																										3/5/08		0.04

		9/24/07		0.025						7/31/07		0.04						2/14/08		0.04						0.292		0.309		0.485		61		1180																				3/6/08		0.04

		9/25/07		0.035						8/1/07		0.03						2/15/08		0.037		69		50		0.28		0.31		0.414		61		1172																				3/7/08		0.04

		9/26/07		0.025						8/2/07		0.035						2/19/08		0.035		69		48		0.293		0.309		0.426		60		1184																				3/8/08		0.04

		9/27/07		0.02						8/3/07		0.03						2/20/08		0.03		70		46		0.26		0.309		0.41		63		1184																				3/10/08		0.04

		9/28/07		0.02						8/4/07		0.03						2/21/08		0.032		70		46		0.29		0.305		0.441		62		1164																				3/11/08		0.04

		9/29/07		0.02						8/6/07		0.03						2/22/08		0.031		70		45		0.281		0.307		0.419		62		1184																				3/12/08		0.04

		10/1/07		0.015						8/7/07		0.025						2/25/08		0.069		70		46		0.288		0.311		0.421		63		1184																				3/13/08		0.04

		10/2/07		0.035						8/8/07		0.03						2/26/08		0.068		70		44		0.281		0.312		0.413		64		1192																				3/14/08		0.04

		10/3/07		0.03						8/9/07		0.045						2/27/08		0.067		70		45		0.288		0.311		0.413		62		1184																				3/15/08		0.04

		10/4/07		0.04						8/10/07		0.04						2/28/08		0.063		70		46		0.283		0.31		0.457		62		1172																				3/17/08		0.04

		10/5/07		0.025						8/13/07		0.04						2/29/08		0.064		70		45		0.256		0.311		0.409		63		1184																				3/18/08		0.04

		10/8/07		0.03						8/14/07		0.04						3/3/08		0.07		70		33		0.285		0.311		0.435		63		1204																				3/19/08		0.04

		10/9/07		0.03						8/15/07		0.04						3/4/08		0.07		70		44		0.261		0.311		0.438		63		1184																				3/20/08		0.04

		10/10/07		0.03						8/17/07		0.04						3/5/08		0.069		70		44		0.291		0.311		0.445		63		1184																				3/21/08		0.04

		10/11/07		0.03						8/20/07		0.03						3/6/08		0.068		70		44		0.281		0.311		0.458		61		1184																				3/22/08		0.04

		10/12/07		0.02						8/21/07		0.03						3/7/08		0.067		70		44		0.282		0.322		0.455		63		1192																				3/24/08		0.04

		10/15/07		0.03						8/22/07		0.035						3/10/08		0.069		70		46		0.264		0.321		0.428		64		1184																				3/25/08		0.04

		10/16/07		0.02						8/23/07		0.03						3/11/08		0.071		70		43		0.285		0.322		0.438		63		1204																				3/26/08		0.045

		10/17/07		0.04						8/24/07		0.035						3/12/08		0.056		70		44		0.261		0.312		0.422		62		1188																				3/27/08		0.04		70		25

		10/18/07		0.04						8/25/07		0.02						3/14/08		0.067		70		43		0.261		0.321		0.451		63		1184																				3/28/08		0.04		70		41

		10/19/07		0.025						8/27/07		0.025						3/17/08		0.069		70		45		0.26		0.32		0.439		63		1196																				3/31/08		0.04		70		28

		10/22/07		0.03						8/28/07		0.025						3/18/08		0.062		70		47		0.279		0.32		0.422		63		1196																				4/1/08		0.04		70		29

		10/23/07		0.03						8/29/07		0.03						3/19/08		0.053		70		44		0.273		0.321		0.419		64		1192																				4/2/08		0.055		70		36

		10/24/07		0.04						8/30/07		0.03						3/20/08		0.064		70		33		0.262		0.321		0.431		64		1192																				4/3/08		0.04		69		40

		10/25/07		0.035						8/31/07		0.03						3/21/08		0.063		70		35		0.277		0.322		0.439		63		1196																				4/4/08		0.045		70		44

		10/26/07		0.045						9/4/07		0.03						3/24/08		0.052		70		42		0.238		0.321		0.418		63		1184																				4/5/08		0.04		70		41

		10/29/07		0.02						9/5/07		0.03						3/25/08		0.057		70		38		0.264		0.319		0.445		63		1192																				4/7/08		0.05		70		44

		10/30/07		0.02						9/6/07		0.03						3/26/08		0.056		70		35		0.276		0.321		0.447		63		1204																				4/8/08		0.05		70		44

		10/31/07		0.02						9/7/07		0.03						3/27/08		0.07		70		24		0.28		0.32		0.46		63		1204																				4/9/08		0.05		70		44

		11/1/07		0.03						9/8/07		0.03						3/28/08		0.05		70		40		0.26		0.32		0.44		63		1192																				4/10/08		0.05		70		44

		11/2/07		0.025						9/10/07		0.02						3/31/08		0.06		70		27		0.3		0.32		0.48		63		1204																				4/11/08		0.05		70		46

		11/5/07		0.03						9/11/07		0.02						4/1/08		0.06		70		28		0.28		0.32		0.46		61		1192																				4/14/08		0.05		72		41

		11/6/07		0.025						9/12/07		0.03						4/2/08		0.06		70		30		0.28		0.32		0.44		63		1204																				4/15/08		0.05		74		42

		11/7/07		0.025						9/13/07		0.02						4/3/08		0.06		70		38		0.28		0.32		0.44		64		1192																				4/16/08		0.05		70		45

		11/8/07		0.085						9/14/07		0.035						4/4/08		0.05		70		44		0.26		0.32		0.44		63		1196																				4/17/08		0.045		72		46

		11/9/07		0.08						9/17/07		0.03						4/5/08		0.05		70		40		0.26		0.32		0.44		63		1196																				4/18/08		0.04		70		48

		11/12/07		0.075						9/18/07		0.03						4/7/08		0.055		70		44		0.26		0.32		0.46		65		1204																				4/19/08		0.05		69		48

		11/13/07		0.08						9/19/07		0.04						4/8/08		0.055		70		44		0.28		0.32		0.44		61		1192																				4/21/08		0.05		73		47

		11/14/07		0.075						9/20/07		0.04						4/9/08		0.055		70		46		0.28		0.32		0.44		63		1196																				4/22/08		0.045		77		46

		11/15/07		0.075						9/21/07		0.03						4/10/08		0.05		70		45		0.28		0.32		0.44		61		1204																				4/23/08		0.05		71		45

		11/16/07		0.07						9/24/07		0.025						4/11/08		0.05		70		42		0.28		0.32		0.44		61		1192																				4/24/08		0.045		73		46

		11/19/07		0.075						9/25/07		0.025						4/14/08		0.05		70		43		0.28		0.32		0.46		61		1196																				4/25/08		0.04		70		46

		11/20/07		0.07						9/26/07		0.03						4/15/08		0.05		73		41		0.28		0.32		0.44		62		1196																				4/30/08		0.06		69		26

		11/21/07		0.075						9/27/07		0.03						4/16/08		0.05		72		43		0.28		0.32		0.48		62		1196																				5/1/08		0.04		75		42

		11/26/07		0.08						9/28/07		0.03						4/17/08		0.05		72		44		0.28		0.32		0.48		62		1196																				5/2/08		0.04		72		35

		11/27/07		0.08						9/29/07		0.025						4/18/08		0.05		72		45		0.28		0.32		0.48		62		1196																				5/3/08		0.04		78		34

		11/28/07		0.08						10/1/07		0.03						4/19/08		0.06		72		44		0.28		0.32		0.48		62		1196																				5/5/08		0.04		71		40

		11/29/07		0.075						10/2/07		0.025						4/21/08		0.055		71		45		0.28		0.32		0.46		64		1196																				5/6/08		0.045		75		40

		11/30/07		0.08						10/3/07		0.03						4/22/08		0.05		72		43		0.28		0.32		0.46		64		1196																				5/7/08		0.05		72		36

		12/3/07		0.07						10/4/07		0.03						4/23/08		0.05		73		42		0.28		0.32		0.48		63		1196																				5/8/08		0.045		72		38

		12/4/07		0.08						10/5/07		0.02						4/24/08		0.055		73		45		0.28		0.32		0.46		63		1196																				5/9/08		0.04		74		34

		12/5/07		0.07						10/8/07		0.03						4/25/08		0.05		73		41		0.26		0.32		0.44		63		1204																				5/10/08		0.045		72		34

		12/6/07		0.08						10/9/07		0.02						4/28/08								0.26		0.32		0.44		63		1204																				5/12/08		0.055		69		28

		12/7/07		0.075						10/10/07		0.025						4/29/08								0.28		0.32		0.44		60		1184																				5/13/08		0.04		75		31

		12/10/07		0.075						10/11/07		0.03						4/30/08		0.06		70		25		0.28		0.32		0.46		60		1192																				5/14/08		0.05		71		38

		12/11/07		0.075						10/12/07		0.02						5/1/08		0.055		73		39		0.28		0.32		0.46		60		1196																				5/15/08		0.04		72		42

		12/12/07		0.075						10/15/07		0.025						5/2/08		0.045		72		34		0.28		0.32		0.46		60		1210																				5/16/08		0.04		71		48

		12/13/07		0.075						10/16/07		0.025						5/3/08		0.05		73		38		0.28		0.32		0.46		60		1210																				5/19/08		0.04		75		42

		12/14/07		0.075						10/17/07		0.03						5/5/08		0.04		72		38		0.28		0.32		0.44		60		1192																				5/20/08		0.04		73		44

		12/17/07		0.08						10/18/07		0.025						5/6/08		0.04		73		42		0.28		0.32		0.44		60		1184																				5/21/08		0.04		71		36

		12/18/07		0.075						10/19/07		0.025						5/7/08		0.04		73		37		0.28		0.32		0.44		62		1196																				5/22/08		0.04		73		30

		12/19/07		0.08						10/22/07		0.025						5/8/08		0.04		73		35		0.28		0.32		0.44		60		1196																				5/23/08		0.04		71		36

		12/20/07		0.08						10/23/07		0.02						5/9/08		0.04		72		34		0.3		0.32		0.46		62		1204																				5/27/08		0.02		73		37

		12/21/07		0.08						10/24/07		0.035						5/10/08		0.04		72		32		0.3		0.32		0.46		62		1204																				5/28/08		0.03		71		39

		12/26/07		0.08						10/25/07		0.025						5/12/08		0.055		68		28		0.26		0.32		0.42		60		1196																				5/29/08		0.03		74		39

		12/27/07		0.08						10/26/07		0.035						5/13/08		0.04		73		31		0.26		0.32		0.46		61		1192																				5/30/08		0.04		72		38

		12/28/07		0.075						10/29/07		0.025						5/14/08		0.045		73		25		0.3		0.32		0.46		60		1184																				5/31/08		0.025		72		39

		12/31/07		0.08						10/30/07		0.03						5/15/08		0.035		73		39		0.3		0.32		0.46		60		1196																				6/2/08		0.025		74		27

		1/2/08		0.09						10/31/07		0.03						5/16/08		0.035		73		45		0.3		0.32		0.44		60		1184																				6/3/08		0.02		71		34

		1/3/08		0.075						11/1/07		0.04						5/19/08		0.045		72		41		0.28		0.32		0.44		60		1204																				6/4/08		0.025		69		33

		1/4/08		0.09						11/2/07		0.03						5/20/08		0.045		73		42		0.28		0.32		0.44		62		1196																				6/5/08		0.025		71		39

		1/7/08		0.125						11/5/07		0.025						5/21/08		0.045		70		35		0.28		0.32		0.46		60		1196																				6/6/08		0.025		71		32

		1/8/08		0.08						11/6/07		0.03						5/22/08		0.045		72		30		0.28		0.32		0.42		61		1176																				6/9/08		0.03		72		43

		1/9/08		0.08						11/7/07		0.035						5/23/08		0.045		73		34		0.28		0.32		0.46		61		1172																				6/10/08		0.03		73		33

		1/10/08		0.08						11/8/07		0.05						5/27/08		0.035		73		36		0.28		0.32		0.44		61		1196																				6/11/08		0.025		70		33

		1/11/08		0.08						11/9/07		0.05						5/28/08		0.04		72		37		0.28		0.32		0.44		61		1204																				6/12/08		0.025		71		35

		1/14/08		0.09						11/12/07		0.03						5/29/08		0.04		73		37		0.26		0.32		0.44		61		1200																				6/13/08		0.025		75		32

		1/15/08		0.085						11/13/07		0.05						5/30/08		0.04		72		37		0.28		0.32		0.48		61		1196																				6/16/08		0.025		72		37

		1/16/08		0.09						11/14/07		0.05						6/2/08		0.04		71		30		0.28		0.28		0.44		60		1200																				6/17/08		0.03		72		26

		1/17/08		0.08						11/15/07		0.05						6/3/08		0.035		72		35		0.28		0.32		0.42		61		1196																				6/18/08		0.025		73		33

		1/18/08		0.09						11/16/07		0.05						6/4/08		0.035		70		33		0.28		0.32		0.44		61		1188																				6/19/08		0.025		71		29

		1/21/08		0.04						11/19/07		0.05						6/5/08		0.035		71		37		0.3		0.32		0.44		61		1192																				6/20/08		0.02		73		33

		1/22/08		0.11						11/20/07		0.05						6/6/08		0.035		71		31		0.28		0.32		0.44		61		1188																				6/21/08		0.025		74		27

		1/23/08		0.09						11/21/07		0.05						6/9/08		0.04		72		40		0.32		0.32		0.48		61		1188																				6/23/08		0.02		72		37

		1/24/08		0.09						11/26/07		0.05						6/10/08		0.04		72		31		0.3		0.32		0.44		55		1172																				6/24/08		0.025		73		35

		1/25/08		0.095						11/27/07		0.05						6/11/08		0.04		70		34		0.3		0.32		0.48		55		1196																				6/25/08		0.03		72		36

		1/28/08		0.09						11/28/07		0.05						6/12/08		0.04		72		31		0.3		0.32		0.48		55		1196																				6/26/08		0.03		74		35

		1/29/08		0.09						11/29/07		0.045						6/13/08		0.05		71		36		0.26		0.32		0.44		55		1208																				6/27/08		0.02		71		39

		1/30/08		0.1						11/30/07		0.05						6/16/08		0.05		73		34		0.3		0.32		0.46		55		1204																				6/30/08		0.02		73		38

		1/31/08		0.105						12/3/07		0.05						6/17/08		0.05		73		24		0.28		0.32		0.44		55		1216																				7/1/08		0.055		73		39

		2/1/08		0.09						12/4/07		0.05						6/18/08		0.05		73		31		0.3		0.32		0.44		55		1196																				7/2/08		0.055		73		38

		2/4/08		0.03						12/5/07		0.045						6/19/08		0.05		71		30		0.28		0.32		0.46		55		1196																				7/3/08		0.065		71		39

		2/5/08		0.04						12/6/07		0.05						6/20/08		0.05		73		28		0.28		0.32		0.46		55		1196																				7/7/08		0.055		75		38

		2/6/08		0.025						12/7/07		0.045						6/21/08		0.045		72		30		0.26		0.32		0.46		55		32																				7/8/08		0.05		72		40

		2/7/08		0.02						12/10/07		0.05						6/23/08		0.05		73		39		0.28		0.32		0.44		57		32																				7/9/08		0.06		73		39

		2/8/08		0.04						12/11/07		0.045						6/24/08		0.05		72		34		0.28		0.32		0.42		60		32																				7/10/08		0.06		74		39

		2/9/08		0.05						12/12/07		0.045						6/25/08		0.04		73		36		0.28		0.32		0.44		60		32																				7/11/08		0.06		71		40

		2/11/08		0.02						12/13/07		0.045						6/26/08		0.04		72		34		0.28		0.32		0.44		60		32																				7/12/08		0.06		73		42

		2/12/08		0.035						12/14/07		0.045						6/27/08		0.04		71		38		0.32		0.32		0.44		60		32																				7/14/08		0.06		72		41

		2/13/08		0.025						12/17/07		0.045						6/30/08		0.04		73		37		0.3		0.32		0.44		60		32																				7/15/08		0.06		71		41

		2/14/08		0.025						12/18/07		0.04						7/1/08		0.035		71		38		0.28		0.32		0.44		60		32																				7/16/08		0.065		72		40

		2/15/08		0.03						12/19/07		0.04						7/2/08		0.07		72		38		0.3		0.32		0.46		60		32																				7/17/08		0.05		71		41

		2/19/08		0.03						12/20/07		0.03						7/3/08		0.08		72		38		0.32		0.32		0.48		57		32																				7/18/08		0.065		72		40

		2/20/08		0.05						12/21/07		0.04						7/7/08		0.06		73		40		0.28		0.32		0.44		57		32																				7/19/08		0.06		72		39

		2/21/08		0.03						12/26/07		0.04						7/8/08		0.06		72		38		0.28		0.32		0.42		60		32																				7/21/08		0.06		71		40

		2/22/08		0.03						12/27/07		0.04						7/9/08		0.06		73		39		0.28		0.32		0.42																								7/22/08		0.05		74		36

		2/23/08		0.035						12/28/07		0.04						7/10/08		0.07		72		40		0.32		0.32		0.48		55		1104																				7/23/08		0.07		72		39

		2/24/08		0.035						12/31/07		0.04						7/11/08		0.065		71		39		0.3		0.32		0.48		55		1104																				7/24/08		0.05		72		37

		2/25/08		0.03						1/2/08		0.04						7/12/08		0.08		73		40																														7/25/08		0.06		71		38

		2/26/08		0.035						1/3/08		0.04						7/14/08		0.08		72		40		0.3		0.32		0.48		61		1200																				7/26/08		0.07		71		38

		2/27/08		0.03						1/4/08		0.04						7/15/08		0.09		71		40		0.28		0.32		0.42		61		1200																				7/28/08		0.06		70		41

		2/28/08		0.03						1/7/08		0.025						7/16/08		0.09		72		39		0.28		0.32		0.42		61		1200																				7/29/08		0.06		70		41

		2/29/08		0.03						1/8/08		0.03						7/17/08		0.08		72		39		0.28		0.32		0.44		61		1200																				7/30/08		0.06		71		39

		3/1/08		0.035						1/9/08		0.03						7/18/08		0.09		72		38		0.3		0.32		0.48		61		1200																				7/31/08		0.065		71		40

		3/3/08		0.03						1/10/08		0.03						7/19/08		0.09		73		37																														8/1/08		0.06		73		36

		3/4/08		0.035						1/11/08		0.03						7/21/08		0.09		72		38		0.28		0.32		0.4		61		1200																				8/2/08		0.06		71		40

		3/5/08		0.043						1/14/08		0.025						7/22/08		0.08		73		37		0.24		0.32		0.42		61		1200																				8/4/08		0.06		72		40

		3/6/08		0.043						1/15/08		0.03						7/23/08		0.09		71		38		0.28		0.32		0.44		61		1200																				8/5/08		0.06		73		39

		3/7/08		0.043						1/16/08		0.03						7/24/08		0.09		72		36		0.26		0.32		0.46		61		1200																				8/6/08		0.06		71		41

		3/10/08		0.043						1/17/08		0.03						7/25/08		0.09		72		36		0.24		0.32		0.42		61		1200																				8/7/08		0.06		72		39

		3/11/08		0.042						1/18/08		0.025						7/26/08		0.09		71		37		0.28		0.32		0.46		61		1200																				8/8/08		0.05		72		40

		3/12/08		0.039						1/21/08		0.035						7/28/08		0.09		71		38		0.3		0.32		0.46		61		1200																				8/9/08		0.055		71		40

		3/13/08		0.03						1/22/08		0.03						7/29/08		0.06		70		40		0.3		0.32		0.44																								8/11/08		0.06		71		39

		3/14/08		0.041						1/23/08		0.035						7/30/08		0.07		71		38		0.3		0.32		0.48																								8/12/08		0.065		71		41

		3/17/08		0.047						1/24/08		0.03						7/31/08		0.075		71		38																														8/13/08		0.055		71		41

		3/18/08		0.048						1/25/08		0.035						8/1/08		0.07		72		37		0.3		0.32		0.48																								8/14/08		0.05		71		41

		3/19/08		0.047						1/28/08		0.035						8/2/08		0.07		72		38																														8/15/08		0.05		72		39

		3/20/08		0.042						1/29/08		0.035						8/4/08		0.07		73		37		0.28		0.32		0.44																								8/16/08		0.06		72		40

		3/21/08		0.043						1/30/08		0.025						8/5/08		0.06		73		37		0.28		0.34		0.48																								8/18/08		0.06		72		41

		3/22/08		0.045						1/31/08		0.03						8/6/08		0.07		71		38		0.28		0.32		0.48																								8/19/08		0.06		72		41

		3/24/08		0.043						2/1/08		0.03						8/7/08		0.06		71		38		0.32		0.32		0.48																								8/20/08		0.06		71		40

		3/25/08		0.045						2/4/08		0.035						8/8/08		0.06		72		38		0.26		0.32		0.44																								8/21/08		0.05		73		44

		3/26/08		0.043						2/5/08		0.025						8/9/08		0.06		71		40																														8/22/08		0.05		72		40

		3/27/08		0.04						2/6/08		0.035						8/11/08		0.07		71		38		0.28		0.32		0.44																								8/23/08		0.05		72		41

		3/28/08		0.04						2/7/08		0.025						8/12/08		0.07		71		40		0.28		0.32		0.44																								8/25/08		0.06		71		40

		3/31/08		0.045						2/8/08		0.02						8/13/08		0.065		71		40		0.28		0.3		0.46																								8/26/08		0.06		70		39

		4/1/08		0.045						2/9/08		0.02						8/14/08		0.05		71		39		0.26		0.32		0.42																								8/27/08		0.05		71		40

		4/2/08		0.045						2/14/08		0.035						8/15/08		0.06		71		38		0.26		0.32		0.42																								8/28/08		0.055		71		40

		4/3/08		0.04						2/15/08		0.033						8/16/08		0.06		71		40																														8/29/08		0.055		72		39

		4/4/08		0.045						2/19/08		0.036						8/18/08		0.065		71		41		0.26		0.32		0.42																								9/2/08		0.055		69		32

		4/5/08		0.045						2/20/08		0.037						8/19/08		0.06		72		40		0.28		0.32		0.44																								9/3/08		0.055		72		39

		4/7/08		0.045						2/21/08		0.037						8/20/08		0.06		71		31		0.26		0.32		0.42																								9/4/08		0.055		70		38

		4/8/08		0.04						2/22/08		0.034						8/21/08		0.05		73		42		0.28		0.32		0.48																								9/5/08		0.06		71		36

		4/9/08		0.04						2/25/08		0.044						8/22/08		0.06		71		38		0.24		0.32		0.44																								9/6/08		0.06		71		39

		4/10/08		0.04						2/26/08		0.043						8/23/08		0.06		72		40																														9/8/08		0.06		74		38

		4/11/08		0.045						2/27/08		0.043						8/25/08		0.06		71		40		0.26		0.32		0.46																								9/9/08		0.06		72		40

		4/14/08		0.045						2/28/08		0.044						8/26/08		0.06		70		38		0.26		0.32		0.44																								9/10/08		0.06		72		40

		4/15/08		0.04						2/29/08		0.046						8/27/08		0.05		71		38		0.26		0.32		0.44																								9/11/08		0.06		71		41

		4/16/08		0.04						3/3/08		0.045						8/28/08		0.05		71		38		0.26		0.3		0.44																								9/12/08		0.06		70		40

		4/17/08		0.04						3/4/08		0.044						8/29/08		0.065		72		38		0.28		0.3		0.44																								9/13/08		0.06		70		41

		4/18/08		0.04						3/5/08		0.039						9/2/08		0.06		69		31		0.24		0.32		0.42																								9/15/08		0.06		70		40

		4/19/08		0.05						3/6/08		0.039						9/3/08		0.06		72		40		0.28		0.32		0.44																								9/16/08		0.06		71		40

		4/21/08		0.05						3/7/08		0.038						9/4/08		0.06		70		37		0.26		0.32		0.44																								9/17/08		0.06		70		30

		4/22/08		0.045						3/10/08		0.037						9/5/08		0.06		70		36		0.26		0.32		0.44																								9/18/08		0.06		71		37

		4/23/08		0.04						3/11/08		0.04						9/6/08		0.06		70		38																														9/19/08		0.06		72		43

		4/24/08		0.04						3/12/08		0.036						9/8/08		0.06		72		41		0.24		0.32		0.42																								9/20/08		0.06		72		42

		4/25/08		0.04						3/14/08		0.039						9/9/08		0.06		71		40		0.24		0.32		0.44																								9/22/08		0.06		71		39

		4/30/08		0.04						3/17/08		0.038						9/10/08		0.06		70		41		0.28		0.32		0.46																								9/23/08		0.065		72		37

		5/1/08		0.04						3/18/08		0.038						9/11/08		0.06		70		41		0.26		0.32		0.42																								9/24/08		0.055		70		33

		5/2/08		0.04						3/19/08		0.037						9/12/08		0.06		70		40		0.28		0.32		0.48																								9/25/08		0.06		72		32

		5/3/08		0.045						3/20/08		0.039						9/13/08		0.06		70		40																														9/26/08		0.06		72		43

		5/5/08		0.04						3/21/08		0.038						9/15/08		0.06		69		41		0.3		0.32		0.44																								9/27/08		0.06		70		37

		5/6/08		0.04						3/24/08		0.038						9/16/08		0.06		69		41		0.24		0.3		0.42																								9/29/08		0.06		71		40

		5/7/08		0.045						3/25/08		0.038						9/17/08		0.07		69		38		0.26		0.32		0.46																								9/30/08		0.06		75		33

		5/8/08		0.04						3/26/08		0.039						9/18/08		0.06		70		38		0.26		0.32		0.42

		5/9/08		0.04						3/27/08		0.045						9/19/08		0.06		73		42		0.26		0.32		0.42

		5/10/08		0.04						3/28/08		0.04						9/20/08		0.05		73		41

		5/12/08		0.04						3/31/08		0.04						9/22/08		0.06		71		38		0.24		0.32		0.44

		5/13/08		0.04						4/1/08		0.04						9/23/08		0.065		71		37		0.26		0.32		0.44

		5/14/08		0.04						4/2/08		0.04						9/24/08		0.055		71		32		0.26		0.32		0.42

		5/15/08		0.04						4/3/08		0.035						9/25/08		0.06		71		32		0.28		0.32		0.48

		5/16/08		0.04						4/4/08		0.04						9/26/08		0.055		73		41		0.24		0.32		0.44

		5/19/08		0.04						4/5/08		0.035						9/27/08		0.06		71		35

		5/20/08		0.04						4/7/08		0.04						9/29/08		0.06		70		40		0.26		0.32		0.44

		5/21/08		0.04						4/8/08		0.04						9/30/08		0.05		71		36		0.24		0.32		0.44

		5/22/08		0.04						4/9/08		0.035						10/1/08								0.24		0.32		0.44

		5/23/08		0.04						4/10/08		0.04						10/2/08								0.24		0.32		0.44

		5/27/08		0.04						4/11/08		0.04

		5/28/08		0.04						4/14/08		0.04

		5/29/08		0.05						4/15/08		0.04

		5/30/08		0.04						4/16/08		0.04

		5/31/08		0.045						4/17/08		0.04

		6/2/08		0.04						4/18/08		0.035

		6/3/08		0.04						4/19/08		0.05

		6/4/08		0.04						4/21/08		0.05

		6/5/08		0.04						4/22/08		0.04

		6/6/08		0.04						4/23/08		0.04

		6/9/08		0.04						4/24/08		0.04

		6/10/08		0.04						4/25/08		0.04

		6/11/08		0.04						4/30/08		0.04

		6/12/08		0.04						5/1/08		0.04

		6/13/08		0.04						5/2/08		0.04

		6/16/08		0.04						5/3/08		0.04

		6/17/08		0.04						5/5/08		0.04

		6/18/08		0.04						5/6/08		0.04

		6/19/08		0.04						5/7/08		0.04

		6/20/08		0.04						5/8/08		0.04

		6/21/08		0.035						5/9/08		0.04

		6/23/08		0.035						5/10/08		0.04

		6/24/08		0.04						5/12/08		0.04

		6/25/08		0.035						5/13/08		0.04

		6/26/08		0.035						5/14/08		0.04

		6/27/08		0.035						5/15/08		0.04

		6/30/08		0.035						5/16/08		0.04

		7/1/08		0.03						5/19/08		0.04

		7/2/08		0.03						5/20/08		0.04

		7/3/08		0.035						5/21/08		0.04

		7/7/08		0.03						5/22/08		0.04

		7/8/08		0.03						5/23/08		0.04

		7/9/08		0.035						5/27/08		0.04

		7/10/08		0.035						5/28/08		0.04

		7/11/08		0.035						5/29/08		0.04

		7/12/08		0.03						5/30/08		0.04

		7/14/08		0.025						6/2/08		0.04

		7/15/08		0.03						6/3/08		0.035

		7/16/08		0.03						6/4/08		0.035

		7/17/08		0.03						6/5/08		0.035

		7/18/08		0.04						6/6/08		0.035

		7/19/08		0.03						6/9/08		0.035

		7/21/08		0.03						6/10/08		0.035

		7/22/08		0.03						6/11/08		0.035

		7/23/08		0.02						6/12/08		0.035

		7/24/08		0.025						6/13/08		0.04

		7/25/08		0.01						6/16/08		0.035

		7/26/08		0.01						6/17/08		0.045

		7/28/08		0.01						6/18/08		0.045

		7/29/08		0.03						6/19/08		0.045

		7/30/08		0.01						6/20/08		0.035

		7/31/08		0.015						6/21/08		0.035

		8/1/08		0.025						6/23/08		0.035

		8/2/08		0.03						6/24/08		0.045

		8/4/08		0.03						6/25/08		0.035

		8/5/08		0.03						6/26/08		0.035

		8/6/08		0.04						6/27/08		0.035

		8/7/08		0.035						6/30/08		0.035

		8/8/08		0.03						7/1/08		0.04

		8/9/08		0.03						7/2/08		0.04

		8/11/08		0.035						7/3/08		0.04

		8/12/08		0.035						7/7/08		0.04

		8/13/08		0.035						7/8/08		0.04

		8/14/08		0.03						7/9/08		0.04

		8/15/08		0.03						7/10/08		0.04

		8/16/08		0.03						7/11/08		0.04

		8/18/08		0.03						7/12/08		0.04

		8/19/08		0.04						7/14/08		0.04

		8/20/08		0.03						7/15/08		0.04

		8/21/08		0.03						7/16/08		0.04

		8/22/08		0.03						7/17/08		0.04

		8/23/08		0.03						7/18/08		0.04

		8/25/08		0.03						7/19/08		0.04

		8/26/08		0.03						7/21/08		0.04

		8/27/08		0.03						7/22/08		0.04

		8/28/08		0.03						7/23/08		0.04

		8/29/08		0.03						7/24/08		0.04

		9/2/08		0.03						7/25/08		0.04

		9/3/08		0.03						7/26/08		0.04

		9/4/08		0.03						7/28/08		0.04

		9/5/08		0.03						7/29/08		0.04

		9/6/08		0.03						7/30/08		0.04

		9/8/08		0.03						7/31/08		0.04

		9/9/08		0.03						8/1/08		0.045

		9/10/08		0.03						8/2/08		0.04

		9/11/08		0.03						8/4/08		0.04

		9/12/08		0.03						8/5/08		0.04

		9/13/08		0.03						8/6/08		0.05

		9/15/08		0.035						8/7/08		0.04

		9/16/08		0.03						8/8/08		0.04

		9/17/08		0.03						8/9/08		0.04

		9/18/08		0.03						8/11/08		0.04

		9/19/08		0.03						8/12/08		0.04

		9/20/08		0.03						8/13/08		0.04

		9/22/08		0.03						8/14/08		0.04

		9/23/08		0.03						8/15/08		0.04

		9/24/08		0.025						8/16/08		0.04

		9/25/08		0.03						8/18/08		0.04

		9/26/08		0.03						8/19/08		0.04

		9/27/08		0.03						8/20/08		0.04

		9/29/08		0.03						8/21/08		0.04

		9/30/08		0.03						8/22/08		0.04

		10/1/08		0.03						8/23/08		0.04

		10/2/08		0.03						8/25/08		0.04

		10/3/08		0.03						8/26/08		0.04

		10/4/08		0.03						8/27/08		0.04

		10/6/08		0.03						8/28/08		0.04

		10/7/08		0.04						8/29/08		0.04

		10/8/08		0.03						9/2/08		0.04

		10/9/08		0.03						9/3/08		0.04

		10/10/08		0.03						9/4/08		0.04

		10/11/08		0.03						9/5/08		0.04

		10/13/08		0.03						9/6/08		0.04

		10/14/08		0.03						9/8/08		0.04

		10/15/08		0.03						9/9/08		0.04

		10/16/08		0.04						9/10/08		0.04

		10/17/08		0.03						9/11/08		0.04

		10/18/08		0.03						9/12/08		0.04

		10/20/08		0.03						9/13/08		0.04

		10/21/08		0.03						9/15/08		0.04

		10/22/08		0.03						9/16/08		0.04

		10/23/08		0.03						9/17/08		0.04

		10/24/08		0.03						9/18/08		0.04

		10/25/08		0.03						9/19/08		0.04

		10/27/08		0.03						9/20/08		0.04

		10/28/08		0.03						9/22/08		0.04

		10/29/08		0.03						9/23/08		0.045

		10/30/08		0.03						9/24/08		0.045

		10/31/08		0.03						9/25/08		0.045

		11/3/08		0.03						9/26/08		0.04

		11/4/08		0.03						9/27/08		0.04

										9/29/08		0.04

										9/30/08		0.04

										10/1/08		0.04

										10/2/08		0.04

										10/3/08		0.04

										10/4/08		0.04

										10/6/08		0.04

										10/7/08		0.05

										10/8/08		0.045

										10/9/08		0.04

										10/10/08		0.04

										10/11/08		0.04

										10/13/08		0.045

										10/14/08		0.04

										10/15/08		0.045

										10/16/08		0.04

										10/17/08		0.04

										10/18/08		0.04

										10/20/08		0.04

										10/21/08		0.04

										10/22/08		0.04

										10/23/08		0.04

										10/24/08		0.04

										10/25/08		0.04

										10/27/08		0.04

										10/28/08		0.04

										10/29/08		0.04

										10/30/08		0.04

										10/31/08		0.04

										11/3/08		0.04

										11/4/08		0.04

										11/5/08		0.05

										11/6/08		0.04

										11/7/08		0.04

										11/8/08		0.045

										11/10/08		0.04

										11/11/08		0.04

										11/12/08		0.04

										11/13/08		0.04

										11/14/08		0.04

										11/15/08		0.04

										11/17/08		0.04

										11/18/08		0.04

										11/19/08		0.04

										11/20/08		0.045

										11/21/08		0.045

										11/22/08		0.04

										11/24/08		0.04

										11/25/08		0.04

										11/26/08		0.04

										12/1/08		0.04





CER Pressure

		



Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)

R&D Bio-Safety Cabinet South (left axis)

Date

Diff. Pressure (Water Column In.)

Mfg Bio-Safety Cabinet South CFM

Figure 7.  CER2 Bio-Safety Cabinet Differential Pressure Daily Run Chart



Conf-Rel

		



Bio-Safety Cabinet Alert Level (left axis)

Bio-Safety Cabinet Action  Level (left axis)

R&D Bio-Safety Cabinet North (left axis)

R&D Bio-Safety Cabinet South (left axis)

Mfg Bio-Safety Cabinet North (left axis)

Mfg Bio-Safety Cabinet South Downflow (cfm) (right axis)

Mfg Bio-Safety Cabinet South Exhaust (cfm) (right axis)

Date

Diff. Pressure (Water Column In.)

Mfg Bio-Safety Cabinet (cfm)

Figure 8.  Bio-Safety Cabinet Differential Pressure - Monthly Average



Temp-Humid

		



CER1

CER Change Room

CER2

CER3

CER Alert Level

CER Action Level

Date

Diff. Pressure (Water Column In.)

Figure 5.  CER Differential Pressure Daily Run Chart



Sheet1

		



CER1

CER Change Room

CER 2

CER 3

CER Alert Level

CER Action Level

Date

Diff. Pressure (Water Column In.)

Figure 6.  CER Differential Pressure - Monthly Average



		TO:		DCN 0273 File

		FROM:		Andy Pearson

		DATE:		3/3/07

		RE:		Confidence and Reliability Levels for CER Monitoring

		The table below shows 95/95, and 95/99 confidence/reliability levels for  CER and Change Room

		monitoring carried out from Feb 06 to Feb 07.

		Recommended action and alert levels correspond to worst case 95/95 (alert) and 95/99 (action) values.

						95/95 Limit		Recommended Alert Level		95/99 Limit		95/99 Limit		Recommended Action Level

		Airstrips (utl)		CER1		17		35		21		21		45

				CER2		15				20		20

				CER3		34				43		43

		Contact Plates (utl)		CER1		5		6		6		6		7

				CER2		4				5		5

				CER3		6				7		7

		0.5um Particle Counts (utl)		CER1		1092		3800		1324		1324		4500

				CER3		3797				4549		4549

				CER2		1232		1250		1495		1495		1500

		5.0um Particle Counts (utl)		CER1		159		410		200		200		500

				CER3		410				497		497

				CER2		91		90		107		107		105

		Pressure Differential (ltl)		CER1		0.011		0.030		0.003		0.003		0.005

				CER1/2 Chg Rm		0.021				0.013		0.013

				CER2		-0.021				-0.045		-0.045

				CER3		0.040				0.035		0.035

		Andy Pearson

		Sr.Quality Engineer





		CER2								CER1								CER3								QA

		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 2 Temperature(°F)		CER 2 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 1 Temperature(°F)		CER 1 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		CER 3 Temperature(°F)		CER 3 Humidity(%)		Date(dd-mmm-yy)		Time (hh:mm:ss)		QA Temperature(°F)		QA Humidity(%)

		29-Aug-07		16:07:10		75.81		46.5		29-Aug-07		16:06:20		76.4		48		29-Aug-07		16:07:53		75.81		74		9-Oct-07		16:25:59		78.2		33

		29-Aug-07		18:07:10		74.01		40.5		29-Aug-07		18:06:20		70.41		41.5		29-Aug-07		18:07:53		74.6		41.5		9-Oct-07		18:25:59		75.81		35.5

		29-Aug-07		20:07:10		74.6		40.5		29-Aug-07		20:06:20		71.6		43.5		29-Aug-07		20:07:53		73.4		43		9-Oct-07		20:25:59		75.2		34.5

		29-Aug-07		22:07:10		75.81		40.5		29-Aug-07		22:06:20		71.6		46.5		29-Aug-07		22:07:53		74.6		42		9-Oct-07		22:25:59		74.6		35

		30-Aug-07		0:07:10		75.81		40.5		30-Aug-07		0:06:20		71.6		47.5		30-Aug-07		0:07:53		75.2		41.5		10-Oct-07		0:25:59		73.4		36

		30-Aug-07		2:07:10		75.81		41		30-Aug-07		2:06:20		71		49		30-Aug-07		2:07:53		75.81		41.5		10-Oct-07		2:25:59		72.8		37

		30-Aug-07		4:07:10		75.2		42.5		30-Aug-07		4:06:20		71		51		30-Aug-07		4:07:53		75.2		41.5		10-Oct-07		4:25:59		72.21		38

		30-Aug-07		6:07:10		75.81		41		30-Aug-07		6:06:20		71.6		46.5		30-Aug-07		6:07:53		75.2		42		10-Oct-07		6:25:59		72.21		39

		30-Aug-07		8:07:10		75.81		45.5		30-Aug-07		8:06:20		72.21		55.5		30-Aug-07		8:07:53		75.2		44		10-Oct-07		8:25:59		71.6		41.5

		30-Aug-07		10:07:10		74.6		43.5		30-Aug-07		10:06:20		72.21		41.5		30-Aug-07		10:07:53		74.6		45		10-Oct-07		10:25:59		72.8		42.5

		30-Aug-07		12:07:10		74.6		43.5		30-Aug-07		12:06:20		71.6		46		30-Aug-07		12:07:53		72.8		45.5		10-Oct-07		12:25:59		74.01		42.5

		30-Aug-07		14:07:10		74.6		43		30-Aug-07		14:06:20		72.21		43		30-Aug-07		14:07:53		72.21		44.5		10-Oct-07		14:25:59		75.2		43

		30-Aug-07		16:07:10		75.2		43.5		30-Aug-07		16:06:20		72.21		43.5		30-Aug-07		16:07:53		72.8		44.5		10-Oct-07		16:25:59		75.2		42

		30-Aug-07		18:07:10		75.2		45		30-Aug-07		18:06:20		70.41		49.5		30-Aug-07		18:07:53		71.6		46		10-Oct-07		18:25:59		75.2		41

		30-Aug-07		20:07:10		75.2		45.5		30-Aug-07		20:06:20		71.6		52		30-Aug-07		20:07:53		75.81		45		10-Oct-07		20:25:59		74.01		42.5

		30-Aug-07		22:07:10		76.4		45		30-Aug-07		22:06:20		71		53.5		30-Aug-07		22:07:53		75.2		45		10-Oct-07		22:25:59		73.4		43.5

		31-Aug-07		0:07:10		76.4		44.5		31-Aug-07		0:06:20		71		53.5		31-Aug-07		0:07:53		75.2		44.5		11-Oct-07		0:25:59		72.8		44.5

		31-Aug-07		2:07:10		75.81		44.5		31-Aug-07		2:06:20		71.6		53		31-Aug-07		2:07:53		75.2		45.5		11-Oct-07		2:25:59		72.21		45

		31-Aug-07		4:07:10		75.81		45		31-Aug-07		4:06:20		71.6		53		31-Aug-07		4:07:53		72.8		41.5		11-Oct-07		4:25:59		71.6		45.5

		31-Aug-07		6:07:10		75.81		45.5		31-Aug-07		6:06:20		72.21		54		31-Aug-07		6:07:53		71		54.5		11-Oct-07		6:25:59		72.21		45

		31-Aug-07		8:07:10		75.2		44		31-Aug-07		8:06:20		72.21		43.5		31-Aug-07		8:07:53		71.6		50.5		11-Oct-07		8:25:59		71.6		46.5

		31-Aug-07		10:07:10		74.6		45.5		31-Aug-07		10:06:20		72.21		49.5		31-Aug-07		10:07:53		72.21		44.5		11-Oct-07		10:25:59		72.8		48.5

		31-Aug-07		12:07:10		74.6		49.5		31-Aug-07		12:06:20		71.6		60.5		31-Aug-07		12:07:53		72.21		45		11-Oct-07		12:25:59		74.6		44.5

		31-Aug-07		14:07:10		74.6		45.5		31-Aug-07		14:06:20		71.6		44		31-Aug-07		14:07:53		72.8		47		11-Oct-07		14:25:59		75.81		42.5

		31-Aug-07		16:07:10		74.6		48		31-Aug-07		16:06:20		71.6		56.5		31-Aug-07		16:07:53		72.8		43.5		11-Oct-07		16:25:59		76.4		42.5

		31-Aug-07		18:07:10		75.2		46.5		31-Aug-07		18:06:20		70.41		54.5		31-Aug-07		18:07:53		71		50		11-Oct-07		18:25:59		76.4		41

		31-Aug-07		20:07:10		75.2		46		31-Aug-07		20:06:20		71.6		53		31-Aug-07		20:07:53		74.6		50		11-Oct-07		20:25:59		74.6		41.5

		31-Aug-07		22:07:10		76.4		44		31-Aug-07		22:06:20		71.6		48.5		31-Aug-07		22:07:53		75.2		47		11-Oct-07		22:25:59		74.6		41

		1-Sep-07		0:07:10		76.4		42.5		1-Sep-07		0:06:20		71.6		46.5		1-Sep-07		0:07:53		75.2		45.5		12-Oct-07		0:25:59		73.4		41

		1-Sep-07		2:07:10		76.4		44		1-Sep-07		2:06:20		71.6		53		1-Sep-07		2:07:53		74.6		45.5		12-Oct-07		2:25:59		71.6		41

		1-Sep-07		4:07:10		76.4		44		1-Sep-07		4:06:20		71.6		53		1-Sep-07		4:07:53		72.8		50		12-Oct-07		4:25:59		71		41.5

		1-Sep-07		6:07:10		76.4		45		1-Sep-07		6:06:20		73.4		56.5		1-Sep-07		6:07:53		71.6		45		12-Oct-07		6:25:59		70.41		41.5

		1-Sep-07		8:07:10		75.2		42.5		1-Sep-07		8:06:20		72.21		41		1-Sep-07		8:07:53		71.6		53		12-Oct-07		8:25:59		69.8		41.5

		1-Sep-07		10:07:10		74.6		43.5		1-Sep-07		10:06:20		71.6		42		1-Sep-07		10:07:53		72.21		43.5		12-Oct-07		10:25:59		71.6		44.5

		1-Sep-07		12:07:10		74.6		51.5		1-Sep-07		12:06:20		70.41		64		1-Sep-07		12:07:53		71.6		45.5		12-Oct-07		12:25:59		74.6		43.5

		1-Sep-07		14:07:10		74.6		52		1-Sep-07		14:06:20		70.41		64.5		1-Sep-07		14:07:53		71		50.5		12-Oct-07		14:25:59		75.2		42.5

		1-Sep-07		16:07:10		74.6		46.5		1-Sep-07		16:06:20		70.41		52.5		1-Sep-07		16:07:53		71		57.5		12-Oct-07		16:25:59		75.2		42.5

		1-Sep-07		18:07:10		74.6		45.5		1-Sep-07		18:06:20		70.41		50.5		1-Sep-07		18:07:53		71		58.5		12-Oct-07		18:25:59		74.6		40

		1-Sep-07		20:07:10		74.6		49.5		1-Sep-07		20:06:20		71		56		1-Sep-07		20:07:53		71		55.5		12-Oct-07		20:25:59		74.01		40.5

		1-Sep-07		22:07:10		75.2		47		1-Sep-07		22:06:20		71		56		1-Sep-07		22:07:53		72.21		50.5		12-Oct-07		22:25:59		74.01		40

		2-Sep-07		0:07:10		75.2		45		2-Sep-07		0:06:20		71.6		52.5		2-Sep-07		0:07:53		72.21		50		13-Oct-07		0:25:59		72.8		40.5

		2-Sep-07		2:07:10		75.2		44.5		2-Sep-07		2:06:20		71		51		2-Sep-07		2:07:53		71.6		50		13-Oct-07		2:25:59		71.6		41

		2-Sep-07		4:07:10		74.6		44		2-Sep-07		4:06:20		70.41		51.5		2-Sep-07		4:07:53		70.41		49.5		13-Oct-07		4:25:59		71		42.5

		2-Sep-07		6:07:10		74.01		41.5		2-Sep-07		6:06:20		71		45.5		2-Sep-07		6:07:53		69.2		48.5		13-Oct-07		6:25:59		71.6		43

		2-Sep-07		8:07:10		73.4		44		2-Sep-07		8:06:20		69.8		51		2-Sep-07		8:07:53		69.2		51		13-Oct-07		8:25:59		71		46

		2-Sep-07		10:07:10		74.01		48.5		2-Sep-07		10:06:20		70.41		57.5		2-Sep-07		10:07:53		71		48.5		13-Oct-07		10:25:59		72.21		47.5

		2-Sep-07		12:07:10		74.6		49.5		2-Sep-07		12:06:20		70.41		59.5		2-Sep-07		12:07:53		71		53		13-Oct-07		12:25:59		72.8		47

		2-Sep-07		14:07:10		75.81		49.5		2-Sep-07		14:06:20		70.41		60.5		2-Sep-07		14:07:53		71		60		13-Oct-07		14:25:59		72.21		47.5

		2-Sep-07		16:07:10		76.4		43.5		2-Sep-07		16:06:20		70.41		47.5		2-Sep-07		16:07:53		71		46.5		13-Oct-07		16:25:59		74.01		47

		2-Sep-07		18:07:10		76.4		46.5		2-Sep-07		18:06:20		69.8		55.5		2-Sep-07		18:07:53		71		58		13-Oct-07		18:25:59		74.6		44.5

		2-Sep-07		20:07:10		77		44		2-Sep-07		20:06:20		71		52.5		2-Sep-07		20:07:53		74.01		47		13-Oct-07		20:25:59		72.8		45.5

		2-Sep-07		22:07:10		77		41.5		2-Sep-07		22:06:20		71.6		51		2-Sep-07		22:07:53		74.6		44.5		13-Oct-07		22:25:59		71.6		45

		3-Sep-07		0:07:10		76.4		41		3-Sep-07		0:06:20		71		50.5		3-Sep-07		0:07:53		74.01		44.5		14-Oct-07		0:25:59		71		45

		3-Sep-07		2:07:10		75.81		40		3-Sep-07		2:06:20		71		44		3-Sep-07		2:07:53		72.21		45.5		14-Oct-07		2:25:59		69.8		43.5

		3-Sep-07		4:07:10		75.2		39		3-Sep-07		4:06:20		71		41.5		3-Sep-07		4:07:53		71		46.5		14-Oct-07		4:25:59		69.2		43

		3-Sep-07		6:07:10		75.2		40		3-Sep-07		6:06:20		71.6		46		3-Sep-07		6:07:53		69.2		47.5		14-Oct-07		6:25:59		69.2		42.5

		3-Sep-07		8:07:10		74.01		42		3-Sep-07		8:06:20		69.8		49		3-Sep-07		8:07:53		68.61		49.5		14-Oct-07		8:25:59		69.2		41

		3-Sep-07		10:07:10		74.01		43		3-Sep-07		10:06:20		70.41		48		3-Sep-07		10:07:53		70.41		52		14-Oct-07		10:25:59		71		44

		3-Sep-07		12:07:10		74.6		41.5		3-Sep-07		12:06:20		70.41		43.5		3-Sep-07		12:07:53		71		43.5		14-Oct-07		12:25:59		72.21		45

		3-Sep-07		14:07:10		75.2		43		3-Sep-07		14:06:20		70.41		47		3-Sep-07		14:07:53		71.6		52		14-Oct-07		14:25:59		74.01		44.5

		3-Sep-07		16:07:10		75.81		44.5		3-Sep-07		16:06:20		69.8		49.5		3-Sep-07		16:07:53		71.6		52		14-Oct-07		16:25:59		75.2		44.5

		3-Sep-07		18:07:10		76.4		40.5		3-Sep-07		18:06:20		70.41		47		3-Sep-07		18:07:53		71		45		14-Oct-07		18:25:59		75.81		44

		3-Sep-07		20:07:10		77.61		40		3-Sep-07		20:06:20		71.6		45.5		3-Sep-07		20:07:53		75.81		42		14-Oct-07		20:25:59		74.6		44.5

		3-Sep-07		22:07:10		77		41		3-Sep-07		22:06:20		71.6		50.5		3-Sep-07		22:07:53		74.6		43.5		14-Oct-07		22:25:59		73.4		45

		4-Sep-07		0:07:10		76.4		40.5		4-Sep-07		0:06:20		71		50		4-Sep-07		0:07:53		74.6		43.5		15-Oct-07		0:25:59		72.8		45.5

		4-Sep-07		2:07:10		75.81		40		4-Sep-07		2:06:20		71		49.5		4-Sep-07		2:07:53		72.8		44		15-Oct-07		2:25:59		72.21		46

		4-Sep-07		4:07:10		75.81		39.5		4-Sep-07		4:06:20		71.6		47		4-Sep-07		4:07:53		71.6		45		15-Oct-07		4:25:59		71.6		46

		4-Sep-07		6:07:10		74.6		40		4-Sep-07		6:06:20		71		47.5		4-Sep-07		6:07:53		69.8		46.5		15-Oct-07		6:25:59		71		46.5

		4-Sep-07		8:07:10		74.01		39.5		4-Sep-07		8:06:20		70.41		42		4-Sep-07		8:07:53		69.8		48.5		15-Oct-07		8:25:59		70.41		47

		4-Sep-07		10:07:10		74.01		45.5		4-Sep-07		10:06:20		69.8		53.5		4-Sep-07		10:07:53		71		52		15-Oct-07		10:25:59		69.8		47.5

		4-Sep-07		12:07:10		74.01		48		4-Sep-07		12:06:20		69.8		55		4-Sep-07		12:07:53		71		45.5		15-Oct-07		12:25:59		70.41		48.5

		4-Sep-07		14:07:10		74.01		49		4-Sep-07		14:06:20		70.41		52		4-Sep-07		14:07:53		71		58.5		15-Oct-07		14:25:59		71.6		49

		4-Sep-07		16:07:10		74.6		47.5		4-Sep-07		16:06:20		70.41		50		4-Sep-07		16:07:53		71		49		15-Oct-07		16:25:59		73.4		48

		4-Sep-07		18:07:10		74.6		47.5		4-Sep-07		18:06:20		70.41		50		4-Sep-07		18:07:53		71		49.5		15-Oct-07		18:25:59		74.6		45.5

		4-Sep-07		20:07:10		75.2		50		4-Sep-07		20:06:20		71		58.5		4-Sep-07		20:07:53		71.6		55.5		15-Oct-07		20:25:59		72.8		46

		4-Sep-07		22:07:10		75.81		47.5		4-Sep-07		22:06:20		71.6		56		4-Sep-07		22:07:53		74.01		50		15-Oct-07		22:25:59		71.6		46

		5-Sep-07		0:07:10		75.81		46.5		5-Sep-07		0:06:20		71		56.5		5-Sep-07		0:07:53		74.01		49.5		16-Oct-07		0:25:59		71		46

		5-Sep-07		2:07:10		75.81		44.5		5-Sep-07		2:06:20		71		47.5		5-Sep-07		2:07:53		72.8		50.5		16-Oct-07		2:25:59		70.41		46.5

		5-Sep-07		4:07:10		75.2		45.5		5-Sep-07		4:06:20		71		55		5-Sep-07		4:07:53		71.6		49		16-Oct-07		4:25:59		69.8		46

		5-Sep-07		6:07:10		75.2		47		5-Sep-07		6:06:20		71.6		55		5-Sep-07		6:07:53		70.41		48		16-Oct-07		6:25:59		70.41		46.5

		5-Sep-07		8:07:10		75.2		45		5-Sep-07		8:06:20		72.21		45.5		5-Sep-07		8:07:53		71		53		16-Oct-07		8:25:59		69.8		47.5

		5-Sep-07		10:07:10		74.6		51.5		5-Sep-07		10:06:20		72.21		55		5-Sep-07		10:07:53		72.8		46.5		16-Oct-07		10:25:59		71		49.5

		5-Sep-07		12:07:10		74.01		50.5		5-Sep-07		12:06:20		71		56		5-Sep-07		12:07:53		72.21		57.5		16-Oct-07		12:25:59		72.21		52

		5-Sep-07		14:07:10		74.01		48		5-Sep-07		14:06:20		71.6		54.5		5-Sep-07		14:07:53		72.21		54		16-Oct-07		14:25:59		73.4		52.5

		5-Sep-07		16:07:10		74.01		49		5-Sep-07		16:06:20		71		54		5-Sep-07		16:07:53		72.21		51		16-Oct-07		16:25:59		75.2		47.5

		5-Sep-07		18:07:10		74.6		49		5-Sep-07		18:06:20		70.41		60		5-Sep-07		18:07:53		71.6		48.5		16-Oct-07		18:25:59		75.81		47.5

		5-Sep-07		20:07:10		74.6		48		5-Sep-07		20:06:20		71.6		55		5-Sep-07		20:07:53		71		58		16-Oct-07		20:25:59		74.01		48.5

		5-Sep-07		22:07:10		75.81		46.5		5-Sep-07		22:06:20		71		55.5		5-Sep-07		22:07:53		75.2		47		16-Oct-07		22:25:59		73.4		49

		6-Sep-07		0:07:10		75.81		43.5		6-Sep-07		0:06:20		71.6		50.5		6-Sep-07		0:07:53		74.6		47		17-Oct-07		0:25:59		72.21		49

		6-Sep-07		2:07:10		75.2		44.5		6-Sep-07		2:06:20		71		52.5		6-Sep-07		2:07:53		73.4		47		17-Oct-07		2:25:59		71		48

		6-Sep-07		4:07:10		75.2		43.5		6-Sep-07		4:06:20		71.6		51		6-Sep-07		4:07:53		72.21		48.5		17-Oct-07		4:25:59		70.41		47.5

		6-Sep-07		6:07:10		75.2		42.5		6-Sep-07		6:06:20		71.6		48.5		6-Sep-07		6:07:53		71		50.5		17-Oct-07		6:25:59		69.8		46

		6-Sep-07		8:07:10		75.2		45.5		6-Sep-07		8:06:20		72.21		52		6-Sep-07		8:07:53		71.6		48.5		17-Oct-07		8:25:59		69.2		46.5

		6-Sep-07		10:07:10		75.2		43.5		6-Sep-07		10:06:20		72.21		46		6-Sep-07		10:07:53		72.21		49.5		17-Oct-07		10:25:59		70.41		49

		6-Sep-07		12:07:10		74.6		41.5		6-Sep-07		12:06:20		71.6		42.5		6-Sep-07		12:07:53		72.21		52		17-Oct-07		12:25:59		71.6		51.5

		6-Sep-07		14:07:10		74.01		40		6-Sep-07		14:06:20		71.6		40.5		6-Sep-07		14:07:53		72.21		42		17-Oct-07		14:25:59		72.21		53

		6-Sep-07		16:07:10		74.6		40		6-Sep-07		16:06:20		71.6		43		6-Sep-07		16:07:53		72.21		40		17-Oct-07		16:25:59		72.8		54

		6-Sep-07		18:07:10		74.6		38		6-Sep-07		18:06:20		69.8		42		6-Sep-07		18:07:53		72.21		37.5		17-Oct-07		18:25:59		74.01		50.5

		6-Sep-07		20:07:10		75.2		38		6-Sep-07		20:06:20		71.6		43		6-Sep-07		20:07:53		75.2		39.5		17-Oct-07		20:25:59		72.21		48.5

		6-Sep-07		22:07:10		75.81		38.5		6-Sep-07		22:06:20		71.6		45.5		6-Sep-07		22:07:53		75.2		39.5		17-Oct-07		22:25:59		71		48

		7-Sep-07		0:07:10		75.81		39		7-Sep-07		0:06:20		71.6		46.5		7-Sep-07		0:07:53		75.2		39.5		18-Oct-07		0:25:59		70.41		47

		7-Sep-07		2:07:10		75.81		39		7-Sep-07		2:06:20		71.6		46		7-Sep-07		2:07:53		74.01		41		18-Oct-07		2:25:59		69.2		45.5

		7-Sep-07		4:07:10		75.2		39		7-Sep-07		4:06:20		71		46		7-Sep-07		4:07:53		72.21		37		18-Oct-07		4:25:59		68.61		45

		7-Sep-07		6:07:10		75.81		38		7-Sep-07		6:06:20		71.6		44		7-Sep-07		6:07:53		71		45.5		18-Oct-07		6:25:59		69.2		46

		7-Sep-07		8:07:10		75.81		41		7-Sep-07		8:06:20		71.6		50		7-Sep-07		8:07:53		71.6		39.5		18-Oct-07		8:25:59		69.2		47

		7-Sep-07		10:07:10		75.2		38.5		7-Sep-07		10:06:20		71.6		40.5		7-Sep-07		10:07:53		72.21		40		18-Oct-07		10:25:59		70.41		50

		7-Sep-07		12:07:10		74.6		40		7-Sep-07		12:06:20		71		42.5		7-Sep-07		12:07:53		72.21		51.5		18-Oct-07		12:25:59		72.8		48.5

		7-Sep-07		14:07:10		74.6		43		7-Sep-07		14:06:20		71.6		42		7-Sep-07		14:07:53		71.6		42.5		18-Oct-07		14:25:59		74.6		45

		7-Sep-07		16:07:10		75.81		46		7-Sep-07		16:06:20		71		61		7-Sep-07		16:07:53		71.6		44.5		18-Oct-07		16:25:59		75.81		43

		7-Sep-07		18:07:10		75.2		45.5		7-Sep-07		18:06:20		71		48		7-Sep-07		18:07:53		71		53.5		18-Oct-07		18:25:59		75.81		43

		7-Sep-07		20:07:10		75.81		49		7-Sep-07		20:06:20		71.6		57		7-Sep-07		20:07:53		71.6		55		18-Oct-07		20:25:59		74.6		43.5

		7-Sep-07		22:07:10		75.81		48.5		7-Sep-07		22:06:20		71.6		58		7-Sep-07		22:07:53		72.8		52		18-Oct-07		22:25:59		73.4		44

		8-Sep-07		0:07:10		75.2		47.5		8-Sep-07		0:06:20		71		56.5		8-Sep-07		0:07:53		72.8		51		19-Oct-07		0:25:59		72.21		44.5

		8-Sep-07		2:07:10		75.2		47		8-Sep-07		2:06:20		71.6		55		8-Sep-07		2:07:53		72.21		51.5		19-Oct-07		2:25:59		71		44.5

		8-Sep-07		4:07:10		75.2		47		8-Sep-07		4:06:20		71		55.5		8-Sep-07		4:07:53		71.6		51		19-Oct-07		4:25:59		70.41		45

		8-Sep-07		6:07:10		75.81		47		8-Sep-07		6:06:20		71.6		54.5		8-Sep-07		6:07:53		71		55		19-Oct-07		6:25:59		70.41		45.5

		8-Sep-07		8:07:10		75.2		47.5		8-Sep-07		8:06:20		72.21		56		8-Sep-07		8:07:53		71.6		57		19-Oct-07		8:25:59		70.41		46.5

		8-Sep-07		10:07:10		74.6		44.5		8-Sep-07		10:06:20		72.21		45		8-Sep-07		10:07:53		72.21		46.5		19-Oct-07		10:25:59		71.6		47.5

		8-Sep-07		12:07:10		74.6		50.5		8-Sep-07		12:06:20		71		57		8-Sep-07		12:07:53		72.21		45		19-Oct-07		12:25:59		73.4		46

		8-Sep-07		14:07:10		74.01		46		8-Sep-07		14:06:20		72.21		46		8-Sep-07		14:07:53		71.6		46.5		19-Oct-07		14:25:59		75.2		45.5

		8-Sep-07		16:07:10		74.01		53		8-Sep-07		16:06:20		71		67		8-Sep-07		16:07:53		71.6		50.5		19-Oct-07		16:25:59		74.6		49

		8-Sep-07		18:07:10		74.01		53		8-Sep-07		18:06:20		70.41		63		8-Sep-07		18:07:53		71		53.5		19-Oct-07		18:25:59		74.6		50.5

		8-Sep-07		20:07:10		74.6		51		8-Sep-07		20:06:20		71		58		8-Sep-07		20:07:53		70.41		57		19-Oct-07		20:25:59		74.01		51.5

		8-Sep-07		22:07:10		74.6		48		8-Sep-07		22:06:20		71		55		8-Sep-07		22:07:53		70.41		54		19-Oct-07		22:25:59		74.01		51

		9-Sep-07		0:07:10		74.6		45		9-Sep-07		0:06:20		71		46		9-Sep-07		0:07:53		69.8		53		20-Oct-07		0:25:59		73.4		51.5

		9-Sep-07		2:07:10		74.01		45.5		9-Sep-07		2:06:20		71		52.5		9-Sep-07		2:07:53		69.2		52.5		20-Oct-07		2:25:59		72.8		52.5

		9-Sep-07		4:07:10		74.01		46.5		9-Sep-07		4:06:20		71		53.5		9-Sep-07		4:07:53		69.2		55		20-Oct-07		4:25:59		72.8		53

		9-Sep-07		6:07:10		74.01		48.5		9-Sep-07		6:06:20		71.6		56		9-Sep-07		6:07:53		68.61		56		20-Oct-07		6:25:59		72.8		54

		9-Sep-07		8:07:10		74.01		46		9-Sep-07		8:06:20		71		50		9-Sep-07		8:07:53		68.61		57		20-Oct-07		8:25:59		72.8		56.5

		9-Sep-07		10:07:10		73.4		50.5		9-Sep-07		10:06:20		70.41		57.5		9-Sep-07		10:07:53		68.61		58		20-Oct-07		10:25:59		74.01		57.5

		9-Sep-07		12:07:10		73.4		51.5		9-Sep-07		12:06:20		70.41		56.5		9-Sep-07		12:07:53		69.8		57.5		20-Oct-07		12:25:59		75.2		57.5

		9-Sep-07		14:07:10		73.4		55		9-Sep-07		14:06:20		70.41		63.5		9-Sep-07		14:07:53		70.41		54.5		20-Oct-07		14:25:59		75.81		57

		9-Sep-07		16:07:10		74.6		54		9-Sep-07		16:06:20		70.41		64.5		9-Sep-07		16:07:53		71		51		20-Oct-07		16:25:59		75.81		57

		9-Sep-07		18:07:10		75.2		50		9-Sep-07		18:06:20		70.41		55		9-Sep-07		18:07:53		70.41		60		20-Oct-07		18:25:59		75.81		56

		9-Sep-07		20:07:10		75.2		44.5		9-Sep-07		20:06:20		71.6		47		9-Sep-07		20:07:53		70.41		55		20-Oct-07		20:25:59		74.01		54.5

		9-Sep-07		22:07:10		74.6		47		9-Sep-07		22:06:20		71		54.5		9-Sep-07		22:07:53		69.8		54		20-Oct-07		22:25:59		72.8		53

		10-Sep-07		0:07:10		74.6		46		10-Sep-07		0:06:20		71		52.5		10-Sep-07		0:07:53		69.2		53.5		21-Oct-07		0:25:59		71.6		51

		10-Sep-07		2:07:10		74.6		45.5		10-Sep-07		2:06:20		71.6		51		10-Sep-07		2:07:53		68.61		53.5		21-Oct-07		2:25:59		71		50

		10-Sep-07		4:07:10		74.01		45		10-Sep-07		4:06:20		71.6		50		10-Sep-07		4:07:53		68.61		54		21-Oct-07		4:25:59		70.41		49.5

		10-Sep-07		6:07:10		74.01		45		10-Sep-07		6:06:20		71		51		10-Sep-07		6:07:53		68		54.5		21-Oct-07		6:25:59		69.8		47.5

		10-Sep-07		8:07:10		72.8		44.5		10-Sep-07		8:06:20		69.8		50.5		10-Sep-07		8:07:53		67.4		54.5		21-Oct-07		8:25:59		69.2		45.5

		10-Sep-07		10:07:10		72.8		45.5		10-Sep-07		10:06:20		69.8		46.5		10-Sep-07		10:07:53		67.4		55		21-Oct-07		10:25:59		69.2		48

		10-Sep-07		12:07:10		72.8		46		10-Sep-07		12:06:20		70.41		49.5		10-Sep-07		12:07:53		68.61		56		21-Oct-07		12:25:59		70.41		45.5

		10-Sep-07		14:07:10		73.4		49		10-Sep-07		14:06:20		70.41		56.5		10-Sep-07		14:07:53		69.8		59.5		21-Oct-07		14:25:59		71		42

		10-Sep-07		16:07:10		74.01		53.5		10-Sep-07		16:06:20		70.41		62.5		10-Sep-07		16:07:53		70.41		49		21-Oct-07		16:25:59		72.21		39

		10-Sep-07		18:07:10		74.6		52.5		10-Sep-07		18:06:20		70.41		63		10-Sep-07		18:07:53		71		56		21-Oct-07		18:25:59		73.4		36.5

		10-Sep-07		20:07:10		75.2		49		10-Sep-07		20:06:20		71.6		55.5		10-Sep-07		20:07:53		71.6		54.5		21-Oct-07		20:25:59		72.21		38

		10-Sep-07		22:07:10		74.6		48		10-Sep-07		22:06:20		71		56		10-Sep-07		22:07:53		70.41		54		21-Oct-07		22:25:59		71		40

		11-Sep-07		0:07:10		74.6		47		11-Sep-07		0:06:20		71		54.5		11-Sep-07		0:07:53		69.8		53.5		22-Oct-07		0:25:59		69.8		39.5

		11-Sep-07		2:07:10		74.01		45.5		11-Sep-07		2:06:20		71		52		11-Sep-07		2:07:53		68.61		53.5		22-Oct-07		2:25:59		69.2		39.5

		11-Sep-07		4:07:10		74.01		44.5		11-Sep-07		4:06:20		71.6		48.5		11-Sep-07		4:07:53		68		53.5		22-Oct-07		4:25:59		69.2		39

		11-Sep-07		6:07:10		74.01		43		11-Sep-07		6:06:20		71		48		11-Sep-07		6:07:53		68.61		52		22-Oct-07		6:25:59		68.61		38.5

		11-Sep-07		8:07:10		74.01		43.5		11-Sep-07		8:06:20		70.41		45		11-Sep-07		8:07:53		71.6		51.5		22-Oct-07		8:25:59		68		37.5

		11-Sep-07		10:07:10		74.6		46.5		11-Sep-07		10:06:20		71		45.5		11-Sep-07		10:07:53		71.6		48		22-Oct-07		10:25:59		68		37.5

		11-Sep-07		12:07:10		74.01		52.5		11-Sep-07		12:06:20		71		63		11-Sep-07		12:07:53		72.21		46		22-Oct-07		12:25:59		69.2		36

		11-Sep-07		14:07:10		74.6		46.5		11-Sep-07		14:06:20		71.6		45		11-Sep-07		14:07:53		71.6		45		22-Oct-07		14:25:59		72.21		33

		11-Sep-07		16:07:10		75.2		48.5		11-Sep-07		16:06:20		70.41		52		11-Sep-07		16:07:53		71		63		22-Oct-07		16:25:59		72.8		33

		11-Sep-07		18:07:10		74.6		49.5		11-Sep-07		18:06:20		70.41		54		11-Sep-07		18:07:53		71		60.5		22-Oct-07		18:25:59		72.8		32.5

		11-Sep-07		20:07:10		75.2		50.5		11-Sep-07		20:06:20		71		58.5		11-Sep-07		20:07:53		70.41		57.5		22-Oct-07		20:25:59		72.8		31.5

		11-Sep-07		22:07:10		75.2		45.5		11-Sep-07		22:06:20		71.6		51.5		11-Sep-07		22:07:53		72.21		52		22-Oct-07		22:25:59		72.21		35

		12-Sep-07		0:07:10		74.6		46.5		12-Sep-07		0:06:20		71.6		53		12-Sep-07		0:07:53		71.6		51		23-Oct-07		0:25:59		71.6		36

		12-Sep-07		2:07:10		74.6		45.5		12-Sep-07		2:06:20		71.6		51.5		12-Sep-07		2:07:53		71		51		23-Oct-07		2:25:59		70.41		37

		12-Sep-07		4:07:10		74.01		46.5		12-Sep-07		4:06:20		70.41		53.5		12-Sep-07		4:07:53		70.41		52		23-Oct-07		4:25:59		69.8		36.5

		12-Sep-07		6:07:10		74.6		46.5		12-Sep-07		6:06:20		71		53		12-Sep-07		6:07:53		70.41		50		23-Oct-07		6:25:59		69.8		36.5

		12-Sep-07		8:07:10		74.01		45.5		12-Sep-07		8:06:20		71.6		44.5		12-Sep-07		8:07:53		71		48.5		23-Oct-07		8:25:59		68.61		37.5

		12-Sep-07		10:07:10		74.01		47.5		12-Sep-07		10:06:20		72.21		55		12-Sep-07		10:07:53		71.6		56		23-Oct-07		10:25:59		71.6		39

		12-Sep-07		12:07:10		74.6		47		12-Sep-07		12:06:20		71.6		53		12-Sep-07		12:07:53		72.21		52		23-Oct-07		12:25:59		74.6		37.5

		12-Sep-07		14:07:10		74.01		46		12-Sep-07		14:06:20		71.6		43		12-Sep-07		14:07:53		71.6		54		23-Oct-07		14:25:59		75.2		37

		12-Sep-07		16:07:10		74.6		49		12-Sep-07		16:06:20		71		53		12-Sep-07		16:07:53		71.6		46.5		23-Oct-07		16:25:59		75.81		36.5

		12-Sep-07		18:07:10		74.6		53		12-Sep-07		18:06:20		70.41		65		12-Sep-07		18:07:53		71		62.5		23-Oct-07		18:25:59		75.81		35.5

		12-Sep-07		20:07:10		74.6		52		12-Sep-07		20:06:20		71		60.5		12-Sep-07		20:07:53		71		54.5		23-Oct-07		20:25:59		74.6		36

		12-Sep-07		22:07:10		74.6		49		12-Sep-07		22:06:20		71.6		56.5		12-Sep-07		22:07:53		72.8		52.5		23-Oct-07		22:25:59		74.01		37.5

		13-Sep-07		0:07:10		75.2		49		13-Sep-07		0:06:20		71.6		56.5		13-Sep-07		0:07:53		72.8		53		24-Oct-07		0:25:59		73.4		38.5

		13-Sep-07		2:07:10		75.2		48.5		13-Sep-07		2:06:20		71		57		13-Sep-07		2:07:53		72.21		53		24-Oct-07		2:25:59		72.21		39

		13-Sep-07		4:07:10		74.6		48.5		13-Sep-07		4:06:20		70.41		58.5		13-Sep-07		4:07:53		71.6		56		24-Oct-07		4:25:59		71		39.5

		13-Sep-07		6:07:10		75.2		49		13-Sep-07		6:06:20		71		58		13-Sep-07		6:07:53		70.41		50.5		24-Oct-07		6:25:59		71		39

		13-Sep-07		8:07:10		74.6		50		13-Sep-07		8:06:20		71		52.5		13-Sep-07		8:07:53		71		56		24-Oct-07		8:25:59		69.8		39.5

		13-Sep-07		10:07:10		74.01		45.5		13-Sep-07		10:06:20		71.6		44.5		13-Sep-07		10:07:53		71.6		57		24-Oct-07		10:25:59		72.21		42.5

		13-Sep-07		12:07:10		74.6		48		13-Sep-07		12:06:20		71.6		52.5		13-Sep-07		12:07:53		71.6		48		24-Oct-07		12:25:59		75.2		41

		13-Sep-07		14:07:10		74.6		45.5		13-Sep-07		14:06:20		71.6		44		13-Sep-07		14:07:53		70.41		61.5		24-Oct-07		14:25:59		75.81		40.5

		13-Sep-07		16:07:10		74.6		52.5		13-Sep-07		16:06:20		70.41		58		13-Sep-07		16:07:53		71		61.5		24-Oct-07		16:25:59		76.4		40.5

		13-Sep-07		18:07:10		75.2		47		13-Sep-07		18:06:20		70.41		51		13-Sep-07		18:07:53		70.41		59.5		24-Oct-07		18:25:59		75.81		42.5

		13-Sep-07		20:07:10		75.2		48		13-Sep-07		20:06:20		71.6		55.5		13-Sep-07		20:07:53		71.6		55		24-Oct-07		20:25:59		75.2		45

		13-Sep-07		22:07:10		74.6		47.5		13-Sep-07		22:06:20		71		54.5		13-Sep-07		22:07:53		71.6		52.5		24-Oct-07		22:25:59		75.81		44.5

		14-Sep-07		0:07:10		74.6		46.5		14-Sep-07		0:06:20		71.6		53		14-Sep-07		0:07:53		71.6		51.5		25-Oct-07		0:25:59		74.6		43

		14-Sep-07		2:07:10		74.6		46.5		14-Sep-07		2:06:20		71		51.5		14-Sep-07		2:07:53		71.6		51.5		25-Oct-07		2:25:59		73.4		43

		14-Sep-07		4:07:10		74.6		44.5		14-Sep-07		4:06:20		71.6		50		14-Sep-07		4:07:53		71		45		25-Oct-07		4:25:59		72.21		43

		14-Sep-07		6:07:10		74.6		43.5		14-Sep-07		6:06:20		71		49.5		14-Sep-07		6:07:53		71		51		25-Oct-07		6:25:59		71.6		43

		14-Sep-07		8:07:10		74.01		46		14-Sep-07		8:06:20		71.6		54		14-Sep-07		8:07:53		71		53		25-Oct-07		8:25:59		71		42.5

		14-Sep-07		10:07:10		74.6		46.5		14-Sep-07		10:06:20		71.6		55.5		14-Sep-07		10:07:53		72.21		47.5		25-Oct-07		10:25:59		73.4		44

		14-Sep-07		12:07:10		74.01		47.5		14-Sep-07		12:06:20		70.41		53		14-Sep-07		12:07:53		72.21		43		25-Oct-07		12:25:59		75.2		44

		14-Sep-07		14:07:10		74.6		49		14-Sep-07		14:06:20		71.6		56		14-Sep-07		14:07:53		71.6		48		25-Oct-07		14:25:59		75.81		43

		14-Sep-07		16:07:10		75.2		46.5		14-Sep-07		16:06:20		71		53		14-Sep-07		16:07:53		71.6		58.5		25-Oct-07		16:25:59		75.81		41

		14-Sep-07		18:07:10		75.2		50.5		14-Sep-07		18:06:20		71		64.5		14-Sep-07		18:07:53		71		62		25-Oct-07		18:25:59		75.81		44.5

		14-Sep-07		20:07:10		75.2		50		14-Sep-07		20:06:20		71.6		59		14-Sep-07		20:07:53		72.8		55.5		25-Oct-07		20:25:59		75.2		43.5

		14-Sep-07		22:07:10		75.2		50.5		14-Sep-07		22:06:20		71.6		59.5		14-Sep-07		22:07:53		74.01		52.5		25-Oct-07		22:25:59		74.6		42.5

		15-Sep-07		0:07:10		75.2		48.5		15-Sep-07		0:06:20		71		51.5		15-Sep-07		0:07:53		73.4		52		26-Oct-07		0:25:59		73.4		42.5

		15-Sep-07		2:07:10		74.6		48		15-Sep-07		2:06:20		71.6		56		15-Sep-07		2:07:53		73.4		52		26-Oct-07		2:25:59		72.21		43

		15-Sep-07		4:07:10		74.6		48.5		15-Sep-07		4:06:20		71.6		55.5		15-Sep-07		4:07:53		72.21		54.5		26-Oct-07		4:25:59		71		42.5

		15-Sep-07		6:07:10		75.2		49.5		15-Sep-07		6:06:20		71.6		58.5		15-Sep-07		6:07:53		71		51		26-Oct-07		6:25:59		70.41		41.5

		15-Sep-07		8:07:10		75.2		46		15-Sep-07		8:06:20		72.21		49		15-Sep-07		8:07:53		71.6		56		26-Oct-07		8:25:59		69.2		41

		15-Sep-07		10:07:10		74.6		50		15-Sep-07		10:06:20		71.6		57.5		15-Sep-07		10:07:53		71.6		50		26-Oct-07		10:25:59		71		44.5

		15-Sep-07		12:07:10		74.01		51		15-Sep-07		12:06:20		71		51		15-Sep-07		12:07:53		72.21		49.5		26-Oct-07		12:25:59		74.6		43.5

		15-Sep-07		14:07:10		74.6		46.5		15-Sep-07		14:06:20		71.6		47.5		15-Sep-07		14:07:53		71.6		54		26-Oct-07		14:25:59		75.81		43.5

		15-Sep-07		16:07:10		74.6		45.5		15-Sep-07		16:06:20		69.2		50.5		15-Sep-07		16:07:53		71.6		53		26-Oct-07		16:25:59		76.4		43.5

		15-Sep-07		18:07:10		73.4		46		15-Sep-07		18:06:20		68		50		15-Sep-07		18:07:53		71		48.5		26-Oct-07		18:25:59		75.81		44

		15-Sep-07		20:07:10		74.6		45		15-Sep-07		20:06:20		71		52		15-Sep-07		20:07:53		71		50.5		26-Oct-07		20:25:59		74.6		43

		15-Sep-07		22:07:10		75.2		44.5		15-Sep-07		22:06:20		71.6		52		15-Sep-07		22:07:53		72.8		48		26-Oct-07		22:25:59		73.4		42.5

		16-Sep-07		0:07:10		75.2		44		16-Sep-07		0:06:20		71		51.5		16-Sep-07		0:07:53		72.8		48		27-Oct-07		0:25:59		72.21		43

		16-Sep-07		2:07:10		75.2		43		16-Sep-07		2:06:20		71.6		49.5		16-Sep-07		2:07:53		72.21		47.5		27-Oct-07		2:25:59		71		44

		16-Sep-07		4:07:10		74.6		44		16-Sep-07		4:06:20		71		51		16-Sep-07		4:07:53		71		48.5		27-Oct-07		4:25:59		70.41		44.5

		16-Sep-07		6:07:10		74.01		43		16-Sep-07		6:06:20		69.8		44		16-Sep-07		6:07:53		71		49		27-Oct-07		6:25:59		70.41		45.5

		16-Sep-07		8:07:10		73.4		44		16-Sep-07		8:06:20		68.61		54		16-Sep-07		8:07:53		70.41		48		27-Oct-07		8:25:59		70.41		46

		16-Sep-07		10:07:10		73.4		45.5		16-Sep-07		10:06:20		68.61		57		16-Sep-07		10:07:53		69.8		52.5		27-Oct-07		10:25:59		72.21		45.5

		16-Sep-07		12:07:10		72.8		46		16-Sep-07		12:06:20		68.61		47.5		16-Sep-07		12:07:53		70.41		56		27-Oct-07		12:25:59		74.6		44

		16-Sep-07		14:07:10		73.4		44.5		16-Sep-07		14:06:20		68.61		47		16-Sep-07		14:07:53		71		51		27-Oct-07		14:25:59		75.2		42.5

		16-Sep-07		16:07:10		74.6		45		16-Sep-07		16:06:20		68.61		52		16-Sep-07		16:07:53		71		50.5		27-Oct-07		16:25:59		75.2		43.5

		16-Sep-07		18:07:10		74.6		46		16-Sep-07		18:06:20		68.61		59		16-Sep-07		18:07:53		70.41		53		27-Oct-07		18:25:59		74.6		44

		16-Sep-07		20:07:10		75.81		45		16-Sep-07		20:06:20		71		54		16-Sep-07		20:07:53		71.6		51.5		27-Oct-07		20:25:59		72.21		43.5

		16-Sep-07		22:07:10		75.2		44.5		16-Sep-07		22:06:20		71		52.5		16-Sep-07		22:07:53		72.21		49.5		27-Oct-07		22:25:59		71.6		44

		17-Sep-07		0:07:10		75.2		43		17-Sep-07		0:06:20		71		51.5		17-Sep-07		0:07:53		71.6		49		28-Oct-07		0:25:59		70.41		43.5

		17-Sep-07		2:07:10		74.6		42.5		17-Sep-07		2:06:20		70.41		49.5		17-Sep-07		2:07:53		70.41		48.5		28-Oct-07		2:25:59		69.2		42.5

		17-Sep-07		4:07:10		74.01		41.5		17-Sep-07		4:06:20		70.41		47		17-Sep-07		4:07:53		69.8		48		28-Oct-07		4:25:59		68.61		42

		17-Sep-07		6:07:10		73.4		41.5		17-Sep-07		6:06:20		69.8		42		17-Sep-07		6:07:53		69.2		49		28-Oct-07		6:25:59		68.61		41.5

		17-Sep-07		8:07:10		72.21		44.5		17-Sep-07		8:06:20		68		52.5		17-Sep-07		8:07:53		69.2		50		28-Oct-07		8:25:59		68		42

		17-Sep-07		10:07:10		72.8		47.5		17-Sep-07		10:06:20		68.61		57.5		17-Sep-07		10:07:53		70.41		49.5		28-Oct-07		10:25:59		67.4		44.5

		17-Sep-07		12:07:10		72.8		50.5		17-Sep-07		12:06:20		68.61		61		17-Sep-07		12:07:53		71		49.5		28-Oct-07		12:25:59		68.61		45.5

		17-Sep-07		14:07:10		74.01		45.5		17-Sep-07		14:06:20		69.2		52		17-Sep-07		14:07:53		71		57		28-Oct-07		14:25:59		69.8		46

		17-Sep-07		16:07:10		74.6		49.5		17-Sep-07		16:06:20		68.61		58		17-Sep-07		16:07:53		71		51.5		28-Oct-07		16:25:59		71.6		47

		17-Sep-07		18:07:10		74.6		48.5		17-Sep-07		18:06:20		68.61		61.5		17-Sep-07		18:07:53		71		50		28-Oct-07		18:25:59		71.6		45

		17-Sep-07		20:07:10		75.81		46		17-Sep-07		20:06:20		71		55		17-Sep-07		20:07:53		74.01		48		28-Oct-07		20:25:59		70.41		45

		17-Sep-07		22:07:10		75.81		44		17-Sep-07		22:06:20		71.6		52		17-Sep-07		22:07:53		74.6		46.5		28-Oct-07		22:25:59		69.8		44.5

		18-Sep-07		0:07:10		75.2		42.5		18-Sep-07		0:06:20		71		50		18-Sep-07		0:07:53		73.4		45.5		29-Oct-07		0:25:59		69.2		44

		18-Sep-07		2:07:10		75.2		41.5		18-Sep-07		2:06:20		71.6		48		18-Sep-07		2:07:53		72.21		45.5		29-Oct-07		2:25:59		68.61		44

		18-Sep-07		4:07:10		74.6		40.5		18-Sep-07		4:06:20		71		46.5		18-Sep-07		4:07:53		71		45.5		29-Oct-07		4:25:59		68.61		44

		18-Sep-07		6:07:10		74.6		39.5		18-Sep-07		6:06:20		69.8		45		18-Sep-07		6:07:53		70.41		45.5		29-Oct-07		6:25:59		68		43.5

		18-Sep-07		8:07:10		72.8		40		18-Sep-07		8:06:20		69.2		39.5		18-Sep-07		8:07:53		71		44.5		29-Oct-07		8:25:59		67.4		43

		18-Sep-07		10:07:10		73.4		42.5		18-Sep-07		10:06:20		70.41		46.5		18-Sep-07		10:07:53		71.6		42.5		29-Oct-07		10:25:59		68.61		45.5

		18-Sep-07		12:07:10		73.4		44.5		18-Sep-07		12:06:20		69.8		51		18-Sep-07		12:07:53		72.21		43.5		29-Oct-07		12:25:59		70.41		46.5

		18-Sep-07		14:07:10		73.4		42.5		18-Sep-07		14:06:20		69.8		42		18-Sep-07		14:07:53		71.6		43.5		29-Oct-07		14:25:59		72.21		47.5

		18-Sep-07		16:07:10		74.01		47.5		18-Sep-07		16:06:20		69.2		61		18-Sep-07		16:07:53		71		49.5		29-Oct-07		16:25:59		74.6		47.5

		18-Sep-07		18:07:10		74.01		43.5		18-Sep-07		18:06:20		69.2		49.5		18-Sep-07		18:07:53		71		43		29-Oct-07		18:25:59		75.2		47

		18-Sep-07		20:07:10		74.6		44		18-Sep-07		20:06:20		71.6		50		18-Sep-07		20:07:53		71.6		51.5		29-Oct-07		20:25:59		74.01		46

		18-Sep-07		22:07:10		75.2		42.5		18-Sep-07		22:06:20		71.6		50.5		18-Sep-07		22:07:53		73.4		46		29-Oct-07		22:25:59		72.8		46

		19-Sep-07		0:07:10		75.2		42.5		19-Sep-07		0:06:20		71		49.5		19-Sep-07		0:07:53		73.4		44.5		30-Oct-07		0:25:59		71.6		46

		19-Sep-07		2:07:10		74.6		41		19-Sep-07		2:06:20		71		48		19-Sep-07		2:07:53		72.8		44		30-Oct-07		2:25:59		71		46

		19-Sep-07		4:07:10		74.6		40		19-Sep-07		4:06:20		71		46		19-Sep-07		4:07:53		71		44		30-Oct-07		4:25:59		69.8		45.5

		19-Sep-07		6:07:10		74.01		38.5		19-Sep-07		6:06:20		70.41		41.5		19-Sep-07		6:07:53		70.41		43.5		30-Oct-07		6:25:59		69.8		46

		19-Sep-07		8:07:10		72.8		41		19-Sep-07		8:06:20		69.8		48		19-Sep-07		8:07:53		71		42.5		30-Oct-07		8:25:59		69.2		48

		19-Sep-07		10:07:10		72.8		43.5		19-Sep-07		10:06:20		70.41		51.5		19-Sep-07		10:07:53		71.6		45.5		30-Oct-07		10:25:59		71		48

		19-Sep-07		12:07:10		73.4		45.5		19-Sep-07		12:06:20		70.41		56		19-Sep-07		12:07:53		72.21		53		30-Oct-07		12:25:59		72.8		49

		19-Sep-07		14:07:10		74.6		43.5		19-Sep-07		14:06:20		72.21		49		19-Sep-07		14:07:53		71.6		41		30-Oct-07		14:25:59		74.6		48

		19-Sep-07		16:07:10		73.4		42.5		19-Sep-07		16:06:20		68.61		45		19-Sep-07		16:07:53		72.21		48		30-Oct-07		16:25:59		75.2		47.5

		19-Sep-07		18:07:10		73.4		42		19-Sep-07		18:06:20		68.61		43		19-Sep-07		18:07:53		71		50		30-Oct-07		18:25:59		75.2		45

		19-Sep-07		20:07:10		74.6		42		19-Sep-07		20:06:20		70.41		49		19-Sep-07		20:07:53		71		47.5		30-Oct-07		20:25:59		72.8		45.5

		19-Sep-07		22:07:10		74.6		39.5		19-Sep-07		22:06:20		70.41		46.5		19-Sep-07		22:07:53		72.21		42.5		30-Oct-07		22:25:59		71.6		46.5

		20-Sep-07		0:07:10		74.6		38		20-Sep-07		0:06:20		70.41		44		20-Sep-07		0:07:53		71.6		41		31-Oct-07		0:25:59		71		46.5

		20-Sep-07		2:07:10		74.01		37		20-Sep-07		2:06:20		70.41		42		20-Sep-07		2:07:53		71		40.5		31-Oct-07		2:25:59		70.41		47.5

		20-Sep-07		4:07:10		73.4		36		20-Sep-07		4:06:20		70.41		41		20-Sep-07		4:07:53		69.8		40.5		31-Oct-07		4:25:59		70.41		48

		20-Sep-07		6:07:10		72.8		36		20-Sep-07		6:06:20		69.8		40		20-Sep-07		6:07:53		69.8		40		31-Oct-07		6:25:59		70.41		48.5

		20-Sep-07		8:07:10		72.8		37.5		20-Sep-07		8:06:20		69.8		44		20-Sep-07		8:07:53		71		39.5		31-Oct-07		8:25:59		69.8		48

		20-Sep-07		10:07:10		73.4		37.5		20-Sep-07		10:06:20		70.41		45.5		20-Sep-07		10:07:53		71.6		35.5		31-Oct-07		10:25:59		71.6		48

		20-Sep-07		12:07:10		73.4		36		20-Sep-07		12:06:20		69.2		35.5		20-Sep-07		12:07:53		72.21		34.5		31-Oct-07		12:25:59		72.21		47.5

		20-Sep-07		14:07:10		73.4		34		20-Sep-07		14:06:20		69.8		36		20-Sep-07		14:07:53		71.6		39.5		31-Oct-07		14:25:59		73.4		46.5

		20-Sep-07		16:07:10		73.4		34		20-Sep-07		16:06:20		68.61		37.5		20-Sep-07		16:07:53		71		33		31-Oct-07		16:25:59		74.6		46

		20-Sep-07		18:07:10		74.01		34.5		20-Sep-07		18:06:20		68		41.5		20-Sep-07		18:07:53		70.41		38.5		31-Oct-07		18:25:59		75.2		44.5

		20-Sep-07		20:07:10		74.6		36		20-Sep-07		20:06:20		69.8		41		20-Sep-07		20:07:53		72.8		37.5		31-Oct-07		20:25:59		72.8		44.5

		20-Sep-07		22:07:10		74.6		34		20-Sep-07		22:06:20		70.41		39.5		20-Sep-07		22:07:53		72.21		36.5		31-Oct-07		22:25:59		72.21		45.5

		21-Sep-07		0:07:10		74.01		34.5		21-Sep-07		0:06:20		69.8		40.5		21-Sep-07		0:07:53		71.6		37.5		1-Nov-07		0:25:59		70.41		46

		21-Sep-07		2:07:10		74.01		33.5		21-Sep-07		2:06:20		70.41		36		21-Sep-07		2:07:53		71		37		1-Nov-07		2:25:59		69.8		47

		21-Sep-07		4:07:10		73.4		33		21-Sep-07		4:06:20		70.41		38		21-Sep-07		4:07:53		69.8		37		1-Nov-07		4:25:59		69.8		48

		21-Sep-07		6:07:10		73.4		34.5		21-Sep-07		6:06:20		69.8		39.5		21-Sep-07		6:07:53		69.8		39		1-Nov-07		6:25:59		69.8		48.5

		21-Sep-07		8:07:10		72.8		37.5		21-Sep-07		8:06:20		69.8		44.5		21-Sep-07		8:07:53		71		39		1-Nov-07		8:25:59		69.8		48.5

		21-Sep-07		10:07:10		72.8		38.5		21-Sep-07		10:06:20		69.8		41.5		21-Sep-07		10:07:53		71.6		42		1-Nov-07		10:25:59		72.21		48

		21-Sep-07		12:07:10		74.6		37		21-Sep-07		12:06:20		73.4		36		21-Sep-07		12:07:53		71.6		36.5		1-Nov-07		12:25:59		72.8		48.5

		21-Sep-07		14:07:10		74.6		38.5		21-Sep-07		14:06:20		71.6		45		21-Sep-07		14:07:53		71		41.5		1-Nov-07		14:25:59		73.4		48.5

		21-Sep-07		16:07:10		74.6		38		21-Sep-07		16:06:20		70.41		45.5		21-Sep-07		16:07:53		71		41		1-Nov-07		16:25:59		74.01		49.5

		21-Sep-07		18:07:10		74.6		37.5		21-Sep-07		18:06:20		70.41		44		21-Sep-07		18:07:53		71		40.5		1-Nov-07		18:25:59		74.01		48

		21-Sep-07		20:07:10		75.81		35		21-Sep-07		20:06:20		72.21		39		21-Sep-07		20:07:53		71.6		39		1-Nov-07		20:25:59		72.21		48

		21-Sep-07		22:07:10		75.81		33.5		21-Sep-07		22:06:20		72.8		37.5		21-Sep-07		22:07:53		71		38		1-Nov-07		22:25:59		71.6		49

		22-Sep-07		0:07:10		75.2		33		22-Sep-07		0:06:20		72.21		37		22-Sep-07		0:07:53		70.41		38.5		2-Nov-07		0:25:59		71		49

		22-Sep-07		2:07:10		74.6		32.5		22-Sep-07		2:06:20		71.6		36.5		22-Sep-07		2:07:53		68.61		38.5		2-Nov-07		2:25:59		70.41		49.5

		22-Sep-07		4:07:10		73.4		33		22-Sep-07		4:06:20		70.41		37.5		22-Sep-07		4:07:53		68		39.5		2-Nov-07		4:25:59		69.8		49

		22-Sep-07		6:07:10		72.8		33.5		22-Sep-07		6:06:20		69.8		37.5		22-Sep-07		6:07:53		67.4		40.5		2-Nov-07		6:25:59		69.8		48

		22-Sep-07		8:07:10		72.8		33.5		22-Sep-07		8:06:20		71.6		37.5		22-Sep-07		8:07:53		69.2		40		2-Nov-07		8:25:59		71.6		46.5

		22-Sep-07		10:07:10		73.4		36		22-Sep-07		10:06:20		72.21		39		22-Sep-07		10:07:53		71.6		43.5		2-Nov-07		10:25:59		71.6		48

		22-Sep-07		12:07:10		73.4		36.5		22-Sep-07		12:06:20		71.6		40.5		22-Sep-07		12:07:53		71.6		44.5		2-Nov-07		12:25:59		73.4		48

		22-Sep-07		14:07:10		74.01		38		22-Sep-07		14:06:20		71		40.5		22-Sep-07		14:07:53		72.21		43		2-Nov-07		14:25:59		75.2		48

		22-Sep-07		16:07:10		74.6		40.5		22-Sep-07		16:06:20		70.41		47		22-Sep-07		16:07:53		71.6		47		2-Nov-07		16:25:59		75.2		49.5

		22-Sep-07		18:07:10		74.6		38.5		22-Sep-07		18:06:20		70.41		45		22-Sep-07		18:07:53		71		38.5		2-Nov-07		18:25:59		75.2		50

		22-Sep-07		20:07:10		75.2		37.5		22-Sep-07		20:06:20		72.21		42		22-Sep-07		20:07:53		70.41		44		2-Nov-07		20:25:59		74.6		46

		22-Sep-07		22:07:10		75.81		37.5		22-Sep-07		22:06:20		72.8		42.5		22-Sep-07		22:07:53		71.6		43		2-Nov-07		22:25:59		73.4		45.5

		23-Sep-07		0:07:10		75.81		38.5		23-Sep-07		0:06:20		73.4		43.5		23-Sep-07		0:07:53		71.6		44.5		3-Nov-07		0:25:59		71.6		45

		23-Sep-07		2:07:10		75.2		40		23-Sep-07		2:06:20		72.21		46.5		23-Sep-07		2:07:53		71		46.5		3-Nov-07		2:25:59		69.8		44

		23-Sep-07		4:07:10		75.2		41		23-Sep-07		4:06:20		72.8		46		23-Sep-07		4:07:53		71		47.5		3-Nov-07		4:25:59		69.2		43

		23-Sep-07		6:07:10		74.6		42		23-Sep-07		6:06:20		71.6		44		23-Sep-07		6:07:53		71.6		48		3-Nov-07		6:25:59		69.2		42

		23-Sep-07		8:07:10		74.01		44.5		23-Sep-07		8:06:20		69.8		52		23-Sep-07		8:07:53		71		43.5		3-Nov-07		8:25:59		71.6		39.5

		23-Sep-07		10:07:10		73.4		44.5		23-Sep-07		10:06:20		70.41		50.5		23-Sep-07		10:07:53		71.6		56		3-Nov-07		10:25:59		71.6		42.5

		23-Sep-07		12:07:10		74.01		44.5		23-Sep-07		12:06:20		70.41		48		23-Sep-07		12:07:53		71		49		3-Nov-07		12:25:59		75.2		42.5

		23-Sep-07		14:07:10		73.4		48.5		23-Sep-07		14:06:20		70.41		56.5		23-Sep-07		14:07:53		71		54		3-Nov-07		14:25:59		76.4		42.5

		23-Sep-07		16:07:10		74.01		50.5		23-Sep-07		16:06:20		70.41		60		23-Sep-07		16:07:53		70.41		51		3-Nov-07		16:25:59		75.81		42

		23-Sep-07		18:07:10		73.4		50.5		23-Sep-07		18:06:20		70.41		59		23-Sep-07		18:07:53		69.8		56.5		3-Nov-07		18:25:59		75.81		43.5

		23-Sep-07		20:07:10		74.6		49.5		23-Sep-07		20:06:20		72.21		55		23-Sep-07		20:07:53		69.8		56		3-Nov-07		20:25:59		74.6		43

		23-Sep-07		22:07:10		74.6		48		23-Sep-07		22:06:20		72.21		52.5		23-Sep-07		22:07:53		70.41		55.5		3-Nov-07		22:25:59		73.4		43.5

		24-Sep-07		0:07:10		74.6		47.5		24-Sep-07		0:06:20		72.21		52		24-Sep-07		0:07:53		69.8		54.5		4-Nov-07		0:25:59		71.6		43

		24-Sep-07		2:07:10		74.6		47.5		24-Sep-07		2:06:20		72.21		52		24-Sep-07		2:07:53		69.8		55		4-Nov-07		2:25:59		70.41		42

		24-Sep-07		4:07:10		74.6		47		24-Sep-07		4:06:20		72.21		51.5		24-Sep-07		4:07:53		69.8		54.5		4-Nov-07		4:25:59		69.2		41

		24-Sep-07		6:07:10		74.01		46.5		24-Sep-07		6:06:20		71.6		46		24-Sep-07		6:07:53		69.8		54.5		4-Nov-07		6:25:59		68.61		40

		24-Sep-07		8:07:10		73.4		49		24-Sep-07		8:06:20		70.41		56		24-Sep-07		8:07:53		69.2		55		4-Nov-07		8:25:59		67.4		38.5

		24-Sep-07		10:07:10		72.8		50.5		24-Sep-07		10:06:20		69.8		56.5		24-Sep-07		10:07:53		69.8		55.5		4-Nov-07		10:25:59		68		40.5

		24-Sep-07		12:07:10		72.8		51		24-Sep-07		12:06:20		69.2		55.5		24-Sep-07		12:07:53		69.8		56		4-Nov-07		12:25:59		69.2		42.5

		24-Sep-07		14:07:10		73.4		50		24-Sep-07		14:06:20		69.8		56.5		24-Sep-07		14:07:53		70.41		51.5		4-Nov-07		14:25:59		71		43

		24-Sep-07		16:07:10		74.01		46		24-Sep-07		16:06:20		69.8		44		24-Sep-07		16:07:53		70.41		48		4-Nov-07		16:25:59		72.21		43

		24-Sep-07		18:07:10		74.01		45		24-Sep-07		18:06:20		69.8		51		24-Sep-07		18:07:53		71		46.5		4-Nov-07		18:25:59		72.8		41.5

		24-Sep-07		20:07:10		75.2		40		24-Sep-07		20:06:20		72.8		39.5		24-Sep-07		20:07:53		72.21		45		4-Nov-07		20:25:59		71.6		39

		24-Sep-07		22:07:10		75.81		40		24-Sep-07		22:06:20		73.4		43.5		24-Sep-07		22:07:53		71.6		45.5		4-Nov-07		22:25:59		70.41		39.5
